## 2024-FULL
Dry Core Transformer Losses Proposed for 2024
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 6.7091 | 0.1002 |  | 6.0878
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.0781 | 9.1064 | 10.1845 | 0.97827 | 11.1628
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.4375 | 12.1418 | 13.5793 | 1.3044 | 14.8837
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.8328 | 15.2748 | 17.1076 | 1.6631 | 18.7706
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.4438 | 21.0532 | 23.497 | 2.2174 | 25.7144
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.9468 | 24.4786 | 27.4255 | 2.6739 | 30.0994
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.3041 | 27.3846 | 30.6887 | 2.9981 | 33.6867 |  | 2024 Proposed Rates
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.8992 | 32.2135 | 36.1127 | 3.5381 | 39.6507 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 4.8515 | 39.9484 | 44.7999 | 4.4022 | 49.2021 | GS 50 to 1,499 kW | 0.0203 | 3.9418 | 2.2887 | 6.4211
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 4.9615 | 40.8649 | 45.8263 | 4.502 | 50.3283 | GS 1,500 to 4,999 kW | 0.02169 | 4.0927 | 2.4461 | 5.9581
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25168 | 45.7304 | 0.77368 | 426.7904 | 5.1907 | 42.7644 | 47.9551 | 4.71 | 52.6651 | Large Use | 0.02443 | 4.5371 | 2.7545 | 5.8841
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 5.5781 | 45.9583 | 51.5365 | 5.0615 | 56.598
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 5.9655 | 49.1522 | 55.1178 | 5.4131 | 60.5308
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 7.403 | 61.2941 | 68.6971 | 6.7174 | 75.4145 | Tier 1 | 0.087 | November 1, 2022 Rate
500 KVA 1PH 1.2KV BIL |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
750 KVA 1PH 1.2KV BIL |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | Tier 2 | 0.103 | November 1, 2022 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.56135 | 4.9433 | 5.5047 | 0.50936 | 6.014
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034807 | 6.3244 | 0.12856 | 74.7619 | 0.86251 | 7.4911 | 8.3537 | 0.78263 | 9.1363 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.725 | 14.9823 | 16.7073 | 1.5653 | 18.2726 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.1562 | 18.2127 | 20.369 | 1.9565 | 22.3255 | RRRP | 0.0007
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.875 | 24.2836 | 27.1586 | 2.6087 | 29.7674
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.2406 | 36.2305 | 40.4711 | 3.8479 | 44.319
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24097 | 43.7844 | 0.76597 | 427.0344 | 5.139 | 42.7889 | 47.9279 | 4.6631 | 52.5909
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 5.567 | 46.6699 | 52.2369 | 5.0515 | 57.2884
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 5.9997 | 50.6048 | 56.6045 | 5.4441 | 62.0486
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28381 | 51.5683 | 0.95881 | 544.3183 | 6.4328 | 54.5407 | 60.9735 | 5.837 | 66.8105
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 7.7984 | 66.4875 | 74.286 | 7.0762 | 81.3622
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5562 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 13.0548 | 120.9261 | 133.9809 | 11.8457 | 145.8266
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 14.8069 | 139.0723 | 153.8792 | 13.4356 | 167.3147
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 19.4068 | 176.2777 | 195.6845 | 17.6095 | 213.2939
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 21.7788 | 199.1964 | 220.9752 | 19.7618 | 240.737
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 29.1101 | 264.4166 | 293.5267 | 26.4142 | 319.9409
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1245 | 204.3274 | 5.1745 | 3160.8274 | 34.7166 | 316.7149 | 351.4315 | 31.5015 | 382.933
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 41.6887 | 380.9601 | 422.6488 | 37.8279 | 460.4767
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 49.164 | 450.6912 | 499.8552 | 44.6108 | 544.4661
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 60.3769 | 555.2879 | 615.6648 | 54.7853 | 670.4502
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 69.3618 | 641.4769 | 710.8387 | 62.9381 | 773.7767
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains May 1, 2022 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2022
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2024 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2023
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2022-0042
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 6.7091 | 0.1002 |  | 6.0878
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.0781 | 9.1064 | 10.1845 | 0.97827 | 11.1628
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.4375 | 12.1418 | 13.5793 | 1.3044 | 14.8837
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.8328 | 15.2748 | 17.1076 | 1.6631 | 18.7706
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.4438 | 21.0532 | 23.497 | 2.2174 | 25.7144
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.9468 | 24.4786 | 27.4255 | 2.6739 | 30.0994
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.3041 | 27.3846 | 30.6887 | 2.9981 | 33.6867
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.8992 | 32.2135 | 36.1127 | 3.5381 | 39.6507
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 4.8515 | 39.9484 | 44.7999 | 4.4022 | 49.2021
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 4.9615 | 40.8649 | 45.8263 | 4.502 | 50.3283
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.1907 | 42.7644 | 47.9551 | 4.71 | 52.6651
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 5.5781 | 45.9583 | 51.5365 | 5.0615 | 56.598
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 5.9655 | 49.1522 | 55.1178 | 5.4131 | 60.5308
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 7.403 | 61.2941 | 68.6971 | 6.7174 | 75.4145
500 KVA 1PH 1.2KV BIL | 0 | 0 | 0 | 0 | 0 | 0 | 0
750 KVA 1PH 1.2KV BIL | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.56135 | 4.9433 | 5.5047 | 0.50936 | 6.014
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.86251 | 7.4911 | 8.3537 | 0.78263 | 9.1363
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.725 | 14.9823 | 16.7073 | 1.5653 | 18.2726
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.1562 | 18.2127 | 20.369 | 1.9565 | 22.3255
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.875 | 24.2836 | 27.1586 | 2.6087 | 29.7674
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.2406 | 36.2305 | 40.4711 | 3.8479 | 44.319
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.139 | 42.7889 | 47.9279 | 4.6631 | 52.5909
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 5.567 | 46.6699 | 52.2369 | 5.0515 | 57.2884
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 5.9997 | 50.6048 | 56.6045 | 5.4441 | 62.0486
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 6.4328 | 54.5407 | 60.9735 | 5.837 | 66.8105
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 7.7984 | 66.4875 | 74.286 | 7.0762 | 81.3622
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 13.0548 | 120.9261 | 133.9809 | 11.8457 | 145.8266
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 14.8069 | 139.0723 | 153.8792 | 13.4356 | 167.3147
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 19.4068 | 176.2777 | 195.6845 | 17.6095 | 213.2939
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 21.7788 | 199.1964 | 220.9752 | 19.7618 | 240.737
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 29.1101 | 264.4166 | 293.5267 | 26.4142 | 319.9409
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 34.7166 | 316.7149 | 351.4315 | 31.5015 | 382.933
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 41.6887 | 380.9601 | 422.6488 | 37.8279 | 460.4767
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 49.164 | 450.6912 | 499.8552 | 44.6108 | 544.4661
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 60.3769 | 555.2879 | 615.6648 | 54.7853 | 670.4502
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 69.3618 | 641.4769 | 710.8387 | 62.9381 | 773.7767
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard