## Appendix 2-R
|  |  |  | File Number: |  |  | EB-2023-0195
|  |  |  | Exhibit: |  |  | 8
|  |  |  | Tab: |  |  | 4
|  |  |  | Schedule: |  |  | 1
|  |  |  | Page: |  |  | 1 of 1
|  |  |  | Date: |  |  | UPDATED
Appendix 2-R
Loss Factors
5-Year Average
|  | 2019 | 2020 | 2021 | 2022 | 2023
Losses Within Distributor's System
A(1) | "Wholesale" kWh delivered to distributor (higher value) | 24420899863.7583 | 23686189277.476 | 23484889467.893 | 24054524228.9199 | 23729818100.7326 | 23875264187.7559
A(2) | "Wholesale" kWh delivered to distributor (lower value) | 24342662265.3663 | 23605244242.4153 | 23407180505.3288 | 23980672710.9006 | 23657833542.7703 | 23798718653.3563
B | Portion of "Wholesale" kWh delivered to distributor for its Large Use Customer(s) | 1927839897.615 | 1816539853.0279 | 1680085795.6806 | 1722691956.1659 | 1696212673.295 | 1768674035.1569
C | Net "Wholesale" kWh delivered to distributor = A(2) - B | 22414822367.7513 | 21788704389.3873 | 21727094709.6483 | 22257980754.7347 | 21961620869.4753 | 22030044618.1994
D | "Retail" kWh delivered by distributor | 23681343595.5124 | 22958447912.3748 | 22775841621.351 | 23359362103.5041 | 23094572706.3623 | 23173913587.8209
E | Portion of "Retail" kWh delivered by distributor to its Large Use Customer(s) | 1911193687.308 | 1802898409.0525 | 1668226732.2402 | 1710331665.4616 | 1684015682.542 | 1755333235.3209
F | Net "Retail" kWh delivered by distributor = D - E | 21770149908.2044 | 21155549503.3223 | 21107614889.1108 | 21649030438.0425 | 21410557023.8203 | 21418580352.5001
G | Loss Factor in Distributor's system = C / F | 1.0296 | 1.0299 | 1.0293 | 1.0281 | 1.0257 | 1.0285
Losses Upstream of Distributor's System
H | Supply Facilities Loss Factor | 1.0032 | 1.0034 | 1.0033 | 1.0031 | 1.003 | 1.0032
Total Losses
I | Total Loss Factor = G x H | 1.0329 | 1.0335 | 1.0328 | 1.0313 | 1.0289 | 1.0319
Notes:
A(1) | If directly connected to the IESO-controlled grid, kWh pertains to the virtual meter on the primary or high voltage side of the transformer at the interface with the transmission grid. This corresponds to the "With Losses" kWh value provided by the IESO's MV-WEB. It is the higher of the two values provided by MV-WEB.
If fully embedded within a host distributor, kWh pertains to the virtual meter on the primary or high voltage side of the transformer, at the interface between the host distributor and the transmission grid. For example, if the host distributor is Hydro One Networks Inc., kWh from the Hydro One Networks' invoice corresponding to "Total kWh w Losses" should be reported. This corresponds to the higher of the two kWh values provided in Hydro One Networks' invoice.
If partially embedded, kWh pertains to the sum of the above.
A(2) | If directly connected to the IESO-controlled grid, kWh pertains to a metering installation on the secondary or low voltage side of the transformer at the interface with the transmission grid. This corresponds to the "Without Losses" kWh value provided by the IESO's MV-WEB. It is the lower of the two kWh values provided by MV-WEB.
If fully embedded with the host distributor, kWh pertains to a metering installation on the secondary or low voltage side of the transformer at the interface between the embedded distributor and the host distributor. For example, if the host distributor is Hydro One Networks Inc., kWh from the Hydro One Networks' invoice corresponding to "Total kWh" should be reported. This corresponds to the lower of the two kWh values provided in Hydro One Networks' invoice.
If partially embedded, kWh pertains to the sum of the above.
Additionally, kWh pertaining to distributed generation directly connected to the distributor's own distribution network should be included in A(2).
B | If a Large Use Customer is metered on the secondary or low voltage side of the transformer, the default loss is 1% (i.e., B = 1.01 X E). This value should not include supply facility losses. However, the total loss factor on the tariff of rate and charges and applied to customers consumption should include the supply facility loss factor.
D | kWh corresponding to D should equal metered or estimated kWh at the customer’s delivery point.
E | Metered consumption of Large Use customers.
G and I | These loss factors pertain to secondary-metered customers with demand less than 5,000 kW.
H | Actual Supply Facility Loss Factor as calculated by dividing A(1) by A(2).