## Sheet1
Asset Condition Assessment ("ACA") Asset Class | Useful Life used in 2020 CIR | Useful Life used in 2025 CIR | Primary Driver for Useful Life Change | Assets past useful life in 2020 CIR (2017 YE) | Assets past useful life in 2025 CIR (2022 YE) | Forecasted Assets past useful life by 2029 (using 2022 YE, assuming no investment) | Probability of Failure ("PoF") Curve Available (Y/N)* | PoF Curve Data
Cable Chambers | 65 | 65 | No change | 11.72% | 20.72% | 30.97% | Y | 3rd Party - Industry Data
4kV Oil Circuit Breaker | 45 | 45 | No change | 67.91% | 93.1% | 93.1% | Y | 3rd Party - Industry Data
AirBlast Circuit Breaker | 45 | 45 | No change | 89.74% | 98.08% | 98.08% | Y | 3rd Party - Industry Data
Air Magnetic Circuit Breaker | 45 | 45 | No change | 44.6% | 74.09% | 84.82% | Y | 3rd Party - Industry Data
Oil KSO Circuit Breaker | 45 | 45 | No change | 35% | 39.13% | 95.65% | Y | 3rd Party - Industry Data
SF6 Circuit Breaker | 45 | 45 | No change | 0% | 0% | 0% | Y | 3rd Party - Industry Data
Vacuum Circuit Breaker | 45 | 45 | No change | 1.796% | 1.212% | 1.455% | Y | 3rd Party - Industry Data
Network Protectors | 30 | 35 | Adopted based on feedback from Depreciation Study (see Exhibit 2A, Tab 2, Schedule 1, Appendix D) | 26.04% | 14.93% | 18.52% | Y | 3rd Party - Industry Data
Overhead Gang operated Switches | 45 | 30 | Adopted based on feedback from Depreciation Study (see Exhibit 2A, Tab 2, Schedule 1, Appendix D) | 3.199% | 29.38% | 47.93% | Y | 3rd Party - Industry Data
Air Insulated Padmount Switch | 30 | 40 | Adopted based on feedback from Depreciation Study (see Exhibit 2A, Tab 2, Schedule 1, Appendix D) | 0% | 6.667% | 14.17% | Y | Toronto Hydro Data
SF6 Insulated Padmount Switch | 40 | 40 | No change | 4.878% | 0% | 0% | Y | Toronto Hydro Data
SCADAMATE Switches | 45 | 30 | Adopted based on feedback from Depreciation Study (see Exhibit 2A, Tab 2, Schedule 1, Appendix D) | 0% | 0.3419% | 1.88% | Y | Toronto Hydro Data
Air Insulated Submersible Switch | 40 | 40 | No change | 11.06% | 13% | 25.18% | Y | Toronto Hydro Data
SF6 Insulated Submersible Switch | 40 | 40 | No change | 5.051% | 3.491% | 6.366% | Y | Toronto Hydro Data
Station Power Transformers | 44 | 45 | Adopted based on feedback from Depreciation Study (see Exhibit 2A, Tab 2, Schedule 1, Appendix D) | 59.5% | 46.24% | 49.71% | Y | Toronto Hydro Data
Network Transformers | 35 | 35 | No change | 19.54% | 18.68% | 22.99% | Y | Toronto Hydro Data
Padmount Transformers | 35 | 30 | Adopted based on feedback from Depreciation Study (see Exhibit 2A, Tab 2, Schedule 1, Appendix D) | 11.73% | 19.55% | 31.99% | Y | Toronto Hydro Data
Submersible Transformers | 33 | 30 | Adopted based on feedback from Depreciation Study (see Exhibit 2A, Tab 2, Schedule 1, Appendix D) | 7.863% | 7.215% | 18.59% | Y | Toronto Hydro Data
Vault Transformers | 35 | 30 | Adopted based on feedback from Depreciation Study (see Exhibit 2A, Tab 2, Schedule 1, Appendix D) | 38.36% | 53.54% | 61.69% | Y | Toronto Hydro Data
Underground Vaults (Combined) | 60 | 60 | No change | 1.14% | 2.874% | 11.92% | Y | 3rd Party - Industry Data
Wood Poles | 45 | 45 | No change | 31.78% | 26.87% | 31.84% | Y | Toronto Hydro Data
*Toronto Hydro does not have a defined timeline for updating the existing PoF curves