## TS & MS
Table 1: TS Switchgear Breakers Condition from Figure 3 including 2017 ACA
HI | 2017 | 2022 | 2029 (Without Investments)
HI1 | 633 | 688 | 631
HI2 | 78 | 46 | 58
HI3 | 302 | 255 | 101
HI4 | 7 | 12 | 200
HI5 | 49 | 28 | 39
Table 2: TS Outdoor Breakers Condition Figure 8 including 2017 ACA
HI | 2017 | 2022 | 2029 (Without Investment)
HI1 | 44 | 72 | 52
HI2 | 8 | 8 | 12
HI3 | 21 | 7 | 4
HI4 | 13 | 5 | 16
HI5 | 3 | 0 | 8
Table 3: MS Air Mag Circuit Breakers Condition from Figure 14 including 2017 ACA
HI | 2017 | 2022 | 2029 (Without Investment)
HI1 | 97 | 13 | 4
HI2 | 70 | 27 | 10
HI3 | 141 | 251 | 22
HI4 | 20 | 1 | 202
HI5 | 39 | 13 | 8
Table 4: MS Power Transformer Condition from Figure 16 including 2017 ACA
HI | 2017 | 2022 | 2029 (Without Investment)
HI1 | 83 | 86 | 61
HI2 | 77 | 64 | 5
HI3 | 61 | 12 | 45
HI4 | 13 | 8 | 6
HI5 | 8 | 0 | 7

## B&A - C&M
Table 15: Relay Type, Quantity, and Useful Life
Relay Type | Number of Assets | Obsolete / Past Useful Life 2024 | Obsolete / Past Useful Life 2029 (With Investments) | Obsolete / Past Useful Life 2029 (Without Investments) | % Obsolete / Past Useful Life 2024 | % Obsolete / Past Useful Life 2029 (With Investments) | % Obsolete / Past Useful Life 2029 (Without Investments)
TS Relay | 1063 | 419 | 307 | 407 | 39% | 29% | 38%
MS Relay | 724 | 365 | 85 | 215 | 50% | 12% | 30%
Pilot Wire Relay | 71 | 14 | 0 | 14 | 20% | 0% | 20%
Transfer Trip Relay | 33 | 7 | 0 | 7 | 21% | 0% | 21%
Total | 1891 | 805 | 392 | 643 | 43% | 21% | 34%
Table 16: Battery and Ancillary Systems Demographics
Asset Type | Total # of Assets | Useful Life | Assets Beyond Useful Life (2024) | Assets Beyond Useful Life Without Investments (2029) | Assets Beyond Useful Life with Investments (2029)
Battery | 148 | 10 | 18 | 69 | 14
Charger | 148 | 20 | 11 | 20 | 16
Station Service Transformers | 44 | 45 | 3 | 3 | 0
AC Panels | 21 | - | 5 | 5 | 0
Air Compressors[1] | 14 | 15 | 0 | 0 | 0
Total | 361 |  | 37 | 97 | 30
Percentage |  |  | 10% | 27% | 8%
[1] No work is planned for in 2025-2029 as no air compressor is beyond useful life. During 2020-2024 one Air Compressor was replaced reactively and the other station was sold to a third party.
Table 17: Battery and Charger Systems Demographics
Asset Type | Assets Beyond Useful Life (2024) | Assets Beyond Useful Life | Assets Beyond Useful Life with Investments (2029)
Without Investments (2029)
MS Battery | 11% | 43% | 11%
TS Battery | 19% | 62% | 0%
MS Charger | 9% | 16% | 13%
TS Charger Systems | 0 | 4% | 0%