## Unit Cost Estimates
Program | Segment | Asset Type | Unit of Measure | Unit Cost Used to Estimate 2025-2029 Program | Assumptions
Generation Protection, Monitoring and Control | Antenna Installation | SCADA RTU | Units | 15000 | Unit cost estimate is based on a combination of antenna installation and material costs from past contracts and purchased material. In addition, it also accounts for foreseeable increases in labour and material.
Generation Protection, Monitoring and Control | Monitoring & Control Systems | SCADA RTU | Units | 10000 | Unit cost estimate is based on the cost of the meter and RTU enclosure.
Metering |  | Residential & Small C&I | Units | 1-Phase: $ 217.26 3-Phase: $ 846.67 3-Phase Delta: $ 843.90 Network: $ 281.90 | Unit cost estimate is based on the 2022 cost of each individual meter along with installation and auxilliary material costs.
Metering |  | Large Customer & Interval |  | ION: $ 10,000.00
Metering |  | Suite Metering |  | $ 650.00
Metering |  | Samp./Meter Repl. | Units | Sampling: $873 Reverification: $242 | Samp / Meter Replacement is dependent on the meter unit type. The Sampling and Reverification unit costs can vary from approximately $200 to $10,000 based on the meter unit type.
Load Demand |  | Load Transfers – Bus | MVA | 250000 | Please refer to Load Demand Program E5.3.4 for details on how cost estimates were derived.
Load Demand |  | Feeder Transfers | # | 500000
Load Demand |  | Cable Upgrades | # | 1850000
Load Demand |  | Network Equipment Upgrades | # | 300000
Load Demand |  | Civil Enhancements | # areas targeted | 5000000
Customer Connections | Generation Connections | Renewable | MW | Not Applicable | There are no forecasted program costs for Generation Connections. For Generation Connections, the cost for Toronto Hydro to facilitate DER connections are recoverable through customer paid fees.
Customer Connections | Generation Connections | Energy Storage | MW
Customer Connections | Generation Connections | Non-Renewable | MW
Area Conversion | Box Construction Conversion | Not Applicable | Poles Converted on Box Construction Feeders | 39837 | Unit costs are based on total actual costs over 2018-2022 divided by the number of poles converted over that period. Note that this unit cost includes the costs for work required to replace all assets such as transformers, conductors, switches, and civil infrastructure and not just poles.
Area Conversion | Rear Lot Conversion | Not Applicable | Rear Lot Customers Converted | 57924 | Unit cost is based on 2020-2022 actual cost of fully completed conversion projects and number of customers converted by such projects. A representative unit cost per customer calculation was provided as part of the response to interrogatory 2B-AMPCO-51 (note that calculation includes 2023 actuals).
Network System Renewal | Network Unit Renewal | Network Units | Units | 300000 | Unit cost estimate is based on historical projects attained in 2022.
Network System Renewal | Network Vault Renewal | Vault Rebuilds | Units | 1800000 | The unit cost estimates for Network Vault Rebuild and Network Vault Roof Rebuild are calculated based on the average costs of projects completed in 2021, 2022, and 2023.
Network System Renewal | Network Vault Renewal | Roof Rebuilds | Units | 360000
Network System Renewal | Network Vault Renewal | Vault Decommission | Units | $150,000 - $180,000 | The unit cost for Network Vault Decommission was derived based on past project(s) - Actual cost range: $150-$180K.
Network Circuit Reconfiguration | Network Circuit Reconfiguration | Reconfiguration | Units | Not Applicable | The projected cost of segment was derived based on the unique reconfiguration requirement of the given network areas. Hence, unit cost is not applicable for estimate projections.
Overhead Renewal | Overhead System Renewal | Poles | Units | 8106.4185 | Unit cost estimates are based on a weighted average of ISA costs related to the Overhead Renewal Program from 2020-2022 specific to each of these asset types.
Overhead Renewal | Overhead System Renewal | Transformers | Units | 18362.3528
Overhead Renewal | Overhead System Renewal | OH Switches | Units | 7313.9024
Overhead Renewal | Overhead System Renewal | Conductors (Primary) | km | 35068.4651
Stations Renewal | Stations TS | TS Switchgear | Units | 16200000 | Unit cost estimates are based on the latest estimates of ongoing projects, with updated material costs and updated Hydro One contributions.
Stations Renewal | Stations TS | TS Breakers (Outdoor) | Units | 600000 | Unit cost estimates are based on historical actuals and updated material costs.
Stations Renewal | Stations TS | TS Switch (Outdoor) | Units | 100000 | Unit cost estimates are based on historical actuals and updated material costs.
Stations Renewal | Stations MS | MS Switchgear | NA | Not Applicable | Program expenditure was not developed on a unit cost basis. Each station can potentially vary as a result of different configurations resulting in variable costs from station to station.
Stations Renewal | Stations MS | Power Transformer | NA | Not Applicable | Program expenditure was not developed on a unit cost basis. Power transformers may have different ratings (capacity, voltage level) for different stations and the cost may vary from station to station.
Stations Renewal | Stations MS | MS Primary Supply | Units | 430000 | Unit cost estimates are based on historical actuals and updated material costs.
Stations Renewal | Stations Control & Monitoring | RTU Renewal TS | Bus Pair | 500000 | Unit cost estimates are dependent on several factors, including how many switchgear supplied, and can vary from one location to the next. The estimates leverage historical ISA and capital expenditure data, but can also consider other inputs such as estimated costs for 2023-2024 projects.
Stations Renewal | Stations Control & Monitoring | General Alarm | Units | 150000
Stations Renewal | Stations Control & Monitoring | RTU Renewal MS | Units | 250000
Stations Renewal | Stations Control & Monitoring | TS Relay | Units/Locations | 185000
Stations Renewal | Stations Control & Monitoring | MS Relay | Units/Locations | 85000
Stations Renewal | Stations Control & Monitoring | Transfer Trip Relay | Units/Locations | 435000
Stations Renewal | Stations Control & Monitoring | Pilot Wire Relay | Units/Locations | 265000
Stations Renewal | Stations Ancillary and Battery | MS Battery units | Units | 31000 | Unit cost estimates are based on historical actuals and updated material costs.
Stations Renewal | Stations Ancillary and Battery | TS Battery units | Units | 93000 | Unit cost estimates are based on historical actuals and updated material costs.
Stations Renewal | Stations Ancillary and Battery | MS Charger units | Units | 45000 | Unit cost estimates are based on historical actuals and updated material costs.
Stations Renewal | Stations Ancillary and Battery | TS Charger units | Units | 110000 | Unit cost estimates are based on historical actuals and updated material costs.
Stations Renewal | Stations Ancillary and Battery | Sump Pump Installations | Units | 750000 | Unit cost estimates are based on historical actuals and updated material costs.
Stations Renewal | Stations Ancillary and Battery | SST | Units | 400000 | Unit cost estimates are based on historical actuals and updated material costs.
Stations Renewal | Stations Ancillary and Battery | AC Panels | Units | 750000 | Unit cost estimates are based on historical actuals and updated material costs.
Underground Renewal - Horseshoe | Underground Circuit Renewal - Horseshoe | Total Cable | Circuit km | 206128 | Unit cost estimate is based on a weighted average of ISA costs related to the Underground Renewal - Horseshoe Program from 2020-2022 specific to this asset type. Civil and secondary cabling costs are not accounted for within the unit cost shown and are proportionally added to the program costs.
Underground Renewal - Horseshoe | Underground Circuit Renewal - Horseshoe | Transformers | Units | 34859 | Unit cost estimate is based on a weighted average of ISA costs related to the Underground Renewal - Horseshoe Program from 2020-2022 specific to this asset type.
Underground Renewal - Horseshoe | Underground Circuit Renewal - Horseshoe | UG Switches | Units | 132910 | Unit cost estimate is based on a weighted average of ISA costs related to the Underground Renewal - Horseshoe Program from 2020-2022 specific to this asset type.
Underground Renewal - Downtown | Underground Cable Renewal | PILC Cable | km | 1200000 | Cost estimate is based on 2022 historical projects. Fully allocated unit cost per year was provided as part of response to interrogatory 2B-Staff-203
Underground Renewal - Downtown | Underground Cable Renewal | AILC Cable | km | 500000 | Cost estimate is based on 2022 historical projects. Fully allocated unit cost per year was provided as part of response to interrogatory 2B-Staff-203
Underground Renewal - Downtown | Underground Cable Renewal | Fiber Optic Cable | km | 100000 | Unit cost estimate is based on latest available project estimates in 2023.
Underground Renewal - Downtown | Cable Chamber Renewal | Cable Chamber | Units | 450000 | The unit cost for each asset type was calculated based on historical ISA data from 2020 to 2022 with additional amounts to capture the trend of increasing cost (e.g. additional civil and electrical work not considered during high level estimating) noted in 2023-2024 design estimates.
Underground Renewal - Downtown | Cable Chamber Renewal | Cable Chamber Roof | Units | 80000
Underground Renewal - Downtown | Cable Chamber Renewal | Cable Chamber Abandonment | Units | 25000
Underground Renewal - Downtown | Cable Chamber Renewal | Cable Chamber Lid | Units | 14350
Underground Renewal - Downtown | Underground Residential Distribution Renewal | URD Submersible Switches | Units | $200,000 | The unit costs for URD TX, URD switches, URD roof rebuild were derived based on the combination of historical projects (2021, 2022) and recently developed work packages at that time, as the sample size of actual attained units was relatively low.
Underground Renewal - Downtown | Underground Residential Distribution Renewal | URD Transformers | Units | $75,000
Underground Renewal - Downtown | Underground Residential Distribution Renewal | URD Vault Roof | Units | $200,000
Underground Renewal - Downtown | Underground Residential Distribution Renewal | FCIs | Units | $2,000 | High-level unit cost was determined based on the preliminary material costs available at the time.
Underground Renewal - Downtown | Underground Switchgear Renewal | Underground Switches | Units | 102500 | The unit costs are bottom-up estimates of labour and material requirements.
Reactive and Corrective Capital |  | Transformers | NA | Not Applicable | Forecasted expenditures within this program were not developed on the basis of asset specific unit costs but rather historical data. For details on how the forecasts were developed, please refer to the Expenditure Plan section E6.7.4 of the Reactive and Corrective Capital Program.
Reactive and Corrective Capital |  | Pole | NA
Reactive and Corrective Capital |  | Switches | NA
Reactive and Corrective Capital |  | Switchgear | NA
Non-Wires Solutions | Energy Storage (ESS) | Battery Energy Storage System | MW | 2220000 | Average cost per MW for a four hour system. Cost is based on industry benchmark for the BESS technology.
Network Condition and Monitoring | NCMC | Commissioned Vaults | Units | 74453 | Unit cost estimate is based on the summed cost of the 3 main components of NCMC (fibre, VCB, and Commissioning). The planned annual program cost depends on how much of each component is planned in a given year.
System Enhancements | Contingency Enhancement | SCADA Switches | Units | 100000 | Unit cost estimate is based on the cost of SCADA unit and associated components. High level cost estimating exercise was conducted using SAP data in 2023 to derive this estimate.
System Enhancements | Contingency Enhancement | Reclosers | Units | 105000 | Unit cost estimate is based on a bottom-up analysis of the cost of a recloser unit and associated components using 2023 data.
System Enhancements | Contingency Enhancement | Undersized circuit replaced | km | 460000 | Unit cost estimate is based on the 2023 cost for the standard trunk cable size used in the Horseshoe system.
System Enhancements | Downtown Contingency | # of Station Ties | NA | Not Applicable | Forecast cost is project specific for one tie between Esplanade and Copeland.
IT-OT Systems | Core Backend Infrastructure Assets |  | NA | Not Applicable | Forecasted expenditures within this program were not developed on the basis of unit costs but rather an aggregate of the burdened costs of multiple components. Please refer to the IT Hardware and Communication Infrastructure E8.4.4.1 and E8.4.4.3 for additional details.
IT-OT Systems | Endpoint Assets |  | NA
IT-OT Systems | IT Hardware - Cybersecurity Systems and Controls |  | NA
IT-OT Systems | Communication Infrastructure |  | NA
Facilities |  | Ontario Building Code Compliance | NA | Not Applicable | Forecasted expenditures were not developed on the basis of asset specific unit costs but rather project specific information.
Facilities |  | Video Management System Upgrades | NA
Fleet and Equipment |  | LD - Pickup Trucks | Units | 110000 | Unit cost estimates are based on historical purchases of similar vehicles over the past (1-3 years), with consideration for future inflationary market condition, potential changes in specifications and technological advancements in the transportation industry.
Fleet and Equipment |  | HD - Cubevan (2020 sprinter & 2020 Command unit) | Units | 340000
Fleet and Equipment |  | HD - Large Digger Derrick | Units | 600000
Fleet and Equipment |  | HD - Single Bucket | Units | 460000
Fleet and Equipment |  | LD - SUV's | Units | 70000
Fleet and Equipment |  | HD - Double Bucket | Units | 500000
Fleet and Equipment |  | HD - Van with Aerial | Units | 500000
Fleet and Equipment |  | HD - Small Crane truck | Units | 500000
Fleet and Equipment |  | HD - Large Crane truck | Units | 600000
Fleet and Equipment |  | HD - Dump Truck | Units | 500000
Fleet and Equipment |  | LD - Passenger Minivan | Units | 100000
Fleet and Equipment |  | LD - Cargo Minivans | Units | 100000
Fleet and Equipment |  | LD - Fullsize Van | Units | 120000
Fleet and Equipment |  | LD - Cars | Units | 60000
File Number: EB-2023-0195
Schedule: JT3.4
Page: 1
Date: 22-Apr-24