## 2025-FULL
Dry Core Transformer Losses Proposed for 2025
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 7.9826 | 0.1199 |  | 6.2222
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.2828 | 10.8967 | 12.1795 | 0.99987 | 13.1794
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.7103 | 14.529 | 16.2393 | 1.3332 | 17.5725
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.1807 | 18.2779 | 20.4586 | 1.6998 | 22.1583
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.9076 | 25.1924 | 28.1 | 2.2664 | 30.3664
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.5062 | 29.2913 | 32.7975 | 2.733 | 35.5304
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.9312 | 32.7686 | 36.6998 | 3.0642 | 39.7641 |  | 2025 Proposed Rates
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.6393 | 38.5469 | 43.1862 | 3.6162 | 46.8023 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.7724 | 47.8025 | 53.5749 | 4.4994 | 58.0742 | GS 50 to 1,499 kW | 0.02068 | 4.7412 | 2.6767 | 6.5553
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 5.9032 | 48.8992 | 54.8024 | 4.6014 | 59.4037 | GS 1,500 to 4,999 kW | 0.0221 | 4.9227 | 2.8608 | 6.0796
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 6.176 | 51.1722 | 57.3482 | 4.814 | 62.1622 | Large Use | 0.02489 | 5.4572 | 3.2215 | 6.0316
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 6.6369 | 54.994 | 61.631 | 5.1733 | 66.8043
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 7.0979 | 58.8159 | 65.9138 | 5.5326 | 71.4463
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 8.8082 | 73.3449 | 82.1531 | 6.8657 | 89.0188 | Tier 1 | 0.103 | November 1, 2023 Rate
500 KVA 1PH 1.2KV BIL |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
750 KVA 1PH 1.2KV BIL |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | Tier 2 | 0.125 | November 1, 2023 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.6679 | 5.9152 | 6.5831 | 0.52061 | 7.1037
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 1.0262 | 8.964 | 9.9902 | 0.79991 | 10.7901 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 2.0524 | 17.9279 | 19.9804 | 1.5998 | 21.5802 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.5655 | 21.7935 | 24.359 | 1.9997 | 26.3587 | RRRP | 0.0014
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.4207 | 29.058 | 32.4787 | 2.6663 | 35.145
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 5.0456 | 43.3536 | 48.3992 | 3.9328 | 52.332
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 6.1145 | 51.2014 | 57.3159 | 4.766 | 62.0819
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 6.6237 | 55.8455 | 62.4692 | 5.163 | 67.6322
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 7.1386 | 60.5541 | 67.6926 | 5.5643 | 73.2569
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 7.6538 | 65.2638 | 72.9176 | 5.9659 | 78.8835
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 9.2787 | 79.5594 | 88.8381 | 7.2324 | 96.0705
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 15.5327 | 144.701 | 160.2337 | 12.1073 | 172.341
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 17.6174 | 166.4149 | 184.0323 | 13.7322 | 197.7645
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 23.0904 | 210.9351 | 234.0255 | 17.9982 | 252.0238
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 25.9127 | 238.3598 | 264.2725 | 20.1981 | 284.4706
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 34.6357 | 316.4026 | 351.0383 | 26.9974 | 378.0357
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 41.3063 | 378.9832 | 420.2895 | 32.1969 | 452.4864
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 49.6018 | 455.8594 | 505.4612 | 38.663 | 544.1242
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 58.496 | 539.3002 | 597.7962 | 45.5957 | 643.3919
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 71.8373 | 664.4613 | 736.2986 | 55.9948 | 792.2934
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 82.5276 | 767.5956 | 850.1232 | 64.3276 | 914.4508
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains May 1, 2022 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2022
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2025 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2025
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2023-0032
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 7.9826 | 0.1199 |  | 6.2222
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.2828 | 10.8967 | 12.1795 | 0.99987 | 13.1794
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.7103 | 14.529 | 16.2393 | 1.3332 | 17.5725
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.1807 | 18.2779 | 20.4586 | 1.6998 | 22.1583
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.9076 | 25.1924 | 28.1 | 2.2664 | 30.3664
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.5062 | 29.2913 | 32.7975 | 2.733 | 35.5304
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.9312 | 32.7686 | 36.6998 | 3.0642 | 39.7641
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.6393 | 38.5469 | 43.1862 | 3.6162 | 46.8023
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.7724 | 47.8025 | 53.5749 | 4.4994 | 58.0742
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 5.9032 | 48.8992 | 54.8024 | 4.6014 | 59.4037
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 6.176 | 51.1722 | 57.3482 | 4.814 | 62.1622
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 6.6369 | 54.994 | 61.631 | 5.1733 | 66.8043
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 7.0979 | 58.8159 | 65.9138 | 5.5326 | 71.4463
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 8.8082 | 73.3449 | 82.1531 | 6.8657 | 89.0188
500 KVA 1PH 1.2KV BIL | 0 | 0 | 0 | 0 | 0 | 0 | 0
750 KVA 1PH 1.2KV BIL | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.6679 | 5.9152 | 6.5831 | 0.52061 | 7.1037
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 1.0262 | 8.964 | 9.9902 | 0.79991 | 10.7901
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 2.0524 | 17.9279 | 19.9804 | 1.5998 | 21.5802
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.5655 | 21.7935 | 24.359 | 1.9997 | 26.3587
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.4207 | 29.058 | 32.4787 | 2.6663 | 35.145
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 5.0456 | 43.3536 | 48.3992 | 3.9328 | 52.332
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 6.1145 | 51.2014 | 57.3159 | 4.766 | 62.0819
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 6.6237 | 55.8455 | 62.4692 | 5.163 | 67.6322
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 7.1386 | 60.5541 | 67.6926 | 5.5643 | 73.2569
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 7.6538 | 65.2638 | 72.9176 | 5.9659 | 78.8835
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 9.2787 | 79.5594 | 88.8381 | 7.2324 | 96.0705
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 15.5327 | 144.701 | 160.2337 | 12.1073 | 172.341
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 17.6174 | 166.4149 | 184.0323 | 13.7322 | 197.7645
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 23.0904 | 210.9351 | 234.0255 | 17.9982 | 252.0238
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 25.9127 | 238.3598 | 264.2725 | 20.1981 | 284.4706
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 34.6357 | 316.4026 | 351.0383 | 26.9974 | 378.0357
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 41.3063 | 378.9832 | 420.2895 | 32.1969 | 452.4864
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 49.6018 | 455.8594 | 505.4612 | 38.663 | 544.1242
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 58.496 | 539.3002 | 597.7962 | 45.5957 | 643.3919
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 71.8373 | 664.4613 | 736.2986 | 55.9948 | 792.2934
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 82.5276 | 767.5956 | 850.1232 | 64.3276 | 914.4508
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard