## 2025-FULL
Dry Core Transformer Losses Updated for 2025
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 8.251 | 0.1075 |  | 6.2222
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.47 | 3.67 | 4.14 | 0.35 | 4.49
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.33 | 9.77 | 11.1 | 1 | 12.1
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.77 | 13.03 | 14.8 | 1.33 | 16.13
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.25 | 16.39 | 18.64 | 1.7 | 20.34
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 3.01 | 22.59 | 25.6 | 2.27 | 27.87
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.62 | 26.26 | 29.88 | 2.73 | 32.61 |  | 2025 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 4.06 | 29.38 | 33.44 | 3.06 | 36.5 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.8 | 34.56 | 39.36 | 3.62 | 42.98 | GS 50 to 1,499 kW | 0.02063 | 4.848 | 2.8187 | 6.5553
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.97 | 42.86 | 48.83 | 4.5 | 53.33 | GS 1,500 to 4,999 kW | 0.02204 | 5.0337 | 3.0126 | 6.0796
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 6.1 | 43.84 | 49.94 | 4.6 | 54.54 | Large Use | 0.02482 | 5.5802 | 3.3924 | 6.0316
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 6.38 | 45.88 | 52.26 | 4.81 | 57.07
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 6.86 | 49.31 | 56.17 | 5.17 | 61.34
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 7.34 | 52.73 | 60.07 | 5.53 | 65.6 | Tier 1 | 0.093
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 8.4 | 60.55 | 68.95 | 6.33 | 75.28
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 9.1 | 65.76 | 74.86 | 6.87 | 81.73 | Tier 2 | 0.11
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.69 | 5.3 | 5.99 | 0.52 | 6.51
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 1.06 | 8.04 | 9.1 | 0.8 | 9.9 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 2.12 | 16.07 | 18.19 | 1.6 | 19.79 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.65 | 19.54 | 22.19 | 2 | 24.19 | RRRP | 0.0015
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.54 | 26.05 | 29.59 | 2.67 | 32.26
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 5.22 | 38.87 | 44.09 | 3.93 | 48.02
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.58 | 41.2 | 46.78 | 4.21 | 50.99
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 6.32 | 45.91 | 52.23 | 4.77 | 57
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 6.85 | 50.07 | 56.92 | 5.16 | 62.08
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 7.38 | 54.29 | 61.67 | 5.56 | 67.23
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 7.91 | 58.51 | 66.42 | 5.97 | 72.39
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 9.59 | 71.33 | 80.92 | 7.23 | 88.15
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 13.9 | 110.27 | 124.17 | 10.48 | 134.65
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 16.06 | 129.74 | 145.8 | 12.11 | 157.91
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 18.21 | 149.2 | 167.41 | 13.73 | 181.14
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 23.87 | 189.12 | 212.99 | 18 | 230.99
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 26.78 | 213.71 | 240.49 | 20.2 | 260.69
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 35.8 | 283.68 | 319.48 | 27 | 346.48
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 42.7 | 339.79 | 382.49 | 32.2 | 414.69
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 51.27 | 408.71 | 459.98 | 38.66 | 498.64
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 60.46 | 483.53 | 543.99 | 45.6 | 589.59
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 74.25 | 595.74 | 669.99 | 55.99 | 725.98
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 85.3 | 688.21 | 773.51 | 64.33 | 837.84
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2024 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2025
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2025 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2025
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0035
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 8.251 | 0.1075 |  | 6.2222
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.47 | 3.67 | 4.14 | 0.35 | 4.49
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.33 | 9.77 | 11.1 | 1 | 12.1
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.77 | 13.03 | 14.8 | 1.33 | 16.13
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.25 | 16.39 | 18.64 | 1.7 | 20.34
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 3.01 | 22.59 | 25.6 | 2.27 | 27.87
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.62 | 26.26 | 29.88 | 2.73 | 32.61
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 4.06 | 29.38 | 33.44 | 3.06 | 36.5
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.8 | 34.56 | 39.36 | 3.62 | 42.98
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.97 | 42.86 | 48.83 | 4.5 | 53.33
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 6.1 | 43.84 | 49.94 | 4.6 | 54.54
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 6.38 | 45.88 | 52.26 | 4.81 | 57.07
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 6.86 | 49.31 | 56.17 | 5.17 | 61.34
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 7.34 | 52.73 | 60.07 | 5.53 | 65.6
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 8.4 | 60.55 | 68.95 | 6.33 | 75.28
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 9.1 | 65.76 | 74.86 | 6.87 | 81.73
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.69 | 5.3 | 5.99 | 0.52 | 6.51
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 1.06 | 8.04 | 9.1 | 0.8 | 9.9
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 2.12 | 16.07 | 18.19 | 1.6 | 19.79
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.65 | 19.54 | 22.19 | 2 | 24.19
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.54 | 26.05 | 29.59 | 2.67 | 32.26
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 5.22 | 38.87 | 44.09 | 3.93 | 48.02
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.58 | 41.2 | 46.78 | 4.21 | 50.99
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 6.32 | 45.91 | 52.23 | 4.77 | 57
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 6.85 | 50.07 | 56.92 | 5.16 | 62.08
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 7.38 | 54.29 | 61.67 | 5.56 | 67.23
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 7.91 | 58.51 | 66.42 | 5.97 | 72.39
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 9.59 | 71.33 | 80.92 | 7.23 | 88.15
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 13.9 | 110.27 | 124.17 | 10.48 | 134.65
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 16.06 | 129.74 | 145.8 | 12.11 | 157.91
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 18.21 | 149.2 | 167.41 | 13.73 | 181.14
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 23.87 | 189.12 | 212.99 | 18 | 230.99
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 26.78 | 213.71 | 240.49 | 20.2 | 260.69
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 35.8 | 283.68 | 319.48 | 27 | 346.48
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 42.7 | 339.79 | 382.49 | 32.2 | 414.69
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 51.27 | 408.71 | 459.98 | 38.66 | 498.64
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 60.46 | 483.53 | 543.99 | 45.6 | 589.59
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 74.25 | 595.74 | 669.99 | 55.99 | 725.98
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 85.3 | 688.21 | 773.51 | 64.33 | 837.84
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard