## Appendix 2-BB Service Life
[12 empty] | File Number: |  | EB-2024-0115
[12 empty] | Exhibit: |  | 2
[12 empty] | Tab: |  | 7
[12 empty] | Schedule: |  | 1
[12 empty] | Attachment: |  | A
[12 empty] | Date: |  | ORIGINAL
Appendix 2-BB
Service Life Comparison
Table F-1 from Kinetrics Report1
|  | Asset Details |  |  | Useful Life |  |  | USoA Account Number | USoA Account Description | Current |  | Proposed |  | Outside Range of Min, Max TUL?
Parent* | # | Category¦ Component ¦ Type |  |  | MIN UL | TUL | MAX UL |  |  | Years | Rate | Years | Rate | Below Min TUL | Above Max TUL
OH | 1 | Fully Dressed Wood Poles | Overall |  | 35 | 45 | 75 | 1830 | Poles, Towers & Fixtures | 45 | 2.222%
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
| 2 | Fully Dressed Concrete Poles | Overall |  | 50 | 60 | 80
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
| 3 | Fully Dressed Steel Poles | Overall |  | 60 | 60 | 80
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
| 4 | OH Line Switch |  |  | 30 | 45 | 55 | 1835 | Overhead Conductors & Devices | 25 | 4%
| 5 | OH Line Switch Motor |  |  | 15 | 25 | 25
| 6 | OH Line Switch RTU |  |  | 15 | 20 | 20 | 1970 | Load Management Controls Customer Premises | 10 | 10%
| 7 | OH Integral Switches |  |  | 35 | 45 | 60
| 8 | OH Conductors |  |  | 50 | 60 | 75 | 1835 | Overhead Conductors & Devices | 45 | 2.222%
| 9 | OH Transformers & Voltage Regulators |  |  | 30 | 40 | 60
| 10 | OH Shunt Capacitor Banks |  |  | 25 | 30 | 40
| 11 | Reclosers |  |  | 25 | 40 | 55 | 1835 | Overhead Conductors & Devices | 25 | 4%
TS & MS | 12 | Power Transformers | Overall |  | 30 | 45 | 60 | 1820 | Distribution Station Equipment <50 kV | 45 | 2.222%
|  |  | Bushing |  | 10 | 20 | 30
|  |  | Tap Changer |  | 20 | 30 | 60
| 13 | Station Service Transformer |  |  | 30 | 45 | 55 | 1820 | Distribution Station Equipment <50 kV | 45 | 2.222%
| 14 | Station Grounding Transformer |  |  | 30 | 40 | 40
| 15 | Station DC System | Overall |  | 10 | 20 | 30
|  |  | Battery Bank |  | 10 | 15 | 15 | 1825 | Storage Battery Equipment | 2025-10-20 | 5%-10%
|  |  | Charger |  | 20 | 20 | 30
| 16 | Station Metal Clad Switchgear | Overall |  | 30 | 40 | 60 | 1820 | Distribution Station Equipment <50 kV | 40 | 2.5%
|  |  | Removable Breaker |  | 25 | 40 | 60 | 1820 | Distribution Station Equipment <50 kV | 25 | 4%
| 17 | Station Independent Breakers |  |  | 35 | 45 | 65
| 18 | Station Switch |  |  | 30 | 50 | 60
| 19 | Electromechanical Relays |  |  | 25 | 35 | 50
| 20 | Solid State Relays |  |  | 10 | 30 | 45
| 21 | Digital & Numeric Relays |  |  | 15 | 20 | 20
| 22 | Rigid Busbars |  |  | 30 | 55 | 60
| 23 | Steel Structure |  |  | 35 | 50 | 90
UG | 24 | Primary Paper Insulated Lead Covered (PILC) Cables |  |  | 60 | 65 | 75 | 1845 | Underground Conductors & Devices | 60 | 1.667%
| 25 | Primary Ethylene-Propylene Rubber (EPR) Cables |  |  | 20 | 25 | 25
| 26 | Primary Non-Tree Retardant (Non-TR) Cross Linked Polyethylene (XLPE) Cables Direct Buried |  |  | 20 | 25 | 30
| 27 | Primary Non-TR XLPE Cables in Duct |  |  | 20 | 25 | 30
| 28 | Primary TR XLPE Cables Direct Buried |  |  | 25 | 30 | 35
| 29 | Primary TR XLPE Cables in Duct |  |  | 35 | 40 | 55
| 30 | Secondary PILC Cables |  |  | 70 | 75 | 80
| 31 | Secondary Cables Direct Buried |  |  | 25 | 35 | 40 | 1855 | Services (Overhead & Underground) | 45 | 2.222%
| 32 | Secondary Cables in Duct |  |  | 35 | 40 | 60 | 1855 | Services (Overhead & Underground) | 45 | 2.222%
| 33 | Network Tranformers | Overall |  | 20 | 35 | 50
|  |  | Protector |  | 20 | 35 | 40
| 34 | Pad-Mounted Transformers |  |  | 25 | 40 | 45 | 1850 | Line Transformers | 35 | 2.857%
| 35 | Submersible/Vault Transformers |  |  | 25 | 35 | 45 | 1850 | Line Transformers | 35 | 2.857%
| 36 | UG Foundation |  |  | 35 | 55 | 70 | 1840 | Underground Conduit | 40 | 2.5%
| 37 | UG Vaults | Overall |  | 40 | 60 | 80
|  |  | Roof |  | 20 | 30 | 45
| 38 | UG Vault Switches |  |  | 20 | 35 | 50 | 1845 | Underground Conductors & Devices | 25 | 4%
| 39 | Pad-Mounted Switchgear |  |  | 20 | 30 | 45
| 40 | Ducts |  |  | 30 | 50 | 85 | 1840 | Underground Conduit | 40 | 2.5%
| 41 | Concrete Encased Duct Banks |  |  | 35 | 55 | 80 | 1840 | Underground Conduit | 40 | 2.5%
| 42 | Cable Chambers |  |  | 50 | 60 | 80
S | 43 | Remote SCADA |  |  | 15 | 20 | 30 | 1980 | System Supervisor Equipment | 15 | 6.667%
Table F-2 from Kinetrics Report1
|  | Asset Details |  |  | Useful Life Range |  |  | USoA Account Number | USoA Account Description | Current |  | Proposed |  | Outside Range of Min, Max TUL?
| # | Category¦ Component ¦ Type | [7 empty] | Years | Rate | Years | Rate | Below Min Range | Above Max Range
| 1 | Office Equipment |  |  | 5 | 15 |  | 1915 | Office Furniture & Equipment | 10 | 10%
| 2 | Vehicles | Trucks & Buckets |  | 5 | 15 |  | 1930 | Transportation Equipment | 2025-08-15 | 7%-13%
|  |  | Trailers |  | 5 | 20 |  | 1930 | Transportation Equipment | 2025-12-15 | 7%-9%%
|  |  | Vans |  | 5 | 10 |  | 1930 | Transportation Equipment | 10 | 10%
| 3 | Administrative Buildings |  |  | 50 | 75 |  | 1908 | Buildings & Fixtures | 20-75 | 1.3%-5%
| 4 | Leasehold Improvements |  |  | Lease dependent
| 5 |  | Station Buildings |  | 20 | 75 |  | 1808 | Buildings | 75 | 1.333%
|  |  | Parking |  | 25 | 30 |  | 1808 | Buildings | 20 | 5%
|  |  | Fence |  | 25 | 60
|  |  | Roof |  | 20 | 30 |  | 1808 | Buildings | 25 | 4%
| 6 | Computer Equipment | Hardware |  | 3 | 5 |  | 1920 | Computer Equipment - Hardware | 2025-04-10 | 10%-25%
|  |  | Software |  | 2 | 5 |  | 1611 | Computer Software | 2025-05-10 | 10%-20%
| 7 | Equipment | Power Operated |  | 5 | 10 |  | 1950 | Power Operated Equipment | 15 | 6.667%
|  |  | Stores |  | 5 | 10 |  | 1935 | Stores Equipment | 10 | 10%
|  |  | Tools, Shop, Garage Equipment |  | 5 | 10 |  | 1940 | Tools, Shop & Garage Equipment | 10 | 10%
|  |  | Measurement & Testing Equipment |  | 5 | 10 |  | 1945 | Measurement & Testing Equipment | 10 | 10%
| 8 | Communication | Towers |  | 60 | 70
|  |  | Wireless |  | 2 | 10 |  | 1955 | Communications Equipment | 8 | 12.5%
| 9 | Residential Energy Meters |  |  | 25 | 35
| 10 | Industrial/Commercial Energy Meters |  |  | 25 | 35
| 11 | Wholesale Energy Meters |  |  | 15 | 30 |  | 1820 | Distribution Station Equipment <50 kV | 15 | 6.667%
| 12 | Current & Potential Transformer (CT & PT) |  |  | 35 | 50
| 13 | Smart Meters |  |  | 5 | 15 |  | 1860 | Meters (Smart Meters) | 15 | 6.667%
| 14 | Repeaters - Smart Metering |  |  | 10 | 15
| 15 | Data Collectors - Smart Metering |  |  | 15 | 20
* TS & MS = Transformer and Municipal Stations UG = Underground Systems S = Monitoring and Control Systems
Note 1: | Tables F-1 and F-2 above are to be used as a reference in order to complete columns J, K, L and N.
See pages 17-19 of Kinetrics Report