## 2026-FULL
Dry Core Transformer Losses Effective Jan 1, 2026
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 8.6344 | 0.1075 |  | 7.9072
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.48795 | 3.6678 | 4.1558 | 0.44686 | 4.6026
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.3875 | 9.7698 | 11.1573 | 1.2707 | 12.428
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.85 | 13.0264 | 14.8764 | 1.6942 | 16.5706
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.3587 | 16.3876 | 18.7463 | 2.1601 | 20.9064
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 3.145 | 22.587 | 25.732 | 2.8802 | 28.6122
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.7925 | 26.262 | 30.0545 | 3.4731 | 33.5276 |  | 2026 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 4.2522 | 29.3797 | 33.6319 | 3.8941 | 37.526 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 5.0181 | 34.5604 | 39.5785 | 4.5955 | 44.174 | GS 50 to 1,499 kW | 0.02456 | 5.1058 | 2.915 | 8.0854
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 6.2437 | 42.8588 | 49.1025 | 5.7179 | 54.8204 | GS 1,500 to 4,999 kW | 0.02625 | 5.3013 | 3.1155 | 7.756
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 6.3852 | 43.842 | 50.2273 | 5.8475 | 56.0748 | Large Use | 0.02956 | 5.8769 | 3.5083 | 7.8803
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 6.6803 | 45.88 | 52.5603 | 6.1177 | 58.678
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 7.1789 | 49.3066 | 56.4854 | 6.5743 | 63.0597
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 7.6774 | 52.7332 | 60.4106 | 7.0309 | 67.4415 | Tier 1 | 0.093 | November 1, 2024 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 8.7888 | 60.5522 | 69.341 | 8.0487 | 77.3897
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 9.5274 | 65.7596 | 75.287 | 8.7251 | 84.0121
[14 empty] | Tier 2 | 0.11 | November 1, 2024 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.72244 | 5.3035 | 6.0259 | 0.6616 | 6.6875
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 1.11 | 8.0369 | 9.1469 | 1.0165 | 10.1635 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 2.22 | 16.0738 | 18.2938 | 2.0331 | 20.3269 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.775 | 19.5396 | 22.3146 | 2.5413 | 24.8559 | RRRP | 0.0015
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.7 | 26.0528 | 29.7528 | 3.3884 | 33.1412
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 5.4575 | 38.87 | 44.3276 | 4.9979 | 49.3255
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.8408 | 41.1958 | 47.0366 | 5.3489 | 52.3855
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 6.6137 | 45.9062 | 52.5199 | 6.0567 | 58.5767
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 7.1646 | 50.07 | 57.2346 | 6.5612 | 63.7958
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 7.7215 | 54.2916 | 62.013 | 7.0712 | 69.0842
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 8.2788 | 58.5142 | 66.793 | 7.5816 | 74.3746
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 10.0363 | 71.3314 | 81.3677 | 9.1911 | 90.5588
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 14.5461 | 110.2679 | 124.814 | 13.3211 | 138.1351
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 16.801 | 129.7361 | 146.5371 | 15.3861 | 161.9232
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 19.0559 | 149.2043 | 168.2602 | 17.4511 | 185.7113
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 24.9758 | 189.1203 | 214.0961 | 22.8725 | 236.9686
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 28.0285 | 213.7087 | 241.7373 | 25.6681 | 267.4053
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 37.4638 | 283.6804 | 321.1442 | 34.3087 | 355.4529
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 44.6791 | 339.7889 | 384.468 | 40.9164 | 425.3844
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 53.6519 | 408.7147 | 462.3666 | 49.1336 | 511.5002
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 63.2724 | 483.526 | 546.7984 | 57.9438 | 604.7422
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 77.703 | 595.743 | 673.4461 | 71.1592 | 744.6052
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 89.2662 | 688.2112 | 777.4775 | 81.7485 | 859.226
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2024 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2024
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2027-FULL
Dry Core Transformer Losses Effective Jan 1, 2027
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 8.6351 | 0.1075 |  | 8.7449
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.48799 | 3.6678 | 4.1558 | 0.4942 | 4.65
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.3876 | 9.7698 | 11.1574 | 1.4053 | 12.5627
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.8502 | 13.0264 | 14.8766 | 1.8737 | 16.7502
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.3589 | 16.3876 | 18.7465 | 2.3889 | 21.1355
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 3.1453 | 22.587 | 25.7323 | 3.1853 | 28.9176
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.7928 | 26.262 | 30.0548 | 3.841 | 33.8958 |  | 2027 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 4.2525 | 29.3797 | 33.6322 | 4.3066 | 37.9389 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 5.0185 | 34.5604 | 39.5789 | 5.0823 | 44.6612 | GS 50 to 1,499 kW | 0.0252 | 5.1058 | 2.915 | 8.8107
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 6.2442 | 42.8588 | 49.103 | 6.3236 | 55.4266 | GS 1,500 to 4,999 kW | 0.02694 | 5.3013 | 3.1155 | 8.5495
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 6.3857 | 43.842 | 50.2278 | 6.467 | 56.6948 | Large Use | 0.03034 | 5.8769 | 3.5083 | 8.8746
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 6.6808 | 45.88 | 52.5608 | 6.7658 | 59.3266
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 7.1795 | 49.3066 | 56.486 | 7.2708 | 63.7568
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 7.6781 | 52.7332 | 60.4113 | 7.7757 | 68.187 | Tier 1 | 0.093 | November 1, 2024 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 8.7895 | 60.5522 | 69.3417 | 8.9014 | 78.2431
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 9.5282 | 65.7596 | 75.2878 | 9.6494 | 84.9372
[14 empty] | Tier 2 | 0.11 | November 1, 2024 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.7225 | 5.3035 | 6.026 | 0.73169 | 6.7576
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 1.1101 | 8.0369 | 9.147 | 1.1242 | 10.2712 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 2.2202 | 16.0738 | 18.294 | 2.2485 | 20.5425 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.7752 | 19.5396 | 22.3148 | 2.8105 | 25.1254 | RRRP | 0.0015
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.7003 | 26.0528 | 29.7531 | 3.7474 | 33.5005
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 5.458 | 38.87 | 44.328 | 5.5274 | 49.8554
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.8413 | 41.1958 | 47.0371 | 5.9156 | 52.9526
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 6.6143 | 45.9062 | 52.5205 | 6.6984 | 59.2189
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 7.1652 | 50.07 | 57.2352 | 7.2563 | 64.4915
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 7.7221 | 54.2916 | 62.0137 | 7.8203 | 69.834
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 8.2795 | 58.5142 | 66.7937 | 8.3848 | 75.1785
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 10.0371 | 71.3314 | 81.3686 | 10.1648 | 91.5334
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 14.5473 | 110.2679 | 124.8152 | 14.7323 | 139.5475
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 16.8024 | 129.7361 | 146.5385 | 17.0161 | 163.5546
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 19.0575 | 149.2043 | 168.2618 | 19.2999 | 187.5617
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 24.9779 | 189.1203 | 214.0982 | 25.2956 | 239.3938
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 28.0308 | 213.7087 | 241.7396 | 28.3874 | 270.1269
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 37.4668 | 283.6804 | 321.1472 | 37.9434 | 359.0906
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 44.6827 | 339.7889 | 384.4717 | 45.2511 | 429.7228
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 53.6563 | 408.7147 | 462.371 | 54.3388 | 516.7098
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 63.2775 | 483.526 | 546.8035 | 64.0824 | 610.886
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 77.7094 | 595.743 | 673.4524 | 78.6978 | 752.1502
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 89.2735 | 688.2112 | 777.4847 | 90.4091 | 867.8938
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2024 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2024
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2028-FULL
Dry Core Transformer Losses Effective Jan 1, 2028
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 8.6355 | 0.1075 |  | 9.5987
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.48801 | 3.6678 | 4.1558 | 0.54245 | 4.6983
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.3877 | 9.7698 | 11.1575 | 1.5425 | 12.6999
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.8502 | 13.0264 | 14.8766 | 2.0566 | 16.9333
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.359 | 16.3876 | 18.7466 | 2.6222 | 21.3688
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 3.1454 | 22.587 | 25.7324 | 3.4963 | 29.2287
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.7929 | 26.262 | 30.0549 | 4.2161 | 34.271 |  | 2028 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 4.2527 | 29.3797 | 33.6324 | 4.7271 | 38.3595 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 5.0187 | 34.5604 | 39.5791 | 5.5785 | 45.1576 | GS 50 to 1,499 kW | 0.02553 | 5.1058 | 2.915 | 9.5497
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 6.2445 | 42.8588 | 49.1033 | 6.941 | 56.0443 | GS 1,500 to 4,999 kW | 0.02729 | 5.3013 | 3.1155 | 9.3593
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 6.386 | 43.842 | 50.2281 | 7.0984 | 57.3264 | Large Use | 0.03073 | 5.8769 | 3.5083 | 9.8872
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 6.6811 | 45.88 | 52.5611 | 7.4264 | 59.9875
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 7.1798 | 49.3066 | 56.4863 | 7.9807 | 64.467
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 7.6784 | 52.7332 | 60.4116 | 8.5349 | 68.9465 | Tier 1 | 0.093 | November 1, 2024 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 8.7899 | 60.5522 | 69.3421 | 9.7704 | 79.1125
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 9.5286 | 65.7596 | 75.2882 | 10.5915 | 85.8797
[14 empty] | Tier 2 | 0.11 | November 1, 2024 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.72253 | 5.3035 | 6.026 | 0.80313 | 6.8291
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 1.1102 | 8.0369 | 9.1471 | 1.234 | 10.381 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 2.2203 | 16.0738 | 18.2941 | 2.468 | 20.7621 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.7753 | 19.5396 | 22.315 | 3.0849 | 25.3999 | RRRP | 0.0015
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.7005 | 26.0528 | 29.7533 | 4.1132 | 33.8665
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 5.4582 | 38.87 | 44.3282 | 6.0671 | 50.3953
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.8415 | 41.1958 | 47.0373 | 6.4931 | 53.5304
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 6.6145 | 45.9062 | 52.5207 | 7.3524 | 59.8731
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 7.1655 | 50.07 | 57.2354 | 7.9648 | 65.2002
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 7.7224 | 54.2916 | 62.014 | 8.5838 | 70.5978
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 8.2798 | 58.5142 | 66.794 | 9.2034 | 75.9974
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 10.0375 | 71.3314 | 81.369 | 11.1572 | 92.5262
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 14.5479 | 110.2679 | 124.8158 | 16.1707 | 140.9865
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 16.8031 | 129.7361 | 146.5392 | 18.6775 | 165.2166
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 19.0583 | 149.2043 | 168.2626 | 21.1842 | 189.4468
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 24.9789 | 189.1203 | 214.0992 | 27.7653 | 241.8645
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 28.032 | 213.7087 | 241.7407 | 31.1589 | 272.8996
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 37.4684 | 283.6804 | 321.1488 | 41.6479 | 362.7967
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 44.6846 | 339.7889 | 384.4735 | 49.6691 | 434.1426
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 53.6585 | 408.7147 | 462.3732 | 59.6441 | 522.0173
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 63.2801 | 483.526 | 546.8062 | 70.339 | 617.1452
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 77.7126 | 595.743 | 673.4556 | 86.3814 | 759.837
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 89.2772 | 688.2112 | 777.4884 | 99.236 | 876.7244
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2024 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2024
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2029-FULL
Dry Core Transformer Losses Effective Jan 1, 2029
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 8.6359 | 0.1075 |  | 10.2702
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.48804 | 3.6678 | 4.1559 | 0.5804 | 4.7363
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.3877 | 9.7698 | 11.1575 | 1.6504 | 12.8079
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.8503 | 13.0264 | 14.8767 | 2.2005 | 17.0772
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.3592 | 16.3876 | 18.7468 | 2.8056 | 21.5524
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 3.1456 | 22.587 | 25.7326 | 3.7409 | 29.4735
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.7931 | 26.262 | 30.0551 | 4.511 | 34.5661 |  | 2029 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 4.2529 | 29.3797 | 33.6326 | 5.0578 | 38.6904 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 5.019 | 34.5604 | 39.5794 | 5.9688 | 45.5482 | GS 50 to 1,499 kW | 0.02595 | 5.1058 | 2.915 | 10.1577
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 6.2448 | 42.8588 | 49.1036 | 7.4266 | 56.5302 | GS 1,500 to 4,999 kW | 0.02773 | 5.3013 | 3.1155 | 10.0269
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 6.3863 | 43.842 | 50.2284 | 7.5949 | 57.8233 | Large Use | 0.03123 | 5.8769 | 3.5083 | 10.6261
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 6.6815 | 45.88 | 52.5614 | 7.9459 | 60.5074
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 7.1801 | 49.3066 | 56.4867 | 8.539 | 65.0257
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 7.6788 | 52.7332 | 60.412 | 9.132 | 69.544 | Tier 1 | 0.093 | November 1, 2024 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 8.7904 | 60.5522 | 69.3425 | 10.4539 | 79.7965
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 9.5291 | 65.7596 | 75.2887 | 11.3325 | 86.6212
[14 empty] | Tier 2 | 0.11 | November 1, 2024 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.72257 | 5.3035 | 6.026 | 0.85931 | 6.8853
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 1.1102 | 8.0369 | 9.1471 | 1.3203 | 10.4674 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 2.2204 | 16.0738 | 18.2942 | 2.6406 | 20.9349 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.7755 | 19.5396 | 22.3151 | 3.3008 | 25.6158 | RRRP | 0.0015
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.7007 | 26.0528 | 29.7535 | 4.401 | 34.1545
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 5.4585 | 38.87 | 44.3285 | 6.4915 | 50.82
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.8418 | 41.1958 | 47.0376 | 6.9474 | 53.985
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 6.6149 | 45.9062 | 52.5211 | 7.8667 | 60.3878
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 7.1658 | 50.07 | 57.2358 | 8.522 | 65.7578
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 7.7228 | 54.2916 | 62.0144 | 9.1843 | 71.1987
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 8.2802 | 58.5142 | 66.7945 | 9.8473 | 76.6417
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 10.0381 | 71.3314 | 81.3695 | 11.9378 | 93.3073
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 14.5487 | 110.2679 | 124.8165 | 17.302 | 142.1185
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 16.804 | 129.7361 | 146.5401 | 19.9841 | 166.5241
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 19.0593 | 149.2043 | 168.2636 | 22.6662 | 190.9298
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 24.9802 | 189.1203 | 214.1005 | 29.7077 | 243.8082
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 28.0334 | 213.7087 | 241.7422 | 33.3387 | 275.0809
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 37.4703 | 283.6804 | 321.1508 | 44.5615 | 365.7123
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 44.6869 | 339.7889 | 384.4759 | 53.1438 | 437.6197
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 53.6613 | 408.7147 | 462.376 | 63.8167 | 526.1927
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 63.2835 | 483.526 | 546.8095 | 75.2598 | 622.0692
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 77.7167 | 595.743 | 673.4597 | 92.4244 | 765.8841
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 89.2819 | 688.2112 | 777.4931 | 106.1783 | 883.6714
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2024 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2024
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2030-FULL
Dry Core Transformer Losses Effective Jan 1, 2030
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 8.6364 | 0.1075 |  | 11.0118
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.48807 | 3.6678 | 4.1559 | 0.62231 | 4.7782
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.3878 | 9.7698 | 11.1576 | 1.7695 | 12.9272
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.8504 | 13.0264 | 14.8768 | 2.3594 | 17.2362
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.3593 | 16.3876 | 18.7469 | 3.0082 | 21.7551
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 3.1458 | 22.587 | 25.7328 | 4.011 | 29.7438
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.7934 | 26.262 | 30.0554 | 4.8367 | 34.8921 |  | 2030 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 4.2532 | 29.3797 | 33.6329 | 5.423 | 39.0559 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 5.0193 | 34.5604 | 39.5797 | 6.3998 | 45.9795 | GS 50 to 1,499 kW | 0.0264 | 5.1058 | 2.915 | 10.7699
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 6.2452 | 42.8588 | 49.1039 | 7.9629 | 57.0668 | GS 1,500 to 4,999 kW | 0.02822 | 5.3013 | 3.1155 | 10.609
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 6.3867 | 43.842 | 50.2288 | 8.1434 | 58.3721 | Large Use | 0.03177 | 5.8769 | 3.5083 | 11.6566
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 6.6819 | 45.88 | 52.5618 | 8.5197 | 61.0815
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 7.1805 | 49.3066 | 56.4871 | 9.1555 | 65.6427
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 7.6792 | 52.7332 | 60.4124 | 9.7914 | 70.2038 | Tier 1 | 0.093 | November 1, 2024 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 8.7909 | 60.5522 | 69.343 | 11.2088 | 80.5518
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 9.5297 | 65.7596 | 75.2893 | 12.1508 | 87.44
[14 empty] | Tier 2 | 0.11 | November 1, 2024 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.72261 | 5.3035 | 6.0261 | 0.92136 | 6.9474
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 1.1103 | 8.0369 | 9.1472 | 1.4157 | 10.5628 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 2.2205 | 16.0738 | 18.2944 | 2.8313 | 21.1257 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.7757 | 19.5396 | 22.3153 | 3.5391 | 25.8544 | RRRP | 0.0015
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.7009 | 26.0528 | 29.7537 | 4.7188 | 34.4725
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 5.4588 | 38.87 | 44.3288 | 6.9602 | 51.2891
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.8421 | 41.1958 | 47.0379 | 7.449 | 54.4869
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 6.6153 | 45.9062 | 52.5215 | 8.4348 | 60.9563
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 7.1662 | 50.07 | 57.2362 | 9.1373 | 66.3736
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 7.7232 | 54.2916 | 62.0148 | 9.8475 | 71.8623
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 8.2807 | 58.5142 | 66.7949 | 10.5583 | 77.3532
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 10.0386 | 71.3314 | 81.3701 | 12.7998 | 94.1698
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 14.5495 | 110.2679 | 124.8174 | 18.5513 | 143.3687
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 16.8049 | 129.7361 | 146.541 | 21.4271 | 167.9681
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 19.0604 | 149.2043 | 168.2647 | 24.3029 | 192.5676
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 24.9816 | 189.1203 | 214.1019 | 31.8528 | 245.9548
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 28.035 | 213.7087 | 241.7438 | 35.7461 | 277.4899
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 37.4725 | 283.6804 | 321.1529 | 47.7792 | 368.9321
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 44.6895 | 339.7889 | 384.4784 | 56.9813 | 441.4597
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 53.6644 | 408.7147 | 462.3791 | 68.4248 | 530.8039
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 63.2871 | 483.526 | 546.8131 | 80.6942 | 627.5073
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 77.7211 | 595.743 | 673.4641 | 99.0982 | 772.5624
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 89.287 | 688.2112 | 777.4982 | 113.8453 | 891.3435
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2024 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2024
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2026 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2026
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 8.6344 | 0.1075 |  | 7.9072
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.48795 | 3.6678 | 4.1558 | 0.44686 | 4.6026
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.3875 | 9.7698 | 11.1573 | 1.2707 | 12.428
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.85 | 13.0264 | 14.8764 | 1.6942 | 16.5706
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.3587 | 16.3876 | 18.7463 | 2.1601 | 20.9064
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 3.145 | 22.587 | 25.732 | 2.8802 | 28.6122
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.7925 | 26.262 | 30.0545 | 3.4731 | 33.5276
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 4.2522 | 29.3797 | 33.6319 | 3.8941 | 37.526
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 5.0181 | 34.5604 | 39.5785 | 4.5955 | 44.174
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 6.2437 | 42.8588 | 49.1025 | 5.7179 | 54.8204
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 6.3852 | 43.842 | 50.2273 | 5.8475 | 56.0748
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 6.6803 | 45.88 | 52.5603 | 6.1177 | 58.678
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 7.1789 | 49.3066 | 56.4854 | 6.5743 | 63.0597
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 7.6774 | 52.7332 | 60.4106 | 7.0309 | 67.4415
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 8.7888 | 60.5522 | 69.341 | 8.0487 | 77.3897
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 9.5274 | 65.7596 | 75.287 | 8.7251 | 84.0121
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.72244 | 5.3035 | 6.0259 | 0.6616 | 6.6875
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 1.11 | 8.0369 | 9.1469 | 1.0165 | 10.1635
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 2.22 | 16.0738 | 18.2938 | 2.0331 | 20.3269
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.775 | 19.5396 | 22.3146 | 2.5413 | 24.8559
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.7 | 26.0528 | 29.7528 | 3.3884 | 33.1412
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 5.4575 | 38.87 | 44.3276 | 4.9979 | 49.3255
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.8408 | 41.1958 | 47.0366 | 5.3489 | 52.3855
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 6.6137 | 45.9062 | 52.5199 | 6.0567 | 58.5767
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 7.1646 | 50.07 | 57.2346 | 6.5612 | 63.7958
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 7.7215 | 54.2916 | 62.013 | 7.0712 | 69.0842
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 8.2788 | 58.5142 | 66.793 | 7.5816 | 74.3746
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 10.0363 | 71.3314 | 81.3677 | 9.1911 | 90.5588
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 14.5461 | 110.2679 | 124.814 | 13.3211 | 138.1351
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 16.801 | 129.7361 | 146.5371 | 15.3861 | 161.9232
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 19.0559 | 149.2043 | 168.2602 | 17.4511 | 185.7113
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 24.9758 | 189.1203 | 214.0961 | 22.8725 | 236.9686
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 28.0285 | 213.7087 | 241.7373 | 25.6681 | 267.4053
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 37.4638 | 283.6804 | 321.1442 | 34.3087 | 355.4529
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 44.6791 | 339.7889 | 384.468 | 40.9164 | 425.3844
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 53.6519 | 408.7147 | 462.3666 | 49.1336 | 511.5002
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 63.2724 | 483.526 | 546.7984 | 57.9438 | 604.7422
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 77.703 | 595.743 | 673.4461 | 71.1592 | 744.6052
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 89.2662 | 688.2112 | 777.4775 | 81.7485 | 859.226
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2027 PDF
PROPOSED - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2027
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 8.6351 | 0.1075 |  | 8.7449
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.48799 | 3.6678 | 4.1558 | 0.4942 | 4.65
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.3876 | 9.7698 | 11.1574 | 1.4053 | 12.5627
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.8502 | 13.0264 | 14.8766 | 1.8737 | 16.7502
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.3589 | 16.3876 | 18.7465 | 2.3889 | 21.1355
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 3.1453 | 22.587 | 25.7323 | 3.1853 | 28.9176
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.7928 | 26.262 | 30.0548 | 3.841 | 33.8958
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 4.2525 | 29.3797 | 33.6322 | 4.3066 | 37.9389
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 5.0185 | 34.5604 | 39.5789 | 5.0823 | 44.6612
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 6.2442 | 42.8588 | 49.103 | 6.3236 | 55.4266
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 6.3857 | 43.842 | 50.2278 | 6.467 | 56.6948
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 6.6808 | 45.88 | 52.5608 | 6.7658 | 59.3266
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 7.1795 | 49.3066 | 56.486 | 7.2708 | 63.7568
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 7.6781 | 52.7332 | 60.4113 | 7.7757 | 68.187
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 8.7895 | 60.5522 | 69.3417 | 8.9014 | 78.2431
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 9.5282 | 65.7596 | 75.2878 | 9.6494 | 84.9372
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.7225 | 5.3035 | 6.026 | 0.73169 | 6.7576
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 1.1101 | 8.0369 | 9.147 | 1.1242 | 10.2712
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 2.2202 | 16.0738 | 18.294 | 2.2485 | 20.5425
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.7752 | 19.5396 | 22.3148 | 2.8105 | 25.1254
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.7003 | 26.0528 | 29.7531 | 3.7474 | 33.5005
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 5.458 | 38.87 | 44.328 | 5.5274 | 49.8554
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.8413 | 41.1958 | 47.0371 | 5.9156 | 52.9526
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 6.6143 | 45.9062 | 52.5205 | 6.6984 | 59.2189
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 7.1652 | 50.07 | 57.2352 | 7.2563 | 64.4915
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 7.7221 | 54.2916 | 62.0137 | 7.8203 | 69.834
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 8.2795 | 58.5142 | 66.7937 | 8.3848 | 75.1785
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 10.0371 | 71.3314 | 81.3686 | 10.1648 | 91.5334
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 14.5473 | 110.2679 | 124.8152 | 14.7323 | 139.5475
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 16.8024 | 129.7361 | 146.5385 | 17.0161 | 163.5546
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 19.0575 | 149.2043 | 168.2618 | 19.2999 | 187.5617
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 24.9779 | 189.1203 | 214.0982 | 25.2956 | 239.3938
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 28.0308 | 213.7087 | 241.7396 | 28.3874 | 270.1269
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 37.4668 | 283.6804 | 321.1472 | 37.9434 | 359.0906
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 44.6827 | 339.7889 | 384.4717 | 45.2511 | 429.7228
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 53.6563 | 408.7147 | 462.371 | 54.3388 | 516.7098
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 63.2775 | 483.526 | 546.8035 | 64.0824 | 610.886
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 77.7094 | 595.743 | 673.4524 | 78.6978 | 752.1502
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 89.2735 | 688.2112 | 777.4847 | 90.4091 | 867.8938
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2028 PDF
PROPOSED - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2028
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 8.6355 | 0.1075 |  | 9.5987
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.48801 | 3.6678 | 4.1558 | 0.54245 | 4.6983
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.3877 | 9.7698 | 11.1575 | 1.5425 | 12.6999
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.8502 | 13.0264 | 14.8766 | 2.0566 | 16.9333
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.359 | 16.3876 | 18.7466 | 2.6222 | 21.3688
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 3.1454 | 22.587 | 25.7324 | 3.4963 | 29.2287
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.7929 | 26.262 | 30.0549 | 4.2161 | 34.271
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 4.2527 | 29.3797 | 33.6324 | 4.7271 | 38.3595
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 5.0187 | 34.5604 | 39.5791 | 5.5785 | 45.1576
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 6.2445 | 42.8588 | 49.1033 | 6.941 | 56.0443
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 6.386 | 43.842 | 50.2281 | 7.0984 | 57.3264
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 6.6811 | 45.88 | 52.5611 | 7.4264 | 59.9875
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 7.1798 | 49.3066 | 56.4863 | 7.9807 | 64.467
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 7.6784 | 52.7332 | 60.4116 | 8.5349 | 68.9465
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 8.7899 | 60.5522 | 69.3421 | 9.7704 | 79.1125
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 9.5286 | 65.7596 | 75.2882 | 10.5915 | 85.8797
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.72253 | 5.3035 | 6.026 | 0.80313 | 6.8291
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 1.1102 | 8.0369 | 9.1471 | 1.234 | 10.381
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 2.2203 | 16.0738 | 18.2941 | 2.468 | 20.7621
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.7753 | 19.5396 | 22.315 | 3.0849 | 25.3999
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.7005 | 26.0528 | 29.7533 | 4.1132 | 33.8665
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 5.4582 | 38.87 | 44.3282 | 6.0671 | 50.3953
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.8415 | 41.1958 | 47.0373 | 6.4931 | 53.5304
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 6.6145 | 45.9062 | 52.5207 | 7.3524 | 59.8731
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 7.1655 | 50.07 | 57.2354 | 7.9648 | 65.2002
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 7.7224 | 54.2916 | 62.014 | 8.5838 | 70.5978
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 8.2798 | 58.5142 | 66.794 | 9.2034 | 75.9974
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 10.0375 | 71.3314 | 81.369 | 11.1572 | 92.5262
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 14.5479 | 110.2679 | 124.8158 | 16.1707 | 140.9865
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 16.8031 | 129.7361 | 146.5392 | 18.6775 | 165.2166
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 19.0583 | 149.2043 | 168.2626 | 21.1842 | 189.4468
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 24.9789 | 189.1203 | 214.0992 | 27.7653 | 241.8645
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 28.032 | 213.7087 | 241.7407 | 31.1589 | 272.8996
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 37.4684 | 283.6804 | 321.1488 | 41.6479 | 362.7967
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 44.6846 | 339.7889 | 384.4735 | 49.6691 | 434.1426
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 53.6585 | 408.7147 | 462.3732 | 59.6441 | 522.0173
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 63.2801 | 483.526 | 546.8062 | 70.339 | 617.1452
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 77.7126 | 595.743 | 673.4556 | 86.3814 | 759.837
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 89.2772 | 688.2112 | 777.4884 | 99.236 | 876.7244
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2030 PDF
PROPOSED - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2030
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 8.6364 | 0.1075 |  | 11.0118
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.48807 | 3.6678 | 4.1559 | 0.62231 | 4.7782
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.3878 | 9.7698 | 11.1576 | 1.7695 | 12.9272
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.8504 | 13.0264 | 14.8768 | 2.3594 | 17.2362
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.3593 | 16.3876 | 18.7469 | 3.0082 | 21.7551
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 3.1458 | 22.587 | 25.7328 | 4.011 | 29.7438
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.7934 | 26.262 | 30.0554 | 4.8367 | 34.8921
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 4.2532 | 29.3797 | 33.6329 | 5.423 | 39.0559
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 5.0193 | 34.5604 | 39.5797 | 6.3998 | 45.9795
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 6.2452 | 42.8588 | 49.1039 | 7.9629 | 57.0668
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 6.3867 | 43.842 | 50.2288 | 8.1434 | 58.3721
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 6.6819 | 45.88 | 52.5618 | 8.5197 | 61.0815
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 7.1805 | 49.3066 | 56.4871 | 9.1555 | 65.6427
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 7.6792 | 52.7332 | 60.4124 | 9.7914 | 70.2038
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 8.7909 | 60.5522 | 69.343 | 11.2088 | 80.5518
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 9.5297 | 65.7596 | 75.2893 | 12.1508 | 87.44
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.72261 | 5.3035 | 6.0261 | 0.92136 | 6.9474
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 1.1103 | 8.0369 | 9.1472 | 1.4157 | 10.5628
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 2.2205 | 16.0738 | 18.2944 | 2.8313 | 21.1257
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.7757 | 19.5396 | 22.3153 | 3.5391 | 25.8544
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.7009 | 26.0528 | 29.7537 | 4.7188 | 34.4725
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 5.4588 | 38.87 | 44.3288 | 6.9602 | 51.2891
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.8421 | 41.1958 | 47.0379 | 7.449 | 54.4869
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 6.6153 | 45.9062 | 52.5215 | 8.4348 | 60.9563
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 7.1662 | 50.07 | 57.2362 | 9.1373 | 66.3736
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 7.7232 | 54.2916 | 62.0148 | 9.8475 | 71.8623
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 8.2807 | 58.5142 | 66.7949 | 10.5583 | 77.3532
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 10.0386 | 71.3314 | 81.3701 | 12.7998 | 94.1698
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 14.5495 | 110.2679 | 124.8174 | 18.5513 | 143.3687
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 16.8049 | 129.7361 | 146.541 | 21.4271 | 167.9681
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 19.0604 | 149.2043 | 168.2647 | 24.3029 | 192.5676
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 24.9816 | 189.1203 | 214.1019 | 31.8528 | 245.9548
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 28.035 | 213.7087 | 241.7438 | 35.7461 | 277.4899
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 37.4725 | 283.6804 | 321.1529 | 47.7792 | 368.9321
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 44.6895 | 339.7889 | 384.4784 | 56.9813 | 441.4597
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 53.6644 | 408.7147 | 462.3791 | 68.4248 | 530.8039
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 63.2871 | 483.526 | 546.8131 | 80.6942 | 627.5073
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 77.7211 | 595.743 | 673.4641 | 99.0982 | 772.5624
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 89.287 | 688.2112 | 777.4982 | 113.8453 | 891.3435
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2029 PDF
PROPOSED - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2029
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 8.6359 | 0.1075 |  | 10.2702
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.48804 | 3.6678 | 4.1559 | 0.5804 | 4.7363
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.3877 | 9.7698 | 11.1575 | 1.6504 | 12.8079
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.8503 | 13.0264 | 14.8767 | 2.2005 | 17.0772
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.3592 | 16.3876 | 18.7468 | 2.8056 | 21.5524
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 3.1456 | 22.587 | 25.7326 | 3.7409 | 29.4735
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.7931 | 26.262 | 30.0551 | 4.511 | 34.5661
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 4.2529 | 29.3797 | 33.6326 | 5.0578 | 38.6904
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 5.019 | 34.5604 | 39.5794 | 5.9688 | 45.5482
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 6.2448 | 42.8588 | 49.1036 | 7.4266 | 56.5302
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 6.3863 | 43.842 | 50.2284 | 7.5949 | 57.8233
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 6.6815 | 45.88 | 52.5614 | 7.9459 | 60.5074
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 7.1801 | 49.3066 | 56.4867 | 8.539 | 65.0257
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 7.6788 | 52.7332 | 60.412 | 9.132 | 69.544
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 8.7904 | 60.5522 | 69.3425 | 10.4539 | 79.7965
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 9.5286 | 65.7596 | 75.2887 | 11.3325 | 86.6212
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.72253 | 5.3035 | 6.026 | 0.85931 | 6.8853
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 1.1102 | 8.0369 | 9.1471 | 1.3203 | 10.4674
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 2.2203 | 16.0738 | 18.2942 | 2.6406 | 20.9349
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.7753 | 19.5396 | 22.3151 | 3.3008 | 25.6158
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.7005 | 26.0528 | 29.7535 | 4.401 | 34.1545
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 5.4582 | 38.87 | 44.3285 | 6.4915 | 50.82
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.8415 | 41.1958 | 47.0376 | 6.9474 | 53.985
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 6.6145 | 45.9062 | 52.5211 | 7.8667 | 60.3878
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 7.1655 | 50.07 | 57.2358 | 8.522 | 65.7578
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 7.7224 | 54.2916 | 62.0144 | 9.1843 | 71.1987
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 8.2798 | 58.5142 | 66.7945 | 9.8473 | 76.6417
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 10.0375 | 71.3314 | 81.3695 | 11.9378 | 93.3073
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 14.5479 | 110.2679 | 124.8165 | 17.302 | 142.1185
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 16.8031 | 129.7361 | 146.5401 | 19.9841 | 166.5241
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 19.0583 | 149.2043 | 168.2636 | 22.6662 | 190.9298
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 24.9789 | 189.1203 | 214.1005 | 29.7077 | 243.8082
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 28.032 | 213.7087 | 241.7422 | 33.3387 | 275.0809
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 37.4684 | 283.6804 | 321.1508 | 44.5615 | 365.7123
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 44.6846 | 339.7889 | 384.4759 | 53.1438 | 437.6197
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 53.6585 | 408.7147 | 462.376 | 63.8167 | 526.1927
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 63.2801 | 483.526 | 546.8095 | 75.2598 | 622.0692
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 77.7126 | 595.743 | 673.4597 | 92.4244 | 765.8841
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 89.2772 | 688.2112 | 777.4931 | 106.1783 | 883.6714
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard