## Cover
OEB Vulnerability Assessment & System Hardening
VASH Toolkit Model
2025-04-11
Private and confidential
DISCLAIMER
Guidehouse Inc. (Guidehouse) has provided the information in this publication for informational purposes only. The information has been obtained from sources believed to be reliable; however, Guidehouse does not make any express or implied warranty or representation concerning such information. Any market forecasts or predictions contained in the publication reflect Guidehouse’s current expectations based on market data and trend analysis. Market predictions and expectations are inherently uncertain and actual results may differ materially from those contained in the publication. Guidehouse and its subsidiaries and affiliates hereby disclaim liability for any loss or damage caused by errors or omissions in this publication.
CONTACTS
Donald Lau | Zubin Panchal
Manager, Electricity Distribution | Senior Advisor, Electricity Distribution
Donald.Lau@oeb.ca | Zubin.Panchal@oeb.ca

## Table of Contents
DRAFT
Ontario Energy Board Vulnerability Assessment & System Hardening (VASH) Toolkit - Table of Contents
Disclaimer
Contents
This file contains the following pages:
|  | Color | Tab Name | Description/Purpose
|  |  | Table of Contents | Contains a model overview and tab descriptions.
|  | Tab Link | VA Toolkit User Guide | The User Guide outlines the step-by-step methodology to employ the Vulnerability Assessment Toolkit model to analyze asset class and location vulnerability to climate perils. The example of reviewing the vulnerability of Class 3 poles in County 1 to high wind probabilities is provided as an illustrative example.
|  | Tab Link | 1. LDC Asset Summary | Summarizes asset counts by analysis location. Locations with no assets of a specific class will have no vulnerability for that class regardless of climate projections. For locations and class combinations with higher vulnerability, an LDC may review its asset counts to understand the pervasiveness of the resiliency challenge.
|  | Tab Link | 2. Asset Class Failure Thresh | Characterizes the expected resilience of LDC assets identified in the Asset Summary to specific climate perils. Sub classes may be included to better estimate failure thresholds across a variety of perils. The total annual probability of failure is the summation across climate perils. LDCs may leverage design standards to quickly review vulnerability or refine failure thresholds with additional condition data of field equipment.
|  | Tab Link | 3. Climate Severity Calculator | Supports the development of tab '4. Climate Peril Probability'. Users may input chosen climate projections (from ECCC) to estimate annual probabilities of failure at different times in the future.
|  | Tab Link | 4. Climate Peril Probability | Projects the annual probability of specific events (relevant to assets in the Asset Summary) occurring at targeted grid locations through time. Climate perils and severity thresholds are linked to specific asset failure modes and thresholds. For example, wind gusts may be evaluated at 80, 100, and 120 kph as these relate to different class pole failures.
|  | Tab Link | 5. VA Heatmap | Categorizes vulnerability for each asset class in 5-year time intervals at a specified location by user-defined vulnerability bins. The annual probability of failures are summed across applicable climate perils based on asset class failure thresholds.
|  | Tab Link | 6. Generic BCA Inputs | User inputs that describe the unit costs related to asset failure (i.e., repair and replace costs). These costs should be those that scale with asset count. Project level costs such as administration should be entered in tab '7. Project Characteristics'.
|  | Tab Link | 7. Project Characteristics | User inputs that describe the characteristics of a single project associated with a single location. Users should use this tab to assess the benefits and costs of individual projects. See tab 'BCA Toolkit User Guide' for example project types.
|  | Tab Link | 8. Project BCA Results | Presents results of project BCA calculations based on inputs provided in tabs 1-7.
The following tabs contain intermediate calculations for the workbook to function and should not be edited.
|  | Color | Tab Name | Description/Purpose
|  |  | Calibration | Calculates calibration factor to ground modeled failures against actual observed failures. Calibration accounts for covariance of probability of failure associated with assets (e.g. similar assets in relatively close proximity)
Raw Climate Data
Int VA Calcs
Int BCA Costs
Int BCA Ann Fail Prob
Int BCA Ann Fail Costs
Int BCA Ann PWFC
Int BCA Ann PWVOLL
Indices
Key
User Input
Input from List (Dropdown)
Fixed Input
Calculated Value
Calculated Value
Linked Value
Model Result
The Vulnerability Assessment (VA) and Benefit-Cost Analysis (BCA) Toolkits, together comprising the VASH Toolkit, are designed to support LDCs as an option for streamlining the identification of vulnerable asset classes and locations, as well as evaluating the cost-effectiveness of mitigation activities intended to reduce resiliency risk to existing assets and customers. The toolkit illustrates a generic assessment methodology option compliant with OEB expectations for evaluation of resiliency risk, resulting in a heatmap that supports narrowing assets for further review and a summary of project benefit-cost results.
The VA Toolkit (tabs 1-5) combines climate data, design standards, and asset location summaries. Inputs may be developed by LDCs using a variety of sources including the LDCs internal data, CSA guidelines, publicly available climate data, and proprietary climate data. The OEB does not specify a data source expectation. LDCs may leverage data commensurate with their planning granularity and needs.
The BCA Toolkit (tabs 6-8) allows users to characterize projects aimed at reducing the frequency and/or criticality of asset failures caused by the climate perils analyzed in the VA Toolkit. Inputs are based on the utility's existing asset base, proposed replacement assets, projected costs, and criticality values derived from the DOE ICE calculator.
While this toolkit is a fully functioning model that may be used by LDCs, the onus remains on the LDCs to ensure accuracy of the data and results. The prepopulated values are illustrative only and should not be used for vulnerability assessments. LDCs must provide their own climate peril probabilities, asset class failure thresholds, asset summaries, project characteristics, outage criticality values to operate the model.
This deliverable was prepared by Guidehouse Inc. for the use and benefit of, and pursuant to a client relationship exclusively with the OEB ("Client"). The work presented in this deliverable represents Guidehouse’s professional judgement based on the information available at the time this report was prepared. Any third party relying on the information in this deliverable does so entirely at their own risk and shall have no right of recourse against the Vendor. Accordingly, Guidehouse disclaims any contractual or other responsibility to others based on their access to or use of the deliverable.
Users should populate cells marked as 'User Input' based on the scheme shown below. All other cells are calculated by the model or given as fixed values.

## VA Toolkit User Guide
DRAFT - Example Data Illustrative
Ontario Energy Board Vulnerability Assessment Toolkit - User Guide
3. Climate Peril Probability
2. Asset Class Failure
Thresholds
5. Vulnerability Assessment Heatmap
The User Guide outlines the step-by-step methodology to employ the Vulnerability Assessment Toolkit model to analyze asset class and location vulnerability to climate perils. The example of reviewing the vulnerability of Class 3 poles in County 1 to high wind probabilities is provided as an illustrative example.
1. LDC Asset Summary
Step 1: Users should populate the Asset Summary with their installed asset base by location. Asset sub classes may be utilized to add granularity to failure thresholds. Additionally the counts of each asset class or sub class should be included as available. If actual counts are not available, populating with a "1" will ensure correct model calculations. Locations and classes for inclusion are based on user discretion. Generally, locations should be chosen based on likelihood of varying climate conditions and asset classes and sub classes based on variations in the expected weather event resilience of those technologies.
Example: The LDC populates the summary of their poles in Location 1 by Class. Based on the counts, the LDC is interested in the vulnerability of their most populous sub class, Class 3 poles, as it may represent greater risk.
Step 2: Users set up the Asset Class Failure Modes & Thresholds table to include the asset classes and sub classes identified in the Asset Summary process. Leveraging CSA guidelines, OEM design standards, or other engineering resources, asset classes and sub classes are assigned to climate perils, and severity thresholds that pose a threat to the equipment are determined. The unit basis of the climate peril identified should be included and referenced in the development of climate peril probabilities.
Example: The LDC populates the provided table with the asset class and sub classes from Step 1. Wind (1 min gusts measured in kph) is determined to be the primary climate peril applicable to utility poles. Severity thresholds for wind are researched based on manufacturer specifications and populate the remainder of the table. The 150 Class 3 poles in Location 1 are designed to withstand 80 kph gusts.
Step 3: Users set up the Climate Peril Probability Model with the climate perils and severity thresholds identified in Step 2 as relevant to the asset summary at locations identified in Step 1. Leveraging Environment Canada data, CSA working documents, proprietary climate data, or other sources, the annual probability of occurrence is developed for a specific climate peril, severity threshold, location, and time period. Data for climate projections is highly variable, therefore, forecast time periods are discretionary and may be adjusted to match best available data. '3. Climate Severity Calculator' is provided to facilitate populating '4. Climate Peril Probability'
Example: The LDC populates the provided table with the climate perils and thresholds from Step 2 for each location from Step 1. The annual frequency of wind gusts in Location 1 at different thresholds is researched and populated in 5-year increments based on available data. As we know from Step 2, the 150 Class 3 poles in Location 1 are designed to withstand 80 kph gusts; which has a 0.8% annual probability of occurrence in 2025 but increases to a 1.6% annual probability of occurrence by 2050.
Step 4: The Vulnerability Assessment Heatmap will automatically populate after Step 3 is complete. Users may toggle the Location field to view each specified location in Step 1 individually to reveal differences in vulnerability based on the Asset Summary and Climate Peril Probability model. Additionally, users may designate cutoff points for vulnerability categories ranging from Low to High (annual probabilities above the "High" field with be labeled "Very High"). The Annual Probability Bins represent the low end of a probability range considered to be in the category. The resulting heatmap may be used to identify areas of system vulnerability for further research and/or prioritize asset classes and locations for investment review.
Example: The LDC sets the Location field to Location 1 and the Annual Probability Bins at 1%, 5%, and 10% (representing the risk of a 1/100-, 1/20-, and 1/10-year event respectively). The resulting analysis of Class 3 poles in Location 1 shows Low vulnerability (less than 1% per year in this example) until 2035 when the vulnerability becomes Medium (between 1% and 5% per year in this example). The LDC may choose to focus research effort and investment on hardening other locations or asset classes with greater risk and revisit Class 3 poles in Location 1 when developing a future DSP.

## VA Definitions
Ontario Energy Board Vulnerability Assessment Toolkit - Definitions
Term | Definition
Location | A point or an area associated with 1 or more assets. Locations are used to map asset classes to the specific probability of climate perils occurring. Definitions of locations are up to the discretion of the user, and can be chosen to be as granular or as coarse as needed to capture geographic variation in likelihood of climate conditions.
Asset Class | A type of asset, such as a pole or overhead conductor. Asset classes should be chosen to accurately differentiate between the weather event resilience of different assets.
Sub Class | A sub category of asset within an asset class. Sub classes may be used to further differentiate failure thresholds of different assets within a class; for example, to differentiate the resilience of different classes of pole to wind gusts.
Vulnerability | Vulnerability represents the probability that an asset (or group of assets) will fail given it is within the location of occurrence of one or more climate perils.
Risk | Risk quantifies the financial exposure of an asset or group of assets at a location, accounting for probability of failure in response to climate perils as well as criticality of failure (e.g., value of lost load).
Severity Threshold | Estimated point over which a given asset class would be expected to fail in response to a particular climate peril .

## 1. LDC Asset Summary
DRAFT - Example Data Illustrative
| Table 1: Asset Class Summary |  |  | Table 2: Asset Class and Sub-Class Locations and Counts
| Asset Class | Unit Basis |  | Location | Asset Class | Sub Class | Count | Unit Basis
| Pole | pole | Location 1PoleClass 5 | Location 1 | Pole | Class 5 | 50 | pole
|  |  | Location 1PoleClass 4 | Location 1 | Pole | Class 4 | 100 | pole
|  |  | Location 1PoleClass 3 | Location 1 | Pole | Class 3 | 150 | pole
|  |  | Location 1PoleClass 2 | Location 1 | Pole | Class 2 | 30 | pole
Users should populate Table 1 with the unique list of asset classes and their unit basis to be included in the assessment. Table 2 should be populated with the installed asset base by location. Asset sub classes may be utilized to add granularity to failure thresholds. Additionally the counts of each asset class or sub class should be included as available. If actual counts are not available, populating with a "1" will ensure correct model calculations. Locations and classes for inclusion are based on user discretion. Generally, locations should be chosen based on likelihood of varying climate conditions and asset classes and sub classes based on variations in the expected weather event resilience of those technologies. A single unit basis should be defined for each Asset Class (Columns K and L). This list should also contain potential replacement assets associated with projects to be defined in Tabs 6 and 7; for example, to describe a program that involves undergrounding of overhead conductors, an asset class of "Underground Conductor" should be included (e.g., with a count of 0, if none exist yet).

## 2. Asset Class Failure Thresh
DRAFT - Example Data Illustrative
Asset Class Failure Modes & Thresholds
| Table 3: Climate Peril Summary |  | Table 4: Asset Class Failure Thresholds
| Climate Peril | Unit Basis | Asset Class | Sub Class | Climate Peril | Severity Threshold | Unit Basis
| Wind | kph (10-min avg.) | Pole | Class 5 | Wind | 80 | kph (10-min avg.)
| Ice | mm ice accretion | Pole | Class 4 | Wind | 85 | kph (10-min avg.)
|  |  | Pole | Class 3 | Wind | 100 | kph (10-min avg.)
|  |  | Pole | Class 2 | Wind | 110 | kph (10-min avg.)
Users populate Table 3 with the unique list of climate perils being assessed and the unit basis by which the severity of this peril will be considered. Table 4 should include the asset classes and sub classes identified in the Asset Summary tab and - leveraging CSA guidelines, OEM design standards, or other engineering resources - be assigned to climate perils, and severity thresholds that pose a threat to the equipment. The unit basis of the climate peril identified should be included and referenced in the development of climate peril probabilities. A single unit basis should be defined for each climate peril.

## 3. Climate Severity Calculator
DRAFT - Example Data Illustrative
Asset Sub-Class Probability of Failure Calculator Tool
Scenario Selection
|  | Location | Location 1
|  | Climate Scenario | RCP6.0
|  | Climate Peril | Ice Accretion
|  | Unit Basis | mm ice accretion
|  | Severity Threshold | 10
Annual Event Probability Projection
|  | Climate Peril | Severity Threshold | Unit Basis | Location | 2023 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2055 | 2060 | 2065 | 2070 | 2075 | 2080 | 2085 | 2090 | 2095 | 2100
|  | Ice Accretion | 10 | mm ice accretion | Location 1 | 0.2827 | 0.28306 | 0.28342 | 0.28379 | 0.28415 | 0.28451 | 0.28342 | 0.28197 | 0.28052 | 0.27905 | 0.27759 | 0.27658 | 0.27557 | 0.27455 | 0.26908 | 0.26459 | 0.26005
Projected Ice Accretion
|  | Location ID | Year | 10 | 20 | 50 | 100 | 200 | Estimated Failure Threshold | Lower Wind Speed | Upper Wind Speed | Lower Return Period | Upper Return Period | Annual Probability of Failure
| Location 1Ice Accretion2023RCP6.0 | Location 1 | 2023 | 18.2256 | 21.7202 | 26.2483 | 29.7204 | 33.1729 | 10 | 0 | 18.2256 | 1 | 10 | 0.2827
| Location 1Ice Accretion2025RCP6.0 | Location 1 | 2025 | 18.2442 | 21.7568 | 26.3145 | 29.8051 | 33.2785 | 10 | 0 | 18.2442 | 1 | 10 | 0.28306
| Location 1Ice Accretion2030RCP6.0 | Location 1 | 2030 | 18.2627 | 21.7934 | 26.3806 | 29.8898 | 33.3841 | 10 | 0 | 18.2627 | 1 | 10 | 0.28342
| Location 1Ice Accretion2035RCP6.0 | Location 1 | 2035 | 18.2812 | 21.83 | 26.4468 | 29.9745 | 33.4896 | 10 | 0 | 18.2812 | 1 | 10 | 0.28379
| Location 1Ice Accretion2040RCP6.0 | Location 1 | 2040 | 18.2997 | 21.8666 | 26.5129 | 30.0593 | 33.5952 | 10 | 0 | 18.2997 | 1 | 10 | 0.28415
| Location 1Ice Accretion2045RCP6.0 | Location 1 | 2045 | 18.3183 | 21.9032 | 26.5791 | 30.144 | 33.7008 | 10 | 0 | 18.3183 | 1 | 10 | 0.28451
| Location 1Ice Accretion2050RCP6.0 | Location 1 | 2050 | 18.2627 | 21.8871 | 26.6135 | 30.2108 | 33.8064 | 10 | 0 | 18.2627 | 1 | 10 | 0.28342
| Location 1Ice Accretion2055RCP6.0 | Location 1 | 2055 | 18.1886 | 21.8344 | 26.5817 | 30.1928 | 33.8064 | 10 | 0 | 18.1886 | 1 | 10 | 0.28197
| Location 1Ice Accretion2060RCP6.0 | Location 1 | 2060 | 18.1145 | 21.7817 | 26.55 | 30.1749 | 33.8064 | 10 | 0 | 18.1145 | 1 | 10 | 0.28052
| Location 1Ice Accretion2065RCP6.0 | Location 1 | 2065 | 18.0404 | 21.729 | 26.5182 | 30.1569 | 33.8064 | 10 | 0 | 18.0404 | 1 | 10 | 0.27905
| Location 1Ice Accretion2070RCP6.0 | Location 1 | 2070 | 17.9663 | 21.6763 | 26.4865 | 30.139 | 33.8064 | 10 | 0 | 17.9663 | 1 | 10 | 0.27759
| Location 1Ice Accretion2075RCP6.0 | Location 1 | 2075 | 17.9154 | 21.6543 | 26.5063 | 30.1838 | 33.8814 | 10 | 0 | 17.9154 | 1 | 10 | 0.27658
| Location 1Ice Accretion2080RCP6.0 | Location 1 | 2080 | 17.8645 | 21.6324 | 26.5261 | 30.2287 | 33.9564 | 10 | 0 | 17.8645 | 1 | 10 | 0.27557
| Location 1Ice Accretion2085RCP6.0 | Location 1 | 2085 | 17.8135 | 21.6104 | 26.546 | 30.2735 | 34.0314 | 10 | 0 | 17.8135 | 1 | 10 | 0.27455
| Location 1Ice Accretion2090RCP6.0 | Location 1 | 2090 | 17.5403 | 21.3688 | 26.3365 | 30.0892 | 33.8619 | 10 | 0 | 17.5403 | 1 | 10 | 0.26908
| Location 1Ice Accretion2095RCP6.0 | Location 1 | 2095 | 17.3181 | 21.1492 | 26.1072 | 29.8599 | 33.6174 | 10 | 0 | 17.3181 | 1 | 10 | 0.26459
| Location 1Ice Accretion2100RCP6.0 | Location 1 | 2100 | 17.0958 | 20.9296 | 25.8779 | 29.6307 | 33.3729 | 10 | 0 | 17.0958 | 1 | 10 | 0.26005
Source: TBD
|  |  |  | 0.005 | 0.01 | 0.02 | 0.05 | 0.1
|  |  | Ice Accretion | 33.2785 | 29.8051 | 26.3145 | 21.7568 | 18.2442
|  |  | Estimated Failure Threshold | 10 | 10 | 10 | 10 | 10
Users may leverage climate projections obtained from ECCC to estimate the annual probability of failures that their assets are exposed to. Using the Scenario Selection cells below: each climate peril, severity threshold, and location to be populated in '4. Climate Peril Probability' should be evaluated for its exceedance probability in 5-year increments. The results from the Annual Event Probability Projection cells (B18:U18) may be copied as values directly into columns G:V in '4. Climate Peril Probability' to support input development.

## 4. Climate Peril Probability
DRAFT - Example Data Illustrative
Climate Peril Probability Model
Table 5: Climate Peril Probability Projections
Annual Event Probability Forecast
|  | Climate Peril | Severity Threshold | Unit Basis | Location | 2023 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2055 | 2060 | 2065 | 2070 | 2075 | 2080 | 2085 | 2090 | 2095 | 2100
| Location 1Wind110 | Wind | 110 | kph (10-min avg.) | Location 1 | 0.0071709 | 0.0073129 | 0.0074565 | 0.0076015 | 0.007748 | 0.007896 | 0.0080934 | 0.0081414 | 0.0081897 | 0.0082382 | 0.0082869 | 0.0085599 | 0.0088372 | 0.0091188 | 0.0098446 | 0.010298 | 0.010765
| Location 1Wind100 | Wind | 100 | kph (10-min avg.) | Location 1 | 0.018976 | 0.019268 | 0.019562 | 0.019858 | 0.020204 | 0.020598 | 0.021132 | 0.021269 | 0.021406 | 0.021544 | 0.021683 | 0.022406 | 0.023141 | 0.023886 | 0.02589 | 0.027176 | 0.028502
| Location 1Wind85 | Wind | 85 | kph (10-min avg.) | Location 1 | 0.093916 | 0.094911 | 0.095908 | 0.096906 | 0.097906 | 0.098907 | 0.10007 | 0.10016 | 0.10025 | 0.10034 | 0.10043 | 0.10085 | 0.10127 | 0.10169 | 0.10293 | 0.10374 | 0.10456
| Location 1Wind80 | Wind | 80 | kph (10-min avg.) | Location 1 | 0.11796 | 0.11822 | 0.11849 | 0.11875 | 0.11902 | 0.11929 | 0.11965 | 0.11975 | 0.11985 | 0.11995 | 0.12005 | 0.12051 | 0.12098 | 0.12144 | 0.1228 | 0.1237 | 0.1246
Users should populate Table 5 with the climate perils and severity thresholds identified in Tab 2 as relevant to the asset summary at locations identified in Tab 1. Leveraging Environment Canada data, CSA working documents, proprietary climate data, or other sources, the annual probability of occurrence is developed for a specific climate peril, severity threshold, location, and time period. Tab '3. Climate Severity Calculator' is available to support generic option input development using ECCC data. This table should include every unique combination of Climate Peril and severity threshold as defined in Tab 2, for each Location of interest.

## 5. VA Heatmap
DRAFT - Example Data Illustrative
Vulnerability Heatmap
[20 empty] | Legend |  | List of Locations
[20 empty] | Bin Option | Definition | Location 1
[20 empty] | 0.01 | 1-in-100 year event
[20 empty] | 0.02 | 1-in-50 year event
[20 empty] | 0.05 | 1-in-20 year event
[20 empty] | 0.1 | 1-in-10 year event
[20 empty] | 0.2 | 1-in-5 year event
|  | Location |  | Location 1
|  |  |  | Low | Medium | High | Very High
|  | Annual Probability Bin |  | 0.01 | 0.05 | 0.1 | >0.1
Asset Vulnerability Heatmap
|  | Asset Class | Sub Class | 2025 | 2030 | 2035 | 2040 | 2045 | 2040 | 2055 | 2060 | 2065 | 2070 | 2075 | 2080 | 2085 | 2090 | 2095 | 2100
| Location 1PoleClass 5 | Pole | Class 5 | Very High | Very High | Very High | Very High | Very High | Very High | Very High | Very High | Very High | Very High | Very High | Very High | Very High | Very High | Very High | Very High
| Location 1PoleClass 4 | Pole | Class 4 | High | High | High | High | High | Very High | Very High | Very High | Very High | Very High | Very High | Very High | Very High | Very High | Very High | Very High
| Location 1PoleClass 3 | Pole | Class 3 | Medium | Medium | Medium | Medium | Medium | Medium | Medium | Medium | Medium | Medium | Medium | Medium | Medium | Medium | Medium | Medium
| Location 1PoleClass 2 | Pole | Class 2 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low | Medium | Medium
The Vulnerability Assessment Heatmap will automatically populate after Tabs 1, 2 and 4 are complete. Users may toggle the Location field to view each user-specified location in Tab 1 individually to reveal differences in vulnerability based on the Asset Summary and Climate Peril Probability model. Additionally, users may designate cutoff points for vulnerability categories ranging from Low to High (annual probabilities above the "High" field with be labeled "Very High"). The Annual Probability Bins represent the low end of a probability range considered to be in the category. The resulting heatmap may be used to identify areas of system vulnerability for further research and/or prioritize asset classes and locations for investment review.

## 6. Generic BCA Inputs
DRAFT - Example Data Illustrative
Generic BCA Inputs
Table 5: Asset Repair and Replace Costs
|  | Asset Class | Asset Sub-Class | Unit Basis | Unit | Cost Data Year | Repair Cost | Replace Cost | Replace %
| PoleClass 5 | Pole | Class 5 | pole | $/unit | 2025 | 500 | 4000 | 50%
| PoleClass 4 | Pole | Class 4 | pole | $/unit | 2025 | 500 | 4400 | 50%
| PoleClass 3 | Pole | Class 3 | pole | $/unit | 2025 | 500 | 4840 | 50%
| PoleClass 2 | Pole | Class 2 | pole | $/unit | 2025 | 500 | 5324 | 50%
TBD BCA inputs used across projects
In Table 5 users should input the expected costs to repair and replace equipment for the asset classes and sub-classes populated from the VA. Repair and replace costs should represent all capital cost incurred by the utility when addressing asset failures (i.e., equipment cost, labor, etc.) but should only include costs that scale on a per asset basis. Other costs, such as project administration and O&M, should be included in '7. Project Characteristics'. The repair and replace values may be used across evaluated projects and will derive project budgets and BCA costs.
Additionally, the expected replacement percent should be estimated based on the climate perils and failure thresholds incorporated into the VA. For example, if a specific replacement failure threshold (e.g., from CSA guidelines) was used to analyze vulnerability, this should be set to 100%. If a threshold based on historic asset class outages was used, an estimate of actual repair versus replace expectations may be appropriate. Note that all failures will cause a customer interruption in the model with the replace and repaire percentages aligning the capital costs of those failures to LDC experience.

## 7. Project Characteristics
DRAFT - Example Data Illustrative
Project Characteristics
Table 6: Project Characteristics
Project Type Inputs
|  |  |  | Location |  | Location 1
|  |  |  | Project Type |  | End-of-Life
|  |  |  | Impact Type |  | Both
Table 7: Project Economic Variables
|  |  |  | Variable | Unit | Value
|  |  |  | Inflation | % | 2%
|  |  |  | Nominal Utility Discount Rate (WACC) | % | 7%
|  |  |  | Social Discount Rate | % | 4%
|  |  |  | Baseline O&M Cost (% of Total Costs) | % | 1.5%
|  |  |  | Scenario O&M Cost (% of Total Costs) | % | 1.5%
|  |  |  | Tax Rate | % | 26.5%
|  |  |  | Incremental Project Non-Asset Costs | $ | 280000
Table 8: Project Lifetime Variables
|  |  |  | Variable | Unit | Value
|  |  |  | Project Start Year | year | 2026
|  |  |  | Project Expected Lifetime1 | years | 40
|  |  |  | Starting Asset's Remaining Useful Lifetime2 | years | 10
1EUL should not exceed 75
2RUL only required for the early retirement program type.
Table 9: Criticality Variables
|  |  |  | Variable | Unit | Baseline Value | Project Value
|  |  |  | Average Outage Duration | minutes | 120 | 120
|  |  |  | Estimated Customers Interrupted (Res) | count | 100 | 70
|  |  |  | Estimated Customers Interrupted (Small C&I) | count | 5 | 5
|  |  |  | Estimated Customers Interrupted (Med/Large C&I) | count | 1 | 0
|  |  |  | Value of Lost Load (VOLL) | $/Outage Event | 17961 | 4468
|  |  |  | Calibration Year | year | 2025 | N/A
|  |  |  | Historic Annual Outage Events2 | Count | 2.2 | N/A
2These outages should reflect those caused by the climate perils addressed in this risk analysis. Inclusion of historic outages from other causes will inflate results.
Table 10: Applicable Assets
|  |  |  | Existing Assets |  |  | Standard Assets |  |  | Replacement Assets |  |  |  | Project Budget | Cost for BCA
| Existing | Standard | Replace | Asset Class | Asset Sub-Class | Unit Basis | Code Asset Class | Code Asset Sub-Class | Baseline Count | Replacement Asset Class | Replacement Asset Sub-Class | Project Count | Unit Basis | Budget ($) | BCA Cost ($)
| PoleClass 5 |  |  | Pole | Class 5 | pole
| PoleClass 4 | PoleClass 3 | PoleClass 2 | Pole | Class 4 | pole | Pole | Class 3 | 100 | Pole | Class 2 | 100 | pole | 532400 | 109380.4683
| PoleClass 3 |  |  | Pole | Class 3 | pole
| PoleClass 2 |  |  | Pole | Class 2 | pole
Users should develop project characteristics that accurately reflect a potential VASH investment opportunity. The toolkit is designed to evaluate one project at a time based on the comprehensive VA.
Table 6: Project Characteristics:
The project location is predetermined based on the location being viewed in '5. VA Heatmap'. This location should reflect the region in which the project being evaluated will be implemented by choosing the closest location with climate data. There are three Project Type options based on the status of the LDC's existing assets. End-of-Life should be selected if the project will replace assets that would have been replaced in the absence of resiliency planning due to age or condition. Early Retirement should be selected if the project will replace assets that would have been expected to remain in service beyond the start date of the project. Retrofit should be selected if the project will not impact existing assets (e.g., sectionalizing or back-up generation).
There are three Impact Type Options based on the mitigation goal of the project. Frequency should be selected if the project increases the robustness of assets to climate perils (i.e., changes the expected failure threshold) but does not impact the duration or number of customers impacted by remaining outages at that location. Criticality should be selected if the project reduces the expected outage durations and/or number of customers impacted by an outage but does not reduce the expected frequency of these events. Both should be selected if the project will reduce the frequency and criticality of outages.
Table 7: Project Economic Variables:
Users should input an estimate for common economic analysis variables. Inflation is the expected annual inflation rate for the duration of the project lifetime. The nominal utility discount rate (WACC) is the rate used for present value calculations of utility costs. The societal discount rate is the rate used for customer impact present value calculations (given by IESO at 4%). Baseline O&M Cost (% of Total Costs) represent the percent of total asset base costs attributable to O&M. Scenario O&M Cost (% of Total Costs) represent the percent of total asset scenario costs attributable to O&M. The tax rate is the combined federal plus provincial tax rate. Additionally, an estimate of incremental non-asset project costs should be included. This represents a one-time cost that does not scale by number of assets in the project. Examples may include engineering costs, other admin, or fees. For Retrofit projects that do not include changes to Starting Assets, this field should be used to estimate the entire project cost.
Table 8: Project Lifetime Variables:
Resiliency investments mitigate risk for the lifetime of installed assets and therefore the lifetime benefits of a project should be analyzed. Users should input the project start year and an estimate for the expected lifetime of the project. Project lifetimes are the expected field life of the assets being invested in. If multiple asset classes are included in the project, a weighted average lifetime may be used. A remaining useful life (RUL) for Existing Assets is required for early retirement projects. This should be the expected number of years that these assets would have continued to be in service in the absence of the resiliency project. This field will be blurred for other Project Types.
Table 9: Criticality Variables:
The BCA Toolkit is designed to leverage per outage event value of lost load (VOLL) estimates for the area impacted by a project. To develop these values using the ICE Calculator, as accepted in the Generic BCA Option, the expected outage duration and number of customers interrupted for three customer classes is required. These values may be input into the ICE Calculator to yield the VOLL in $/outage event. See the BCA Toolkit User Guide for guidance on leveraging the ICE Calculator do develop these inputs. A baseline value is necessary for all Project Types. This scenario's inputs should reflect historical values for outage durations and number of customers impacted for the climate perils that the project will address. For Frequency Impact Type projects, the Project Value should Equal the Baseline Value as there is no change in the criticality of remaining outages after project implementation. For Criticality and Both Project Types, the resulting duration and customer counts should be input into the ICE Calculator as a separate scenario to determine the post-project implementation VOLL.
An estimate of the count of historic annual outages for the project location and climate perils addressed should be developed. Counts should be as granular as possible, however, a 5-year average for an applicable feeder, substation, or section is appropriate. If no historic outages tied to cause codes related to the targeted climate peril for mitigation exist for the project location but the VA suggests that a project may be prudent, the system average annual historic outage frequency from these perils may be applied.
Table 10: Applicable Assets:
Users should identify the Existing Asset classes prepopulated from the VA that are relevant to the project being evaluated. Users should then populate the Replacement Assets fields with the asset class, sub-class, and total count of assets in the proposed project. If the Standard asset sub-class is different from the Existing Assets due to a codes/standards change during the Existing Assets' lifetime, users should fill the Standard Assets with what would have been used in the absence of the resiliency investment. If there has not been a change, fill in the Standard Assets with the same sub-class as the Existing Assets. The baseline count should align with the Existing and Standard Assets' unit basis and the project count should align with the Replacement Assets' unit basis (e.g., an undergrounding program Existing may be per pole and the Replacement may be per km).
The total project budget and BCA cost will calculate automatically. Note that the BCA cost will differ from project budget based on the Project Type selected in the Project Characteristics and the adjustment to the present value of customer revenue requirement. For End-of-life and Early Retirement projects, the model will expect to see a change in asset class for project-applicable assets and an appropriate count. For retrofit projects, Replacement Assets and counts should equal the Existing Assets that are considered in the development of the historic customer outage estimate. Note: Retrofit projects will have $0 budget and BCA cost regardless of the asset counts.

## 8. Project BCA Results
DRAFT - Example Data Illustrative
Project BCA Results
Project Summary Metrics
| Metric | Unit | Expected Value
| Total PV Benefits from Avoided Repairs and Replacements | PV 2026$ | 103846.1424
| Total PV Benefits from Frequency Reductions (VOLL) | PV 2026$ | 73619.2419
| Total PV Benefits from Criticality Reductions (VOLL) | PV 2026$ | 34201.5332
| Total PV Costs | PV 2026$ | 742160.0369
| BCR | ratio | 0.2852
| Expected Annual Average CMI Reduction1 | CMI | 4425.9589
| Expected Lifetime CMI Reduction | CMI | 177038.3561
1Simple average over project lifetime.
Project BCA results are automatically calculated based of the inputs in each of the previous model tabs. Benefits are provided based on three primary categories: avoided repair and replace costs, VOLL from reductions in outage frequency, and VOLL from reductions in outage criticality. It is common for some benefit categories to be $0 based on project characteristics. A benefit-cost ratio (BCR) greater than 1.0 indicates that the present value of lifecycle benefits of the project being evaluated is greater than the upfront incremental costs of that program. The estimated annual and lifetime reductions in customer minutes of interruption (CMI) for the project is also provided.

## Calibration
Project Scenario PV Benefits |  | Repair/Replace Risk |  | Risk VOLL from Outage Frequency |  | Risk VOLL from Outage Criticality |  | Annual event Theta for Calibration
Asset Class | Asset Sub-Class | Baseline | Project | Baseline | Project | Baseline | Project | Asset Class | Asset Sub-Class | Baseline | Scenario |  | Total Modeled Event Probability | Theta | RUL for Model
Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 |  | Baseline | 9.4911 | 0.2318 | 0
Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 9.4911 |  | Primary Scenario |  | N/A
Pole | Class 3 | 177750.0799 | 0 | 119146.0883 | 0 | 0 | 0 | Pole | Class 3 | 0 |  | Low |  | N/A
Pole | Class 2 | 0 | 73903.9374 | 0 | 45526.8464 | 45526.8464 | 11325.3132 | Pole | Class 2 | 0 |  | High |  | N/A
Calculates the calibration multiplier based on historic annual outage input and a sum over the modeled asset failures in the calibration year. RUL for model is used to automatically zero out the RUL for end-of-life and retrofit project types. The PV benefit streams are summarized for incorporation into final outputs.

## Climate Data
DRAFT - Example Data Illustrative
Climate Data
Return Interval
|  | Location ID | Climate Peril | Scenario | Year | 10 | 20 | 50 | 100 | 200 | Location List
| Location 1Ice Accretion2023RCP4.5 | Location 1 | Ice Accretion | RCP4.5 | 2023 | 18.2256 | 21.7202 | 26.2483 | 29.7204 | 33.1729 | Location 1
| Location 1Ice Accretion2025RCP4.5 | Location 1 | Ice Accretion | RCP4.5 | 2025 | 18.2442 | 21.7568 | 26.3145 | 29.8051 | 33.2785
| Location 1Ice Accretion2030RCP4.5 | Location 1 | Ice Accretion | RCP4.5 | 2030 | 18.2627 | 21.7934 | 26.3806 | 29.8898 | 33.3841
| Location 1Ice Accretion2035RCP4.5 | Location 1 | Ice Accretion | RCP4.5 | 2035 | 18.2812 | 21.83 | 26.4468 | 29.9745 | 33.4896
| Location 1Ice Accretion2040RCP4.5 | Location 1 | Ice Accretion | RCP4.5 | 2040 | 18.2997 | 21.8666 | 26.5129 | 30.0593 | 33.5952
| Location 1Ice Accretion2045RCP4.5 | Location 1 | Ice Accretion | RCP4.5 | 2045 | 18.3183 | 21.9032 | 26.5791 | 30.144 | 33.7008
| Location 1Ice Accretion2050RCP4.5 | Location 1 | Ice Accretion | RCP4.5 | 2050 | 18.2627 | 21.8871 | 26.6135 | 30.2108 | 33.8064
| Location 1Ice Accretion2055RCP4.5 | Location 1 | Ice Accretion | RCP4.5 | 2055 | 18.1886 | 21.8344 | 26.5817 | 30.1928 | 33.8064
| Location 1Ice Accretion2060RCP4.5 | Location 1 | Ice Accretion | RCP4.5 | 2060 | 18.1145 | 21.7817 | 26.55 | 30.1749 | 33.8064
| Location 1Ice Accretion2065RCP4.5 | Location 1 | Ice Accretion | RCP4.5 | 2065 | 18.0404 | 21.729 | 26.5182 | 30.1569 | 33.8064
| Location 1Ice Accretion2070RCP4.5 | Location 1 | Ice Accretion | RCP4.5 | 2070 | 17.9663 | 21.6763 | 26.4865 | 30.139 | 33.8064
| Location 1Ice Accretion2075RCP4.5 | Location 1 | Ice Accretion | RCP4.5 | 2075 | 17.9324 | 21.6617 | 26.4997 | 30.1689 | 33.8564
| Location 1Ice Accretion2080RCP4.5 | Location 1 | Ice Accretion | RCP4.5 | 2080 | 17.8984 | 21.647 | 26.5129 | 30.1988 | 33.9064
| Location 1Ice Accretion2085RCP4.5 | Location 1 | Ice Accretion | RCP4.5 | 2085 | 17.8645 | 21.6324 | 26.5261 | 30.2287 | 33.9564
| Location 1Ice Accretion2090RCP4.5 | Location 1 | Ice Accretion | RCP4.5 | 2090 | 17.8305 | 21.6177 | 26.5394 | 30.2586 | 34.0064
| Location 1Ice Accretion2095RCP4.5 | Location 1 | Ice Accretion | RCP4.5 | 2095 | 17.7966 | 21.6031 | 26.5526 | 30.2885 | 34.0564
| Location 1Ice Accretion2100RCP4.5 | Location 1 | Ice Accretion | RCP4.5 | 2100 | 17.7626 | 21.5884 | 26.5658 | 30.3184 | 34.1064
| Location 1Ice Accretion2023RCP6.0 | Location 1 | Ice Accretion | RCP6.0 | 2023 | 18.2256 | 21.7202 | 26.2483 | 29.7204 | 33.1729
| Location 1Ice Accretion2025RCP6.0 | Location 1 | Ice Accretion | RCP6.0 | 2025 | 18.2442 | 21.7568 | 26.3145 | 29.8051 | 33.2785
| Location 1Ice Accretion2030RCP6.0 | Location 1 | Ice Accretion | RCP6.0 | 2030 | 18.2627 | 21.7934 | 26.3806 | 29.8898 | 33.3841
| Location 1Ice Accretion2035RCP6.0 | Location 1 | Ice Accretion | RCP6.0 | 2035 | 18.2812 | 21.83 | 26.4468 | 29.9745 | 33.4896
| Location 1Ice Accretion2040RCP6.0 | Location 1 | Ice Accretion | RCP6.0 | 2040 | 18.2997 | 21.8666 | 26.5129 | 30.0593 | 33.5952
| Location 1Ice Accretion2045RCP6.0 | Location 1 | Ice Accretion | RCP6.0 | 2045 | 18.3183 | 21.9032 | 26.5791 | 30.144 | 33.7008
| Location 1Ice Accretion2050RCP6.0 | Location 1 | Ice Accretion | RCP6.0 | 2050 | 18.2627 | 21.8871 | 26.6135 | 30.2108 | 33.8064
| Location 1Ice Accretion2055RCP6.0 | Location 1 | Ice Accretion | RCP6.0 | 2055 | 18.1886 | 21.8344 | 26.5817 | 30.1928 | 33.8064
| Location 1Ice Accretion2060RCP6.0 | Location 1 | Ice Accretion | RCP6.0 | 2060 | 18.1145 | 21.7817 | 26.55 | 30.1749 | 33.8064
| Location 1Ice Accretion2065RCP6.0 | Location 1 | Ice Accretion | RCP6.0 | 2065 | 18.0404 | 21.729 | 26.5182 | 30.1569 | 33.8064
| Location 1Ice Accretion2070RCP6.0 | Location 1 | Ice Accretion | RCP6.0 | 2070 | 17.9663 | 21.6763 | 26.4865 | 30.139 | 33.8064
| Location 1Ice Accretion2075RCP6.0 | Location 1 | Ice Accretion | RCP6.0 | 2075 | 17.9154 | 21.6543 | 26.5063 | 30.1838 | 33.8814
| Location 1Ice Accretion2080RCP6.0 | Location 1 | Ice Accretion | RCP6.0 | 2080 | 17.8645 | 21.6324 | 26.5261 | 30.2287 | 33.9564
| Location 1Ice Accretion2085RCP6.0 | Location 1 | Ice Accretion | RCP6.0 | 2085 | 17.8135 | 21.6104 | 26.546 | 30.2735 | 34.0314
| Location 1Ice Accretion2090RCP6.0 | Location 1 | Ice Accretion | RCP6.0 | 2090 | 17.5403 | 21.3688 | 26.3365 | 30.0892 | 33.8619
| Location 1Ice Accretion2095RCP6.0 | Location 1 | Ice Accretion | RCP6.0 | 2095 | 17.3181 | 21.1492 | 26.1072 | 29.8599 | 33.6174
| Location 1Ice Accretion2100RCP6.0 | Location 1 | Ice Accretion | RCP6.0 | 2100 | 17.0958 | 20.9296 | 25.8779 | 29.6307 | 33.3729
| Location 1Ice Accretion2023RCP8.5 | Location 1 | Ice Accretion | RCP8.5 | 2023 | 18.2256 | 21.7202 | 26.2483 | 29.7204 | 33.1729
| Location 1Ice Accretion2025RCP8.5 | Location 1 | Ice Accretion | RCP8.5 | 2025 | 18.2627 | 21.7934 | 26.3806 | 29.8898 | 33.3841
| Location 1Ice Accretion2030RCP8.5 | Location 1 | Ice Accretion | RCP8.5 | 2030 | 18.2997 | 21.8666 | 26.5129 | 30.0593 | 33.5952
| Location 1Ice Accretion2035RCP8.5 | Location 1 | Ice Accretion | RCP8.5 | 2035 | 18.3368 | 21.9398 | 26.6452 | 30.2287 | 33.8064
| Location 1Ice Accretion2040RCP8.5 | Location 1 | Ice Accretion | RCP8.5 | 2040 | 18.2133 | 21.852 | 26.5923 | 30.1988 | 33.8064
| Location 1Ice Accretion2045RCP8.5 | Location 1 | Ice Accretion | RCP8.5 | 2045 | 18.0898 | 21.7641 | 26.5394 | 30.1689 | 33.8064
| Location 1Ice Accretion2050RCP8.5 | Location 1 | Ice Accretion | RCP8.5 | 2050 | 17.8984 | 21.647 | 26.5129 | 30.1988 | 33.9064
| Location 1Ice Accretion2055RCP8.5 | Location 1 | Ice Accretion | RCP8.5 | 2055 | 17.8305 | 21.6177 | 26.5394 | 30.2586 | 34.0064
| Location 1Ice Accretion2060RCP8.5 | Location 1 | Ice Accretion | RCP8.5 | 2060 | 17.5403 | 21.3688 | 26.3365 | 30.0892 | 33.8619
| Location 1Ice Accretion2065RCP8.5 | Location 1 | Ice Accretion | RCP8.5 | 2065 | 17.3181 | 21.1492 | 26.1072 | 29.8599 | 33.6174
| Location 1Ice Accretion2070RCP8.5 | Location 1 | Ice Accretion | RCP8.5 | 2070 | 16.6945 | 20.483 | 25.3751 | 29.0825 | 32.7728
| Location 1Ice Accretion2075RCP8.5 | Location 1 | Ice Accretion | RCP8.5 | 2075 | 16.2932 | 20.0365 | 24.8724 | 28.5344 | 32.1727
| Location 1Ice Accretion2080RCP8.5 | Location 1 | Ice Accretion | RCP8.5 | 2080 | 15.8919 | 19.5899 | 24.3697 | 27.9862 | 31.5726
| Location 1Ice Accretion2085RCP8.5 | Location 1 | Ice Accretion | RCP8.5 | 2085 | 15.0584 | 18.6126 | 23.2054 | 26.6856 | 30.139
| Location 1Ice Accretion2090RCP8.5 | Location 1 | Ice Accretion | RCP8.5 | 2090 | 14.2249 | 17.6353 | 22.0412 | 25.3849 | 28.7054
| Location 1Ice Accretion2095RCP8.5 | Location 1 | Ice Accretion | RCP8.5 | 2095 | 14.2249 | 17.6353 | 22.0412 | 25.3849 | 28.7054
| Location 1Ice Accretion2100RCP8.5 | Location 1 | Ice Accretion | RCP8.5 | 2100 | 14.2249 | 17.6353 | 22.0412 | 25.3849 | 28.7054
| Location 1Wind2023RCP4.5 | Location 1 | Wind | RCP4.5 | 2023 | 84.4572 | 90.4515 | 97.471 | 104.4481 | 111.4344
| Location 1Wind2025RCP4.5 | Location 1 | Wind | RCP4.5 | 2025 | 84.5463 | 90.5676 | 97.6231 | 104.6314 | 111.6498
| Location 1Wind2030RCP4.5 | Location 1 | Wind | RCP4.5 | 2030 | 84.6354 | 90.6838 | 97.7751 | 104.8146 | 111.8651
| Location 1Wind2035RCP4.5 | Location 1 | Wind | RCP4.5 | 2035 | 84.7246 | 90.7999 | 97.9272 | 104.9979 | 112.0804
| Location 1Wind2040RCP4.5 | Location 1 | Wind | RCP4.5 | 2040 | 84.8137 | 90.916 | 98.0792 | 105.1812 | 112.2957
| Location 1Wind2045RCP4.5 | Location 1 | Wind | RCP4.5 | 2045 | 84.9028 | 91.0321 | 98.2313 | 105.3644 | 112.5111
| Location 1Wind2050RCP4.5 | Location 1 | Wind | RCP4.5 | 2050 | 85.0254 | 91.1893 | 98.4352 | 105.6073 | 112.7921
| Location 1Wind2055RCP4.5 | Location 1 | Wind | RCP4.5 | 2055 | 85.0588 | 91.2304 | 98.4871 | 105.6669 | 112.8578
| Location 1Wind2060RCP4.5 | Location 1 | Wind | RCP4.5 | 2060 | 85.0922 | 91.2715 | 98.539 | 105.7265 | 112.9234
| Location 1Wind2065RCP4.5 | Location 1 | Wind | RCP4.5 | 2065 | 85.1256 | 91.3125 | 98.5908 | 105.7861 | 112.9891
| Location 1Wind2070RCP4.5 | Location 1 | Wind | RCP4.5 | 2070 | 85.1591 | 91.3536 | 98.6427 | 105.8457 | 113.0548
| Location 1Wind2075RCP4.5 | Location 1 | Wind | RCP4.5 | 2075 | 85.2621 | 91.4906 | 98.822 | 106.0615 | 113.3103
| Location 1Wind2080RCP4.5 | Location 1 | Wind | RCP4.5 | 2080 | 85.3652 | 91.6275 | 99.0012 | 106.2773 | 113.5658
| Location 1Wind2085RCP4.5 | Location 1 | Wind | RCP4.5 | 2085 | 85.4682 | 91.7645 | 99.1805 | 106.4931 | 113.8212
| Location 1Wind2090RCP4.5 | Location 1 | Wind | RCP4.5 | 2090 | 85.5713 | 91.9014 | 99.3598 | 106.7089 | 114.0767
| Location 1Wind2095RCP4.5 | Location 1 | Wind | RCP4.5 | 2095 | 85.6743 | 92.0384 | 99.5391 | 106.9247 | 114.3322
| Location 1Wind2100RCP4.5 | Location 1 | Wind | RCP4.5 | 2100 | 85.7774 | 92.1754 | 99.7183 | 107.1405 | 114.5876
| Location 1Wind2023RCP6.0 | Location 1 | Wind | RCP6.0 | 2023 | 84.4572 | 90.4515 | 97.471 | 104.4481 | 111.4344
| Location 1Wind2025RCP6.0 | Location 1 | Wind | RCP6.0 | 2025 | 84.5463 | 90.5676 | 97.6231 | 104.6314 | 111.6498
| Location 1Wind2030RCP6.0 | Location 1 | Wind | RCP6.0 | 2030 | 84.6354 | 90.6838 | 97.7751 | 104.8146 | 111.8651
| Location 1Wind2035RCP6.0 | Location 1 | Wind | RCP6.0 | 2035 | 84.7246 | 90.7999 | 97.9272 | 104.9979 | 112.0804
| Location 1Wind2040RCP6.0 | Location 1 | Wind | RCP6.0 | 2040 | 84.8137 | 90.916 | 98.0792 | 105.1812 | 112.2957
| Location 1Wind2045RCP6.0 | Location 1 | Wind | RCP6.0 | 2045 | 84.9028 | 91.0321 | 98.2313 | 105.3644 | 112.5111
| Location 1Wind2050RCP6.0 | Location 1 | Wind | RCP6.0 | 2050 | 85.0254 | 91.1893 | 98.4352 | 105.6073 | 112.7921
| Location 1Wind2055RCP6.0 | Location 1 | Wind | RCP6.0 | 2055 | 85.0588 | 91.2304 | 98.4871 | 105.6669 | 112.8578
| Location 1Wind2060RCP6.0 | Location 1 | Wind | RCP6.0 | 2060 | 85.0922 | 91.2715 | 98.539 | 105.7265 | 112.9234
| Location 1Wind2065RCP6.0 | Location 1 | Wind | RCP6.0 | 2065 | 85.1256 | 91.3125 | 98.5908 | 105.7861 | 112.9891
| Location 1Wind2070RCP6.0 | Location 1 | Wind | RCP6.0 | 2070 | 85.1591 | 91.3536 | 98.6427 | 105.8457 | 113.0548
| Location 1Wind2075RCP6.0 | Location 1 | Wind | RCP6.0 | 2075 | 85.3136 | 91.5591 | 98.9116 | 106.1694 | 113.438
| Location 1Wind2080RCP6.0 | Location 1 | Wind | RCP6.0 | 2080 | 85.4682 | 91.7645 | 99.1805 | 106.4931 | 113.8212
| Location 1Wind2085RCP6.0 | Location 1 | Wind | RCP6.0 | 2085 | 85.6228 | 91.9699 | 99.4494 | 106.8168 | 114.2044
| Location 1Wind2090RCP6.0 | Location 1 | Wind | RCP6.0 | 2090 | 86.0782 | 92.5326 | 100.1441 | 107.6303 | 115.1387
| Location 1Wind2095RCP6.0 | Location 1 | Wind | RCP6.0 | 2095 | 86.379 | 92.8899 | 100.5699 | 108.1202 | 115.6898
| Location 1Wind2100RCP6.0 | Location 1 | Wind | RCP6.0 | 2100 | 86.6797 | 93.2472 | 100.9957 | 108.61 | 116.2409
| Location 1Wind2023RCP8.5 | Location 1 | Wind | RCP8.5 | 2023 | 84.4572 | 90.4515 | 97.471 | 104.4481 | 111.4344
| Location 1Wind2025RCP8.5 | Location 1 | Wind | RCP8.5 | 2025 | 84.6354 | 90.6838 | 97.7751 | 104.8146 | 111.8651
| Location 1Wind2030RCP8.5 | Location 1 | Wind | RCP8.5 | 2030 | 84.8137 | 90.916 | 98.0792 | 105.1812 | 112.2957
| Location 1Wind2035RCP8.5 | Location 1 | Wind | RCP8.5 | 2035 | 84.9919 | 91.1482 | 98.3834 | 105.5477 | 112.7264
| Location 1Wind2040RCP8.5 | Location 1 | Wind | RCP8.5 | 2040 | 85.0476 | 91.2167 | 98.4698 | 105.647 | 112.8359
| Location 1Wind2045RCP8.5 | Location 1 | Wind | RCP8.5 | 2045 | 85.1033 | 91.2852 | 98.5562 | 105.7463 | 112.9453
| Location 1Wind2050RCP8.5 | Location 1 | Wind | RCP8.5 | 2050 | 85.3652 | 91.6275 | 99.0012 | 106.2773 | 113.5658
| Location 1Wind2055RCP8.5 | Location 1 | Wind | RCP8.5 | 2055 | 85.5713 | 91.9014 | 99.3598 | 106.7089 | 114.0767
| Location 1Wind2060RCP8.5 | Location 1 | Wind | RCP8.5 | 2060 | 86.0782 | 92.5326 | 100.1441 | 107.6303 | 115.1387
| Location 1Wind2065RCP8.5 | Location 1 | Wind | RCP8.5 | 2065 | 86.379 | 92.8899 | 100.5699 | 108.1202 | 115.6898
| Location 1Wind2070RCP8.5 | Location 1 | Wind | RCP8.5 | 2070 | 86.9443 | 93.5925 | 101.4503 | 109.1512 | 116.8759
| Location 1Wind2075RCP8.5 | Location 1 | Wind | RCP8.5 | 2075 | 87.2089 | 93.9379 | 101.9048 | 109.6924 | 117.5109
| Location 1Wind2080RCP8.5 | Location 1 | Wind | RCP8.5 | 2080 | 87.4735 | 94.2832 | 102.3594 | 110.2337 | 118.1459
| Location 1Wind2085RCP8.5 | Location 1 | Wind | RCP8.5 | 2085 | 87.8245 | 94.7254 | 102.9213 | 110.9016 | 118.9178
| Location 1Wind2090RCP8.5 | Location 1 | Wind | RCP8.5 | 2090 | 88.1754 | 95.1675 | 103.4831 | 111.5696 | 119.6897
| Location 1Wind2095RCP8.5 | Location 1 | Wind | RCP8.5 | 2095 | 88.1754 | 95.1675 | 103.4831 | 111.5696 | 119.6897
| Location 1Wind2100RCP8.5 | Location 1 | Wind | RCP8.5 | 2100 | 88.1754 | 95.1675 | 103.4831 | 111.5696 | 119.6897
TBD
Climate inputs developed through the use of ECCC and CSA data. Use of this climate data is optional and links to to tab '3. Climate Severity Calculator'.

## Int VA Calcs
DRAFT - Example Data Illustrative
Risk Heatmap
Guidehouse, October 2024
|  | Location | Location 1
[7 empty] | Annual Event Probability Forecast | [19 empty] | Total Annual Probability Across Perils
|  | Asset Class | Sub Class | Climate Peril | Severity Threshold | 2023 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2055 | 2060 | 2065 | 2070 | 2075 | 2080 | 2085 | 2090 | 2095 | 2100 |  | Asset Class | Sub Class | 2023 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2055 | 2060 | 2065 | 2070 | 2075 | 2080 | 2085 | 2090 | 2095 | 2100 | Unique Asset List | Class List | Sub Class List
Location 1PoleClass 5 | Location 1Wind80 | Pole | Class 5 | Wind | 80 | 0.11796 | 0.11822 | 0.11849 | 0.11875 | 0.11902 | 0.11929 | 0.11965 | 0.11975 | 0.11985 | 0.11995 | 0.12005 | 0.12051 | 0.12098 | 0.12144 | 0.1228 | 0.1237 | 0.1246 | Location 1PoleClass 5 | Pole | Class 5 | 11.8% | 11.82% | 11.85% | 11.88% | 11.9% | 11.93% | 11.97% | 11.98% | 11.99% | 12% | 12.01% | 12.05% | 12.1% | 12.14% | 12.28% | 12.37% | 12.46% | Pole-Class 5 | Pole | Class 5
Location 1PoleClass 4 | Location 1Wind85 | Pole | Class 4 | Wind | 85 | 0.093916 | 0.094911 | 0.095908 | 0.096906 | 0.097906 | 0.098907 | 0.10007 | 0.10016 | 0.10025 | 0.10034 | 0.10043 | 0.10085 | 0.10127 | 0.10169 | 0.10293 | 0.10374 | 0.10456 | Location 1PoleClass 4 | Pole | Class 4 | 9.392% | 9.491% | 9.591% | 9.691% | 9.791% | 9.891% | 10.01% | 10.02% | 10.02% | 10.03% | 10.04% | 10.09% | 10.13% | 10.17% | 10.29% | 10.37% | 10.46% | Pole-Class 4 | Pole | Class 4
Location 1PoleClass 3 | Location 1Wind100 | Pole | Class 3 | Wind | 100 | 0.018976 | 0.019268 | 0.019562 | 0.019858 | 0.020204 | 0.020598 | 0.021132 | 0.021269 | 0.021406 | 0.021544 | 0.021683 | 0.022406 | 0.023141 | 0.023886 | 0.02589 | 0.027176 | 0.028502 | Location 1PoleClass 3 | Pole | Class 3 | 1.898% | 1.927% | 1.956% | 1.986% | 2.02% | 2.06% | 2.113% | 2.127% | 2.141% | 2.154% | 2.168% | 2.241% | 2.314% | 2.389% | 2.589% | 2.718% | 2.85% | Pole-Class 3 | Pole | Class 3
Location 1PoleClass 2 | Location 1Wind110 | Pole | Class 2 | Wind | 110 | 0.0071709 | 0.0073129 | 0.0074565 | 0.0076015 | 0.007748 | 0.007896 | 0.0080934 | 0.0081414 | 0.0081897 | 0.0082382 | 0.0082869 | 0.0085599 | 0.0088372 | 0.0091188 | 0.0098446 | 0.010298 | 0.010765 | Location 1PoleClass 2 | Pole | Class 2 | 0.7171% | 0.7313% | 0.7457% | 0.7602% | 0.7748% | 0.7896% | 0.8093% | 0.8141% | 0.819% | 0.8238% | 0.8287% | 0.856% | 0.8837% | 0.9119% | 0.9845% | 1.03% | 1.077% | Pole-Class 2 | Pole | Class 2

## Revenue Requirement Calculation
GLOBAL ASSUMPTIONS |  |  | Baseline Customer Revenue Requirement Multiplier |  |  |  | Scenario Customer Revenue Requirement Multiplier
|  |  | Asset Lifetime | 40 |  | Customer PV of Revenue Requirement for a $1 Investment | Asset Lifetime | 40 |  | Customer PV of Revenue Requirement for a $1 Investment
Asset Capital Cost | 1 |  | Depreciation | 2.5% |  | 2.2599 | Depreciation | 2.5% |  | 2.2599
|  |  |  | Opening Book Value | Nominal Revenue Requirement by Year | Present Value of Revenue Requirement in Year 1 Constant Dollars |  | Opening Book Value | Nominal Revenue Requirement by Year | Present Value of Revenue Requirement in Year 1 Constant Dollars
|  |  | Year |  |  |  | Year
Per IESO Guide for NWAs |  |  | 1 | 1 | 0.125 | 0.125 | 1 | 1 | 0.125 | 0.125
IESO_NWA_Guide_Regional_Planning |  |  | 2 | 0.975 | 0.10855 | 0.10642 | 2 | 0.975 | 0.10855 | 0.10642
Inflation Rate | 2% |  | 3 | 0.95 | 0.10651 | 0.10237 | 3 | 0.95 | 0.10651 | 0.10237
Social Discount Rate | 4% |  | 4 | 0.925 | 0.10475 | 0.098708 | 4 | 0.925 | 0.10475 | 0.098708
Pre-tax WACC | 7% |  | 5 | 0.9 | 0.103 | 0.095156 | 5 | 0.9 | 0.103 | 0.095156
|  |  | 6 | 0.875 | 0.10125 | 0.091705 | 6 | 0.875 | 0.10125 | 0.091705
|  |  | 7 | 0.85 | 0.0995 | 0.088353 | 7 | 0.85 | 0.0995 | 0.088353
OEB Cost of Capital Parameters |  |  | 8 | 0.825 | 0.09775 | 0.085097 | 8 | 0.825 | 0.09775 | 0.085097
|  |  | 9 | 0.8 | 0.096 | 0.081935 | 9 | 0.8 | 0.096 | 0.081935
Other Assumptions |  |  | 10 | 0.775 | 0.09425 | 0.078864 | 10 | 0.775 | 0.09425 | 0.078864
Tax Rate | 26.5% | 15% federal and 11.5% provincial | 11 | 0.75 | 0.0925 | 0.075882 | 11 | 0.75 | 0.0925 | 0.075882
Base O & M Costs | 1.5% |  | 12 | 0.725 | 0.09075 | 0.072987 | 12 | 0.725 | 0.09075 | 0.072987
Scenario O& M Costs | 1.5% |  | 13 | 0.7 | 0.089 | 0.070176 | 13 | 0.7 | 0.089 | 0.070176
|  |  | 14 | 0.675 | 0.08725 | 0.067447 | 14 | 0.675 | 0.08725 | 0.067447
Federal Tax Rate |  |  | 15 | 0.65 | 0.0855 | 0.064798 | 15 | 0.65 | 0.0855 | 0.064798
Provincial Tax Rate |  |  | 16 | 0.625 | 0.08375 | 0.062227 | 16 | 0.625 | 0.08375 | 0.062227
|  |  | 17 | 0.6 | 0.082 | 0.059733 | 17 | 0.6 | 0.082 | 0.059733
|  |  | 18 | 0.575 | 0.08025 | 0.057312 | 18 | 0.575 | 0.08025 | 0.057312
|  |  | 19 | 0.55 | 0.0785 | 0.054963 | 19 | 0.55 | 0.0785 | 0.054963
|  |  | 20 | 0.525 | 0.07675 | 0.052684 | 20 | 0.525 | 0.07675 | 0.052684
|  |  | 21 | 0.5 | 0.075 | 0.050473 | 21 | 0.5 | 0.075 | 0.050473
|  |  | 22 | 0.475 | 0.07325 | 0.048329 | 22 | 0.475 | 0.07325 | 0.048329
|  |  | 23 | 0.45 | 0.0715 | 0.046249 | 23 | 0.45 | 0.0715 | 0.046249
|  |  | 24 | 0.425 | 0.06975 | 0.044232 | 24 | 0.425 | 0.06975 | 0.044232
|  |  | 25 | 0.4 | 0.068 | 0.042277 | 25 | 0.4 | 0.068 | 0.042277
|  |  | 26 | 0.375 | 0.06625 | 0.040381 | 26 | 0.375 | 0.06625 | 0.040381
|  |  | 27 | 0.35 | 0.0645 | 0.038544 | 27 | 0.35 | 0.0645 | 0.038544
|  |  | 28 | 0.325 | 0.06275 | 0.036763 | 28 | 0.325 | 0.06275 | 0.036763
|  |  | 29 | 0.3 | 0.061 | 0.035037 | 29 | 0.3 | 0.061 | 0.035037
|  |  | 30 | 0.275 | 0.05925 | 0.033364 | 30 | 0.275 | 0.05925 | 0.033364
|  |  | 31 | 0.25 | 0.0575 | 0.031744 | 31 | 0.25 | 0.0575 | 0.031744
|  |  | 32 | 0.225 | 0.05575 | 0.030174 | 32 | 0.225 | 0.05575 | 0.030174
|  |  | 33 | 0.2 | 0.054 | 0.028654 | 33 | 0.2 | 0.054 | 0.028654
|  |  | 34 | 0.175 | 0.05225 | 0.027182 | 34 | 0.175 | 0.05225 | 0.027182
|  |  | 35 | 0.15 | 0.0505 | 0.025756 | 35 | 0.15 | 0.0505 | 0.025756
|  |  | 36 | 0.125 | 0.04875 | 0.024376 | 36 | 0.125 | 0.04875 | 0.024376
|  |  | 37 | 0.1 | 0.047 | 0.02304 | 37 | 0.1 | 0.047 | 0.02304
|  |  | 38 | 0.075 | 0.04525 | 0.021748 | 38 | 0.075 | 0.04525 | 0.021748
|  |  | 39 | 0.05 | 0.0435 | 0.020497 | 39 | 0.05 | 0.0435 | 0.020497
|  |  | 40 | 0.025 | 0.04175 | 0.019286 | 40 | 0.025 | 0.04175 | 0.019286
|  |  | 41 | 0 | 0 | 0 | 41 | 0 | 0 | 0
|  |  | 42 | 0 | 0 | 0 | 42 | 0 | 0 | 0
|  |  | 43 | 0 | 0 | 0 | 43 | 0 | 0 | 0
|  |  | 44 | 0 | 0 | 0 | 44 | 0 | 0 | 0
|  |  | 45 | 0 | 0 | 0 | 45 | 0 | 0 | 0
|  |  | 46 | 0 | 0 | 0 | 46 | 0 | 0 | 0
|  |  | 47 | 0 | 0 | 0 | 47 | 0 | 0 | 0
|  |  | 48 | 0 | 0 | 0 | 48 | 0 | 0 | 0
|  |  | 49 | 0 | 0 | 0 | 49 | 0 | 0 | 0
|  |  | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0
|  |  | 51 | 0 | 0 | 0 | 51 | 0 | 0 | 0
|  |  | 52 | 0 | 0 | 0 | 52 | 0 | 0 | 0
|  |  | 53 | 0 | 0 | 0 | 53 | 0 | 0 | 0
|  |  | 54 | 0 | 0 | 0 | 54 | 0 | 0 | 0
|  |  | 55 | 0 | 0 | 0 | 55 | 0 | 0 | 0
|  |  | 56 | 0 | 0 | 0 | 56 | 0 | 0 | 0
|  |  | 57 | 0 | 0 | 0 | 57 | 0 | 0 | 0
|  |  | 58 | 0 | 0 | 0 | 58 | 0 | 0 | 0
|  |  | 59 | 0 | 0 | 0 | 59 | 0 | 0 | 0
|  |  | 60 | 0 | 0 | 0 | 60 | 0 | 0 | 0
|  |  | 61 | 0 | 0 | 0 | 61 | 0 | 0 | 0
|  |  | 62 | 0 | 0 | 0 | 62 | 0 | 0 | 0
|  |  | 63 | 0 | 0 | 0 | 63 | 0 | 0 | 0
|  |  | 64 | 0 | 0 | 0 | 64 | 0 | 0 | 0
|  |  | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0
|  |  | 66 | 0 | 0 | 0 | 66 | 0 | 0 | 0
|  |  | 67 | 0 | 0 | 0 | 67 | 0 | 0 | 0
|  |  | 68 | 0 | 0 | 0 | 68 | 0 | 0 | 0
|  |  | 69 | 0 | 0 | 0 | 69 | 0 | 0 | 0
|  |  | 70 | 0 | 0 | 0 | 70 | 0 | 0 | 0
|  |  | 71 | 0 | 0 | 0 | 71 | 0 | 0 | 0
|  |  | 72 | 0 | 0 | 0 | 72 | 0 | 0 | 0
|  |  | 73 | 0 | 0 | 0 | 73 | 0 | 0 | 0
|  |  | 74 | 0 | 0 | 0 | 74 | 0 | 0 | 0
|  |  | 75 | 0 | 0 | 0 | 75 | 0 | 0 | 0
|  |  | 76 | 0 | 0 | 0 | 76 | 0 | 0 | 0
|  |  | 77 | 0 | 0 | 0 | 77 | 0 | 0 | 0
|  |  | 78 | 0 | 0 | 0 | 78 | 0 | 0 | 0
|  |  | 79 | 0 | 0 | 0 | 79 | 0 | 0 | 0
|  |  | 80 | 0 | 0 | 0 | 80 | 0 | 0 | 0
|  |  | 81 | 0 | 0 | 0 | 81 | 0 | 0 | 0
|  |  | 82 | 0 | 0 | 0 | 82 | 0 | 0 | 0
|  |  | 83 | 0 | 0 | 0 | 83 | 0 | 0 | 0
|  |  | 84 | 0 | 0 | 0 | 84 | 0 | 0 | 0
|  |  | 85 | 0 | 0 | 0 | 85 | 0 | 0 | 0
|  |  | 86 | 0 | 0 | 0 | 86 | 0 | 0 | 0
|  |  | 87 | 0 | 0 | 0 | 87 | 0 | 0 | 0
|  |  | 88 | 0 | 0 | 0 | 88 | 0 | 0 | 0
|  |  | 89 | 0 | 0 | 0 | 89 | 0 | 0 | 0
|  |  | 90 | 0 | 0 | 0 | 90 | 0 | 0 | 0
|  |  | 91 | 0 | 0 | 0 | 91 | 0 | 0 | 0
|  |  | 92 | 0 | 0 | 0 | 92 | 0 | 0 | 0
|  |  | 93 | 0 | 0 | 0 | 93 | 0 | 0 | 0
|  |  | 94 | 0 | 0 | 0 | 94 | 0 | 0 | 0
|  |  | 95 | 0 | 0 | 0 | 95 | 0 | 0 | 0
|  |  | 96 | 0 | 0 | 0 | 96 | 0 | 0 | 0
|  |  | 97 | 0 | 0 | 0 | 97 | 0 | 0 | 0
|  |  | 98 | 0 | 0 | 0 | 98 | 0 | 0 | 0
|  |  | 99 | 0 | 0 | 0 | 99 | 0 | 0 | 0
|  |  | 100 | 0 | 0 | 0 | 100 | 0 | 0 | 0
|  |  | 101 |  |  |  | 101
Note on K111: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is included only to ensure that the indexing for the nominal payment (which captures the depreciation in each yar) works properly.
Note on P111: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is included only to ensure that the indexing for the nominal payment (which captures the depreciation in each yar) works properly.
Calculates the baseline and scenario utility cost to PV customer cost multiplier. This value is applied to utility investment spending to estimate the PV of lifetime customer rate impacts from the investment. The multiplier considers O&M changes from the investment as well as tax, WACC, and project lifetime. This multiplier aligns the VASH BCA methodology with the DST to allow for consistent evaluation of customer benefits from resiliency investments.

## Int BCA Costs
Early Retirement Cost Adjustment
Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101
Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 4 | -1093804.6829 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
For early retirement projects, the BCA cost is adjusted to account for what would have occurred in the absence of the resiliency investment. The assumption is that the LDC would have replaced the existing assets with standard assets after the RUL period is over. This tab calculates the credit that should be applied to the full upfront cost of the replacement assets (in customer revenue requirement) to account for the avoided future investment at the end of the RUL period.

## Int BCA Ann Fail Prob
Asset Class Annual Probability of Failure Uncalibrated | [79 empty] | Asset Class Annual Probability of Failure Calibrated | [79 empty] | Total Existing Asset Class Annual Probability of Failure Calibrated | [79 empty] | Total Replacement Asset Class Annual Probability of Failure Calibrated | [79 empty] | Total Standard Asset Class Annual Probability of Failure Calibrated
Asset Class | Asset Sub-Class | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | Asset Class | Asset Sub-Class | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | Asset Class | Asset Sub-Class | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | Asset Class | Asset Sub-Class | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | Asset Class | Asset Sub-Class | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100
Pole | Class 5 | 0.11796 | 0.11809 | 0.11822 | 0.11828 | 0.11833 | 0.11838 | 0.11843 | 0.11849 | 0.11854 | 0.11859 | 0.11865 | 0.1187 | 0.11875 | 0.11881 | 0.11886 | 0.11891 | 0.11897 | 0.11902 | 0.11907 | 0.11913 | 0.11918 | 0.11923 | 0.11929 | 0.11936 | 0.11943 | 0.11951 | 0.11958 | 0.11965 | 0.11967 | 0.11969 | 0.11971 | 0.11973 | 0.11975 | 0.11977 | 0.11979 | 0.11981 | 0.11983 | 0.11985 | 0.11987 | 0.11989 | 0.11991 | 0.11993 | 0.11995 | 0.11997 | 0.11999 | 0.12001 | 0.12003 | 0.12005 | 0.12014 | 0.12024 | 0.12033 | 0.12042 | 0.12051 | 0.12061 | 0.1207 | 0.12079 | 0.12088 | 0.12098 | 0.12107 | 0.12116 | 0.12125 | 0.12135 | 0.12144 | 0.12171 | 0.12198 | 0.12226 | 0.12253 | 0.1228 | 0.12298 | 0.12316 | 0.12334 | 0.12352 | 0.1237 | 0.12388 | 0.12406 | 0.12424 | 0.12442 | 0.1246 | Pole | Class 5 | 0.027342 | 0.027372 | 0.027403 | 0.027416 | 0.027428 | 0.02744 | 0.027453 | 0.027465 | 0.027477 | 0.02749 | 0.027502 | 0.027514 | 0.027527 | 0.027539 | 0.027551 | 0.027564 | 0.027576 | 0.027588 | 0.027601 | 0.027613 | 0.027625 | 0.027638 | 0.02765 | 0.027667 | 0.027684 | 0.027701 | 0.027718 | 0.027735 | 0.02774 | 0.027744 | 0.027749 | 0.027753 | 0.027758 | 0.027763 | 0.027767 | 0.027772 | 0.027777 | 0.027781 | 0.027786 | 0.02779 | 0.027795 | 0.0278 | 0.027804 | 0.027809 | 0.027814 | 0.027818 | 0.027823 | 0.027827 | 0.027849 | 0.02787 | 0.027892 | 0.027913 | 0.027935 | 0.027956 | 0.027977 | 0.027999 | 0.02802 | 0.028042 | 0.028063 | 0.028085 | 0.028106 | 0.028127 | 0.028149 | 0.028212 | 0.028275 | 0.028338 | 0.028401 | 0.028465 | 0.028506 | 0.028548 | 0.02859 | 0.028631 | 0.028673 | 0.028715 | 0.028757 | 0.028798 | 0.02884 | 0.028882 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 4 | 0.093916 | 0.094414 | 0.094911 | 0.095111 | 0.09531 | 0.095509 | 0.095709 | 0.095908 | 0.096108 | 0.096307 | 0.096507 | 0.096707 | 0.096906 | 0.097106 | 0.097306 | 0.097506 | 0.097706 | 0.097906 | 0.098106 | 0.098306 | 0.098507 | 0.098707 | 0.098907 | 0.099139 | 0.099372 | 0.099604 | 0.099836 | 0.10007 | 0.10009 | 0.1001 | 0.10012 | 0.10014 | 0.10016 | 0.10018 | 0.1002 | 0.10021 | 0.10023 | 0.10025 | 0.10027 | 0.10029 | 0.1003 | 0.10032 | 0.10034 | 0.10036 | 0.10038 | 0.10039 | 0.10041 | 0.10043 | 0.10051 | 0.1006 | 0.10068 | 0.10077 | 0.10085 | 0.10093 | 0.10102 | 0.1011 | 0.10119 | 0.10127 | 0.10135 | 0.10144 | 0.10152 | 0.1016 | 0.10169 | 0.10194 | 0.10218 | 0.10243 | 0.10268 | 0.10293 | 0.10309 | 0.10325 | 0.10342 | 0.10358 | 0.10374 | 0.10391 | 0.10407 | 0.10424 | 0.1044 | 0.10456 | Pole | Class 4 | 0.021769 | 0.021885 | 0.022 | 0.022046 | 0.022092 | 0.022139 | 0.022185 | 0.022231 | 0.022277 | 0.022324 | 0.02237 | 0.022416 | 0.022462 | 0.022509 | 0.022555 | 0.022601 | 0.022648 | 0.022694 | 0.022741 | 0.022787 | 0.022833 | 0.02288 | 0.022926 | 0.02298 | 0.023034 | 0.023088 | 0.023142 | 0.023195 | 0.0232 | 0.023204 | 0.023208 | 0.023212 | 0.023216 | 0.023221 | 0.023225 | 0.023229 | 0.023233 | 0.023237 | 0.023242 | 0.023246 | 0.02325 | 0.023254 | 0.023258 | 0.023263 | 0.023267 | 0.023271 | 0.023275 | 0.023279 | 0.023299 | 0.023318 | 0.023338 | 0.023357 | 0.023377 | 0.023396 | 0.023415 | 0.023435 | 0.023454 | 0.023474 | 0.023493 | 0.023513 | 0.023532 | 0.023552 | 0.023571 | 0.023628 | 0.023686 | 0.023743 | 0.0238 | 0.023858 | 0.023896 | 0.023934 | 0.023972 | 0.024009 | 0.024047 | 0.024085 | 0.024123 | 0.024161 | 0.024199 | 0.024237 | Pole | Class 4 | 2.1769 | 2.1885 | 2.2 | 2.2046 | 2.2092 | 2.2139 | 2.2185 | 2.2231 | 2.2277 | 2.2324 | 2.237 | 2.2416 | 2.2462 | 2.2509 | 2.2555 | 2.2601 | 2.2648 | 2.2694 | 2.2741 | 2.2787 | 2.2833 | 2.288 | 2.2926 | 2.298 | 2.3034 | 2.3088 | 2.3142 | 2.3195 | 2.32 | 2.3204 | 2.3208 | 2.3212 | 2.3216 | 2.3221 | 2.3225 | 2.3229 | 2.3233 | 2.3237 | 2.3242 | 2.3246 | 2.325 | 2.3254 | 2.3258 | 2.3263 | 2.3267 | 2.3271 | 2.3275 | 2.3279 | 2.3299 | 2.3318 | 2.3338 | 2.3357 | 2.3377 | 2.3396 | 2.3415 | 2.3435 | 2.3454 | 2.3474 | 2.3493 | 2.3513 | 2.3532 | 2.3552 | 2.3571 | 2.3628 | 2.3686 | 2.3743 | 2.38 | 2.3858 | 2.3896 | 2.3934 | 2.3972 | 2.4009 | 2.4047 | 2.4085 | 2.4123 | 2.4161 | 2.4199 | 2.4237 | Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 3 | 0.018976 | 0.019122 | 0.019268 | 0.019327 | 0.019386 | 0.019444 | 0.019503 | 0.019562 | 0.019621 | 0.01968 | 0.019739 | 0.019799 | 0.019858 | 0.019927 | 0.019996 | 0.020065 | 0.020135 | 0.020204 | 0.020283 | 0.020361 | 0.02044 | 0.020519 | 0.020598 | 0.020704 | 0.020811 | 0.020918 | 0.021025 | 0.021132 | 0.021159 | 0.021186 | 0.021214 | 0.021241 | 0.021269 | 0.021296 | 0.021324 | 0.021351 | 0.021379 | 0.021406 | 0.021434 | 0.021462 | 0.021489 | 0.021517 | 0.021544 | 0.021572 | 0.0216 | 0.021627 | 0.021655 | 0.021683 | 0.021828 | 0.021972 | 0.022117 | 0.022262 | 0.022406 | 0.022553 | 0.0227 | 0.022847 | 0.022994 | 0.023141 | 0.02329 | 0.023439 | 0.023588 | 0.023737 | 0.023886 | 0.024287 | 0.024688 | 0.025088 | 0.025489 | 0.02589 | 0.026147 | 0.026404 | 0.026662 | 0.026919 | 0.027176 | 0.027441 | 0.027707 | 0.027972 | 0.028237 | 0.028502 | Pole | Class 3 | 0.0043986 | 0.0044324 | 0.0044663 | 0.0044799 | 0.0044935 | 0.0045071 | 0.0045208 | 0.0045344 | 0.0045481 | 0.0045618 | 0.0045755 | 0.0045892 | 0.0046029 | 0.004619 | 0.004635 | 0.0046511 | 0.0046671 | 0.0046831 | 0.0047014 | 0.0047196 | 0.0047379 | 0.0047562 | 0.0047744 | 0.0047992 | 0.0048239 | 0.0048487 | 0.0048734 | 0.0048982 | 0.0049046 | 0.0049109 | 0.0049173 | 0.0049236 | 0.00493 | 0.0049364 | 0.0049427 | 0.0049491 | 0.0049555 | 0.0049619 | 0.0049683 | 0.0049747 | 0.0049811 | 0.0049875 | 0.0049939 | 0.0050003 | 0.0050067 | 0.0050131 | 0.0050196 | 0.005026 | 0.0050595 | 0.005093 | 0.0051266 | 0.0051601 | 0.0051936 | 0.0052277 | 0.0052617 | 0.0052958 | 0.0053298 | 0.0053639 | 0.0053984 | 0.005433 | 0.0054676 | 0.0055021 | 0.0055367 | 0.0056296 | 0.0057224 | 0.0058153 | 0.0059082 | 0.0060011 | 0.0060607 | 0.0061204 | 0.00618 | 0.0062397 | 0.0062993 | 0.0063608 | 0.0064223 | 0.0064837 | 0.0065452 | 0.0066067 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0.43986 | 0.44324 | 0.44663 | 0.44799 | 0.44935 | 0.45071 | 0.45208 | 0.45344 | 0.45481 | 0.45618 | 0.45755 | 0.45892 | 0.46029 | 0.4619 | 0.4635 | 0.46511 | 0.46671 | 0.46831 | 0.47014 | 0.47196 | 0.47379 | 0.47562 | 0.47744 | 0.47992 | 0.48239 | 0.48487 | 0.48734 | 0.48982 | 0.49046 | 0.49109 | 0.49173 | 0.49236 | 0.493 | 0.49364 | 0.49427 | 0.49491 | 0.49555 | 0.49619 | 0.49683 | 0.49747 | 0.49811 | 0.49875 | 0.49939 | 0.50003 | 0.50067 | 0.50131 | 0.50196 | 0.5026 | 0.50595 | 0.5093 | 0.51266 | 0.51601 | 0.51936 | 0.52277 | 0.52617 | 0.52958 | 0.53298 | 0.53639 | 0.53984 | 0.5433 | 0.54676 | 0.55021 | 0.55367 | 0.56296 | 0.57224 | 0.58153 | 0.59082 | 0.60011 | 0.60607 | 0.61204 | 0.618 | 0.62397 | 0.62993 | 0.63608 | 0.64223 | 0.64837 | 0.65452 | 0.66067
Pole | Class 2 | 0.0071709 | 0.0072419 | 0.0073129 | 0.0073417 | 0.0073704 | 0.0073991 | 0.0074278 | 0.0074565 | 0.0074855 | 0.0075145 | 0.0075435 | 0.0075725 | 0.0076015 | 0.0076308 | 0.0076601 | 0.0076894 | 0.0077187 | 0.007748 | 0.0077776 | 0.0078072 | 0.0078368 | 0.0078664 | 0.007896 | 0.0079355 | 0.007975 | 0.0080144 | 0.0080539 | 0.0080934 | 0.008103 | 0.0081126 | 0.0081222 | 0.0081318 | 0.0081414 | 0.0081511 | 0.0081608 | 0.0081704 | 0.0081801 | 0.0081897 | 0.0081994 | 0.0082091 | 0.0082188 | 0.0082285 | 0.0082382 | 0.008248 | 0.0082577 | 0.0082675 | 0.0082772 | 0.0082869 | 0.0083415 | 0.0083961 | 0.0084507 | 0.0085053 | 0.0085599 | 0.0086154 | 0.0086708 | 0.0087263 | 0.0087817 | 0.0088372 | 0.0088935 | 0.0089498 | 0.0090061 | 0.0090625 | 0.0091188 | 0.0092639 | 0.0094091 | 0.0095543 | 0.0096994 | 0.0098446 | 0.0099353 | 0.010026 | 0.010117 | 0.010208 | 0.010298 | 0.010392 | 0.010485 | 0.010578 | 0.010672 | 0.010765 | Pole | Class 2 | 0.0016622 | 0.0016786 | 0.0016951 | 0.0017018 | 0.0017084 | 0.0017151 | 0.0017217 | 0.0017284 | 0.0017351 | 0.0017418 | 0.0017486 | 0.0017553 | 0.001762 | 0.0017688 | 0.0017756 | 0.0017824 | 0.0017892 | 0.001796 | 0.0018028 | 0.0018097 | 0.0018165 | 0.0018234 | 0.0018303 | 0.0018394 | 0.0018486 | 0.0018577 | 0.0018669 | 0.001876 | 0.0018782 | 0.0018805 | 0.0018827 | 0.0018849 | 0.0018871 | 0.0018894 | 0.0018916 | 0.0018939 | 0.0018961 | 0.0018983 | 0.0019006 | 0.0019028 | 0.0019051 | 0.0019073 | 0.0019096 | 0.0019118 | 0.0019141 | 0.0019164 | 0.0019186 | 0.0019209 | 0.0019335 | 0.0019462 | 0.0019588 | 0.0019715 | 0.0019841 | 0.001997 | 0.0020099 | 0.0020227 | 0.0020356 | 0.0020484 | 0.0020615 | 0.0020745 | 0.0020876 | 0.0021006 | 0.0021137 | 0.0021473 | 0.002181 | 0.0022146 | 0.0022483 | 0.0022819 | 0.002303 | 0.002324 | 0.002345 | 0.0023661 | 0.0023871 | 0.0024087 | 0.0024304 | 0.002452 | 0.0024737 | 0.0024953 | Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 0.16622 | 0.16786 | 0.16951 | 0.17018 | 0.17084 | 0.17151 | 0.17217 | 0.17284 | 0.17351 | 0.17418 | 0.17486 | 0.17553 | 0.1762 | 0.17688 | 0.17756 | 0.17824 | 0.17892 | 0.1796 | 0.18028 | 0.18097 | 0.18165 | 0.18234 | 0.18303 | 0.18394 | 0.18486 | 0.18577 | 0.18669 | 0.1876 | 0.18782 | 0.18805 | 0.18827 | 0.18849 | 0.18871 | 0.18894 | 0.18916 | 0.18939 | 0.18961 | 0.18983 | 0.19006 | 0.19028 | 0.19051 | 0.19073 | 0.19096 | 0.19118 | 0.19141 | 0.19164 | 0.19186 | 0.19209 | 0.19335 | 0.19462 | 0.19588 | 0.19715 | 0.19841 | 0.1997 | 0.20099 | 0.20227 | 0.20356 | 0.20484 | 0.20615 | 0.20745 | 0.20876 | 0.21006 | 0.21137 | 0.21473 | 0.2181 | 0.22146 | 0.22483 | 0.22819 | 0.2303 | 0.2324 | 0.2345 | 0.23661 | 0.23871 | 0.24087 | 0.24304 | 0.2452 | 0.24737 | 0.24953 | Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Climate data given in 5-year increments in linearly interpolated to provide annual probability of failures at the asset sub-class level. These failure probabilities are calibrated using the calibration multiplier derived on the Calibration tab and then scaled to the asset counts by sub-class for the existing, standard, and replacement cases. These are used to scale VOLL benefits calibrated to annual expected outage counts.

## Int BCA Ann Fail Costs
Asset Class Annual Failure Repair and Replace Cost
Asset Class | Asset Sub-Class | Unit Basis | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100
Pole | Class 5 | pole | 2240.2922 | 2245.098 | 2250 | 2255 | 2260.1 | 2265.302 | 2270.608 | 2276.0202 | 2281.5406 | 2287.1714 | 2292.9148 | 2298.7731 | 2304.7486 | 2310.8436 | 2317.0604 | 2323.4017 | 2329.8697 | 2336.4671 | 2343.1964 | 2350.0604 | 2357.0616 | 2364.2028 | 2371.4868 | 2378.9166 | 2386.4949 | 2394.2248 | 2402.1093 | 2410.1515 | 2418.3545 | 2426.7216 | 2435.2561 | 2443.9612 | 2452.8404 | 2461.8972 | 2471.1351 | 2480.5579 | 2490.169 | 2499.9724 | 2509.9718 | 2520.1713 | 2530.5747 | 2541.1862 | 2552.0099 | 2563.0501 | 2574.3111 | 2585.7973 | 2597.5133 | 2609.4636 | 2621.6528 | 2634.0859 | 2646.7676 | 2659.7029 | 2672.897 | 2686.3549 | 2700.082 | 2714.0837 | 2728.3654 | 2742.9327 | 2757.7913 | 2772.9471 | 2788.4061 | 2804.1742 | 2820.2577 | 2836.6629 | 2853.3961 | 2870.464 | 2887.8733 | 2905.6308 | 2923.7434 | 2942.2183 | 2961.0626 | 2980.2839 | 2999.8896 | 3019.8873 | 3040.2851 | 3061.0908 | 3082.3126 | 3103.9589
Pole | Class 4 | pole | 2440.2922 | 2445.098 | 2450 | 2455 | 2460.1 | 2465.302 | 2470.608 | 2476.0202 | 2481.5406 | 2487.1714 | 2492.9148 | 2498.7731 | 2504.7486 | 2510.8436 | 2517.0604 | 2523.4017 | 2529.8697 | 2536.4671 | 2543.1964 | 2550.0604 | 2557.0616 | 2564.2028 | 2571.4868 | 2578.9166 | 2586.4949 | 2594.2248 | 2602.1093 | 2610.1515 | 2618.3545 | 2626.7216 | 2635.2561 | 2643.9612 | 2652.8404 | 2661.8972 | 2671.1351 | 2680.5579 | 2690.169 | 2699.9724 | 2709.9718 | 2720.1713 | 2730.5747 | 2741.1862 | 2752.0099 | 2763.0501 | 2774.3111 | 2785.7973 | 2797.5133 | 2809.4636 | 2821.6528 | 2834.0859 | 2846.7676 | 2859.7029 | 2872.897 | 2886.3549 | 2900.082 | 2914.0837 | 2928.3654 | 2942.9327 | 2957.7913 | 2972.9471 | 2988.4061 | 3004.1742 | 3020.2577 | 3036.6629 | 3053.3961 | 3070.464 | 3087.8733 | 3105.6308 | 3123.7434 | 3142.2183 | 3161.0626 | 3180.2839 | 3199.8896 | 3219.8873 | 3240.2851 | 3261.0908 | 3282.3126 | 3303.9589
Pole | Class 3 | pole | 2660.2922 | 2665.098 | 2670 | 2675 | 2680.1 | 2685.302 | 2690.608 | 2696.0202 | 2701.5406 | 2707.1714 | 2712.9148 | 2718.7731 | 2724.7486 | 2730.8436 | 2737.0604 | 2743.4017 | 2749.8697 | 2756.4671 | 2763.1964 | 2770.0604 | 2777.0616 | 2784.2028 | 2791.4868 | 2798.9166 | 2806.4949 | 2814.2248 | 2822.1093 | 2830.1515 | 2838.3545 | 2846.7216 | 2855.2561 | 2863.9612 | 2872.8404 | 2881.8972 | 2891.1351 | 2900.5579 | 2910.169 | 2919.9724 | 2929.9718 | 2940.1713 | 2950.5747 | 2961.1862 | 2972.0099 | 2983.0501 | 2994.3111 | 3005.7973 | 3017.5133 | 3029.4636 | 3041.6528 | 3054.0859 | 3066.7676 | 3079.7029 | 3092.897 | 3106.3549 | 3120.082 | 3134.0837 | 3148.3654 | 3162.9327 | 3177.7913 | 3192.9471 | 3208.4061 | 3224.1742 | 3240.2577 | 3256.6629 | 3273.3961 | 3290.464 | 3307.8733 | 3325.6308 | 3343.7434 | 3362.2183 | 3381.0626 | 3400.2839 | 3419.8896 | 3439.8873 | 3460.2851 | 3481.0908 | 3502.3126 | 3523.9589
Pole | Class 2 | pole | 2902.2922 | 2907.098 | 2912 | 2917 | 2922.1 | 2927.302 | 2932.608 | 2938.0202 | 2943.5406 | 2949.1714 | 2954.9148 | 2960.7731 | 2966.7486 | 2972.8436 | 2979.0604 | 2985.4017 | 2991.8697 | 2998.4671 | 3005.1964 | 3012.0604 | 3019.0616 | 3026.2028 | 3033.4868 | 3040.9166 | 3048.4949 | 3056.2248 | 3064.1093 | 3072.1515 | 3080.3545 | 3088.7216 | 3097.2561 | 3105.9612 | 3114.8404 | 3123.8972 | 3133.1351 | 3142.5579 | 3152.169 | 3161.9724 | 3171.9718 | 3182.1713 | 3192.5747 | 3203.1862 | 3214.0099 | 3225.0501 | 3236.3111 | 3247.7973 | 3259.5133 | 3271.4636 | 3283.6528 | 3296.0859 | 3308.7676 | 3321.7029 | 3334.897 | 3348.3549 | 3362.082 | 3376.0837 | 3390.3654 | 3404.9327 | 3419.7913 | 3434.9471 | 3450.4061 | 3466.1742 | 3482.2577 | 3498.6629 | 3515.3961 | 3532.464 | 3549.8733 | 3567.6308 | 3585.7434 | 3604.2183 | 3623.0626 | 3642.2839 | 3661.8896 | 3681.8873 | 3702.2851 | 3723.0908 | 3744.3126 | 3765.9589
Expected annual avoided asset damages cost are the weighted repair and replacement costs from tab '6. Generic BCA Inputs'. This tab calculates the per unit weighted value for a single failure.

## Int BCA Ann PWFC
Asset Class Annual Probability Weighted Failure Repair and Replace Cost | [78 empty] | Baseline Asset Class Annual Probability Weighted Failure Repair and Replace Cost | [78 empty] | Replacement Asset Class Annual Probability Weighted Failure Repair and Replace Cost
Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101
Pole | Class 5 | 3944.9057 | 266.7102 | 267.4337 | 268.1698 | 268.9188 | 269.6809 | 270.4565 | 271.2457 | 272.0489 | 272.8663 | 273.6983 | 274.5451 | 275.4071 | 276.2845 | 277.1777 | 278.087 | 279.0126 | 279.9551 | 280.9146 | 281.8916 | 282.8864 | 283.9468 | 285.0261 | 286.1246 | 287.2428 | 288.3809 | 289.4108 | 290.4605 | 291.5307 | 292.6216 | 293.7337 | 294.8675 | 296.0233 | 297.2016 | 298.4029 | 299.6276 | 300.8762 | 302.1491 | 303.447 | 304.7702 | 306.1193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 4 | 3506.564 | 233.497 | 234.4725 | 235.4597 | 236.459 | 237.4706 | 238.4954 | 239.5331 | 240.584 | 241.6482 | 242.7261 | 243.8187 | 244.9257 | 246.0472 | 247.1836 | 248.3353 | 249.5033 | 250.6873 | 251.8874 | 253.1043 | 254.338 | 255.6721 | 257.0244 | 258.3952 | 259.7851 | 261.1945 | 262.0628 | 262.9478 | 263.8499 | 264.7693 | 265.7065 | 266.6619 | 267.6357 | 268.6284 | 269.6403 | 270.6718 | 271.7233 | 272.7952 | 273.888 | 275.0021 | 276.1378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 3 | 786.5302 | 51.6994 | 51.9555 | 52.2142 | 52.4756 | 52.7396 | 53.0074 | 53.278 | 53.5515 | 53.8279 | 54.1074 | 54.4174 | 54.7307 | 55.0474 | 55.3674 | 55.691 | 56.0446 | 56.402 | 56.7633 | 57.1285 | 57.4978 | 57.9498 | 58.4065 | 58.868 | 59.3343 | 59.8057 | 60.0569 | 60.3119 | 60.5711 | 60.8342 | 61.1016 | 61.3735 | 61.6498 | 61.9306 | 62.2158 | 62.5058 | 62.8007 | 63.1005 | 63.4053 | 63.715 | 64.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 177750.0799 | 11683.6955 | 11741.5734 | 11800.035 | 11859.0933 | 11918.7618 | 11979.2775 | 12040.4319 | 12102.2391 | 12164.7139 | 12227.871 | 12297.9336 | 12368.7377 | 12440.3001 | 12512.638 | 12585.7688 | 12665.6758 | 12746.4417 | 12828.0861 | 12910.629 | 12994.091 | 13096.2372 | 13199.441 | 13303.7272 | 13409.1211 | 13515.6487 | 13572.4109 | 13630.0602 | 13688.6156 | 13748.096 | 13808.5212 | 13869.9735 | 13932.4113 | 13995.8555 | 14060.3274 | 14125.8487 | 14192.5051 | 14260.2562 | 14329.1252 | 14399.1359 | 14470.3122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 2 | 327.0191 | 21.4156 | 21.537 | 21.6593 | 21.7828 | 21.9074 | 22.0339 | 22.1616 | 22.2905 | 22.4205 | 22.5518 | 22.6853 | 22.82 | 22.9561 | 23.0935 | 23.2323 | 23.3733 | 23.5159 | 23.6599 | 23.8054 | 23.9525 | 24.1312 | 24.3116 | 24.4939 | 24.678 | 24.864 | 24.96 | 25.0575 | 25.1566 | 25.2571 | 25.3593 | 25.4632 | 25.5688 | 25.676 | 25.785 | 25.8957 | 26.0084 | 26.1229 | 26.2393 | 26.3575 | 26.4778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 73903.9374 | 4839.7735 | 4867.195 | 4894.8532 | 4922.7535 | 4950.9016 | 4979.4998 | 5008.358 | 5037.4819 | 5066.8778 | 5096.5517 | 5126.7083 | 5157.1567 | 5187.9034 | 5218.9554 | 5250.3196 | 5282.2028 | 5314.4136 | 5346.9593 | 5379.8476 | 5413.0863 | 5453.4667 | 5494.2475 | 5535.438 | 5577.0478 | 5619.0866 | 5640.7858 | 5662.8214 | 5685.2005 | 5707.9304 | 5731.0185 | 5754.5011 | 5778.3572 | 5802.5949 | 5827.2221 | 5852.247 | 5877.7073 | 5903.5824 | 5929.8811 | 5956.6124 | 5983.7853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Caclulates the probability weighted annual expected failure costs for repair/replacement of assets from climate peril projections. Scales to baseline scenario assets (existing for pre-RUL and standard for post-RUL) and replacement scenario asset counts by sub-class from tab '7. Project Characteristics'. Avoided repair and replace benefits are adjusted to represent avoided PV revenue requirement to align with BCA costs and the DST perspective.

## Int BCA Ann PWVOLL
Baseline Scenario Asset Class Annual Probability Weighted VOLL (Per Event Method) - with Dual | [78 empty] | Replacement Scenario Asset Class Annual Probability Weighted VOLL (Per Event Method) | [78 empty] | Replacement Scenario Asset Class Annual Probability Weighted VOLL Criticality Reduction (Per Event Method)
Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101
Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 3 | 119146.0883 | 8046.3079 | 8070.7798 | 8095.2518 | 8119.7237 | 8144.1957 | 8168.82 | 8193.4444 | 8218.0687 | 8242.6931 | 8267.3174 | 8296.1295 | 8324.9416 | 8353.7536 | 8382.5657 | 8411.3778 | 8444.1669 | 8476.9561 | 8509.7453 | 8542.5344 | 8575.3236 | 8619.7918 | 8664.2601 | 8708.7283 | 8753.1966 | 8797.6648 | 8809.0801 | 8820.4954 | 8831.9107 | 8843.3259 | 8854.7412 | 8866.1964 | 8877.6515 | 8889.1067 | 8900.5619 | 8912.017 | 8923.512 | 8935.007 | 8946.502 | 8957.9971 | 8969.4921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 45526.8464 | 3056.531 | 3068.4841 | 3080.4371 | 3092.3901 | 3104.3431 | 3116.4194 | 3128.4956 | 3140.5718 | 3152.6481 | 3164.7243 | 3176.9234 | 3189.1226 | 3201.3217 | 3213.5208 | 3225.7199 | 3238.0415 | 3250.3631 | 3262.6847 | 3275.0063 | 3287.328 | 3303.759 | 3320.1901 | 3336.6211 | 3353.0522 | 3369.4832 | 3373.4875 | 3377.4917 | 3381.496 | 3385.5002 | 3389.5045 | 3393.5257 | 3397.5469 | 3401.5681 | 3405.5893 | 3409.6105 | 3413.6487 | 3417.6869 | 3421.7251 | 3425.7633 | 3429.8016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 11325.3132 | 760.3463 | 763.3198 | 766.2932 | 769.2667 | 772.2401 | 775.2442 | 778.2483 | 781.2524 | 784.2565 | 787.2606 | 790.2953 | 793.33 | 796.3646 | 799.3993 | 802.434 | 805.4991 | 808.5642 | 811.6294 | 814.6945 | 817.7597 | 821.8471 | 825.9345 | 830.0219 | 834.1093 | 838.1967 | 839.1928 | 840.1889 | 841.185 | 842.1811 | 843.1772 | 844.1775 | 845.1779 | 846.1782 | 847.1785 | 848.1788 | 849.1834 | 850.1879 | 851.1925 | 852.197 | 853.2016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Calculates the expected value of last load (VOLL) to customers from resulting modeled and calibrated frequency of outages in the baseline and replacement scenarios. Annual outage event projections are taken from 'Int BCA Ann Fail Prob' for each scenario and includes dual baseline for the baseline scenario. The replacement scenario VOLL is calculated from remaining outage projections after hardening investments. The criticality VOLL is calculated from the remaining replacement scenario frequency and the updated per outage VOLL from '7. Project Characteristics'.

## Int BCA Ann CMI
Baseline Scenario Asset Class Annual CMI (Per Event Method) | [78 empty] | Scenario Asset Class Annual Probability Weighted CMI (Per Event Method)
Asset Class | Asset Sub-Class | Lifetime Total CMI Reduction | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | Asset Class | Asset Sub-Class | Lifetime Total CMI Reduction | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101
Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 3 | 242746.7886 | 5698.4041 | 5715.7352 | 5733.0662 | 5750.3973 | 5767.7284 | 5785.1674 | 5802.6063 | 5820.0453 | 5837.4843 | 5854.9233 | 5875.328 | 5895.7328 | 5916.1375 | 5936.5423 | 5956.947 | 5980.1683 | 6003.3897 | 6026.611 | 6049.8323 | 6073.0536 | 6104.5461 | 6136.0385 | 6167.531 | 6199.0235 | 6230.5159 | 6238.6002 | 6246.6846 | 6254.7689 | 6262.8532 | 6270.9375 | 6279.0501 | 6287.1626 | 6295.2752 | 6303.3877 | 6311.5003 | 6319.6411 | 6327.7818 | 6335.9226 | 6344.0634 | 6352.2042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 65708.4326 | 1531.584 | 1537.5734 | 1543.5629 | 1549.5524 | 1555.5419 | 1561.5931 | 1567.6444 | 1573.6956 | 1579.7468 | 1585.7981 | 1591.9109 | 1598.0237 | 1604.1365 | 1610.2493 | 1616.3621 | 1622.5363 | 1628.7104 | 1634.8846 | 1641.0588 | 1647.233 | 1655.4664 | 1663.6997 | 1671.9331 | 1680.1665 | 1688.3998 | 1690.4063 | 1692.4128 | 1694.4192 | 1696.4257 | 1698.4322 | 1700.4472 | 1702.4621 | 1704.4771 | 1706.4921 | 1708.507 | 1710.5305 | 1712.554 | 1714.5775 | 1716.601 | 1718.6245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Calculates the expected annual CMI from outages caused by climate perils modeled in the VASH Toolkit for the baseline and replacement scenarios. Modeled outage frequency from 'Int BCA Ann Fail Prob' are scaled to the number of customers and duration from '7. Project Characteristics'.