## Cover
OEB Vulnerability Assessment & System Hardening
VASH Toolkit Model
2025-07-29
Private and confidential
DISCLAIMER
This tool (“Report”) was prepared by Guidehouse Canada Ltd. (“Guidehouse”) pursuant to a contract with the Ontario Energy Board (OEB). Accordingly, Guidehouse disclaims any contractual or other responsibility to others based on their access to or use of the Report. The Report was prepared on the basis of information and assumptions set forth in associated appendices, underlying work papers, and other limiting conditions and assumptions. The work presented in this Report represents Guidehouse’s reasonable professional judgments based on the information available at the time and/or provided to Guidehouse. Guidehouse is not responsible for, and expressly disclaims, the reader’s use of, or reliance upon, the Report, nor any decisions based on the Report. Notice pertaining to certain underlying inputs for climate projection data (provided on a one time basis): With the permission of Canadian Standards Association, (operating as “CSA Group”), 178 Rexdale Blvd., Toronto, ON, M9W 1R3, material is reproduced from CSA Group standard CSA C22.3 No. 1:25, Overhead systems. This material is not the complete and official position of CSA Group on the referenced subjects, which is represented solely by the Standard in its entirety. While use of the material has been authorized, CSA Group is not responsible for the manner in which the data is presented, nor for any representations and interpretations. No further reproduction is permitted. For more information or to purchase standard(s) from CSA Group, please visit store.csagroup.org or call 1-800-463-6727.
CONTACTS
Donald Lau | Zubin Panchal
Manager, Electricity Distribution | Senior Advisor, Electricity Distribution
Donald.Lau@oeb.ca | Zubin.Panchal@oeb.ca

## Table of Contents
DRAFT
Ontario Energy Board Vulnerability Assessment & System Hardening (VASH) Toolkit - Table of Contents
Disclaimer
Contents
This file contains the following pages:
|  | Color | Tab Name | Description/Purpose
|  |  | Table of Contents | Contains a model overview and tab descriptions.
|  | Tab Link | VA Toolkit User Guide | The User Guide outlines the step-by-step methodology to employ the VA Toolkit model to analyze asset class and location vulnerability to climate perils. The example of reviewing the vulnerability of Class 3 poles in County 1 to high wind probabilities is provided as an illustrative example.
|  | Tab Link | Model Logic Diagrams | Provides high level and detailed logic and variable flow diagrams for the VA and BCA Toolkits.
|  | Tab Link | 1. LDC Asset Summary | Summarizes asset counts by analysis location. Locations with no assets of a specific class will have no vulnerability for that class regardless of climate projections. For locations and class combinations with higher vulnerability, an LDC may review its asset counts to understand the pervasiveness of the resiliency challenge.
|  | Tab Link | 2. Asset Class Failure Thresh | Characterizes the expected resilience of LDC assets identified in the Asset Summary to specific climate perils. Sub classes may be included to better estimate failure thresholds across a variety of perils. The total annual probability of failure is the summation of expected threshold exceedances across climate perils relevant to a particular asset class. LDCs may leverage design standards to quickly review vulnerability or refine failure thresholds with additional condition data of field equipment.
|  | Tab Link | 3. Climate Severity Calculator | Supports the development of tab '4. Climate Peril Probability'. Users may input chosen climate projections (from ECCC) to estimate annual probabilities of failure at different times in the future.
|  | Tab Link | 4. Climate Peril Probability | Projects the annual probability of specific events (relevant to assets in the Asset Summary) occurring at targeted grid locations through time. Climate perils and severity thresholds are linked to specific asset failure modes and thresholds. For example, wind gusts may be evaluated at 80, 100, and 120 kph as these relate to different class pole failures.
|  | Tab Link | 5. VA Heatmap | Categorizes vulnerability for each asset class in 5-year time intervals at a specified location by user-defined vulnerability bins. The annual probability of failures are summed across applicable climate perils based on asset class failure thresholds.
|  | Tab Link | 6. Generic BCA Inputs | User inputs that describe the unit costs related to asset failure (i.e., repair and replace costs). These costs should be those that scale with asset count. Project level costs such as administration should be entered in tab '7. Project Characteristics'.
|  | Tab Link | 7. Project Characteristics | User inputs that describe the characteristics of a single project associated with a single location. Users should use this tab to assess the benefits and costs of individual projects. See tab 'BCA Toolkit User Guide' for example project types.
|  | Tab Link | 8. Project BCA Results | Presents results of project BCA calculations based on inputs provided in tabs 1-7.
The following tabs contain intermediate calculations for the workbook to function and should not be edited.
|  | Color | Tab Name | Description/Purpose
|  |  | Calibration | Calculates calibration factor to ground modeled failures against actual observed failures. Calibration accounts for covariance of probability of failure associated with assets (e.g. similar assets in relatively close proximity)
Raw Climate Data
Int VA Calcs
Int BCA Costs
Int BCA Ann Fail Prob
Int BCA Ann Fail Costs
Int BCA Ann PWFC
Int BCA Ann PWVOLL
Indices
Key
User Input
Input from List (Dropdown)
Fixed Input
Calculated Value
Calculated Value
Linked Value
Model Result
The Vulnerability Assessment (VA) and Benefit-Cost Analysis (BCA) Toolkits—together forming the VASH Toolkit—are designed to support Local Distribution Companies (LDCs) in developing asset class- and location-specific climate vulnerability profiles. These vulnerabilities are expressed as the annual probability that a climate event will exceed an asset’s expected failure threshold. The toolkit streamlines the identification of vulnerable assets and locations and supports the evaluation of cost-effective mitigation measures that reduce resiliency risks while prioritizing customer value.
The toolkit illustrates a generic assessment methodology option compliant with OEB expectations for evaluation of resiliency risk, resulting in a heatmap that supports narrowing assets for further review and a summary of project benefit-cost results. Alternatively, LDCs can file a customized VA and BCA as part of their DSP, but it must adhere to principles outlined by the OEB. For this option, while the OEB does not prescribe a data source and LDCs may leverage data commensurate with their planning granularity and needs, the OEB does identify minimum criteria in Section 4.1 of the VASH Report.
The VA Toolkit (tabs 1-5) applies a climate projection to assess vulnerabilities using an asset-based approach by combining climate data, design standards, and asset location summaries. Inputs may be developed by LDCs using a variety of sources including the LDCs internal data, CSA guidelines, publicly available climate data, and proprietary climate data. The output provides a vulnerability heatmap that identifies areas for further investigation and investment prioritization.
The BCA Toolkit (tabs 6-8) is designed to support the evaluation of targeted system hardening projects at specific grid locations evaluated in the VA. The BCA Toolkit provides a generic framework for calculating the lifetime present value of benefits and costs of a project, a benefit-cost ratio (BCR), and the expected annual and lifetime reduction in customer minutes of interruption (CMI). Inputs are based on the utility's existing asset base, proposed replacement assets, projected costs, and criticality values derived from the DOE ICE calculator.
While this toolkit is a fully functioning model that may be used by LDCs, the onus remains on the LDCs to ensure accuracy of the data and results. It is also important to clarify that the use of the VASH Toolkit does not imply OEB endorsement of any specific investment decisions that may be supported by the toolkit’s outputs. The toolkit is intended to assist with planning and justification; however, any proposed investments remain subject to review and approval through the OEB’s adjudicative process, such as during a cost of service proceeding. This example combines hypothetical pole replacement and sectionalization measures to reduce both the number and duration of outages. It is provided to demonstrate the Toolkit’s capability to evaluate multi-component projects and and does not imply regulatory support for the investment.
The Report does not constitute a recommendation on investment decisions nor does it provide investment advice. Guidehouse has not been requested to opine as to, and does not guarantee, warrant or opine upon: (i) any underlying business decision by a user to proceed (or not to proceed) with an investment ; or (ii) whether a proposed investment will be approved by the OEB. Any conclusion expressed in the Report should not amount to any form of guarantee that Guidehouse has determined or predicted future events or circumstances, and no such reliance may be inferred or implied.
Users should populate cells marked as 'User Input' based on the scheme shown below. All other cells are calculated by the model or given as fixed values.

## VA Toolkit User Guide
DRAFT - Example Data Illustrative
Ontario Energy Board Vulnerability Assessment Toolkit - User Guide
4. Climate Peril Probability
2. Asset Class Failure
Thresholds
5. Vulnerability Assessment Heatmap
The User Guide outlines the step-by-step methodology to employ the Vulnerability Assessment Toolkit model to analyze asset class and location vulnerability to climate perils. The example of reviewing the vulnerability of Class 3 poles in County 1 to high wind probabilities is provided as an illustrative example.
1. LDC Asset Summary
Step 1: Users should populate the Asset Summary with their installed asset base by location. Asset sub classes may be utilized to add granularity to failure thresholds. Additionally the counts of each asset class or sub class should be included as available. If actual counts are not available, populating with a "1" will ensure correct model calculations. Locations and classes for inclusion are based on user discretion. Generally, locations should be chosen based on likelihood of varying climate conditions and asset classes and sub classes based on variations in the expected weather event resilience of those technologies.
Example: The LDC populates the summary of their poles in Location 1 by Class. Based on the counts, the LDC is interested in the vulnerability of their most populous sub class, Class 3 poles, as it may represent greater risk.
Step 2: Users set up the Asset Class Failure Modes & Thresholds table to include the asset classes and sub classes identified in the Asset Summary process. Leveraging CSA guidelines, OEM design standards, or other engineering resources, asset classes and sub classes are assigned to climate perils, and severity thresholds that pose a threat to the equipment are determined. The unit basis of the climate peril identified should be included and referenced in the development of climate peril probabilities. The OEB notes that utilities may choose to rely upon the CSA Group’s published guidelines for technical standards as an input to the expected failure modes for assets.
Example: The LDC populates the provided table with the asset class and sub classes from Step 1. Wind (1 min gusts measured in kph) is determined to be the primary climate peril applicable to utility poles. Severity thresholds for wind are researched based on manufacturer specifications and populate the remainder of the table. The 150 Class 3 poles in Location 1 are designed to withstand 80 kph gusts.
Step 4: Users set up the Climate Peril Probability Model with the climate perils and severity thresholds identified in Step 2 as relevant to the asset summary at locations identified in Step 1. Leveraging Environment Canada data, CSA working documents, proprietary climate data, or other sources, the annual probability of occurrence is developed for a specific climate peril, severity threshold, location, and time period. Data for climate projections is highly variable, therefore, forecast time periods are discretionary and may be adjusted to match best available data. '3. Climate Severity Calculator' is provided to facilitate populating '4. Climate Peril Probability'. The OEB expects distributors to employ projection data rather than historical actuals to populate the climate peril probability inputs in VAs.
Example: The LDC populates the provided table with the climate perils and thresholds from Step 2 for each location from Step 1. The annual frequency of wind gusts in Location 1 at different thresholds is researched and populated in 5-year increments based on available data. As we know from Step 2, the 150 Class 3 poles in Location 1 are designed to withstand 80 kph gusts; which has a 0.8% annual probability of occurrence in 2025 but increases to a 1.6% annual probability of occurrence by 2050.
Step 5: The Vulnerability Assessment Heatmap will automatically populate after Step 3 is complete. Users may toggle the Location field to view each specified location in Step 1 individually to reveal differences in vulnerability based on the Asset Summary and Climate Peril Probability model. Additionally, users may designate cutoff points for vulnerability categories ranging from Low to High (annual probabilities above the "High" field with be labeled "Very High"). The Annual Probability Bins represent the low end of a probability range considered to be in the category. The resulting heatmap may be used to identify areas of system vulnerability for further research and/or prioritize asset classes and locations for investment review.
Example: The LDC sets the Location field to Location 1 and the Annual Probability Bins at 1%, 5%, and 10% (representing the risk of a 1/100-, 1/20-, and 1/10-year event respectively). The resulting analysis of Class 3 poles in Location 1 shows Low vulnerability (less than 1% per year in this example) until 2035 when the vulnerability becomes Medium (between 1% and 5% per year in this example). The LDC may choose to focus research effort and investment on hardening other locations or asset classes with greater risk and revisit Class 3 poles in Location 1 when developing a future DSP.
3. Climate Severity Calculator
Step 3: Users may leverage climate projections obtained from ECCC to estimate the annual probability of failures that their assets are exposed to. Using the Scenario Selection cells, each climate peril, severity threshold, and location to be populated in the following step (4. Climate Peril Probability) should be evaluated for its exceedance probability in 5-year increments. The results from the Annual Event Probability Projection cells may be copied as values directly into the following step ('4. Climate Peril Probability') to support input development. To maintain consistency with CSA/ECCC standards, the OEB recommends the use of RCP 8.5 for asset classes with expected useful lives less than 60 years and RCP 6.0 for expected useful lives greater than 60 years. However, the ultimate choice of scenario is at the discretion of the distributor, and so is the use of this calculator (i.e., LDCs do not have to leverage the Climate Severity Calculator if they can populate the Annual Event Probabilities for their assets of interest directly into the following step).
Example: The LDC The LDC populates the desired location, climate scenario, climate peril, and severity threshold. For the annual event probability projection to be developed. In this instance, under climate scenario RCP8.5 in Thedford, Wind being selected as a climate peril with a threshold of 100 kph (10-min avg.), the annual event probabilities range from 0.0190 to 0.0212 between 2023 and 2040

## VA Definitions
DRAFT
Ontario Energy Board Vulnerability Assessment Toolkit - Definitions
| Term | Definition
| Location | A point or an area associated with 1 or more assets. Locations are used to map asset classes to the specific probability of climate perils occurring. Definitions of locations are up to the discretion of the user, and can be chosen to be as granular or as coarse as needed to capture geographic variation in likelihood of climate conditions.
| Asset Class | A type of asset, such as a pole or overhead conductor. Asset classes should be chosen to accurately differentiate between the weather event resilience of different assets.
| Sub Class | A sub category of asset within an asset class. Sub classes may be used to further differentiate failure thresholds of different assets within a class; for example, to differentiate the resilience of different classes of pole to wind gusts.
| Vulnerability | Vulnerability represents the probability that an asset (or group of assets) will fail given it is within the location of occurrence of one or more climate perils.
| Risk | Risk quantifies the financial exposure of an asset or group of assets at a location, accounting for probability of failure in response to climate perils as well as criticality of failure (e.g., value of lost load).
| Severity Threshold | Estimated point over which a given asset class would be expected to fail in response to a particular climate peril .
| Estimated Useful Life (EUL) | The expected period during which an asset can operate efficiently, safely, and economically before it typically needs to be retired or replaced. Also referred to as "lifetime" in the VASH Report. Does not correspond to "End-of-Life", which refers to the lifetime of the asset at its failure.

## Model Logic Diagrams
DRAFT - Example Data Illustrative
Ontario Energy Board Vulnerability Assessment Toolkit - Model Logic Diagrams
Diagram 1: Vulnerability Assessment Toolkit Flow Diagram
Diagram 2: Benefit-Cost Analysis Toolkit Flow Diagram
Diagram 3: Avoided Repair and Replacement Benefit Calculation Flow Diagram
Diagram 4: Value of Lost Load Benefit Calculation Flow Diagram
Diagram 5: Project Cost Calculation Flow Diagram
This tab contains five (5) flow diagrams illustrating key model features and how variables interact to calculate project benefits and costs. Diagrams include: Vulnerability Assessment Toolkit flow, Benefit-Cost Analysis Toolkit flow, avoided repair and replacement benefit calculation, value of lost load benefit calculation, and project cost calculation.

## 1. LDC Asset Summary
DRAFT - Example Data Illustrative
| Table 1: Asset Class Summary |  |  | Table 2: Asset Class and Sub-Class Locations and Counts
| Asset Class | Unit Basis |  | Location | Asset Class | Sub Class | Count | Unit Basis
| Pole | pole | ThedfordPoleClass 5 | Thedford | Pole | Class 5 | 50 | pole
|  |  | ThedfordPoleClass 4 | Thedford | Pole | Class 4 | 100 | pole
|  |  | ThedfordPoleClass 3 | Thedford | Pole | Class 3 | 150 | pole
|  |  | ThedfordPoleClass 2 | Thedford | Pole | Class 2 | 30 | pole
Users should populate Table 1 with the unique list of asset classes and their unit basis to be included in the assessment. Table 2 should be populated with the installed asset base by location. Asset sub classes may be utilized to add granularity to failure thresholds. Additionally the counts of each asset class or sub class should be included as available. If actual counts are not available, populating with a "1" will ensure correct model calculations. Locations and classes for inclusion are based on user discretion. Generally, locations should be chosen based on likelihood of varying climate conditions and asset classes and sub classes based on variations in the expected weather event resilience of those technologies. A single unit basis should be defined for each Asset Class (Columns C and B). This list should also contain potential replacement assets associated with projects to be defined in Tabs 6 and 7; for example, to describe a program that involves undergrounding of overhead conductors, an asset class of "Underground Conductor" should be included (e.g., with a count of 0, if none exist yet).

## 2. Asset Class Failure Thresh
DRAFT - Example Data Illustrative
Asset Class Failure Modes & Thresholds
| Table 3: Climate Peril Summary |  | Table 4: Asset Class Failure Thresholds
| Climate Peril | Unit Basis | Asset Class | Sub Class | Climate Peril | Severity Threshold | Unit Basis
| Wind | kph (10-min avg.) | Pole | Class 5 | Wind | 80 | kph (10-min avg.)
| Ice | mm ice accretion | Pole | Class 4 | Wind | 85 | kph (10-min avg.)
|  |  | Pole | Class 3 | Wind | 100 | kph (10-min avg.)
|  |  | Pole | Class 2 | Wind | 110 | kph (10-min avg.)
Users populate Table 3 with the unique list of climate perils being assessed and the unit basis by which the severity of this peril will be considered. Table 4 should include the asset classes and sub classes identified in the Asset Summary tab and - leveraging CSA guidelines, OEM design standards, or other engineering resources - be assigned to climate perils, and severity thresholds that pose a threat to the equipment. The unit basis of the climate peril identified should be included and referenced in the development of climate peril probabilities. A single unit basis should be defined for each climate peril.

## 3. Climate Severity Calculator
DRAFT - Example Data Illustrative
Asset Sub-Class Probability of Failure Calculator Tool
Scenario Selection
|  | Location | Ailsa Craig
|  | Climate Scenario | RCP8.5
|  | Climate Peril | Wind
|  | Unit Basis | kph (10-min avg.)
|  | Severity Threshold | 85
Annual Event Probability Projection
|  | Climate Peril | Severity Threshold | Unit Basis | Location | 2023 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2055 | 2060 | 2065 | 2070 | 2075 | 2080 | 2085 | 2090 | 2095 | 2100
|  | Wind | 85 | kph (10-min avg.) | Ailsa Craig | 0.10145 | 0.10194 | 0.10243 | 0.10292 | 0.10308 | 0.10323 | 0.10395 | 0.10452 | 0.10592 | 0.10675 | 0.10831 | 0.10905 | 0.10978 | 0.11075 | 0.11173 | 0.11173 | 0.11173
Return Interval
|  | Location ID | Year | 10 | 20 | 2023: 50; 2025: 100; 2030: 200; 2035: Estimated Failure Threshold; 2040: Lower Wind Speed; 2045: Upper Wind Speed; 2050: Lower Return Period; 2055: Upper Return Period; 2060: Annual Probability of Failure
| Ailsa CraigWind2023RCP8.5 | Ailsa Craig | 2023 | 85.5352 | 92.2975 | 2023: 99.4602; 2025: 106.5797; 2030: 113.7086; 2035: 85; 2040: 0; 2045: 85.5352; 2050: 1; 2055: 10; 2060: 0.10145
| Ailsa CraigWind2025RCP8.5 | Ailsa Craig | 2025 | 85.7157 | 92.5344 | 2023: 99.7705; 2025: 106.9537; 2030: 114.148; 2035: 85; 2040: 0; 2045: 85.7157; 2050: 1; 2055: 10; 2060: 0.10194
| Ailsa CraigWind2030RCP8.5 | Ailsa Craig | 2030 | 85.8962 | 92.7714 | 2023: 100.0809; 2025: 107.3277; 2030: 114.5875; 2035: 85; 2040: 0; 2045: 85.8962; 2050: 1; 2055: 10; 2060: 0.10243
| Ailsa CraigWind2035RCP8.5 | Ailsa Craig | 2035 | 86.0768 | 93.0084 | 2023: 100.3912; 2025: 107.7017; 2030: 115.0269; 2035: 85; 2040: 0; 2045: 86.0768; 2050: 1; 2055: 10; 2060: 0.10292
| Ailsa CraigWind2040RCP8.5 | Ailsa Craig | 2040 | 86.1332 | 93.0782 | 2023: 100.4794; 2025: 107.8031; 2030: 115.1386; 2035: 85; 2040: 0; 2045: 86.1332; 2050: 1; 2055: 10; 2060: 0.10308
| Ailsa CraigWind2045RCP8.5 | Ailsa Craig | 2045 | 86.1896 | 93.1481 | 2023: 100.5676; 2025: 107.9044; 2030: 115.2504; 2035: 85; 2040: 0; 2045: 86.1896; 2050: 1; 2055: 10; 2060: 0.10323
| Ailsa CraigWind2050RCP8.5 | Ailsa Craig | 2050 | 86.4547 | 93.4975 | 2023: 101.0217; 2025: 108.4462; 2030: 115.8834; 2035: 85; 2040: 0; 2045: 86.4547; 2050: 1; 2055: 10; 2060: 0.10395
| Ailsa CraigWind2055RCP8.5 | Ailsa Craig | 2055 | 86.6635 | 93.777 | 2023: 101.3875; 2025: 108.8866; 2030: 116.4048; 2035: 85; 2040: 0; 2045: 86.6635; 2050: 1; 2055: 10; 2060: 0.10452
| Ailsa CraigWind2060RCP8.5 | Ailsa Craig | 2060 | 87.1768 | 94.421 | 2023: 102.1879; 2025: 109.8269; 2030: 117.4885; 2035: 85; 2040: 0; 2045: 87.1768; 2050: 1; 2055: 10; 2060: 0.10592
| Ailsa CraigWind2065RCP8.5 | Ailsa Craig | 2065 | 87.4815 | 94.7856 | 2023: 102.6223; 2025: 110.3267; 2030: 118.0508; 2035: 85; 2040: 0; 2045: 87.4815; 2050: 1; 2055: 10; 2060: 0.10675
| Ailsa CraigWind2070RCP8.5 | Ailsa Craig | 2070 | 88.0541 | 95.5026 | 2023: 103.5207; 2025: 111.3788; 2030: 119.2611; 2035: 85; 2040: 0; 2045: 88.0541; 2050: 1; 2055: 10; 2060: 0.10831
| Ailsa CraigWind2075RCP8.5 | Ailsa Craig | 2075 | 88.322 | 95.855 | 2023: 103.9845; 2025: 111.9311; 2030: 119.9091; 2035: 85; 2040: 0; 2045: 88.322; 2050: 1; 2055: 10; 2060: 0.10905
| Ailsa CraigWind2080RCP8.5 | Ailsa Craig | 2080 | 88.59 | 96.2074 | 2023: 104.4484; 2025: 112.4833; 2030: 120.5571; 2035: 85; 2040: 0; 2045: 88.59; 2050: 1; 2055: 10; 2060: 0.10978
| Ailsa CraigWind2085RCP8.5 | Ailsa Craig | 2085 | 88.9454 | 96.6585 | 2023: 105.0217; 2025: 113.1649; 2030: 121.3447; 2035: 85; 2040: 0; 2045: 88.9454; 2050: 1; 2055: 10; 2060: 0.11075
| Ailsa CraigWind2090RCP8.5 | Ailsa Craig | 2090 | 89.3008 | 97.1097 | 2023: 105.595; 2025: 113.8465; 2030: 122.1323; 2035: 85; 2040: 0; 2045: 89.3008; 2050: 1; 2055: 10; 2060: 0.11173
| Ailsa CraigWind2095RCP8.5 | Ailsa Craig | 2095 | 89.3008 | 97.1097 | 2023: 105.595; 2025: 113.8465; 2030: 122.1323; 2035: 85; 2040: 0; 2045: 89.3008; 2050: 1; 2055: 10; 2060: 0.11173
| Ailsa CraigWind2100RCP8.5 | Ailsa Craig | 2100 | 89.3008 | 97.1097 | 2023: 105.595; 2025: 113.8465; 2030: 122.1323; 2035: 85; 2040: 0; 2045: 89.3008; 2050: 1; 2055: 10; 2060: 0.11173
Source: Table I.4, CSA C22.3 No. 1:25, Overhead systems. © 2025 Canadian Standards Association. Please visit store.csagroup.org CSA and ECCC data analysis (OEB 2025)
|  |  |  | 0.005 | 0.01 | 2023: 0.02; 2025: 0.05; 2030: 0.1
|  |  | Wind | 114.148 | 106.9537 | 2023: 99.7705; 2025: 92.5344; 2030: 85.7157
|  |  | Estimated Failure Threshold | 85 | 85 | 2023: 85; 2025: 85; 2030: 85
Users may leverage climate projections obtained from ECCC to estimate the annual probability of failures that their assets are exposed to. Using the Scenario Selection cells below: each climate peril, severity threshold, and location to be populated in '4. Climate Peril Probability' should be evaluated for its exceedance probability in 5-year increments. The results from the Annual Event Probability Projection cells (G18:W18) may be copied as values directly into columns G:W in '4. Climate Peril Probability' to support input development.
To maintain consistency with CSA/ECCC standards, the OEB recommends the use of RCP 8.5 for asset classes with expected useful lives less than 60 years and RCP 6.0 for expected useful lives greater than 60 years. However, the ultimate choice of scenario is at the discretion of the distributor.

## 4. Climate Peril Probability
DRAFT - Example Data Illustrative
Climate Peril Probability Model
Table 5: Climate Peril Probability Projections
Annual Event Probability Forecast
|  | Climate Peril | Severity Threshold | Unit Basis | Location | 2023 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2055 | 2060 | 2065 | 2070 | 2075 | 2080 | 2085 | 2090 | 2095 | 2100
| ThedfordWind110 | Wind | 110 | kph (10-min avg.) | Thedford | 0.0071709 | 0.0074565 | 0.007748 | 0.0080455 | 0.0081254 | 0.0082059 | 0.0086518 | 0.0090244 | 0.0098446 | 0.010298 | 0.011293 | 0.011835 | 0.012389 | 0.013092 | 0.013814 | 0.013814 | 0.013814
| ThedfordWind100 | Wind | 100 | kph (10-min avg.) | Thedford | 0.018976 | 0.019562 | 0.020204 | 0.020995 | 0.021223 | 0.021452 | 0.02265 | 0.023636 | 0.02589 | 0.027176 | 0.029906 | 0.031338 | 0.032797 | 0.034672 | 0.036595 | 0.036595 | 0.036595
| ThedfordWind85 | Wind | 85 | kph (10-min avg.) | Thedford | 0.10145 | 0.10194 | 0.10243 | 0.10292 | 0.10308 | 0.10323 | 0.10395 | 0.10452 | 0.10592 | 0.10675 | 0.10831 | 0.10905 | 0.10978 | 0.11075 | 0.11173 | 0.11173 | 0.11173
| ThedfordWind80 | Wind | 80 | kph (10-min avg.) | Thedford | 0.11607 | 0.1166 | 0.11712 | 0.11765 | 0.11782 | 0.11798 | 0.11876 | 0.11937 | 0.12087 | 0.12176 | 0.12344 | 0.12423 | 0.12502 | 0.12606 | 0.1271 | 0.1271 | 0.1271
Users should populate Table 5 with the climate perils and severity thresholds identified in Tab 2 as relevant to the asset summary at locations identified in Tab 1. Leveraging Environment Canada data, CSA working documents, proprietary climate data, or other sources, the annual probability of occurrence is developed for a specific climate peril, severity threshold, location, and time period. Tab '3. Climate Severity Calculator' is available to support generic option input development using ECCC data. This table should include every unique combination of Climate Peril and severity threshold as defined in Tab 2, for each Location of interest.

## 5. VA Heatmap
DRAFT - Example Data Illustrative
Vulnerability Heatmap
[20 empty] | Annual Probability Bin Examples |  | List of Locations
[20 empty] | Bin | Definition | Thedford
[20 empty] | 0.01 | 1-in-100 year event
[20 empty] | 0.02 | 1-in-50 year event
[20 empty] | 0.05 | 1-in-20 year event
[20 empty] | 0.1 | 1-in-10 year event
[20 empty] | 0.2 | 1-in-5 year event
|  | Location |  | Thedford
|  |  |  | Low | Medium | High | Very High
|  | Annual Probability Bin |  | 0.02 | 0.1 | 0.2 | >0.2
Asset Vulnerability Heatmap
|  | Asset Class | Sub Class | 2025 | 2030 | 2035 | 2040 | 2045 | 2040 | 2055 | 2060 | 2065 | 2070 | 2075 | 2080 | 2085 | 2090 | 2095 | 2100 | Heat Map | Bin
| ThedfordPoleClass 5 | Pole | Class 5 | 0.1166 | 0.11712 | 0.11765 | 0.11782 | 0.11798 | 0.11876 | 0.11937 | 0.12087 | 0.12176 | 0.12344 | 0.12423 | 0.12502 | 0.12606 | 0.1271 | 0.1271 | 0.1271 |  | Low
| ThedfordPoleClass 4 | Pole | Class 4 | 0.10194 | 0.10243 | 0.10292 | 0.10308 | 0.10323 | 0.10395 | 0.10452 | 0.10592 | 0.10675 | 0.10831 | 0.10905 | 0.10978 | 0.11075 | 0.11173 | 0.11173 | 0.11173 |  | Medium
| ThedfordPoleClass 3 | Pole | Class 3 | 0.019562 | 0.020204 | 0.020995 | 0.021223 | 0.021452 | 0.02265 | 0.023636 | 0.02589 | 0.027176 | 0.029906 | 0.031338 | 0.032797 | 0.034672 | 0.036595 | 0.036595 | 0.036595 |  | High
| ThedfordPoleClass 2 | Pole | Class 2 | 0.0074565 | 0.007748 | 0.0080455 | 0.0081254 | 0.0082059 | 0.0086518 | 0.0090244 | 0.0098446 | 0.010298 | 0.011293 | 0.011835 | 0.012389 | 0.013092 | 0.013814 | 0.013814 | 0.013814 |  | Very High
N/A
The Vulnerability Assessment Heatmap will automatically populate after Tabs 1, 2 and 4 are complete. Users may toggle the Location field to view each user-specified location in Tab 1 individually to reveal differences in vulnerability based on the Asset Summary and Climate Peril Probability model. Additionally, users may designate cutoff points for vulnerability categories ranging from Low to High (annual probabilities above the "High" field with be labeled "Very High"). The Annual Probability Bins represent the low end of a probability range considered to be in the category. The resulting heatmap may be used to identify areas of system vulnerability for further research and/or prioritize asset classes and locations for investment review. Values populating the heatmap cells are the annual probability that a climate peril exceeds the specified asset class' failure thresholds at the specified location. A higher value implies increased vulnerabiltiy. Although applicants may adjust vulnerability bin thresholds to fit their needs, the OEB has suggested standard bins: Low < 2%, Medium < 10%, High < 20%, and Very High > 20%.

## 6. Generic BCA Inputs
DRAFT - Example Data Illustrative
Generic BCA Inputs
Table 5: Asset Repair and Replace Costs
|  | Asset Class | Asset Sub-Class | Unit Basis | Unit | Cost Data Year | Repair Cost | Replace Cost | Replace %
| PoleClass 5 | Pole | Class 5 | pole | $/unit | 2025 | 500 | 4000 | 50%
| PoleClass 4 | Pole | Class 4 | pole | $/unit | 2025 | 500 | 4400 | 50%
| PoleClass 3 | Pole | Class 3 | pole | $/unit | 2025 | 500 | 4840 | 50%
| PoleClass 2 | Pole | Class 2 | pole | $/unit | 2025 | 500 | 5324 | 50%
TBD BCA inputs used across projects
In Table 5 users should input the expected costs to repair and replace equipment for the asset classes and sub-classes populated from the VA. Repair and replace costs should represent all capital cost incurred by the utility when addressing asset failures (i.e., equipment cost, labor, etc.) but should only include costs that scale on a per asset basis. Other costs, such as project administration and OM&A, should be included in '7. Project Characteristics'. The repair and replace values may be used across evaluated projects and will derive project budgets and BCA costs.
Additionally, the expected replacement percent should be estimated based on the climate perils and failure thresholds incorporated into the VA. For example, if a specific replacement failure threshold (e.g., from CSA guidelines) was used to analyze vulnerability, this should be set to 100%. If a threshold based on historic asset class outages was used, an estimate of actual repair versus replace expectations may be appropriate. Note that all failures will cause a customer interruption in the model with the replace and repaire percentages aligning the capital costs of those failures to LDC experience.

## 7. Project Characteristics
DRAFT - Example Data Illustrative
Project Characteristics
Table 6: Project Characteristics
Project Type Inputs
|  |  |  | Location |  | Thedford
|  |  |  | Project Type |  | End-of-Life
|  |  |  | Impact Type |  | Both
Table 7: Project Economic Variables
|  |  |  | Variable | Unit | Value
|  |  |  | Inflation | % | 2%
|  |  |  | Nominal Utility Discount Rate (WACC) | % | 7%
|  |  |  | Social Discount Rate | % | 4%
|  |  |  | Baseline OM&A Cost (% of Total Costs) | % | 1.5%
|  |  |  | Scenario OM&A Cost (% of Total Costs) | % | 1.5%
|  |  |  | Tax Rate | % | 26.5%
|  |  |  | Incremental Project Non-Asset Costs | $ | 280000
Table 8: Project Lifetime Variables
|  |  |  | Variable | Unit | Value
|  |  |  | Project Start Year | year | 2026
|  |  |  | Project Expected Lifetime1 | years | 40
|  |  |  | Starting Asset's Remaining Useful Lifetime2 | years | 10
1EUL should not exceed 75
2RUL only required for the early retirement program type.
Table 9: Criticality Variables
|  |  |  | Variable | Unit | Baseline Value | Project Value
|  |  |  | Average Outage Duration | minutes | 120 | 120
|  |  |  | Estimated Customers Interrupted (Res) | count | 100 | 70
|  |  |  | Estimated Customers Interrupted (Small C&I) | count | 5 | 5
|  |  |  | Estimated Customers Interrupted (Med/Large C&I) | count | 1 | 0
|  |  |  | Value of Lost Load (VOLL) | $/Outage Event | 17961 | 4468
|  |  |  | Calibration Year | year | 2025 | N/A
|  |  |  | Historic Annual Outage Events2 | Count | 2.2 | N/A
2These outages should reflect those caused by the climate perils addressed in this risk analysis. Inclusion of historic outages from other causes will inflate results.
Table 10: Applicable Assets
|  |  |  | Existing Assets |  |  | Standard Assets |  |  | Replacement Assets |  |  |  | Project Budget | Cost for BCA
| Existing | Standard | Replace | Asset Class | Asset Sub-Class | Unit Basis | Code Asset Class | Code Asset Sub-Class | Baseline Count | Replacement Asset Class | Replacement Asset Sub-Class | Project Count | Unit Basis | Budget ($) | BCA Cost ($)
| PoleClass 5 |  |  | Pole | Class 5 | pole
| PoleClass 4 | PoleClass 3 | PoleClass 2 | Pole | Class 4 | pole | Pole | Class 3 | 100 | Pole | Class 2 | 100 | pole | 532400 | 109380.4683
| PoleClass 3 |  |  | Pole | Class 3 | pole
| PoleClass 2 |  |  | Pole | Class 2 | pole
Users should develop project characteristics that accurately reflect a potential VASH investment opportunity. The toolkit is designed to evaluate one project at a time based on the comprehensive VA.
Table 6: Project Characteristics:
The project location is predetermined based on the location being viewed in '5. VA Heatmap'. This location should reflect the region in which the project being evaluated will be implemented by choosing the closest location with climate data. There are three Project Type options based on the status of the LDC's existing assets. End-of-Life should be selected if the project will replace assets that would have been replaced in the absence of resiliency planning due to age or condition. Early Retirement should be selected if the project will replace assets that would have been expected to remain in service beyond the start date of the project. Retrofit should be selected if the project will not impact existing assets (e.g., sectionalizing or back-up generation).
There are three Impact Type Options based on the mitigation goal of the project. Frequency should be selected if the project increases the robustness of assets to climate perils (i.e., changes the expected failure threshold) but does not impact the duration or number of customers impacted by remaining outages at that location. Criticality should be selected if the project reduces the expected outage durations and/or number of customers impacted by an outage but does not reduce the expected frequency of these events. Both should be selected if the project will reduce the frequency and criticality of outages.
Table 7: Project Economic Variables:
Users should input an estimate for common economic analysis variables. Inflation is the expected annual inflation rate for the duration of the project lifetime. The nominal utility discount rate (WACC) is the rate used for present value calculations of utility costs. The societal discount rate is the rate used for customer impact present value calculations (given by IESO at 4%). Baseline OM&A Cost (% of Total Costs) represent the percent of total asset base costs attributable to OM&A. Scenario OM&A Cost (% of Total Costs) represent the percent of total asset scenario costs attributable to OM&A. The tax rate is the combined federal plus provincial tax rate. Project non-asset costs, which are one-time costs that do not scale by the number of assets in the project, must be added to the total asset costs to estimate the full cost of a system hardening project. Examples of these costs include engineering expenses, administrative fees, overhead burden, and any other measurable changes in costs incurred that are attributable to the implementation of the system hardening project.
Table 8: Project Lifetime Variables:
Resiliency investments mitigate risk for the lifetime of installed assets and therefore the lifetime benefits of a project should be analyzed. Users should input the project start year and an estimate for the expected lifetime of the project. Project lifetimes are the expected field life of the assets being invested in. If multiple asset classes are included in the project, a weighted average lifetime may be used. A remaining useful life (RUL) for Existing Assets is required for early retirement projects. This should be the expected number of years that these assets would have continued to be in service in the absence of the resiliency project. This field will be blurred for other Project Types.
Table 9: Criticality Variables:
The BCA Toolkit is designed to leverage per outage event value of lost load (VOLL) estimates for the area impacted by a project. To develop these values using the ICE Calculator, as accepted in the Generic BCA Option, the expected outage duration and number of customers interrupted for three customer classes is required. These values may be input into the ICE Calculator to yield the VOLL in $/outage event. See the BCA Toolkit User Guide for guidance on leveraging the ICE Calculator do develop these inputs. A baseline value is necessary for all Project Types. This scenario's inputs should reflect historical values for outage durations and number of customers impacted for the climate perils that the project will address. For Frequency Impact Type projects, the Project Value should Equal the Baseline Value as there is no change in the criticality of remaining outages after project implementation. For Criticality and Both Project Types, the resulting duration and customer counts should be input into the ICE Calculator as a separate scenario to determine the post-project implementation VOLL. The OEB proposes an acceptable starting point ICE composite value including input variables from the following states: New York, Michigan, Ohio, and Iowa. However, a distributor may choose any single or combination of states as a starting point based on comparability to its territory.
An estimate of the count of historic annual outages for the project location and climate perils addressed should be developed. Counts should be as granular as possible, however, a 5-year average for an applicable feeder, substation, or section is appropriate. If no historic outages tied to cause codes related to the targeted climate peril for mitigation exist for the project location but the VA suggests that a project may be prudent, the system average annual historic outage frequency from these perils may be applied.
Table 10: Applicable Assets:
Users should identify the Existing Asset classes prepopulated from the VA that are relevant to the project being evaluated. Users should then populate the Replacement Assets fields with the asset class, sub-class, and total count of assets in the proposed project. If the Standard asset sub-class is different from the Existing Assets due to a codes/standards change during the Existing Assets' lifetime, users should fill the Standard Assets with what would have been used in the absence of the resiliency investment. If there has not been a change, fill in the Standard Assets with the same sub-class as the Existing Assets. The baseline count should align with the Existing and Standard Assets' unit basis and the project count should align with the Replacement Assets' unit basis (e.g., an undergrounding program Existing may be per pole and the Replacement may be per km).
The total project budget and BCA cost will calculate automatically. Note that the BCA cost will differ from project budget based on the Project Type selected in the Project Characteristics and the adjustment to the present value of customer revenue requirement. For End-of-life and Early Retirement projects, the model will expect to see a change in asset class for project-applicable assets and an appropriate count. For retrofit projects AND projects that are Criticality only, Replacement Assets and counts should equal the Starting Assets that are considered in the development of the historic customer outage estimate. Note: Retrofit AND Criticality only projects will have $0 budget and BCA cost regardless of the asset counts (i.e., the entire project budget is considered in the Incremental Project Non-Asset Costs).

## 8. Project BCA Results
DRAFT - Example Data Illustrative
Project BCA Results
Project Summary Metrics
| Metric | Unit | Expected Value
| Total PV Benefits from Avoided Repairs and Replacements | PV 2026$ | 109725.013
| Total PV Benefits from Frequency Reductions (VOLL) | PV 2026$ | 72352.0571
| Total PV Benefits from Criticality Reductions (VOLL) | PV 2026$ | 33672.943
| Total PV Costs | PV 2026$ | 742160.0369
| BCR | ratio | 0.29071
| Expected Annual Average CMI Reduction1 | CMI | 4512.1414
| Expected Lifetime CMI Reduction | CMI | 180485.657
1Simple average over project lifetime.
Project BCA results are automatically calculated based of the inputs in each of the previous model tabs. Benefits are provided based on three primary categories: avoided repair and replace costs, VOLL from reductions in outage frequency, and VOLL from reductions in outage criticality. It is common for some benefit categories to be $0 based on project characteristics. A benefit-cost ratio (BCR) greater than 1.0 indicates that the present value of lifecycle benefits of the project being evaluated is greater than the upfront incremental costs of that program. The estimated annual and lifetime reductions in customer minutes of interruption (CMI) for the project is also provided.

## Calibration
Project Scenario PV Benefits |  | Repair/Replace Risk |  | Risk VOLL from Outage Frequency |  | Risk VOLL from Outage Criticality |  | Annual event Theta for Calibration
Asset Class | Asset Sub-Class | Baseline | Project | Baseline | Project | Baseline | Project | Asset Class | Asset Sub-Class | Baseline | Scenario |  | Total Modeled Event Probability | Theta | RUL for Model
Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 |  | Baseline | 10.1941 | 0.21581 | 0
Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 10.1941 |  | Primary Scenario |  | N/A
Pole | Class 3 | 187938.5335 | 0 | 117175.2787 | 0 | 0 | 0 | Pole | Class 3 | 0 |  | Low |  | N/A
Pole | Class 2 | 0 | 78213.5205 | 0 | 44823.2216 | 44823.2216 | 11150.2786 | Pole | Class 2 | 0 |  | High |  | N/A
Calculates the calibration multiplier based on historic annual outage input and a sum over the modeled asset failures in the calibration year. RUL for model is used to automatically zero out the RUL for end-of-life and retrofit project types. The PV benefit streams are summarized for incorporation into final outputs.

## Climate Data
DRAFT - Example Data Illustrative
Climate Data
Return Interval
|  | Location ID | Climate Peril | Scenario | Year | 10 | 20 | 50 | 100 | 200 | Location List
| Ailsa CraigIce Accretion2023RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425 | Ailsa Craig
| Ailsa CraigIce Accretion2025RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2025 | 17.1352 | 20.5563 | 24.8625 | 28.1605 | 31.4423 | Ajax
| Ailsa CraigIce Accretion2030RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2030 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542 | Alexandria
| Ailsa CraigIce Accretion2035RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2035 | 17.17 | 20.6255 | 24.9875 | 28.3206 | 31.6418 | Alliston
| Ailsa CraigIce Accretion2040RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2040 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415 | Almonte
| Ailsa CraigIce Accretion2045RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2045 | 17.2048 | 20.6947 | 25.1125 | 28.4807 | 31.8412 | Armstrong
| Ailsa CraigIce Accretion2050RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2050 | 17.1526 | 20.6794 | 25.145 | 28.5438 | 31.941 | Arnprior
| Ailsa CraigIce Accretion2055RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2055 | 17.083 | 20.6296 | 25.115 | 28.5268 | 31.941 | Atikokan
| Ailsa CraigIce Accretion2060RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2060 | 17.0134 | 20.5799 | 25.085 | 28.5099 | 31.941 | Attawapiskat
| Ailsa CraigIce Accretion2065RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2065 | 16.9439 | 20.53 | 25.055 | 28.4929 | 31.941 | Aurora
| Ailsa CraigIce Accretion2070RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2070 | 16.8743 | 20.4802 | 25.025 | 28.476 | 31.941 | Bancroft
| Ailsa CraigIce Accretion2075RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2075 | 16.8424 | 20.4664 | 25.0375 | 28.5042 | 31.9883 | Barrie
| Ailsa CraigIce Accretion2080RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2080 | 16.8105 | 20.4526 | 25.05 | 28.5325 | 32.0355 | Barriefield
| Ailsa CraigIce Accretion2085RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2085 | 16.7786 | 20.4387 | 25.0625 | 28.5607 | 32.0827 | Beaverton
| Ailsa CraigIce Accretion2090RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2090 | 16.7467 | 20.4249 | 25.075 | 28.589 | 32.13 | Belleville
| Ailsa CraigIce Accretion2095RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2095 | 16.7148 | 20.4111 | 25.0875 | 28.6172 | 32.1773 | Belmont
| Ailsa CraigIce Accretion2100RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.3972 | 25.1 | 28.6455 | 32.2245 | Bowmanville
| Ailsa CraigIce Accretion2023RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425 | Bracebridge
| Ailsa CraigIce Accretion2025RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2025 | 17.1352 | 20.5563 | 24.8625 | 28.1605 | 31.4423 | Bradford
| Ailsa CraigIce Accretion2030RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2030 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542 | Brampton
| Ailsa CraigIce Accretion2035RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2035 | 17.17 | 20.6255 | 24.9875 | 28.3206 | 31.6418 | Brantford
| Ailsa CraigIce Accretion2040RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2040 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415 | Brighton
| Ailsa CraigIce Accretion2045RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2045 | 17.2048 | 20.6947 | 25.1125 | 28.4807 | 31.8412 | Brockville
| Ailsa CraigIce Accretion2050RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2050 | 17.1526 | 20.6794 | 25.145 | 28.5438 | 31.941 | Burk's Falls
| Ailsa CraigIce Accretion2055RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2055 | 17.083 | 20.6296 | 25.115 | 28.5268 | 31.941 | Burlington
| Ailsa CraigIce Accretion2060RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2060 | 17.0134 | 20.5799 | 25.085 | 28.5099 | 31.941 | CFB Borden
| Ailsa CraigIce Accretion2065RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2065 | 16.9439 | 20.53 | 25.055 | 28.4929 | 31.941 | Cambridge
| Ailsa CraigIce Accretion2070RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2070 | 16.8743 | 20.4802 | 25.025 | 28.476 | 31.941 | Campbellford
| Ailsa CraigIce Accretion2075RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2075 | 16.8264 | 20.4595 | 25.0437 | 28.5184 | 32.0119 | Cannington
| Ailsa CraigIce Accretion2080RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2080 | 16.7786 | 20.4387 | 25.0625 | 28.5607 | 32.0827 | Carleton Place
| Ailsa CraigIce Accretion2085RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2085 | 16.7308 | 20.418 | 25.0813 | 28.6031 | 32.1536 | Cavan
| Ailsa CraigIce Accretion2090RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2090 | 16.4742 | 20.1898 | 24.8833 | 28.4289 | 31.9935 | Centralia
| Ailsa CraigIce Accretion2095RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2095 | 16.2654 | 19.9822 | 24.6667 | 28.2123 | 31.7625 | Chapleau
| Ailsa CraigIce Accretion2100RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2100 | 16.0566 | 19.7747 | 24.45 | 27.9957 | 31.5315 | Chatham
| Ailsa CraigIce Accretion2023RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425 | Chesley
| Ailsa CraigIce Accretion2025RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2025 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542 | Clinton
| Ailsa CraigIce Accretion2030RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2030 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415 | Coboconk
| Ailsa CraigIce Accretion2035RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2035 | 17.2222 | 20.7293 | 25.175 | 28.5607 | 31.941 | Cobourg
| Ailsa CraigIce Accretion2040RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2040 | 17.1062 | 20.6462 | 25.125 | 28.5325 | 31.941 | Cochrane
| Ailsa CraigIce Accretion2045RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2045 | 16.9902 | 20.5633 | 25.075 | 28.5042 | 31.941 | Colborne
| Ailsa CraigIce Accretion2050RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2050 | 16.8105 | 20.4526 | 25.05 | 28.5325 | 32.0355 | Collingwood
| Ailsa CraigIce Accretion2055RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2055 | 16.7467 | 20.4249 | 25.075 | 28.589 | 32.13 | Cornwall
| Ailsa CraigIce Accretion2060RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2060 | 16.4742 | 20.1898 | 24.8833 | 28.4289 | 31.9935 | Corunna
| Ailsa CraigIce Accretion2065RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2065 | 16.2654 | 19.9822 | 24.6667 | 28.2123 | 31.7625 | Deep River
| Ailsa CraigIce Accretion2070RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2070 | 15.6797 | 19.3528 | 23.975 | 27.4778 | 30.9645 | Deseronto
| Ailsa CraigIce Accretion2075RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2075 | 15.3028 | 18.9309 | 23.5 | 26.9599 | 30.3975 | Dorchester
| Ailsa CraigIce Accretion2080RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2080 | 14.9259 | 18.509 | 23.025 | 26.442 | 29.8305 | Dorion
| Ailsa CraigIce Accretion2085RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2085 | 14.1431 | 17.5856 | 21.925 | 25.2131 | 28.476 | Dresden
| Ailsa CraigIce Accretion2090RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2090 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215 | Dryden
| Ailsa CraigIce Accretion2095RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2095 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215 | Dundalk
| Ailsa CraigIce Accretion2100RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2100 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215 | Dunnville
| Ailsa CraigWind2023RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086 | Durham
| Ailsa CraigWind2025RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283 | Dutton
| Ailsa CraigWind2030RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148 | Earlton
| Ailsa CraigWind2035RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678 | Edison
| Ailsa CraigWind2040RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875 | Elliot Lake
| Ailsa CraigWind2045RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072 | Elmvale
| Ailsa CraigWind2050RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939 | Embro
| Ailsa CraigWind2055RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161 | Englehart
| Ailsa CraigWind2060RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228 | Espanola
| Ailsa CraigWind2065RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295 | Etobicoke
| Ailsa CraigWind2070RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621 | Exeter
| Ailsa CraigWind2075RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2075 | 86.3504 | 93.3577 | 100.8387 | 108.226 | 115.6228 | Fenelon Falls
| Ailsa CraigWind2080RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2080 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834 | Fergus
| Ailsa CraigWind2085RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2085 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441 | Forest
| Ailsa CraigWind2090RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2090 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048 | Fort Erie
| Ailsa CraigWind2095RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2095 | 86.7678 | 93.9167 | 101.5705 | 109.1068 | 116.6655 | Fort Erie (Ridgeway)
| Ailsa CraigWind2100RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2100 | 86.8722 | 94.0565 | 101.7534 | 109.327 | 116.9262 | Fort Frances
| Ailsa CraigWind2023RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086 | Gananoque
| Ailsa CraigWind2025RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283 | Geraldton
| Ailsa CraigWind2030RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148 | Glencoe
| Ailsa CraigWind2035RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678 | Goderich
| Ailsa CraigWind2040RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875 | Gore Bay
| Ailsa CraigWind2045RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072 | Graham
| Ailsa CraigWind2050RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939 | Gravenhurst (Muskoka Airport)
| Ailsa CraigWind2055RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161 | Grimsby
| Ailsa CraigWind2060RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228 | Guelph
| Ailsa CraigWind2065RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295 | Guthrie
| Ailsa CraigWind2070RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621 | Haileybury
| Ailsa CraigWind2075RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2075 | 86.4026 | 93.4276 | 100.9302 | 108.3361 | 115.7531 | Haldimand (Caledonia)
| Ailsa CraigWind2080RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2080 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441 | Haldimand (Hagersville)
| Ailsa CraigWind2085RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2085 | 86.7157 | 93.8469 | 101.479 | 108.9967 | 116.5351 | Haliburton
| Ailsa CraigWind2090RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2090 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885 | Halton Hills (Georgetown)
| Ailsa CraigWind2095RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2095 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508 | Hamilton
| Ailsa CraigWind2100RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2100 | 87.7861 | 95.1502 | 103.0568 | 110.8265 | 118.6131 | Hanover
| Ailsa CraigWind2023RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086 | Hastings
| Ailsa CraigWind2025RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2025 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148 | Hawkesbury
| Ailsa CraigWind2030RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2030 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875 | Hearst
| Ailsa CraigWind2035RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2035 | 86.0768 | 93.0084 | 100.3912 | 107.7017 | 115.0269 | Honey Harbour
| Ailsa CraigWind2040RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2040 | 86.1332 | 93.0782 | 100.4794 | 107.8031 | 115.1386 | Hornepayne
| Ailsa CraigWind2045RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2045 | 86.1896 | 93.1481 | 100.5676 | 107.9044 | 115.2504 | Huntsville
| Ailsa CraigWind2050RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2050 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834 | Ingersoll
| Ailsa CraigWind2055RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2055 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048 | Iroquois Falls
| Ailsa CraigWind2060RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2060 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885 | Jellicoe
| Ailsa CraigWind2065RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2065 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508 | Kapuskasing
| Ailsa CraigWind2070RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2070 | 88.0541 | 95.5026 | 103.5207 | 111.3788 | 119.2611 | Kemptville
| Ailsa CraigWind2075RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2075 | 88.322 | 95.855 | 103.9845 | 111.9311 | 119.9091 | Kenora
| Ailsa CraigWind2080RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2080 | 88.59 | 96.2074 | 104.4484 | 112.4833 | 120.5571 | Killaloe
| Ailsa CraigWind2085RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2085 | 88.9454 | 96.6585 | 105.0217 | 113.1649 | 121.3447 | Kincardine
| Ailsa CraigWind2090RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2090 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323 | Kingston
| Ailsa CraigWind2095RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2095 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323 | Kinmount
| Ailsa CraigWind2100RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2100 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323 | Kirkland Lake
| AjaxIce Accretion2023RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185 | Kitchener
| AjaxIce Accretion2025RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218 | Kitchenuhmaykoosib
| AjaxIce Accretion2030RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585 | Lakefield
| AjaxIce Accretion2035RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952 | Lansdowne House
| AjaxIce Accretion2040RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332 | Leamington
| AjaxIce Accretion2045RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687 | Lindsay
| AjaxIce Accretion2050RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122 | Lion's Head
| AjaxIce Accretion2055RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385 | Listowel
| AjaxIce Accretion2060RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555 | London
| AjaxIce Accretion2065RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715 | Lucan
| AjaxIce Accretion2070RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988 | Maitland
| AjaxIce Accretion2075RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195 | Markdale
| AjaxIce Accretion2080RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051 | Markham
| AjaxIce Accretion2085RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825 | Martin
| AjaxIce Accretion2090RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114 | Matheson
| AjaxIce Accretion2095RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455 | Mattawa
| AjaxIce Accretion2100RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177 | Midland
| AjaxIce Accretion2023RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185 | Milton
| AjaxIce Accretion2025RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218 | Milverton
| AjaxIce Accretion2030RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585 | Minden
| AjaxIce Accretion2035RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952 | Mississauga
| AjaxIce Accretion2040RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332 | Mississauga Port Credit
| AjaxIce Accretion2045RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687 | Mitchell
| AjaxIce Accretion2050RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122 | Moosonee
| AjaxIce Accretion2055RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385 | Morrisburg
| AjaxIce Accretion2060RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555 | Mount Forest
| AjaxIce Accretion2065RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715 | Nakina
| AjaxIce Accretion2070RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988 | Nanticoke (Jarvis)
| AjaxIce Accretion2075RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352 | Nanticoke (Port Dover)
| AjaxIce Accretion2080RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825 | Napanee
| AjaxIce Accretion2085RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298 | New Liskeard
| AjaxIce Accretion2090RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694 | Newcastle
| AjaxIce Accretion2095RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211 | Newmarket
| AjaxIce Accretion2100RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728 | Niagara Falls
| AjaxIce Accretion2023RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185 | North Bay
| AjaxIce Accretion2025RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585 | North York
| AjaxIce Accretion2030RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332 | Norwood
| AjaxIce Accretion2035RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055 | Oakville
| AjaxIce Accretion2040RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933 | Orangeville
| AjaxIce Accretion2045RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605 | Orillia
| AjaxIce Accretion2050RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051 | Oshawa
| AjaxIce Accretion2055RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114 | Ottawa (Barrhaven)
| AjaxIce Accretion2060RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694 | Ottawa (Kanata)
| AjaxIce Accretion2065RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211 | Ottawa (M-C Int'l Airport)
| AjaxIce Accretion2070RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085 | Ottawa (Orleans)
| AjaxIce Accretion2075RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489 | Ottawa (city hall)
| AjaxIce Accretion2080RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695 | Owen Sound
| AjaxIce Accretion2085RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157 | Pagwa River
| AjaxIce Accretion2090RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562 | Paris
| AjaxIce Accretion2095RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562 | Parkhill
| AjaxIce Accretion2100RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562 | Parry Sound
| AjaxWind2023RCP4.5 | Ajax | Wind | RCP4.5 | 2023 | 83.9588 | 90.3904 | 97.1552 | 103.9249 | 110.6906 | Pelham (Fonthill)
| AjaxWind2025RCP4.5 | Ajax | Wind | RCP4.5 | 2025 | 83.9742 | 90.4235 | 97.2086 | 103.9959 | 110.779 | Pembroke
| AjaxWind2030RCP4.5 | Ajax | Wind | RCP4.5 | 2030 | 83.9895 | 90.4566 | 97.2619 | 104.0668 | 110.8675 | Penetanguishene
| AjaxWind2035RCP4.5 | Ajax | Wind | RCP4.5 | 2035 | 84.0049 | 90.4897 | 97.3152 | 104.1377 | 110.956 | Perth
| AjaxWind2040RCP4.5 | Ajax | Wind | RCP4.5 | 2040 | 84.0202 | 90.5227 | 97.3686 | 104.2086 | 111.0444 | Petawawa
| AjaxWind2045RCP4.5 | Ajax | Wind | RCP4.5 | 2045 | 84.0356 | 90.5558 | 97.4219 | 104.2795 | 111.1329 | Peterborough
| AjaxWind2050RCP4.5 | Ajax | Wind | RCP4.5 | 2050 | 84.133 | 90.6917 | 97.6053 | 104.502 | 111.3983 | Petrolia
| AjaxWind2055RCP4.5 | Ajax | Wind | RCP4.5 | 2055 | 84.2151 | 90.7946 | 97.7353 | 104.6535 | 111.5752 | Pickering (Dunbarton)
| AjaxWind2060RCP4.5 | Ajax | Wind | RCP4.5 | 2060 | 84.2972 | 90.8974 | 97.8652 | 104.8051 | 111.7521 | Picton
| AjaxWind2065RCP4.5 | Ajax | Wind | RCP4.5 | 2065 | 84.3793 | 91.0002 | 97.9952 | 104.9566 | 111.9291 | Plattsville
| AjaxWind2070RCP4.5 | Ajax | Wind | RCP4.5 | 2070 | 84.4614 | 91.1031 | 98.1252 | 105.1081 | 112.106 | Point Alexander
| AjaxWind2075RCP4.5 | Ajax | Wind | RCP4.5 | 2075 | 84.6037 | 91.2865 | 98.3596 | 105.3866 | 112.4285 | Port Burwell
| AjaxWind2080RCP4.5 | Ajax | Wind | RCP4.5 | 2080 | 84.7461 | 91.4699 | 98.594 | 105.6651 | 112.7511 | Port Colborne
| AjaxWind2085RCP4.5 | Ajax | Wind | RCP4.5 | 2085 | 84.8885 | 91.6534 | 98.8285 | 105.9436 | 113.0736 | Port Elgin
| AjaxWind2090RCP4.5 | Ajax | Wind | RCP4.5 | 2090 | 85.0309 | 91.8368 | 99.0629 | 106.2221 | 113.3961 | Port Hope
| AjaxWind2095RCP4.5 | Ajax | Wind | RCP4.5 | 2095 | 85.1733 | 92.0202 | 99.2973 | 106.5006 | 113.7186 | Port Perry
| AjaxWind2100RCP4.5 | Ajax | Wind | RCP4.5 | 2100 | 85.3157 | 92.2036 | 99.5317 | 106.7792 | 114.0412 | Port Stanley
| AjaxWind2023RCP6.0 | Ajax | Wind | RCP6.0 | 2023 | 83.9588 | 90.3904 | 97.1552 | 103.9249 | 110.6906 | Prescott
| AjaxWind2025RCP6.0 | Ajax | Wind | RCP6.0 | 2025 | 83.9742 | 90.4235 | 97.2086 | 103.9959 | 110.779 | Princeton
| AjaxWind2030RCP6.0 | Ajax | Wind | RCP6.0 | 2030 | 83.9895 | 90.4566 | 97.2619 | 104.0668 | 110.8675 | Raith
| AjaxWind2035RCP6.0 | Ajax | Wind | RCP6.0 | 2035 | 84.0049 | 90.4897 | 97.3152 | 104.1377 | 110.956 | Rayside-Balfour (Chelmsford)
| AjaxWind2040RCP6.0 | Ajax | Wind | RCP6.0 | 2040 | 84.0202 | 90.5227 | 97.3686 | 104.2086 | 111.0444 | Red Lake
| AjaxWind2045RCP6.0 | Ajax | Wind | RCP6.0 | 2045 | 84.0356 | 90.5558 | 97.4219 | 104.2795 | 111.1329 | Renfrew
| AjaxWind2050RCP6.0 | Ajax | Wind | RCP6.0 | 2050 | 84.133 | 90.6917 | 97.6053 | 104.502 | 111.3983 | Richmond Hill
| AjaxWind2055RCP6.0 | Ajax | Wind | RCP6.0 | 2055 | 84.2151 | 90.7946 | 97.7353 | 104.6535 | 111.5752 | Rockland
| AjaxWind2060RCP6.0 | Ajax | Wind | RCP6.0 | 2060 | 84.2972 | 90.8974 | 97.8652 | 104.8051 | 111.7521 | Sarnia
| AjaxWind2065RCP6.0 | Ajax | Wind | RCP6.0 | 2065 | 84.3793 | 91.0002 | 97.9952 | 104.9566 | 111.9291 | Sault Ste. Marie
| AjaxWind2070RCP6.0 | Ajax | Wind | RCP6.0 | 2070 | 84.4614 | 91.1031 | 98.1252 | 105.1081 | 112.106 | Scarborough
| AjaxWind2075RCP6.0 | Ajax | Wind | RCP6.0 | 2075 | 84.6749 | 91.3782 | 98.4768 | 105.5259 | 112.5898 | Schreiber
| AjaxWind2080RCP6.0 | Ajax | Wind | RCP6.0 | 2080 | 84.8885 | 91.6534 | 98.8285 | 105.9436 | 113.0736 | Seaforth
| AjaxWind2085RCP6.0 | Ajax | Wind | RCP6.0 | 2085 | 85.1021 | 91.9285 | 99.1801 | 106.3614 | 113.5574 | Shelburne
| AjaxWind2090RCP6.0 | Ajax | Wind | RCP6.0 | 2090 | 85.7568 | 92.7449 | 100.201 | 107.5576 | 114.9332 | Simcoe
| AjaxWind2095RCP6.0 | Ajax | Wind | RCP6.0 | 2095 | 86.1979 | 93.2862 | 100.8703 | 108.336 | 115.8252 | Sioux Lookout
| AjaxWind2100RCP6.0 | Ajax | Wind | RCP6.0 | 2100 | 86.6391 | 93.8274 | 101.5396 | 109.1144 | 116.7172 | Smiths Falls
| AjaxWind2023RCP8.5 | Ajax | Wind | RCP8.5 | 2023 | 83.9588 | 90.3904 | 97.1552 | 103.9249 | 110.6906 | Smithville
| AjaxWind2025RCP8.5 | Ajax | Wind | RCP8.5 | 2025 | 83.9895 | 90.4566 | 97.2619 | 104.0668 | 110.8675 | Smooth Rock Falls
| AjaxWind2030RCP8.5 | Ajax | Wind | RCP8.5 | 2030 | 84.0202 | 90.5227 | 97.3686 | 104.2086 | 111.0444 | South River
| AjaxWind2035RCP8.5 | Ajax | Wind | RCP8.5 | 2035 | 84.0509 | 90.5889 | 97.4753 | 104.3505 | 111.2214 | Southampton
| AjaxWind2040RCP8.5 | Ajax | Wind | RCP8.5 | 2040 | 84.1878 | 90.7603 | 97.6919 | 104.603 | 111.5162 | St. Catharines
| AjaxWind2045RCP8.5 | Ajax | Wind | RCP8.5 | 2045 | 84.3246 | 90.9317 | 97.9086 | 104.8556 | 111.8111 | St. Mary's
| AjaxWind2050RCP8.5 | Ajax | Wind | RCP8.5 | 2050 | 84.7461 | 91.4699 | 98.594 | 105.6651 | 112.7511 | St. Thomas
| AjaxWind2055RCP8.5 | Ajax | Wind | RCP8.5 | 2055 | 85.0309 | 91.8368 | 99.0629 | 106.2221 | 113.3961 | Stirling
| AjaxWind2060RCP8.5 | Ajax | Wind | RCP8.5 | 2060 | 85.7568 | 92.7449 | 100.201 | 107.5576 | 114.9332 | Stratford
| AjaxWind2065RCP8.5 | Ajax | Wind | RCP8.5 | 2065 | 86.1979 | 93.2862 | 100.8703 | 108.336 | 115.8252 | Strathroy
| AjaxWind2070RCP8.5 | Ajax | Wind | RCP8.5 | 2070 | 86.7703 | 94.0048 | 101.7756 | 109.405 | 117.0563 | Sturgeon Falls
| AjaxWind2075RCP8.5 | Ajax | Wind | RCP8.5 | 2075 | 86.9015 | 94.1822 | 102.0117 | 109.6957 | 117.3954 | Sudbury
| AjaxWind2080RCP8.5 | Ajax | Wind | RCP8.5 | 2080 | 87.0327 | 94.3597 | 102.2477 | 109.9863 | 117.7345 | Sundridge
| AjaxWind2085RCP8.5 | Ajax | Wind | RCP8.5 | 2085 | 87.3133 | 94.7566 | 102.7909 | 110.6505 | 118.5252 | Tavistock
| AjaxWind2090RCP8.5 | Ajax | Wind | RCP8.5 | 2090 | 87.5939 | 95.1535 | 103.3341 | 111.3148 | 119.3158 | Temagami
| AjaxWind2095RCP8.5 | Ajax | Wind | RCP8.5 | 2095 | 87.5939 | 95.1535 | 103.3341 | 111.3148 | 119.3158 | Thamesford
| AjaxWind2100RCP8.5 | Ajax | Wind | RCP8.5 | 2100 | 87.5939 | 95.1535 | 103.3341 | 111.3148 | 119.3158 | Thedford
| AlexandriaIce Accretion2023RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2023 | 20.8545 | 24.8751 | 29.94 | 33.8322 | 37.7244 | Thunder Bay
| AlexandriaIce Accretion2025RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2025 | 20.8823 | 24.9207 | 30.005 | 33.9113 | 37.8189 | Tillsonburg
| AlexandriaIce Accretion2030RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2030 | 20.9102 | 24.9664 | 30.07 | 33.9904 | 37.9134 | Timmins
| AlexandriaIce Accretion2035RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2035 | 20.938 | 25.012 | 30.135 | 34.0695 | 38.0079 | Timmins (Porcupine)
| AlexandriaIce Accretion2040RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2040 | 20.9658 | 25.0577 | 30.2 | 34.1486 | 38.1024 | Toronto (LBP Int'l Airport)
| AlexandriaIce Accretion2045RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2045 | 20.9937 | 25.1033 | 30.265 | 34.2277 | 38.1969 | Toronto (city hall)
| AlexandriaIce Accretion2050RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2050 | 21.0299 | 25.1689 | 30.372 | 34.361 | 38.3519 | Trenton
| AlexandriaIce Accretion2055RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2055 | 21.0382 | 25.1888 | 30.414 | 34.4153 | 38.4124 | Trout Creek
| AlexandriaIce Accretion2060RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2060 | 21.0466 | 25.2088 | 30.456 | 34.4695 | 38.4728 | Uxbridge
| AlexandriaIce Accretion2065RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2065 | 21.0549 | 25.2287 | 30.498 | 34.5238 | 38.5333 | Vaughan (Woodbridge)
| AlexandriaIce Accretion2070RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2070 | 21.0633 | 25.2486 | 30.54 | 34.578 | 38.5938 | Vittoria
| AlexandriaIce Accretion2075RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2075 | 21.1155 | 25.3316 | 30.665 | 34.7362 | 38.7828 | Walkerton
| AlexandriaIce Accretion2080RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2080 | 21.1676 | 25.4146 | 30.79 | 34.8944 | 38.9718 | Wallaceburg
| AlexandriaIce Accretion2085RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2085 | 21.2198 | 25.4976 | 30.915 | 35.0526 | 39.1608 | Waterloo
| AlexandriaIce Accretion2090RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2090 | 21.272 | 25.5806 | 31.04 | 35.2108 | 39.3498 | Watford
| AlexandriaIce Accretion2095RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2095 | 21.3242 | 25.6636 | 31.165 | 35.369 | 39.5388 | Wawa
| AlexandriaIce Accretion2100RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2100 | 21.3764 | 25.7466 | 31.29 | 35.5272 | 39.7278 | Welland
| AlexandriaIce Accretion2023RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2023 | 20.8545 | 24.8751 | 29.94 | 33.8322 | 37.7244 | West Lorne
| AlexandriaIce Accretion2025RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2025 | 20.8823 | 24.9207 | 30.005 | 33.9113 | 37.8189 | Whitby
| AlexandriaIce Accretion2030RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2030 | 20.9102 | 24.9664 | 30.07 | 33.9904 | 37.9134 | Whitby (Brooklin)
| AlexandriaIce Accretion2035RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2035 | 20.938 | 25.012 | 30.135 | 34.0695 | 38.0079 | White River
| AlexandriaIce Accretion2040RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2040 | 20.9658 | 25.0577 | 30.2 | 34.1486 | 38.1024 | Wiarton
| AlexandriaIce Accretion2045RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2045 | 20.9937 | 25.1033 | 30.265 | 34.2277 | 38.1969 | Windsor
| AlexandriaIce Accretion2050RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2050 | 21.0299 | 25.1689 | 30.372 | 34.361 | 38.3519 | Wingham
| AlexandriaIce Accretion2055RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2055 | 21.0382 | 25.1888 | 30.414 | 34.4153 | 38.4124 | Woodstock
| AlexandriaIce Accretion2060RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2060 | 21.0466 | 25.2088 | 30.456 | 34.4695 | 38.4728 | Wyoming
| AlexandriaIce Accretion2065RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2065 | 21.0549 | 25.2287 | 30.498 | 34.5238 | 38.5333
| AlexandriaIce Accretion2070RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2070 | 21.0633 | 25.2486 | 30.54 | 34.578 | 38.5938
| AlexandriaIce Accretion2075RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2075 | 21.1415 | 25.3731 | 30.7275 | 34.8153 | 38.8773
| AlexandriaIce Accretion2080RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2080 | 21.2198 | 25.4976 | 30.915 | 35.0526 | 39.1608
| AlexandriaIce Accretion2085RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2085 | 21.2981 | 25.6221 | 31.1025 | 35.2899 | 39.4443
| AlexandriaIce Accretion2090RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2090 | 21.3346 | 25.7466 | 31.33 | 35.595 | 39.8412
| AlexandriaIce Accretion2095RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2095 | 21.2929 | 25.7466 | 31.37 | 35.6628 | 39.9546
| AlexandriaIce Accretion2100RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2100 | 21.2511 | 25.7466 | 31.41 | 35.7306 | 40.068
| AlexandriaIce Accretion2023RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2023 | 20.8545 | 24.8751 | 29.94 | 33.8322 | 37.7244
| AlexandriaIce Accretion2025RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2025 | 20.9102 | 24.9664 | 30.07 | 33.9904 | 37.9134
| AlexandriaIce Accretion2030RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2030 | 20.9658 | 25.0577 | 30.2 | 34.1486 | 38.1024
| AlexandriaIce Accretion2035RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2035 | 21.0215 | 25.149 | 30.33 | 34.3068 | 38.2914
| AlexandriaIce Accretion2040RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2040 | 21.0354 | 25.1822 | 30.4 | 34.3972 | 38.3922
| AlexandriaIce Accretion2045RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2045 | 21.0493 | 25.2154 | 30.47 | 34.4876 | 38.493
| AlexandriaIce Accretion2050RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2050 | 21.1676 | 25.4146 | 30.79 | 34.8944 | 38.9718
| AlexandriaIce Accretion2055RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2055 | 21.272 | 25.5806 | 31.04 | 35.2108 | 39.3498
| AlexandriaIce Accretion2060RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2060 | 21.3346 | 25.7466 | 31.33 | 35.595 | 39.8412
| AlexandriaIce Accretion2065RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2065 | 21.2929 | 25.7466 | 31.37 | 35.6628 | 39.9546
| AlexandriaIce Accretion2070RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2070 | 21.0911 | 25.5972 | 31.27 | 35.6063 | 39.942
| AlexandriaIce Accretion2075RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2075 | 20.9311 | 25.4478 | 31.13 | 35.482 | 39.816
| AlexandriaIce Accretion2080RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2080 | 20.771 | 25.2984 | 30.99 | 35.3577 | 39.69
| AlexandriaIce Accretion2085RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2085 | 19.9464 | 24.3771 | 29.94 | 34.2051 | 38.4237
| AlexandriaIce Accretion2090RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2090 | 19.1219 | 23.4558 | 28.89 | 33.0525 | 37.1574
| AlexandriaIce Accretion2095RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2095 | 19.1219 | 23.4558 | 28.89 | 33.0525 | 37.1574
| AlexandriaIce Accretion2100RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2100 | 19.1219 | 23.4558 | 28.89 | 33.0525 | 37.1574
| AlexandriaWind2023RCP4.5 | Alexandria | Wind | RCP4.5 | 2023 | 77.5502 | 83.4573 | 89.649 | 95.8667 | 102.087
| AlexandriaWind2025RCP4.5 | Alexandria | Wind | RCP4.5 | 2025 | 77.593 | 83.5047 | 89.703 | 95.926 | 102.1503
| AlexandriaWind2030RCP4.5 | Alexandria | Wind | RCP4.5 | 2030 | 77.6357 | 83.5521 | 89.757 | 95.9854 | 102.2135
| AlexandriaWind2035RCP4.5 | Alexandria | Wind | RCP4.5 | 2035 | 77.6784 | 83.5996 | 89.811 | 96.0448 | 102.2768
| AlexandriaWind2040RCP4.5 | Alexandria | Wind | RCP4.5 | 2040 | 77.7212 | 83.647 | 89.865 | 96.1042 | 102.3401
| AlexandriaWind2045RCP4.5 | Alexandria | Wind | RCP4.5 | 2045 | 77.7639 | 83.6944 | 89.919 | 96.1636 | 102.4033
| AlexandriaWind2050RCP4.5 | Alexandria | Wind | RCP4.5 | 2050 | 77.7429 | 83.6699 | 89.8902 | 96.1305 | 102.364
| AlexandriaWind2055RCP4.5 | Alexandria | Wind | RCP4.5 | 2055 | 77.6792 | 83.5979 | 89.8074 | 96.0381 | 102.2614
| AlexandriaWind2060RCP4.5 | Alexandria | Wind | RCP4.5 | 2060 | 77.6155 | 83.5259 | 89.7246 | 95.9456 | 102.1588
| AlexandriaWind2065RCP4.5 | Alexandria | Wind | RCP4.5 | 2065 | 77.5518 | 83.4539 | 89.6418 | 95.8532 | 102.0562
| AlexandriaWind2070RCP4.5 | Alexandria | Wind | RCP4.5 | 2070 | 77.488 | 83.3819 | 89.559 | 95.7607 | 101.9536
| AlexandriaWind2075RCP4.5 | Alexandria | Wind | RCP4.5 | 2075 | 77.4311 | 83.3164 | 89.484 | 95.6773 | 101.863
| AlexandriaWind2080RCP4.5 | Alexandria | Wind | RCP4.5 | 2080 | 77.3741 | 83.2508 | 89.409 | 95.5938 | 101.7724
| AlexandriaWind2085RCP4.5 | Alexandria | Wind | RCP4.5 | 2085 | 77.3171 | 83.1852 | 89.334 | 95.5103 | 101.6817
| AlexandriaWind2090RCP4.5 | Alexandria | Wind | RCP4.5 | 2090 | 77.2601 | 83.1197 | 89.259 | 95.4269 | 101.5911
| AlexandriaWind2095RCP4.5 | Alexandria | Wind | RCP4.5 | 2095 | 77.2031 | 83.0541 | 89.184 | 95.3434 | 101.5005
| AlexandriaWind2100RCP4.5 | Alexandria | Wind | RCP4.5 | 2100 | 77.1461 | 82.9886 | 89.109 | 95.26 | 101.4098
| AlexandriaWind2023RCP6.0 | Alexandria | Wind | RCP6.0 | 2023 | 77.5502 | 83.4573 | 89.649 | 95.8667 | 102.087
| AlexandriaWind2025RCP6.0 | Alexandria | Wind | RCP6.0 | 2025 | 77.593 | 83.5047 | 89.703 | 95.926 | 102.1503
| AlexandriaWind2030RCP6.0 | Alexandria | Wind | RCP6.0 | 2030 | 77.6357 | 83.5521 | 89.757 | 95.9854 | 102.2135
| AlexandriaWind2035RCP6.0 | Alexandria | Wind | RCP6.0 | 2035 | 77.6784 | 83.5996 | 89.811 | 96.0448 | 102.2768
| AlexandriaWind2040RCP6.0 | Alexandria | Wind | RCP6.0 | 2040 | 77.7212 | 83.647 | 89.865 | 96.1042 | 102.3401
| AlexandriaWind2045RCP6.0 | Alexandria | Wind | RCP6.0 | 2045 | 77.7639 | 83.6944 | 89.919 | 96.1636 | 102.4033
| AlexandriaWind2050RCP6.0 | Alexandria | Wind | RCP6.0 | 2050 | 77.7429 | 83.6699 | 89.8902 | 96.1305 | 102.364
| AlexandriaWind2055RCP6.0 | Alexandria | Wind | RCP6.0 | 2055 | 77.6792 | 83.5979 | 89.8074 | 96.0381 | 102.2614
| AlexandriaWind2060RCP6.0 | Alexandria | Wind | RCP6.0 | 2060 | 77.6155 | 83.5259 | 89.7246 | 95.9456 | 102.1588
| AlexandriaWind2065RCP6.0 | Alexandria | Wind | RCP6.0 | 2065 | 77.5518 | 83.4539 | 89.6418 | 95.8532 | 102.0562
| AlexandriaWind2070RCP6.0 | Alexandria | Wind | RCP6.0 | 2070 | 77.488 | 83.3819 | 89.559 | 95.7607 | 101.9536
| AlexandriaWind2075RCP6.0 | Alexandria | Wind | RCP6.0 | 2075 | 77.4026 | 83.2836 | 89.4465 | 95.6355 | 101.8177
| AlexandriaWind2080RCP6.0 | Alexandria | Wind | RCP6.0 | 2080 | 77.3171 | 83.1852 | 89.334 | 95.5103 | 101.6817
| AlexandriaWind2085RCP6.0 | Alexandria | Wind | RCP6.0 | 2085 | 77.2316 | 83.0869 | 89.2215 | 95.3852 | 101.5458
| AlexandriaWind2090RCP6.0 | Alexandria | Wind | RCP6.0 | 2090 | 77.1098 | 82.9607 | 89.091 | 95.2503 | 101.4064
| AlexandriaWind2095RCP6.0 | Alexandria | Wind | RCP6.0 | 2095 | 77.0736 | 82.9328 | 89.073 | 95.2407 | 101.403
| AlexandriaWind2100RCP6.0 | Alexandria | Wind | RCP6.0 | 2100 | 77.0373 | 82.9049 | 89.055 | 95.2311 | 101.3996
| AlexandriaWind2023RCP8.5 | Alexandria | Wind | RCP8.5 | 2023 | 77.5502 | 83.4573 | 89.649 | 95.8667 | 102.087
| AlexandriaWind2025RCP8.5 | Alexandria | Wind | RCP8.5 | 2025 | 77.6357 | 83.5521 | 89.757 | 95.9854 | 102.2135
| AlexandriaWind2030RCP8.5 | Alexandria | Wind | RCP8.5 | 2030 | 77.7212 | 83.647 | 89.865 | 96.1042 | 102.3401
| AlexandriaWind2035RCP8.5 | Alexandria | Wind | RCP8.5 | 2035 | 77.8067 | 83.7418 | 89.973 | 96.223 | 102.4666
| AlexandriaWind2040RCP8.5 | Alexandria | Wind | RCP8.5 | 2040 | 77.7005 | 83.6219 | 89.835 | 96.0689 | 102.2956
| AlexandriaWind2045RCP8.5 | Alexandria | Wind | RCP8.5 | 2045 | 77.5943 | 83.5019 | 89.697 | 95.9148 | 102.1246
| AlexandriaWind2050RCP8.5 | Alexandria | Wind | RCP8.5 | 2050 | 77.3741 | 83.2508 | 89.409 | 95.5938 | 101.7724
| AlexandriaWind2055RCP8.5 | Alexandria | Wind | RCP8.5 | 2055 | 77.2601 | 83.1197 | 89.259 | 95.4269 | 101.5911
| AlexandriaWind2060RCP8.5 | Alexandria | Wind | RCP8.5 | 2060 | 77.1098 | 82.9607 | 89.091 | 95.2503 | 101.4064
| AlexandriaWind2065RCP8.5 | Alexandria | Wind | RCP8.5 | 2065 | 77.0736 | 82.9328 | 89.073 | 95.2407 | 101.403
| AlexandriaWind2070RCP8.5 | Alexandria | Wind | RCP8.5 | 2070 | 77.1073 | 82.9941 | 89.166 | 95.3627 | 101.5501
| AlexandriaWind2075RCP8.5 | Alexandria | Wind | RCP8.5 | 2075 | 77.1772 | 83.0834 | 89.277 | 95.4943 | 101.7005
| AlexandriaWind2080RCP8.5 | Alexandria | Wind | RCP8.5 | 2080 | 77.2471 | 83.1727 | 89.388 | 95.6259 | 101.851
| AlexandriaWind2085RCP8.5 | Alexandria | Wind | RCP8.5 | 2085 | 77.2277 | 83.1518 | 89.3745 | 95.6115 | 101.8408
| AlexandriaWind2090RCP8.5 | Alexandria | Wind | RCP8.5 | 2090 | 77.2083 | 83.1308 | 89.361 | 95.597 | 101.8305
| AlexandriaWind2095RCP8.5 | Alexandria | Wind | RCP8.5 | 2095 | 77.2083 | 83.1308 | 89.361 | 95.597 | 101.8305
| AlexandriaWind2100RCP8.5 | Alexandria | Wind | RCP8.5 | 2100 | 77.2083 | 83.1308 | 89.361 | 95.597 | 101.8305
| AllistonIce Accretion2023RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2023 | 15.9885 | 19.1854 | 23.23 | 26.3279 | 29.4147
| AllistonIce Accretion2025RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2025 | 16.0285 | 19.2491 | 23.3258 | 26.4448 | 29.5548
| AllistonIce Accretion2030RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2030 | 16.0685 | 19.3127 | 23.4217 | 26.5618 | 29.6948
| AllistonIce Accretion2035RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2035 | 16.1085 | 19.3763 | 23.5175 | 26.6787 | 29.8349
| AllistonIce Accretion2040RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2040 | 16.1485 | 19.44 | 23.6133 | 26.7957 | 29.975
| AllistonIce Accretion2045RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2045 | 16.1885 | 19.5036 | 23.7092 | 26.9126 | 30.1151
| AllistonIce Accretion2050RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2050 | 16.1197 | 19.4565 | 23.6854 | 26.9048 | 30.1218
| AllistonIce Accretion2055RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2055 | 16.0109 | 19.3458 | 23.5658 | 26.7801 | 29.9885
| AllistonIce Accretion2060RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2060 | 15.902 | 19.2351 | 23.4462 | 26.6553 | 29.8552
| AllistonIce Accretion2065RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2065 | 15.7932 | 19.1244 | 23.3266 | 26.5306 | 29.7219
| AllistonIce Accretion2070RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2070 | 15.6844 | 19.0136 | 23.207 | 26.4058 | 29.5886
| AllistonIce Accretion2075RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2075 | 15.6497 | 18.9977 | 23.2147 | 26.4275 | 29.6272
| AllistonIce Accretion2080RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2080 | 15.615 | 18.9818 | 23.2223 | 26.4492 | 29.6659
| AllistonIce Accretion2085RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2085 | 15.5803 | 18.9659 | 23.23 | 26.4708 | 29.7045
| AllistonIce Accretion2090RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2090 | 15.5457 | 18.95 | 23.2377 | 26.4925 | 29.7431
| AllistonIce Accretion2095RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2095 | 15.511 | 18.9341 | 23.2453 | 26.5141 | 29.7818
| AllistonIce Accretion2100RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2100 | 15.4763 | 18.9182 | 23.253 | 26.5358 | 29.8204
| AllistonIce Accretion2023RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2023 | 15.9885 | 19.1854 | 23.23 | 26.3279 | 29.4147
| AllistonIce Accretion2025RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2025 | 16.0285 | 19.2491 | 23.3258 | 26.4448 | 29.5548
| AllistonIce Accretion2030RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2030 | 16.0685 | 19.3127 | 23.4217 | 26.5618 | 29.6948
| AllistonIce Accretion2035RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2035 | 16.1085 | 19.3763 | 23.5175 | 26.6787 | 29.8349
| AllistonIce Accretion2040RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2040 | 16.1485 | 19.44 | 23.6133 | 26.7957 | 29.975
| AllistonIce Accretion2045RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2045 | 16.1885 | 19.5036 | 23.7092 | 26.9126 | 30.1151
| AllistonIce Accretion2050RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2050 | 16.1197 | 19.4565 | 23.6854 | 26.9048 | 30.1218
| AllistonIce Accretion2055RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2055 | 16.0109 | 19.3458 | 23.5658 | 26.7801 | 29.9885
| AllistonIce Accretion2060RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2060 | 15.902 | 19.2351 | 23.4462 | 26.6553 | 29.8552
| AllistonIce Accretion2065RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2065 | 15.7932 | 19.1244 | 23.3266 | 26.5306 | 29.7219
| AllistonIce Accretion2070RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2070 | 15.6844 | 19.0136 | 23.207 | 26.4058 | 29.5886
| AllistonIce Accretion2075RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2075 | 15.6324 | 18.9898 | 23.2185 | 26.4383 | 29.6465
| AllistonIce Accretion2080RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2080 | 15.5803 | 18.9659 | 23.23 | 26.4708 | 29.7045
| AllistonIce Accretion2085RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2085 | 15.5283 | 18.9421 | 23.2415 | 26.5033 | 29.7625
| AllistonIce Accretion2090RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2090 | 15.1936 | 18.6191 | 22.931 | 26.2066 | 29.4727
| AllistonIce Accretion2095RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2095 | 14.9108 | 18.32 | 22.609 | 25.8774 | 29.1249
| AllistonIce Accretion2100RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2100 | 14.6281 | 18.021 | 22.287 | 25.5482 | 28.7771
| AllistonIce Accretion2023RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2023 | 15.9885 | 19.1854 | 23.23 | 26.3279 | 29.4147
| AllistonIce Accretion2025RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2025 | 16.0685 | 19.3127 | 23.4217 | 26.5618 | 29.6948
| AllistonIce Accretion2030RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2030 | 16.1485 | 19.44 | 23.6133 | 26.7957 | 29.975
| AllistonIce Accretion2035RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2035 | 16.2285 | 19.5672 | 23.805 | 27.0296 | 30.2551
| AllistonIce Accretion2040RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2040 | 16.0471 | 19.3827 | 23.6057 | 26.8217 | 30.0329
| AllistonIce Accretion2045RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2045 | 15.8658 | 19.1982 | 23.4063 | 26.6138 | 29.8108
| AllistonIce Accretion2050RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2050 | 15.615 | 18.9818 | 23.2223 | 26.4492 | 29.6659
| AllistonIce Accretion2055RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2055 | 15.5457 | 18.95 | 23.2377 | 26.4925 | 29.7431
| AllistonIce Accretion2060RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2060 | 15.1936 | 18.6191 | 22.931 | 26.2066 | 29.4727
| AllistonIce Accretion2065RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2065 | 14.9108 | 18.32 | 22.609 | 25.8774 | 29.1249
| AllistonIce Accretion2070RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2070 | 14.2706 | 17.6392 | 21.873 | 25.0977 | 28.3038
| AllistonIce Accretion2075RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2075 | 13.9132 | 17.2574 | 21.459 | 24.6472 | 27.8305
| AllistonIce Accretion2080RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2080 | 13.5558 | 16.8756 | 21.045 | 24.1967 | 27.3571
| AllistonIce Accretion2085RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2085 | 12.8516 | 16.0451 | 20.056 | 23.0921 | 26.1255
| AllistonIce Accretion2090RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2090 | 12.1474 | 15.2147 | 19.067 | 21.9875 | 24.8938
| AllistonIce Accretion2095RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2095 | 12.1474 | 15.2147 | 19.067 | 21.9875 | 24.8938
| AllistonIce Accretion2100RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2100 | 12.1474 | 15.2147 | 19.067 | 21.9875 | 24.8938
| AllistonWind2023RCP4.5 | Alliston | Wind | RCP4.5 | 2023 | 78.001 | 84.0097 | 90.333 | 96.6563 | 102.9796
| AllistonWind2025RCP4.5 | Alliston | Wind | RCP4.5 | 2025 | 78.0256 | 84.0446 | 90.381 | 96.7157 | 103.0514
| AllistonWind2030RCP4.5 | Alliston | Wind | RCP4.5 | 2030 | 78.0502 | 84.0794 | 90.429 | 96.7751 | 103.1233
| AllistonWind2035RCP4.5 | Alliston | Wind | RCP4.5 | 2035 | 78.0748 | 84.1143 | 90.477 | 96.8345 | 103.1951
| AllistonWind2040RCP4.5 | Alliston | Wind | RCP4.5 | 2040 | 78.0994 | 84.1492 | 90.525 | 96.8939 | 103.2669
| AllistonWind2045RCP4.5 | Alliston | Wind | RCP4.5 | 2045 | 78.124 | 84.1841 | 90.573 | 96.9532 | 103.3387
| AllistonWind2050RCP4.5 | Alliston | Wind | RCP4.5 | 2050 | 78.1999 | 84.2675 | 90.666 | 97.055 | 103.4495
| AllistonWind2055RCP4.5 | Alliston | Wind | RCP4.5 | 2055 | 78.2512 | 84.316 | 90.711 | 97.0974 | 103.4885
| AllistonWind2060RCP4.5 | Alliston | Wind | RCP4.5 | 2060 | 78.3025 | 84.3646 | 90.756 | 97.1397 | 103.5275
| AllistonWind2065RCP4.5 | Alliston | Wind | RCP4.5 | 2065 | 78.3538 | 84.4131 | 90.801 | 97.1821 | 103.5665
| AllistonWind2070RCP4.5 | Alliston | Wind | RCP4.5 | 2070 | 78.4051 | 84.4617 | 90.846 | 97.2245 | 103.6055
| AllistonWind2075RCP4.5 | Alliston | Wind | RCP4.5 | 2075 | 78.4802 | 84.5649 | 90.984 | 97.3914 | 103.8021
| AllistonWind2080RCP4.5 | Alliston | Wind | RCP4.5 | 2080 | 78.5553 | 84.6681 | 91.122 | 97.5583 | 103.9988
| AllistonWind2085RCP4.5 | Alliston | Wind | RCP4.5 | 2085 | 78.6304 | 84.7714 | 91.26 | 97.7252 | 104.1954
| AllistonWind2090RCP4.5 | Alliston | Wind | RCP4.5 | 2090 | 78.7056 | 84.8746 | 91.398 | 97.8922 | 104.3921
| AllistonWind2095RCP4.5 | Alliston | Wind | RCP4.5 | 2095 | 78.7807 | 84.9778 | 91.536 | 98.0591 | 104.5887
| AllistonWind2100RCP4.5 | Alliston | Wind | RCP4.5 | 2100 | 78.8558 | 85.0811 | 91.674 | 98.226 | 104.7854
| AllistonWind2023RCP6.0 | Alliston | Wind | RCP6.0 | 2023 | 78.001 | 84.0097 | 90.333 | 96.6563 | 102.9796
| AllistonWind2025RCP6.0 | Alliston | Wind | RCP6.0 | 2025 | 78.0256 | 84.0446 | 90.381 | 96.7157 | 103.0514
| AllistonWind2030RCP6.0 | Alliston | Wind | RCP6.0 | 2030 | 78.0502 | 84.0794 | 90.429 | 96.7751 | 103.1233
| AllistonWind2035RCP6.0 | Alliston | Wind | RCP6.0 | 2035 | 78.0748 | 84.1143 | 90.477 | 96.8345 | 103.1951
| AllistonWind2040RCP6.0 | Alliston | Wind | RCP6.0 | 2040 | 78.0994 | 84.1492 | 90.525 | 96.8939 | 103.2669
| AllistonWind2045RCP6.0 | Alliston | Wind | RCP6.0 | 2045 | 78.124 | 84.1841 | 90.573 | 96.9532 | 103.3387
| AllistonWind2050RCP6.0 | Alliston | Wind | RCP6.0 | 2050 | 78.1999 | 84.2675 | 90.666 | 97.055 | 103.4495
| AllistonWind2055RCP6.0 | Alliston | Wind | RCP6.0 | 2055 | 78.2512 | 84.316 | 90.711 | 97.0974 | 103.4885
| AllistonWind2060RCP6.0 | Alliston | Wind | RCP6.0 | 2060 | 78.3025 | 84.3646 | 90.756 | 97.1397 | 103.5275
| AllistonWind2065RCP6.0 | Alliston | Wind | RCP6.0 | 2065 | 78.3538 | 84.4131 | 90.801 | 97.1821 | 103.5665
| AllistonWind2070RCP6.0 | Alliston | Wind | RCP6.0 | 2070 | 78.4051 | 84.4617 | 90.846 | 97.2245 | 103.6055
| AllistonWind2075RCP6.0 | Alliston | Wind | RCP6.0 | 2075 | 78.5178 | 84.6165 | 91.053 | 97.4749 | 103.9005
| AllistonWind2080RCP6.0 | Alliston | Wind | RCP6.0 | 2080 | 78.6304 | 84.7714 | 91.26 | 97.7252 | 104.1954
| AllistonWind2085RCP6.0 | Alliston | Wind | RCP6.0 | 2085 | 78.7431 | 84.9262 | 91.467 | 97.9756 | 104.4904
| AllistonWind2090RCP6.0 | Alliston | Wind | RCP6.0 | 2090 | 79.1174 | 85.4047 | 92.073 | 98.6915 | 105.3189
| AllistonWind2095RCP6.0 | Alliston | Wind | RCP6.0 | 2095 | 79.3791 | 85.7283 | 92.472 | 99.1569 | 105.8524
| AllistonWind2100RCP6.0 | Alliston | Wind | RCP6.0 | 2100 | 79.6407 | 86.052 | 92.871 | 99.6224 | 106.3859
| AllistonWind2023RCP8.5 | Alliston | Wind | RCP8.5 | 2023 | 78.001 | 84.0097 | 90.333 | 96.6563 | 102.9796
| AllistonWind2025RCP8.5 | Alliston | Wind | RCP8.5 | 2025 | 78.0502 | 84.0794 | 90.429 | 96.7751 | 103.1233
| AllistonWind2030RCP8.5 | Alliston | Wind | RCP8.5 | 2030 | 78.0994 | 84.1492 | 90.525 | 96.8939 | 103.2669
| AllistonWind2035RCP8.5 | Alliston | Wind | RCP8.5 | 2035 | 78.1486 | 84.2189 | 90.621 | 97.0126 | 103.4105
| AllistonWind2040RCP8.5 | Alliston | Wind | RCP8.5 | 2040 | 78.2341 | 84.2999 | 90.696 | 97.0832 | 103.4755
| AllistonWind2045RCP8.5 | Alliston | Wind | RCP8.5 | 2045 | 78.3196 | 84.3808 | 90.771 | 97.1539 | 103.5405
| AllistonWind2050RCP8.5 | Alliston | Wind | RCP8.5 | 2050 | 78.5553 | 84.6681 | 91.122 | 97.5583 | 103.9988
| AllistonWind2055RCP8.5 | Alliston | Wind | RCP8.5 | 2055 | 78.7056 | 84.8746 | 91.398 | 97.8922 | 104.3921
| AllistonWind2060RCP8.5 | Alliston | Wind | RCP8.5 | 2060 | 79.1174 | 85.4047 | 92.073 | 98.6915 | 105.3189
| AllistonWind2065RCP8.5 | Alliston | Wind | RCP8.5 | 2065 | 79.3791 | 85.7283 | 92.472 | 99.1569 | 105.8524
| AllistonWind2070RCP8.5 | Alliston | Wind | RCP8.5 | 2070 | 79.8402 | 86.3198 | 93.225 | 100.0493 | 106.8853
| AllistonWind2075RCP8.5 | Alliston | Wind | RCP8.5 | 2075 | 80.0396 | 86.5876 | 93.579 | 100.4762 | 107.3846
| AllistonWind2080RCP8.5 | Alliston | Wind | RCP8.5 | 2080 | 80.2391 | 86.8555 | 93.933 | 100.9031 | 107.8839
| AllistonWind2085RCP8.5 | Alliston | Wind | RCP8.5 | 2085 | 80.3401 | 86.9894 | 94.113 | 101.115 | 108.1353
| AllistonWind2090RCP8.5 | Alliston | Wind | RCP8.5 | 2090 | 80.4412 | 87.1233 | 94.293 | 101.3269 | 108.3866
| AllistonWind2095RCP8.5 | Alliston | Wind | RCP8.5 | 2095 | 80.4412 | 87.1233 | 94.293 | 101.3269 | 108.3866
| AllistonWind2100RCP8.5 | Alliston | Wind | RCP8.5 | 2100 | 80.4412 | 87.1233 | 94.293 | 101.3269 | 108.3866
| AlmonteIce Accretion2023RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2023 | 17.9473 | 21.3426 | 25.636 | 28.9393 | 32.2358
| AlmonteIce Accretion2025RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2025 | 17.9412 | 21.339 | 25.6403 | 28.9491 | 32.2468
| AlmonteIce Accretion2030RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2030 | 17.9352 | 21.3354 | 25.6447 | 28.9589 | 32.2577
| AlmonteIce Accretion2035RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2035 | 17.9292 | 21.3318 | 25.649 | 28.9687 | 32.2686
| AlmonteIce Accretion2040RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2040 | 17.9231 | 21.3282 | 25.6533 | 28.9785 | 32.2795
| AlmonteIce Accretion2045RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2045 | 17.9171 | 21.3246 | 25.6577 | 28.9883 | 32.2904
| AlmonteIce Accretion2050RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2050 | 17.9147 | 21.3426 | 25.7036 | 29.0568 | 32.3734
| AlmonteIce Accretion2055RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2055 | 17.9183 | 21.3642 | 25.7452 | 29.1156 | 32.4455
| AlmonteIce Accretion2060RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2060 | 17.9219 | 21.3858 | 25.7868 | 29.1743 | 32.5176
| AlmonteIce Accretion2065RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2065 | 17.9256 | 21.4074 | 25.8284 | 29.2331 | 32.5896
| AlmonteIce Accretion2070RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2070 | 17.9292 | 21.4289 | 25.87 | 29.2919 | 32.6617
| AlmonteIce Accretion2075RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2075 | 18.0106 | 21.5476 | 26.0347 | 29.4877 | 32.8965
| AlmonteIce Accretion2080RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2080 | 18.092 | 21.6663 | 26.1993 | 29.6836 | 33.1313
| AlmonteIce Accretion2085RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2085 | 18.1734 | 21.785 | 26.364 | 29.8795 | 33.3661
| AlmonteIce Accretion2090RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2090 | 18.2548 | 21.9037 | 26.5287 | 30.0753 | 33.6008
| AlmonteIce Accretion2095RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2095 | 18.3362 | 22.0224 | 26.6933 | 30.2712 | 33.8356
| AlmonteIce Accretion2100RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2100 | 18.4177 | 22.1411 | 26.858 | 30.4671 | 34.0704
| AlmonteIce Accretion2023RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2023 | 17.9473 | 21.3426 | 25.636 | 28.9393 | 32.2358
| AlmonteIce Accretion2025RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2025 | 17.9412 | 21.339 | 25.6403 | 28.9491 | 32.2468
| AlmonteIce Accretion2030RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2030 | 17.9352 | 21.3354 | 25.6447 | 28.9589 | 32.2577
| AlmonteIce Accretion2035RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2035 | 17.9292 | 21.3318 | 25.649 | 28.9687 | 32.2686
| AlmonteIce Accretion2040RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2040 | 17.9231 | 21.3282 | 25.6533 | 28.9785 | 32.2795
| AlmonteIce Accretion2045RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2045 | 17.9171 | 21.3246 | 25.6577 | 28.9883 | 32.2904
| AlmonteIce Accretion2050RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2050 | 17.9147 | 21.3426 | 25.7036 | 29.0568 | 32.3734
| AlmonteIce Accretion2055RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2055 | 17.9183 | 21.3642 | 25.7452 | 29.1156 | 32.4455
| AlmonteIce Accretion2060RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2060 | 17.9219 | 21.3858 | 25.7868 | 29.1743 | 32.5176
| AlmonteIce Accretion2065RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2065 | 17.9256 | 21.4074 | 25.8284 | 29.2331 | 32.5896
| AlmonteIce Accretion2070RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2070 | 17.9292 | 21.4289 | 25.87 | 29.2919 | 32.6617
| AlmonteIce Accretion2075RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2075 | 18.0513 | 21.607 | 26.117 | 29.5857 | 33.0139
| AlmonteIce Accretion2080RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2080 | 18.1734 | 21.785 | 26.364 | 29.8795 | 33.3661
| AlmonteIce Accretion2085RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2085 | 18.2955 | 21.963 | 26.611 | 30.1733 | 33.7182
| AlmonteIce Accretion2090RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2090 | 18.4056 | 22.1627 | 26.9273 | 30.5552 | 34.1905
| AlmonteIce Accretion2095RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2095 | 18.3935 | 22.1842 | 26.9967 | 30.6433 | 34.3106
| AlmonteIce Accretion2100RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2100 | 18.3815 | 22.2058 | 27.066 | 30.7315 | 34.4308
| AlmonteIce Accretion2023RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2023 | 17.9473 | 21.3426 | 25.636 | 28.9393 | 32.2358
| AlmonteIce Accretion2025RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2025 | 17.9352 | 21.3354 | 25.6447 | 28.9589 | 32.2577
| AlmonteIce Accretion2030RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2030 | 17.9231 | 21.3282 | 25.6533 | 28.9785 | 32.2795
| AlmonteIce Accretion2035RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2035 | 17.9111 | 21.321 | 25.662 | 28.9981 | 32.3014
| AlmonteIce Accretion2040RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2040 | 17.9171 | 21.357 | 25.7313 | 29.096 | 32.4215
| AlmonteIce Accretion2045RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2045 | 17.9231 | 21.393 | 25.8007 | 29.1939 | 32.5416
| AlmonteIce Accretion2050RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2050 | 18.092 | 21.6663 | 26.1993 | 29.6836 | 33.1313
| AlmonteIce Accretion2055RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2055 | 18.2548 | 21.9037 | 26.5287 | 30.0753 | 33.6008
| AlmonteIce Accretion2060RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2060 | 18.4056 | 22.1627 | 26.9273 | 30.5552 | 34.1905
| AlmonteIce Accretion2065RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2065 | 18.3935 | 22.1842 | 26.9967 | 30.6433 | 34.3106
| AlmonteIce Accretion2070RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2070 | 18.1885 | 22.0044 | 26.8493 | 30.5062 | 34.1905
| AlmonteIce Accretion2075RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2075 | 17.9955 | 21.803 | 26.6327 | 30.281 | 33.9503
| AlmonteIce Accretion2080RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2080 | 17.8025 | 21.6016 | 26.416 | 30.0557 | 33.71
| AlmonteIce Accretion2085RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2085 | 17.0608 | 20.7492 | 25.415 | 28.954 | 32.4979
| AlmonteIce Accretion2090RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2090 | 16.319 | 19.8968 | 24.414 | 27.8522 | 31.2858
| AlmonteIce Accretion2095RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2095 | 16.319 | 19.8968 | 24.414 | 27.8522 | 31.2858
| AlmonteIce Accretion2100RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2100 | 16.319 | 19.8968 | 24.414 | 27.8522 | 31.2858
| AlmonteWind2023RCP4.5 | Almonte | Wind | RCP4.5 | 2023 | 74.8164 | 80.6518 | 86.8084 | 92.9402 | 99.0792
| AlmonteWind2025RCP4.5 | Almonte | Wind | RCP4.5 | 2025 | 74.9241 | 80.7811 | 86.9646 | 93.1212 | 99.2851
| AlmonteWind2030RCP4.5 | Almonte | Wind | RCP4.5 | 2030 | 75.0318 | 80.9104 | 87.1209 | 93.3021 | 99.491
| AlmonteWind2035RCP4.5 | Almonte | Wind | RCP4.5 | 2035 | 75.1395 | 81.0397 | 87.2771 | 93.4831 | 99.6969
| AlmonteWind2040RCP4.5 | Almonte | Wind | RCP4.5 | 2040 | 75.2471 | 81.169 | 87.4333 | 93.6641 | 99.9028
| AlmonteWind2045RCP4.5 | Almonte | Wind | RCP4.5 | 2045 | 75.3548 | 81.2983 | 87.5896 | 93.8451 | 100.1086
| AlmonteWind2050RCP4.5 | Almonte | Wind | RCP4.5 | 2050 | 75.4476 | 81.4052 | 87.7148 | 93.9874 | 100.2675
| AlmonteWind2055RCP4.5 | Almonte | Wind | RCP4.5 | 2055 | 75.4328 | 81.3828 | 87.6839 | 93.9487 | 100.2204
| AlmonteWind2060RCP4.5 | Almonte | Wind | RCP4.5 | 2060 | 75.4179 | 81.3605 | 87.6529 | 93.9101 | 100.1734
| AlmonteWind2065RCP4.5 | Almonte | Wind | RCP4.5 | 2065 | 75.4031 | 81.3381 | 87.622 | 93.8714 | 100.1263
| AlmonteWind2070RCP4.5 | Almonte | Wind | RCP4.5 | 2070 | 75.3882 | 81.3157 | 87.591 | 93.8328 | 100.0792
| AlmonteWind2075RCP4.5 | Almonte | Wind | RCP4.5 | 2075 | 75.4155 | 81.3517 | 87.6397 | 93.8911 | 100.1462
| AlmonteWind2080RCP4.5 | Almonte | Wind | RCP4.5 | 2080 | 75.4427 | 81.3876 | 87.6885 | 93.9494 | 100.2132
| AlmonteWind2085RCP4.5 | Almonte | Wind | RCP4.5 | 2085 | 75.4699 | 81.4236 | 87.7372 | 94.0076 | 100.2802
| AlmonteWind2090RCP4.5 | Almonte | Wind | RCP4.5 | 2090 | 75.4971 | 81.4596 | 87.7859 | 94.0659 | 100.3472
| AlmonteWind2095RCP4.5 | Almonte | Wind | RCP4.5 | 2095 | 75.5244 | 81.4956 | 87.8347 | 94.1242 | 100.4142
| AlmonteWind2100RCP4.5 | Almonte | Wind | RCP4.5 | 2100 | 75.5516 | 81.5316 | 87.8834 | 94.1825 | 100.4812
| AlmonteWind2023RCP6.0 | Almonte | Wind | RCP6.0 | 2023 | 74.8164 | 80.6518 | 86.8084 | 92.9402 | 99.0792
| AlmonteWind2025RCP6.0 | Almonte | Wind | RCP6.0 | 2025 | 74.9241 | 80.7811 | 86.9646 | 93.1212 | 99.2851
| AlmonteWind2030RCP6.0 | Almonte | Wind | RCP6.0 | 2030 | 75.0318 | 80.9104 | 87.1209 | 93.3021 | 99.491
| AlmonteWind2035RCP6.0 | Almonte | Wind | RCP6.0 | 2035 | 75.1395 | 81.0397 | 87.2771 | 93.4831 | 99.6969
| AlmonteWind2040RCP6.0 | Almonte | Wind | RCP6.0 | 2040 | 75.2471 | 81.169 | 87.4333 | 93.6641 | 99.9028
| AlmonteWind2045RCP6.0 | Almonte | Wind | RCP6.0 | 2045 | 75.3548 | 81.2983 | 87.5896 | 93.8451 | 100.1086
| AlmonteWind2050RCP6.0 | Almonte | Wind | RCP6.0 | 2050 | 75.4476 | 81.4052 | 87.7148 | 93.9874 | 100.2675
| AlmonteWind2055RCP6.0 | Almonte | Wind | RCP6.0 | 2055 | 75.4328 | 81.3828 | 87.6839 | 93.9487 | 100.2204
| AlmonteWind2060RCP6.0 | Almonte | Wind | RCP6.0 | 2060 | 75.4179 | 81.3605 | 87.6529 | 93.9101 | 100.1734
| AlmonteWind2065RCP6.0 | Almonte | Wind | RCP6.0 | 2065 | 75.4031 | 81.3381 | 87.622 | 93.8714 | 100.1263
| AlmonteWind2070RCP6.0 | Almonte | Wind | RCP6.0 | 2070 | 75.3882 | 81.3157 | 87.591 | 93.8328 | 100.0792
| AlmonteWind2075RCP6.0 | Almonte | Wind | RCP6.0 | 2075 | 75.4291 | 81.3697 | 87.6641 | 93.9202 | 100.1797
| AlmonteWind2080RCP6.0 | Almonte | Wind | RCP6.0 | 2080 | 75.4699 | 81.4236 | 87.7372 | 94.0076 | 100.2802
| AlmonteWind2085RCP6.0 | Almonte | Wind | RCP6.0 | 2085 | 75.5108 | 81.4776 | 87.8103 | 94.0951 | 100.3807
| AlmonteWind2090RCP6.0 | Almonte | Wind | RCP6.0 | 2090 | 75.4971 | 81.449 | 87.7573 | 94.026 | 100.2917
| AlmonteWind2095RCP6.0 | Almonte | Wind | RCP6.0 | 2095 | 75.4427 | 81.3663 | 87.6311 | 93.8696 | 100.1021
| AlmonteWind2100RCP6.0 | Almonte | Wind | RCP6.0 | 2100 | 75.3882 | 81.2837 | 87.505 | 93.7132 | 99.9126
| AlmonteWind2023RCP8.5 | Almonte | Wind | RCP8.5 | 2023 | 74.8164 | 80.6518 | 86.8084 | 92.9402 | 99.0792
| AlmonteWind2025RCP8.5 | Almonte | Wind | RCP8.5 | 2025 | 75.0318 | 80.9104 | 87.1209 | 93.3021 | 99.491
| AlmonteWind2030RCP8.5 | Almonte | Wind | RCP8.5 | 2030 | 75.2471 | 81.169 | 87.4333 | 93.6641 | 99.9028
| AlmonteWind2035RCP8.5 | Almonte | Wind | RCP8.5 | 2035 | 75.4625 | 81.4276 | 87.7458 | 94.026 | 100.3145
| AlmonteWind2040RCP8.5 | Almonte | Wind | RCP8.5 | 2040 | 75.4377 | 81.3903 | 87.6942 | 93.9616 | 100.2361
| AlmonteWind2045RCP8.5 | Almonte | Wind | RCP8.5 | 2045 | 75.413 | 81.353 | 87.6426 | 93.8972 | 100.1577
| AlmonteWind2050RCP8.5 | Almonte | Wind | RCP8.5 | 2050 | 75.4427 | 81.3876 | 87.6885 | 93.9494 | 100.2132
| AlmonteWind2055RCP8.5 | Almonte | Wind | RCP8.5 | 2055 | 75.4971 | 81.4596 | 87.7859 | 94.0659 | 100.3472
| AlmonteWind2060RCP8.5 | Almonte | Wind | RCP8.5 | 2060 | 75.4971 | 81.449 | 87.7573 | 94.026 | 100.2917
| AlmonteWind2065RCP8.5 | Almonte | Wind | RCP8.5 | 2065 | 75.4427 | 81.3663 | 87.6311 | 93.8696 | 100.1021
| AlmonteWind2070RCP8.5 | Almonte | Wind | RCP8.5 | 2070 | 75.4204 | 81.313 | 87.5308 | 93.7377 | 99.9354
| AlmonteWind2075RCP8.5 | Almonte | Wind | RCP8.5 | 2075 | 75.4526 | 81.3423 | 87.5566 | 93.7622 | 99.9583
| AlmonteWind2080RCP8.5 | Almonte | Wind | RCP8.5 | 2080 | 75.4848 | 81.3717 | 87.5824 | 93.7868 | 99.9812
| AlmonteWind2085RCP8.5 | Almonte | Wind | RCP8.5 | 2085 | 75.5108 | 81.4116 | 87.6383 | 93.8512 | 100.0596
| AlmonteWind2090RCP8.5 | Almonte | Wind | RCP8.5 | 2090 | 75.5368 | 81.4516 | 87.6942 | 93.9156 | 100.1381
| AlmonteWind2095RCP8.5 | Almonte | Wind | RCP8.5 | 2095 | 75.5368 | 81.4516 | 87.6942 | 93.9156 | 100.1381
| AlmonteWind2100RCP8.5 | Almonte | Wind | RCP8.5 | 2100 | 75.5368 | 81.4516 | 87.6942 | 93.9156 | 100.1381
| ArmstrongIce Accretion2023RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2023 | 9.2721 | 11.0382 | 13.299 | 15.0132 | 16.7404
| ArmstrongIce Accretion2025RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2025 | 9.3867 | 11.1694 | 13.4463 | 15.1772 | 16.9205
| ArmstrongIce Accretion2030RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2030 | 9.5013 | 11.3007 | 13.5937 | 15.3413 | 17.1007
| ArmstrongIce Accretion2035RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2035 | 9.6159 | 11.432 | 13.741 | 15.5053 | 17.2809
| ArmstrongIce Accretion2040RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2040 | 9.7305 | 11.5633 | 13.8883 | 15.6693 | 17.4611
| ArmstrongIce Accretion2045RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2045 | 9.8451 | 11.6946 | 14.0357 | 15.8334 | 17.6413
| ArmstrongIce Accretion2050RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2050 | 9.9741 | 11.8409 | 14.2012 | 16.018 | 17.8411
| ArmstrongIce Accretion2055RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2055 | 9.9886 | 11.8561 | 14.2194 | 16.0385 | 17.8608
| ArmstrongIce Accretion2060RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2060 | 10.0031 | 11.8712 | 14.2376 | 16.0591 | 17.8804
| ArmstrongIce Accretion2065RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2065 | 10.0175 | 11.8863 | 14.2558 | 16.0797 | 17.9001
| ArmstrongIce Accretion2070RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2070 | 10.032 | 11.9014 | 14.274 | 16.1002 | 17.9197
| ArmstrongIce Accretion2075RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2075 | 10.0471 | 11.9212 | 14.2978 | 16.1272 | 17.9525
| ArmstrongIce Accretion2080RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2080 | 10.0622 | 11.9409 | 14.3217 | 16.1541 | 17.9852
| ArmstrongIce Accretion2085RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2085 | 10.0772 | 11.9607 | 14.3455 | 16.181 | 18.018
| ArmstrongIce Accretion2090RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2090 | 10.0923 | 11.9805 | 14.3693 | 16.208 | 18.0508
| ArmstrongIce Accretion2095RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2095 | 10.1074 | 12.0003 | 14.3932 | 16.2349 | 18.0835
| ArmstrongIce Accretion2100RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2100 | 10.1225 | 12.0201 | 14.417 | 16.2618 | 18.1163
| ArmstrongIce Accretion2023RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2023 | 9.2721 | 11.0382 | 13.299 | 15.0132 | 16.7404
| ArmstrongIce Accretion2025RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2025 | 9.3867 | 11.1694 | 13.4463 | 15.1772 | 16.9205
| ArmstrongIce Accretion2030RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2030 | 9.5013 | 11.3007 | 13.5937 | 15.3413 | 17.1007
| ArmstrongIce Accretion2035RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2035 | 9.6159 | 11.432 | 13.741 | 15.5053 | 17.2809
| ArmstrongIce Accretion2040RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2040 | 9.7305 | 11.5633 | 13.8883 | 15.6693 | 17.4611
| ArmstrongIce Accretion2045RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2045 | 9.8451 | 11.6946 | 14.0357 | 15.8334 | 17.6413
| ArmstrongIce Accretion2050RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2050 | 9.9741 | 11.8409 | 14.2012 | 16.018 | 17.8411
| ArmstrongIce Accretion2055RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2055 | 9.9886 | 11.8561 | 14.2194 | 16.0385 | 17.8608
| ArmstrongIce Accretion2060RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2060 | 10.0031 | 11.8712 | 14.2376 | 16.0591 | 17.8804
| ArmstrongIce Accretion2065RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2065 | 10.0175 | 11.8863 | 14.2558 | 16.0797 | 17.9001
| ArmstrongIce Accretion2070RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2070 | 10.032 | 11.9014 | 14.274 | 16.1002 | 17.9197
| ArmstrongIce Accretion2075RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2075 | 10.0546 | 11.931 | 14.3098 | 16.1406 | 17.9689
| ArmstrongIce Accretion2080RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2080 | 10.0772 | 11.9607 | 14.3455 | 16.181 | 18.018
| ArmstrongIce Accretion2085RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2085 | 10.0999 | 11.9904 | 14.3812 | 16.2214 | 18.0671
| ArmstrongIce Accretion2090RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2090 | 10.0863 | 11.9913 | 14.3953 | 16.2471 | 18.0999
| ArmstrongIce Accretion2095RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2095 | 10.0501 | 11.9625 | 14.3737 | 16.2324 | 18.0835
| ArmstrongIce Accretion2100RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2100 | 10.0139 | 11.9337 | 14.352 | 16.2178 | 18.0671
| ArmstrongIce Accretion2023RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2023 | 9.2721 | 11.0382 | 13.299 | 15.0132 | 16.7404
| ArmstrongIce Accretion2025RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2025 | 9.5013 | 11.3007 | 13.5937 | 15.3413 | 17.1007
| ArmstrongIce Accretion2030RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2030 | 9.7305 | 11.5633 | 13.8883 | 15.6693 | 17.4611
| ArmstrongIce Accretion2035RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2035 | 9.9596 | 11.8258 | 14.183 | 15.9974 | 17.8214
| ArmstrongIce Accretion2040RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2040 | 9.9838 | 11.851 | 14.2133 | 16.0317 | 17.8542
| ArmstrongIce Accretion2045RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2045 | 10.0079 | 11.8762 | 14.2437 | 16.066 | 17.887
| ArmstrongIce Accretion2050RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2050 | 10.0622 | 11.9409 | 14.3217 | 16.1541 | 17.9852
| ArmstrongIce Accretion2055RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2055 | 10.0923 | 11.9805 | 14.3693 | 16.208 | 18.0508
| ArmstrongIce Accretion2060RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2060 | 10.0863 | 11.9913 | 14.3953 | 16.2471 | 18.0999
| ArmstrongIce Accretion2065RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2065 | 10.0501 | 11.9625 | 14.3737 | 16.2324 | 18.0835
| ArmstrongIce Accretion2070RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2070 | 10.0772 | 12.0129 | 14.4603 | 16.3402 | 18.2091
| ArmstrongIce Accretion2075RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2075 | 10.1406 | 12.092 | 14.5687 | 16.4626 | 18.3511
| ArmstrongIce Accretion2080RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2080 | 10.2039 | 12.1711 | 14.677 | 16.585 | 18.493
| ArmstrongIce Accretion2085RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2085 | 10.0184 | 11.9661 | 14.4365 | 16.3206 | 18.1982
| ArmstrongIce Accretion2090RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2090 | 9.833 | 11.7611 | 14.196 | 16.0562 | 17.9033
| ArmstrongIce Accretion2095RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2095 | 9.833 | 11.7611 | 14.196 | 16.0562 | 17.9033
| ArmstrongIce Accretion2100RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2100 | 9.833 | 11.7611 | 14.196 | 16.0562 | 17.9033
| ArmstrongWind2023RCP4.5 | Armstrong | Wind | RCP4.5 | 2023 | 71.5974 | 77.0588 | 82.7925 | 88.5347 | 94.2888
| ArmstrongWind2025RCP4.5 | Armstrong | Wind | RCP4.5 | 2025 | 71.7144 | 77.1964 | 82.9544 | 88.7197 | 94.4938
| ArmstrongWind2030RCP4.5 | Armstrong | Wind | RCP4.5 | 2030 | 71.8315 | 77.3341 | 83.1162 | 88.9047 | 94.6988
| ArmstrongWind2035RCP4.5 | Armstrong | Wind | RCP4.5 | 2035 | 71.9486 | 77.4717 | 83.2781 | 89.0898 | 94.9039
| ArmstrongWind2040RCP4.5 | Armstrong | Wind | RCP4.5 | 2040 | 72.0656 | 77.6094 | 83.4399 | 89.2748 | 95.1089
| ArmstrongWind2045RCP4.5 | Armstrong | Wind | RCP4.5 | 2045 | 72.1827 | 77.7471 | 83.6018 | 89.4598 | 95.3139
| ArmstrongWind2050RCP4.5 | Armstrong | Wind | RCP4.5 | 2050 | 72.4187 | 78.0237 | 83.9279 | 89.8313 | 95.7289
| ArmstrongWind2055RCP4.5 | Armstrong | Wind | RCP4.5 | 2055 | 72.5377 | 78.1626 | 84.0923 | 90.0178 | 95.939
| ArmstrongWind2060RCP4.5 | Armstrong | Wind | RCP4.5 | 2060 | 72.6566 | 78.3015 | 84.2566 | 90.2043 | 96.1491
| ArmstrongWind2065RCP4.5 | Armstrong | Wind | RCP4.5 | 2065 | 72.7756 | 78.4405 | 84.421 | 90.3908 | 96.3591
| ArmstrongWind2070RCP4.5 | Armstrong | Wind | RCP4.5 | 2070 | 72.8946 | 78.5794 | 84.5853 | 90.5773 | 96.5692
| ArmstrongWind2075RCP4.5 | Armstrong | Wind | RCP4.5 | 2075 | 72.9746 | 78.6708 | 84.6877 | 90.6898 | 96.6922
| ArmstrongWind2080RCP4.5 | Armstrong | Wind | RCP4.5 | 2080 | 73.0546 | 78.7621 | 84.79 | 90.8023 | 96.8152
| ArmstrongWind2085RCP4.5 | Armstrong | Wind | RCP4.5 | 2085 | 73.1347 | 78.8534 | 84.8924 | 90.9148 | 96.9382
| ArmstrongWind2090RCP4.5 | Armstrong | Wind | RCP4.5 | 2090 | 73.2147 | 78.9448 | 84.9948 | 91.0273 | 97.0612
| ArmstrongWind2095RCP4.5 | Armstrong | Wind | RCP4.5 | 2095 | 73.2947 | 79.0361 | 85.0971 | 91.1398 | 97.1842
| ArmstrongWind2100RCP4.5 | Armstrong | Wind | RCP4.5 | 2100 | 73.3748 | 79.1275 | 85.1995 | 91.2523 | 97.3072
| ArmstrongWind2023RCP6.0 | Armstrong | Wind | RCP6.0 | 2023 | 71.5974 | 77.0588 | 82.7925 | 88.5347 | 94.2888
| ArmstrongWind2025RCP6.0 | Armstrong | Wind | RCP6.0 | 2025 | 71.7144 | 77.1964 | 82.9544 | 88.7197 | 94.4938
| ArmstrongWind2030RCP6.0 | Armstrong | Wind | RCP6.0 | 2030 | 71.8315 | 77.3341 | 83.1162 | 88.9047 | 94.6988
| ArmstrongWind2035RCP6.0 | Armstrong | Wind | RCP6.0 | 2035 | 71.9486 | 77.4717 | 83.2781 | 89.0898 | 94.9039
| ArmstrongWind2040RCP6.0 | Armstrong | Wind | RCP6.0 | 2040 | 72.0656 | 77.6094 | 83.4399 | 89.2748 | 95.1089
| ArmstrongWind2045RCP6.0 | Armstrong | Wind | RCP6.0 | 2045 | 72.1827 | 77.7471 | 83.6018 | 89.4598 | 95.3139
| ArmstrongWind2050RCP6.0 | Armstrong | Wind | RCP6.0 | 2050 | 72.4187 | 78.0237 | 83.9279 | 89.8313 | 95.7289
| ArmstrongWind2055RCP6.0 | Armstrong | Wind | RCP6.0 | 2055 | 72.5377 | 78.1626 | 84.0923 | 90.0178 | 95.939
| ArmstrongWind2060RCP6.0 | Armstrong | Wind | RCP6.0 | 2060 | 72.6566 | 78.3015 | 84.2566 | 90.2043 | 96.1491
| ArmstrongWind2065RCP6.0 | Armstrong | Wind | RCP6.0 | 2065 | 72.7756 | 78.4405 | 84.421 | 90.3908 | 96.3591
| ArmstrongWind2070RCP6.0 | Armstrong | Wind | RCP6.0 | 2070 | 72.8946 | 78.5794 | 84.5853 | 90.5773 | 96.5692
| ArmstrongWind2075RCP6.0 | Armstrong | Wind | RCP6.0 | 2075 | 73.0146 | 78.7164 | 84.7388 | 90.7461 | 96.7537
| ArmstrongWind2080RCP6.0 | Armstrong | Wind | RCP6.0 | 2080 | 73.1347 | 78.8534 | 84.8924 | 90.9148 | 96.9382
| ArmstrongWind2085RCP6.0 | Armstrong | Wind | RCP6.0 | 2085 | 73.2547 | 78.9905 | 85.046 | 91.0835 | 97.1227
| ArmstrongWind2090RCP6.0 | Armstrong | Wind | RCP6.0 | 2090 | 73.3461 | 79.094 | 85.1608 | 91.2079 | 97.2599
| ArmstrongWind2095RCP6.0 | Armstrong | Wind | RCP6.0 | 2095 | 73.3174 | 79.0606 | 85.122 | 91.1635 | 97.2126
| ArmstrongWind2100RCP6.0 | Armstrong | Wind | RCP6.0 | 2100 | 73.2888 | 79.0271 | 85.0833 | 91.1191 | 97.1653
| ArmstrongWind2023RCP8.5 | Armstrong | Wind | RCP8.5 | 2023 | 71.5974 | 77.0588 | 82.7925 | 88.5347 | 94.2888
| ArmstrongWind2025RCP8.5 | Armstrong | Wind | RCP8.5 | 2025 | 71.8315 | 77.3341 | 83.1162 | 88.9047 | 94.6988
| ArmstrongWind2030RCP8.5 | Armstrong | Wind | RCP8.5 | 2030 | 72.0656 | 77.6094 | 83.4399 | 89.2748 | 95.1089
| ArmstrongWind2035RCP8.5 | Armstrong | Wind | RCP8.5 | 2035 | 72.2997 | 77.8847 | 83.7636 | 89.6448 | 95.5189
| ArmstrongWind2040RCP8.5 | Armstrong | Wind | RCP8.5 | 2040 | 72.498 | 78.1163 | 84.0375 | 89.9556 | 95.869
| ArmstrongWind2045RCP8.5 | Armstrong | Wind | RCP8.5 | 2045 | 72.6963 | 78.3478 | 84.3114 | 90.2665 | 96.2191
| ArmstrongWind2050RCP8.5 | Armstrong | Wind | RCP8.5 | 2050 | 73.0546 | 78.7621 | 84.79 | 90.8023 | 96.8152
| ArmstrongWind2055RCP8.5 | Armstrong | Wind | RCP8.5 | 2055 | 73.2147 | 78.9448 | 84.9948 | 91.0273 | 97.0612
| ArmstrongWind2060RCP8.5 | Armstrong | Wind | RCP8.5 | 2060 | 73.3461 | 79.094 | 85.1608 | 91.2079 | 97.2599
| ArmstrongWind2065RCP8.5 | Armstrong | Wind | RCP8.5 | 2065 | 73.3174 | 79.0606 | 85.122 | 91.1635 | 97.2126
| ArmstrongWind2070RCP8.5 | Armstrong | Wind | RCP8.5 | 2070 | 73.4608 | 79.2458 | 85.36 | 91.4447 | 97.5374
| ArmstrongWind2075RCP8.5 | Armstrong | Wind | RCP8.5 | 2075 | 73.6328 | 79.4645 | 85.6366 | 91.7703 | 97.9096
| ArmstrongWind2080RCP8.5 | Armstrong | Wind | RCP8.5 | 2080 | 73.8048 | 79.6832 | 85.9133 | 92.096 | 98.2818
| ArmstrongWind2085RCP8.5 | Armstrong | Wind | RCP8.5 | 2085 | 73.8227 | 79.6987 | 85.9299 | 92.1137 | 98.3007
| ArmstrongWind2090RCP8.5 | Armstrong | Wind | RCP8.5 | 2090 | 73.8406 | 79.7141 | 85.9465 | 92.1315 | 98.3196
| ArmstrongWind2095RCP8.5 | Armstrong | Wind | RCP8.5 | 2095 | 73.8406 | 79.7141 | 85.9465 | 92.1315 | 98.3196
| ArmstrongWind2100RCP8.5 | Armstrong | Wind | RCP8.5 | 2100 | 73.8406 | 79.7141 | 85.9465 | 92.1315 | 98.3196
| ArnpriorIce Accretion2023RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2023 | 18.5812 | 22.0739 | 26.514 | 29.8998 | 33.3056
| ArnpriorIce Accretion2025RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2025 | 18.578 | 22.0664 | 26.5005 | 29.8845 | 33.2829
| ArnpriorIce Accretion2030RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2030 | 18.5749 | 22.0589 | 26.487 | 29.8693 | 33.2602
| ArnpriorIce Accretion2035RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2035 | 18.5718 | 22.0514 | 26.4735 | 29.854 | 33.2375
| ArnpriorIce Accretion2040RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2040 | 18.5687 | 22.044 | 26.46 | 29.8388 | 33.2149
| ArnpriorIce Accretion2045RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2045 | 18.5655 | 22.0365 | 26.4465 | 29.8235 | 33.1922
| ArnpriorIce Accretion2050RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2050 | 18.5737 | 22.0604 | 26.4924 | 29.8876 | 33.2648
| ArnpriorIce Accretion2055RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2055 | 18.5849 | 22.0918 | 26.5518 | 29.9669 | 33.36
| ArnpriorIce Accretion2060RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2060 | 18.5962 | 22.1232 | 26.6112 | 30.0462 | 33.4553
| ArnpriorIce Accretion2065RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2065 | 18.6075 | 22.1545 | 26.6706 | 30.1256 | 33.5505
| ArnpriorIce Accretion2070RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2070 | 18.6188 | 22.1859 | 26.73 | 30.2049 | 33.6458
| ArnpriorIce Accretion2075RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2075 | 18.6876 | 22.2942 | 26.883 | 30.393 | 33.8726
| ArnpriorIce Accretion2080RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2080 | 18.7565 | 22.4025 | 27.036 | 30.5812 | 34.0994
| ArnpriorIce Accretion2085RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2085 | 18.8254 | 22.5108 | 27.189 | 30.7693 | 34.3262
| ArnpriorIce Accretion2090RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2090 | 18.8943 | 22.6192 | 27.342 | 30.9575 | 34.553
| ArnpriorIce Accretion2095RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2095 | 18.9632 | 22.7275 | 27.495 | 31.1456 | 34.7798
| ArnpriorIce Accretion2100RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2100 | 19.0321 | 22.8358 | 27.648 | 31.3338 | 35.0066
| ArnpriorIce Accretion2023RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2023 | 18.5812 | 22.0739 | 26.514 | 29.8998 | 33.3056
| ArnpriorIce Accretion2025RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2025 | 18.578 | 22.0664 | 26.5005 | 29.8845 | 33.2829
| ArnpriorIce Accretion2030RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2030 | 18.5749 | 22.0589 | 26.487 | 29.8693 | 33.2602
| ArnpriorIce Accretion2035RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2035 | 18.5718 | 22.0514 | 26.4735 | 29.854 | 33.2375
| ArnpriorIce Accretion2040RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2040 | 18.5687 | 22.044 | 26.46 | 29.8388 | 33.2149
| ArnpriorIce Accretion2045RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2045 | 18.5655 | 22.0365 | 26.4465 | 29.8235 | 33.1922
| ArnpriorIce Accretion2050RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2050 | 18.5737 | 22.0604 | 26.4924 | 29.8876 | 33.2648
| ArnpriorIce Accretion2055RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2055 | 18.5849 | 22.0918 | 26.5518 | 29.9669 | 33.36
| ArnpriorIce Accretion2060RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2060 | 18.5962 | 22.1232 | 26.6112 | 30.0462 | 33.4553
| ArnpriorIce Accretion2065RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2065 | 18.6075 | 22.1545 | 26.6706 | 30.1256 | 33.5505
| ArnpriorIce Accretion2070RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2070 | 18.6188 | 22.1859 | 26.73 | 30.2049 | 33.6458
| ArnpriorIce Accretion2075RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2075 | 18.7221 | 22.3484 | 26.9595 | 30.4871 | 33.986
| ArnpriorIce Accretion2080RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2080 | 18.8254 | 22.5108 | 27.189 | 30.7693 | 34.3262
| ArnpriorIce Accretion2085RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2085 | 18.9288 | 22.6733 | 27.4185 | 31.0516 | 34.6664
| ArnpriorIce Accretion2090RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2090 | 19.0383 | 22.8881 | 27.765 | 31.4863 | 35.1994
| ArnpriorIce Accretion2095RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2095 | 19.0446 | 22.9404 | 27.882 | 31.6389 | 35.3921
| ArnpriorIce Accretion2100RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2100 | 19.0509 | 22.9927 | 27.999 | 31.7914 | 35.5849
| ArnpriorIce Accretion2023RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2023 | 18.5812 | 22.0739 | 26.514 | 29.8998 | 33.3056
| ArnpriorIce Accretion2025RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2025 | 18.5749 | 22.0589 | 26.487 | 29.8693 | 33.2602
| ArnpriorIce Accretion2030RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2030 | 18.5687 | 22.044 | 26.46 | 29.8388 | 33.2149
| ArnpriorIce Accretion2035RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2035 | 18.5624 | 22.029 | 26.433 | 29.8083 | 33.1695
| ArnpriorIce Accretion2040RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2040 | 18.5812 | 22.0813 | 26.532 | 29.9405 | 33.3283
| ArnpriorIce Accretion2045RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2045 | 18.6 | 22.1336 | 26.631 | 30.0727 | 33.487
| ArnpriorIce Accretion2050RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2050 | 18.7565 | 22.4025 | 27.036 | 30.5812 | 34.0994
| ArnpriorIce Accretion2055RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2055 | 18.8943 | 22.6192 | 27.342 | 30.9575 | 34.553
| ArnpriorIce Accretion2060RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2060 | 19.0383 | 22.8881 | 27.765 | 31.4863 | 35.1994
| ArnpriorIce Accretion2065RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2065 | 19.0446 | 22.9404 | 27.882 | 31.6389 | 35.3921
| ArnpriorIce Accretion2070RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2070 | 18.9507 | 22.9105 | 27.936 | 31.7507 | 35.5622
| ArnpriorIce Accretion2075RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2075 | 18.8505 | 22.8283 | 27.873 | 31.7101 | 35.5396
| ArnpriorIce Accretion2080RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2080 | 18.7503 | 22.7461 | 27.81 | 31.6694 | 35.5169
| ArnpriorIce Accretion2085RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2085 | 18.1585 | 22.0739 | 27.027 | 30.7998 | 34.5643
| ArnpriorIce Accretion2090RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2090 | 17.5666 | 21.4016 | 26.244 | 29.9303 | 33.6118
| ArnpriorIce Accretion2095RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2095 | 17.5666 | 21.4016 | 26.244 | 29.9303 | 33.6118
| ArnpriorIce Accretion2100RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2100 | 17.5666 | 21.4016 | 26.244 | 29.9303 | 33.6118
| ArnpriorWind2023RCP4.5 | Arnprior | Wind | RCP4.5 | 2023 | 76.3208 | 82.3065 | 88.6248 | 94.9227 | 101.2229
| ArnpriorWind2025RCP4.5 | Arnprior | Wind | RCP4.5 | 2025 | 76.4094 | 82.4197 | 88.77 | 95.0938 | 101.4218
| ArnpriorWind2030RCP4.5 | Arnprior | Wind | RCP4.5 | 2030 | 76.4981 | 82.5329 | 88.9152 | 95.2648 | 101.6208
| ArnpriorWind2035RCP4.5 | Arnprior | Wind | RCP4.5 | 2035 | 76.5867 | 82.6461 | 89.0604 | 95.4359 | 101.8198
| ArnpriorWind2040RCP4.5 | Arnprior | Wind | RCP4.5 | 2040 | 76.6754 | 82.7593 | 89.2056 | 95.6069 | 102.0188
| ArnpriorWind2045RCP4.5 | Arnprior | Wind | RCP4.5 | 2045 | 76.764 | 82.8725 | 89.3508 | 95.778 | 102.2177
| ArnpriorWind2050RCP4.5 | Arnprior | Wind | RCP4.5 | 2050 | 76.7661 | 82.8679 | 89.3394 | 95.7588 | 102.192
| ArnpriorWind2055RCP4.5 | Arnprior | Wind | RCP4.5 | 2055 | 76.6795 | 82.7501 | 89.1827 | 95.5686 | 101.9673
| ArnpriorWind2060RCP4.5 | Arnprior | Wind | RCP4.5 | 2060 | 76.5928 | 82.6322 | 89.0261 | 95.3784 | 101.7425
| ArnpriorWind2065RCP4.5 | Arnprior | Wind | RCP4.5 | 2065 | 76.5062 | 82.5144 | 88.8694 | 95.1882 | 101.5178
| ArnpriorWind2070RCP4.5 | Arnprior | Wind | RCP4.5 | 2070 | 76.4196 | 82.3965 | 88.7128 | 94.998 | 101.2931
| ArnpriorWind2075RCP4.5 | Arnprior | Wind | RCP4.5 | 2075 | 76.4614 | 82.4511 | 88.7817 | 95.0796 | 101.3884
| ArnpriorWind2080RCP4.5 | Arnprior | Wind | RCP4.5 | 2080 | 76.5032 | 82.5056 | 88.8507 | 95.1612 | 101.4837
| ArnpriorWind2085RCP4.5 | Arnprior | Wind | RCP4.5 | 2085 | 76.545 | 82.5602 | 88.9196 | 95.2428 | 101.579
| ArnpriorWind2090RCP4.5 | Arnprior | Wind | RCP4.5 | 2090 | 76.5867 | 82.6148 | 88.9885 | 95.3244 | 101.6743
| ArnpriorWind2095RCP4.5 | Arnprior | Wind | RCP4.5 | 2095 | 76.6285 | 82.6693 | 89.0575 | 95.4061 | 101.7696
| ArnpriorWind2100RCP4.5 | Arnprior | Wind | RCP4.5 | 2100 | 76.6703 | 82.7239 | 89.1264 | 95.4877 | 101.8649
| ArnpriorWind2023RCP6.0 | Arnprior | Wind | RCP6.0 | 2023 | 76.3208 | 82.3065 | 88.6248 | 94.9227 | 101.2229
| ArnpriorWind2025RCP6.0 | Arnprior | Wind | RCP6.0 | 2025 | 76.4094 | 82.4197 | 88.77 | 95.0938 | 101.4218
| ArnpriorWind2030RCP6.0 | Arnprior | Wind | RCP6.0 | 2030 | 76.4981 | 82.5329 | 88.9152 | 95.2648 | 101.6208
| ArnpriorWind2035RCP6.0 | Arnprior | Wind | RCP6.0 | 2035 | 76.5867 | 82.6461 | 89.0604 | 95.4359 | 101.8198
| ArnpriorWind2040RCP6.0 | Arnprior | Wind | RCP6.0 | 2040 | 76.6754 | 82.7593 | 89.2056 | 95.6069 | 102.0188
| ArnpriorWind2045RCP6.0 | Arnprior | Wind | RCP6.0 | 2045 | 76.764 | 82.8725 | 89.3508 | 95.778 | 102.2177
| ArnpriorWind2050RCP6.0 | Arnprior | Wind | RCP6.0 | 2050 | 76.7661 | 82.8679 | 89.3394 | 95.7588 | 102.192
| ArnpriorWind2055RCP6.0 | Arnprior | Wind | RCP6.0 | 2055 | 76.6795 | 82.7501 | 89.1827 | 95.5686 | 101.9673
| ArnpriorWind2060RCP6.0 | Arnprior | Wind | RCP6.0 | 2060 | 76.5928 | 82.6322 | 89.0261 | 95.3784 | 101.7425
| ArnpriorWind2065RCP6.0 | Arnprior | Wind | RCP6.0 | 2065 | 76.5062 | 82.5144 | 88.8694 | 95.1882 | 101.5178
| ArnpriorWind2070RCP6.0 | Arnprior | Wind | RCP6.0 | 2070 | 76.4196 | 82.3965 | 88.7128 | 94.998 | 101.2931
| ArnpriorWind2075RCP6.0 | Arnprior | Wind | RCP6.0 | 2075 | 76.4823 | 82.4784 | 88.8162 | 95.1204 | 101.4361
| ArnpriorWind2080RCP6.0 | Arnprior | Wind | RCP6.0 | 2080 | 76.545 | 82.5602 | 88.9196 | 95.2428 | 101.579
| ArnpriorWind2085RCP6.0 | Arnprior | Wind | RCP6.0 | 2085 | 76.6076 | 82.642 | 89.023 | 95.3652 | 101.722
| ArnpriorWind2090RCP6.0 | Arnprior | Wind | RCP6.0 | 2090 | 76.488 | 82.4865 | 88.8213 | 95.1298 | 101.4469
| ArnpriorWind2095RCP6.0 | Arnprior | Wind | RCP6.0 | 2095 | 76.3056 | 82.2492 | 88.5163 | 94.772 | 101.0289
| ArnpriorWind2100RCP6.0 | Arnprior | Wind | RCP6.0 | 2100 | 76.1232 | 82.0119 | 88.2112 | 94.4142 | 100.6109
| ArnpriorWind2023RCP8.5 | Arnprior | Wind | RCP8.5 | 2023 | 76.3208 | 82.3065 | 88.6248 | 94.9227 | 101.2229
| ArnpriorWind2025RCP8.5 | Arnprior | Wind | RCP8.5 | 2025 | 76.4981 | 82.5329 | 88.9152 | 95.2648 | 101.6208
| ArnpriorWind2030RCP8.5 | Arnprior | Wind | RCP8.5 | 2030 | 76.6754 | 82.7593 | 89.2056 | 95.6069 | 102.0188
| ArnpriorWind2035RCP8.5 | Arnprior | Wind | RCP8.5 | 2035 | 76.8527 | 82.9858 | 89.496 | 95.949 | 102.4167
| ArnpriorWind2040RCP8.5 | Arnprior | Wind | RCP8.5 | 2040 | 76.7083 | 82.7893 | 89.2349 | 95.632 | 102.0422
| ArnpriorWind2045RCP8.5 | Arnprior | Wind | RCP8.5 | 2045 | 76.564 | 82.5929 | 88.9739 | 95.315 | 101.6676
| ArnpriorWind2050RCP8.5 | Arnprior | Wind | RCP8.5 | 2050 | 76.5032 | 82.5056 | 88.8507 | 95.1612 | 101.4837
| ArnpriorWind2055RCP8.5 | Arnprior | Wind | RCP8.5 | 2055 | 76.5867 | 82.6148 | 88.9885 | 95.3244 | 101.6743
| ArnpriorWind2060RCP8.5 | Arnprior | Wind | RCP8.5 | 2060 | 76.488 | 82.4865 | 88.8213 | 95.1298 | 101.4469
| ArnpriorWind2065RCP8.5 | Arnprior | Wind | RCP8.5 | 2065 | 76.3056 | 82.2492 | 88.5163 | 94.772 | 101.0289
| ArnpriorWind2070RCP8.5 | Arnprior | Wind | RCP8.5 | 2070 | 76.0928 | 81.9573 | 88.1261 | 94.3012 | 100.4705
| ArnpriorWind2075RCP8.5 | Arnprior | Wind | RCP8.5 | 2075 | 76.0624 | 81.9027 | 88.0411 | 94.1882 | 100.33
| ArnpriorWind2080RCP8.5 | Arnprior | Wind | RCP8.5 | 2080 | 76.032 | 81.8482 | 87.956 | 94.0753 | 100.1896
| ArnpriorWind2085RCP8.5 | Arnprior | Wind | RCP8.5 | 2085 | 75.8231 | 81.5945 | 87.648 | 93.7222 | 99.7883
| ArnpriorWind2090RCP8.5 | Arnprior | Wind | RCP8.5 | 2090 | 75.6141 | 81.3408 | 87.34 | 93.3691 | 99.387
| ArnpriorWind2095RCP8.5 | Arnprior | Wind | RCP8.5 | 2095 | 75.6141 | 81.3408 | 87.34 | 93.3691 | 99.387
| ArnpriorWind2100RCP8.5 | Arnprior | Wind | RCP8.5 | 2100 | 75.6141 | 81.3408 | 87.34 | 93.3691 | 99.387
| AtikokanIce Accretion2023RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2023 | 11.0118 | 13.1472 | 15.84 | 17.8992 | 19.9584
| AtikokanIce Accretion2025RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2025 | 11.0205 | 13.1555 | 15.8525 | 17.9133 | 19.9742
| AtikokanIce Accretion2030RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2030 | 11.0292 | 13.1638 | 15.865 | 17.9275 | 19.9899
| AtikokanIce Accretion2035RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2035 | 11.0379 | 13.1721 | 15.8775 | 17.9416 | 20.0056
| AtikokanIce Accretion2040RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2040 | 11.0466 | 13.1804 | 15.89 | 17.9557 | 20.0214
| AtikokanIce Accretion2045RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2045 | 11.0553 | 13.1887 | 15.9025 | 17.9698 | 20.0371
| AtikokanIce Accretion2050RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2050 | 11.018 | 13.1347 | 15.828 | 17.8822 | 19.9357
| AtikokanIce Accretion2055RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2055 | 10.9721 | 13.0725 | 15.741 | 17.7805 | 19.8185
| AtikokanIce Accretion2060RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2060 | 10.9262 | 13.0102 | 15.654 | 17.6788 | 19.7014
| AtikokanIce Accretion2065RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2065 | 10.8802 | 12.948 | 15.567 | 17.5771 | 19.5842
| AtikokanIce Accretion2070RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2070 | 10.8343 | 12.8857 | 15.48 | 17.4754 | 19.467
| AtikokanIce Accretion2075RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2075 | 10.8187 | 12.8691 | 15.465 | 17.4613 | 19.4512
| AtikokanIce Accretion2080RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2080 | 10.803 | 12.8525 | 15.45 | 17.4472 | 19.4355
| AtikokanIce Accretion2085RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2085 | 10.7874 | 12.8359 | 15.435 | 17.4331 | 19.4197
| AtikokanIce Accretion2090RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2090 | 10.7717 | 12.8193 | 15.42 | 17.4189 | 19.404
| AtikokanIce Accretion2095RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2095 | 10.756 | 12.8027 | 15.405 | 17.4048 | 19.3882
| AtikokanIce Accretion2100RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2100 | 10.7404 | 12.7861 | 15.39 | 17.3907 | 19.3725
| AtikokanIce Accretion2023RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2023 | 11.0118 | 13.1472 | 15.84 | 17.8992 | 19.9584
| AtikokanIce Accretion2025RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2025 | 11.0205 | 13.1555 | 15.8525 | 17.9133 | 19.9742
| AtikokanIce Accretion2030RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2030 | 11.0292 | 13.1638 | 15.865 | 17.9275 | 19.9899
| AtikokanIce Accretion2035RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2035 | 11.0379 | 13.1721 | 15.8775 | 17.9416 | 20.0056
| AtikokanIce Accretion2040RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2040 | 11.0466 | 13.1804 | 15.89 | 17.9557 | 20.0214
| AtikokanIce Accretion2045RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2045 | 11.0553 | 13.1887 | 15.9025 | 17.9698 | 20.0371
| AtikokanIce Accretion2050RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2050 | 11.018 | 13.1347 | 15.828 | 17.8822 | 19.9357
| AtikokanIce Accretion2055RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2055 | 10.9721 | 13.0725 | 15.741 | 17.7805 | 19.8185
| AtikokanIce Accretion2060RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2060 | 10.9262 | 13.0102 | 15.654 | 17.6788 | 19.7014
| AtikokanIce Accretion2065RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2065 | 10.8802 | 12.948 | 15.567 | 17.5771 | 19.5842
| AtikokanIce Accretion2070RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2070 | 10.8343 | 12.8857 | 15.48 | 17.4754 | 19.467
| AtikokanIce Accretion2075RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2075 | 10.8108 | 12.8608 | 15.4575 | 17.4543 | 19.4434
| AtikokanIce Accretion2080RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2080 | 10.7874 | 12.8359 | 15.435 | 17.4331 | 19.4197
| AtikokanIce Accretion2085RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2085 | 10.7639 | 12.811 | 15.4125 | 17.4119 | 19.3961
| AtikokanIce Accretion2090RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2090 | 10.7752 | 12.8359 | 15.46 | 17.4698 | 19.467
| AtikokanIce Accretion2095RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2095 | 10.81 | 12.8857 | 15.53 | 17.5489 | 19.5615
| AtikokanIce Accretion2100RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2100 | 10.8448 | 12.9355 | 15.6 | 17.628 | 19.656
| AtikokanIce Accretion2023RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2023 | 11.0118 | 13.1472 | 15.84 | 17.8992 | 19.9584
| AtikokanIce Accretion2025RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2025 | 11.0292 | 13.1638 | 15.865 | 17.9275 | 19.9899
| AtikokanIce Accretion2030RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2030 | 11.0466 | 13.1804 | 15.89 | 17.9557 | 20.0214
| AtikokanIce Accretion2035RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2035 | 11.064 | 13.197 | 15.915 | 17.9839 | 20.0529
| AtikokanIce Accretion2040RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2040 | 10.9874 | 13.0932 | 15.77 | 17.8144 | 19.8576
| AtikokanIce Accretion2045RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2045 | 10.9109 | 12.9895 | 15.625 | 17.6449 | 19.6623
| AtikokanIce Accretion2050RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2050 | 10.803 | 12.8525 | 15.45 | 17.4472 | 19.4355
| AtikokanIce Accretion2055RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2055 | 10.7717 | 12.8193 | 15.42 | 17.4189 | 19.404
| AtikokanIce Accretion2060RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2060 | 10.7752 | 12.8359 | 15.46 | 17.4698 | 19.467
| AtikokanIce Accretion2065RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2065 | 10.81 | 12.8857 | 15.53 | 17.5489 | 19.5615
| AtikokanIce Accretion2070RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2070 | 10.7961 | 12.8899 | 15.555 | 17.5828 | 19.6119
| AtikokanIce Accretion2075RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2075 | 10.7473 | 12.8442 | 15.51 | 17.5376 | 19.5678
| AtikokanIce Accretion2080RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2080 | 10.6986 | 12.7986 | 15.465 | 17.4924 | 19.5237
| AtikokanIce Accretion2085RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2085 | 10.3333 | 12.3628 | 14.94 | 16.8991 | 18.8622
| AtikokanIce Accretion2090RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2090 | 9.968 | 11.9271 | 14.415 | 16.3059 | 18.2007
| AtikokanIce Accretion2095RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2095 | 9.968 | 11.9271 | 14.415 | 16.3059 | 18.2007
| AtikokanIce Accretion2100RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2100 | 9.968 | 11.9271 | 14.415 | 16.3059 | 18.2007
| AtikokanWind2023RCP4.5 | Atikokan | Wind | RCP4.5 | 2023 | 74.2149 | 79.916 | 85.914 | 91.9096 | 97.9125
| AtikokanWind2025RCP4.5 | Atikokan | Wind | RCP4.5 | 2025 | 74.2818 | 79.9933 | 86.0043 | 92.0108 | 98.0253
| AtikokanWind2030RCP4.5 | Atikokan | Wind | RCP4.5 | 2030 | 74.3486 | 80.0706 | 86.0946 | 92.112 | 98.138
| AtikokanWind2035RCP4.5 | Atikokan | Wind | RCP4.5 | 2035 | 74.4154 | 80.148 | 86.1849 | 92.2132 | 98.2508
| AtikokanWind2040RCP4.5 | Atikokan | Wind | RCP4.5 | 2040 | 74.4823 | 80.2253 | 86.2752 | 92.3145 | 98.3635
| AtikokanWind2045RCP4.5 | Atikokan | Wind | RCP4.5 | 2045 | 74.5491 | 80.3026 | 86.3655 | 92.4157 | 98.4763
| AtikokanWind2050RCP4.5 | Atikokan | Wind | RCP4.5 | 2050 | 74.6932 | 80.4743 | 86.571 | 92.6531 | 98.7439
| AtikokanWind2055RCP4.5 | Atikokan | Wind | RCP4.5 | 2055 | 74.7704 | 80.5687 | 86.6863 | 92.7893 | 98.8988
| AtikokanWind2060RCP4.5 | Atikokan | Wind | RCP4.5 | 2060 | 74.8476 | 80.663 | 86.8015 | 92.9255 | 99.0537
| AtikokanWind2065RCP4.5 | Atikokan | Wind | RCP4.5 | 2065 | 74.9249 | 80.7574 | 86.9168 | 93.0617 | 99.2086
| AtikokanWind2070RCP4.5 | Atikokan | Wind | RCP4.5 | 2070 | 75.0021 | 80.8518 | 87.032 | 93.1979 | 99.3635
| AtikokanWind2075RCP4.5 | Atikokan | Wind | RCP4.5 | 2075 | 75.1073 | 80.9811 | 87.1882 | 93.3773 | 99.5662
| AtikokanWind2080RCP4.5 | Atikokan | Wind | RCP4.5 | 2080 | 75.2125 | 81.1104 | 87.3445 | 93.5567 | 99.7688
| AtikokanWind2085RCP4.5 | Atikokan | Wind | RCP4.5 | 2085 | 75.3177 | 81.2397 | 87.5007 | 93.7362 | 99.9714
| AtikokanWind2090RCP4.5 | Atikokan | Wind | RCP4.5 | 2090 | 75.4229 | 81.369 | 87.6569 | 93.9156 | 100.174
| AtikokanWind2095RCP4.5 | Atikokan | Wind | RCP4.5 | 2095 | 75.5281 | 81.4983 | 87.8132 | 94.0951 | 100.3766
| AtikokanWind2100RCP4.5 | Atikokan | Wind | RCP4.5 | 2100 | 75.6333 | 81.6276 | 87.9694 | 94.2745 | 100.5792
| AtikokanWind2023RCP6.0 | Atikokan | Wind | RCP6.0 | 2023 | 74.2149 | 79.916 | 85.914 | 91.9096 | 97.9125
| AtikokanWind2025RCP6.0 | Atikokan | Wind | RCP6.0 | 2025 | 74.2818 | 79.9933 | 86.0043 | 92.0108 | 98.0253
| AtikokanWind2030RCP6.0 | Atikokan | Wind | RCP6.0 | 2030 | 74.3486 | 80.0706 | 86.0946 | 92.112 | 98.138
| AtikokanWind2035RCP6.0 | Atikokan | Wind | RCP6.0 | 2035 | 74.4154 | 80.148 | 86.1849 | 92.2132 | 98.2508
| AtikokanWind2040RCP6.0 | Atikokan | Wind | RCP6.0 | 2040 | 74.4823 | 80.2253 | 86.2752 | 92.3145 | 98.3635
| AtikokanWind2045RCP6.0 | Atikokan | Wind | RCP6.0 | 2045 | 74.5491 | 80.3026 | 86.3655 | 92.4157 | 98.4763
| AtikokanWind2050RCP6.0 | Atikokan | Wind | RCP6.0 | 2050 | 74.6932 | 80.4743 | 86.571 | 92.6531 | 98.7439
| AtikokanWind2055RCP6.0 | Atikokan | Wind | RCP6.0 | 2055 | 74.7704 | 80.5687 | 86.6863 | 92.7893 | 98.8988
| AtikokanWind2060RCP6.0 | Atikokan | Wind | RCP6.0 | 2060 | 74.8476 | 80.663 | 86.8015 | 92.9255 | 99.0537
| AtikokanWind2065RCP6.0 | Atikokan | Wind | RCP6.0 | 2065 | 74.9249 | 80.7574 | 86.9168 | 93.0617 | 99.2086
| AtikokanWind2070RCP6.0 | Atikokan | Wind | RCP6.0 | 2070 | 75.0021 | 80.8518 | 87.032 | 93.1979 | 99.3635
| AtikokanWind2075RCP6.0 | Atikokan | Wind | RCP6.0 | 2075 | 75.1599 | 81.0457 | 87.2663 | 93.467 | 99.6675
| AtikokanWind2080RCP6.0 | Atikokan | Wind | RCP6.0 | 2080 | 75.3177 | 81.2397 | 87.5007 | 93.7362 | 99.9714
| AtikokanWind2085RCP6.0 | Atikokan | Wind | RCP6.0 | 2085 | 75.4755 | 81.4336 | 87.7351 | 94.0053 | 100.2753
| AtikokanWind2090RCP6.0 | Atikokan | Wind | RCP6.0 | 2090 | 75.8635 | 81.9422 | 88.3965 | 94.7929 | 101.1904
| AtikokanWind2095RCP6.0 | Atikokan | Wind | RCP6.0 | 2095 | 76.0937 | 82.2568 | 88.8237 | 95.3112 | 101.8015
| AtikokanWind2100RCP6.0 | Atikokan | Wind | RCP6.0 | 2100 | 76.3239 | 82.5714 | 89.2508 | 95.8296 | 102.4126
| AtikokanWind2023RCP8.5 | Atikokan | Wind | RCP8.5 | 2023 | 74.2149 | 79.916 | 85.914 | 91.9096 | 97.9125
| AtikokanWind2025RCP8.5 | Atikokan | Wind | RCP8.5 | 2025 | 74.3486 | 80.0706 | 86.0946 | 92.112 | 98.138
| AtikokanWind2030RCP8.5 | Atikokan | Wind | RCP8.5 | 2030 | 74.4823 | 80.2253 | 86.2752 | 92.3145 | 98.3635
| AtikokanWind2035RCP8.5 | Atikokan | Wind | RCP8.5 | 2035 | 74.6159 | 80.3799 | 86.4558 | 92.5169 | 98.589
| AtikokanWind2040RCP8.5 | Atikokan | Wind | RCP8.5 | 2040 | 74.7447 | 80.5372 | 86.6479 | 92.7439 | 98.8472
| AtikokanWind2045RCP8.5 | Atikokan | Wind | RCP8.5 | 2045 | 74.8734 | 80.6945 | 86.8399 | 92.9709 | 99.1054
| AtikokanWind2050RCP8.5 | Atikokan | Wind | RCP8.5 | 2050 | 75.2125 | 81.1104 | 87.3445 | 93.5567 | 99.7688
| AtikokanWind2055RCP8.5 | Atikokan | Wind | RCP8.5 | 2055 | 75.4229 | 81.369 | 87.6569 | 93.9156 | 100.174
| AtikokanWind2060RCP8.5 | Atikokan | Wind | RCP8.5 | 2060 | 75.8635 | 81.9422 | 88.3965 | 94.7929 | 101.1904
| AtikokanWind2065RCP8.5 | Atikokan | Wind | RCP8.5 | 2065 | 76.0937 | 82.2568 | 88.8237 | 95.3112 | 101.8015
| AtikokanWind2070RCP8.5 | Atikokan | Wind | RCP8.5 | 2070 | 76.4427 | 82.7073 | 89.4027 | 95.9983 | 102.6021
| AtikokanWind2075RCP8.5 | Atikokan | Wind | RCP8.5 | 2075 | 76.5615 | 82.8433 | 89.5547 | 96.167 | 102.7917
| AtikokanWind2080RCP8.5 | Atikokan | Wind | RCP8.5 | 2080 | 76.6803 | 82.9793 | 89.7066 | 96.3357 | 102.9812
| AtikokanWind2085RCP8.5 | Atikokan | Wind | RCP8.5 | 2085 | 76.7138 | 83.0112 | 89.7324 | 96.3587 | 102.9959
| AtikokanWind2090RCP8.5 | Atikokan | Wind | RCP8.5 | 2090 | 76.7472 | 83.0432 | 89.7582 | 96.3817 | 103.0106
| AtikokanWind2095RCP8.5 | Atikokan | Wind | RCP8.5 | 2095 | 76.7472 | 83.0432 | 89.7582 | 96.3817 | 103.0106
| AtikokanWind2100RCP8.5 | Atikokan | Wind | RCP8.5 | 2100 | 76.7472 | 83.0432 | 89.7582 | 96.3817 | 103.0106
| AttawapiskatIce Accretion2023RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2023 | 10.636 | 12.6865 | 15.285 | 17.272 | 19.2591
| AttawapiskatIce Accretion2025RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2025 | 10.6934 | 12.7529 | 15.365 | 17.3624 | 19.3567
| AttawapiskatIce Accretion2030RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2030 | 10.7508 | 12.8193 | 15.445 | 17.4528 | 19.4544
| AttawapiskatIce Accretion2035RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2035 | 10.8082 | 12.8857 | 15.525 | 17.5432 | 19.552
| AttawapiskatIce Accretion2040RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2040 | 10.8656 | 12.9521 | 15.605 | 17.6336 | 19.6497
| AttawapiskatIce Accretion2045RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2045 | 10.923 | 13.0185 | 15.685 | 17.724 | 19.7473
| AttawapiskatIce Accretion2050RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2050 | 10.9888 | 13.1024 | 15.792 | 17.8483 | 19.8866
| AttawapiskatIce Accretion2055RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2055 | 10.9972 | 13.1198 | 15.819 | 17.8822 | 19.9282
| AttawapiskatIce Accretion2060RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2060 | 11.0055 | 13.1372 | 15.846 | 17.9161 | 19.9697
| AttawapiskatIce Accretion2065RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2065 | 11.0139 | 13.1547 | 15.873 | 17.95 | 20.0113
| AttawapiskatIce Accretion2070RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2070 | 11.0222 | 13.1721 | 15.9 | 17.9839 | 20.0529
| AttawapiskatIce Accretion2075RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2075 | 10.9178 | 13.0601 | 15.7775 | 17.8512 | 19.9143
| AttawapiskatIce Accretion2080RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2080 | 10.8134 | 12.948 | 15.655 | 17.7184 | 19.7757
| AttawapiskatIce Accretion2085RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2085 | 10.7091 | 12.836 | 15.5325 | 17.5856 | 19.6371
| AttawapiskatIce Accretion2090RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2090 | 10.6047 | 12.7239 | 15.41 | 17.4528 | 19.4985
| AttawapiskatIce Accretion2095RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2095 | 10.5003 | 12.6118 | 15.2875 | 17.3201 | 19.3599
| AttawapiskatIce Accretion2100RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2100 | 10.3959 | 12.4998 | 15.165 | 17.1873 | 19.2213
| AttawapiskatIce Accretion2023RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2023 | 10.636 | 12.6865 | 15.285 | 17.272 | 19.2591
| AttawapiskatIce Accretion2025RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2025 | 10.6934 | 12.7529 | 15.365 | 17.3624 | 19.3567
| AttawapiskatIce Accretion2030RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2030 | 10.7508 | 12.8193 | 15.445 | 17.4528 | 19.4544
| AttawapiskatIce Accretion2035RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2035 | 10.8082 | 12.8857 | 15.525 | 17.5432 | 19.552
| AttawapiskatIce Accretion2040RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2040 | 10.8656 | 12.9521 | 15.605 | 17.6336 | 19.6497
| AttawapiskatIce Accretion2045RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2045 | 10.923 | 13.0185 | 15.685 | 17.724 | 19.7473
| AttawapiskatIce Accretion2050RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2050 | 10.9888 | 13.1024 | 15.792 | 17.8483 | 19.8866
| AttawapiskatIce Accretion2055RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2055 | 10.9972 | 13.1198 | 15.819 | 17.8822 | 19.9282
| AttawapiskatIce Accretion2060RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2060 | 11.0055 | 13.1372 | 15.846 | 17.9161 | 19.9697
| AttawapiskatIce Accretion2065RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2065 | 11.0139 | 13.1547 | 15.873 | 17.95 | 20.0113
| AttawapiskatIce Accretion2070RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2070 | 11.0222 | 13.1721 | 15.9 | 17.9839 | 20.0529
| AttawapiskatIce Accretion2075RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2075 | 10.8656 | 13.004 | 15.7163 | 17.7848 | 19.845
| AttawapiskatIce Accretion2080RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2080 | 10.7091 | 12.836 | 15.5325 | 17.5856 | 19.6371
| AttawapiskatIce Accretion2085RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2085 | 10.5525 | 12.6679 | 15.3487 | 17.3865 | 19.4292
| AttawapiskatIce Accretion2090RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2090 | 10.1176 | 12.1968 | 14.825 | 16.8257 | 18.8307
| AttawapiskatIce Accretion2095RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2095 | 9.8393 | 11.8939 | 14.485 | 16.4641 | 18.4401
| AttawapiskatIce Accretion2100RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2100 | 9.5609 | 11.5909 | 14.145 | 16.1025 | 18.0495
| AttawapiskatIce Accretion2023RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2023 | 10.636 | 12.6865 | 15.285 | 17.272 | 19.2591
| AttawapiskatIce Accretion2025RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2025 | 10.7508 | 12.8193 | 15.445 | 17.4528 | 19.4544
| AttawapiskatIce Accretion2030RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2030 | 10.8656 | 12.9521 | 15.605 | 17.6336 | 19.6497
| AttawapiskatIce Accretion2035RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2035 | 10.9805 | 13.0849 | 15.765 | 17.8144 | 19.845
| AttawapiskatIce Accretion2040RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2040 | 10.9944 | 13.114 | 15.81 | 17.8709 | 19.9143
| AttawapiskatIce Accretion2045RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2045 | 11.0083 | 13.1431 | 15.855 | 17.9274 | 19.9836
| AttawapiskatIce Accretion2050RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2050 | 10.8134 | 12.948 | 15.655 | 17.7184 | 19.7757
| AttawapiskatIce Accretion2055RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2055 | 10.6047 | 12.7239 | 15.41 | 17.4528 | 19.4985
| AttawapiskatIce Accretion2060RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2060 | 10.1176 | 12.1968 | 14.825 | 16.8257 | 18.8307
| AttawapiskatIce Accretion2065RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2065 | 9.8393 | 11.8939 | 14.485 | 16.4641 | 18.4401
| AttawapiskatIce Accretion2070RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2070 | 9.2339 | 11.2216 | 13.725 | 15.6392 | 17.5455
| AttawapiskatIce Accretion2075RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2075 | 8.9068 | 10.8522 | 13.305 | 15.1759 | 17.0415
| AttawapiskatIce Accretion2080RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2080 | 8.5798 | 10.4829 | 12.885 | 14.7126 | 16.5375
| AttawapiskatIce Accretion2085RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2085 | 8.1101 | 9.9538 | 12.2775 | 14.0431 | 15.8004
| AttawapiskatIce Accretion2090RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2090 | 7.6404 | 9.4246 | 11.67 | 13.3735 | 15.0633
| AttawapiskatIce Accretion2095RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2095 | 7.6404 | 9.4246 | 11.67 | 13.3735 | 15.0633
| AttawapiskatIce Accretion2100RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2100 | 7.6404 | 9.4246 | 11.67 | 13.3735 | 15.0633
| AttawapiskatWind2023RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2023 | 81.1105 | 87.2015 | 93.5864 | 100.0067 | 106.4206
| AttawapiskatWind2025RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2025 | 81.1362 | 87.2233 | 93.5989 | 100.0151 | 106.4224
| AttawapiskatWind2030RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2030 | 81.1619 | 87.2452 | 93.6115 | 100.0235 | 106.4242
| AttawapiskatWind2035RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2035 | 81.1876 | 87.267 | 93.624 | 100.0318 | 106.426
| AttawapiskatWind2040RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2040 | 81.2133 | 87.2889 | 93.6365 | 100.0402 | 106.4277
| AttawapiskatWind2045RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2045 | 81.239 | 87.3107 | 93.6491 | 100.0486 | 106.4295
| AttawapiskatWind2050RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2050 | 81.354 | 87.4322 | 93.7782 | 100.1837 | 106.5728
| AttawapiskatWind2055RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2055 | 81.4433 | 87.5319 | 93.8947 | 100.3104 | 106.7142
| AttawapiskatWind2060RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2060 | 81.5326 | 87.6316 | 94.0113 | 100.4372 | 106.8557
| AttawapiskatWind2065RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2065 | 81.6219 | 87.7312 | 94.1278 | 100.5639 | 106.9971
| AttawapiskatWind2070RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2070 | 81.7112 | 87.8309 | 94.2444 | 100.6906 | 107.1386
| AttawapiskatWind2075RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2075 | 81.7477 | 87.8702 | 94.282 | 100.7292 | 107.1779
| AttawapiskatWind2080RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2080 | 81.7842 | 87.9096 | 94.3196 | 100.7677 | 107.2172
| AttawapiskatWind2085RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2085 | 81.8207 | 87.9489 | 94.3572 | 100.8063 | 107.2564
| AttawapiskatWind2090RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2090 | 81.8573 | 87.9882 | 94.3948 | 100.8449 | 107.2957
| AttawapiskatWind2095RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2095 | 81.8938 | 88.0276 | 94.4324 | 100.8834 | 107.335
| AttawapiskatWind2100RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2100 | 81.9303 | 88.0669 | 94.47 | 100.922 | 107.3743
| AttawapiskatWind2023RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2023 | 81.1105 | 87.2015 | 93.5864 | 100.0067 | 106.4206
| AttawapiskatWind2025RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2025 | 81.1362 | 87.2233 | 93.5989 | 100.0151 | 106.4224
| AttawapiskatWind2030RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2030 | 81.1619 | 87.2452 | 93.6115 | 100.0235 | 106.4242
| AttawapiskatWind2035RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2035 | 81.1876 | 87.267 | 93.624 | 100.0318 | 106.426
| AttawapiskatWind2040RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2040 | 81.2133 | 87.2889 | 93.6365 | 100.0402 | 106.4277
| AttawapiskatWind2045RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2045 | 81.239 | 87.3107 | 93.6491 | 100.0486 | 106.4295
| AttawapiskatWind2050RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2050 | 81.354 | 87.4322 | 93.7782 | 100.1837 | 106.5728
| AttawapiskatWind2055RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2055 | 81.4433 | 87.5319 | 93.8947 | 100.3104 | 106.7142
| AttawapiskatWind2060RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2060 | 81.5326 | 87.6316 | 94.0113 | 100.4372 | 106.8557
| AttawapiskatWind2065RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2065 | 81.6219 | 87.7312 | 94.1278 | 100.5639 | 106.9971
| AttawapiskatWind2070RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2070 | 81.7112 | 87.8309 | 94.2444 | 100.6906 | 107.1386
| AttawapiskatWind2075RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2075 | 81.766 | 87.8899 | 94.3008 | 100.7485 | 107.1975
| AttawapiskatWind2080RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2080 | 81.8207 | 87.9489 | 94.3572 | 100.8063 | 107.2564
| AttawapiskatWind2085RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2085 | 81.8755 | 88.0079 | 94.4136 | 100.8641 | 107.3154
| AttawapiskatWind2090RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2090 | 81.9547 | 88.0844 | 94.4794 | 100.9253 | 107.3707
| AttawapiskatWind2095RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2095 | 81.979 | 88.1019 | 94.4888 | 100.9287 | 107.3672
| AttawapiskatWind2100RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2100 | 82.0034 | 88.1194 | 94.4982 | 100.932 | 107.3636
| AttawapiskatWind2023RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2023 | 81.1105 | 87.2015 | 93.5864 | 100.0067 | 106.4206
| AttawapiskatWind2025RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2025 | 81.1619 | 87.2452 | 93.6115 | 100.0235 | 106.4242
| AttawapiskatWind2030RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2030 | 81.2133 | 87.2889 | 93.6365 | 100.0402 | 106.4277
| AttawapiskatWind2035RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2035 | 81.2647 | 87.3326 | 93.6616 | 100.057 | 106.4313
| AttawapiskatWind2040RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2040 | 81.4136 | 87.4987 | 93.8559 | 100.2682 | 106.6671
| AttawapiskatWind2045RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2045 | 81.5624 | 87.6648 | 94.0501 | 100.4794 | 106.9028
| AttawapiskatWind2050RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2050 | 81.7842 | 87.9096 | 94.3196 | 100.7677 | 107.2172
| AttawapiskatWind2055RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2055 | 81.8573 | 87.9882 | 94.3948 | 100.8449 | 107.2957
| AttawapiskatWind2060RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2060 | 81.9547 | 88.0844 | 94.4794 | 100.9253 | 107.3707
| AttawapiskatWind2065RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2065 | 81.979 | 88.1019 | 94.4888 | 100.9287 | 107.3672
| AttawapiskatWind2070RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2070 | 82.1549 | 88.2767 | 94.6674 | 101.1097 | 107.5529
| AttawapiskatWind2075RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2075 | 82.3064 | 88.4341 | 94.8366 | 101.2874 | 107.7422
| AttawapiskatWind2080RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2080 | 82.4579 | 88.5914 | 95.0058 | 101.4651 | 107.9316
| AttawapiskatWind2085RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2085 | 82.7866 | 89.0023 | 95.5087 | 102.0535 | 108.5959
| AttawapiskatWind2090RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2090 | 83.1154 | 89.4132 | 96.0116 | 102.6419 | 109.2603
| AttawapiskatWind2095RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2095 | 83.1154 | 89.4132 | 96.0116 | 102.6419 | 109.2603
| AttawapiskatWind2100RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2100 | 83.1154 | 89.4132 | 96.0116 | 102.6419 | 109.2603
| AuroraIce Accretion2023RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
| AuroraIce Accretion2025RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2025 | 17.4222 | 20.9229 | 25.3542 | 28.7444 | 32.1247
| AuroraIce Accretion2030RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2030 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
| AuroraIce Accretion2035RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2035 | 17.5092 | 21.0612 | 25.5625 | 28.9986 | 32.4292
| AuroraIce Accretion2040RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2040 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
| AuroraIce Accretion2045RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2045 | 17.5962 | 21.1996 | 25.7708 | 29.2529 | 32.7338
| AuroraIce Accretion2050RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2050 | 17.5214 | 21.1484 | 25.745 | 29.2444 | 32.7411
| AuroraIce Accretion2055RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2055 | 17.4031 | 21.0281 | 25.615 | 29.1088 | 32.5962
| AuroraIce Accretion2060RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2060 | 17.2848 | 20.9077 | 25.485 | 28.9732 | 32.4513
| AuroraIce Accretion2065RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2065 | 17.1665 | 20.7873 | 25.355 | 28.8376 | 32.3064
| AuroraIce Accretion2070RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2070 | 17.0482 | 20.667 | 25.225 | 28.702 | 32.1615
| AuroraIce Accretion2075RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2075 | 17.0105 | 20.6497 | 25.2333 | 28.7255 | 32.2035
| AuroraIce Accretion2080RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2080 | 16.9728 | 20.6324 | 25.2417 | 28.7491 | 32.2455
| AuroraIce Accretion2085RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2085 | 16.9352 | 20.6151 | 25.25 | 28.7726 | 32.2875
| AuroraIce Accretion2090RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2090 | 16.8975 | 20.5978 | 25.2583 | 28.7962 | 32.3295
| AuroraIce Accretion2095RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2095 | 16.8598 | 20.5805 | 25.2667 | 28.8197 | 32.3715
| AuroraIce Accretion2100RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2100 | 16.8221 | 20.5633 | 25.275 | 28.8432 | 32.4135
| AuroraIce Accretion2023RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
| AuroraIce Accretion2025RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2025 | 17.4222 | 20.9229 | 25.3542 | 28.7444 | 32.1247
| AuroraIce Accretion2030RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2030 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
| AuroraIce Accretion2035RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2035 | 17.5092 | 21.0612 | 25.5625 | 28.9986 | 32.4292
| AuroraIce Accretion2040RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2040 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
| AuroraIce Accretion2045RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2045 | 17.5962 | 21.1996 | 25.7708 | 29.2529 | 32.7338
| AuroraIce Accretion2050RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2050 | 17.5214 | 21.1484 | 25.745 | 29.2444 | 32.7411
| AuroraIce Accretion2055RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2055 | 17.4031 | 21.0281 | 25.615 | 29.1088 | 32.5962
| AuroraIce Accretion2060RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2060 | 17.2848 | 20.9077 | 25.485 | 28.9732 | 32.4513
| AuroraIce Accretion2065RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2065 | 17.1665 | 20.7873 | 25.355 | 28.8376 | 32.3064
| AuroraIce Accretion2070RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2070 | 17.0482 | 20.667 | 25.225 | 28.702 | 32.1615
| AuroraIce Accretion2075RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2075 | 16.9917 | 20.6411 | 25.2375 | 28.7373 | 32.2245
| AuroraIce Accretion2080RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2080 | 16.9352 | 20.6151 | 25.25 | 28.7726 | 32.2875
| AuroraIce Accretion2085RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2085 | 16.8786 | 20.5892 | 25.2625 | 28.8079 | 32.3505
| AuroraIce Accretion2090RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2090 | 16.5147 | 20.2382 | 24.925 | 28.4854 | 32.0355
| AuroraIce Accretion2095RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2095 | 16.2074 | 19.9131 | 24.575 | 28.1276 | 31.6575
| AuroraIce Accretion2100RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2100 | 15.9001 | 19.588 | 24.225 | 27.7697 | 31.2795
| AuroraIce Accretion2023RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
| AuroraIce Accretion2025RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2025 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
| AuroraIce Accretion2030RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2030 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
| AuroraIce Accretion2035RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2035 | 17.6397 | 21.2687 | 25.875 | 29.38 | 32.886
| AuroraIce Accretion2040RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2040 | 17.4425 | 21.0682 | 25.6583 | 29.154 | 32.6445
| AuroraIce Accretion2045RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2045 | 17.2454 | 20.8676 | 25.4417 | 28.928 | 32.403
| AuroraIce Accretion2050RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2050 | 16.9728 | 20.6324 | 25.2417 | 28.7491 | 32.2455
| AuroraIce Accretion2055RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2055 | 16.8975 | 20.5978 | 25.2583 | 28.7962 | 32.3295
| AuroraIce Accretion2060RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2060 | 16.5147 | 20.2382 | 24.925 | 28.4854 | 32.0355
| AuroraIce Accretion2065RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2065 | 16.2074 | 19.9131 | 24.575 | 28.1276 | 31.6575
| AuroraIce Accretion2070RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2070 | 15.5116 | 19.173 | 23.775 | 27.2801 | 30.765
| AuroraIce Accretion2075RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2075 | 15.1231 | 18.758 | 23.325 | 26.7904 | 30.2505
| AuroraIce Accretion2080RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2080 | 14.7345 | 18.343 | 22.875 | 26.3007 | 29.736
| AuroraIce Accretion2085RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2085 | 13.9691 | 17.4404 | 21.8 | 25.1001 | 28.3972
| AuroraIce Accretion2090RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2090 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
| AuroraIce Accretion2095RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2095 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
| AuroraIce Accretion2100RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2100 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
| AuroraWind2023RCP4.5 | Aurora | Wind | RCP4.5 | 2023 | 77.1343 | 83.0762 | 89.3293 | 95.5824 | 101.8354
| AuroraWind2025RCP4.5 | Aurora | Wind | RCP4.5 | 2025 | 77.1586 | 83.1107 | 89.3768 | 95.6411 | 101.9064
| AuroraWind2030RCP4.5 | Aurora | Wind | RCP4.5 | 2030 | 77.183 | 83.1452 | 89.4242 | 95.6998 | 101.9774
| AuroraWind2035RCP4.5 | Aurora | Wind | RCP4.5 | 2035 | 77.2073 | 83.1797 | 89.4717 | 95.7585 | 102.0485
| AuroraWind2040RCP4.5 | Aurora | Wind | RCP4.5 | 2040 | 77.2316 | 83.2142 | 89.5192 | 95.8173 | 102.1195
| AuroraWind2045RCP4.5 | Aurora | Wind | RCP4.5 | 2045 | 77.256 | 83.2487 | 89.5666 | 95.876 | 102.1905
| AuroraWind2050RCP4.5 | Aurora | Wind | RCP4.5 | 2050 | 77.331 | 83.3312 | 89.6586 | 95.9766 | 102.3001
| AuroraWind2055RCP4.5 | Aurora | Wind | RCP4.5 | 2055 | 77.3817 | 83.3792 | 89.7031 | 96.0185 | 102.3386
| AuroraWind2060RCP4.5 | Aurora | Wind | RCP4.5 | 2060 | 77.4325 | 83.4272 | 89.7476 | 96.0604 | 102.3772
| AuroraWind2065RCP4.5 | Aurora | Wind | RCP4.5 | 2065 | 77.4832 | 83.4752 | 89.7921 | 96.1023 | 102.4158
| AuroraWind2070RCP4.5 | Aurora | Wind | RCP4.5 | 2070 | 77.5339 | 83.5232 | 89.8366 | 96.1442 | 102.4543
| AuroraWind2075RCP4.5 | Aurora | Wind | RCP4.5 | 2075 | 77.6082 | 83.6253 | 89.9731 | 96.3093 | 102.6488
| AuroraWind2080RCP4.5 | Aurora | Wind | RCP4.5 | 2080 | 77.6825 | 83.7274 | 90.1095 | 96.4743 | 102.8432
| AuroraWind2085RCP4.5 | Aurora | Wind | RCP4.5 | 2085 | 77.7568 | 83.8295 | 90.246 | 96.6394 | 103.0377
| AuroraWind2090RCP4.5 | Aurora | Wind | RCP4.5 | 2090 | 77.8311 | 83.9315 | 90.3825 | 96.8045 | 103.2322
| AuroraWind2095RCP4.5 | Aurora | Wind | RCP4.5 | 2095 | 77.9053 | 84.0336 | 90.5189 | 96.9695 | 103.4266
| AuroraWind2100RCP4.5 | Aurora | Wind | RCP4.5 | 2100 | 77.9796 | 84.1357 | 90.6554 | 97.1346 | 103.6211
| AuroraWind2023RCP6.0 | Aurora | Wind | RCP6.0 | 2023 | 77.1343 | 83.0762 | 89.3293 | 95.5824 | 101.8354
| AuroraWind2025RCP6.0 | Aurora | Wind | RCP6.0 | 2025 | 77.1586 | 83.1107 | 89.3768 | 95.6411 | 101.9064
| AuroraWind2030RCP6.0 | Aurora | Wind | RCP6.0 | 2030 | 77.183 | 83.1452 | 89.4242 | 95.6998 | 101.9774
| AuroraWind2035RCP6.0 | Aurora | Wind | RCP6.0 | 2035 | 77.2073 | 83.1797 | 89.4717 | 95.7585 | 102.0485
| AuroraWind2040RCP6.0 | Aurora | Wind | RCP6.0 | 2040 | 77.2316 | 83.2142 | 89.5192 | 95.8173 | 102.1195
| AuroraWind2045RCP6.0 | Aurora | Wind | RCP6.0 | 2045 | 77.256 | 83.2487 | 89.5666 | 95.876 | 102.1905
| AuroraWind2050RCP6.0 | Aurora | Wind | RCP6.0 | 2050 | 77.331 | 83.3312 | 89.6586 | 95.9766 | 102.3001
| AuroraWind2055RCP6.0 | Aurora | Wind | RCP6.0 | 2055 | 77.3817 | 83.3792 | 89.7031 | 96.0185 | 102.3386
| AuroraWind2060RCP6.0 | Aurora | Wind | RCP6.0 | 2060 | 77.4325 | 83.4272 | 89.7476 | 96.0604 | 102.3772
| AuroraWind2065RCP6.0 | Aurora | Wind | RCP6.0 | 2065 | 77.4832 | 83.4752 | 89.7921 | 96.1023 | 102.4158
| AuroraWind2070RCP6.0 | Aurora | Wind | RCP6.0 | 2070 | 77.5339 | 83.5232 | 89.8366 | 96.1442 | 102.4543
| AuroraWind2075RCP6.0 | Aurora | Wind | RCP6.0 | 2075 | 77.6453 | 83.6763 | 90.0413 | 96.3918 | 102.746
| AuroraWind2080RCP6.0 | Aurora | Wind | RCP6.0 | 2080 | 77.7568 | 83.8295 | 90.246 | 96.6394 | 103.0377
| AuroraWind2085RCP6.0 | Aurora | Wind | RCP6.0 | 2085 | 77.8682 | 83.9826 | 90.4507 | 96.887 | 103.3294
| AuroraWind2090RCP6.0 | Aurora | Wind | RCP6.0 | 2090 | 78.2384 | 84.4557 | 91.05 | 97.5949 | 104.1487
| AuroraWind2095RCP6.0 | Aurora | Wind | RCP6.0 | 2095 | 78.4971 | 84.7758 | 91.4445 | 98.0552 | 104.6763
| AuroraWind2100RCP6.0 | Aurora | Wind | RCP6.0 | 2100 | 78.7558 | 85.0958 | 91.8391 | 98.5154 | 105.2039
| AuroraWind2023RCP8.5 | Aurora | Wind | RCP8.5 | 2023 | 77.1343 | 83.0762 | 89.3293 | 95.5824 | 101.8354
| AuroraWind2025RCP8.5 | Aurora | Wind | RCP8.5 | 2025 | 77.183 | 83.1452 | 89.4242 | 95.6998 | 101.9774
| AuroraWind2030RCP8.5 | Aurora | Wind | RCP8.5 | 2030 | 77.2316 | 83.2142 | 89.5192 | 95.8173 | 102.1195
| AuroraWind2035RCP8.5 | Aurora | Wind | RCP8.5 | 2035 | 77.2803 | 83.2832 | 89.6141 | 95.9347 | 102.2615
| AuroraWind2040RCP8.5 | Aurora | Wind | RCP8.5 | 2040 | 77.3648 | 83.3632 | 89.6883 | 96.0045 | 102.3258
| AuroraWind2045RCP8.5 | Aurora | Wind | RCP8.5 | 2045 | 77.4494 | 83.4432 | 89.7624 | 96.0744 | 102.3901
| AuroraWind2050RCP8.5 | Aurora | Wind | RCP8.5 | 2050 | 77.6825 | 83.7274 | 90.1095 | 96.4743 | 102.8432
| AuroraWind2055RCP8.5 | Aurora | Wind | RCP8.5 | 2055 | 77.8311 | 83.9315 | 90.3825 | 96.8045 | 103.2322
| AuroraWind2060RCP8.5 | Aurora | Wind | RCP8.5 | 2060 | 78.2384 | 84.4557 | 91.05 | 97.5949 | 104.1487
| AuroraWind2065RCP8.5 | Aurora | Wind | RCP8.5 | 2065 | 78.4971 | 84.7758 | 91.4445 | 98.0552 | 104.6763
| AuroraWind2070RCP8.5 | Aurora | Wind | RCP8.5 | 2070 | 78.9531 | 85.3607 | 92.1892 | 98.9376 | 105.6976
| AuroraWind2075RCP8.5 | Aurora | Wind | RCP8.5 | 2075 | 79.1503 | 85.6256 | 92.5392 | 99.3598 | 106.1914
| AuroraWind2080RCP8.5 | Aurora | Wind | RCP8.5 | 2080 | 79.3476 | 85.8904 | 92.8893 | 99.782 | 106.6852
| AuroraWind2085RCP8.5 | Aurora | Wind | RCP8.5 | 2085 | 79.4475 | 86.0229 | 93.0673 | 99.9915 | 106.9338
| AuroraWind2090RCP8.5 | Aurora | Wind | RCP8.5 | 2090 | 79.5474 | 86.1553 | 93.2453 | 100.201 | 107.1823
| AuroraWind2095RCP8.5 | Aurora | Wind | RCP8.5 | 2095 | 79.5474 | 86.1553 | 93.2453 | 100.201 | 107.1823
| AuroraWind2100RCP8.5 | Aurora | Wind | RCP8.5 | 2100 | 79.5474 | 86.1553 | 93.2453 | 100.201 | 107.1823
| BancroftIce Accretion2023RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2023 | 17.1874 | 20.4802 | 24.675 | 27.8827 | 31.0905
| BancroftIce Accretion2025RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2025 | 17.2077 | 20.501 | 24.6958 | 27.9016 | 31.1115
| BancroftIce Accretion2030RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2030 | 17.228 | 20.5217 | 24.7167 | 27.9204 | 31.1325
| BancroftIce Accretion2035RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2035 | 17.2483 | 20.5425 | 24.7375 | 27.9392 | 31.1535
| BancroftIce Accretion2040RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2040 | 17.2686 | 20.5633 | 24.7583 | 27.9581 | 31.1745
| BancroftIce Accretion2045RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2045 | 17.2889 | 20.584 | 24.7792 | 27.9769 | 31.1955
| BancroftIce Accretion2050RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2050 | 17.2848 | 20.5965 | 24.8 | 28.0127 | 31.2354
| BancroftIce Accretion2055RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2055 | 17.2605 | 20.5881 | 24.8 | 28.0296 | 31.2543
| BancroftIce Accretion2060RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2060 | 17.2361 | 20.5799 | 24.8 | 28.0466 | 31.2732
| BancroftIce Accretion2065RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2065 | 17.2118 | 20.5715 | 24.8 | 28.0635 | 31.2921
| BancroftIce Accretion2070RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2070 | 17.1874 | 20.5633 | 24.8 | 28.0805 | 31.311
| BancroftIce Accretion2075RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2075 | 17.286 | 20.6947 | 24.9792 | 28.2924 | 31.5577
| BancroftIce Accretion2080RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2080 | 17.3846 | 20.8261 | 25.1583 | 28.5042 | 31.8045
| BancroftIce Accretion2085RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2085 | 17.4831 | 20.9575 | 25.3375 | 28.7161 | 32.0512
| BancroftIce Accretion2090RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2090 | 17.5817 | 21.0889 | 25.5167 | 28.928 | 32.298
| BancroftIce Accretion2095RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2095 | 17.6803 | 21.2203 | 25.6958 | 29.1399 | 32.5448
| BancroftIce Accretion2100RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2100 | 17.7789 | 21.3517 | 25.875 | 29.3517 | 32.7915
| BancroftIce Accretion2023RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2023 | 17.1874 | 20.4802 | 24.675 | 27.8827 | 31.0905
| BancroftIce Accretion2025RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2025 | 17.2077 | 20.501 | 24.6958 | 27.9016 | 31.1115
| BancroftIce Accretion2030RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2030 | 17.228 | 20.5217 | 24.7167 | 27.9204 | 31.1325
| BancroftIce Accretion2035RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2035 | 17.2483 | 20.5425 | 24.7375 | 27.9392 | 31.1535
| BancroftIce Accretion2040RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2040 | 17.2686 | 20.5633 | 24.7583 | 27.9581 | 31.1745
| BancroftIce Accretion2045RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2045 | 17.2889 | 20.584 | 24.7792 | 27.9769 | 31.1955
| BancroftIce Accretion2050RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2050 | 17.2848 | 20.5965 | 24.8 | 28.0127 | 31.2354
| BancroftIce Accretion2055RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2055 | 17.2605 | 20.5881 | 24.8 | 28.0296 | 31.2543
| BancroftIce Accretion2060RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2060 | 17.2361 | 20.5799 | 24.8 | 28.0466 | 31.2732
| BancroftIce Accretion2065RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2065 | 17.2118 | 20.5715 | 24.8 | 28.0635 | 31.2921
| BancroftIce Accretion2070RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2070 | 17.1874 | 20.5633 | 24.8 | 28.0805 | 31.311
| BancroftIce Accretion2075RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2075 | 17.3353 | 20.7604 | 25.0688 | 28.3983 | 31.6811
| BancroftIce Accretion2080RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2080 | 17.4831 | 20.9575 | 25.3375 | 28.7161 | 32.0512
| BancroftIce Accretion2085RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2085 | 17.631 | 21.1546 | 25.6062 | 29.0339 | 32.4214
| BancroftIce Accretion2090RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2090 | 17.7731 | 21.3725 | 25.9333 | 29.4271 | 32.907
| BancroftIce Accretion2095RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2095 | 17.7673 | 21.3933 | 25.9917 | 29.5024 | 33.0225
| BancroftIce Accretion2100RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2100 | 17.7615 | 21.414 | 26.05 | 29.5777 | 33.138
| BancroftIce Accretion2023RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2023 | 17.1874 | 20.4802 | 24.675 | 27.8827 | 31.0905
| BancroftIce Accretion2025RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2025 | 17.228 | 20.5217 | 24.7167 | 27.9204 | 31.1325
| BancroftIce Accretion2030RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2030 | 17.2686 | 20.5633 | 24.7583 | 27.9581 | 31.1745
| BancroftIce Accretion2035RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2035 | 17.3092 | 20.6047 | 24.8 | 27.9957 | 31.2165
| BancroftIce Accretion2040RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2040 | 17.2686 | 20.5909 | 24.8 | 28.024 | 31.248
| BancroftIce Accretion2045RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2045 | 17.228 | 20.5771 | 24.8 | 28.0522 | 31.2795
| BancroftIce Accretion2050RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2050 | 17.3846 | 20.8261 | 25.1583 | 28.5042 | 31.8045
| BancroftIce Accretion2055RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2055 | 17.5817 | 21.0889 | 25.5167 | 28.928 | 32.298
| BancroftIce Accretion2060RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2060 | 17.7731 | 21.3725 | 25.9333 | 29.4271 | 32.907
| BancroftIce Accretion2065RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2065 | 17.7673 | 21.3933 | 25.9917 | 29.5024 | 33.0225
| BancroftIce Accretion2070RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2070 | 17.7209 | 21.414 | 26.0833 | 29.6437 | 33.222
| BancroftIce Accretion2075RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2075 | 17.6803 | 21.414 | 26.1167 | 29.7096 | 33.306
| BancroftIce Accretion2080RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2080 | 17.6397 | 21.414 | 26.15 | 29.7755 | 33.39
| BancroftIce Accretion2085RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2085 | 17.3092 | 21.0613 | 25.775 | 29.38 | 32.9805
| BancroftIce Accretion2090RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2090 | 16.9786 | 20.7085 | 25.4 | 28.9845 | 32.571
| BancroftIce Accretion2095RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2095 | 16.9786 | 20.7085 | 25.4 | 28.9845 | 32.571
| BancroftIce Accretion2100RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2100 | 16.9786 | 20.7085 | 25.4 | 28.9845 | 32.571
| BancroftWind2023RCP4.5 | Bancroft | Wind | RCP4.5 | 2023 | 69.5483 | 74.9952 | 80.752 | 86.4817 | 92.2123
| BancroftWind2025RCP4.5 | Bancroft | Wind | RCP4.5 | 2025 | 69.6128 | 75.082 | 80.868 | 86.6215 | 92.378
| BancroftWind2030RCP4.5 | Bancroft | Wind | RCP4.5 | 2030 | 69.6773 | 75.1688 | 80.984 | 86.7613 | 92.5437
| BancroftWind2035RCP4.5 | Bancroft | Wind | RCP4.5 | 2035 | 69.7417 | 75.2556 | 81.1 | 86.9011 | 92.7094
| BancroftWind2040RCP4.5 | Bancroft | Wind | RCP4.5 | 2040 | 69.8062 | 75.3424 | 81.216 | 87.0409 | 92.875
| BancroftWind2045RCP4.5 | Bancroft | Wind | RCP4.5 | 2045 | 69.8707 | 75.4292 | 81.332 | 87.1807 | 93.0407
| BancroftWind2050RCP4.5 | Bancroft | Wind | RCP4.5 | 2050 | 69.9435 | 75.5115 | 81.4256 | 87.2846 | 93.1553
| BancroftWind2055RCP4.5 | Bancroft | Wind | RCP4.5 | 2055 | 69.9517 | 75.5071 | 81.4032 | 87.2487 | 93.1043
| BancroftWind2060RCP4.5 | Bancroft | Wind | RCP4.5 | 2060 | 69.96 | 75.5026 | 81.3808 | 87.2127 | 93.0532
| BancroftWind2065RCP4.5 | Bancroft | Wind | RCP4.5 | 2065 | 69.9683 | 75.4981 | 81.3584 | 87.1768 | 93.0021
| BancroftWind2070RCP4.5 | Bancroft | Wind | RCP4.5 | 2070 | 69.9766 | 75.4937 | 81.336 | 87.1408 | 92.951
| BancroftWind2075RCP4.5 | Bancroft | Wind | RCP4.5 | 2075 | 69.987 | 75.5024 | 81.3413 | 87.1437 | 92.9526
| BancroftWind2080RCP4.5 | Bancroft | Wind | RCP4.5 | 2080 | 69.9973 | 75.511 | 81.3467 | 87.1465 | 92.9541
| BancroftWind2085RCP4.5 | Bancroft | Wind | RCP4.5 | 2085 | 70.0077 | 75.5197 | 81.352 | 87.1494 | 92.9556
| BancroftWind2090RCP4.5 | Bancroft | Wind | RCP4.5 | 2090 | 70.0181 | 75.5284 | 81.3573 | 87.1522 | 92.9571
| BancroftWind2095RCP4.5 | Bancroft | Wind | RCP4.5 | 2095 | 70.0284 | 75.5371 | 81.3627 | 87.1551 | 92.9586
| BancroftWind2100RCP4.5 | Bancroft | Wind | RCP4.5 | 2100 | 70.0388 | 75.5458 | 81.368 | 87.1579 | 92.9602
| BancroftWind2023RCP6.0 | Bancroft | Wind | RCP6.0 | 2023 | 69.5483 | 74.9952 | 80.752 | 86.4817 | 92.2123
| BancroftWind2025RCP6.0 | Bancroft | Wind | RCP6.0 | 2025 | 69.6128 | 75.082 | 80.868 | 86.6215 | 92.378
| BancroftWind2030RCP6.0 | Bancroft | Wind | RCP6.0 | 2030 | 69.6773 | 75.1688 | 80.984 | 86.7613 | 92.5437
| BancroftWind2035RCP6.0 | Bancroft | Wind | RCP6.0 | 2035 | 69.7417 | 75.2556 | 81.1 | 86.9011 | 92.7094
| BancroftWind2040RCP6.0 | Bancroft | Wind | RCP6.0 | 2040 | 69.8062 | 75.3424 | 81.216 | 87.0409 | 92.875
| BancroftWind2045RCP6.0 | Bancroft | Wind | RCP6.0 | 2045 | 69.8707 | 75.4292 | 81.332 | 87.1807 | 93.0407
| BancroftWind2050RCP6.0 | Bancroft | Wind | RCP6.0 | 2050 | 69.9435 | 75.5115 | 81.4256 | 87.2846 | 93.1553
| BancroftWind2055RCP6.0 | Bancroft | Wind | RCP6.0 | 2055 | 69.9517 | 75.5071 | 81.4032 | 87.2487 | 93.1043
| BancroftWind2060RCP6.0 | Bancroft | Wind | RCP6.0 | 2060 | 69.96 | 75.5026 | 81.3808 | 87.2127 | 93.0532
| BancroftWind2065RCP6.0 | Bancroft | Wind | RCP6.0 | 2065 | 69.9683 | 75.4981 | 81.3584 | 87.1768 | 93.0021
| BancroftWind2070RCP6.0 | Bancroft | Wind | RCP6.0 | 2070 | 69.9766 | 75.4937 | 81.336 | 87.1408 | 92.951
| BancroftWind2075RCP6.0 | Bancroft | Wind | RCP6.0 | 2075 | 69.9922 | 75.5067 | 81.344 | 87.1451 | 92.9533
| BancroftWind2080RCP6.0 | Bancroft | Wind | RCP6.0 | 2080 | 70.0077 | 75.5197 | 81.352 | 87.1494 | 92.9556
| BancroftWind2085RCP6.0 | Bancroft | Wind | RCP6.0 | 2085 | 70.0232 | 75.5327 | 81.36 | 87.1536 | 92.9579
| BancroftWind2090RCP6.0 | Bancroft | Wind | RCP6.0 | 2090 | 70.0549 | 75.5458 | 81.3467 | 87.1208 | 92.9024
| BancroftWind2095RCP6.0 | Bancroft | Wind | RCP6.0 | 2095 | 70.071 | 75.5458 | 81.3253 | 87.0837 | 92.8446
| BancroftWind2100RCP6.0 | Bancroft | Wind | RCP6.0 | 2100 | 70.0871 | 75.5458 | 81.304 | 87.0466 | 92.7869
| BancroftWind2023RCP8.5 | Bancroft | Wind | RCP8.5 | 2023 | 69.5483 | 74.9952 | 80.752 | 86.4817 | 92.2123
| BancroftWind2025RCP8.5 | Bancroft | Wind | RCP8.5 | 2025 | 69.6773 | 75.1688 | 80.984 | 86.7613 | 92.5437
| BancroftWind2030RCP8.5 | Bancroft | Wind | RCP8.5 | 2030 | 69.8062 | 75.3424 | 81.216 | 87.0409 | 92.875
| BancroftWind2035RCP8.5 | Bancroft | Wind | RCP8.5 | 2035 | 69.9352 | 75.516 | 81.448 | 87.3206 | 93.2064
| BancroftWind2040RCP8.5 | Bancroft | Wind | RCP8.5 | 2040 | 69.949 | 75.5086 | 81.4107 | 87.2606 | 93.1213
| BancroftWind2045RCP8.5 | Bancroft | Wind | RCP8.5 | 2045 | 69.9628 | 75.5011 | 81.3733 | 87.2007 | 93.0362
| BancroftWind2050RCP8.5 | Bancroft | Wind | RCP8.5 | 2050 | 69.9973 | 75.511 | 81.3467 | 87.1465 | 92.9541
| BancroftWind2055RCP8.5 | Bancroft | Wind | RCP8.5 | 2055 | 70.0181 | 75.5284 | 81.3573 | 87.1522 | 92.9571
| BancroftWind2060RCP8.5 | Bancroft | Wind | RCP8.5 | 2060 | 70.0549 | 75.5458 | 81.3467 | 87.1208 | 92.9024
| BancroftWind2065RCP8.5 | Bancroft | Wind | RCP8.5 | 2065 | 70.071 | 75.5458 | 81.3253 | 87.0837 | 92.8446
| BancroftWind2070RCP8.5 | Bancroft | Wind | RCP8.5 | 2070 | 70.1217 | 75.5656 | 81.3067 | 87.0381 | 92.7656
| BancroftWind2075RCP8.5 | Bancroft | Wind | RCP8.5 | 2075 | 70.1562 | 75.5854 | 81.3093 | 87.0295 | 92.7443
| BancroftWind2080RCP8.5 | Bancroft | Wind | RCP8.5 | 2080 | 70.1908 | 75.6053 | 81.312 | 87.021 | 92.723
| BancroftWind2085RCP8.5 | Bancroft | Wind | RCP8.5 | 2085 | 70.2978 | 75.7578 | 81.52 | 87.2735 | 93.0194
| BancroftWind2090RCP8.5 | Bancroft | Wind | RCP8.5 | 2090 | 70.4049 | 75.9103 | 81.728 | 87.526 | 93.3158
| BancroftWind2095RCP8.5 | Bancroft | Wind | RCP8.5 | 2095 | 70.4049 | 75.9103 | 81.728 | 87.526 | 93.3158
| BancroftWind2100RCP8.5 | Bancroft | Wind | RCP8.5 | 2100 | 70.4049 | 75.9103 | 81.728 | 87.526 | 93.3158
| BarrieIce Accretion2023RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2023 | 15.6684 | 18.7464 | 22.632 | 25.6001 | 28.5453
| BarrieIce Accretion2025RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2025 | 15.663 | 18.7432 | 22.6358 | 25.6088 | 28.5646
| BarrieIce Accretion2030RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2030 | 15.6577 | 18.74 | 22.6397 | 25.6175 | 28.5839
| BarrieIce Accretion2035RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2035 | 15.6524 | 18.7368 | 22.6435 | 25.6261 | 28.6033
| BarrieIce Accretion2040RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2040 | 15.647 | 18.7337 | 22.6473 | 25.6348 | 28.6226
| BarrieIce Accretion2045RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2045 | 15.6417 | 18.7305 | 22.6512 | 25.6435 | 28.6419
| BarrieIce Accretion2050RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2050 | 15.5947 | 18.6967 | 22.6366 | 25.6417 | 28.6554
| BarrieIce Accretion2055RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2055 | 15.5531 | 18.6662 | 22.6182 | 25.6313 | 28.6496
| BarrieIce Accretion2060RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2060 | 15.5115 | 18.6357 | 22.5998 | 25.6209 | 28.6438
| BarrieIce Accretion2065RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2065 | 15.4699 | 18.6051 | 22.5814 | 25.6105 | 28.638
| BarrieIce Accretion2070RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2070 | 15.4283 | 18.5746 | 22.563 | 25.6001 | 28.6322
| BarrieIce Accretion2075RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2075 | 15.4283 | 18.5968 | 22.6128 | 25.6695 | 28.7192
| BarrieIce Accretion2080RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2080 | 15.4283 | 18.6191 | 22.6627 | 25.7388 | 28.8061
| BarrieIce Accretion2085RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2085 | 15.4283 | 18.6414 | 22.7125 | 25.8081 | 28.8931
| BarrieIce Accretion2090RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2090 | 15.4283 | 18.6637 | 22.7623 | 25.8774 | 28.98
| BarrieIce Accretion2095RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2095 | 15.4283 | 18.6859 | 22.8122 | 25.9467 | 29.0669
| BarrieIce Accretion2100RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2100 | 15.4283 | 18.7082 | 22.862 | 26.016 | 29.1539
| BarrieIce Accretion2023RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2023 | 15.6684 | 18.7464 | 22.632 | 25.6001 | 28.5453
| BarrieIce Accretion2025RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2025 | 15.663 | 18.7432 | 22.6358 | 25.6088 | 28.5646
| BarrieIce Accretion2030RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2030 | 15.6577 | 18.74 | 22.6397 | 25.6175 | 28.5839
| BarrieIce Accretion2035RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2035 | 15.6524 | 18.7368 | 22.6435 | 25.6261 | 28.6033
| BarrieIce Accretion2040RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2040 | 15.647 | 18.7337 | 22.6473 | 25.6348 | 28.6226
| BarrieIce Accretion2045RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2045 | 15.6417 | 18.7305 | 22.6512 | 25.6435 | 28.6419
| BarrieIce Accretion2050RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2050 | 15.5947 | 18.6967 | 22.6366 | 25.6417 | 28.6554
| BarrieIce Accretion2055RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2055 | 15.5531 | 18.6662 | 22.6182 | 25.6313 | 28.6496
| BarrieIce Accretion2060RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2060 | 15.5115 | 18.6357 | 22.5998 | 25.6209 | 28.6438
| BarrieIce Accretion2065RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2065 | 15.4699 | 18.6051 | 22.5814 | 25.6105 | 28.638
| BarrieIce Accretion2070RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2070 | 15.4283 | 18.5746 | 22.563 | 25.6001 | 28.6322
| BarrieIce Accretion2075RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2075 | 15.4283 | 18.608 | 22.6377 | 25.7041 | 28.7627
| BarrieIce Accretion2080RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2080 | 15.4283 | 18.6414 | 22.7125 | 25.8081 | 28.8931
| BarrieIce Accretion2085RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2085 | 15.4283 | 18.6748 | 22.7873 | 25.912 | 29.0235
| BarrieIce Accretion2090RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2090 | 15.2523 | 18.53 | 22.6857 | 25.8341 | 28.98
| BarrieIce Accretion2095RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2095 | 15.0762 | 18.3519 | 22.5093 | 25.6521 | 28.8061
| BarrieIce Accretion2100RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2100 | 14.9002 | 18.1737 | 22.333 | 25.4702 | 28.6322
| BarrieIce Accretion2023RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2023 | 15.6684 | 18.7464 | 22.632 | 25.6001 | 28.5453
| BarrieIce Accretion2025RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2025 | 15.6577 | 18.74 | 22.6397 | 25.6175 | 28.5839
| BarrieIce Accretion2030RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2030 | 15.647 | 18.7337 | 22.6473 | 25.6348 | 28.6226
| BarrieIce Accretion2035RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2035 | 15.6364 | 18.7273 | 22.655 | 25.6521 | 28.6612
| BarrieIce Accretion2040RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2040 | 15.567 | 18.6764 | 22.6243 | 25.6348 | 28.6516
| BarrieIce Accretion2045RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2045 | 15.4977 | 18.6255 | 22.5937 | 25.6175 | 28.6419
| BarrieIce Accretion2050RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2050 | 15.4283 | 18.6191 | 22.6627 | 25.7388 | 28.8061
| BarrieIce Accretion2055RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2055 | 15.4283 | 18.6637 | 22.7623 | 25.8774 | 28.98
| BarrieIce Accretion2060RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2060 | 15.2523 | 18.53 | 22.6857 | 25.8341 | 28.98
| BarrieIce Accretion2065RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2065 | 15.0762 | 18.3519 | 22.5093 | 25.6521 | 28.8061
| BarrieIce Accretion2070RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2070 | 14.6441 | 17.9191 | 22.0647 | 25.2016 | 28.3521
| BarrieIce Accretion2075RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2075 | 14.388 | 17.6646 | 21.7963 | 24.9331 | 28.072
| BarrieIce Accretion2080RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2080 | 14.1319 | 17.4101 | 21.528 | 24.6645 | 27.7918
| BarrieIce Accretion2085RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2085 | 13.4758 | 16.6465 | 20.6425 | 23.6769 | 26.6906
| BarrieIce Accretion2090RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2090 | 12.8196 | 15.8829 | 19.757 | 22.6893 | 25.5893
| BarrieIce Accretion2095RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2095 | 12.8196 | 15.8829 | 19.757 | 22.6893 | 25.5893
| BarrieIce Accretion2100RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2100 | 12.8196 | 15.8829 | 19.757 | 22.6893 | 25.5893
| BarrieWind2023RCP4.5 | Barrie | Wind | RCP4.5 | 2023 | 76.374 | 82.2738 | 88.484 | 94.6967 | 100.9019
| BarrieWind2025RCP4.5 | Barrie | Wind | RCP4.5 | 2025 | 76.3955 | 82.301 | 88.5192 | 94.7375 | 100.9503
| BarrieWind2030RCP4.5 | Barrie | Wind | RCP4.5 | 2030 | 76.417 | 82.3283 | 88.5544 | 94.7783 | 100.9988
| BarrieWind2035RCP4.5 | Barrie | Wind | RCP4.5 | 2035 | 76.4386 | 82.3556 | 88.5896 | 94.8191 | 101.0473
| BarrieWind2040RCP4.5 | Barrie | Wind | RCP4.5 | 2040 | 76.4601 | 82.3829 | 88.6248 | 94.8599 | 101.0958
| BarrieWind2045RCP4.5 | Barrie | Wind | RCP4.5 | 2045 | 76.4816 | 82.4102 | 88.66 | 94.9007 | 101.1443
| BarrieWind2050RCP4.5 | Barrie | Wind | RCP4.5 | 2050 | 76.6232 | 82.5766 | 88.8554 | 95.1204 | 101.3914
| BarrieWind2055RCP4.5 | Barrie | Wind | RCP4.5 | 2055 | 76.7433 | 82.7157 | 89.0155 | 95.2993 | 101.5901
| BarrieWind2060RCP4.5 | Barrie | Wind | RCP4.5 | 2060 | 76.8633 | 82.8548 | 89.1757 | 95.4782 | 101.7887
| BarrieWind2065RCP4.5 | Barrie | Wind | RCP4.5 | 2065 | 76.9834 | 82.9939 | 89.3358 | 95.6571 | 101.9873
| BarrieWind2070RCP4.5 | Barrie | Wind | RCP4.5 | 2070 | 77.1035 | 83.1331 | 89.496 | 95.836 | 102.186
| BarrieWind2075RCP4.5 | Barrie | Wind | RCP4.5 | 2075 | 77.1617 | 83.2095 | 89.5957 | 95.9553 | 102.3231
| BarrieWind2080RCP4.5 | Barrie | Wind | RCP4.5 | 2080 | 77.22 | 83.2858 | 89.6955 | 96.0746 | 102.4602
| BarrieWind2085RCP4.5 | Barrie | Wind | RCP4.5 | 2085 | 77.2782 | 83.3622 | 89.7952 | 96.1939 | 102.5973
| BarrieWind2090RCP4.5 | Barrie | Wind | RCP4.5 | 2090 | 77.3365 | 83.4386 | 89.8949 | 96.3131 | 102.7344
| BarrieWind2095RCP4.5 | Barrie | Wind | RCP4.5 | 2095 | 77.3947 | 83.515 | 89.9947 | 96.4324 | 102.8715
| BarrieWind2100RCP4.5 | Barrie | Wind | RCP4.5 | 2100 | 77.453 | 83.5914 | 90.0944 | 96.5517 | 103.0086
| BarrieWind2023RCP6.0 | Barrie | Wind | RCP6.0 | 2023 | 76.374 | 82.2738 | 88.484 | 94.6967 | 100.9019
| BarrieWind2025RCP6.0 | Barrie | Wind | RCP6.0 | 2025 | 76.3955 | 82.301 | 88.5192 | 94.7375 | 100.9503
| BarrieWind2030RCP6.0 | Barrie | Wind | RCP6.0 | 2030 | 76.417 | 82.3283 | 88.5544 | 94.7783 | 100.9988
| BarrieWind2035RCP6.0 | Barrie | Wind | RCP6.0 | 2035 | 76.4386 | 82.3556 | 88.5896 | 94.8191 | 101.0473
| BarrieWind2040RCP6.0 | Barrie | Wind | RCP6.0 | 2040 | 76.4601 | 82.3829 | 88.6248 | 94.8599 | 101.0958
| BarrieWind2045RCP6.0 | Barrie | Wind | RCP6.0 | 2045 | 76.4816 | 82.4102 | 88.66 | 94.9007 | 101.1443
| BarrieWind2050RCP6.0 | Barrie | Wind | RCP6.0 | 2050 | 76.6232 | 82.5766 | 88.8554 | 95.1204 | 101.3914
| BarrieWind2055RCP6.0 | Barrie | Wind | RCP6.0 | 2055 | 76.7433 | 82.7157 | 89.0155 | 95.2993 | 101.5901
| BarrieWind2060RCP6.0 | Barrie | Wind | RCP6.0 | 2060 | 76.8633 | 82.8548 | 89.1757 | 95.4782 | 101.7887
| BarrieWind2065RCP6.0 | Barrie | Wind | RCP6.0 | 2065 | 76.9834 | 82.9939 | 89.3358 | 95.6571 | 101.9873
| BarrieWind2070RCP6.0 | Barrie | Wind | RCP6.0 | 2070 | 77.1035 | 83.1331 | 89.496 | 95.836 | 102.186
| BarrieWind2075RCP6.0 | Barrie | Wind | RCP6.0 | 2075 | 77.1908 | 83.2476 | 89.6456 | 96.015 | 102.3916
| BarrieWind2080RCP6.0 | Barrie | Wind | RCP6.0 | 2080 | 77.2782 | 83.3622 | 89.7952 | 96.1939 | 102.5973
| BarrieWind2085RCP6.0 | Barrie | Wind | RCP6.0 | 2085 | 77.3656 | 83.4768 | 89.9448 | 96.3728 | 102.8029
| BarrieWind2090RCP6.0 | Barrie | Wind | RCP6.0 | 2090 | 77.7291 | 83.9242 | 90.4933 | 97.0099 | 103.5302
| BarrieWind2095RCP6.0 | Barrie | Wind | RCP6.0 | 2095 | 78.0052 | 84.257 | 90.8923 | 97.4682 | 104.0519
| BarrieWind2100RCP6.0 | Barrie | Wind | RCP6.0 | 2100 | 78.2812 | 84.5898 | 91.2912 | 97.9264 | 104.5736
| BarrieWind2023RCP8.5 | Barrie | Wind | RCP8.5 | 2023 | 76.374 | 82.2738 | 88.484 | 94.6967 | 100.9019
| BarrieWind2025RCP8.5 | Barrie | Wind | RCP8.5 | 2025 | 76.417 | 82.3283 | 88.5544 | 94.7783 | 100.9988
| BarrieWind2030RCP8.5 | Barrie | Wind | RCP8.5 | 2030 | 76.4601 | 82.3829 | 88.6248 | 94.8599 | 101.0958
| BarrieWind2035RCP8.5 | Barrie | Wind | RCP8.5 | 2035 | 76.5032 | 82.4374 | 88.6952 | 94.9415 | 101.1928
| BarrieWind2040RCP8.5 | Barrie | Wind | RCP8.5 | 2040 | 76.7033 | 82.6693 | 88.9621 | 95.2397 | 101.5238
| BarrieWind2045RCP8.5 | Barrie | Wind | RCP8.5 | 2045 | 76.9034 | 82.9012 | 89.2291 | 95.5379 | 101.8549
| BarrieWind2050RCP8.5 | Barrie | Wind | RCP8.5 | 2050 | 77.22 | 83.2858 | 89.6955 | 96.0746 | 102.4602
| BarrieWind2055RCP8.5 | Barrie | Wind | RCP8.5 | 2055 | 77.3365 | 83.4386 | 89.8949 | 96.3131 | 102.7344
| BarrieWind2060RCP8.5 | Barrie | Wind | RCP8.5 | 2060 | 77.7291 | 83.9242 | 90.4933 | 97.0099 | 103.5302
| BarrieWind2065RCP8.5 | Barrie | Wind | RCP8.5 | 2065 | 78.0052 | 84.257 | 90.8923 | 97.4682 | 104.0519
| BarrieWind2070RCP8.5 | Barrie | Wind | RCP8.5 | 2070 | 78.4282 | 84.7671 | 91.5112 | 98.1806 | 104.8612
| BarrieWind2075RCP8.5 | Barrie | Wind | RCP8.5 | 2075 | 78.5751 | 84.9445 | 91.7312 | 98.4349 | 105.1487
| BarrieWind2080RCP8.5 | Barrie | Wind | RCP8.5 | 2080 | 78.722 | 85.1218 | 91.9512 | 98.6891 | 105.4363
| BarrieWind2085RCP8.5 | Barrie | Wind | RCP8.5 | 2085 | 78.7524 | 85.1545 | 91.982 | 98.7221 | 105.4664
| BarrieWind2090RCP8.5 | Barrie | Wind | RCP8.5 | 2090 | 78.7828 | 85.1873 | 92.0128 | 98.755 | 105.4965
| BarrieWind2095RCP8.5 | Barrie | Wind | RCP8.5 | 2095 | 78.7828 | 85.1873 | 92.0128 | 98.755 | 105.4965
| BarrieWind2100RCP8.5 | Barrie | Wind | RCP8.5 | 2100 | 78.7828 | 85.1873 | 92.0128 | 98.755 | 105.4965
| BarriefieldIce Accretion2023RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2023 | 18.092 | 21.5584 | 25.974 | 29.3506 | 32.6945
| BarriefieldIce Accretion2025RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2025 | 18.1674 | 21.6627 | 26.1127 | 29.5122 | 32.8856
| BarriefieldIce Accretion2030RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2030 | 18.2428 | 21.767 | 26.2513 | 29.6738 | 33.0767
| BarriefieldIce Accretion2035RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2035 | 18.3181 | 21.8713 | 26.39 | 29.8354 | 33.2678
| BarriefieldIce Accretion2040RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2040 | 18.3935 | 21.9756 | 26.5287 | 29.997 | 33.4589
| BarriefieldIce Accretion2045RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2045 | 18.4689 | 22.0799 | 26.6673 | 30.1586 | 33.65
| BarriefieldIce Accretion2050RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2050 | 18.443 | 22.0807 | 26.6968 | 30.2085 | 33.7297
| BarriefieldIce Accretion2055RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2055 | 18.3417 | 21.9771 | 26.5876 | 30.0969 | 33.6183
| BarriefieldIce Accretion2060RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2060 | 18.2404 | 21.8735 | 26.4784 | 29.9852 | 33.5069
| BarriefieldIce Accretion2065RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2065 | 18.139 | 21.7699 | 26.3692 | 29.8736 | 33.3955
| BarriefieldIce Accretion2070RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2070 | 18.0377 | 21.6663 | 26.26 | 29.7619 | 33.2842
| BarriefieldIce Accretion2075RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2075 | 18.0498 | 21.7059 | 26.3293 | 29.855 | 33.3988
| BarriefieldIce Accretion2080RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2080 | 18.0618 | 21.7454 | 26.3987 | 29.948 | 33.5135
| BarriefieldIce Accretion2085RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2085 | 18.0739 | 21.785 | 26.468 | 30.041 | 33.6281
| BarriefieldIce Accretion2090RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2090 | 18.086 | 21.8246 | 26.5373 | 30.1341 | 33.7428
| BarriefieldIce Accretion2095RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2095 | 18.098 | 21.8641 | 26.6067 | 30.2271 | 33.8575
| BarriefieldIce Accretion2100RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2100 | 18.1101 | 21.9037 | 26.676 | 30.3202 | 33.9721
| BarriefieldIce Accretion2023RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2023 | 18.092 | 21.5584 | 25.974 | 29.3506 | 32.6945
| BarriefieldIce Accretion2025RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2025 | 18.1674 | 21.6627 | 26.1127 | 29.5122 | 32.8856
| BarriefieldIce Accretion2030RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2030 | 18.2428 | 21.767 | 26.2513 | 29.6738 | 33.0767
| BarriefieldIce Accretion2035RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2035 | 18.3181 | 21.8713 | 26.39 | 29.8354 | 33.2678
| BarriefieldIce Accretion2040RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2040 | 18.3935 | 21.9756 | 26.5287 | 29.997 | 33.4589
| BarriefieldIce Accretion2045RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2045 | 18.4689 | 22.0799 | 26.6673 | 30.1586 | 33.65
| BarriefieldIce Accretion2050RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2050 | 18.443 | 22.0807 | 26.6968 | 30.2085 | 33.7297
| BarriefieldIce Accretion2055RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2055 | 18.3417 | 21.9771 | 26.5876 | 30.0969 | 33.6183
| BarriefieldIce Accretion2060RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2060 | 18.2404 | 21.8735 | 26.4784 | 29.9852 | 33.5069
| BarriefieldIce Accretion2065RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2065 | 18.139 | 21.7699 | 26.3692 | 29.8736 | 33.3955
| BarriefieldIce Accretion2070RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2070 | 18.0377 | 21.6663 | 26.26 | 29.7619 | 33.2842
| BarriefieldIce Accretion2075RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2075 | 18.0558 | 21.7257 | 26.364 | 29.9015 | 33.4562
| BarriefieldIce Accretion2080RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2080 | 18.0739 | 21.785 | 26.468 | 30.041 | 33.6281
| BarriefieldIce Accretion2085RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2085 | 18.092 | 21.8444 | 26.572 | 30.1806 | 33.8001
| BarriefieldIce Accretion2090RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2090 | 17.8025 | 21.5584 | 26.2947 | 29.899 | 33.5135
| BarriefieldIce Accretion2095RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2095 | 17.495 | 21.2131 | 25.9133 | 29.4779 | 33.0548
| BarriefieldIce Accretion2100RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2100 | 17.1874 | 20.8679 | 25.532 | 29.0568 | 32.5962
| BarriefieldIce Accretion2023RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2023 | 18.092 | 21.5584 | 25.974 | 29.3506 | 32.6945
| BarriefieldIce Accretion2025RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2025 | 18.2428 | 21.767 | 26.2513 | 29.6738 | 33.0767
| BarriefieldIce Accretion2030RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2030 | 18.3935 | 21.9756 | 26.5287 | 29.997 | 33.4589
| BarriefieldIce Accretion2035RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2035 | 18.5443 | 22.1842 | 26.806 | 30.3202 | 33.8411
| BarriefieldIce Accretion2040RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2040 | 18.3754 | 22.0116 | 26.624 | 30.1341 | 33.6554
| BarriefieldIce Accretion2045RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2045 | 18.2066 | 21.839 | 26.442 | 29.948 | 33.4698
| BarriefieldIce Accretion2050RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2050 | 18.0618 | 21.7454 | 26.3987 | 29.948 | 33.5135
| BarriefieldIce Accretion2055RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2055 | 18.086 | 21.8246 | 26.5373 | 30.1341 | 33.7428
| BarriefieldIce Accretion2060RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2060 | 17.8025 | 21.5584 | 26.2947 | 29.899 | 33.5135
| BarriefieldIce Accretion2065RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2065 | 17.495 | 21.2131 | 25.9133 | 29.4779 | 33.0548
| BarriefieldIce Accretion2070RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2070 | 16.9401 | 20.6089 | 25.246 | 28.763 | 32.2795
| BarriefieldIce Accretion2075RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2075 | 16.6929 | 20.3499 | 24.96 | 28.4692 | 31.9628
| BarriefieldIce Accretion2080RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2080 | 16.4456 | 20.091 | 24.674 | 28.1754 | 31.6462
| BarriefieldIce Accretion2085RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2085 | 15.8305 | 19.368 | 23.816 | 27.2059 | 30.5651
| BarriefieldIce Accretion2090RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2090 | 15.2154 | 18.6451 | 22.958 | 26.2363 | 29.484
| BarriefieldIce Accretion2095RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2095 | 15.2154 | 18.6451 | 22.958 | 26.2363 | 29.484
| BarriefieldIce Accretion2100RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2100 | 15.2154 | 18.6451 | 22.958 | 26.2363 | 29.484
| BarriefieldWind2023RCP4.5 | Barriefield | Wind | RCP4.5 | 2023 | 87.8991 | 94.5754 | 101.592 | 108.627 | 115.6637
| BarriefieldWind2025RCP4.5 | Barriefield | Wind | RCP4.5 | 2025 | 87.8829 | 94.547 | 101.5444 | 108.5652 | 115.5862
| BarriefieldWind2030RCP4.5 | Barriefield | Wind | RCP4.5 | 2030 | 87.8668 | 94.5185 | 101.4968 | 108.5033 | 115.5087
| BarriefieldWind2035RCP4.5 | Barriefield | Wind | RCP4.5 | 2035 | 87.8506 | 94.49 | 101.4492 | 108.4415 | 115.4312
| BarriefieldWind2040RCP4.5 | Barriefield | Wind | RCP4.5 | 2040 | 87.8345 | 94.4616 | 101.4016 | 108.3797 | 115.3536
| BarriefieldWind2045RCP4.5 | Barriefield | Wind | RCP4.5 | 2045 | 87.8183 | 94.4331 | 101.354 | 108.3178 | 115.2761
| BarriefieldWind2050RCP4.5 | Barriefield | Wind | RCP4.5 | 2050 | 87.9131 | 94.5394 | 101.4716 | 108.4459 | 115.4149
| BarriefieldWind2055RCP4.5 | Barriefield | Wind | RCP4.5 | 2055 | 88.0241 | 94.6741 | 101.6369 | 108.6358 | 115.6312
| BarriefieldWind2060RCP4.5 | Barriefield | Wind | RCP4.5 | 2060 | 88.1351 | 94.8088 | 101.8021 | 108.8257 | 115.8474
| BarriefieldWind2065RCP4.5 | Barriefield | Wind | RCP4.5 | 2065 | 88.2461 | 94.9435 | 101.9674 | 109.0156 | 116.0637
| BarriefieldWind2070RCP4.5 | Barriefield | Wind | RCP4.5 | 2070 | 88.357 | 95.0782 | 102.1326 | 109.2055 | 116.28
| BarriefieldWind2075RCP4.5 | Barriefield | Wind | RCP4.5 | 2075 | 88.4774 | 95.2426 | 102.3502 | 109.4674 | 116.5862
| BarriefieldWind2080RCP4.5 | Barriefield | Wind | RCP4.5 | 2080 | 88.5978 | 95.407 | 102.5678 | 109.7294 | 116.8924
| BarriefieldWind2085RCP4.5 | Barriefield | Wind | RCP4.5 | 2085 | 88.7182 | 95.5714 | 102.7854 | 109.9913 | 117.1986
| BarriefieldWind2090RCP4.5 | Barriefield | Wind | RCP4.5 | 2090 | 88.8385 | 95.7359 | 103.003 | 110.2532 | 117.5048
| BarriefieldWind2095RCP4.5 | Barriefield | Wind | RCP4.5 | 2095 | 88.9589 | 95.9003 | 103.2206 | 110.5152 | 117.811
| BarriefieldWind2100RCP4.5 | Barriefield | Wind | RCP4.5 | 2100 | 89.0793 | 96.0647 | 103.4382 | 110.7771 | 118.1172
| BarriefieldWind2023RCP6.0 | Barriefield | Wind | RCP6.0 | 2023 | 87.8991 | 94.5754 | 101.592 | 108.627 | 115.6637
| BarriefieldWind2025RCP6.0 | Barriefield | Wind | RCP6.0 | 2025 | 87.8829 | 94.547 | 101.5444 | 108.5652 | 115.5862
| BarriefieldWind2030RCP6.0 | Barriefield | Wind | RCP6.0 | 2030 | 87.8668 | 94.5185 | 101.4968 | 108.5033 | 115.5087
| BarriefieldWind2035RCP6.0 | Barriefield | Wind | RCP6.0 | 2035 | 87.8506 | 94.49 | 101.4492 | 108.4415 | 115.4312
| BarriefieldWind2040RCP6.0 | Barriefield | Wind | RCP6.0 | 2040 | 87.8345 | 94.4616 | 101.4016 | 108.3797 | 115.3536
| BarriefieldWind2045RCP6.0 | Barriefield | Wind | RCP6.0 | 2045 | 87.8183 | 94.4331 | 101.354 | 108.3178 | 115.2761
| BarriefieldWind2050RCP6.0 | Barriefield | Wind | RCP6.0 | 2050 | 87.9131 | 94.5394 | 101.4716 | 108.4459 | 115.4149
| BarriefieldWind2055RCP6.0 | Barriefield | Wind | RCP6.0 | 2055 | 88.0241 | 94.6741 | 101.6369 | 108.6358 | 115.6312
| BarriefieldWind2060RCP6.0 | Barriefield | Wind | RCP6.0 | 2060 | 88.1351 | 94.8088 | 101.8021 | 108.8257 | 115.8474
| BarriefieldWind2065RCP6.0 | Barriefield | Wind | RCP6.0 | 2065 | 88.2461 | 94.9435 | 101.9674 | 109.0156 | 116.0637
| BarriefieldWind2070RCP6.0 | Barriefield | Wind | RCP6.0 | 2070 | 88.357 | 95.0782 | 102.1326 | 109.2055 | 116.28
| BarriefieldWind2075RCP6.0 | Barriefield | Wind | RCP6.0 | 2075 | 88.5376 | 95.3248 | 102.459 | 109.5984 | 116.7393
| BarriefieldWind2080RCP6.0 | Barriefield | Wind | RCP6.0 | 2080 | 88.7182 | 95.5714 | 102.7854 | 109.9913 | 117.1986
| BarriefieldWind2085RCP6.0 | Barriefield | Wind | RCP6.0 | 2085 | 88.8987 | 95.8181 | 103.1118 | 110.3842 | 117.6579
| BarriefieldWind2090RCP6.0 | Barriefield | Wind | RCP6.0 | 2090 | 89.2818 | 96.3272 | 103.7782 | 111.1846 | 118.5901
| BarriefieldWind2095RCP6.0 | Barriefield | Wind | RCP6.0 | 2095 | 89.4844 | 96.5896 | 104.1182 | 111.592 | 119.063
| BarriefieldWind2100RCP6.0 | Barriefield | Wind | RCP6.0 | 2100 | 89.687 | 96.8521 | 104.4582 | 111.9995 | 119.5358
| BarriefieldWind2023RCP8.5 | Barriefield | Wind | RCP8.5 | 2023 | 87.8991 | 94.5754 | 101.592 | 108.627 | 115.6637
| BarriefieldWind2025RCP8.5 | Barriefield | Wind | RCP8.5 | 2025 | 87.8668 | 94.5185 | 101.4968 | 108.5033 | 115.5087
| BarriefieldWind2030RCP8.5 | Barriefield | Wind | RCP8.5 | 2030 | 87.8345 | 94.4616 | 101.4016 | 108.3797 | 115.3536
| BarriefieldWind2035RCP8.5 | Barriefield | Wind | RCP8.5 | 2035 | 87.8022 | 94.4047 | 101.3064 | 108.256 | 115.1986
| BarriefieldWind2040RCP8.5 | Barriefield | Wind | RCP8.5 | 2040 | 87.9871 | 94.6292 | 101.5818 | 108.5725 | 115.5591
| BarriefieldWind2045RCP8.5 | Barriefield | Wind | RCP8.5 | 2045 | 88.1721 | 94.8537 | 101.8572 | 108.889 | 115.9195
| BarriefieldWind2050RCP8.5 | Barriefield | Wind | RCP8.5 | 2050 | 88.5978 | 95.407 | 102.5678 | 109.7294 | 116.8924
| BarriefieldWind2055RCP8.5 | Barriefield | Wind | RCP8.5 | 2055 | 88.8385 | 95.7359 | 103.003 | 110.2532 | 117.5048
| BarriefieldWind2060RCP8.5 | Barriefield | Wind | RCP8.5 | 2060 | 89.2818 | 96.3272 | 103.7782 | 111.1846 | 118.5901
| BarriefieldWind2065RCP8.5 | Barriefield | Wind | RCP8.5 | 2065 | 89.4844 | 96.5896 | 104.1182 | 111.592 | 119.063
| BarriefieldWind2070RCP8.5 | Barriefield | Wind | RCP8.5 | 2070 | 89.7604 | 96.9596 | 104.6078 | 112.185 | 119.7568
| BarriefieldWind2075RCP8.5 | Barriefield | Wind | RCP8.5 | 2075 | 89.8338 | 97.0671 | 104.7574 | 112.3705 | 119.9777
| BarriefieldWind2080RCP8.5 | Barriefield | Wind | RCP8.5 | 2080 | 89.9072 | 97.1746 | 104.907 | 112.5561 | 120.1986
| BarriefieldWind2085RCP8.5 | Barriefield | Wind | RCP8.5 | 2085 | 90.0789 | 97.4117 | 105.2283 | 112.9435 | 120.6638
| BarriefieldWind2090RCP8.5 | Barriefield | Wind | RCP8.5 | 2090 | 90.2507 | 97.6489 | 105.5496 | 113.331 | 121.1289
| BarriefieldWind2095RCP8.5 | Barriefield | Wind | RCP8.5 | 2095 | 90.2507 | 97.6489 | 105.5496 | 113.331 | 121.1289
| BarriefieldWind2100RCP8.5 | Barriefield | Wind | RCP8.5 | 2100 | 90.2507 | 97.6489 | 105.5496 | 113.331 | 121.1289
| BeavertonIce Accretion2023RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
| BeavertonIce Accretion2025RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
| BeavertonIce Accretion2030RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
| BeavertonIce Accretion2035RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
| BeavertonIce Accretion2040RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
| BeavertonIce Accretion2045RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
| BeavertonIce Accretion2050RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
| BeavertonIce Accretion2055RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
| BeavertonIce Accretion2060RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
| BeavertonIce Accretion2065RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
| BeavertonIce Accretion2070RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
| BeavertonIce Accretion2075RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2075 | 17.2744 | 20.8814 | 25.4167 | 28.8762 | 32.34
| BeavertonIce Accretion2080RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2080 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
| BeavertonIce Accretion2085RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2085 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
| BeavertonIce Accretion2090RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2090 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
| BeavertonIce Accretion2095RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2095 | 17.2048 | 20.9091 | 25.5833 | 29.121 | 32.676
| BeavertonIce Accretion2100RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2100 | 17.1874 | 20.916 | 25.625 | 29.1822 | 32.76
| BeavertonIce Accretion2023RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
| BeavertonIce Accretion2025RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
| BeavertonIce Accretion2030RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
| BeavertonIce Accretion2035RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
| BeavertonIce Accretion2040RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
| BeavertonIce Accretion2045RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
| BeavertonIce Accretion2050RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
| BeavertonIce Accretion2055RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
| BeavertonIce Accretion2060RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
| BeavertonIce Accretion2065RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
| BeavertonIce Accretion2070RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
| BeavertonIce Accretion2075RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2075 | 17.2657 | 20.8849 | 25.4375 | 28.9068 | 32.382
| BeavertonIce Accretion2080RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2080 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
| BeavertonIce Accretion2085RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2085 | 17.2135 | 20.9056 | 25.5625 | 29.0904 | 32.634
| BeavertonIce Accretion2090RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2090 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
| BeavertonIce Accretion2095RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2095 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
| BeavertonIce Accretion2100RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2100 | 16.2654 | 19.8992 | 24.5 | 27.9957 | 31.4685
| BeavertonIce Accretion2023RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
| BeavertonIce Accretion2025RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2025 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
| BeavertonIce Accretion2030RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2030 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
| BeavertonIce Accretion2035RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2035 | 17.6919 | 21.2272 | 25.725 | 29.154 | 32.6025
| BeavertonIce Accretion2040RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2040 | 17.5585 | 21.1097 | 25.6083 | 29.041 | 32.487
| BeavertonIce Accretion2045RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2045 | 17.4251 | 20.9921 | 25.4917 | 28.928 | 32.3715
| BeavertonIce Accretion2050RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2050 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
| BeavertonIce Accretion2055RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2055 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
| BeavertonIce Accretion2060RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2060 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
| BeavertonIce Accretion2065RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2065 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
| BeavertonIce Accretion2070RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2070 | 15.9987 | 19.6226 | 24.2083 | 27.685 | 31.143
| BeavertonIce Accretion2075RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2075 | 15.7319 | 19.3459 | 23.9167 | 27.3742 | 30.8175
| BeavertonIce Accretion2080RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2080 | 15.4652 | 19.0693 | 23.625 | 27.0635 | 30.492
| BeavertonIce Accretion2085RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2085 | 14.8911 | 18.426 | 22.8875 | 26.2584 | 29.6258
| BeavertonIce Accretion2090RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2090 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
| BeavertonIce Accretion2095RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2095 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
| BeavertonIce Accretion2100RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2100 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
| BeavertonWind2023RCP4.5 | Beaverton | Wind | RCP4.5 | 2023 | 73.8804 | 79.5796 | 85.5695 | 91.5594 | 97.5589
| BeavertonWind2025RCP4.5 | Beaverton | Wind | RCP4.5 | 2025 | 73.9134 | 79.6231 | 85.6276 | 91.6306 | 97.6413
| BeavertonWind2030RCP4.5 | Beaverton | Wind | RCP4.5 | 2030 | 73.9465 | 79.6666 | 85.6857 | 91.7019 | 97.7236
| BeavertonWind2035RCP4.5 | Beaverton | Wind | RCP4.5 | 2035 | 73.9795 | 79.7101 | 85.7437 | 91.7731 | 97.806
| BeavertonWind2040RCP4.5 | Beaverton | Wind | RCP4.5 | 2040 | 74.0125 | 79.7535 | 85.8018 | 91.8443 | 97.8884
| BeavertonWind2045RCP4.5 | Beaverton | Wind | RCP4.5 | 2045 | 74.0456 | 79.797 | 85.8599 | 91.9156 | 97.9707
| BeavertonWind2050RCP4.5 | Beaverton | Wind | RCP4.5 | 2050 | 74.1446 | 79.918 | 86.0081 | 92.0869 | 98.1655
| BeavertonWind2055RCP4.5 | Beaverton | Wind | RCP4.5 | 2055 | 74.2107 | 79.9954 | 86.0982 | 92.1869 | 98.2779
| BeavertonWind2060RCP4.5 | Beaverton | Wind | RCP4.5 | 2060 | 74.2768 | 80.0729 | 86.1883 | 92.287 | 98.3903
| BeavertonWind2065RCP4.5 | Beaverton | Wind | RCP4.5 | 2065 | 74.3428 | 80.1504 | 86.2784 | 92.387 | 98.5027
| BeavertonWind2070RCP4.5 | Beaverton | Wind | RCP4.5 | 2070 | 74.4089 | 80.2278 | 86.3685 | 92.4871 | 98.6151
| BeavertonWind2075RCP4.5 | Beaverton | Wind | RCP4.5 | 2075 | 74.481 | 80.3174 | 86.479 | 92.6174 | 98.7637
| BeavertonWind2080RCP4.5 | Beaverton | Wind | RCP4.5 | 2080 | 74.5532 | 80.407 | 86.5895 | 92.7478 | 98.9123
| BeavertonWind2085RCP4.5 | Beaverton | Wind | RCP4.5 | 2085 | 74.6254 | 80.4966 | 86.7 | 92.8781 | 99.0609
| BeavertonWind2090RCP4.5 | Beaverton | Wind | RCP4.5 | 2090 | 74.6976 | 80.5862 | 86.8105 | 93.0085 | 99.2094
| BeavertonWind2095RCP4.5 | Beaverton | Wind | RCP4.5 | 2095 | 74.7697 | 80.6758 | 86.921 | 93.1389 | 99.358
| BeavertonWind2100RCP4.5 | Beaverton | Wind | RCP4.5 | 2100 | 74.8419 | 80.7654 | 87.0315 | 93.2692 | 99.5066
| BeavertonWind2023RCP6.0 | Beaverton | Wind | RCP6.0 | 2023 | 73.8804 | 79.5796 | 85.5695 | 91.5594 | 97.5589
| BeavertonWind2025RCP6.0 | Beaverton | Wind | RCP6.0 | 2025 | 73.9134 | 79.6231 | 85.6276 | 91.6306 | 97.6413
| BeavertonWind2030RCP6.0 | Beaverton | Wind | RCP6.0 | 2030 | 73.9465 | 79.6666 | 85.6857 | 91.7019 | 97.7236
| BeavertonWind2035RCP6.0 | Beaverton | Wind | RCP6.0 | 2035 | 73.9795 | 79.7101 | 85.7437 | 91.7731 | 97.806
| BeavertonWind2040RCP6.0 | Beaverton | Wind | RCP6.0 | 2040 | 74.0125 | 79.7535 | 85.8018 | 91.8443 | 97.8884
| BeavertonWind2045RCP6.0 | Beaverton | Wind | RCP6.0 | 2045 | 74.0456 | 79.797 | 85.8599 | 91.9156 | 97.9707
| BeavertonWind2050RCP6.0 | Beaverton | Wind | RCP6.0 | 2050 | 74.1446 | 79.918 | 86.0081 | 92.0869 | 98.1655
| BeavertonWind2055RCP6.0 | Beaverton | Wind | RCP6.0 | 2055 | 74.2107 | 79.9954 | 86.0982 | 92.1869 | 98.2779
| BeavertonWind2060RCP6.0 | Beaverton | Wind | RCP6.0 | 2060 | 74.2768 | 80.0729 | 86.1883 | 92.287 | 98.3903
| BeavertonWind2065RCP6.0 | Beaverton | Wind | RCP6.0 | 2065 | 74.3428 | 80.1504 | 86.2784 | 92.387 | 98.5027
| BeavertonWind2070RCP6.0 | Beaverton | Wind | RCP6.0 | 2070 | 74.4089 | 80.2278 | 86.3685 | 92.4871 | 98.6151
| BeavertonWind2075RCP6.0 | Beaverton | Wind | RCP6.0 | 2075 | 74.5171 | 80.3622 | 86.5343 | 92.6826 | 98.838
| BeavertonWind2080RCP6.0 | Beaverton | Wind | RCP6.0 | 2080 | 74.6254 | 80.4966 | 86.7 | 92.8781 | 99.0609
| BeavertonWind2085RCP6.0 | Beaverton | Wind | RCP6.0 | 2085 | 74.7336 | 80.631 | 86.8658 | 93.0737 | 99.2837
| BeavertonWind2090RCP6.0 | Beaverton | Wind | RCP6.0 | 2090 | 75.0792 | 81.0368 | 87.3488 | 93.6209 | 99.8974
| BeavertonWind2095RCP6.0 | Beaverton | Wind | RCP6.0 | 2095 | 75.3165 | 81.3082 | 87.6662 | 93.9726 | 100.2883
| BeavertonWind2100RCP6.0 | Beaverton | Wind | RCP6.0 | 2100 | 75.5538 | 81.5796 | 87.9835 | 94.3242 | 100.6791
| BeavertonWind2023RCP8.5 | Beaverton | Wind | RCP8.5 | 2023 | 73.8804 | 79.5796 | 85.5695 | 91.5594 | 97.5589
| BeavertonWind2025RCP8.5 | Beaverton | Wind | RCP8.5 | 2025 | 73.9465 | 79.6666 | 85.6857 | 91.7019 | 97.7236
| BeavertonWind2030RCP8.5 | Beaverton | Wind | RCP8.5 | 2030 | 74.0125 | 79.7535 | 85.8018 | 91.8443 | 97.8884
| BeavertonWind2035RCP8.5 | Beaverton | Wind | RCP8.5 | 2035 | 74.0786 | 79.8405 | 85.918 | 91.9868 | 98.0531
| BeavertonWind2040RCP8.5 | Beaverton | Wind | RCP8.5 | 2040 | 74.1887 | 79.9696 | 86.0682 | 92.1536 | 98.2404
| BeavertonWind2045RCP8.5 | Beaverton | Wind | RCP8.5 | 2045 | 74.2988 | 80.0987 | 86.2183 | 92.3203 | 98.4278
| BeavertonWind2050RCP8.5 | Beaverton | Wind | RCP8.5 | 2050 | 74.5532 | 80.407 | 86.5895 | 92.7478 | 98.9123
| BeavertonWind2055RCP8.5 | Beaverton | Wind | RCP8.5 | 2055 | 74.6976 | 80.5862 | 86.8105 | 93.0085 | 99.2094
| BeavertonWind2060RCP8.5 | Beaverton | Wind | RCP8.5 | 2060 | 75.0792 | 81.0368 | 87.3488 | 93.6209 | 99.8974
| BeavertonWind2065RCP8.5 | Beaverton | Wind | RCP8.5 | 2065 | 75.3165 | 81.3082 | 87.6662 | 93.9726 | 100.2883
| BeavertonWind2070RCP8.5 | Beaverton | Wind | RCP8.5 | 2070 | 75.637 | 81.6876 | 88.1167 | 94.4819 | 100.8632
| BeavertonWind2075RCP8.5 | Beaverton | Wind | RCP8.5 | 2075 | 75.7202 | 81.7957 | 88.2498 | 94.6395 | 101.0473
| BeavertonWind2080RCP8.5 | Beaverton | Wind | RCP8.5 | 2080 | 75.8034 | 81.9037 | 88.383 | 94.7972 | 101.2314
| BeavertonWind2085RCP8.5 | Beaverton | Wind | RCP8.5 | 2085 | 75.9979 | 82.1764 | 88.7655 | 95.2656 | 101.7886
| BeavertonWind2090RCP8.5 | Beaverton | Wind | RCP8.5 | 2090 | 76.1924 | 82.4491 | 89.148 | 95.734 | 102.3458
| BeavertonWind2095RCP8.5 | Beaverton | Wind | RCP8.5 | 2095 | 76.1924 | 82.4491 | 89.148 | 95.734 | 102.3458
| BeavertonWind2100RCP8.5 | Beaverton | Wind | RCP8.5 | 2100 | 76.1924 | 82.4491 | 89.148 | 95.734 | 102.3458
| BellevilleIce Accretion2023RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| BellevilleIce Accretion2025RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
| BellevilleIce Accretion2030RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| BellevilleIce Accretion2035RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
| BellevilleIce Accretion2040RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| BellevilleIce Accretion2045RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
| BellevilleIce Accretion2050RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
| BellevilleIce Accretion2055RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
| BellevilleIce Accretion2060RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
| BellevilleIce Accretion2065RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
| BellevilleIce Accretion2070RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
| BellevilleIce Accretion2075RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2075 | 16.8859 | 20.3972 | 24.8292 | 28.2123 | 31.5682
| BellevilleIce Accretion2080RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2080 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
| BellevilleIce Accretion2085RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2085 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
| BellevilleIce Accretion2090RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2090 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
| BellevilleIce Accretion2095RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2095 | 16.7235 | 20.3142 | 24.8458 | 28.2877 | 31.7152
| BellevilleIce Accretion2100RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.2935 | 24.85 | 28.3065 | 31.752
| BellevilleIce Accretion2023RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| BellevilleIce Accretion2025RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
| BellevilleIce Accretion2030RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| BellevilleIce Accretion2035RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
| BellevilleIce Accretion2040RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| BellevilleIce Accretion2045RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
| BellevilleIce Accretion2050RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
| BellevilleIce Accretion2055RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
| BellevilleIce Accretion2060RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
| BellevilleIce Accretion2065RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
| BellevilleIce Accretion2070RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
| BellevilleIce Accretion2075RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2075 | 16.8656 | 20.3869 | 24.8313 | 28.2217 | 31.5866
| BellevilleIce Accretion2080RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2080 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
| BellevilleIce Accretion2085RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2085 | 16.7438 | 20.3246 | 24.8438 | 28.2782 | 31.6969
| BellevilleIce Accretion2090RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2090 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
| BellevilleIce Accretion2095RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2095 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
| BellevilleIce Accretion2100RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2100 | 15.6565 | 19.173 | 23.6 | 26.9505 | 30.2715
| BellevilleIce Accretion2023RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| BellevilleIce Accretion2025RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2025 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| BellevilleIce Accretion2030RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2030 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| BellevilleIce Accretion2035RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2035 | 17.6745 | 21.2272 | 25.725 | 29.154 | 32.571
| BellevilleIce Accretion2040RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2040 | 17.4251 | 20.9575 | 25.425 | 28.8338 | 32.2245
| BellevilleIce Accretion2045RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2045 | 17.1758 | 20.6877 | 25.125 | 28.5137 | 31.878
| BellevilleIce Accretion2050RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2050 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
| BellevilleIce Accretion2055RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2055 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
| BellevilleIce Accretion2060RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2060 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
| BellevilleIce Accretion2065RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2065 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
| BellevilleIce Accretion2070RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2070 | 15.2216 | 18.6888 | 23.05 | 26.3478 | 29.631
| BellevilleIce Accretion2075RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2075 | 14.7867 | 18.2047 | 22.5 | 25.7452 | 28.9905
| BellevilleIce Accretion2080RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2080 | 14.3518 | 17.7205 | 21.95 | 25.1425 | 28.35
| BellevilleIce Accretion2085RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2085 | 13.6908 | 16.9424 | 21.025 | 24.0972 | 27.1845
| BellevilleIce Accretion2090RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2090 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| BellevilleIce Accretion2095RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2095 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| BellevilleIce Accretion2100RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2100 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| BellevilleWind2023RCP4.5 | Belleville | Wind | RCP4.5 | 2023 | 85.129 | 91.7051 | 98.6174 | 105.5311 | 112.4462
| BellevilleWind2025RCP4.5 | Belleville | Wind | RCP4.5 | 2025 | 85.0966 | 91.6701 | 98.5831 | 105.4944 | 112.4089
| BellevilleWind2030RCP4.5 | Belleville | Wind | RCP4.5 | 2030 | 85.0641 | 91.6352 | 98.5488 | 105.4577 | 112.3717
| BellevilleWind2035RCP4.5 | Belleville | Wind | RCP4.5 | 2035 | 85.0317 | 91.6003 | 98.5145 | 105.421 | 112.3345
| BellevilleWind2040RCP4.5 | Belleville | Wind | RCP4.5 | 2040 | 84.9993 | 91.5653 | 98.4802 | 105.3843 | 112.2972
| BellevilleWind2045RCP4.5 | Belleville | Wind | RCP4.5 | 2045 | 84.9668 | 91.5304 | 98.4459 | 105.3476 | 112.26
| BellevilleWind2050RCP4.5 | Belleville | Wind | RCP4.5 | 2050 | 85.0545 | 91.6559 | 98.6213 | 105.5626 | 112.5177
| BellevilleWind2055RCP4.5 | Belleville | Wind | RCP4.5 | 2055 | 85.1747 | 91.8163 | 98.831 | 105.8142 | 112.8126
| BellevilleWind2060RCP4.5 | Belleville | Wind | RCP4.5 | 2060 | 85.2949 | 91.9767 | 99.0408 | 106.0659 | 113.1076
| BellevilleWind2065RCP4.5 | Belleville | Wind | RCP4.5 | 2065 | 85.415 | 92.1371 | 99.2505 | 106.3176 | 113.4025
| BellevilleWind2070RCP4.5 | Belleville | Wind | RCP4.5 | 2070 | 85.5352 | 92.2975 | 99.4602 | 106.5692 | 113.6974
| BellevilleWind2075RCP4.5 | Belleville | Wind | RCP4.5 | 2075 | 85.5958 | 92.381 | 99.5713 | 106.7038 | 113.8557
| BellevilleWind2080RCP4.5 | Belleville | Wind | RCP4.5 | 2080 | 85.6565 | 92.4646 | 99.6823 | 106.8384 | 114.014
| BellevilleWind2085RCP4.5 | Belleville | Wind | RCP4.5 | 2085 | 85.7171 | 92.5481 | 99.7934 | 106.9729 | 114.1723
| BellevilleWind2090RCP4.5 | Belleville | Wind | RCP4.5 | 2090 | 85.7778 | 92.6317 | 99.9045 | 107.1075 | 114.3305
| BellevilleWind2095RCP4.5 | Belleville | Wind | RCP4.5 | 2095 | 85.8384 | 92.7152 | 100.0155 | 107.2421 | 114.4888
| BellevilleWind2100RCP4.5 | Belleville | Wind | RCP4.5 | 2100 | 85.8991 | 92.7987 | 100.1266 | 107.3766 | 114.6471
| BellevilleWind2023RCP6.0 | Belleville | Wind | RCP6.0 | 2023 | 85.129 | 91.7051 | 98.6174 | 105.5311 | 112.4462
| BellevilleWind2025RCP6.0 | Belleville | Wind | RCP6.0 | 2025 | 85.0966 | 91.6701 | 98.5831 | 105.4944 | 112.4089
| BellevilleWind2030RCP6.0 | Belleville | Wind | RCP6.0 | 2030 | 85.0641 | 91.6352 | 98.5488 | 105.4577 | 112.3717
| BellevilleWind2035RCP6.0 | Belleville | Wind | RCP6.0 | 2035 | 85.0317 | 91.6003 | 98.5145 | 105.421 | 112.3345
| BellevilleWind2040RCP6.0 | Belleville | Wind | RCP6.0 | 2040 | 84.9993 | 91.5653 | 98.4802 | 105.3843 | 112.2972
| BellevilleWind2045RCP6.0 | Belleville | Wind | RCP6.0 | 2045 | 84.9668 | 91.5304 | 98.4459 | 105.3476 | 112.26
| BellevilleWind2050RCP6.0 | Belleville | Wind | RCP6.0 | 2050 | 85.0545 | 91.6559 | 98.6213 | 105.5626 | 112.5177
| BellevilleWind2055RCP6.0 | Belleville | Wind | RCP6.0 | 2055 | 85.1747 | 91.8163 | 98.831 | 105.8142 | 112.8126
| BellevilleWind2060RCP6.0 | Belleville | Wind | RCP6.0 | 2060 | 85.2949 | 91.9767 | 99.0408 | 106.0659 | 113.1076
| BellevilleWind2065RCP6.0 | Belleville | Wind | RCP6.0 | 2065 | 85.415 | 92.1371 | 99.2505 | 106.3176 | 113.4025
| BellevilleWind2070RCP6.0 | Belleville | Wind | RCP6.0 | 2070 | 85.5352 | 92.2975 | 99.4602 | 106.5692 | 113.6974
| BellevilleWind2075RCP6.0 | Belleville | Wind | RCP6.0 | 2075 | 85.6262 | 92.4228 | 99.6268 | 106.7711 | 113.9348
| BellevilleWind2080RCP6.0 | Belleville | Wind | RCP6.0 | 2080 | 85.7171 | 92.5481 | 99.7934 | 106.9729 | 114.1723
| BellevilleWind2085RCP6.0 | Belleville | Wind | RCP6.0 | 2085 | 85.8081 | 92.6734 | 99.96 | 107.1748 | 114.4097
| BellevilleWind2090RCP6.0 | Belleville | Wind | RCP6.0 | 2090 | 86.1896 | 93.1512 | 100.5578 | 107.88 | 115.2168
| BellevilleWind2095RCP6.0 | Belleville | Wind | RCP6.0 | 2095 | 86.4801 | 93.5036 | 100.989 | 108.3833 | 115.7866
| BellevilleWind2100RCP6.0 | Belleville | Wind | RCP6.0 | 2100 | 86.7707 | 93.856 | 101.4202 | 108.8866 | 116.3564
| BellevilleWind2023RCP8.5 | Belleville | Wind | RCP8.5 | 2023 | 85.129 | 91.7051 | 98.6174 | 105.5311 | 112.4462
| BellevilleWind2025RCP8.5 | Belleville | Wind | RCP8.5 | 2025 | 85.0641 | 91.6352 | 98.5488 | 105.4577 | 112.3717
| BellevilleWind2030RCP8.5 | Belleville | Wind | RCP8.5 | 2030 | 84.9993 | 91.5653 | 98.4802 | 105.3843 | 112.2972
| BellevilleWind2035RCP8.5 | Belleville | Wind | RCP8.5 | 2035 | 84.9344 | 91.4954 | 98.4116 | 105.3109 | 112.2227
| BellevilleWind2040RCP8.5 | Belleville | Wind | RCP8.5 | 2040 | 85.1346 | 91.7628 | 98.7611 | 105.7303 | 112.7143
| BellevilleWind2045RCP8.5 | Belleville | Wind | RCP8.5 | 2045 | 85.3349 | 92.0301 | 99.1107 | 106.1498 | 113.2059
| BellevilleWind2050RCP8.5 | Belleville | Wind | RCP8.5 | 2050 | 85.6565 | 92.4646 | 99.6823 | 106.8384 | 114.014
| BellevilleWind2055RCP8.5 | Belleville | Wind | RCP8.5 | 2055 | 85.7778 | 92.6317 | 99.9045 | 107.1075 | 114.3305
| BellevilleWind2060RCP8.5 | Belleville | Wind | RCP8.5 | 2060 | 86.1896 | 93.1512 | 100.5578 | 107.88 | 115.2168
| BellevilleWind2065RCP8.5 | Belleville | Wind | RCP8.5 | 2065 | 86.4801 | 93.5036 | 100.989 | 108.3833 | 115.7866
| BellevilleWind2070RCP8.5 | Belleville | Wind | RCP8.5 | 2070 | 86.6917 | 93.7679 | 101.3189 | 108.7748 | 116.2372
| BellevilleWind2075RCP8.5 | Belleville | Wind | RCP8.5 | 2075 | 86.6127 | 93.6798 | 101.2177 | 108.6629 | 116.118
| BellevilleWind2080RCP8.5 | Belleville | Wind | RCP8.5 | 2080 | 86.5337 | 93.5917 | 101.1164 | 108.5511 | 115.9989
| BellevilleWind2085RCP8.5 | Belleville | Wind | RCP8.5 | 2085 | 86.741 | 93.9061 | 101.5672 | 109.1121 | 116.6748
| BellevilleWind2090RCP8.5 | Belleville | Wind | RCP8.5 | 2090 | 86.9484 | 94.2205 | 102.018 | 109.6731 | 117.3507
| BellevilleWind2095RCP8.5 | Belleville | Wind | RCP8.5 | 2095 | 86.9484 | 94.2205 | 102.018 | 109.6731 | 117.3507
| BellevilleWind2100RCP8.5 | Belleville | Wind | RCP8.5 | 2100 | 86.9484 | 94.2205 | 102.018 | 109.6731 | 117.3507
| BelmontIce Accretion2023RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2023 | 20.5831 | 24.7008 | 29.91 | 33.8661 | 37.8378
| BelmontIce Accretion2025RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2025 | 20.4614 | 24.568 | 29.765 | 33.7135 | 37.674
| BelmontIce Accretion2030RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2030 | 20.3396 | 24.4352 | 29.62 | 33.561 | 37.5102
| BelmontIce Accretion2035RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2035 | 20.2178 | 24.3024 | 29.475 | 33.4085 | 37.3464
| BelmontIce Accretion2040RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2040 | 20.096 | 24.1696 | 29.33 | 33.2559 | 37.1826
| BelmontIce Accretion2045RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2045 | 19.9743 | 24.0368 | 29.185 | 33.1033 | 37.0188
| BelmontIce Accretion2050RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2050 | 19.4642 | 23.4757 | 28.554 | 32.422 | 36.2804
| BelmontIce Accretion2055RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2055 | 19.0759 | 23.0474 | 28.068 | 31.8931 | 35.7059
| BelmontIce Accretion2060RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2060 | 18.6876 | 22.6192 | 27.582 | 31.3643 | 35.1313
| BelmontIce Accretion2065RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2065 | 18.2994 | 22.1909 | 27.096 | 30.8354 | 34.5568
| BelmontIce Accretion2070RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2070 | 17.9111 | 21.7626 | 26.61 | 30.3066 | 33.9822
| BelmontIce Accretion2075RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2075 | 17.7754 | 21.6257 | 26.47 | 30.1597 | 33.831
| BelmontIce Accretion2080RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2080 | 17.6397 | 21.4887 | 26.33 | 30.0128 | 33.6798
| BelmontIce Accretion2085RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2085 | 17.504 | 21.3517 | 26.19 | 29.8659 | 33.5286
| BelmontIce Accretion2090RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2090 | 17.3683 | 21.2148 | 26.05 | 29.719 | 33.3774
| BelmontIce Accretion2095RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2095 | 17.2326 | 21.0778 | 25.91 | 29.5721 | 33.2262
| BelmontIce Accretion2100RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2100 | 17.0969 | 20.9409 | 25.77 | 29.4252 | 33.075
| BelmontIce Accretion2023RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2023 | 20.5831 | 24.7008 | 29.91 | 33.8661 | 37.8378
| BelmontIce Accretion2025RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2025 | 20.4614 | 24.568 | 29.765 | 33.7135 | 37.674
| BelmontIce Accretion2030RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2030 | 20.3396 | 24.4352 | 29.62 | 33.561 | 37.5102
| BelmontIce Accretion2035RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2035 | 20.2178 | 24.3024 | 29.475 | 33.4085 | 37.3464
| BelmontIce Accretion2040RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2040 | 20.096 | 24.1696 | 29.33 | 33.2559 | 37.1826
| BelmontIce Accretion2045RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2045 | 19.9743 | 24.0368 | 29.185 | 33.1033 | 37.0188
| BelmontIce Accretion2050RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2050 | 19.4642 | 23.4757 | 28.554 | 32.422 | 36.2804
| BelmontIce Accretion2055RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2055 | 19.0759 | 23.0474 | 28.068 | 31.8931 | 35.7059
| BelmontIce Accretion2060RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2060 | 18.6876 | 22.6192 | 27.582 | 31.3643 | 35.1313
| BelmontIce Accretion2065RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2065 | 18.2994 | 22.1909 | 27.096 | 30.8354 | 34.5568
| BelmontIce Accretion2070RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2070 | 17.9111 | 21.7626 | 26.61 | 30.3066 | 33.9822
| BelmontIce Accretion2075RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2075 | 17.7075 | 21.5572 | 26.4 | 30.0862 | 33.7554
| BelmontIce Accretion2080RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2080 | 17.504 | 21.3517 | 26.19 | 29.8659 | 33.5286
| BelmontIce Accretion2085RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2085 | 17.3005 | 21.1463 | 25.98 | 29.6456 | 33.3018
| BelmontIce Accretion2090RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2090 | 16.6098 | 20.3931 | 25.15 | 28.7472 | 32.3316
| BelmontIce Accretion2095RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2095 | 16.1228 | 19.8453 | 24.53 | 28.0692 | 31.5882
| BelmontIce Accretion2100RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2100 | 15.6357 | 19.2975 | 23.91 | 27.3912 | 30.8448
| BelmontIce Accretion2023RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2023 | 20.5831 | 24.7008 | 29.91 | 33.8661 | 37.8378
| BelmontIce Accretion2025RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2025 | 20.3396 | 24.4352 | 29.62 | 33.561 | 37.5102
| BelmontIce Accretion2030RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2030 | 20.096 | 24.1696 | 29.33 | 33.2559 | 37.1826
| BelmontIce Accretion2035RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2035 | 19.8525 | 23.904 | 29.04 | 32.9508 | 36.855
| BelmontIce Accretion2040RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2040 | 19.2054 | 23.1902 | 28.23 | 32.0694 | 35.8974
| BelmontIce Accretion2045RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2045 | 18.5582 | 22.4764 | 27.42 | 31.188 | 34.9398
| BelmontIce Accretion2050RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2050 | 17.6397 | 21.4887 | 26.33 | 30.0128 | 33.6798
| BelmontIce Accretion2055RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2055 | 17.3683 | 21.2148 | 26.05 | 29.719 | 33.3774
| BelmontIce Accretion2060RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2060 | 16.6098 | 20.3931 | 25.15 | 28.7472 | 32.3316
| BelmontIce Accretion2065RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2065 | 16.1228 | 19.8453 | 24.53 | 28.0692 | 31.5882
| BelmontIce Accretion2070RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2070 | 15.3225 | 18.9655 | 23.55 | 26.9957 | 30.429
| BelmontIce Accretion2075RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2075 | 15.0094 | 18.6335 | 23.19 | 26.6002 | 30.0132
| BelmontIce Accretion2080RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2080 | 14.6963 | 18.3015 | 22.83 | 26.2047 | 29.5974
| BelmontIce Accretion2085RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2085 | 13.7673 | 17.2059 | 21.51 | 24.73 | 27.9531
| BelmontIce Accretion2090RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2090 | 12.8384 | 16.1103 | 20.19 | 23.2554 | 26.3088
| BelmontIce Accretion2095RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2095 | 12.8384 | 16.1103 | 20.19 | 23.2554 | 26.3088
| BelmontIce Accretion2100RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2100 | 12.8384 | 16.1103 | 20.19 | 23.2554 | 26.3088
| BelmontWind2023RCP4.5 | Belmont | Wind | RCP4.5 | 2023 | 88.7974 | 95.7896 | 103.1934 | 110.5588 | 117.9312
| BelmontWind2025RCP4.5 | Belmont | Wind | RCP4.5 | 2025 | 88.909 | 95.9382 | 103.3889 | 110.7935 | 118.2064
| BelmontWind2030RCP4.5 | Belmont | Wind | RCP4.5 | 2030 | 89.0205 | 96.0869 | 103.5844 | 111.0281 | 118.4816
| BelmontWind2035RCP4.5 | Belmont | Wind | RCP4.5 | 2035 | 89.1321 | 96.2355 | 103.7799 | 111.2628 | 118.7568
| BelmontWind2040RCP4.5 | Belmont | Wind | RCP4.5 | 2040 | 89.2437 | 96.3841 | 103.9754 | 111.4974 | 119.032
| BelmontWind2045RCP4.5 | Belmont | Wind | RCP4.5 | 2045 | 89.3552 | 96.5327 | 104.1709 | 111.7321 | 119.3072
| BelmontWind2050RCP4.5 | Belmont | Wind | RCP4.5 | 2050 | 89.5196 | 96.7553 | 104.4684 | 112.0933 | 119.7335
| BelmontWind2055RCP4.5 | Belmont | Wind | RCP4.5 | 2055 | 89.5725 | 96.8293 | 104.5704 | 112.2199 | 119.8847
| BelmontWind2060RCP4.5 | Belmont | Wind | RCP4.5 | 2060 | 89.6253 | 96.9033 | 104.6724 | 112.3465 | 120.0358
| BelmontWind2065RCP4.5 | Belmont | Wind | RCP4.5 | 2065 | 89.6782 | 96.9773 | 104.7744 | 112.4731 | 120.187
| BelmontWind2070RCP4.5 | Belmont | Wind | RCP4.5 | 2070 | 89.731 | 97.0513 | 104.8764 | 112.5997 | 120.3382
| BelmontWind2075RCP4.5 | Belmont | Wind | RCP4.5 | 2075 | 89.8866 | 97.2536 | 105.1382 | 112.9108 | 120.7006
| BelmontWind2080RCP4.5 | Belmont | Wind | RCP4.5 | 2080 | 90.0422 | 97.456 | 105.4 | 113.2218 | 121.063
| BelmontWind2085RCP4.5 | Belmont | Wind | RCP4.5 | 2085 | 90.1978 | 97.6584 | 105.6618 | 113.5329 | 121.4254
| BelmontWind2090RCP4.5 | Belmont | Wind | RCP4.5 | 2090 | 90.3534 | 97.8607 | 105.9236 | 113.8439 | 121.7878
| BelmontWind2095RCP4.5 | Belmont | Wind | RCP4.5 | 2095 | 90.509 | 98.0631 | 106.1854 | 114.155 | 122.1502
| BelmontWind2100RCP4.5 | Belmont | Wind | RCP4.5 | 2100 | 90.6646 | 98.2655 | 106.4472 | 114.466 | 122.5126
| BelmontWind2023RCP6.0 | Belmont | Wind | RCP6.0 | 2023 | 88.7974 | 95.7896 | 103.1934 | 110.5588 | 117.9312
| BelmontWind2025RCP6.0 | Belmont | Wind | RCP6.0 | 2025 | 88.909 | 95.9382 | 103.3889 | 110.7935 | 118.2064
| BelmontWind2030RCP6.0 | Belmont | Wind | RCP6.0 | 2030 | 89.0205 | 96.0869 | 103.5844 | 111.0281 | 118.4816
| BelmontWind2035RCP6.0 | Belmont | Wind | RCP6.0 | 2035 | 89.1321 | 96.2355 | 103.7799 | 111.2628 | 118.7568
| BelmontWind2040RCP6.0 | Belmont | Wind | RCP6.0 | 2040 | 89.2437 | 96.3841 | 103.9754 | 111.4974 | 119.032
| BelmontWind2045RCP6.0 | Belmont | Wind | RCP6.0 | 2045 | 89.3552 | 96.5327 | 104.1709 | 111.7321 | 119.3072
| BelmontWind2050RCP6.0 | Belmont | Wind | RCP6.0 | 2050 | 89.5196 | 96.7553 | 104.4684 | 112.0933 | 119.7335
| BelmontWind2055RCP6.0 | Belmont | Wind | RCP6.0 | 2055 | 89.5725 | 96.8293 | 104.5704 | 112.2199 | 119.8847
| BelmontWind2060RCP6.0 | Belmont | Wind | RCP6.0 | 2060 | 89.6253 | 96.9033 | 104.6724 | 112.3465 | 120.0358
| BelmontWind2065RCP6.0 | Belmont | Wind | RCP6.0 | 2065 | 89.6782 | 96.9773 | 104.7744 | 112.4731 | 120.187
| BelmontWind2070RCP6.0 | Belmont | Wind | RCP6.0 | 2070 | 89.731 | 97.0513 | 104.8764 | 112.5997 | 120.3382
| BelmontWind2075RCP6.0 | Belmont | Wind | RCP6.0 | 2075 | 89.9644 | 97.3548 | 105.2691 | 113.0663 | 120.8818
| BelmontWind2080RCP6.0 | Belmont | Wind | RCP6.0 | 2080 | 90.1978 | 97.6584 | 105.6618 | 113.5329 | 121.4254
| BelmontWind2085RCP6.0 | Belmont | Wind | RCP6.0 | 2085 | 90.4312 | 97.9619 | 106.0545 | 113.9995 | 121.969
| BelmontWind2090RCP6.0 | Belmont | Wind | RCP6.0 | 2090 | 91.0492 | 98.7556 | 107.0626 | 115.19 | 123.3498
| BelmontWind2095RCP6.0 | Belmont | Wind | RCP6.0 | 2095 | 91.4338 | 99.2457 | 107.678 | 115.914 | 124.187
| BelmontWind2100RCP6.0 | Belmont | Wind | RCP6.0 | 2100 | 91.8184 | 99.7358 | 108.2934 | 116.6379 | 125.0243
| BelmontWind2023RCP8.5 | Belmont | Wind | RCP8.5 | 2023 | 88.7974 | 95.7896 | 103.1934 | 110.5588 | 117.9312
| BelmontWind2025RCP8.5 | Belmont | Wind | RCP8.5 | 2025 | 89.0205 | 96.0869 | 103.5844 | 111.0281 | 118.4816
| BelmontWind2030RCP8.5 | Belmont | Wind | RCP8.5 | 2030 | 89.2437 | 96.3841 | 103.9754 | 111.4974 | 119.032
| BelmontWind2035RCP8.5 | Belmont | Wind | RCP8.5 | 2035 | 89.4668 | 96.6813 | 104.3664 | 111.9667 | 119.5824
| BelmontWind2040RCP8.5 | Belmont | Wind | RCP8.5 | 2040 | 89.5549 | 96.8046 | 104.5364 | 112.1777 | 119.8343
| BelmontWind2045RCP8.5 | Belmont | Wind | RCP8.5 | 2045 | 89.6429 | 96.9279 | 104.7064 | 112.3887 | 120.0862
| BelmontWind2050RCP8.5 | Belmont | Wind | RCP8.5 | 2050 | 90.0422 | 97.456 | 105.4 | 113.2218 | 121.063
| BelmontWind2055RCP8.5 | Belmont | Wind | RCP8.5 | 2055 | 90.3534 | 97.8607 | 105.9236 | 113.8439 | 121.7878
| BelmontWind2060RCP8.5 | Belmont | Wind | RCP8.5 | 2060 | 91.0492 | 98.7556 | 107.0626 | 115.19 | 123.3498
| BelmontWind2065RCP8.5 | Belmont | Wind | RCP8.5 | 2065 | 91.4338 | 99.2457 | 107.678 | 115.914 | 124.187
| BelmontWind2070RCP8.5 | Belmont | Wind | RCP8.5 | 2070 | 92.0562 | 100.033 | 108.6708 | 117.0854 | 125.5398
| BelmontWind2075RCP8.5 | Belmont | Wind | RCP8.5 | 2075 | 92.294 | 100.3303 | 109.0482 | 117.5329 | 126.0553
| BelmontWind2080RCP8.5 | Belmont | Wind | RCP8.5 | 2080 | 92.5318 | 100.6275 | 109.4256 | 117.9803 | 126.5708
| BelmontWind2085RCP8.5 | Belmont | Wind | RCP8.5 | 2085 | 92.937 | 101.1634 | 110.1294 | 118.8207 | 127.5592
| BelmontWind2090RCP8.5 | Belmont | Wind | RCP8.5 | 2090 | 93.3421 | 101.6994 | 110.8332 | 119.6611 | 128.5475
| BelmontWind2095RCP8.5 | Belmont | Wind | RCP8.5 | 2095 | 93.3421 | 101.6994 | 110.8332 | 119.6611 | 128.5475
| BelmontWind2100RCP8.5 | Belmont | Wind | RCP8.5 | 2100 | 93.3421 | 101.6994 | 110.8332 | 119.6611 | 128.5475
| BowmanvilleIce Accretion2023RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| BowmanvilleIce Accretion2025RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| BowmanvilleIce Accretion2030RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| BowmanvilleIce Accretion2035RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| BowmanvilleIce Accretion2040RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| BowmanvilleIce Accretion2045RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| BowmanvilleIce Accretion2050RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| BowmanvilleIce Accretion2055RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| BowmanvilleIce Accretion2060RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| BowmanvilleIce Accretion2065RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| BowmanvilleIce Accretion2070RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| BowmanvilleIce Accretion2075RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
| BowmanvilleIce Accretion2080RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| BowmanvilleIce Accretion2085RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| BowmanvilleIce Accretion2090RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| BowmanvilleIce Accretion2095RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
| BowmanvilleIce Accretion2100RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
| BowmanvilleIce Accretion2023RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| BowmanvilleIce Accretion2025RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| BowmanvilleIce Accretion2030RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| BowmanvilleIce Accretion2035RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| BowmanvilleIce Accretion2040RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| BowmanvilleIce Accretion2045RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| BowmanvilleIce Accretion2050RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| BowmanvilleIce Accretion2055RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| BowmanvilleIce Accretion2060RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| BowmanvilleIce Accretion2065RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| BowmanvilleIce Accretion2070RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| BowmanvilleIce Accretion2075RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
| BowmanvilleIce Accretion2080RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| BowmanvilleIce Accretion2085RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
| BowmanvilleIce Accretion2090RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| BowmanvilleIce Accretion2095RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| BowmanvilleIce Accretion2100RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
| BowmanvilleIce Accretion2023RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| BowmanvilleIce Accretion2025RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| BowmanvilleIce Accretion2030RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| BowmanvilleIce Accretion2035RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
| BowmanvilleIce Accretion2040RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
| BowmanvilleIce Accretion2045RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
| BowmanvilleIce Accretion2050RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| BowmanvilleIce Accretion2055RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| BowmanvilleIce Accretion2060RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| BowmanvilleIce Accretion2065RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| BowmanvilleIce Accretion2070RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
| BowmanvilleIce Accretion2075RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
| BowmanvilleIce Accretion2080RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
| BowmanvilleIce Accretion2085RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
| BowmanvilleIce Accretion2090RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| BowmanvilleIce Accretion2095RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| BowmanvilleIce Accretion2100RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| BowmanvilleWind2023RCP4.5 | Bowmanville | Wind | RCP4.5 | 2023 | 84.8244 | 91.3223 | 98.1568 | 104.9963 | 111.8317
| BowmanvilleWind2025RCP4.5 | Bowmanville | Wind | RCP4.5 | 2025 | 84.8399 | 91.3557 | 98.2107 | 105.068 | 111.9211
| BowmanvilleWind2030RCP4.5 | Bowmanville | Wind | RCP4.5 | 2030 | 84.8554 | 91.3891 | 98.2646 | 105.1396 | 112.0105
| BowmanvilleWind2035RCP4.5 | Bowmanville | Wind | RCP4.5 | 2035 | 84.8709 | 91.4225 | 98.3185 | 105.2113 | 112.0998
| BowmanvilleWind2040RCP4.5 | Bowmanville | Wind | RCP4.5 | 2040 | 84.8864 | 91.456 | 98.3724 | 105.2829 | 112.1892
| BowmanvilleWind2045RCP4.5 | Bowmanville | Wind | RCP4.5 | 2045 | 84.9019 | 91.4894 | 98.4263 | 105.3546 | 112.2786
| BowmanvilleWind2050RCP4.5 | Bowmanville | Wind | RCP4.5 | 2050 | 85.0004 | 91.6267 | 98.6115 | 105.5793 | 112.5467
| BowmanvilleWind2055RCP4.5 | Bowmanville | Wind | RCP4.5 | 2055 | 85.0833 | 91.7306 | 98.7428 | 105.7324 | 112.7255
| BowmanvilleWind2060RCP4.5 | Bowmanville | Wind | RCP4.5 | 2060 | 85.1662 | 91.8345 | 98.8742 | 105.8855 | 112.9042
| BowmanvilleWind2065RCP4.5 | Bowmanville | Wind | RCP4.5 | 2065 | 85.2492 | 91.9384 | 99.0055 | 106.0386 | 113.083
| BowmanvilleWind2070RCP4.5 | Bowmanville | Wind | RCP4.5 | 2070 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2617
| BowmanvilleWind2075RCP4.5 | Bowmanville | Wind | RCP4.5 | 2075 | 85.476 | 92.2276 | 99.3736 | 106.4731 | 113.5876
| BowmanvilleWind2080RCP4.5 | Bowmanville | Wind | RCP4.5 | 2080 | 85.6198 | 92.4129 | 99.6105 | 106.7545 | 113.9134
| BowmanvilleWind2085RCP4.5 | Bowmanville | Wind | RCP4.5 | 2085 | 85.7637 | 92.5982 | 99.8473 | 107.0358 | 114.2393
| BowmanvilleWind2090RCP4.5 | Bowmanville | Wind | RCP4.5 | 2090 | 85.9075 | 92.7836 | 100.0841 | 107.3172 | 114.5651
| BowmanvilleWind2095RCP4.5 | Bowmanville | Wind | RCP4.5 | 2095 | 86.0514 | 92.9689 | 100.321 | 107.5986 | 114.891
| BowmanvilleWind2100RCP4.5 | Bowmanville | Wind | RCP4.5 | 2100 | 86.1952 | 93.1542 | 100.5578 | 107.88 | 115.2168
| BowmanvilleWind2023RCP6.0 | Bowmanville | Wind | RCP6.0 | 2023 | 84.8244 | 91.3223 | 98.1568 | 104.9963 | 111.8317
| BowmanvilleWind2025RCP6.0 | Bowmanville | Wind | RCP6.0 | 2025 | 84.8399 | 91.3557 | 98.2107 | 105.068 | 111.9211
| BowmanvilleWind2030RCP6.0 | Bowmanville | Wind | RCP6.0 | 2030 | 84.8554 | 91.3891 | 98.2646 | 105.1396 | 112.0105
| BowmanvilleWind2035RCP6.0 | Bowmanville | Wind | RCP6.0 | 2035 | 84.8709 | 91.4225 | 98.3185 | 105.2113 | 112.0998
| BowmanvilleWind2040RCP6.0 | Bowmanville | Wind | RCP6.0 | 2040 | 84.8864 | 91.456 | 98.3724 | 105.2829 | 112.1892
| BowmanvilleWind2045RCP6.0 | Bowmanville | Wind | RCP6.0 | 2045 | 84.9019 | 91.4894 | 98.4263 | 105.3546 | 112.2786
| BowmanvilleWind2050RCP6.0 | Bowmanville | Wind | RCP6.0 | 2050 | 85.0004 | 91.6267 | 98.6115 | 105.5793 | 112.5467
| BowmanvilleWind2055RCP6.0 | Bowmanville | Wind | RCP6.0 | 2055 | 85.0833 | 91.7306 | 98.7428 | 105.7324 | 112.7255
| BowmanvilleWind2060RCP6.0 | Bowmanville | Wind | RCP6.0 | 2060 | 85.1662 | 91.8345 | 98.8742 | 105.8855 | 112.9042
| BowmanvilleWind2065RCP6.0 | Bowmanville | Wind | RCP6.0 | 2065 | 85.2492 | 91.9384 | 99.0055 | 106.0386 | 113.083
| BowmanvilleWind2070RCP6.0 | Bowmanville | Wind | RCP6.0 | 2070 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2617
| BowmanvilleWind2075RCP6.0 | Bowmanville | Wind | RCP6.0 | 2075 | 85.5479 | 92.3203 | 99.4921 | 106.6138 | 113.7505
| BowmanvilleWind2080RCP6.0 | Bowmanville | Wind | RCP6.0 | 2080 | 85.7637 | 92.5982 | 99.8473 | 107.0358 | 114.2393
| BowmanvilleWind2085RCP6.0 | Bowmanville | Wind | RCP6.0 | 2085 | 85.9794 | 92.8762 | 100.2026 | 107.4579 | 114.7281
| BowmanvilleWind2090RCP6.0 | Bowmanville | Wind | RCP6.0 | 2090 | 86.6409 | 93.701 | 101.234 | 108.6664 | 116.118
| BowmanvilleWind2095RCP6.0 | Bowmanville | Wind | RCP6.0 | 2095 | 87.0866 | 94.2479 | 101.9102 | 109.4529 | 117.0193
| BowmanvilleWind2100RCP6.0 | Bowmanville | Wind | RCP6.0 | 2100 | 87.5322 | 94.7947 | 102.5864 | 110.2393 | 117.9205
| BowmanvilleWind2023RCP8.5 | Bowmanville | Wind | RCP8.5 | 2023 | 84.8244 | 91.3223 | 98.1568 | 104.9963 | 111.8317
| BowmanvilleWind2025RCP8.5 | Bowmanville | Wind | RCP8.5 | 2025 | 84.8554 | 91.3891 | 98.2646 | 105.1396 | 112.0105
| BowmanvilleWind2030RCP8.5 | Bowmanville | Wind | RCP8.5 | 2030 | 84.8864 | 91.456 | 98.3724 | 105.2829 | 112.1892
| BowmanvilleWind2035RCP8.5 | Bowmanville | Wind | RCP8.5 | 2035 | 84.9175 | 91.5228 | 98.4802 | 105.4262 | 112.368
| BowmanvilleWind2040RCP8.5 | Bowmanville | Wind | RCP8.5 | 2040 | 85.0557 | 91.696 | 98.6991 | 105.6814 | 112.6659
| BowmanvilleWind2045RCP8.5 | Bowmanville | Wind | RCP8.5 | 2045 | 85.1939 | 91.8691 | 98.9179 | 105.9366 | 112.9638
| BowmanvilleWind2050RCP8.5 | Bowmanville | Wind | RCP8.5 | 2050 | 85.6198 | 92.4129 | 99.6105 | 106.7545 | 113.9134
| BowmanvilleWind2055RCP8.5 | Bowmanville | Wind | RCP8.5 | 2055 | 85.9075 | 92.7836 | 100.0841 | 107.3172 | 114.5651
| BowmanvilleWind2060RCP8.5 | Bowmanville | Wind | RCP8.5 | 2060 | 86.6409 | 93.701 | 101.234 | 108.6664 | 116.118
| BowmanvilleWind2065RCP8.5 | Bowmanville | Wind | RCP8.5 | 2065 | 87.0866 | 94.2479 | 101.9102 | 109.4529 | 117.0193
| BowmanvilleWind2070RCP8.5 | Bowmanville | Wind | RCP8.5 | 2070 | 87.6648 | 94.974 | 102.8249 | 110.5329 | 118.2631
| BowmanvilleWind2075RCP8.5 | Bowmanville | Wind | RCP8.5 | 2075 | 87.7974 | 95.1532 | 103.0633 | 110.8265 | 118.6057
| BowmanvilleWind2080RCP8.5 | Bowmanville | Wind | RCP8.5 | 2080 | 87.93 | 95.3324 | 103.3018 | 111.1201 | 118.9483
| BowmanvilleWind2085RCP8.5 | Bowmanville | Wind | RCP8.5 | 2085 | 88.2135 | 95.7335 | 103.8506 | 111.7912 | 119.7471
| BowmanvilleWind2090RCP8.5 | Bowmanville | Wind | RCP8.5 | 2090 | 88.4969 | 96.1345 | 104.3994 | 112.4624 | 120.5459
| BowmanvilleWind2095RCP8.5 | Bowmanville | Wind | RCP8.5 | 2095 | 88.4969 | 96.1345 | 104.3994 | 112.4624 | 120.5459
| BowmanvilleWind2100RCP8.5 | Bowmanville | Wind | RCP8.5 | 2100 | 88.4969 | 96.1345 | 104.3994 | 112.4624 | 120.5459
| BracebridgeIce Accretion2023RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2023 | 14.5689 | 17.3951 | 20.979 | 23.7063 | 26.4335
| BracebridgeIce Accretion2025RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2025 | 14.5665 | 17.398 | 20.9895 | 23.7221 | 26.4556
| BracebridgeIce Accretion2030RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2030 | 14.5641 | 17.401 | 21 | 23.7379 | 26.4776
| BracebridgeIce Accretion2035RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2035 | 14.5616 | 17.4039 | 21.0105 | 23.7537 | 26.4997
| BracebridgeIce Accretion2040RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2040 | 14.5592 | 17.4068 | 21.021 | 23.7695 | 26.5217
| BracebridgeIce Accretion2045RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2045 | 14.5568 | 17.4097 | 21.0315 | 23.7854 | 26.5438
| BracebridgeIce Accretion2050RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2050 | 14.5455 | 17.4195 | 21.063 | 23.8392 | 26.6188
| BracebridgeIce Accretion2055RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2055 | 14.5368 | 17.4265 | 21.084 | 23.8771 | 26.6717
| BracebridgeIce Accretion2060RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2060 | 14.528 | 17.4335 | 21.105 | 23.9151 | 26.7246
| BracebridgeIce Accretion2065RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2065 | 14.5192 | 17.4405 | 21.126 | 23.9531 | 26.7775
| BracebridgeIce Accretion2070RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2070 | 14.5105 | 17.4474 | 21.147 | 23.991 | 26.8304
| BracebridgeIce Accretion2075RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2075 | 14.5421 | 17.4968 | 21.224 | 24.082 | 26.9407
| BracebridgeIce Accretion2080RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2080 | 14.5738 | 17.5462 | 21.301 | 24.173 | 27.0509
| BracebridgeIce Accretion2085RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2085 | 14.6055 | 17.5956 | 21.378 | 24.2639 | 27.1612
| BracebridgeIce Accretion2090RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2090 | 14.6371 | 17.645 | 21.455 | 24.3549 | 27.2714
| BracebridgeIce Accretion2095RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2095 | 14.6688 | 17.6944 | 21.532 | 24.4459 | 27.3817
| BracebridgeIce Accretion2100RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2100 | 14.7004 | 17.7437 | 21.609 | 24.5368 | 27.4919
| BracebridgeIce Accretion2023RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2023 | 14.5689 | 17.3951 | 20.979 | 23.7063 | 26.4335
| BracebridgeIce Accretion2025RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2025 | 14.5665 | 17.398 | 20.9895 | 23.7221 | 26.4556
| BracebridgeIce Accretion2030RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2030 | 14.5641 | 17.401 | 21 | 23.7379 | 26.4776
| BracebridgeIce Accretion2035RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2035 | 14.5616 | 17.4039 | 21.0105 | 23.7537 | 26.4997
| BracebridgeIce Accretion2040RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2040 | 14.5592 | 17.4068 | 21.021 | 23.7695 | 26.5217
| BracebridgeIce Accretion2045RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2045 | 14.5568 | 17.4097 | 21.0315 | 23.7854 | 26.5438
| BracebridgeIce Accretion2050RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2050 | 14.5455 | 17.4195 | 21.063 | 23.8392 | 26.6188
| BracebridgeIce Accretion2055RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2055 | 14.5368 | 17.4265 | 21.084 | 23.8771 | 26.6717
| BracebridgeIce Accretion2060RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2060 | 14.528 | 17.4335 | 21.105 | 23.9151 | 26.7246
| BracebridgeIce Accretion2065RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2065 | 14.5192 | 17.4405 | 21.126 | 23.9531 | 26.7775
| BracebridgeIce Accretion2070RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2070 | 14.5105 | 17.4474 | 21.147 | 23.991 | 26.8304
| BracebridgeIce Accretion2075RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2075 | 14.558 | 17.5215 | 21.2625 | 24.1275 | 26.9958
| BracebridgeIce Accretion2080RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2080 | 14.6055 | 17.5956 | 21.378 | 24.2639 | 27.1612
| BracebridgeIce Accretion2085RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2085 | 14.653 | 17.6697 | 21.4935 | 24.4004 | 27.3266
| BracebridgeIce Accretion2090RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2090 | 14.7345 | 17.8251 | 21.749 | 24.7187 | 27.7124
| BracebridgeIce Accretion2095RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2095 | 14.7686 | 17.9064 | 21.889 | 24.9007 | 27.9329
| BracebridgeIce Accretion2100RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2100 | 14.8027 | 17.9878 | 22.029 | 25.0826 | 28.1534
| BracebridgeIce Accretion2023RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2023 | 14.5689 | 17.3951 | 20.979 | 23.7063 | 26.4335
| BracebridgeIce Accretion2025RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2025 | 14.5641 | 17.401 | 21 | 23.7379 | 26.4776
| BracebridgeIce Accretion2030RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2030 | 14.5592 | 17.4068 | 21.021 | 23.7695 | 26.5217
| BracebridgeIce Accretion2035RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2035 | 14.5543 | 17.4126 | 21.042 | 23.8012 | 26.5658
| BracebridgeIce Accretion2040RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2040 | 14.5397 | 17.4242 | 21.077 | 23.8645 | 26.654
| BracebridgeIce Accretion2045RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2045 | 14.5251 | 17.4358 | 21.112 | 23.9277 | 26.7422
| BracebridgeIce Accretion2050RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2050 | 14.5738 | 17.5462 | 21.301 | 24.173 | 27.0509
| BracebridgeIce Accretion2055RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2055 | 14.6371 | 17.645 | 21.455 | 24.3549 | 27.2714
| BracebridgeIce Accretion2060RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2060 | 14.7345 | 17.8251 | 21.749 | 24.7187 | 27.7124
| BracebridgeIce Accretion2065RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2065 | 14.7686 | 17.9064 | 21.889 | 24.9007 | 27.9329
| BracebridgeIce Accretion2070RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2070 | 14.603 | 17.767 | 21.777 | 24.8216 | 27.8712
| BracebridgeIce Accretion2075RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2075 | 14.4033 | 17.5462 | 21.525 | 24.5605 | 27.589
| BracebridgeIce Accretion2080RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2080 | 14.2036 | 17.3254 | 21.273 | 24.2995 | 27.3067
| BracebridgeIce Accretion2085RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2085 | 13.6995 | 16.7589 | 20.622 | 23.5758 | 26.5129
| BracebridgeIce Accretion2090RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2090 | 13.1953 | 16.1925 | 19.971 | 22.852 | 25.7191
| BracebridgeIce Accretion2095RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2095 | 13.1953 | 16.1925 | 19.971 | 22.852 | 25.7191
| BracebridgeIce Accretion2100RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2100 | 13.1953 | 16.1925 | 19.971 | 22.852 | 25.7191
| BracebridgeWind2023RCP4.5 | Bracebridge | Wind | RCP4.5 | 2023 | 76.0852 | 81.9055 | 88.0264 | 94.1506 | 100.2799
| BracebridgeWind2025RCP4.5 | Bracebridge | Wind | RCP4.5 | 2025 | 76.2055 | 82.0596 | 88.22 | 94.3781 | 100.5407
| BracebridgeWind2030RCP4.5 | Bracebridge | Wind | RCP4.5 | 2030 | 76.3259 | 82.2137 | 88.4136 | 94.6057 | 100.8015
| BracebridgeWind2035RCP4.5 | Bracebridge | Wind | RCP4.5 | 2035 | 76.4462 | 82.3679 | 88.6072 | 94.8332 | 101.0624
| BracebridgeWind2040RCP4.5 | Bracebridge | Wind | RCP4.5 | 2040 | 76.5665 | 82.522 | 88.8008 | 95.0608 | 101.3232
| BracebridgeWind2045RCP4.5 | Bracebridge | Wind | RCP4.5 | 2045 | 76.6868 | 82.6761 | 88.9944 | 95.2884 | 101.584
| BracebridgeWind2050RCP4.5 | Bracebridge | Wind | RCP4.5 | 2050 | 76.8101 | 82.8123 | 89.144 | 95.45 | 101.7586
| BracebridgeWind2055RCP4.5 | Bracebridge | Wind | RCP4.5 | 2055 | 76.8132 | 82.7943 | 89.1 | 95.3841 | 101.6723
| BracebridgeWind2060RCP4.5 | Bracebridge | Wind | RCP4.5 | 2060 | 76.8162 | 82.7762 | 89.056 | 95.3182 | 101.586
| BracebridgeWind2065RCP4.5 | Bracebridge | Wind | RCP4.5 | 2065 | 76.8193 | 82.7582 | 89.012 | 95.2523 | 101.4998
| BracebridgeWind2070RCP4.5 | Bracebridge | Wind | RCP4.5 | 2070 | 76.8223 | 82.7402 | 88.968 | 95.1863 | 101.4135
| BracebridgeWind2075RCP4.5 | Bracebridge | Wind | RCP4.5 | 2075 | 76.8489 | 82.7689 | 88.9988 | 95.2209 | 101.4503
| BracebridgeWind2080RCP4.5 | Bracebridge | Wind | RCP4.5 | 2080 | 76.8755 | 82.7975 | 89.0296 | 95.2554 | 101.4871
| BracebridgeWind2085RCP4.5 | Bracebridge | Wind | RCP4.5 | 2085 | 76.9021 | 82.8262 | 89.0604 | 95.2899 | 101.5238
| BracebridgeWind2090RCP4.5 | Bracebridge | Wind | RCP4.5 | 2090 | 76.9287 | 82.8548 | 89.0912 | 95.3244 | 101.5606
| BracebridgeWind2095RCP4.5 | Bracebridge | Wind | RCP4.5 | 2095 | 76.9553 | 82.8835 | 89.122 | 95.359 | 101.5974
| BracebridgeWind2100RCP4.5 | Bracebridge | Wind | RCP4.5 | 2100 | 76.9819 | 82.9121 | 89.1528 | 95.3935 | 101.6342
| BracebridgeWind2023RCP6.0 | Bracebridge | Wind | RCP6.0 | 2023 | 76.0852 | 81.9055 | 88.0264 | 94.1506 | 100.2799
| BracebridgeWind2025RCP6.0 | Bracebridge | Wind | RCP6.0 | 2025 | 76.2055 | 82.0596 | 88.22 | 94.3781 | 100.5407
| BracebridgeWind2030RCP6.0 | Bracebridge | Wind | RCP6.0 | 2030 | 76.3259 | 82.2137 | 88.4136 | 94.6057 | 100.8015
| BracebridgeWind2035RCP6.0 | Bracebridge | Wind | RCP6.0 | 2035 | 76.4462 | 82.3679 | 88.6072 | 94.8332 | 101.0624
| BracebridgeWind2040RCP6.0 | Bracebridge | Wind | RCP6.0 | 2040 | 76.5665 | 82.522 | 88.8008 | 95.0608 | 101.3232
| BracebridgeWind2045RCP6.0 | Bracebridge | Wind | RCP6.0 | 2045 | 76.6868 | 82.6761 | 88.9944 | 95.2884 | 101.584
| BracebridgeWind2050RCP6.0 | Bracebridge | Wind | RCP6.0 | 2050 | 76.8101 | 82.8123 | 89.144 | 95.45 | 101.7586
| BracebridgeWind2055RCP6.0 | Bracebridge | Wind | RCP6.0 | 2055 | 76.8132 | 82.7943 | 89.1 | 95.3841 | 101.6723
| BracebridgeWind2060RCP6.0 | Bracebridge | Wind | RCP6.0 | 2060 | 76.8162 | 82.7762 | 89.056 | 95.3182 | 101.586
| BracebridgeWind2065RCP6.0 | Bracebridge | Wind | RCP6.0 | 2065 | 76.8193 | 82.7582 | 89.012 | 95.2523 | 101.4998
| BracebridgeWind2070RCP6.0 | Bracebridge | Wind | RCP6.0 | 2070 | 76.8223 | 82.7402 | 88.968 | 95.1863 | 101.4135
| BracebridgeWind2075RCP6.0 | Bracebridge | Wind | RCP6.0 | 2075 | 76.8622 | 82.7832 | 89.0142 | 95.2381 | 101.4687
| BracebridgeWind2080RCP6.0 | Bracebridge | Wind | RCP6.0 | 2080 | 76.9021 | 82.8262 | 89.0604 | 95.2899 | 101.5238
| BracebridgeWind2085RCP6.0 | Bracebridge | Wind | RCP6.0 | 2085 | 76.942 | 82.8691 | 89.1066 | 95.3417 | 101.579
| BracebridgeWind2090RCP6.0 | Bracebridge | Wind | RCP6.0 | 2090 | 76.9034 | 82.8003 | 89.0003 | 95.2083 | 101.4168
| BracebridgeWind2095RCP6.0 | Bracebridge | Wind | RCP6.0 | 2095 | 76.8248 | 82.6884 | 88.8477 | 95.0231 | 101.1995
| BracebridgeWind2100RCP6.0 | Bracebridge | Wind | RCP6.0 | 2100 | 76.7463 | 82.5766 | 88.6952 | 94.838 | 100.9821
| BracebridgeWind2023RCP8.5 | Bracebridge | Wind | RCP8.5 | 2023 | 76.0852 | 81.9055 | 88.0264 | 94.1506 | 100.2799
| BracebridgeWind2025RCP8.5 | Bracebridge | Wind | RCP8.5 | 2025 | 76.3259 | 82.2137 | 88.4136 | 94.6057 | 100.8015
| BracebridgeWind2030RCP8.5 | Bracebridge | Wind | RCP8.5 | 2030 | 76.5665 | 82.522 | 88.8008 | 95.0608 | 101.3232
| BracebridgeWind2035RCP8.5 | Bracebridge | Wind | RCP8.5 | 2035 | 76.8071 | 82.8303 | 89.188 | 95.5159 | 101.8449
| BracebridgeWind2040RCP8.5 | Bracebridge | Wind | RCP8.5 | 2040 | 76.8122 | 82.8003 | 89.1147 | 95.4061 | 101.7011
| BracebridgeWind2045RCP8.5 | Bracebridge | Wind | RCP8.5 | 2045 | 76.8172 | 82.7702 | 89.0413 | 95.2962 | 101.5573
| BracebridgeWind2050RCP8.5 | Bracebridge | Wind | RCP8.5 | 2050 | 76.8755 | 82.7975 | 89.0296 | 95.2554 | 101.4871
| BracebridgeWind2055RCP8.5 | Bracebridge | Wind | RCP8.5 | 2055 | 76.9287 | 82.8548 | 89.0912 | 95.3244 | 101.5606
| BracebridgeWind2060RCP8.5 | Bracebridge | Wind | RCP8.5 | 2060 | 76.9034 | 82.8003 | 89.0003 | 95.2083 | 101.4168
| BracebridgeWind2065RCP8.5 | Bracebridge | Wind | RCP8.5 | 2065 | 76.8248 | 82.6884 | 88.8477 | 95.0231 | 101.1995
| BracebridgeWind2070RCP8.5 | Bracebridge | Wind | RCP8.5 | 2070 | 76.8476 | 82.6966 | 88.8389 | 94.998 | 101.1627
| BracebridgeWind2075RCP8.5 | Bracebridge | Wind | RCP8.5 | 2075 | 76.9489 | 82.8166 | 88.9827 | 95.1581 | 101.3433
| BracebridgeWind2080RCP8.5 | Bracebridge | Wind | RCP8.5 | 2080 | 77.0503 | 82.9367 | 89.1264 | 95.3182 | 101.5238
| BracebridgeWind2085RCP8.5 | Bracebridge | Wind | RCP8.5 | 2085 | 77.3732 | 83.3377 | 89.6148 | 95.8878 | 102.1709
| BracebridgeWind2090RCP8.5 | Bracebridge | Wind | RCP8.5 | 2090 | 77.6961 | 83.7387 | 90.1032 | 96.4575 | 102.818
| BracebridgeWind2095RCP8.5 | Bracebridge | Wind | RCP8.5 | 2095 | 77.6961 | 83.7387 | 90.1032 | 96.4575 | 102.818
| BracebridgeWind2100RCP8.5 | Bracebridge | Wind | RCP8.5 | 2100 | 77.6961 | 83.7387 | 90.1032 | 96.4575 | 102.818
| BradfordIce Accretion2023RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2023 | 16.6836 | 20.0196 | 24.24 | 27.4726 | 30.6936
| BradfordIce Accretion2025RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2025 | 16.7254 | 20.086 | 24.34 | 27.5946 | 30.8398
| BradfordIce Accretion2030RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2030 | 16.7671 | 20.1524 | 24.44 | 27.7166 | 30.9859
| BradfordIce Accretion2035RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2035 | 16.8089 | 20.2188 | 24.54 | 27.8387 | 31.1321
| BradfordIce Accretion2040RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2040 | 16.8506 | 20.2852 | 24.64 | 27.9607 | 31.2782
| BradfordIce Accretion2045RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2045 | 16.8924 | 20.3516 | 24.74 | 28.0828 | 31.4244
| BradfordIce Accretion2050RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2050 | 16.8205 | 20.3025 | 24.7152 | 28.0746 | 31.4315
| BradfordIce Accretion2055RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2055 | 16.707 | 20.1869 | 24.5904 | 27.9444 | 31.2924
| BradfordIce Accretion2060RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2060 | 16.5934 | 20.0714 | 24.4656 | 27.8143 | 31.1532
| BradfordIce Accretion2065RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2065 | 16.4799 | 19.9559 | 24.3408 | 27.6841 | 31.0141
| BradfordIce Accretion2070RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2070 | 16.3663 | 19.8403 | 24.216 | 27.5539 | 30.875
| BradfordIce Accretion2075RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2075 | 16.3301 | 19.8237 | 24.224 | 27.5765 | 30.9154
| BradfordIce Accretion2080RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2080 | 16.2939 | 19.8071 | 24.232 | 27.5991 | 30.9557
| BradfordIce Accretion2085RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2085 | 16.2577 | 19.7905 | 24.24 | 27.6217 | 30.996
| BradfordIce Accretion2090RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2090 | 16.2216 | 19.7739 | 24.248 | 27.6443 | 31.0363
| BradfordIce Accretion2095RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2095 | 16.1854 | 19.7573 | 24.256 | 27.6669 | 31.0766
| BradfordIce Accretion2100RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2100 | 16.1492 | 19.7407 | 24.264 | 27.6895 | 31.117
| BradfordIce Accretion2023RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2023 | 16.6836 | 20.0196 | 24.24 | 27.4726 | 30.6936
| BradfordIce Accretion2025RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2025 | 16.7254 | 20.086 | 24.34 | 27.5946 | 30.8398
| BradfordIce Accretion2030RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2030 | 16.7671 | 20.1524 | 24.44 | 27.7166 | 30.9859
| BradfordIce Accretion2035RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2035 | 16.8089 | 20.2188 | 24.54 | 27.8387 | 31.1321
| BradfordIce Accretion2040RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2040 | 16.8506 | 20.2852 | 24.64 | 27.9607 | 31.2782
| BradfordIce Accretion2045RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2045 | 16.8924 | 20.3516 | 24.74 | 28.0828 | 31.4244
| BradfordIce Accretion2050RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2050 | 16.8205 | 20.3025 | 24.7152 | 28.0746 | 31.4315
| BradfordIce Accretion2055RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2055 | 16.707 | 20.1869 | 24.5904 | 27.9444 | 31.2924
| BradfordIce Accretion2060RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2060 | 16.5934 | 20.0714 | 24.4656 | 27.8143 | 31.1532
| BradfordIce Accretion2065RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2065 | 16.4799 | 19.9559 | 24.3408 | 27.6841 | 31.0141
| BradfordIce Accretion2070RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2070 | 16.3663 | 19.8403 | 24.216 | 27.5539 | 30.875
| BradfordIce Accretion2075RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2075 | 16.312 | 19.8154 | 24.228 | 27.5878 | 30.9355
| BradfordIce Accretion2080RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2080 | 16.2577 | 19.7905 | 24.24 | 27.6217 | 30.996
| BradfordIce Accretion2085RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2085 | 16.2035 | 19.7656 | 24.252 | 27.6556 | 31.0565
| BradfordIce Accretion2090RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2090 | 15.8542 | 19.4286 | 23.928 | 27.346 | 30.7541
| BradfordIce Accretion2095RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2095 | 15.5591 | 19.1166 | 23.592 | 27.0025 | 30.3912
| BradfordIce Accretion2100RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2100 | 15.2641 | 18.8045 | 23.256 | 26.659 | 30.0283
| BradfordIce Accretion2023RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2023 | 16.6836 | 20.0196 | 24.24 | 27.4726 | 30.6936
| BradfordIce Accretion2025RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2025 | 16.7671 | 20.1524 | 24.44 | 27.7166 | 30.9859
| BradfordIce Accretion2030RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2030 | 16.8506 | 20.2852 | 24.64 | 27.9607 | 31.2782
| BradfordIce Accretion2035RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2035 | 16.9341 | 20.418 | 24.84 | 28.2048 | 31.5706
| BradfordIce Accretion2040RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2040 | 16.7448 | 20.2254 | 24.632 | 27.9878 | 31.3387
| BradfordIce Accretion2045RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2045 | 16.5556 | 20.0329 | 24.424 | 27.7709 | 31.1069
| BradfordIce Accretion2050RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2050 | 16.2939 | 19.8071 | 24.232 | 27.5991 | 30.9557
| BradfordIce Accretion2055RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2055 | 16.2216 | 19.7739 | 24.248 | 27.6443 | 31.0363
| BradfordIce Accretion2060RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2060 | 15.8542 | 19.4286 | 23.928 | 27.346 | 30.7541
| BradfordIce Accretion2065RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2065 | 15.5591 | 19.1166 | 23.592 | 27.0025 | 30.3912
| BradfordIce Accretion2070RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2070 | 14.8911 | 18.4061 | 22.824 | 26.1889 | 29.5344
| BradfordIce Accretion2075RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2075 | 14.5181 | 18.0077 | 22.392 | 25.7188 | 29.0405
| BradfordIce Accretion2080RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2080 | 14.1452 | 17.6093 | 21.96 | 25.2487 | 28.5466
| BradfordIce Accretion2085RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2085 | 13.4103 | 16.7428 | 20.928 | 24.0961 | 27.2614
| BradfordIce Accretion2090RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2090 | 12.6755 | 15.8762 | 19.896 | 22.9435 | 25.9762
| BradfordIce Accretion2095RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2095 | 12.6755 | 15.8762 | 19.896 | 22.9435 | 25.9762
| BradfordIce Accretion2100RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2100 | 12.6755 | 15.8762 | 19.896 | 22.9435 | 25.9762
| BradfordWind2023RCP4.5 | Bradford | Wind | RCP4.5 | 2023 | 76.2676 | 82.1428 | 88.3256 | 94.5084 | 100.6912
| BradfordWind2025RCP4.5 | Bradford | Wind | RCP4.5 | 2025 | 76.2917 | 82.1769 | 88.3725 | 94.5665 | 100.7614
| BradfordWind2030RCP4.5 | Bradford | Wind | RCP4.5 | 2030 | 76.3157 | 82.211 | 88.4195 | 94.6245 | 100.8316
| BradfordWind2035RCP4.5 | Bradford | Wind | RCP4.5 | 2035 | 76.3398 | 82.2451 | 88.4664 | 94.6826 | 100.9019
| BradfordWind2040RCP4.5 | Bradford | Wind | RCP4.5 | 2040 | 76.3639 | 82.2792 | 88.5133 | 94.7407 | 100.9721
| BradfordWind2045RCP4.5 | Bradford | Wind | RCP4.5 | 2045 | 76.3879 | 82.3133 | 88.5603 | 94.7987 | 101.0423
| BradfordWind2050RCP4.5 | Bradford | Wind | RCP4.5 | 2050 | 76.4621 | 82.3949 | 88.6512 | 94.8982 | 101.1506
| BradfordWind2055RCP4.5 | Bradford | Wind | RCP4.5 | 2055 | 76.5123 | 82.4423 | 88.6952 | 94.9396 | 101.1888
| BradfordWind2060RCP4.5 | Bradford | Wind | RCP4.5 | 2060 | 76.5624 | 82.4898 | 88.7392 | 94.9811 | 101.2269
| BradfordWind2065RCP4.5 | Bradford | Wind | RCP4.5 | 2065 | 76.6126 | 82.5373 | 88.7832 | 95.0225 | 101.265
| BradfordWind2070RCP4.5 | Bradford | Wind | RCP4.5 | 2070 | 76.6627 | 82.5847 | 88.8272 | 95.0639 | 101.3031
| BradfordWind2075RCP4.5 | Bradford | Wind | RCP4.5 | 2075 | 76.7362 | 82.6857 | 88.9621 | 95.2271 | 101.4954
| BradfordWind2080RCP4.5 | Bradford | Wind | RCP4.5 | 2080 | 76.8096 | 82.7866 | 89.0971 | 95.3904 | 101.6877
| BradfordWind2085RCP4.5 | Bradford | Wind | RCP4.5 | 2085 | 76.8831 | 82.8876 | 89.232 | 95.5536 | 101.88
| BradfordWind2090RCP4.5 | Bradford | Wind | RCP4.5 | 2090 | 76.9565 | 82.9885 | 89.3669 | 95.7168 | 102.0723
| BradfordWind2095RCP4.5 | Bradford | Wind | RCP4.5 | 2095 | 77.03 | 83.0894 | 89.5019 | 95.88 | 102.2645
| BradfordWind2100RCP4.5 | Bradford | Wind | RCP4.5 | 2100 | 77.1035 | 83.1904 | 89.6368 | 96.0432 | 102.4568
| BradfordWind2023RCP6.0 | Bradford | Wind | RCP6.0 | 2023 | 76.2676 | 82.1428 | 88.3256 | 94.5084 | 100.6912
| BradfordWind2025RCP6.0 | Bradford | Wind | RCP6.0 | 2025 | 76.2917 | 82.1769 | 88.3725 | 94.5665 | 100.7614
| BradfordWind2030RCP6.0 | Bradford | Wind | RCP6.0 | 2030 | 76.3157 | 82.211 | 88.4195 | 94.6245 | 100.8316
| BradfordWind2035RCP6.0 | Bradford | Wind | RCP6.0 | 2035 | 76.3398 | 82.2451 | 88.4664 | 94.6826 | 100.9019
| BradfordWind2040RCP6.0 | Bradford | Wind | RCP6.0 | 2040 | 76.3639 | 82.2792 | 88.5133 | 94.7407 | 100.9721
| BradfordWind2045RCP6.0 | Bradford | Wind | RCP6.0 | 2045 | 76.3879 | 82.3133 | 88.5603 | 94.7987 | 101.0423
| BradfordWind2050RCP6.0 | Bradford | Wind | RCP6.0 | 2050 | 76.4621 | 82.3949 | 88.6512 | 94.8982 | 101.1506
| BradfordWind2055RCP6.0 | Bradford | Wind | RCP6.0 | 2055 | 76.5123 | 82.4423 | 88.6952 | 94.9396 | 101.1888
| BradfordWind2060RCP6.0 | Bradford | Wind | RCP6.0 | 2060 | 76.5624 | 82.4898 | 88.7392 | 94.9811 | 101.2269
| BradfordWind2065RCP6.0 | Bradford | Wind | RCP6.0 | 2065 | 76.6126 | 82.5373 | 88.7832 | 95.0225 | 101.265
| BradfordWind2070RCP6.0 | Bradford | Wind | RCP6.0 | 2070 | 76.6627 | 82.5847 | 88.8272 | 95.0639 | 101.3031
| BradfordWind2075RCP6.0 | Bradford | Wind | RCP6.0 | 2075 | 76.7729 | 82.7361 | 89.0296 | 95.3088 | 101.5916
| BradfordWind2080RCP6.0 | Bradford | Wind | RCP6.0 | 2080 | 76.8831 | 82.8876 | 89.232 | 95.5536 | 101.88
| BradfordWind2085RCP6.0 | Bradford | Wind | RCP6.0 | 2085 | 76.9933 | 83.039 | 89.4344 | 95.7984 | 102.1684
| BradfordWind2090RCP6.0 | Bradford | Wind | RCP6.0 | 2090 | 77.3593 | 83.5068 | 90.0269 | 96.4983 | 102.9785
| BradfordWind2095RCP6.0 | Bradford | Wind | RCP6.0 | 2095 | 77.6151 | 83.8233 | 90.4171 | 96.9534 | 103.5001
| BradfordWind2100RCP6.0 | Bradford | Wind | RCP6.0 | 2100 | 77.8709 | 84.1397 | 90.8072 | 97.4085 | 104.0218
| BradfordWind2023RCP8.5 | Bradford | Wind | RCP8.5 | 2023 | 76.2676 | 82.1428 | 88.3256 | 94.5084 | 100.6912
| BradfordWind2025RCP8.5 | Bradford | Wind | RCP8.5 | 2025 | 76.3157 | 82.211 | 88.4195 | 94.6245 | 100.8316
| BradfordWind2030RCP8.5 | Bradford | Wind | RCP8.5 | 2030 | 76.3639 | 82.2792 | 88.5133 | 94.7407 | 100.9721
| BradfordWind2035RCP8.5 | Bradford | Wind | RCP8.5 | 2035 | 76.412 | 82.3474 | 88.6072 | 94.8568 | 101.1125
| BradfordWind2040RCP8.5 | Bradford | Wind | RCP8.5 | 2040 | 76.4956 | 82.4265 | 88.6805 | 94.9258 | 101.1761
| BradfordWind2045RCP8.5 | Bradford | Wind | RCP8.5 | 2045 | 76.5791 | 82.5056 | 88.7539 | 94.9949 | 101.2396
| BradfordWind2050RCP8.5 | Bradford | Wind | RCP8.5 | 2050 | 76.8096 | 82.7866 | 89.0971 | 95.3904 | 101.6877
| BradfordWind2055RCP8.5 | Bradford | Wind | RCP8.5 | 2055 | 76.9565 | 82.9885 | 89.3669 | 95.7168 | 102.0723
| BradfordWind2060RCP8.5 | Bradford | Wind | RCP8.5 | 2060 | 77.3593 | 83.5068 | 90.0269 | 96.4983 | 102.9785
| BradfordWind2065RCP8.5 | Bradford | Wind | RCP8.5 | 2065 | 77.6151 | 83.8233 | 90.4171 | 96.9534 | 103.5001
| BradfordWind2070RCP8.5 | Bradford | Wind | RCP8.5 | 2070 | 78.0659 | 84.4016 | 91.1533 | 97.826 | 104.51
| BradfordWind2075RCP8.5 | Bradford | Wind | RCP8.5 | 2075 | 78.261 | 84.6635 | 91.4995 | 98.2434 | 104.9983
| BradfordWind2080RCP8.5 | Bradford | Wind | RCP8.5 | 2080 | 78.456 | 84.9254 | 91.8456 | 98.6608 | 105.4865
| BradfordWind2085RCP8.5 | Bradford | Wind | RCP8.5 | 2085 | 78.5548 | 85.0563 | 92.0216 | 98.868 | 105.7323
| BradfordWind2090RCP8.5 | Bradford | Wind | RCP8.5 | 2090 | 78.6536 | 85.1873 | 92.1976 | 99.0752 | 105.978
| BradfordWind2095RCP8.5 | Bradford | Wind | RCP8.5 | 2095 | 78.6536 | 85.1873 | 92.1976 | 99.0752 | 105.978
| BradfordWind2100RCP8.5 | Bradford | Wind | RCP8.5 | 2100 | 78.6536 | 85.1873 | 92.1976 | 99.0752 | 105.978
| BramptonIce Accretion2023RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| BramptonIce Accretion2025RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
| BramptonIce Accretion2030RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| BramptonIce Accretion2035RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
| BramptonIce Accretion2040RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| BramptonIce Accretion2045RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
| BramptonIce Accretion2050RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
| BramptonIce Accretion2055RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
| BramptonIce Accretion2060RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
| BramptonIce Accretion2065RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
| BramptonIce Accretion2070RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
| BramptonIce Accretion2075RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2075 | 15.5377 | 18.8894 | 23.1125 | 26.329 | 29.5313
| BramptonIce Accretion2080RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2080 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
| BramptonIce Accretion2085RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2085 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
| BramptonIce Accretion2090RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2090 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
| BramptonIce Accretion2095RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2095 | 15.3405 | 18.7511 | 23.0625 | 26.329 | 29.5942
| BramptonIce Accretion2100RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2100 | 15.2912 | 18.7165 | 23.05 | 26.329 | 29.61
| BramptonIce Accretion2023RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| BramptonIce Accretion2025RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
| BramptonIce Accretion2030RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| BramptonIce Accretion2035RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
| BramptonIce Accretion2040RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| BramptonIce Accretion2045RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
| BramptonIce Accretion2050RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
| BramptonIce Accretion2055RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
| BramptonIce Accretion2060RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
| BramptonIce Accretion2065RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
| BramptonIce Accretion2070RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
| BramptonIce Accretion2075RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2075 | 15.513 | 18.8721 | 23.1062 | 26.329 | 29.5391
| BramptonIce Accretion2080RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2080 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
| BramptonIce Accretion2085RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2085 | 15.3652 | 18.7684 | 23.0688 | 26.329 | 29.5864
| BramptonIce Accretion2090RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2090 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
| BramptonIce Accretion2095RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2095 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
| BramptonIce Accretion2100RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2100 | 14.2127 | 17.596 | 21.825 | 25.0577 | 28.2555
| BramptonIce Accretion2023RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| BramptonIce Accretion2025RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2025 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| BramptonIce Accretion2030RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2030 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| BramptonIce Accretion2035RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2035 | 16.6133 | 20.0652 | 24.425 | 27.7415 | 31.059
| BramptonIce Accretion2040RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2040 | 16.2712 | 19.6848 | 23.9917 | 27.2707 | 30.5445
| BramptonIce Accretion2045RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2045 | 15.9291 | 19.3044 | 23.5583 | 26.7998 | 30.03
| BramptonIce Accretion2050RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2050 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
| BramptonIce Accretion2055RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2055 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
| BramptonIce Accretion2060RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2060 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
| BramptonIce Accretion2065RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2065 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
| BramptonIce Accretion2070RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2070 | 13.8125 | 17.1464 | 21.325 | 24.5022 | 27.657
| BramptonIce Accretion2075RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2075 | 13.4124 | 16.6968 | 20.825 | 23.9466 | 27.0585
| BramptonIce Accretion2080RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2080 | 13.0123 | 16.2473 | 20.325 | 23.391 | 26.46
| BramptonIce Accretion2085RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2085 | 12.1338 | 15.1994 | 19.0625 | 21.9785 | 24.885
| BramptonIce Accretion2090RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2090 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| BramptonIce Accretion2095RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2095 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| BramptonIce Accretion2100RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2100 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| BramptonWind2023RCP4.5 | Brampton | Wind | RCP4.5 | 2023 | 81.5651 | 87.9008 | 94.5828 | 101.2539 | 107.9208
| BramptonWind2025RCP4.5 | Brampton | Wind | RCP4.5 | 2025 | 81.5948 | 87.9445 | 94.6455 | 101.3327 | 108.0155
| BramptonWind2030RCP4.5 | Brampton | Wind | RCP4.5 | 2030 | 81.6246 | 87.9882 | 94.7081 | 101.4115 | 108.1102
| BramptonWind2035RCP4.5 | Brampton | Wind | RCP4.5 | 2035 | 81.6544 | 88.0319 | 94.7708 | 101.4902 | 108.2048
| BramptonWind2040RCP4.5 | Brampton | Wind | RCP4.5 | 2040 | 81.6841 | 88.0756 | 94.8335 | 101.569 | 108.2995
| BramptonWind2045RCP4.5 | Brampton | Wind | RCP4.5 | 2045 | 81.7139 | 88.1194 | 94.8961 | 101.6478 | 108.3941
| BramptonWind2050RCP4.5 | Brampton | Wind | RCP4.5 | 2050 | 81.8086 | 88.2417 | 95.0547 | 101.8373 | 108.6152
| BramptonWind2055RCP4.5 | Brampton | Wind | RCP4.5 | 2055 | 81.8735 | 88.3204 | 95.1506 | 101.9479 | 108.7417
| BramptonWind2060RCP4.5 | Brampton | Wind | RCP4.5 | 2060 | 81.9384 | 88.3991 | 95.2464 | 102.0585 | 108.8681
| BramptonWind2065RCP4.5 | Brampton | Wind | RCP4.5 | 2065 | 82.0034 | 88.4778 | 95.3423 | 102.1692 | 108.9946
| BramptonWind2070RCP4.5 | Brampton | Wind | RCP4.5 | 2070 | 82.0683 | 88.5565 | 95.4382 | 102.2798 | 109.121
| BramptonWind2075RCP4.5 | Brampton | Wind | RCP4.5 | 2075 | 82.1576 | 88.6818 | 95.609 | 102.4877 | 109.3675
| BramptonWind2080RCP4.5 | Brampton | Wind | RCP4.5 | 2080 | 82.2469 | 88.8071 | 95.7797 | 102.6955 | 109.614
| BramptonWind2085RCP4.5 | Brampton | Wind | RCP4.5 | 2085 | 82.3362 | 88.9324 | 95.9505 | 102.9034 | 109.8604
| BramptonWind2090RCP4.5 | Brampton | Wind | RCP4.5 | 2090 | 82.4254 | 89.0577 | 96.1213 | 103.1113 | 110.1069
| BramptonWind2095RCP4.5 | Brampton | Wind | RCP4.5 | 2095 | 82.5147 | 89.183 | 96.292 | 103.3191 | 110.3534
| BramptonWind2100RCP4.5 | Brampton | Wind | RCP4.5 | 2100 | 82.604 | 89.3083 | 96.4628 | 103.527 | 110.5998
| BramptonWind2023RCP6.0 | Brampton | Wind | RCP6.0 | 2023 | 81.5651 | 87.9008 | 94.5828 | 101.2539 | 107.9208
| BramptonWind2025RCP6.0 | Brampton | Wind | RCP6.0 | 2025 | 81.5948 | 87.9445 | 94.6455 | 101.3327 | 108.0155
| BramptonWind2030RCP6.0 | Brampton | Wind | RCP6.0 | 2030 | 81.6246 | 87.9882 | 94.7081 | 101.4115 | 108.1102
| BramptonWind2035RCP6.0 | Brampton | Wind | RCP6.0 | 2035 | 81.6544 | 88.0319 | 94.7708 | 101.4902 | 108.2048
| BramptonWind2040RCP6.0 | Brampton | Wind | RCP6.0 | 2040 | 81.6841 | 88.0756 | 94.8335 | 101.569 | 108.2995
| BramptonWind2045RCP6.0 | Brampton | Wind | RCP6.0 | 2045 | 81.7139 | 88.1194 | 94.8961 | 101.6478 | 108.3941
| BramptonWind2050RCP6.0 | Brampton | Wind | RCP6.0 | 2050 | 81.8086 | 88.2417 | 95.0547 | 101.8373 | 108.6152
| BramptonWind2055RCP6.0 | Brampton | Wind | RCP6.0 | 2055 | 81.8735 | 88.3204 | 95.1506 | 101.9479 | 108.7417
| BramptonWind2060RCP6.0 | Brampton | Wind | RCP6.0 | 2060 | 81.9384 | 88.3991 | 95.2464 | 102.0585 | 108.8681
| BramptonWind2065RCP6.0 | Brampton | Wind | RCP6.0 | 2065 | 82.0034 | 88.4778 | 95.3423 | 102.1692 | 108.9946
| BramptonWind2070RCP6.0 | Brampton | Wind | RCP6.0 | 2070 | 82.0683 | 88.5565 | 95.4382 | 102.2798 | 109.121
| BramptonWind2075RCP6.0 | Brampton | Wind | RCP6.0 | 2075 | 82.2022 | 88.7444 | 95.6944 | 102.5916 | 109.4907
| BramptonWind2080RCP6.0 | Brampton | Wind | RCP6.0 | 2080 | 82.3362 | 88.9324 | 95.9505 | 102.9034 | 109.8604
| BramptonWind2085RCP6.0 | Brampton | Wind | RCP6.0 | 2085 | 82.4701 | 89.1203 | 96.2066 | 103.2152 | 110.2301
| BramptonWind2090RCP6.0 | Brampton | Wind | RCP6.0 | 2090 | 82.8854 | 89.6696 | 96.9234 | 104.0735 | 111.2357
| BramptonWind2095RCP6.0 | Brampton | Wind | RCP6.0 | 2095 | 83.1668 | 90.0309 | 97.384 | 104.62 | 111.8715
| BramptonWind2100RCP6.0 | Brampton | Wind | RCP6.0 | 2100 | 83.4482 | 90.3923 | 97.8446 | 105.1664 | 112.5073
| BramptonWind2023RCP8.5 | Brampton | Wind | RCP8.5 | 2023 | 81.5651 | 87.9008 | 94.5828 | 101.2539 | 107.9208
| BramptonWind2025RCP8.5 | Brampton | Wind | RCP8.5 | 2025 | 81.6246 | 87.9882 | 94.7081 | 101.4115 | 108.1102
| BramptonWind2030RCP8.5 | Brampton | Wind | RCP8.5 | 2030 | 81.6841 | 88.0756 | 94.8335 | 101.569 | 108.2995
| BramptonWind2035RCP8.5 | Brampton | Wind | RCP8.5 | 2035 | 81.7436 | 88.1631 | 94.9588 | 101.7266 | 108.4888
| BramptonWind2040RCP8.5 | Brampton | Wind | RCP8.5 | 2040 | 81.8519 | 88.2942 | 95.1186 | 101.911 | 108.6995
| BramptonWind2045RCP8.5 | Brampton | Wind | RCP8.5 | 2045 | 81.9601 | 88.4253 | 95.2784 | 102.0954 | 108.9103
| BramptonWind2050RCP8.5 | Brampton | Wind | RCP8.5 | 2050 | 82.2469 | 88.8071 | 95.7797 | 102.6955 | 109.614
| BramptonWind2055RCP8.5 | Brampton | Wind | RCP8.5 | 2055 | 82.4254 | 89.0577 | 96.1213 | 103.1113 | 110.1069
| BramptonWind2060RCP8.5 | Brampton | Wind | RCP8.5 | 2060 | 82.8854 | 89.6696 | 96.9234 | 104.0735 | 111.2357
| BramptonWind2065RCP8.5 | Brampton | Wind | RCP8.5 | 2065 | 83.1668 | 90.0309 | 97.384 | 104.62 | 111.8715
| BramptonWind2070RCP8.5 | Brampton | Wind | RCP8.5 | 2070 | 83.6078 | 90.6225 | 98.1642 | 105.5587 | 112.9752
| BramptonWind2075RCP8.5 | Brampton | Wind | RCP8.5 | 2075 | 83.7674 | 90.8527 | 98.4838 | 105.951 | 113.4431
| BramptonWind2080RCP8.5 | Brampton | Wind | RCP8.5 | 2080 | 83.927 | 91.0829 | 98.8034 | 106.3432 | 113.9111
| BramptonWind2085RCP8.5 | Brampton | Wind | RCP8.5 | 2085 | 84.1827 | 91.4151 | 99.2311 | 106.8562 | 114.5112
| BramptonWind2090RCP8.5 | Brampton | Wind | RCP8.5 | 2090 | 84.4384 | 91.7473 | 99.6588 | 107.3692 | 115.1113
| BramptonWind2095RCP8.5 | Brampton | Wind | RCP8.5 | 2095 | 84.4384 | 91.7473 | 99.6588 | 107.3692 | 115.1113
| BramptonWind2100RCP8.5 | Brampton | Wind | RCP8.5 | 2100 | 84.4384 | 91.7473 | 99.6588 | 107.3692 | 115.1113
| BrantfordIce Accretion2023RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2023 | 20.5414 | 24.6261 | 29.82 | 33.7644 | 37.7244
| BrantfordIce Accretion2025RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2025 | 20.437 | 24.514 | 29.695 | 33.6345 | 37.5858
| BrantfordIce Accretion2030RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2030 | 20.3326 | 24.402 | 29.57 | 33.5045 | 37.4472
| BrantfordIce Accretion2035RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2035 | 20.2282 | 24.2899 | 29.445 | 33.3745 | 37.3086
| BrantfordIce Accretion2040RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2040 | 20.1239 | 24.1779 | 29.32 | 33.2446 | 37.17
| BrantfordIce Accretion2045RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2045 | 20.0195 | 24.0658 | 29.195 | 33.1146 | 37.0314
| BrantfordIce Accretion2050RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2050 | 19.6354 | 23.65 | 28.74 | 32.6254 | 36.5072
| BrantfordIce Accretion2055RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2055 | 19.3557 | 23.3462 | 28.41 | 32.266 | 36.1217
| BrantfordIce Accretion2060RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2060 | 19.0759 | 23.0425 | 28.08 | 31.9067 | 35.7361
| BrantfordIce Accretion2065RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2065 | 18.7962 | 22.7387 | 27.75 | 31.5473 | 35.3506
| BrantfordIce Accretion2070RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2070 | 18.5165 | 22.4349 | 27.42 | 31.188 | 34.965
| BrantfordIce Accretion2075RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2075 | 18.426 | 22.356 | 27.35 | 31.1258 | 34.902
| BrantfordIce Accretion2080RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2080 | 18.3355 | 22.2772 | 27.28 | 31.0637 | 34.839
| BrantfordIce Accretion2085RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2085 | 18.2451 | 22.1983 | 27.21 | 31.0016 | 34.776
| BrantfordIce Accretion2090RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2090 | 18.1546 | 22.1195 | 27.14 | 30.9394 | 34.713
| BrantfordIce Accretion2095RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2095 | 18.0642 | 22.0406 | 27.07 | 30.8773 | 34.65
| BrantfordIce Accretion2100RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2100 | 17.9737 | 21.9618 | 27 | 30.8151 | 34.587
| BrantfordIce Accretion2023RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2023 | 20.5414 | 24.6261 | 29.82 | 33.7644 | 37.7244
| BrantfordIce Accretion2025RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2025 | 20.437 | 24.514 | 29.695 | 33.6345 | 37.5858
| BrantfordIce Accretion2030RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2030 | 20.3326 | 24.402 | 29.57 | 33.5045 | 37.4472
| BrantfordIce Accretion2035RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2035 | 20.2282 | 24.2899 | 29.445 | 33.3745 | 37.3086
| BrantfordIce Accretion2040RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2040 | 20.1239 | 24.1779 | 29.32 | 33.2446 | 37.17
| BrantfordIce Accretion2045RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2045 | 20.0195 | 24.0658 | 29.195 | 33.1146 | 37.0314
| BrantfordIce Accretion2050RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2050 | 19.6354 | 23.65 | 28.74 | 32.6254 | 36.5072
| BrantfordIce Accretion2055RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2055 | 19.3557 | 23.3462 | 28.41 | 32.266 | 36.1217
| BrantfordIce Accretion2060RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2060 | 19.0759 | 23.0425 | 28.08 | 31.9067 | 35.7361
| BrantfordIce Accretion2065RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2065 | 18.7962 | 22.7387 | 27.75 | 31.5473 | 35.3506
| BrantfordIce Accretion2070RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2070 | 18.5165 | 22.4349 | 27.42 | 31.188 | 34.965
| BrantfordIce Accretion2075RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2075 | 18.3808 | 22.3166 | 27.315 | 31.0948 | 34.8705
| BrantfordIce Accretion2080RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2080 | 18.2451 | 22.1983 | 27.21 | 31.0016 | 34.776
| BrantfordIce Accretion2085RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2085 | 18.1094 | 22.0801 | 27.105 | 30.9083 | 34.6815
| BrantfordIce Accretion2090RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2090 | 17.3822 | 21.2895 | 26.22 | 29.9563 | 33.6546
| BrantfordIce Accretion2095RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2095 | 16.7908 | 20.6172 | 25.44 | 29.0975 | 32.7222
| BrantfordIce Accretion2100RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2100 | 16.1993 | 19.9449 | 24.66 | 28.2387 | 31.7898
| BrantfordIce Accretion2023RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2023 | 20.5414 | 24.6261 | 29.82 | 33.7644 | 37.7244
| BrantfordIce Accretion2025RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2025 | 20.3326 | 24.402 | 29.57 | 33.5045 | 37.4472
| BrantfordIce Accretion2030RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2030 | 20.1239 | 24.1779 | 29.32 | 33.2446 | 37.17
| BrantfordIce Accretion2035RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2035 | 19.9151 | 23.9538 | 29.07 | 32.9847 | 36.8928
| BrantfordIce Accretion2040RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2040 | 19.4489 | 23.4475 | 28.52 | 32.3858 | 36.2502
| BrantfordIce Accretion2045RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2045 | 18.9827 | 22.9412 | 27.97 | 31.7869 | 35.6076
| BrantfordIce Accretion2050RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2050 | 18.3355 | 22.2772 | 27.28 | 31.0637 | 34.839
| BrantfordIce Accretion2055RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2055 | 18.1546 | 22.1195 | 27.14 | 30.9394 | 34.713
| BrantfordIce Accretion2060RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2060 | 17.3822 | 21.2895 | 26.22 | 29.9563 | 33.6546
| BrantfordIce Accretion2065RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2065 | 16.7908 | 20.6172 | 25.44 | 29.0975 | 32.7222
| BrantfordIce Accretion2070RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2070 | 15.8166 | 19.5216 | 24.19 | 27.7189 | 31.2354
| BrantfordIce Accretion2075RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2075 | 15.4339 | 19.0983 | 23.72 | 27.1991 | 30.681
| BrantfordIce Accretion2080RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2080 | 15.0512 | 18.675 | 23.25 | 26.6793 | 30.1266
| BrantfordIce Accretion2085RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2085 | 14.0283 | 17.4798 | 21.795 | 25.0521 | 28.3122
| BrantfordIce Accretion2090RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2090 | 13.0054 | 16.2846 | 20.34 | 23.4249 | 26.4978
| BrantfordIce Accretion2095RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2095 | 13.0054 | 16.2846 | 20.34 | 23.4249 | 26.4978
| BrantfordIce Accretion2100RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2100 | 13.0054 | 16.2846 | 20.34 | 23.4249 | 26.4978
| BrantfordWind2023RCP4.5 | Brantford | Wind | RCP4.5 | 2023 | 86.7541 | 93.5301 | 100.69 | 107.8239 | 114.9576
| BrantfordWind2025RCP4.5 | Brantford | Wind | RCP4.5 | 2025 | 86.7728 | 93.5627 | 100.74 | 107.8881 | 115.0374
| BrantfordWind2030RCP4.5 | Brantford | Wind | RCP4.5 | 2030 | 86.7915 | 93.5952 | 100.79 | 107.9523 | 115.1172
| BrantfordWind2035RCP4.5 | Brantford | Wind | RCP4.5 | 2035 | 86.8102 | 93.6278 | 100.84 | 108.0165 | 115.197
| BrantfordWind2040RCP4.5 | Brantford | Wind | RCP4.5 | 2040 | 86.8289 | 93.6603 | 100.89 | 108.0807 | 115.2768
| BrantfordWind2045RCP4.5 | Brantford | Wind | RCP4.5 | 2045 | 86.8476 | 93.6929 | 100.94 | 108.1449 | 115.3566
| BrantfordWind2050RCP4.5 | Brantford | Wind | RCP4.5 | 2050 | 86.9389 | 93.8203 | 101.112 | 108.3568 | 115.6097
| BrantfordWind2055RCP4.5 | Brantford | Wind | RCP4.5 | 2055 | 87.0114 | 93.9151 | 101.234 | 108.5044 | 115.783
| BrantfordWind2060RCP4.5 | Brantford | Wind | RCP4.5 | 2060 | 87.0839 | 94.01 | 101.356 | 108.6521 | 115.9562
| BrantfordWind2065RCP4.5 | Brantford | Wind | RCP4.5 | 2065 | 87.1565 | 94.1048 | 101.478 | 108.7997 | 116.1295
| BrantfordWind2070RCP4.5 | Brantford | Wind | RCP4.5 | 2070 | 87.229 | 94.1997 | 101.6 | 108.9474 | 116.3028
| BrantfordWind2075RCP4.5 | Brantford | Wind | RCP4.5 | 2075 | 87.3369 | 94.3438 | 101.7883 | 109.1721 | 116.5669
| BrantfordWind2080RCP4.5 | Brantford | Wind | RCP4.5 | 2080 | 87.4449 | 94.488 | 101.9767 | 109.3968 | 116.831
| BrantfordWind2085RCP4.5 | Brantford | Wind | RCP4.5 | 2085 | 87.5528 | 94.6321 | 102.165 | 109.6215 | 117.0951
| BrantfordWind2090RCP4.5 | Brantford | Wind | RCP4.5 | 2090 | 87.6607 | 94.7763 | 102.3533 | 109.8462 | 117.3592
| BrantfordWind2095RCP4.5 | Brantford | Wind | RCP4.5 | 2095 | 87.7687 | 94.9205 | 102.5417 | 110.0709 | 117.6233
| BrantfordWind2100RCP4.5 | Brantford | Wind | RCP4.5 | 2100 | 87.8766 | 95.0646 | 102.73 | 110.2956 | 117.8874
| BrantfordWind2023RCP6.0 | Brantford | Wind | RCP6.0 | 2023 | 86.7541 | 93.5301 | 100.69 | 107.8239 | 114.9576
| BrantfordWind2025RCP6.0 | Brantford | Wind | RCP6.0 | 2025 | 86.7728 | 93.5627 | 100.74 | 107.8881 | 115.0374
| BrantfordWind2030RCP6.0 | Brantford | Wind | RCP6.0 | 2030 | 86.7915 | 93.5952 | 100.79 | 107.9523 | 115.1172
| BrantfordWind2035RCP6.0 | Brantford | Wind | RCP6.0 | 2035 | 86.8102 | 93.6278 | 100.84 | 108.0165 | 115.197
| BrantfordWind2040RCP6.0 | Brantford | Wind | RCP6.0 | 2040 | 86.8289 | 93.6603 | 100.89 | 108.0807 | 115.2768
| BrantfordWind2045RCP6.0 | Brantford | Wind | RCP6.0 | 2045 | 86.8476 | 93.6929 | 100.94 | 108.1449 | 115.3566
| BrantfordWind2050RCP6.0 | Brantford | Wind | RCP6.0 | 2050 | 86.9389 | 93.8203 | 101.112 | 108.3568 | 115.6097
| BrantfordWind2055RCP6.0 | Brantford | Wind | RCP6.0 | 2055 | 87.0114 | 93.9151 | 101.234 | 108.5044 | 115.783
| BrantfordWind2060RCP6.0 | Brantford | Wind | RCP6.0 | 2060 | 87.0839 | 94.01 | 101.356 | 108.6521 | 115.9562
| BrantfordWind2065RCP6.0 | Brantford | Wind | RCP6.0 | 2065 | 87.1565 | 94.1048 | 101.478 | 108.7997 | 116.1295
| BrantfordWind2070RCP6.0 | Brantford | Wind | RCP6.0 | 2070 | 87.229 | 94.1997 | 101.6 | 108.9474 | 116.3028
| BrantfordWind2075RCP6.0 | Brantford | Wind | RCP6.0 | 2075 | 87.3909 | 94.4159 | 101.8825 | 109.2844 | 116.6989
| BrantfordWind2080RCP6.0 | Brantford | Wind | RCP6.0 | 2080 | 87.5528 | 94.6321 | 102.165 | 109.6215 | 117.0951
| BrantfordWind2085RCP6.0 | Brantford | Wind | RCP6.0 | 2085 | 87.7147 | 94.8484 | 102.4475 | 109.9586 | 117.4912
| BrantfordWind2090RCP6.0 | Brantford | Wind | RCP6.0 | 2090 | 88.1961 | 95.4707 | 103.25 | 110.9126 | 118.6018
| BrantfordWind2095RCP6.0 | Brantford | Wind | RCP6.0 | 2095 | 88.5156 | 95.8768 | 103.77 | 111.5297 | 119.3162
| BrantfordWind2100RCP6.0 | Brantford | Wind | RCP6.0 | 2100 | 88.8351 | 96.2829 | 104.29 | 112.1467 | 120.0306
| BrantfordWind2023RCP8.5 | Brantford | Wind | RCP8.5 | 2023 | 86.7541 | 93.5301 | 100.69 | 107.8239 | 114.9576
| BrantfordWind2025RCP8.5 | Brantford | Wind | RCP8.5 | 2025 | 86.7915 | 93.5952 | 100.79 | 107.9523 | 115.1172
| BrantfordWind2030RCP8.5 | Brantford | Wind | RCP8.5 | 2030 | 86.8289 | 93.6603 | 100.89 | 108.0807 | 115.2768
| BrantfordWind2035RCP8.5 | Brantford | Wind | RCP8.5 | 2035 | 86.8663 | 93.7254 | 100.99 | 108.2091 | 115.4364
| BrantfordWind2040RCP8.5 | Brantford | Wind | RCP8.5 | 2040 | 86.9872 | 93.8835 | 101.1933 | 108.4552 | 115.7252
| BrantfordWind2045RCP8.5 | Brantford | Wind | RCP8.5 | 2045 | 87.1081 | 94.0416 | 101.3967 | 108.7013 | 116.014
| BrantfordWind2050RCP8.5 | Brantford | Wind | RCP8.5 | 2050 | 87.4449 | 94.488 | 101.9767 | 109.3968 | 116.831
| BrantfordWind2055RCP8.5 | Brantford | Wind | RCP8.5 | 2055 | 87.6607 | 94.7763 | 102.3533 | 109.8462 | 117.3592
| BrantfordWind2060RCP8.5 | Brantford | Wind | RCP8.5 | 2060 | 88.1961 | 95.4707 | 103.25 | 110.9126 | 118.6018
| BrantfordWind2065RCP8.5 | Brantford | Wind | RCP8.5 | 2065 | 88.5156 | 95.8768 | 103.77 | 111.5297 | 119.3162
| BrantfordWind2070RCP8.5 | Brantford | Wind | RCP8.5 | 2070 | 89.0135 | 96.5309 | 104.63 | 112.5604 | 120.5208
| BrantfordWind2075RCP8.5 | Brantford | Wind | RCP8.5 | 2075 | 89.192 | 96.7789 | 104.97 | 112.9742 | 121.011
| BrantfordWind2080RCP8.5 | Brantford | Wind | RCP8.5 | 2080 | 89.3704 | 97.0269 | 105.31 | 113.3879 | 121.5012
| BrantfordWind2085RCP8.5 | Brantford | Wind | RCP8.5 | 2085 | 89.6424 | 97.3942 | 105.79 | 113.9711 | 122.1852
| BrantfordWind2090RCP8.5 | Brantford | Wind | RCP8.5 | 2090 | 89.9144 | 97.7616 | 106.27 | 114.5542 | 122.8692
| BrantfordWind2095RCP8.5 | Brantford | Wind | RCP8.5 | 2095 | 89.9144 | 97.7616 | 106.27 | 114.5542 | 122.8692
| BrantfordWind2100RCP8.5 | Brantford | Wind | RCP8.5 | 2100 | 89.9144 | 97.7616 | 106.27 | 114.5542 | 122.8692
| BrightonIce Accretion2023RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| BrightonIce Accretion2025RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
| BrightonIce Accretion2030RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| BrightonIce Accretion2035RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
| BrightonIce Accretion2040RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| BrightonIce Accretion2045RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
| BrightonIce Accretion2050RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
| BrightonIce Accretion2055RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
| BrightonIce Accretion2060RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
| BrightonIce Accretion2065RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
| BrightonIce Accretion2070RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
| BrightonIce Accretion2075RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2075 | 16.8859 | 20.3972 | 24.8292 | 28.2123 | 31.5682
| BrightonIce Accretion2080RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2080 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
| BrightonIce Accretion2085RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2085 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
| BrightonIce Accretion2090RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2090 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
| BrightonIce Accretion2095RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2095 | 16.7235 | 20.3142 | 24.8458 | 28.2877 | 31.7152
| BrightonIce Accretion2100RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.2935 | 24.85 | 28.3065 | 31.752
| BrightonIce Accretion2023RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| BrightonIce Accretion2025RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
| BrightonIce Accretion2030RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| BrightonIce Accretion2035RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
| BrightonIce Accretion2040RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| BrightonIce Accretion2045RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
| BrightonIce Accretion2050RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
| BrightonIce Accretion2055RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
| BrightonIce Accretion2060RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
| BrightonIce Accretion2065RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
| BrightonIce Accretion2070RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
| BrightonIce Accretion2075RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2075 | 16.8656 | 20.3869 | 24.8313 | 28.2217 | 31.5866
| BrightonIce Accretion2080RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2080 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
| BrightonIce Accretion2085RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2085 | 16.7438 | 20.3246 | 24.8438 | 28.2782 | 31.6969
| BrightonIce Accretion2090RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2090 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
| BrightonIce Accretion2095RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2095 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
| BrightonIce Accretion2100RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2100 | 15.6565 | 19.173 | 23.6 | 26.9505 | 30.2715
| BrightonIce Accretion2023RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| BrightonIce Accretion2025RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2025 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| BrightonIce Accretion2030RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2030 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| BrightonIce Accretion2035RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2035 | 17.6745 | 21.2272 | 25.725 | 29.154 | 32.571
| BrightonIce Accretion2040RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2040 | 17.4251 | 20.9575 | 25.425 | 28.8338 | 32.2245
| BrightonIce Accretion2045RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2045 | 17.1758 | 20.6877 | 25.125 | 28.5137 | 31.878
| BrightonIce Accretion2050RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2050 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
| BrightonIce Accretion2055RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2055 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
| BrightonIce Accretion2060RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2060 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
| BrightonIce Accretion2065RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2065 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
| BrightonIce Accretion2070RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2070 | 15.2216 | 18.6888 | 23.05 | 26.3478 | 29.631
| BrightonIce Accretion2075RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2075 | 14.7867 | 18.2047 | 22.5 | 25.7452 | 28.9905
| BrightonIce Accretion2080RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2080 | 14.3518 | 17.7205 | 21.95 | 25.1425 | 28.35
| BrightonIce Accretion2085RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2085 | 13.6908 | 16.9424 | 21.025 | 24.0972 | 27.1845
| BrightonIce Accretion2090RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2090 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| BrightonIce Accretion2095RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2095 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| BrightonIce Accretion2100RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2100 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| BrightonWind2023RCP4.5 | Brighton | Wind | RCP4.5 | 2023 | 87.735 | 94.5124 | 101.6363 | 108.7616 | 115.8884
| BrightonWind2025RCP4.5 | Brighton | Wind | RCP4.5 | 2025 | 87.7016 | 94.4764 | 101.6009 | 108.7238 | 115.85
| BrightonWind2030RCP4.5 | Brighton | Wind | RCP4.5 | 2030 | 87.6681 | 94.4404 | 101.5656 | 108.686 | 115.8116
| BrightonWind2035RCP4.5 | Brighton | Wind | RCP4.5 | 2035 | 87.6347 | 94.4043 | 101.5302 | 108.6482 | 115.7733
| BrightonWind2040RCP4.5 | Brighton | Wind | RCP4.5 | 2040 | 87.6013 | 94.3683 | 101.4949 | 108.6103 | 115.7349
| BrightonWind2045RCP4.5 | Brighton | Wind | RCP4.5 | 2045 | 87.5678 | 94.3323 | 101.4595 | 108.5725 | 115.6965
| BrightonWind2050RCP4.5 | Brighton | Wind | RCP4.5 | 2050 | 87.6582 | 94.4616 | 101.6403 | 108.7941 | 115.9621
| BrightonWind2055RCP4.5 | Brighton | Wind | RCP4.5 | 2055 | 87.7821 | 94.627 | 101.8565 | 109.0534 | 116.2661
| BrightonWind2060RCP4.5 | Brighton | Wind | RCP4.5 | 2060 | 87.9059 | 94.7923 | 102.0726 | 109.3128 | 116.57
| BrightonWind2065RCP4.5 | Brighton | Wind | RCP4.5 | 2065 | 88.0298 | 94.9576 | 102.2888 | 109.5722 | 116.874
| BrightonWind2070RCP4.5 | Brighton | Wind | RCP4.5 | 2070 | 88.1536 | 95.1229 | 102.5049 | 109.8315 | 117.178
| BrightonWind2075RCP4.5 | Brighton | Wind | RCP4.5 | 2075 | 88.2161 | 95.209 | 102.6194 | 109.9702 | 117.3411
| BrightonWind2080RCP4.5 | Brighton | Wind | RCP4.5 | 2080 | 88.2786 | 95.2951 | 102.7338 | 110.1089 | 117.5042
| BrightonWind2085RCP4.5 | Brighton | Wind | RCP4.5 | 2085 | 88.3411 | 95.3812 | 102.8483 | 110.2476 | 117.6673
| BrightonWind2090RCP4.5 | Brighton | Wind | RCP4.5 | 2090 | 88.4036 | 95.4673 | 102.9628 | 110.3863 | 117.8304
| BrightonWind2095RCP4.5 | Brighton | Wind | RCP4.5 | 2095 | 88.4661 | 95.5534 | 103.0772 | 110.525 | 117.9936
| BrightonWind2100RCP4.5 | Brighton | Wind | RCP4.5 | 2100 | 88.5286 | 95.6395 | 103.1917 | 110.6637 | 118.1567
| BrightonWind2023RCP6.0 | Brighton | Wind | RCP6.0 | 2023 | 87.735 | 94.5124 | 101.6363 | 108.7616 | 115.8884
| BrightonWind2025RCP6.0 | Brighton | Wind | RCP6.0 | 2025 | 87.7016 | 94.4764 | 101.6009 | 108.7238 | 115.85
| BrightonWind2030RCP6.0 | Brighton | Wind | RCP6.0 | 2030 | 87.6681 | 94.4404 | 101.5656 | 108.686 | 115.8116
| BrightonWind2035RCP6.0 | Brighton | Wind | RCP6.0 | 2035 | 87.6347 | 94.4043 | 101.5302 | 108.6482 | 115.7733
| BrightonWind2040RCP6.0 | Brighton | Wind | RCP6.0 | 2040 | 87.6013 | 94.3683 | 101.4949 | 108.6103 | 115.7349
| BrightonWind2045RCP6.0 | Brighton | Wind | RCP6.0 | 2045 | 87.5678 | 94.3323 | 101.4595 | 108.5725 | 115.6965
| BrightonWind2050RCP6.0 | Brighton | Wind | RCP6.0 | 2050 | 87.6582 | 94.4616 | 101.6403 | 108.7941 | 115.9621
| BrightonWind2055RCP6.0 | Brighton | Wind | RCP6.0 | 2055 | 87.7821 | 94.627 | 101.8565 | 109.0534 | 116.2661
| BrightonWind2060RCP6.0 | Brighton | Wind | RCP6.0 | 2060 | 87.9059 | 94.7923 | 102.0726 | 109.3128 | 116.57
| BrightonWind2065RCP6.0 | Brighton | Wind | RCP6.0 | 2065 | 88.0298 | 94.9576 | 102.2888 | 109.5722 | 116.874
| BrightonWind2070RCP6.0 | Brighton | Wind | RCP6.0 | 2070 | 88.1536 | 95.1229 | 102.5049 | 109.8315 | 117.178
| BrightonWind2075RCP6.0 | Brighton | Wind | RCP6.0 | 2075 | 88.2474 | 95.2521 | 102.6766 | 110.0396 | 117.4227
| BrightonWind2080RCP6.0 | Brighton | Wind | RCP6.0 | 2080 | 88.3411 | 95.3812 | 102.8483 | 110.2476 | 117.6673
| BrightonWind2085RCP6.0 | Brighton | Wind | RCP6.0 | 2085 | 88.4349 | 95.5104 | 103.02 | 110.4556 | 117.912
| BrightonWind2090RCP6.0 | Brighton | Wind | RCP6.0 | 2090 | 88.828 | 96.0027 | 103.6361 | 111.1824 | 118.7439
| BrightonWind2095RCP6.0 | Brighton | Wind | RCP6.0 | 2095 | 89.1275 | 96.3659 | 104.0805 | 111.7012 | 119.3311
| BrightonWind2100RCP6.0 | Brighton | Wind | RCP6.0 | 2100 | 89.4269 | 96.7291 | 104.5249 | 112.2199 | 119.9183
| BrightonWind2023RCP8.5 | Brighton | Wind | RCP8.5 | 2023 | 87.735 | 94.5124 | 101.6363 | 108.7616 | 115.8884
| BrightonWind2025RCP8.5 | Brighton | Wind | RCP8.5 | 2025 | 87.6681 | 94.4404 | 101.5656 | 108.686 | 115.8116
| BrightonWind2030RCP8.5 | Brighton | Wind | RCP8.5 | 2030 | 87.6013 | 94.3683 | 101.4949 | 108.6103 | 115.7349
| BrightonWind2035RCP8.5 | Brighton | Wind | RCP8.5 | 2035 | 87.5344 | 94.2963 | 101.4242 | 108.5347 | 115.6581
| BrightonWind2040RCP8.5 | Brighton | Wind | RCP8.5 | 2040 | 87.7408 | 94.5719 | 101.7844 | 108.967 | 116.1647
| BrightonWind2045RCP8.5 | Brighton | Wind | RCP8.5 | 2045 | 87.9472 | 94.8474 | 102.1447 | 109.3993 | 116.6714
| BrightonWind2050RCP8.5 | Brighton | Wind | RCP8.5 | 2050 | 88.2786 | 95.2951 | 102.7338 | 110.1089 | 117.5042
| BrightonWind2055RCP8.5 | Brighton | Wind | RCP8.5 | 2055 | 88.4036 | 95.4673 | 102.9628 | 110.3863 | 117.8304
| BrightonWind2060RCP8.5 | Brighton | Wind | RCP8.5 | 2060 | 88.828 | 96.0027 | 103.6361 | 111.1824 | 118.7439
| BrightonWind2065RCP8.5 | Brighton | Wind | RCP8.5 | 2065 | 89.1275 | 96.3659 | 104.0805 | 111.7012 | 119.3311
| BrightonWind2070RCP8.5 | Brighton | Wind | RCP8.5 | 2070 | 89.3455 | 96.6383 | 104.4205 | 112.1046 | 119.7955
| BrightonWind2075RCP8.5 | Brighton | Wind | RCP8.5 | 2075 | 89.2641 | 96.5475 | 104.3162 | 111.9893 | 119.6727
| BrightonWind2080RCP8.5 | Brighton | Wind | RCP8.5 | 2080 | 89.1827 | 96.4567 | 104.2118 | 111.8741 | 119.5499
| BrightonWind2085RCP8.5 | Brighton | Wind | RCP8.5 | 2085 | 89.3964 | 96.7808 | 104.6764 | 112.4522 | 120.2465
| BrightonWind2090RCP8.5 | Brighton | Wind | RCP8.5 | 2090 | 89.61 | 97.1048 | 105.141 | 113.0304 | 120.9431
| BrightonWind2095RCP8.5 | Brighton | Wind | RCP8.5 | 2095 | 89.61 | 97.1048 | 105.141 | 113.0304 | 120.9431
| BrightonWind2100RCP8.5 | Brighton | Wind | RCP8.5 | 2100 | 89.61 | 97.1048 | 105.141 | 113.0304 | 120.9431
| BrockvilleIce Accretion2023RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2023 | 20.6249 | 24.5763 | 29.61 | 33.4593 | 37.3086
| BrockvilleIce Accretion2025RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2025 | 20.6945 | 24.6801 | 29.755 | 33.6345 | 37.5102
| BrockvilleIce Accretion2030RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2030 | 20.764 | 24.7838 | 29.9 | 33.8096 | 37.7118
| BrockvilleIce Accretion2035RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2035 | 20.8336 | 24.8875 | 30.045 | 33.9847 | 37.9134
| BrockvilleIce Accretion2040RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2040 | 20.9032 | 24.9913 | 30.19 | 34.1599 | 38.115
| BrockvilleIce Accretion2045RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2045 | 20.9728 | 25.0951 | 30.335 | 34.335 | 38.3166
| BrockvilleIce Accretion2050RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2050 | 20.9046 | 25.0544 | 30.318 | 34.3339 | 38.3368
| BrockvilleIce Accretion2055RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2055 | 20.7668 | 24.91 | 30.156 | 34.1576 | 38.1553
| BrockvilleIce Accretion2060RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2060 | 20.6291 | 24.7655 | 29.994 | 33.9814 | 37.9739
| BrockvilleIce Accretion2065RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2065 | 20.4913 | 24.6211 | 29.832 | 33.8051 | 37.7924
| BrockvilleIce Accretion2070RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2070 | 20.3535 | 24.4767 | 29.67 | 33.6288 | 37.611
| BrockvilleIce Accretion2075RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2075 | 20.4231 | 24.5846 | 29.825 | 33.8209 | 37.8378
| BrockvilleIce Accretion2080RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2080 | 20.4927 | 24.6925 | 29.98 | 34.013 | 38.0646
| BrockvilleIce Accretion2085RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2085 | 20.5623 | 24.8004 | 30.135 | 34.2051 | 38.2914
| BrockvilleIce Accretion2090RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2090 | 20.6318 | 24.9083 | 30.29 | 34.3972 | 38.5182
| BrockvilleIce Accretion2095RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2095 | 20.7014 | 25.0162 | 30.445 | 34.5893 | 38.745
| BrockvilleIce Accretion2100RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2100 | 20.771 | 25.1241 | 30.6 | 34.7814 | 38.9718
| BrockvilleIce Accretion2023RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2023 | 20.6249 | 24.5763 | 29.61 | 33.4593 | 37.3086
| BrockvilleIce Accretion2025RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2025 | 20.6945 | 24.6801 | 29.755 | 33.6345 | 37.5102
| BrockvilleIce Accretion2030RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2030 | 20.764 | 24.7838 | 29.9 | 33.8096 | 37.7118
| BrockvilleIce Accretion2035RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2035 | 20.8336 | 24.8875 | 30.045 | 33.9847 | 37.9134
| BrockvilleIce Accretion2040RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2040 | 20.9032 | 24.9913 | 30.19 | 34.1599 | 38.115
| BrockvilleIce Accretion2045RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2045 | 20.9728 | 25.0951 | 30.335 | 34.335 | 38.3166
| BrockvilleIce Accretion2050RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2050 | 20.9046 | 25.0544 | 30.318 | 34.3339 | 38.3368
| BrockvilleIce Accretion2055RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2055 | 20.7668 | 24.91 | 30.156 | 34.1576 | 38.1553
| BrockvilleIce Accretion2060RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2060 | 20.6291 | 24.7655 | 29.994 | 33.9814 | 37.9739
| BrockvilleIce Accretion2065RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2065 | 20.4913 | 24.6211 | 29.832 | 33.8051 | 37.7924
| BrockvilleIce Accretion2070RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2070 | 20.3535 | 24.4767 | 29.67 | 33.6288 | 37.611
| BrockvilleIce Accretion2075RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2075 | 20.4579 | 24.6385 | 29.9025 | 33.9169 | 37.9512
| BrockvilleIce Accretion2080RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2080 | 20.5623 | 24.8004 | 30.135 | 34.2051 | 38.2914
| BrockvilleIce Accretion2085RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2085 | 20.6666 | 24.9622 | 30.3675 | 34.4932 | 38.6316
| BrockvilleIce Accretion2090RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2090 | 20.6249 | 24.9913 | 30.49 | 34.6797 | 38.8836
| BrockvilleIce Accretion2095RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2095 | 20.4788 | 24.8585 | 30.38 | 34.578 | 38.7954
| BrockvilleIce Accretion2100RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2100 | 20.3326 | 24.7257 | 30.27 | 34.4763 | 38.7072
| BrockvilleIce Accretion2023RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2023 | 20.6249 | 24.5763 | 29.61 | 33.4593 | 37.3086
| BrockvilleIce Accretion2025RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2025 | 20.764 | 24.7838 | 29.9 | 33.8096 | 37.7118
| BrockvilleIce Accretion2030RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2030 | 20.9032 | 24.9913 | 30.19 | 34.1599 | 38.115
| BrockvilleIce Accretion2035RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2035 | 21.0424 | 25.1988 | 30.48 | 34.5102 | 38.5182
| BrockvilleIce Accretion2040RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2040 | 20.8128 | 24.9581 | 30.21 | 34.2164 | 38.2158
| BrockvilleIce Accretion2045RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2045 | 20.5831 | 24.7174 | 29.94 | 33.9226 | 37.9134
| BrockvilleIce Accretion2050RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2050 | 20.4927 | 24.6925 | 29.98 | 34.013 | 38.0646
| BrockvilleIce Accretion2055RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2055 | 20.6318 | 24.9083 | 30.29 | 34.3972 | 38.5182
| BrockvilleIce Accretion2060RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2060 | 20.6249 | 24.9913 | 30.49 | 34.6797 | 38.8836
| BrockvilleIce Accretion2065RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2065 | 20.4788 | 24.8585 | 30.38 | 34.578 | 38.7954
| BrockvilleIce Accretion2070RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2070 | 20.0473 | 24.4103 | 29.91 | 34.0808 | 38.2662
| BrockvilleIce Accretion2075RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2075 | 19.762 | 24.0949 | 29.55 | 33.6853 | 37.8252
| BrockvilleIce Accretion2080RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2080 | 19.4767 | 23.7795 | 29.19 | 33.2898 | 37.3842
| BrockvilleIce Accretion2085RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2085 | 18.7148 | 22.8831 | 28.14 | 32.1202 | 36.0801
| BrockvilleIce Accretion2090RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2090 | 17.9528 | 21.9867 | 27.09 | 30.9507 | 34.776
| BrockvilleIce Accretion2095RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2095 | 17.9528 | 21.9867 | 27.09 | 30.9507 | 34.776
| BrockvilleIce Accretion2100RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2100 | 17.9528 | 21.9867 | 27.09 | 30.9507 | 34.776
| BrockvilleWind2023RCP4.5 | Brockville | Wind | RCP4.5 | 2023 | 80.1315 | 86.3985 | 93.0212 | 99.6213 | 106.2225
| BrockvilleWind2025RCP4.5 | Brockville | Wind | RCP4.5 | 2025 | 80.1355 | 86.3942 | 93.0043 | 99.5934 | 106.1858
| BrockvilleWind2030RCP4.5 | Brockville | Wind | RCP4.5 | 2030 | 80.1395 | 86.3899 | 92.9875 | 99.5655 | 106.149
| BrockvilleWind2035RCP4.5 | Brockville | Wind | RCP4.5 | 2035 | 80.1434 | 86.3857 | 92.9706 | 99.5376 | 106.1123
| BrockvilleWind2040RCP4.5 | Brockville | Wind | RCP4.5 | 2040 | 80.1474 | 86.3814 | 92.9537 | 99.5097 | 106.0756
| BrockvilleWind2045RCP4.5 | Brockville | Wind | RCP4.5 | 2045 | 80.1514 | 86.3771 | 92.9369 | 99.4818 | 106.0389
| BrockvilleWind2050RCP4.5 | Brockville | Wind | RCP4.5 | 2050 | 80.0743 | 86.2496 | 92.7434 | 99.2354 | 105.7358
| BrockvilleWind2055RCP4.5 | Brockville | Wind | RCP4.5 | 2055 | 79.9933 | 86.1264 | 92.5667 | 99.0169 | 105.4694
| BrockvilleWind2060RCP4.5 | Brockville | Wind | RCP4.5 | 2060 | 79.9123 | 86.0032 | 92.3901 | 98.7983 | 105.203
| BrockvilleWind2065RCP4.5 | Brockville | Wind | RCP4.5 | 2065 | 79.8312 | 85.88 | 92.2134 | 98.5798 | 104.9366
| BrockvilleWind2070RCP4.5 | Brockville | Wind | RCP4.5 | 2070 | 79.7502 | 85.7568 | 92.0368 | 98.3612 | 104.6702
| BrockvilleWind2075RCP4.5 | Brockville | Wind | RCP4.5 | 2075 | 79.7171 | 85.714 | 91.9847 | 98.3005 | 104.6021
| BrockvilleWind2080RCP4.5 | Brockville | Wind | RCP4.5 | 2080 | 79.684 | 85.6712 | 91.9325 | 98.2398 | 104.5339
| BrockvilleWind2085RCP4.5 | Brockville | Wind | RCP4.5 | 2085 | 79.6509 | 85.6284 | 91.8804 | 98.1791 | 104.4657
| BrockvilleWind2090RCP4.5 | Brockville | Wind | RCP4.5 | 2090 | 79.6178 | 85.5857 | 91.8283 | 98.1184 | 104.3976
| BrockvilleWind2095RCP4.5 | Brockville | Wind | RCP4.5 | 2095 | 79.5847 | 85.5429 | 91.7761 | 98.0577 | 104.3294
| BrockvilleWind2100RCP4.5 | Brockville | Wind | RCP4.5 | 2100 | 79.5516 | 85.5001 | 91.724 | 97.997 | 104.2612
| BrockvilleWind2023RCP6.0 | Brockville | Wind | RCP6.0 | 2023 | 80.1315 | 86.3985 | 93.0212 | 99.6213 | 106.2225
| BrockvilleWind2025RCP6.0 | Brockville | Wind | RCP6.0 | 2025 | 80.1355 | 86.3942 | 93.0043 | 99.5934 | 106.1858
| BrockvilleWind2030RCP6.0 | Brockville | Wind | RCP6.0 | 2030 | 80.1395 | 86.3899 | 92.9875 | 99.5655 | 106.149
| BrockvilleWind2035RCP6.0 | Brockville | Wind | RCP6.0 | 2035 | 80.1434 | 86.3857 | 92.9706 | 99.5376 | 106.1123
| BrockvilleWind2040RCP6.0 | Brockville | Wind | RCP6.0 | 2040 | 80.1474 | 86.3814 | 92.9537 | 99.5097 | 106.0756
| BrockvilleWind2045RCP6.0 | Brockville | Wind | RCP6.0 | 2045 | 80.1514 | 86.3771 | 92.9369 | 99.4818 | 106.0389
| BrockvilleWind2050RCP6.0 | Brockville | Wind | RCP6.0 | 2050 | 80.0743 | 86.2496 | 92.7434 | 99.2354 | 105.7358
| BrockvilleWind2055RCP6.0 | Brockville | Wind | RCP6.0 | 2055 | 79.9933 | 86.1264 | 92.5667 | 99.0169 | 105.4694
| BrockvilleWind2060RCP6.0 | Brockville | Wind | RCP6.0 | 2060 | 79.9123 | 86.0032 | 92.3901 | 98.7983 | 105.203
| BrockvilleWind2065RCP6.0 | Brockville | Wind | RCP6.0 | 2065 | 79.8312 | 85.88 | 92.2134 | 98.5798 | 104.9366
| BrockvilleWind2070RCP6.0 | Brockville | Wind | RCP6.0 | 2070 | 79.7502 | 85.7568 | 92.0368 | 98.3612 | 104.6702
| BrockvilleWind2075RCP6.0 | Brockville | Wind | RCP6.0 | 2075 | 79.7006 | 85.6926 | 91.9586 | 98.2702 | 104.568
| BrockvilleWind2080RCP6.0 | Brockville | Wind | RCP6.0 | 2080 | 79.6509 | 85.6284 | 91.8804 | 98.1791 | 104.4657
| BrockvilleWind2085RCP6.0 | Brockville | Wind | RCP6.0 | 2085 | 79.6013 | 85.5643 | 91.8022 | 98.0881 | 104.3635
| BrockvilleWind2090RCP6.0 | Brockville | Wind | RCP6.0 | 2090 | 79.4828 | 85.406 | 91.5921 | 97.833 | 104.0619
| BrockvilleWind2095RCP6.0 | Brockville | Wind | RCP6.0 | 2095 | 79.4139 | 85.3119 | 91.4603 | 97.6689 | 103.8627
| BrockvilleWind2100RCP6.0 | Brockville | Wind | RCP6.0 | 2100 | 79.3451 | 85.2178 | 91.3284 | 97.5048 | 103.6634
| BrockvilleWind2023RCP8.5 | Brockville | Wind | RCP8.5 | 2023 | 80.1315 | 86.3985 | 93.0212 | 99.6213 | 106.2225
| BrockvilleWind2025RCP8.5 | Brockville | Wind | RCP8.5 | 2025 | 80.1395 | 86.3899 | 92.9875 | 99.5655 | 106.149
| BrockvilleWind2030RCP8.5 | Brockville | Wind | RCP8.5 | 2030 | 80.1474 | 86.3814 | 92.9537 | 99.5097 | 106.0756
| BrockvilleWind2035RCP8.5 | Brockville | Wind | RCP8.5 | 2035 | 80.1553 | 86.3728 | 92.92 | 99.4539 | 106.0022
| BrockvilleWind2040RCP8.5 | Brockville | Wind | RCP8.5 | 2040 | 80.0203 | 86.1675 | 92.6256 | 99.0897 | 105.5582
| BrockvilleWind2045RCP8.5 | Brockville | Wind | RCP8.5 | 2045 | 79.8852 | 85.9621 | 92.3312 | 98.7255 | 105.1142
| BrockvilleWind2050RCP8.5 | Brockville | Wind | RCP8.5 | 2050 | 79.684 | 85.6712 | 91.9325 | 98.2398 | 104.5339
| BrockvilleWind2055RCP8.5 | Brockville | Wind | RCP8.5 | 2055 | 79.6178 | 85.5857 | 91.8283 | 98.1184 | 104.3976
| BrockvilleWind2060RCP8.5 | Brockville | Wind | RCP8.5 | 2060 | 79.4828 | 85.406 | 91.5921 | 97.833 | 104.0619
| BrockvilleWind2065RCP8.5 | Brockville | Wind | RCP8.5 | 2065 | 79.4139 | 85.3119 | 91.4603 | 97.6689 | 103.8627
| BrockvilleWind2070RCP8.5 | Brockville | Wind | RCP8.5 | 2070 | 79.4722 | 85.386 | 91.5492 | 97.7706 | 103.9815
| BrockvilleWind2075RCP8.5 | Brockville | Wind | RCP8.5 | 2075 | 79.5993 | 85.5543 | 91.77 | 98.0364 | 104.2997
| BrockvilleWind2080RCP8.5 | Brockville | Wind | RCP8.5 | 2080 | 79.7264 | 85.7226 | 91.9908 | 98.3022 | 104.6178
| BrockvilleWind2085RCP8.5 | Brockville | Wind | RCP8.5 | 2085 | 79.7105 | 85.7226 | 92.0092 | 98.3366 | 104.665
| BrockvilleWind2090RCP8.5 | Brockville | Wind | RCP8.5 | 2090 | 79.6946 | 85.7226 | 92.0276 | 98.3711 | 104.7122
| BrockvilleWind2095RCP8.5 | Brockville | Wind | RCP8.5 | 2095 | 79.6946 | 85.7226 | 92.0276 | 98.3711 | 104.7122
| BrockvilleWind2100RCP8.5 | Brockville | Wind | RCP8.5 | 2100 | 79.6946 | 85.7226 | 92.0276 | 98.3711 | 104.7122
| Burk's FallsIce Accretion2023RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2023 | 15.2321 | 18.1504 | 21.868 | 24.7108 | 27.526
| Burk's FallsIce Accretion2025RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2025 | 15.3086 | 18.2509 | 22 | 24.8641 | 27.7061
| Burk's FallsIce Accretion2030RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2030 | 15.3852 | 18.3513 | 22.132 | 25.0174 | 27.8863
| Burk's FallsIce Accretion2035RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2035 | 15.4617 | 18.4517 | 22.264 | 25.1707 | 28.0665
| Burk's FallsIce Accretion2040RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2040 | 15.5382 | 18.5522 | 22.396 | 25.3241 | 28.2467
| Burk's FallsIce Accretion2045RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2045 | 15.6148 | 18.6526 | 22.528 | 25.4774 | 28.4269
| Burk's FallsIce Accretion2050RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2050 | 15.7373 | 18.8261 | 22.7612 | 25.755 | 28.7512
| Burk's FallsIce Accretion2055RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2055 | 15.7832 | 18.8991 | 22.8624 | 25.8793 | 28.8953
| Burk's FallsIce Accretion2060RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2060 | 15.8291 | 18.9721 | 22.9636 | 26.0036 | 29.0395
| Burk's FallsIce Accretion2065RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2065 | 15.875 | 19.0452 | 23.0648 | 26.1279 | 29.1836
| Burk's FallsIce Accretion2070RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2070 | 15.921 | 19.1182 | 23.166 | 26.2522 | 29.3278
| Burk's FallsIce Accretion2075RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2075 | 15.9235 | 19.1395 | 23.21 | 26.3143 | 29.4109
| Burk's FallsIce Accretion2080RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2080 | 15.9261 | 19.1608 | 23.254 | 26.3765 | 29.4941
| Burk's FallsIce Accretion2085RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2085 | 15.9286 | 19.1821 | 23.298 | 26.4386 | 29.5772
| Burk's FallsIce Accretion2090RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2090 | 15.9312 | 19.2034 | 23.342 | 26.5008 | 29.6604
| Burk's FallsIce Accretion2095RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2095 | 15.9337 | 19.2247 | 23.386 | 26.5629 | 29.7436
| Burk's FallsIce Accretion2100RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2100 | 15.9363 | 19.246 | 23.43 | 26.6251 | 29.8267
| Burk's FallsIce Accretion2023RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2023 | 15.2321 | 18.1504 | 21.868 | 24.7108 | 27.526
| Burk's FallsIce Accretion2025RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2025 | 15.3086 | 18.2509 | 22 | 24.8641 | 27.7061
| Burk's FallsIce Accretion2030RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2030 | 15.3852 | 18.3513 | 22.132 | 25.0174 | 27.8863
| Burk's FallsIce Accretion2035RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2035 | 15.4617 | 18.4517 | 22.264 | 25.1707 | 28.0665
| Burk's FallsIce Accretion2040RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2040 | 15.5382 | 18.5522 | 22.396 | 25.3241 | 28.2467
| Burk's FallsIce Accretion2045RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2045 | 15.6148 | 18.6526 | 22.528 | 25.4774 | 28.4269
| Burk's FallsIce Accretion2050RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2050 | 15.7373 | 18.8261 | 22.7612 | 25.755 | 28.7512
| Burk's FallsIce Accretion2055RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2055 | 15.7832 | 18.8991 | 22.8624 | 25.8793 | 28.8953
| Burk's FallsIce Accretion2060RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2060 | 15.8291 | 18.9721 | 22.9636 | 26.0036 | 29.0395
| Burk's FallsIce Accretion2065RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2065 | 15.875 | 19.0452 | 23.0648 | 26.1279 | 29.1836
| Burk's FallsIce Accretion2070RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2070 | 15.921 | 19.1182 | 23.166 | 26.2522 | 29.3278
| Burk's FallsIce Accretion2075RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2075 | 15.9248 | 19.1502 | 23.232 | 26.3454 | 29.4525
| Burk's FallsIce Accretion2080RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2080 | 15.9286 | 19.1821 | 23.298 | 26.4386 | 29.5772
| Burk's FallsIce Accretion2085RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2085 | 15.9324 | 19.2141 | 23.364 | 26.5318 | 29.702
| Burk's FallsIce Accretion2090RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2090 | 15.9618 | 19.2947 | 23.5107 | 26.7328 | 29.9468
| Burk's FallsIce Accretion2095RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2095 | 15.9873 | 19.3434 | 23.5913 | 26.8405 | 30.067
| Burk's FallsIce Accretion2100RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2100 | 16.0128 | 19.3921 | 23.672 | 26.9482 | 30.1871
| Burk's FallsIce Accretion2023RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2023 | 15.2321 | 18.1504 | 21.868 | 24.7108 | 27.526
| Burk's FallsIce Accretion2025RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2025 | 15.3852 | 18.3513 | 22.132 | 25.0174 | 27.8863
| Burk's FallsIce Accretion2030RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2030 | 15.5382 | 18.5522 | 22.396 | 25.3241 | 28.2467
| Burk's FallsIce Accretion2035RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2035 | 15.6913 | 18.753 | 22.66 | 25.6307 | 28.607
| Burk's FallsIce Accretion2040RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2040 | 15.7679 | 18.8748 | 22.8287 | 25.8378 | 28.8473
| Burk's FallsIce Accretion2045RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2045 | 15.8444 | 18.9965 | 22.9973 | 26.045 | 29.0875
| Burk's FallsIce Accretion2050RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2050 | 15.9261 | 19.1608 | 23.254 | 26.3765 | 29.4941
| Burk's FallsIce Accretion2055RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2055 | 15.9312 | 19.2034 | 23.342 | 26.5008 | 29.6604
| Burk's FallsIce Accretion2060RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2060 | 15.9618 | 19.2947 | 23.5107 | 26.7328 | 29.9468
| Burk's FallsIce Accretion2065RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2065 | 15.9873 | 19.3434 | 23.5913 | 26.8405 | 30.067
| Burk's FallsIce Accretion2070RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2070 | 15.8801 | 19.2521 | 23.5253 | 26.7908 | 30.03
| Burk's FallsIce Accretion2075RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2075 | 15.7475 | 19.1121 | 23.3787 | 26.6333 | 29.8729
| Burk's FallsIce Accretion2080RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2080 | 15.6148 | 18.9721 | 23.232 | 26.4759 | 29.7158
| Burk's FallsIce Accretion2085RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2085 | 15.2091 | 18.5248 | 22.715 | 25.9166 | 29.106
| Burk's FallsIce Accretion2090RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2090 | 14.8034 | 18.0774 | 22.198 | 25.3572 | 28.4962
| Burk's FallsIce Accretion2095RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2095 | 14.8034 | 18.0774 | 22.198 | 25.3572 | 28.4962
| Burk's FallsIce Accretion2100RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2100 | 14.8034 | 18.0774 | 22.198 | 25.3572 | 28.4962
| Burk's FallsWind2023RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2023 | 69.3273 | 74.6976 | 80.36 | 86.0109 | 91.6651
| Burk's FallsWind2025RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2025 | 69.371 | 74.7559 | 80.436 | 86.1008 | 91.77
| Burk's FallsWind2030RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2030 | 69.4148 | 74.8142 | 80.512 | 86.1906 | 91.8749
| Burk's FallsWind2035RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2035 | 69.4585 | 74.8724 | 80.588 | 86.2805 | 91.9798
| Burk's FallsWind2040RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2040 | 69.5023 | 74.9307 | 80.664 | 86.3704 | 92.0846
| Burk's FallsWind2045RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2045 | 69.546 | 74.989 | 80.74 | 86.4603 | 92.1895
| Burk's FallsWind2050RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2050 | 69.5842 | 75.0309 | 80.784 | 86.5091 | 92.2397
| Burk's FallsWind2055RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2055 | 69.5787 | 75.0145 | 80.752 | 86.468 | 92.185
| Burk's FallsWind2060RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2060 | 69.5732 | 74.9982 | 80.72 | 86.4269 | 92.1302
| Burk's FallsWind2065RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2065 | 69.5677 | 74.9818 | 80.688 | 86.3858 | 92.0755
| Burk's FallsWind2070RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2070 | 69.5621 | 74.9654 | 80.656 | 86.3447 | 92.0208
| Burk's FallsWind2075RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2075 | 69.6347 | 75.0485 | 80.7533 | 86.4531 | 92.1424
| Burk's FallsWind2080RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2080 | 69.7072 | 75.1316 | 80.8507 | 86.5616 | 92.264
| Burk's FallsWind2085RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2085 | 69.7797 | 75.2147 | 80.948 | 86.67 | 92.3856
| Burk's FallsWind2090RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2090 | 69.8523 | 75.2978 | 81.0453 | 86.7784 | 92.5072
| Burk's FallsWind2095RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2095 | 69.9248 | 75.3808 | 81.1427 | 86.8869 | 92.6288
| Burk's FallsWind2100RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2100 | 69.9973 | 75.4639 | 81.24 | 86.9953 | 92.7504
| Burk's FallsWind2023RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2023 | 69.3273 | 74.6976 | 80.36 | 86.0109 | 91.6651
| Burk's FallsWind2025RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2025 | 69.371 | 74.7559 | 80.436 | 86.1008 | 91.77
| Burk's FallsWind2030RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2030 | 69.4148 | 74.8142 | 80.512 | 86.1906 | 91.8749
| Burk's FallsWind2035RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2035 | 69.4585 | 74.8724 | 80.588 | 86.2805 | 91.9798
| Burk's FallsWind2040RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2040 | 69.5023 | 74.9307 | 80.664 | 86.3704 | 92.0846
| Burk's FallsWind2045RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2045 | 69.546 | 74.989 | 80.74 | 86.4603 | 92.1895
| Burk's FallsWind2050RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2050 | 69.5842 | 75.0309 | 80.784 | 86.5091 | 92.2397
| Burk's FallsWind2055RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2055 | 69.5787 | 75.0145 | 80.752 | 86.468 | 92.185
| Burk's FallsWind2060RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2060 | 69.5732 | 74.9982 | 80.72 | 86.4269 | 92.1302
| Burk's FallsWind2065RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2065 | 69.5677 | 74.9818 | 80.688 | 86.3858 | 92.0755
| Burk's FallsWind2070RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2070 | 69.5621 | 74.9654 | 80.656 | 86.3447 | 92.0208
| Burk's FallsWind2075RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2075 | 69.6709 | 75.0901 | 80.802 | 86.5074 | 92.2032
| Burk's FallsWind2080RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2080 | 69.7797 | 75.2147 | 80.948 | 86.67 | 92.3856
| Burk's FallsWind2085RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2085 | 69.8885 | 75.3393 | 81.094 | 86.8326 | 92.568
| Burk's FallsWind2090RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2090 | 69.8638 | 75.2978 | 81.0293 | 86.7499 | 92.4677
| Burk's FallsWind2095RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2095 | 69.7302 | 75.1316 | 80.8187 | 86.5045 | 92.185
| Burk's FallsWind2100RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2100 | 69.5967 | 74.9654 | 80.608 | 86.2591 | 91.9022
| Burk's FallsWind2023RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2023 | 69.3273 | 74.6976 | 80.36 | 86.0109 | 91.6651
| Burk's FallsWind2025RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2025 | 69.4148 | 74.8142 | 80.512 | 86.1906 | 91.8749
| Burk's FallsWind2030RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2030 | 69.5023 | 74.9307 | 80.664 | 86.3704 | 92.0846
| Burk's FallsWind2035RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2035 | 69.5898 | 75.0473 | 80.816 | 86.5502 | 92.2944
| Burk's FallsWind2040RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2040 | 69.5806 | 75.02 | 80.7627 | 86.4817 | 92.2032
| Burk's FallsWind2045RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2045 | 69.5714 | 74.9927 | 80.7093 | 86.4132 | 92.112
| Burk's FallsWind2050RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2050 | 69.7072 | 75.1316 | 80.8507 | 86.5616 | 92.264
| Burk's FallsWind2055RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2055 | 69.8523 | 75.2978 | 81.0453 | 86.7784 | 92.5072
| Burk's FallsWind2060RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2060 | 69.8638 | 75.2978 | 81.0293 | 86.7499 | 92.4677
| Burk's FallsWind2065RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2065 | 69.7302 | 75.1316 | 80.8187 | 86.5045 | 92.185
| Burk's FallsWind2070RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2070 | 69.7302 | 75.1266 | 80.808 | 86.4874 | 92.1637
| Burk's FallsWind2075RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2075 | 69.8638 | 75.2878 | 81.008 | 86.7157 | 92.4251
| Burk's FallsWind2080RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2080 | 69.9973 | 75.449 | 81.208 | 86.9439 | 92.6866
| Burk's FallsWind2085RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2085 | 70.0284 | 75.4676 | 81.208 | 86.9311 | 92.6592
| Burk's FallsWind2090RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2090 | 70.0595 | 75.4862 | 81.208 | 86.9182 | 92.6318
| Burk's FallsWind2095RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2095 | 70.0595 | 75.4862 | 81.208 | 86.9182 | 92.6318
| Burk's FallsWind2100RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2100 | 70.0595 | 75.4862 | 81.208 | 86.9182 | 92.6318
| BurlingtonIce Accretion2023RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| BurlingtonIce Accretion2025RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
| BurlingtonIce Accretion2030RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| BurlingtonIce Accretion2035RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
| BurlingtonIce Accretion2040RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| BurlingtonIce Accretion2045RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
| BurlingtonIce Accretion2050RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
| BurlingtonIce Accretion2055RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
| BurlingtonIce Accretion2060RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
| BurlingtonIce Accretion2065RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
| BurlingtonIce Accretion2070RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
| BurlingtonIce Accretion2075RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2075 | 15.5377 | 18.8894 | 23.1125 | 26.329 | 29.5313
| BurlingtonIce Accretion2080RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2080 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
| BurlingtonIce Accretion2085RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2085 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
| BurlingtonIce Accretion2090RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2090 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
| BurlingtonIce Accretion2095RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2095 | 15.3405 | 18.7511 | 23.0625 | 26.329 | 29.5942
| BurlingtonIce Accretion2100RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2100 | 15.2912 | 18.7165 | 23.05 | 26.329 | 29.61
| BurlingtonIce Accretion2023RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| BurlingtonIce Accretion2025RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
| BurlingtonIce Accretion2030RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| BurlingtonIce Accretion2035RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
| BurlingtonIce Accretion2040RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| BurlingtonIce Accretion2045RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
| BurlingtonIce Accretion2050RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
| BurlingtonIce Accretion2055RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
| BurlingtonIce Accretion2060RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
| BurlingtonIce Accretion2065RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
| BurlingtonIce Accretion2070RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
| BurlingtonIce Accretion2075RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2075 | 15.513 | 18.8721 | 23.1062 | 26.329 | 29.5391
| BurlingtonIce Accretion2080RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2080 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
| BurlingtonIce Accretion2085RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2085 | 15.3652 | 18.7684 | 23.0688 | 26.329 | 29.5864
| BurlingtonIce Accretion2090RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2090 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
| BurlingtonIce Accretion2095RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2095 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
| BurlingtonIce Accretion2100RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2100 | 14.2127 | 17.596 | 21.825 | 25.0577 | 28.2555
| BurlingtonIce Accretion2023RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| BurlingtonIce Accretion2025RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2025 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| BurlingtonIce Accretion2030RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2030 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| BurlingtonIce Accretion2035RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2035 | 16.6133 | 20.0652 | 24.425 | 27.7415 | 31.059
| BurlingtonIce Accretion2040RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2040 | 16.2712 | 19.6848 | 23.9917 | 27.2707 | 30.5445
| BurlingtonIce Accretion2045RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2045 | 15.9291 | 19.3044 | 23.5583 | 26.7998 | 30.03
| BurlingtonIce Accretion2050RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2050 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
| BurlingtonIce Accretion2055RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2055 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
| BurlingtonIce Accretion2060RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2060 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
| BurlingtonIce Accretion2065RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2065 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
| BurlingtonIce Accretion2070RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2070 | 13.8125 | 17.1464 | 21.325 | 24.5022 | 27.657
| BurlingtonIce Accretion2075RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2075 | 13.4124 | 16.6968 | 20.825 | 23.9466 | 27.0585
| BurlingtonIce Accretion2080RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2080 | 13.0123 | 16.2473 | 20.325 | 23.391 | 26.46
| BurlingtonIce Accretion2085RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2085 | 12.1338 | 15.1994 | 19.0625 | 21.9785 | 24.885
| BurlingtonIce Accretion2090RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2090 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| BurlingtonIce Accretion2095RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2095 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| BurlingtonIce Accretion2100RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2100 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| BurlingtonWind2023RCP4.5 | Burlington | Wind | RCP4.5 | 2023 | 81.5651 | 87.9008 | 94.5828 | 101.2539 | 107.9208
| BurlingtonWind2025RCP4.5 | Burlington | Wind | RCP4.5 | 2025 | 81.5948 | 87.9445 | 94.6455 | 101.3327 | 108.0155
| BurlingtonWind2030RCP4.5 | Burlington | Wind | RCP4.5 | 2030 | 81.6246 | 87.9882 | 94.7081 | 101.4115 | 108.1102
| BurlingtonWind2035RCP4.5 | Burlington | Wind | RCP4.5 | 2035 | 81.6544 | 88.0319 | 94.7708 | 101.4902 | 108.2048
| BurlingtonWind2040RCP4.5 | Burlington | Wind | RCP4.5 | 2040 | 81.6841 | 88.0756 | 94.8335 | 101.569 | 108.2995
| BurlingtonWind2045RCP4.5 | Burlington | Wind | RCP4.5 | 2045 | 81.7139 | 88.1194 | 94.8961 | 101.6478 | 108.3941
| BurlingtonWind2050RCP4.5 | Burlington | Wind | RCP4.5 | 2050 | 81.8086 | 88.2417 | 95.0547 | 101.8373 | 108.6152
| BurlingtonWind2055RCP4.5 | Burlington | Wind | RCP4.5 | 2055 | 81.8735 | 88.3204 | 95.1506 | 101.9479 | 108.7417
| BurlingtonWind2060RCP4.5 | Burlington | Wind | RCP4.5 | 2060 | 81.9384 | 88.3991 | 95.2464 | 102.0585 | 108.8681
| BurlingtonWind2065RCP4.5 | Burlington | Wind | RCP4.5 | 2065 | 82.0034 | 88.4778 | 95.3423 | 102.1692 | 108.9946
| BurlingtonWind2070RCP4.5 | Burlington | Wind | RCP4.5 | 2070 | 82.0683 | 88.5565 | 95.4382 | 102.2798 | 109.121
| BurlingtonWind2075RCP4.5 | Burlington | Wind | RCP4.5 | 2075 | 82.1576 | 88.6818 | 95.609 | 102.4877 | 109.3675
| BurlingtonWind2080RCP4.5 | Burlington | Wind | RCP4.5 | 2080 | 82.2469 | 88.8071 | 95.7797 | 102.6955 | 109.614
| BurlingtonWind2085RCP4.5 | Burlington | Wind | RCP4.5 | 2085 | 82.3362 | 88.9324 | 95.9505 | 102.9034 | 109.8604
| BurlingtonWind2090RCP4.5 | Burlington | Wind | RCP4.5 | 2090 | 82.4254 | 89.0577 | 96.1213 | 103.1113 | 110.1069
| BurlingtonWind2095RCP4.5 | Burlington | Wind | RCP4.5 | 2095 | 82.5147 | 89.183 | 96.292 | 103.3191 | 110.3534
| BurlingtonWind2100RCP4.5 | Burlington | Wind | RCP4.5 | 2100 | 82.604 | 89.3083 | 96.4628 | 103.527 | 110.5998
| BurlingtonWind2023RCP6.0 | Burlington | Wind | RCP6.0 | 2023 | 81.5651 | 87.9008 | 94.5828 | 101.2539 | 107.9208
| BurlingtonWind2025RCP6.0 | Burlington | Wind | RCP6.0 | 2025 | 81.5948 | 87.9445 | 94.6455 | 101.3327 | 108.0155
| BurlingtonWind2030RCP6.0 | Burlington | Wind | RCP6.0 | 2030 | 81.6246 | 87.9882 | 94.7081 | 101.4115 | 108.1102
| BurlingtonWind2035RCP6.0 | Burlington | Wind | RCP6.0 | 2035 | 81.6544 | 88.0319 | 94.7708 | 101.4902 | 108.2048
| BurlingtonWind2040RCP6.0 | Burlington | Wind | RCP6.0 | 2040 | 81.6841 | 88.0756 | 94.8335 | 101.569 | 108.2995
| BurlingtonWind2045RCP6.0 | Burlington | Wind | RCP6.0 | 2045 | 81.7139 | 88.1194 | 94.8961 | 101.6478 | 108.3941
| BurlingtonWind2050RCP6.0 | Burlington | Wind | RCP6.0 | 2050 | 81.8086 | 88.2417 | 95.0547 | 101.8373 | 108.6152
| BurlingtonWind2055RCP6.0 | Burlington | Wind | RCP6.0 | 2055 | 81.8735 | 88.3204 | 95.1506 | 101.9479 | 108.7417
| BurlingtonWind2060RCP6.0 | Burlington | Wind | RCP6.0 | 2060 | 81.9384 | 88.3991 | 95.2464 | 102.0585 | 108.8681
| BurlingtonWind2065RCP6.0 | Burlington | Wind | RCP6.0 | 2065 | 82.0034 | 88.4778 | 95.3423 | 102.1692 | 108.9946
| BurlingtonWind2070RCP6.0 | Burlington | Wind | RCP6.0 | 2070 | 82.0683 | 88.5565 | 95.4382 | 102.2798 | 109.121
| BurlingtonWind2075RCP6.0 | Burlington | Wind | RCP6.0 | 2075 | 82.2022 | 88.7444 | 95.6944 | 102.5916 | 109.4907
| BurlingtonWind2080RCP6.0 | Burlington | Wind | RCP6.0 | 2080 | 82.3362 | 88.9324 | 95.9505 | 102.9034 | 109.8604
| BurlingtonWind2085RCP6.0 | Burlington | Wind | RCP6.0 | 2085 | 82.4701 | 89.1203 | 96.2066 | 103.2152 | 110.2301
| BurlingtonWind2090RCP6.0 | Burlington | Wind | RCP6.0 | 2090 | 82.8854 | 89.6696 | 96.9234 | 104.0735 | 111.2357
| BurlingtonWind2095RCP6.0 | Burlington | Wind | RCP6.0 | 2095 | 83.1668 | 90.0309 | 97.384 | 104.62 | 111.8715
| BurlingtonWind2100RCP6.0 | Burlington | Wind | RCP6.0 | 2100 | 83.4482 | 90.3923 | 97.8446 | 105.1664 | 112.5073
| BurlingtonWind2023RCP8.5 | Burlington | Wind | RCP8.5 | 2023 | 81.5651 | 87.9008 | 94.5828 | 101.2539 | 107.9208
| BurlingtonWind2025RCP8.5 | Burlington | Wind | RCP8.5 | 2025 | 81.6246 | 87.9882 | 94.7081 | 101.4115 | 108.1102
| BurlingtonWind2030RCP8.5 | Burlington | Wind | RCP8.5 | 2030 | 81.6841 | 88.0756 | 94.8335 | 101.569 | 108.2995
| BurlingtonWind2035RCP8.5 | Burlington | Wind | RCP8.5 | 2035 | 81.7436 | 88.1631 | 94.9588 | 101.7266 | 108.4888
| BurlingtonWind2040RCP8.5 | Burlington | Wind | RCP8.5 | 2040 | 81.8519 | 88.2942 | 95.1186 | 101.911 | 108.6995
| BurlingtonWind2045RCP8.5 | Burlington | Wind | RCP8.5 | 2045 | 81.9601 | 88.4253 | 95.2784 | 102.0954 | 108.9103
| BurlingtonWind2050RCP8.5 | Burlington | Wind | RCP8.5 | 2050 | 82.2469 | 88.8071 | 95.7797 | 102.6955 | 109.614
| BurlingtonWind2055RCP8.5 | Burlington | Wind | RCP8.5 | 2055 | 82.4254 | 89.0577 | 96.1213 | 103.1113 | 110.1069
| BurlingtonWind2060RCP8.5 | Burlington | Wind | RCP8.5 | 2060 | 82.8854 | 89.6696 | 96.9234 | 104.0735 | 111.2357
| BurlingtonWind2065RCP8.5 | Burlington | Wind | RCP8.5 | 2065 | 83.1668 | 90.0309 | 97.384 | 104.62 | 111.8715
| BurlingtonWind2070RCP8.5 | Burlington | Wind | RCP8.5 | 2070 | 83.6078 | 90.6225 | 98.1642 | 105.5587 | 112.9752
| BurlingtonWind2075RCP8.5 | Burlington | Wind | RCP8.5 | 2075 | 83.7674 | 90.8527 | 98.4838 | 105.951 | 113.4431
| BurlingtonWind2080RCP8.5 | Burlington | Wind | RCP8.5 | 2080 | 83.927 | 91.0829 | 98.8034 | 106.3432 | 113.9111
| BurlingtonWind2085RCP8.5 | Burlington | Wind | RCP8.5 | 2085 | 84.1827 | 91.4151 | 99.2311 | 106.8562 | 114.5112
| BurlingtonWind2090RCP8.5 | Burlington | Wind | RCP8.5 | 2090 | 84.4384 | 91.7473 | 99.6588 | 107.3692 | 115.1113
| BurlingtonWind2095RCP8.5 | Burlington | Wind | RCP8.5 | 2095 | 84.4384 | 91.7473 | 99.6588 | 107.3692 | 115.1113
| BurlingtonWind2100RCP8.5 | Burlington | Wind | RCP8.5 | 2100 | 84.4384 | 91.7473 | 99.6588 | 107.3692 | 115.1113
| CFB BordenIce Accretion2023RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2023 | 14.9871 | 17.9313 | 21.648 | 24.4871 | 27.3042
| CFB BordenIce Accretion2025RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2025 | 14.982 | 17.9283 | 21.6517 | 24.4954 | 27.3227
| CFB BordenIce Accretion2030RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2030 | 14.9769 | 17.9252 | 21.6553 | 24.5037 | 27.3412
| CFB BordenIce Accretion2035RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2035 | 14.9718 | 17.9222 | 21.659 | 24.512 | 27.3596
| CFB BordenIce Accretion2040RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2040 | 14.9667 | 17.9191 | 21.6627 | 24.5202 | 27.3781
| CFB BordenIce Accretion2045RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2045 | 14.9616 | 17.9161 | 21.6663 | 24.5285 | 27.3966
| CFB BordenIce Accretion2050RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2050 | 14.9167 | 17.8838 | 21.6524 | 24.5269 | 27.4095
| CFB BordenIce Accretion2055RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2055 | 14.8769 | 17.8546 | 21.6348 | 24.5169 | 27.404
| CFB BordenIce Accretion2060RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2060 | 14.8371 | 17.8254 | 21.6172 | 24.507 | 27.3984
| CFB BordenIce Accretion2065RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2065 | 14.7973 | 17.7962 | 21.5996 | 24.497 | 27.3929
| CFB BordenIce Accretion2070RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2070 | 14.7575 | 17.767 | 21.582 | 24.4871 | 27.3874
| CFB BordenIce Accretion2075RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2075 | 14.7575 | 17.7883 | 21.6297 | 24.5534 | 27.4705
| CFB BordenIce Accretion2080RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2080 | 14.7575 | 17.8096 | 21.6773 | 24.6197 | 27.5537
| CFB BordenIce Accretion2085RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2085 | 14.7575 | 17.8309 | 21.725 | 24.686 | 27.6368
| CFB BordenIce Accretion2090RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2090 | 14.7575 | 17.8522 | 21.7727 | 24.7523 | 27.72
| CFB BordenIce Accretion2095RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2095 | 14.7575 | 17.8735 | 21.8203 | 24.8186 | 27.8032
| CFB BordenIce Accretion2100RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2100 | 14.7575 | 17.8948 | 21.868 | 24.8849 | 27.8863
| CFB BordenIce Accretion2023RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2023 | 14.9871 | 17.9313 | 21.648 | 24.4871 | 27.3042
| CFB BordenIce Accretion2025RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2025 | 14.982 | 17.9283 | 21.6517 | 24.4954 | 27.3227
| CFB BordenIce Accretion2030RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2030 | 14.9769 | 17.9252 | 21.6553 | 24.5037 | 27.3412
| CFB BordenIce Accretion2035RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2035 | 14.9718 | 17.9222 | 21.659 | 24.512 | 27.3596
| CFB BordenIce Accretion2040RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2040 | 14.9667 | 17.9191 | 21.6627 | 24.5202 | 27.3781
| CFB BordenIce Accretion2045RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2045 | 14.9616 | 17.9161 | 21.6663 | 24.5285 | 27.3966
| CFB BordenIce Accretion2050RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2050 | 14.9167 | 17.8838 | 21.6524 | 24.5269 | 27.4095
| CFB BordenIce Accretion2055RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2055 | 14.8769 | 17.8546 | 21.6348 | 24.5169 | 27.404
| CFB BordenIce Accretion2060RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2060 | 14.8371 | 17.8254 | 21.6172 | 24.507 | 27.3984
| CFB BordenIce Accretion2065RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2065 | 14.7973 | 17.7962 | 21.5996 | 24.497 | 27.3929
| CFB BordenIce Accretion2070RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2070 | 14.7575 | 17.767 | 21.582 | 24.4871 | 27.3874
| CFB BordenIce Accretion2075RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2075 | 14.7575 | 17.7989 | 21.6535 | 24.5865 | 27.5121
| CFB BordenIce Accretion2080RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2080 | 14.7575 | 17.8309 | 21.725 | 24.686 | 27.6368
| CFB BordenIce Accretion2085RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2085 | 14.7575 | 17.8628 | 21.7965 | 24.7854 | 27.7616
| CFB BordenIce Accretion2090RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2090 | 14.5891 | 17.7244 | 21.6993 | 24.7108 | 27.72
| CFB BordenIce Accretion2095RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2095 | 14.4207 | 17.5539 | 21.5307 | 24.5368 | 27.5537
| CFB BordenIce Accretion2100RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2100 | 14.2523 | 17.3835 | 21.362 | 24.3628 | 27.3874
| CFB BordenIce Accretion2023RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2023 | 14.9871 | 17.9313 | 21.648 | 24.4871 | 27.3042
| CFB BordenIce Accretion2025RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2025 | 14.9769 | 17.9252 | 21.6553 | 24.5037 | 27.3412
| CFB BordenIce Accretion2030RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2030 | 14.9667 | 17.9191 | 21.6627 | 24.5202 | 27.3781
| CFB BordenIce Accretion2035RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2035 | 14.9565 | 17.9131 | 21.67 | 24.5368 | 27.4151
| CFB BordenIce Accretion2040RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2040 | 14.8902 | 17.8644 | 21.6407 | 24.5202 | 27.4058
| CFB BordenIce Accretion2045RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2045 | 14.8238 | 17.8157 | 21.6113 | 24.5037 | 27.3966
| CFB BordenIce Accretion2050RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2050 | 14.7575 | 17.8096 | 21.6773 | 24.6197 | 27.5537
| CFB BordenIce Accretion2055RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2055 | 14.7575 | 17.8522 | 21.7727 | 24.7523 | 27.72
| CFB BordenIce Accretion2060RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2060 | 14.5891 | 17.7244 | 21.6993 | 24.7108 | 27.72
| CFB BordenIce Accretion2065RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2065 | 14.4207 | 17.5539 | 21.5307 | 24.5368 | 27.5537
| CFB BordenIce Accretion2070RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2070 | 14.0074 | 17.1401 | 21.1053 | 24.1059 | 27.1194
| CFB BordenIce Accretion2075RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2075 | 13.7624 | 16.8966 | 20.8487 | 23.849 | 26.8514
| CFB BordenIce Accretion2080RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2080 | 13.5175 | 16.6531 | 20.592 | 23.5921 | 26.5835
| CFB BordenIce Accretion2085RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2085 | 12.8899 | 15.9227 | 19.745 | 22.6475 | 25.5301
| CFB BordenIce Accretion2090RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2090 | 12.2622 | 15.1923 | 18.898 | 21.7028 | 24.4768
| CFB BordenIce Accretion2095RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2095 | 12.2622 | 15.1923 | 18.898 | 21.7028 | 24.4768
| CFB BordenIce Accretion2100RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2100 | 12.2622 | 15.1923 | 18.898 | 21.7028 | 24.4768
| CFB BordenWind2023RCP4.5 | CFB Borden | Wind | RCP4.5 | 2023 | 76.374 | 82.2738 | 88.484 | 94.6967 | 100.9019
| CFB BordenWind2025RCP4.5 | CFB Borden | Wind | RCP4.5 | 2025 | 76.3955 | 82.301 | 88.5192 | 94.7375 | 100.9503
| CFB BordenWind2030RCP4.5 | CFB Borden | Wind | RCP4.5 | 2030 | 76.417 | 82.3283 | 88.5544 | 94.7783 | 100.9988
| CFB BordenWind2035RCP4.5 | CFB Borden | Wind | RCP4.5 | 2035 | 76.4386 | 82.3556 | 88.5896 | 94.8191 | 101.0473
| CFB BordenWind2040RCP4.5 | CFB Borden | Wind | RCP4.5 | 2040 | 76.4601 | 82.3829 | 88.6248 | 94.8599 | 101.0958
| CFB BordenWind2045RCP4.5 | CFB Borden | Wind | RCP4.5 | 2045 | 76.4816 | 82.4102 | 88.66 | 94.9007 | 101.1443
| CFB BordenWind2050RCP4.5 | CFB Borden | Wind | RCP4.5 | 2050 | 76.6232 | 82.5766 | 88.8554 | 95.1204 | 101.3914
| CFB BordenWind2055RCP4.5 | CFB Borden | Wind | RCP4.5 | 2055 | 76.7433 | 82.7157 | 89.0155 | 95.2993 | 101.5901
| CFB BordenWind2060RCP4.5 | CFB Borden | Wind | RCP4.5 | 2060 | 76.8633 | 82.8548 | 89.1757 | 95.4782 | 101.7887
| CFB BordenWind2065RCP4.5 | CFB Borden | Wind | RCP4.5 | 2065 | 76.9834 | 82.9939 | 89.3358 | 95.6571 | 101.9873
| CFB BordenWind2070RCP4.5 | CFB Borden | Wind | RCP4.5 | 2070 | 77.1035 | 83.1331 | 89.496 | 95.836 | 102.186
| CFB BordenWind2075RCP4.5 | CFB Borden | Wind | RCP4.5 | 2075 | 77.1617 | 83.2095 | 89.5957 | 95.9553 | 102.3231
| CFB BordenWind2080RCP4.5 | CFB Borden | Wind | RCP4.5 | 2080 | 77.22 | 83.2858 | 89.6955 | 96.0746 | 102.4602
| CFB BordenWind2085RCP4.5 | CFB Borden | Wind | RCP4.5 | 2085 | 77.2782 | 83.3622 | 89.7952 | 96.1939 | 102.5973
| CFB BordenWind2090RCP4.5 | CFB Borden | Wind | RCP4.5 | 2090 | 77.3365 | 83.4386 | 89.8949 | 96.3131 | 102.7344
| CFB BordenWind2095RCP4.5 | CFB Borden | Wind | RCP4.5 | 2095 | 77.3947 | 83.515 | 89.9947 | 96.4324 | 102.8715
| CFB BordenWind2100RCP4.5 | CFB Borden | Wind | RCP4.5 | 2100 | 77.453 | 83.5914 | 90.0944 | 96.5517 | 103.0086
| CFB BordenWind2023RCP6.0 | CFB Borden | Wind | RCP6.0 | 2023 | 76.374 | 82.2738 | 88.484 | 94.6967 | 100.9019
| CFB BordenWind2025RCP6.0 | CFB Borden | Wind | RCP6.0 | 2025 | 76.3955 | 82.301 | 88.5192 | 94.7375 | 100.9503
| CFB BordenWind2030RCP6.0 | CFB Borden | Wind | RCP6.0 | 2030 | 76.417 | 82.3283 | 88.5544 | 94.7783 | 100.9988
| CFB BordenWind2035RCP6.0 | CFB Borden | Wind | RCP6.0 | 2035 | 76.4386 | 82.3556 | 88.5896 | 94.8191 | 101.0473
| CFB BordenWind2040RCP6.0 | CFB Borden | Wind | RCP6.0 | 2040 | 76.4601 | 82.3829 | 88.6248 | 94.8599 | 101.0958
| CFB BordenWind2045RCP6.0 | CFB Borden | Wind | RCP6.0 | 2045 | 76.4816 | 82.4102 | 88.66 | 94.9007 | 101.1443
| CFB BordenWind2050RCP6.0 | CFB Borden | Wind | RCP6.0 | 2050 | 76.6232 | 82.5766 | 88.8554 | 95.1204 | 101.3914
| CFB BordenWind2055RCP6.0 | CFB Borden | Wind | RCP6.0 | 2055 | 76.7433 | 82.7157 | 89.0155 | 95.2993 | 101.5901
| CFB BordenWind2060RCP6.0 | CFB Borden | Wind | RCP6.0 | 2060 | 76.8633 | 82.8548 | 89.1757 | 95.4782 | 101.7887
| CFB BordenWind2065RCP6.0 | CFB Borden | Wind | RCP6.0 | 2065 | 76.9834 | 82.9939 | 89.3358 | 95.6571 | 101.9873
| CFB BordenWind2070RCP6.0 | CFB Borden | Wind | RCP6.0 | 2070 | 77.1035 | 83.1331 | 89.496 | 95.836 | 102.186
| CFB BordenWind2075RCP6.0 | CFB Borden | Wind | RCP6.0 | 2075 | 77.1908 | 83.2476 | 89.6456 | 96.015 | 102.3916
| CFB BordenWind2080RCP6.0 | CFB Borden | Wind | RCP6.0 | 2080 | 77.2782 | 83.3622 | 89.7952 | 96.1939 | 102.5973
| CFB BordenWind2085RCP6.0 | CFB Borden | Wind | RCP6.0 | 2085 | 77.3656 | 83.4768 | 89.9448 | 96.3728 | 102.8029
| CFB BordenWind2090RCP6.0 | CFB Borden | Wind | RCP6.0 | 2090 | 77.7291 | 83.9242 | 90.4933 | 97.0099 | 103.5302
| CFB BordenWind2095RCP6.0 | CFB Borden | Wind | RCP6.0 | 2095 | 78.0052 | 84.257 | 90.8923 | 97.4682 | 104.0519
| CFB BordenWind2100RCP6.0 | CFB Borden | Wind | RCP6.0 | 2100 | 78.2812 | 84.5898 | 91.2912 | 97.9264 | 104.5736
| CFB BordenWind2023RCP8.5 | CFB Borden | Wind | RCP8.5 | 2023 | 76.374 | 82.2738 | 88.484 | 94.6967 | 100.9019
| CFB BordenWind2025RCP8.5 | CFB Borden | Wind | RCP8.5 | 2025 | 76.417 | 82.3283 | 88.5544 | 94.7783 | 100.9988
| CFB BordenWind2030RCP8.5 | CFB Borden | Wind | RCP8.5 | 2030 | 76.4601 | 82.3829 | 88.6248 | 94.8599 | 101.0958
| CFB BordenWind2035RCP8.5 | CFB Borden | Wind | RCP8.5 | 2035 | 76.5032 | 82.4374 | 88.6952 | 94.9415 | 101.1928
| CFB BordenWind2040RCP8.5 | CFB Borden | Wind | RCP8.5 | 2040 | 76.7033 | 82.6693 | 88.9621 | 95.2397 | 101.5238
| CFB BordenWind2045RCP8.5 | CFB Borden | Wind | RCP8.5 | 2045 | 76.9034 | 82.9012 | 89.2291 | 95.5379 | 101.8549
| CFB BordenWind2050RCP8.5 | CFB Borden | Wind | RCP8.5 | 2050 | 77.22 | 83.2858 | 89.6955 | 96.0746 | 102.4602
| CFB BordenWind2055RCP8.5 | CFB Borden | Wind | RCP8.5 | 2055 | 77.3365 | 83.4386 | 89.8949 | 96.3131 | 102.7344
| CFB BordenWind2060RCP8.5 | CFB Borden | Wind | RCP8.5 | 2060 | 77.7291 | 83.9242 | 90.4933 | 97.0099 | 103.5302
| CFB BordenWind2065RCP8.5 | CFB Borden | Wind | RCP8.5 | 2065 | 78.0052 | 84.257 | 90.8923 | 97.4682 | 104.0519
| CFB BordenWind2070RCP8.5 | CFB Borden | Wind | RCP8.5 | 2070 | 78.4282 | 84.7671 | 91.5112 | 98.1806 | 104.8612
| CFB BordenWind2075RCP8.5 | CFB Borden | Wind | RCP8.5 | 2075 | 78.5751 | 84.9445 | 91.7312 | 98.4349 | 105.1487
| CFB BordenWind2080RCP8.5 | CFB Borden | Wind | RCP8.5 | 2080 | 78.722 | 85.1218 | 91.9512 | 98.6891 | 105.4363
| CFB BordenWind2085RCP8.5 | CFB Borden | Wind | RCP8.5 | 2085 | 78.7524 | 85.1545 | 91.982 | 98.7221 | 105.4664
| CFB BordenWind2090RCP8.5 | CFB Borden | Wind | RCP8.5 | 2090 | 78.7828 | 85.1873 | 92.0128 | 98.755 | 105.4965
| CFB BordenWind2095RCP8.5 | CFB Borden | Wind | RCP8.5 | 2095 | 78.7828 | 85.1873 | 92.0128 | 98.755 | 105.4965
| CFB BordenWind2100RCP8.5 | CFB Borden | Wind | RCP8.5 | 2100 | 78.7828 | 85.1873 | 92.0128 | 98.755 | 105.4965
| CambridgeIce Accretion2023RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
| CambridgeIce Accretion2025RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2025 | 17.3208 | 20.7984 | 25.1958 | 28.5655 | 31.92
| CambridgeIce Accretion2030RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2030 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
| CambridgeIce Accretion2035RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2035 | 17.3788 | 20.8953 | 25.3375 | 28.7444 | 32.13
| CambridgeIce Accretion2040RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2040 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
| CambridgeIce Accretion2045RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2045 | 17.4367 | 20.9921 | 25.4792 | 28.9233 | 32.34
| CambridgeIce Accretion2050RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2050 | 17.4101 | 20.9907 | 25.51 | 28.9788 | 32.4198
| CambridgeIce Accretion2055RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2055 | 17.3544 | 20.9409 | 25.47 | 28.9449 | 32.3946
| CambridgeIce Accretion2060RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2060 | 17.2987 | 20.8911 | 25.43 | 28.911 | 32.3694
| CambridgeIce Accretion2065RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2065 | 17.2431 | 20.8413 | 25.39 | 28.8771 | 32.3442
| CambridgeIce Accretion2070RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2070 | 17.1874 | 20.7915 | 25.35 | 28.8432 | 32.319
| CambridgeIce Accretion2075RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2075 | 17.1555 | 20.7846 | 25.3708 | 28.8809 | 32.3768
| CambridgeIce Accretion2080RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2080 | 17.1236 | 20.7777 | 25.3917 | 28.9186 | 32.4345
| CambridgeIce Accretion2085RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2085 | 17.0917 | 20.7707 | 25.4125 | 28.9562 | 32.4922
| CambridgeIce Accretion2090RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2090 | 17.0598 | 20.7638 | 25.4333 | 28.9939 | 32.55
| CambridgeIce Accretion2095RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2095 | 17.0279 | 20.7569 | 25.4542 | 29.0316 | 32.6077
| CambridgeIce Accretion2100RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2100 | 16.996 | 20.75 | 25.475 | 29.0692 | 32.6655
| CambridgeIce Accretion2023RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
| CambridgeIce Accretion2025RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2025 | 17.3208 | 20.7984 | 25.1958 | 28.5655 | 31.92
| CambridgeIce Accretion2030RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2030 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
| CambridgeIce Accretion2035RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2035 | 17.3788 | 20.8953 | 25.3375 | 28.7444 | 32.13
| CambridgeIce Accretion2040RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2040 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
| CambridgeIce Accretion2045RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2045 | 17.4367 | 20.9921 | 25.4792 | 28.9233 | 32.34
| CambridgeIce Accretion2050RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2050 | 17.4101 | 20.9907 | 25.51 | 28.9788 | 32.4198
| CambridgeIce Accretion2055RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2055 | 17.3544 | 20.9409 | 25.47 | 28.9449 | 32.3946
| CambridgeIce Accretion2060RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2060 | 17.2987 | 20.8911 | 25.43 | 28.911 | 32.3694
| CambridgeIce Accretion2065RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2065 | 17.2431 | 20.8413 | 25.39 | 28.8771 | 32.3442
| CambridgeIce Accretion2070RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2070 | 17.1874 | 20.7915 | 25.35 | 28.8432 | 32.319
| CambridgeIce Accretion2075RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2075 | 17.1396 | 20.7811 | 25.3813 | 28.8997 | 32.4056
| CambridgeIce Accretion2080RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2080 | 17.0917 | 20.7707 | 25.4125 | 28.9562 | 32.4922
| CambridgeIce Accretion2085RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2085 | 17.0439 | 20.7604 | 25.4437 | 29.0127 | 32.5789
| CambridgeIce Accretion2090RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2090 | 16.6887 | 20.4249 | 25.1333 | 28.7114 | 32.298
| CambridgeIce Accretion2095RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2095 | 16.3814 | 20.0998 | 24.7917 | 28.3536 | 31.9305
| CambridgeIce Accretion2100RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2100 | 16.074 | 19.7747 | 24.45 | 27.9957 | 31.563
| CambridgeIce Accretion2023RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
| CambridgeIce Accretion2025RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2025 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
| CambridgeIce Accretion2030RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2030 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
| CambridgeIce Accretion2035RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2035 | 17.4657 | 21.0405 | 25.55 | 29.0127 | 32.445
| CambridgeIce Accretion2040RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2040 | 17.373 | 20.9575 | 25.4833 | 28.9562 | 32.403
| CambridgeIce Accretion2045RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2045 | 17.2802 | 20.8745 | 25.4167 | 28.8997 | 32.361
| CambridgeIce Accretion2050RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2050 | 17.1236 | 20.7777 | 25.3917 | 28.9186 | 32.4345
| CambridgeIce Accretion2055RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2055 | 17.0598 | 20.7638 | 25.4333 | 28.9939 | 32.55
| CambridgeIce Accretion2060RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2060 | 16.6887 | 20.4249 | 25.1333 | 28.7114 | 32.298
| CambridgeIce Accretion2065RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2065 | 16.3814 | 20.0998 | 24.7917 | 28.3536 | 31.9305
| CambridgeIce Accretion2070RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2070 | 15.6507 | 19.3182 | 23.95 | 27.4684 | 30.9855
| CambridgeIce Accretion2075RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2075 | 15.2274 | 18.8617 | 23.45 | 26.9411 | 30.408
| CambridgeIce Accretion2080RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2080 | 14.8041 | 18.4052 | 22.95 | 26.4137 | 29.8305
| CambridgeIce Accretion2085RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2085 | 13.9778 | 17.43 | 21.7875 | 25.086 | 28.3657
| CambridgeIce Accretion2090RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2090 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
| CambridgeIce Accretion2095RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2095 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
| CambridgeIce Accretion2100RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2100 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
| CambridgeWind2023RCP4.5 | Cambridge | Wind | RCP4.5 | 2023 | 83.2259 | 89.6371 | 96.384 | 103.1309 | 109.8887
| CambridgeWind2025RCP4.5 | Cambridge | Wind | RCP4.5 | 2025 | 83.2839 | 89.716 | 96.4912 | 103.261 | 110.0419
| CambridgeWind2030RCP4.5 | Cambridge | Wind | RCP4.5 | 2030 | 83.3419 | 89.7948 | 96.5984 | 103.3911 | 110.1951
| CambridgeWind2035RCP4.5 | Cambridge | Wind | RCP4.5 | 2035 | 83.4 | 89.8737 | 96.7056 | 103.5212 | 110.3484
| CambridgeWind2040RCP4.5 | Cambridge | Wind | RCP4.5 | 2040 | 83.458 | 89.9526 | 96.8128 | 103.6513 | 110.5016
| CambridgeWind2045RCP4.5 | Cambridge | Wind | RCP4.5 | 2045 | 83.516 | 90.0314 | 96.92 | 103.7814 | 110.6548
| CambridgeWind2050RCP4.5 | Cambridge | Wind | RCP4.5 | 2050 | 83.6387 | 90.1889 | 97.1194 | 104.0184 | 110.9284
| CambridgeWind2055RCP4.5 | Cambridge | Wind | RCP4.5 | 2055 | 83.7034 | 90.2674 | 97.2115 | 104.1252 | 111.0488
| CambridgeWind2060RCP4.5 | Cambridge | Wind | RCP4.5 | 2060 | 83.768 | 90.346 | 97.3037 | 104.232 | 111.1692
| CambridgeWind2065RCP4.5 | Cambridge | Wind | RCP4.5 | 2065 | 83.8327 | 90.4246 | 97.3958 | 104.3389 | 111.2895
| CambridgeWind2070RCP4.5 | Cambridge | Wind | RCP4.5 | 2070 | 83.8973 | 90.5031 | 97.488 | 104.4457 | 111.4099
| CambridgeWind2075RCP4.5 | Cambridge | Wind | RCP4.5 | 2075 | 83.9678 | 90.6043 | 97.632 | 104.622 | 111.6215
| CambridgeWind2080RCP4.5 | Cambridge | Wind | RCP4.5 | 2080 | 84.0383 | 90.7055 | 97.776 | 104.7984 | 111.8331
| CambridgeWind2085RCP4.5 | Cambridge | Wind | RCP4.5 | 2085 | 84.1087 | 90.8067 | 97.92 | 104.9747 | 112.0447
| CambridgeWind2090RCP4.5 | Cambridge | Wind | RCP4.5 | 2090 | 84.1792 | 90.9079 | 98.064 | 105.151 | 112.2563
| CambridgeWind2095RCP4.5 | Cambridge | Wind | RCP4.5 | 2095 | 84.2496 | 91.0091 | 98.208 | 105.3274 | 112.4678
| CambridgeWind2100RCP4.5 | Cambridge | Wind | RCP4.5 | 2100 | 84.3201 | 91.1102 | 98.352 | 105.5037 | 112.6794
| CambridgeWind2023RCP6.0 | Cambridge | Wind | RCP6.0 | 2023 | 83.2259 | 89.6371 | 96.384 | 103.1309 | 109.8887
| CambridgeWind2025RCP6.0 | Cambridge | Wind | RCP6.0 | 2025 | 83.2839 | 89.716 | 96.4912 | 103.261 | 110.0419
| CambridgeWind2030RCP6.0 | Cambridge | Wind | RCP6.0 | 2030 | 83.3419 | 89.7948 | 96.5984 | 103.3911 | 110.1951
| CambridgeWind2035RCP6.0 | Cambridge | Wind | RCP6.0 | 2035 | 83.4 | 89.8737 | 96.7056 | 103.5212 | 110.3484
| CambridgeWind2040RCP6.0 | Cambridge | Wind | RCP6.0 | 2040 | 83.458 | 89.9526 | 96.8128 | 103.6513 | 110.5016
| CambridgeWind2045RCP6.0 | Cambridge | Wind | RCP6.0 | 2045 | 83.516 | 90.0314 | 96.92 | 103.7814 | 110.6548
| CambridgeWind2050RCP6.0 | Cambridge | Wind | RCP6.0 | 2050 | 83.6387 | 90.1889 | 97.1194 | 104.0184 | 110.9284
| CambridgeWind2055RCP6.0 | Cambridge | Wind | RCP6.0 | 2055 | 83.7034 | 90.2674 | 97.2115 | 104.1252 | 111.0488
| CambridgeWind2060RCP6.0 | Cambridge | Wind | RCP6.0 | 2060 | 83.768 | 90.346 | 97.3037 | 104.232 | 111.1692
| CambridgeWind2065RCP6.0 | Cambridge | Wind | RCP6.0 | 2065 | 83.8327 | 90.4246 | 97.3958 | 104.3389 | 111.2895
| CambridgeWind2070RCP6.0 | Cambridge | Wind | RCP6.0 | 2070 | 83.8973 | 90.5031 | 97.488 | 104.4457 | 111.4099
| CambridgeWind2075RCP6.0 | Cambridge | Wind | RCP6.0 | 2075 | 84.003 | 90.6549 | 97.704 | 104.7102 | 111.7273
| CambridgeWind2080RCP6.0 | Cambridge | Wind | RCP6.0 | 2080 | 84.1087 | 90.8067 | 97.92 | 104.9747 | 112.0447
| CambridgeWind2085RCP6.0 | Cambridge | Wind | RCP6.0 | 2085 | 84.2144 | 90.9585 | 98.136 | 105.2392 | 112.362
| CambridgeWind2090RCP6.0 | Cambridge | Wind | RCP6.0 | 2090 | 84.6047 | 91.4674 | 98.7968 | 106.0276 | 113.2813
| CambridgeWind2095RCP6.0 | Cambridge | Wind | RCP6.0 | 2095 | 84.8893 | 91.8245 | 99.2416 | 106.5515 | 113.8833
| CambridgeWind2100RCP6.0 | Cambridge | Wind | RCP6.0 | 2100 | 85.1739 | 92.1816 | 99.6864 | 107.0753 | 114.4852
| CambridgeWind2023RCP8.5 | Cambridge | Wind | RCP8.5 | 2023 | 83.2259 | 89.6371 | 96.384 | 103.1309 | 109.8887
| CambridgeWind2025RCP8.5 | Cambridge | Wind | RCP8.5 | 2025 | 83.3419 | 89.7948 | 96.5984 | 103.3911 | 110.1951
| CambridgeWind2030RCP8.5 | Cambridge | Wind | RCP8.5 | 2030 | 83.458 | 89.9526 | 96.8128 | 103.6513 | 110.5016
| CambridgeWind2035RCP8.5 | Cambridge | Wind | RCP8.5 | 2035 | 83.574 | 90.1103 | 97.0272 | 103.9116 | 110.808
| CambridgeWind2040RCP8.5 | Cambridge | Wind | RCP8.5 | 2040 | 83.6818 | 90.2412 | 97.1808 | 104.0896 | 111.0086
| CambridgeWind2045RCP8.5 | Cambridge | Wind | RCP8.5 | 2045 | 83.7896 | 90.3722 | 97.3344 | 104.2676 | 111.2093
| CambridgeWind2050RCP8.5 | Cambridge | Wind | RCP8.5 | 2050 | 84.0383 | 90.7055 | 97.776 | 104.7984 | 111.8331
| CambridgeWind2055RCP8.5 | Cambridge | Wind | RCP8.5 | 2055 | 84.1792 | 90.9079 | 98.064 | 105.151 | 112.2563
| CambridgeWind2060RCP8.5 | Cambridge | Wind | RCP8.5 | 2060 | 84.6047 | 91.4674 | 98.7968 | 106.0276 | 113.2813
| CambridgeWind2065RCP8.5 | Cambridge | Wind | RCP8.5 | 2065 | 84.8893 | 91.8245 | 99.2416 | 106.5515 | 113.8833
| CambridgeWind2070RCP8.5 | Cambridge | Wind | RCP8.5 | 2070 | 85.4254 | 92.5209 | 100.1312 | 107.6129 | 115.1163
| CambridgeWind2075RCP8.5 | Cambridge | Wind | RCP8.5 | 2075 | 85.6768 | 92.8601 | 100.576 | 108.1505 | 115.7474
| CambridgeWind2080RCP8.5 | Cambridge | Wind | RCP8.5 | 2080 | 85.9282 | 93.1994 | 101.0208 | 108.688 | 116.3785
| CambridgeWind2085RCP8.5 | Cambridge | Wind | RCP8.5 | 2085 | 86.1728 | 93.5253 | 101.4528 | 109.2016 | 116.9804
| CambridgeWind2090RCP8.5 | Cambridge | Wind | RCP8.5 | 2090 | 86.4173 | 93.8511 | 101.8848 | 109.7152 | 117.5823
| CambridgeWind2095RCP8.5 | Cambridge | Wind | RCP8.5 | 2095 | 86.4173 | 93.8511 | 101.8848 | 109.7152 | 117.5823
| CambridgeWind2100RCP8.5 | Cambridge | Wind | RCP8.5 | 2100 | 86.4173 | 93.8511 | 101.8848 | 109.7152 | 117.5823
| CampbellfordIce Accretion2023RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3065 | 31.563
| CampbellfordIce Accretion2025RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2025 | 17.544 | 20.9091 | 25.1667 | 28.4148 | 31.6837
| CampbellfordIce Accretion2030RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2030 | 17.6049 | 20.9852 | 25.2583 | 28.5231 | 31.8045
| CampbellfordIce Accretion2035RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2035 | 17.6658 | 21.0613 | 25.35 | 28.6314 | 31.9252
| CampbellfordIce Accretion2040RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2040 | 17.7267 | 21.1373 | 25.4417 | 28.7397 | 32.046
| CampbellfordIce Accretion2045RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2045 | 17.7876 | 21.2134 | 25.5333 | 28.848 | 32.1667
| CampbellfordIce Accretion2050RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2050 | 17.8032 | 21.248 | 25.595 | 28.928 | 32.2623
| CampbellfordIce Accretion2055RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2055 | 17.758 | 21.2065 | 25.565 | 28.8997 | 32.2371
| CampbellfordIce Accretion2060RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2060 | 17.7128 | 21.165 | 25.535 | 28.8715 | 32.2119
| CampbellfordIce Accretion2065RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2065 | 17.6675 | 21.1235 | 25.505 | 28.8432 | 32.1867
| CampbellfordIce Accretion2070RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2070 | 17.6223 | 21.082 | 25.475 | 28.815 | 32.1615
| CampbellfordIce Accretion2075RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2075 | 17.6919 | 21.1927 | 25.6375 | 29.0175 | 32.403
| CampbellfordIce Accretion2080RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2080 | 17.7615 | 21.3033 | 25.8 | 29.2199 | 32.6445
| CampbellfordIce Accretion2085RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2085 | 17.8311 | 21.414 | 25.9625 | 29.4224 | 32.886
| CampbellfordIce Accretion2090RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2090 | 17.9006 | 21.5247 | 26.125 | 29.6248 | 33.1275
| CampbellfordIce Accretion2095RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2095 | 17.9702 | 21.6353 | 26.2875 | 29.8273 | 33.369
| CampbellfordIce Accretion2100RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2100 | 18.0398 | 21.746 | 26.45 | 30.0297 | 33.6105
| CampbellfordIce Accretion2023RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3065 | 31.563
| CampbellfordIce Accretion2025RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2025 | 17.544 | 20.9091 | 25.1667 | 28.4148 | 31.6837
| CampbellfordIce Accretion2030RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2030 | 17.6049 | 20.9852 | 25.2583 | 28.5231 | 31.8045
| CampbellfordIce Accretion2035RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2035 | 17.6658 | 21.0613 | 25.35 | 28.6314 | 31.9252
| CampbellfordIce Accretion2040RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2040 | 17.7267 | 21.1373 | 25.4417 | 28.7397 | 32.046
| CampbellfordIce Accretion2045RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2045 | 17.7876 | 21.2134 | 25.5333 | 28.848 | 32.1667
| CampbellfordIce Accretion2050RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2050 | 17.8032 | 21.248 | 25.595 | 28.928 | 32.2623
| CampbellfordIce Accretion2055RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2055 | 17.758 | 21.2065 | 25.565 | 28.8997 | 32.2371
| CampbellfordIce Accretion2060RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2060 | 17.7128 | 21.165 | 25.535 | 28.8715 | 32.2119
| CampbellfordIce Accretion2065RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2065 | 17.6675 | 21.1235 | 25.505 | 28.8432 | 32.1867
| CampbellfordIce Accretion2070RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2070 | 17.6223 | 21.082 | 25.475 | 28.815 | 32.1615
| CampbellfordIce Accretion2075RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2075 | 17.7267 | 21.248 | 25.7188 | 29.1187 | 32.5237
| CampbellfordIce Accretion2080RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2080 | 17.8311 | 21.414 | 25.9625 | 29.4224 | 32.886
| CampbellfordIce Accretion2085RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2085 | 17.9354 | 21.58 | 26.2063 | 29.7261 | 33.2482
| CampbellfordIce Accretion2090RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2090 | 17.7499 | 21.4486 | 26.1333 | 29.7002 | 33.264
| CampbellfordIce Accretion2095RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2095 | 17.4599 | 21.1512 | 25.8167 | 29.3706 | 32.9175
| CampbellfordIce Accretion2100RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2100 | 17.17 | 20.8537 | 25.5 | 29.041 | 32.571
| CampbellfordIce Accretion2023RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3065 | 31.563
| CampbellfordIce Accretion2025RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2025 | 17.6049 | 20.9852 | 25.2583 | 28.5231 | 31.8045
| CampbellfordIce Accretion2030RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2030 | 17.7267 | 21.1373 | 25.4417 | 28.7397 | 32.046
| CampbellfordIce Accretion2035RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2035 | 17.8485 | 21.2895 | 25.625 | 28.9562 | 32.2875
| CampbellfordIce Accretion2040RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2040 | 17.7731 | 21.2203 | 25.575 | 28.9092 | 32.2455
| CampbellfordIce Accretion2045RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2045 | 17.6977 | 21.1512 | 25.525 | 28.8621 | 32.2035
| CampbellfordIce Accretion2050RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2050 | 17.7615 | 21.3033 | 25.8 | 29.2199 | 32.6445
| CampbellfordIce Accretion2055RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2055 | 17.9006 | 21.5247 | 26.125 | 29.6248 | 33.1275
| CampbellfordIce Accretion2060RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2060 | 17.7499 | 21.4486 | 26.1333 | 29.7002 | 33.264
| CampbellfordIce Accretion2065RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2065 | 17.4599 | 21.1512 | 25.8167 | 29.3706 | 32.9175
| CampbellfordIce Accretion2070RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2070 | 16.8801 | 20.5287 | 25.1417 | 28.6455 | 32.151
| CampbellfordIce Accretion2075RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2075 | 16.5901 | 20.2036 | 24.7833 | 28.25 | 31.731
| CampbellfordIce Accretion2080RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2080 | 16.3002 | 19.8785 | 24.425 | 27.8545 | 31.311
| CampbellfordIce Accretion2085RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2085 | 15.6826 | 19.1626 | 23.5875 | 26.9222 | 30.2715
| CampbellfordIce Accretion2090RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2090 | 15.0651 | 18.4468 | 22.75 | 25.99 | 29.232
| CampbellfordIce Accretion2095RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2095 | 15.0651 | 18.4468 | 22.75 | 25.99 | 29.232
| CampbellfordIce Accretion2100RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2100 | 15.0651 | 18.4468 | 22.75 | 25.99 | 29.232
| CampbellfordWind2023RCP4.5 | Campbellford | Wind | RCP4.5 | 2023 | 74.4377 | 80.2119 | 86.301 | 92.3697 | 98.4518
| CampbellfordWind2025RCP4.5 | Campbellford | Wind | RCP4.5 | 2025 | 74.4674 | 80.2559 | 86.3612 | 92.4464 | 98.5433
| CampbellfordWind2030RCP4.5 | Campbellford | Wind | RCP4.5 | 2030 | 74.4971 | 80.2999 | 86.4214 | 92.523 | 98.6348
| CampbellfordWind2035RCP4.5 | Campbellford | Wind | RCP4.5 | 2035 | 74.5268 | 80.3439 | 86.4816 | 92.5997 | 98.7263
| CampbellfordWind2040RCP4.5 | Campbellford | Wind | RCP4.5 | 2040 | 74.5565 | 80.3879 | 86.5418 | 92.6764 | 98.8178
| CampbellfordWind2045RCP4.5 | Campbellford | Wind | RCP4.5 | 2045 | 74.5862 | 80.4319 | 86.602 | 92.7531 | 98.9093
| CampbellfordWind2050RCP4.5 | Campbellford | Wind | RCP4.5 | 2050 | 74.5922 | 80.4311 | 86.5951 | 92.7414 | 98.891
| CampbellfordWind2055RCP4.5 | Campbellford | Wind | RCP4.5 | 2055 | 74.5684 | 80.3863 | 86.528 | 92.6531 | 98.7812
| CampbellfordWind2060RCP4.5 | Campbellford | Wind | RCP4.5 | 2060 | 74.5446 | 80.3415 | 86.461 | 92.5648 | 98.6714
| CampbellfordWind2065RCP4.5 | Campbellford | Wind | RCP4.5 | 2065 | 74.5209 | 80.2967 | 86.3939 | 92.4764 | 98.5616
| CampbellfordWind2070RCP4.5 | Campbellford | Wind | RCP4.5 | 2070 | 74.4971 | 80.2519 | 86.3268 | 92.3881 | 98.4518
| CampbellfordWind2075RCP4.5 | Campbellford | Wind | RCP4.5 | 2075 | 74.4748 | 80.2266 | 86.2967 | 92.3543 | 98.4158
| CampbellfordWind2080RCP4.5 | Campbellford | Wind | RCP4.5 | 2080 | 74.4526 | 80.2013 | 86.2666 | 92.3206 | 98.3799
| CampbellfordWind2085RCP4.5 | Campbellford | Wind | RCP4.5 | 2085 | 74.4303 | 80.176 | 86.2365 | 92.2869 | 98.3439
| CampbellfordWind2090RCP4.5 | Campbellford | Wind | RCP4.5 | 2090 | 74.408 | 80.1506 | 86.2064 | 92.2531 | 98.308
| CampbellfordWind2095RCP4.5 | Campbellford | Wind | RCP4.5 | 2095 | 74.3857 | 80.1253 | 86.1763 | 92.2194 | 98.272
| CampbellfordWind2100RCP4.5 | Campbellford | Wind | RCP4.5 | 2100 | 74.3635 | 80.1 | 86.1462 | 92.1856 | 98.2361
| CampbellfordWind2023RCP6.0 | Campbellford | Wind | RCP6.0 | 2023 | 74.4377 | 80.2119 | 86.301 | 92.3697 | 98.4518
| CampbellfordWind2025RCP6.0 | Campbellford | Wind | RCP6.0 | 2025 | 74.4674 | 80.2559 | 86.3612 | 92.4464 | 98.5433
| CampbellfordWind2030RCP6.0 | Campbellford | Wind | RCP6.0 | 2030 | 74.4971 | 80.2999 | 86.4214 | 92.523 | 98.6348
| CampbellfordWind2035RCP6.0 | Campbellford | Wind | RCP6.0 | 2035 | 74.5268 | 80.3439 | 86.4816 | 92.5997 | 98.7263
| CampbellfordWind2040RCP6.0 | Campbellford | Wind | RCP6.0 | 2040 | 74.5565 | 80.3879 | 86.5418 | 92.6764 | 98.8178
| CampbellfordWind2045RCP6.0 | Campbellford | Wind | RCP6.0 | 2045 | 74.5862 | 80.4319 | 86.602 | 92.7531 | 98.9093
| CampbellfordWind2050RCP6.0 | Campbellford | Wind | RCP6.0 | 2050 | 74.5922 | 80.4311 | 86.5951 | 92.7414 | 98.891
| CampbellfordWind2055RCP6.0 | Campbellford | Wind | RCP6.0 | 2055 | 74.5684 | 80.3863 | 86.528 | 92.6531 | 98.7812
| CampbellfordWind2060RCP6.0 | Campbellford | Wind | RCP6.0 | 2060 | 74.5446 | 80.3415 | 86.461 | 92.5648 | 98.6714
| CampbellfordWind2065RCP6.0 | Campbellford | Wind | RCP6.0 | 2065 | 74.5209 | 80.2967 | 86.3939 | 92.4764 | 98.5616
| CampbellfordWind2070RCP6.0 | Campbellford | Wind | RCP6.0 | 2070 | 74.4971 | 80.2519 | 86.3268 | 92.3881 | 98.4518
| CampbellfordWind2075RCP6.0 | Campbellford | Wind | RCP6.0 | 2075 | 74.4637 | 80.2139 | 86.2817 | 92.3375 | 98.3978
| CampbellfordWind2080RCP6.0 | Campbellford | Wind | RCP6.0 | 2080 | 74.4303 | 80.176 | 86.2365 | 92.2869 | 98.3439
| CampbellfordWind2085RCP6.0 | Campbellford | Wind | RCP6.0 | 2085 | 74.3969 | 80.138 | 86.1913 | 92.2362 | 98.29
| CampbellfordWind2090RCP6.0 | Campbellford | Wind | RCP6.0 | 2090 | 74.3511 | 80.076 | 86.1061 | 92.1304 | 98.1642
| CampbellfordWind2095RCP6.0 | Campbellford | Wind | RCP6.0 | 2095 | 74.3387 | 80.052 | 86.0659 | 92.0752 | 98.0923
| CampbellfordWind2100RCP6.0 | Campbellford | Wind | RCP6.0 | 2100 | 74.3263 | 80.028 | 86.0258 | 92.02 | 98.0204
| CampbellfordWind2023RCP8.5 | Campbellford | Wind | RCP8.5 | 2023 | 74.4377 | 80.2119 | 86.301 | 92.3697 | 98.4518
| CampbellfordWind2025RCP8.5 | Campbellford | Wind | RCP8.5 | 2025 | 74.4971 | 80.2999 | 86.4214 | 92.523 | 98.6348
| CampbellfordWind2030RCP8.5 | Campbellford | Wind | RCP8.5 | 2030 | 74.5565 | 80.3879 | 86.5418 | 92.6764 | 98.8178
| CampbellfordWind2035RCP8.5 | Campbellford | Wind | RCP8.5 | 2035 | 74.6159 | 80.4759 | 86.6622 | 92.8298 | 99.0008
| CampbellfordWind2040RCP8.5 | Campbellford | Wind | RCP8.5 | 2040 | 74.5763 | 80.4012 | 86.5504 | 92.6825 | 98.8178
| CampbellfordWind2045RCP8.5 | Campbellford | Wind | RCP8.5 | 2045 | 74.5367 | 80.3266 | 86.4386 | 92.5353 | 98.6348
| CampbellfordWind2050RCP8.5 | Campbellford | Wind | RCP8.5 | 2050 | 74.4526 | 80.2013 | 86.2666 | 92.3206 | 98.3799
| CampbellfordWind2055RCP8.5 | Campbellford | Wind | RCP8.5 | 2055 | 74.408 | 80.1506 | 86.2064 | 92.2531 | 98.308
| CampbellfordWind2060RCP8.5 | Campbellford | Wind | RCP8.5 | 2060 | 74.3511 | 80.076 | 86.1061 | 92.1304 | 98.1642
| CampbellfordWind2065RCP8.5 | Campbellford | Wind | RCP8.5 | 2065 | 74.3387 | 80.052 | 86.0659 | 92.0752 | 98.0923
| CampbellfordWind2070RCP8.5 | Campbellford | Wind | RCP8.5 | 2070 | 74.2941 | 79.9853 | 85.9713 | 91.9556 | 97.9452
| CampbellfordWind2075RCP8.5 | Campbellford | Wind | RCP8.5 | 2075 | 74.262 | 79.9427 | 85.9169 | 91.8912 | 97.8701
| CampbellfordWind2080RCP8.5 | Campbellford | Wind | RCP8.5 | 2080 | 74.2298 | 79.9 | 85.8624 | 91.8268 | 97.7949
| CampbellfordWind2085RCP8.5 | Campbellford | Wind | RCP8.5 | 2085 | 74.1889 | 79.872 | 85.8495 | 91.8314 | 97.8096
| CampbellfordWind2090RCP8.5 | Campbellford | Wind | RCP8.5 | 2090 | 74.1481 | 79.844 | 85.8366 | 91.836 | 97.8243
| CampbellfordWind2095RCP8.5 | Campbellford | Wind | RCP8.5 | 2095 | 74.1481 | 79.844 | 85.8366 | 91.836 | 97.8243
| CampbellfordWind2100RCP8.5 | Campbellford | Wind | RCP8.5 | 2100 | 74.1481 | 79.844 | 85.8366 | 91.836 | 97.8243
| CanningtonIce Accretion2023RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
| CanningtonIce Accretion2025RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
| CanningtonIce Accretion2030RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
| CanningtonIce Accretion2035RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
| CanningtonIce Accretion2040RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
| CanningtonIce Accretion2045RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
| CanningtonIce Accretion2050RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
| CanningtonIce Accretion2055RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
| CanningtonIce Accretion2060RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
| CanningtonIce Accretion2065RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
| CanningtonIce Accretion2070RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
| CanningtonIce Accretion2075RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2075 | 17.2744 | 20.8814 | 25.4167 | 28.8762 | 32.34
| CanningtonIce Accretion2080RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2080 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
| CanningtonIce Accretion2085RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2085 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
| CanningtonIce Accretion2090RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2090 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
| CanningtonIce Accretion2095RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2095 | 17.2048 | 20.9091 | 25.5833 | 29.121 | 32.676
| CanningtonIce Accretion2100RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2100 | 17.1874 | 20.916 | 25.625 | 29.1822 | 32.76
| CanningtonIce Accretion2023RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
| CanningtonIce Accretion2025RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
| CanningtonIce Accretion2030RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
| CanningtonIce Accretion2035RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
| CanningtonIce Accretion2040RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
| CanningtonIce Accretion2045RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
| CanningtonIce Accretion2050RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
| CanningtonIce Accretion2055RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
| CanningtonIce Accretion2060RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
| CanningtonIce Accretion2065RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
| CanningtonIce Accretion2070RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
| CanningtonIce Accretion2075RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2075 | 17.2657 | 20.8849 | 25.4375 | 28.9068 | 32.382
| CanningtonIce Accretion2080RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2080 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
| CanningtonIce Accretion2085RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2085 | 17.2135 | 20.9056 | 25.5625 | 29.0904 | 32.634
| CanningtonIce Accretion2090RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2090 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
| CanningtonIce Accretion2095RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2095 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
| CanningtonIce Accretion2100RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2100 | 16.2654 | 19.8992 | 24.5 | 27.9957 | 31.4685
| CanningtonIce Accretion2023RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
| CanningtonIce Accretion2025RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2025 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
| CanningtonIce Accretion2030RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2030 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
| CanningtonIce Accretion2035RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2035 | 17.6919 | 21.2272 | 25.725 | 29.154 | 32.6025
| CanningtonIce Accretion2040RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2040 | 17.5585 | 21.1097 | 25.6083 | 29.041 | 32.487
| CanningtonIce Accretion2045RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2045 | 17.4251 | 20.9921 | 25.4917 | 28.928 | 32.3715
| CanningtonIce Accretion2050RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2050 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
| CanningtonIce Accretion2055RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2055 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
| CanningtonIce Accretion2060RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2060 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
| CanningtonIce Accretion2065RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2065 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
| CanningtonIce Accretion2070RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2070 | 15.9987 | 19.6226 | 24.2083 | 27.685 | 31.143
| CanningtonIce Accretion2075RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2075 | 15.7319 | 19.3459 | 23.9167 | 27.3742 | 30.8175
| CanningtonIce Accretion2080RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2080 | 15.4652 | 19.0693 | 23.625 | 27.0635 | 30.492
| CanningtonIce Accretion2085RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2085 | 14.8911 | 18.426 | 22.8875 | 26.2584 | 29.6258
| CanningtonIce Accretion2090RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2090 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
| CanningtonIce Accretion2095RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2095 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
| CanningtonIce Accretion2100RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2100 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
| CanningtonWind2023RCP4.5 | Cannington | Wind | RCP4.5 | 2023 | 73.8804 | 79.5796 | 85.5695 | 91.5594 | 97.5589
| CanningtonWind2025RCP4.5 | Cannington | Wind | RCP4.5 | 2025 | 73.9134 | 79.6231 | 85.6276 | 91.6306 | 97.6413
| CanningtonWind2030RCP4.5 | Cannington | Wind | RCP4.5 | 2030 | 73.9465 | 79.6666 | 85.6857 | 91.7019 | 97.7236
| CanningtonWind2035RCP4.5 | Cannington | Wind | RCP4.5 | 2035 | 73.9795 | 79.7101 | 85.7437 | 91.7731 | 97.806
| CanningtonWind2040RCP4.5 | Cannington | Wind | RCP4.5 | 2040 | 74.0125 | 79.7535 | 85.8018 | 91.8443 | 97.8884
| CanningtonWind2045RCP4.5 | Cannington | Wind | RCP4.5 | 2045 | 74.0456 | 79.797 | 85.8599 | 91.9156 | 97.9707
| CanningtonWind2050RCP4.5 | Cannington | Wind | RCP4.5 | 2050 | 74.1446 | 79.918 | 86.0081 | 92.0869 | 98.1655
| CanningtonWind2055RCP4.5 | Cannington | Wind | RCP4.5 | 2055 | 74.2107 | 79.9954 | 86.0982 | 92.1869 | 98.2779
| CanningtonWind2060RCP4.5 | Cannington | Wind | RCP4.5 | 2060 | 74.2768 | 80.0729 | 86.1883 | 92.287 | 98.3903
| CanningtonWind2065RCP4.5 | Cannington | Wind | RCP4.5 | 2065 | 74.3428 | 80.1504 | 86.2784 | 92.387 | 98.5027
| CanningtonWind2070RCP4.5 | Cannington | Wind | RCP4.5 | 2070 | 74.4089 | 80.2278 | 86.3685 | 92.4871 | 98.6151
| CanningtonWind2075RCP4.5 | Cannington | Wind | RCP4.5 | 2075 | 74.481 | 80.3174 | 86.479 | 92.6174 | 98.7637
| CanningtonWind2080RCP4.5 | Cannington | Wind | RCP4.5 | 2080 | 74.5532 | 80.407 | 86.5895 | 92.7478 | 98.9123
| CanningtonWind2085RCP4.5 | Cannington | Wind | RCP4.5 | 2085 | 74.6254 | 80.4966 | 86.7 | 92.8781 | 99.0609
| CanningtonWind2090RCP4.5 | Cannington | Wind | RCP4.5 | 2090 | 74.6976 | 80.5862 | 86.8105 | 93.0085 | 99.2094
| CanningtonWind2095RCP4.5 | Cannington | Wind | RCP4.5 | 2095 | 74.7697 | 80.6758 | 86.921 | 93.1389 | 99.358
| CanningtonWind2100RCP4.5 | Cannington | Wind | RCP4.5 | 2100 | 74.8419 | 80.7654 | 87.0315 | 93.2692 | 99.5066
| CanningtonWind2023RCP6.0 | Cannington | Wind | RCP6.0 | 2023 | 73.8804 | 79.5796 | 85.5695 | 91.5594 | 97.5589
| CanningtonWind2025RCP6.0 | Cannington | Wind | RCP6.0 | 2025 | 73.9134 | 79.6231 | 85.6276 | 91.6306 | 97.6413
| CanningtonWind2030RCP6.0 | Cannington | Wind | RCP6.0 | 2030 | 73.9465 | 79.6666 | 85.6857 | 91.7019 | 97.7236
| CanningtonWind2035RCP6.0 | Cannington | Wind | RCP6.0 | 2035 | 73.9795 | 79.7101 | 85.7437 | 91.7731 | 97.806
| CanningtonWind2040RCP6.0 | Cannington | Wind | RCP6.0 | 2040 | 74.0125 | 79.7535 | 85.8018 | 91.8443 | 97.8884
| CanningtonWind2045RCP6.0 | Cannington | Wind | RCP6.0 | 2045 | 74.0456 | 79.797 | 85.8599 | 91.9156 | 97.9707
| CanningtonWind2050RCP6.0 | Cannington | Wind | RCP6.0 | 2050 | 74.1446 | 79.918 | 86.0081 | 92.0869 | 98.1655
| CanningtonWind2055RCP6.0 | Cannington | Wind | RCP6.0 | 2055 | 74.2107 | 79.9954 | 86.0982 | 92.1869 | 98.2779
| CanningtonWind2060RCP6.0 | Cannington | Wind | RCP6.0 | 2060 | 74.2768 | 80.0729 | 86.1883 | 92.287 | 98.3903
| CanningtonWind2065RCP6.0 | Cannington | Wind | RCP6.0 | 2065 | 74.3428 | 80.1504 | 86.2784 | 92.387 | 98.5027
| CanningtonWind2070RCP6.0 | Cannington | Wind | RCP6.0 | 2070 | 74.4089 | 80.2278 | 86.3685 | 92.4871 | 98.6151
| CanningtonWind2075RCP6.0 | Cannington | Wind | RCP6.0 | 2075 | 74.5171 | 80.3622 | 86.5343 | 92.6826 | 98.838
| CanningtonWind2080RCP6.0 | Cannington | Wind | RCP6.0 | 2080 | 74.6254 | 80.4966 | 86.7 | 92.8781 | 99.0609
| CanningtonWind2085RCP6.0 | Cannington | Wind | RCP6.0 | 2085 | 74.7336 | 80.631 | 86.8658 | 93.0737 | 99.2837
| CanningtonWind2090RCP6.0 | Cannington | Wind | RCP6.0 | 2090 | 75.0792 | 81.0368 | 87.3488 | 93.6209 | 99.8974
| CanningtonWind2095RCP6.0 | Cannington | Wind | RCP6.0 | 2095 | 75.3165 | 81.3082 | 87.6662 | 93.9726 | 100.2883
| CanningtonWind2100RCP6.0 | Cannington | Wind | RCP6.0 | 2100 | 75.5538 | 81.5796 | 87.9835 | 94.3242 | 100.6791
| CanningtonWind2023RCP8.5 | Cannington | Wind | RCP8.5 | 2023 | 73.8804 | 79.5796 | 85.5695 | 91.5594 | 97.5589
| CanningtonWind2025RCP8.5 | Cannington | Wind | RCP8.5 | 2025 | 73.9465 | 79.6666 | 85.6857 | 91.7019 | 97.7236
| CanningtonWind2030RCP8.5 | Cannington | Wind | RCP8.5 | 2030 | 74.0125 | 79.7535 | 85.8018 | 91.8443 | 97.8884
| CanningtonWind2035RCP8.5 | Cannington | Wind | RCP8.5 | 2035 | 74.0786 | 79.8405 | 85.918 | 91.9868 | 98.0531
| CanningtonWind2040RCP8.5 | Cannington | Wind | RCP8.5 | 2040 | 74.1887 | 79.9696 | 86.0682 | 92.1536 | 98.2404
| CanningtonWind2045RCP8.5 | Cannington | Wind | RCP8.5 | 2045 | 74.2988 | 80.0987 | 86.2183 | 92.3203 | 98.4278
| CanningtonWind2050RCP8.5 | Cannington | Wind | RCP8.5 | 2050 | 74.5532 | 80.407 | 86.5895 | 92.7478 | 98.9123
| CanningtonWind2055RCP8.5 | Cannington | Wind | RCP8.5 | 2055 | 74.6976 | 80.5862 | 86.8105 | 93.0085 | 99.2094
| CanningtonWind2060RCP8.5 | Cannington | Wind | RCP8.5 | 2060 | 75.0792 | 81.0368 | 87.3488 | 93.6209 | 99.8974
| CanningtonWind2065RCP8.5 | Cannington | Wind | RCP8.5 | 2065 | 75.3165 | 81.3082 | 87.6662 | 93.9726 | 100.2883
| CanningtonWind2070RCP8.5 | Cannington | Wind | RCP8.5 | 2070 | 75.637 | 81.6876 | 88.1167 | 94.4819 | 100.8632
| CanningtonWind2075RCP8.5 | Cannington | Wind | RCP8.5 | 2075 | 75.7202 | 81.7957 | 88.2498 | 94.6395 | 101.0473
| CanningtonWind2080RCP8.5 | Cannington | Wind | RCP8.5 | 2080 | 75.8034 | 81.9037 | 88.383 | 94.7972 | 101.2314
| CanningtonWind2085RCP8.5 | Cannington | Wind | RCP8.5 | 2085 | 75.9979 | 82.1764 | 88.7655 | 95.2656 | 101.7886
| CanningtonWind2090RCP8.5 | Cannington | Wind | RCP8.5 | 2090 | 76.1924 | 82.4491 | 89.148 | 95.734 | 102.3458
| CanningtonWind2095RCP8.5 | Cannington | Wind | RCP8.5 | 2095 | 76.1924 | 82.4491 | 89.148 | 95.734 | 102.3458
| CanningtonWind2100RCP8.5 | Cannington | Wind | RCP8.5 | 2100 | 76.1924 | 82.4491 | 89.148 | 95.734 | 102.3458
| Carleton PlaceIce Accretion2023RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2023 | 18.6375 | 22.1635 | 26.622 | 30.0523 | 33.4757
| Carleton PlaceIce Accretion2025RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2025 | 18.6313 | 22.1598 | 26.6265 | 30.0625 | 33.487
| Carleton PlaceIce Accretion2030RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2030 | 18.625 | 22.156 | 26.631 | 30.0727 | 33.4984
| Carleton PlaceIce Accretion2035RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2035 | 18.6188 | 22.1523 | 26.6355 | 30.0829 | 33.5097
| Carleton PlaceIce Accretion2040RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2040 | 18.6125 | 22.1486 | 26.64 | 30.093 | 33.521
| Carleton PlaceIce Accretion2045RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2045 | 18.6062 | 22.1448 | 26.6445 | 30.1032 | 33.5324
| Carleton PlaceIce Accretion2050RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2050 | 18.6037 | 22.1635 | 26.6922 | 30.1744 | 33.6186
| Carleton PlaceIce Accretion2055RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2055 | 18.6075 | 22.1859 | 26.7354 | 30.2354 | 33.6934
| Carleton PlaceIce Accretion2060RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2060 | 18.6112 | 22.2083 | 26.7786 | 30.2964 | 33.7683
| Carleton PlaceIce Accretion2065RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2065 | 18.615 | 22.2307 | 26.8218 | 30.3575 | 33.8431
| Carleton PlaceIce Accretion2070RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2070 | 18.6188 | 22.2531 | 26.865 | 30.4185 | 33.9179
| Carleton PlaceIce Accretion2075RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2075 | 18.7033 | 22.3764 | 27.036 | 30.6219 | 34.1618
| Carleton PlaceIce Accretion2080RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2080 | 18.7878 | 22.4996 | 27.207 | 30.8253 | 34.4056
| Carleton PlaceIce Accretion2085RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2085 | 18.8724 | 22.6229 | 27.378 | 31.0287 | 34.6494
| Carleton PlaceIce Accretion2090RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2090 | 18.9569 | 22.7462 | 27.549 | 31.2321 | 34.8932
| Carleton PlaceIce Accretion2095RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2095 | 19.0415 | 22.8694 | 27.72 | 31.4355 | 35.137
| Carleton PlaceIce Accretion2100RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2100 | 19.126 | 22.9927 | 27.891 | 31.6389 | 35.3808
| Carleton PlaceIce Accretion2023RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2023 | 18.6375 | 22.1635 | 26.622 | 30.0523 | 33.4757
| Carleton PlaceIce Accretion2025RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2025 | 18.6313 | 22.1598 | 26.6265 | 30.0625 | 33.487
| Carleton PlaceIce Accretion2030RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2030 | 18.625 | 22.156 | 26.631 | 30.0727 | 33.4984
| Carleton PlaceIce Accretion2035RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2035 | 18.6188 | 22.1523 | 26.6355 | 30.0829 | 33.5097
| Carleton PlaceIce Accretion2040RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2040 | 18.6125 | 22.1486 | 26.64 | 30.093 | 33.521
| Carleton PlaceIce Accretion2045RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2045 | 18.6062 | 22.1448 | 26.6445 | 30.1032 | 33.5324
| Carleton PlaceIce Accretion2050RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2050 | 18.6037 | 22.1635 | 26.6922 | 30.1744 | 33.6186
| Carleton PlaceIce Accretion2055RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2055 | 18.6075 | 22.1859 | 26.7354 | 30.2354 | 33.6934
| Carleton PlaceIce Accretion2060RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2060 | 18.6112 | 22.2083 | 26.7786 | 30.2964 | 33.7683
| Carleton PlaceIce Accretion2065RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2065 | 18.615 | 22.2307 | 26.8218 | 30.3575 | 33.8431
| Carleton PlaceIce Accretion2070RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2070 | 18.6188 | 22.2531 | 26.865 | 30.4185 | 33.9179
| Carleton PlaceIce Accretion2075RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2075 | 18.7456 | 22.438 | 27.1215 | 30.7236 | 34.2837
| Carleton PlaceIce Accretion2080RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2080 | 18.8724 | 22.6229 | 27.378 | 31.0287 | 34.6494
| Carleton PlaceIce Accretion2085RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2085 | 18.9992 | 22.8078 | 27.6345 | 31.3338 | 35.0151
| Carleton PlaceIce Accretion2090RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2090 | 19.1135 | 23.0151 | 27.963 | 31.7304 | 35.5055
| Carleton PlaceIce Accretion2095RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2095 | 19.101 | 23.0375 | 28.035 | 31.8219 | 35.6303
| Carleton PlaceIce Accretion2100RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2100 | 19.0885 | 23.0599 | 28.107 | 31.9135 | 35.755
| Carleton PlaceIce Accretion2023RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2023 | 18.6375 | 22.1635 | 26.622 | 30.0523 | 33.4757
| Carleton PlaceIce Accretion2025RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2025 | 18.625 | 22.156 | 26.631 | 30.0727 | 33.4984
| Carleton PlaceIce Accretion2030RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2030 | 18.6125 | 22.1486 | 26.64 | 30.093 | 33.521
| Carleton PlaceIce Accretion2035RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2035 | 18.6 | 22.1411 | 26.649 | 30.1134 | 33.5437
| Carleton PlaceIce Accretion2040RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2040 | 18.6062 | 22.1784 | 26.721 | 30.2151 | 33.6685
| Carleton PlaceIce Accretion2045RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2045 | 18.6125 | 22.2158 | 26.793 | 30.3168 | 33.7932
| Carleton PlaceIce Accretion2050RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2050 | 18.7878 | 22.4996 | 27.207 | 30.8253 | 34.4056
| Carleton PlaceIce Accretion2055RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2055 | 18.9569 | 22.7462 | 27.549 | 31.2321 | 34.8932
| Carleton PlaceIce Accretion2060RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2060 | 19.1135 | 23.0151 | 27.963 | 31.7304 | 35.5055
| Carleton PlaceIce Accretion2065RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2065 | 19.101 | 23.0375 | 28.035 | 31.8219 | 35.6303
| Carleton PlaceIce Accretion2070RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2070 | 18.888 | 22.8507 | 27.882 | 31.6795 | 35.5055
| Carleton PlaceIce Accretion2075RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2075 | 18.6876 | 22.6416 | 27.657 | 31.4456 | 35.2561
| Carleton PlaceIce Accretion2080RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2080 | 18.4872 | 22.4324 | 27.432 | 31.2117 | 35.0066
| Carleton PlaceIce Accretion2085RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2085 | 17.7169 | 21.5472 | 26.3925 | 30.0676 | 33.7478
| Carleton PlaceIce Accretion2090RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2090 | 16.9466 | 20.662 | 25.353 | 28.9235 | 32.4891
| Carleton PlaceIce Accretion2095RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2095 | 16.9466 | 20.662 | 25.353 | 28.9235 | 32.4891
| Carleton PlaceIce Accretion2100RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2100 | 16.9466 | 20.662 | 25.353 | 28.9235 | 32.4891
| Carleton PlaceWind2023RCP4.5 | Carleton Place | Wind | RCP4.5 | 2023 | 74.8164 | 80.6518 | 86.8084 | 92.9402 | 99.0792
| Carleton PlaceWind2025RCP4.5 | Carleton Place | Wind | RCP4.5 | 2025 | 74.9241 | 80.7811 | 86.9646 | 93.1212 | 99.2851
| Carleton PlaceWind2030RCP4.5 | Carleton Place | Wind | RCP4.5 | 2030 | 75.0318 | 80.9104 | 87.1209 | 93.3021 | 99.491
| Carleton PlaceWind2035RCP4.5 | Carleton Place | Wind | RCP4.5 | 2035 | 75.1395 | 81.0397 | 87.2771 | 93.4831 | 99.6969
| Carleton PlaceWind2040RCP4.5 | Carleton Place | Wind | RCP4.5 | 2040 | 75.2471 | 81.169 | 87.4333 | 93.6641 | 99.9028
| Carleton PlaceWind2045RCP4.5 | Carleton Place | Wind | RCP4.5 | 2045 | 75.3548 | 81.2983 | 87.5896 | 93.8451 | 100.1086
| Carleton PlaceWind2050RCP4.5 | Carleton Place | Wind | RCP4.5 | 2050 | 75.4476 | 81.4052 | 87.7148 | 93.9874 | 100.2675
| Carleton PlaceWind2055RCP4.5 | Carleton Place | Wind | RCP4.5 | 2055 | 75.4328 | 81.3828 | 87.6839 | 93.9487 | 100.2204
| Carleton PlaceWind2060RCP4.5 | Carleton Place | Wind | RCP4.5 | 2060 | 75.4179 | 81.3605 | 87.6529 | 93.9101 | 100.1734
| Carleton PlaceWind2065RCP4.5 | Carleton Place | Wind | RCP4.5 | 2065 | 75.4031 | 81.3381 | 87.622 | 93.8714 | 100.1263
| Carleton PlaceWind2070RCP4.5 | Carleton Place | Wind | RCP4.5 | 2070 | 75.3882 | 81.3157 | 87.591 | 93.8328 | 100.0792
| Carleton PlaceWind2075RCP4.5 | Carleton Place | Wind | RCP4.5 | 2075 | 75.4155 | 81.3517 | 87.6397 | 93.8911 | 100.1462
| Carleton PlaceWind2080RCP4.5 | Carleton Place | Wind | RCP4.5 | 2080 | 75.4427 | 81.3876 | 87.6885 | 93.9494 | 100.2132
| Carleton PlaceWind2085RCP4.5 | Carleton Place | Wind | RCP4.5 | 2085 | 75.4699 | 81.4236 | 87.7372 | 94.0076 | 100.2802
| Carleton PlaceWind2090RCP4.5 | Carleton Place | Wind | RCP4.5 | 2090 | 75.4971 | 81.4596 | 87.7859 | 94.0659 | 100.3472
| Carleton PlaceWind2095RCP4.5 | Carleton Place | Wind | RCP4.5 | 2095 | 75.5244 | 81.4956 | 87.8347 | 94.1242 | 100.4142
| Carleton PlaceWind2100RCP4.5 | Carleton Place | Wind | RCP4.5 | 2100 | 75.5516 | 81.5316 | 87.8834 | 94.1825 | 100.4812
| Carleton PlaceWind2023RCP6.0 | Carleton Place | Wind | RCP6.0 | 2023 | 74.8164 | 80.6518 | 86.8084 | 92.9402 | 99.0792
| Carleton PlaceWind2025RCP6.0 | Carleton Place | Wind | RCP6.0 | 2025 | 74.9241 | 80.7811 | 86.9646 | 93.1212 | 99.2851
| Carleton PlaceWind2030RCP6.0 | Carleton Place | Wind | RCP6.0 | 2030 | 75.0318 | 80.9104 | 87.1209 | 93.3021 | 99.491
| Carleton PlaceWind2035RCP6.0 | Carleton Place | Wind | RCP6.0 | 2035 | 75.1395 | 81.0397 | 87.2771 | 93.4831 | 99.6969
| Carleton PlaceWind2040RCP6.0 | Carleton Place | Wind | RCP6.0 | 2040 | 75.2471 | 81.169 | 87.4333 | 93.6641 | 99.9028
| Carleton PlaceWind2045RCP6.0 | Carleton Place | Wind | RCP6.0 | 2045 | 75.3548 | 81.2983 | 87.5896 | 93.8451 | 100.1086
| Carleton PlaceWind2050RCP6.0 | Carleton Place | Wind | RCP6.0 | 2050 | 75.4476 | 81.4052 | 87.7148 | 93.9874 | 100.2675
| Carleton PlaceWind2055RCP6.0 | Carleton Place | Wind | RCP6.0 | 2055 | 75.4328 | 81.3828 | 87.6839 | 93.9487 | 100.2204
| Carleton PlaceWind2060RCP6.0 | Carleton Place | Wind | RCP6.0 | 2060 | 75.4179 | 81.3605 | 87.6529 | 93.9101 | 100.1734
| Carleton PlaceWind2065RCP6.0 | Carleton Place | Wind | RCP6.0 | 2065 | 75.4031 | 81.3381 | 87.622 | 93.8714 | 100.1263
| Carleton PlaceWind2070RCP6.0 | Carleton Place | Wind | RCP6.0 | 2070 | 75.3882 | 81.3157 | 87.591 | 93.8328 | 100.0792
| Carleton PlaceWind2075RCP6.0 | Carleton Place | Wind | RCP6.0 | 2075 | 75.4291 | 81.3697 | 87.6641 | 93.9202 | 100.1797
| Carleton PlaceWind2080RCP6.0 | Carleton Place | Wind | RCP6.0 | 2080 | 75.4699 | 81.4236 | 87.7372 | 94.0076 | 100.2802
| Carleton PlaceWind2085RCP6.0 | Carleton Place | Wind | RCP6.0 | 2085 | 75.5108 | 81.4776 | 87.8103 | 94.0951 | 100.3807
| Carleton PlaceWind2090RCP6.0 | Carleton Place | Wind | RCP6.0 | 2090 | 75.4971 | 81.449 | 87.7573 | 94.026 | 100.2917
| Carleton PlaceWind2095RCP6.0 | Carleton Place | Wind | RCP6.0 | 2095 | 75.4427 | 81.3663 | 87.6311 | 93.8696 | 100.1021
| Carleton PlaceWind2100RCP6.0 | Carleton Place | Wind | RCP6.0 | 2100 | 75.3882 | 81.2837 | 87.505 | 93.7132 | 99.9126
| Carleton PlaceWind2023RCP8.5 | Carleton Place | Wind | RCP8.5 | 2023 | 74.8164 | 80.6518 | 86.8084 | 92.9402 | 99.0792
| Carleton PlaceWind2025RCP8.5 | Carleton Place | Wind | RCP8.5 | 2025 | 75.0318 | 80.9104 | 87.1209 | 93.3021 | 99.491
| Carleton PlaceWind2030RCP8.5 | Carleton Place | Wind | RCP8.5 | 2030 | 75.2471 | 81.169 | 87.4333 | 93.6641 | 99.9028
| Carleton PlaceWind2035RCP8.5 | Carleton Place | Wind | RCP8.5 | 2035 | 75.4625 | 81.4276 | 87.7458 | 94.026 | 100.3145
| Carleton PlaceWind2040RCP8.5 | Carleton Place | Wind | RCP8.5 | 2040 | 75.4377 | 81.3903 | 87.6942 | 93.9616 | 100.2361
| Carleton PlaceWind2045RCP8.5 | Carleton Place | Wind | RCP8.5 | 2045 | 75.413 | 81.353 | 87.6426 | 93.8972 | 100.1577
| Carleton PlaceWind2050RCP8.5 | Carleton Place | Wind | RCP8.5 | 2050 | 75.4427 | 81.3876 | 87.6885 | 93.9494 | 100.2132
| Carleton PlaceWind2055RCP8.5 | Carleton Place | Wind | RCP8.5 | 2055 | 75.4971 | 81.4596 | 87.7859 | 94.0659 | 100.3472
| Carleton PlaceWind2060RCP8.5 | Carleton Place | Wind | RCP8.5 | 2060 | 75.4971 | 81.449 | 87.7573 | 94.026 | 100.2917
| Carleton PlaceWind2065RCP8.5 | Carleton Place | Wind | RCP8.5 | 2065 | 75.4427 | 81.3663 | 87.6311 | 93.8696 | 100.1021
| Carleton PlaceWind2070RCP8.5 | Carleton Place | Wind | RCP8.5 | 2070 | 75.4204 | 81.313 | 87.5308 | 93.7377 | 99.9354
| Carleton PlaceWind2075RCP8.5 | Carleton Place | Wind | RCP8.5 | 2075 | 75.4526 | 81.3423 | 87.5566 | 93.7622 | 99.9583
| Carleton PlaceWind2080RCP8.5 | Carleton Place | Wind | RCP8.5 | 2080 | 75.4848 | 81.3717 | 87.5824 | 93.7868 | 99.9812
| Carleton PlaceWind2085RCP8.5 | Carleton Place | Wind | RCP8.5 | 2085 | 75.5108 | 81.4116 | 87.6383 | 93.8512 | 100.0596
| Carleton PlaceWind2090RCP8.5 | Carleton Place | Wind | RCP8.5 | 2090 | 75.5368 | 81.4516 | 87.6942 | 93.9156 | 100.1381
| Carleton PlaceWind2095RCP8.5 | Carleton Place | Wind | RCP8.5 | 2095 | 75.5368 | 81.4516 | 87.6942 | 93.9156 | 100.1381
| Carleton PlaceWind2100RCP8.5 | Carleton Place | Wind | RCP8.5 | 2100 | 75.5368 | 81.4516 | 87.6942 | 93.9156 | 100.1381
| CavanIce Accretion2023RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2023 | 17.5875 | 20.999 | 25.325 | 28.6172 | 31.941
| CavanIce Accretion2025RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2025 | 17.6542 | 21.0958 | 25.4625 | 28.7867 | 32.1352
| CavanIce Accretion2030RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2030 | 17.7209 | 21.1927 | 25.6 | 28.9562 | 32.3295
| CavanIce Accretion2035RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2035 | 17.7876 | 21.2895 | 25.7375 | 29.1257 | 32.5237
| CavanIce Accretion2040RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2040 | 17.8543 | 21.3863 | 25.875 | 29.2952 | 32.718
| CavanIce Accretion2045RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2045 | 17.9209 | 21.4832 | 26.0125 | 29.4647 | 32.9123
| CavanIce Accretion2050RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2050 | 17.8867 | 21.4804 | 26.045 | 29.5212 | 32.9931
| CavanIce Accretion2055RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2055 | 17.7858 | 21.3808 | 25.94 | 29.4082 | 32.8797
| CavanIce Accretion2060RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2060 | 17.6849 | 21.2812 | 25.835 | 29.2952 | 32.7663
| CavanIce Accretion2065RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2065 | 17.584 | 21.1816 | 25.73 | 29.1822 | 32.6529
| CavanIce Accretion2070RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2070 | 17.4831 | 21.082 | 25.625 | 29.0692 | 32.5395
| CavanIce Accretion2075RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2075 | 17.5237 | 21.1615 | 25.7542 | 29.2387 | 32.7442
| CavanIce Accretion2080RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2080 | 17.5643 | 21.2411 | 25.8833 | 29.4082 | 32.949
| CavanIce Accretion2085RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2085 | 17.6049 | 21.3206 | 26.0125 | 29.5777 | 33.1538
| CavanIce Accretion2090RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2090 | 17.6455 | 21.4002 | 26.1417 | 29.7472 | 33.3585
| CavanIce Accretion2095RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2095 | 17.6861 | 21.4797 | 26.2708 | 29.9167 | 33.5632
| CavanIce Accretion2100RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2100 | 17.7267 | 21.5592 | 26.4 | 30.0862 | 33.768
| CavanIce Accretion2023RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2023 | 17.5875 | 20.999 | 25.325 | 28.6172 | 31.941
| CavanIce Accretion2025RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2025 | 17.6542 | 21.0958 | 25.4625 | 28.7867 | 32.1352
| CavanIce Accretion2030RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2030 | 17.7209 | 21.1927 | 25.6 | 28.9562 | 32.3295
| CavanIce Accretion2035RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2035 | 17.7876 | 21.2895 | 25.7375 | 29.1257 | 32.5237
| CavanIce Accretion2040RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2040 | 17.8543 | 21.3863 | 25.875 | 29.2952 | 32.718
| CavanIce Accretion2045RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2045 | 17.9209 | 21.4832 | 26.0125 | 29.4647 | 32.9123
| CavanIce Accretion2050RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2050 | 17.8867 | 21.4804 | 26.045 | 29.5212 | 32.9931
| CavanIce Accretion2055RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2055 | 17.7858 | 21.3808 | 25.94 | 29.4082 | 32.8797
| CavanIce Accretion2060RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2060 | 17.6849 | 21.2812 | 25.835 | 29.2952 | 32.7663
| CavanIce Accretion2065RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2065 | 17.584 | 21.1816 | 25.73 | 29.1822 | 32.6529
| CavanIce Accretion2070RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2070 | 17.4831 | 21.082 | 25.625 | 29.0692 | 32.5395
| CavanIce Accretion2075RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2075 | 17.544 | 21.2013 | 25.8187 | 29.3235 | 32.8466
| CavanIce Accretion2080RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2080 | 17.6049 | 21.3206 | 26.0125 | 29.5777 | 33.1538
| CavanIce Accretion2085RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2085 | 17.6658 | 21.4399 | 26.2063 | 29.832 | 33.4609
| CavanIce Accretion2090RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2090 | 17.3498 | 21.1512 | 25.95 | 29.606 | 33.243
| CavanIce Accretion2095RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2095 | 16.9728 | 20.7431 | 25.5 | 29.1257 | 32.718
| CavanIce Accretion2100RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2100 | 16.5959 | 20.335 | 25.05 | 28.6455 | 32.193
| CavanIce Accretion2023RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2023 | 17.5875 | 20.999 | 25.325 | 28.6172 | 31.941
| CavanIce Accretion2025RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2025 | 17.7209 | 21.1927 | 25.6 | 28.9562 | 32.3295
| CavanIce Accretion2030RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2030 | 17.8543 | 21.3863 | 25.875 | 29.2952 | 32.718
| CavanIce Accretion2035RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2035 | 17.9876 | 21.58 | 26.15 | 29.6342 | 33.1065
| CavanIce Accretion2040RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2040 | 17.8195 | 21.414 | 25.975 | 29.4459 | 32.9175
| CavanIce Accretion2045RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2045 | 17.6513 | 21.248 | 25.8 | 29.2576 | 32.7285
| CavanIce Accretion2050RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2050 | 17.5643 | 21.2411 | 25.8833 | 29.4082 | 32.949
| CavanIce Accretion2055RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2055 | 17.6455 | 21.4002 | 26.1417 | 29.7472 | 33.3585
| CavanIce Accretion2060RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2060 | 17.3498 | 21.1512 | 25.95 | 29.606 | 33.243
| CavanIce Accretion2065RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2065 | 16.9728 | 20.7431 | 25.5 | 29.1257 | 32.718
| CavanIce Accretion2070RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2070 | 16.2306 | 19.9338 | 24.6083 | 28.1558 | 31.6785
| CavanIce Accretion2075RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2075 | 15.8653 | 19.5327 | 24.1667 | 27.6662 | 31.164
| CavanIce Accretion2080RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2080 | 15.5 | 19.1315 | 23.725 | 27.1765 | 30.6495
| CavanIce Accretion2085RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2085 | 14.9259 | 18.4779 | 22.9625 | 26.3431 | 29.736
| CavanIce Accretion2090RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2090 | 14.3518 | 17.8242 | 22.2 | 25.5097 | 28.8225
| CavanIce Accretion2095RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2095 | 14.3518 | 17.8242 | 22.2 | 25.5097 | 28.8225
| CavanIce Accretion2100RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2100 | 14.3518 | 17.8242 | 22.2 | 25.5097 | 28.8225
| CavanWind2023RCP4.5 | Cavan | Wind | RCP4.5 | 2023 | 73.5868 | 79.1765 | 85.0425 | 90.9318 | 96.8128
| CavanWind2025RCP4.5 | Cavan | Wind | RCP4.5 | 2025 | 73.5917 | 79.1883 | 85.0623 | 90.9576 | 96.8451
| CavanWind2030RCP4.5 | Cavan | Wind | RCP4.5 | 2030 | 73.5966 | 79.2002 | 85.0822 | 90.9833 | 96.8774
| CavanWind2035RCP4.5 | Cavan | Wind | RCP4.5 | 2035 | 73.6015 | 79.2121 | 85.102 | 91.0091 | 96.9097
| CavanWind2040RCP4.5 | Cavan | Wind | RCP4.5 | 2040 | 73.6064 | 79.2239 | 85.1218 | 91.0349 | 96.942
| CavanWind2045RCP4.5 | Cavan | Wind | RCP4.5 | 2045 | 73.6113 | 79.2358 | 85.1417 | 91.0607 | 96.9743
| CavanWind2050RCP4.5 | Cavan | Wind | RCP4.5 | 2050 | 73.7189 | 79.3788 | 85.3281 | 91.2829 | 97.2333
| CavanWind2055RCP4.5 | Cavan | Wind | RCP4.5 | 2055 | 73.8217 | 79.5101 | 85.4947 | 91.4793 | 97.4601
| CavanWind2060RCP4.5 | Cavan | Wind | RCP4.5 | 2060 | 73.9245 | 79.6413 | 85.6613 | 91.6758 | 97.6868
| CavanWind2065RCP4.5 | Cavan | Wind | RCP4.5 | 2065 | 74.0272 | 79.7725 | 85.8279 | 91.8722 | 97.9136
| CavanWind2070RCP4.5 | Cavan | Wind | RCP4.5 | 2070 | 74.13 | 79.9037 | 85.9945 | 92.0687 | 98.1403
| CavanWind2075RCP4.5 | Cavan | Wind | RCP4.5 | 2075 | 74.2278 | 80.0315 | 86.1603 | 92.2673 | 98.3729
| CavanWind2080RCP4.5 | Cavan | Wind | RCP4.5 | 2080 | 74.3257 | 80.1593 | 86.326 | 92.4658 | 98.6054
| CavanWind2085RCP4.5 | Cavan | Wind | RCP4.5 | 2085 | 74.4236 | 80.2871 | 86.4917 | 92.6644 | 98.838
| CavanWind2090RCP4.5 | Cavan | Wind | RCP4.5 | 2090 | 74.5214 | 80.4149 | 86.6575 | 92.863 | 99.0706
| CavanWind2095RCP4.5 | Cavan | Wind | RCP4.5 | 2095 | 74.6193 | 80.5427 | 86.8233 | 93.0616 | 99.3031
| CavanWind2100RCP4.5 | Cavan | Wind | RCP4.5 | 2100 | 74.7171 | 80.6705 | 86.989 | 93.2601 | 99.5357
| CavanWind2023RCP6.0 | Cavan | Wind | RCP6.0 | 2023 | 73.5868 | 79.1765 | 85.0425 | 90.9318 | 96.8128
| CavanWind2025RCP6.0 | Cavan | Wind | RCP6.0 | 2025 | 73.5917 | 79.1883 | 85.0623 | 90.9576 | 96.8451
| CavanWind2030RCP6.0 | Cavan | Wind | RCP6.0 | 2030 | 73.5966 | 79.2002 | 85.0822 | 90.9833 | 96.8774
| CavanWind2035RCP6.0 | Cavan | Wind | RCP6.0 | 2035 | 73.6015 | 79.2121 | 85.102 | 91.0091 | 96.9097
| CavanWind2040RCP6.0 | Cavan | Wind | RCP6.0 | 2040 | 73.6064 | 79.2239 | 85.1218 | 91.0349 | 96.942
| CavanWind2045RCP6.0 | Cavan | Wind | RCP6.0 | 2045 | 73.6113 | 79.2358 | 85.1417 | 91.0607 | 96.9743
| CavanWind2050RCP6.0 | Cavan | Wind | RCP6.0 | 2050 | 73.7189 | 79.3788 | 85.3281 | 91.2829 | 97.2333
| CavanWind2055RCP6.0 | Cavan | Wind | RCP6.0 | 2055 | 73.8217 | 79.5101 | 85.4947 | 91.4793 | 97.4601
| CavanWind2060RCP6.0 | Cavan | Wind | RCP6.0 | 2060 | 73.9245 | 79.6413 | 85.6613 | 91.6758 | 97.6868
| CavanWind2065RCP6.0 | Cavan | Wind | RCP6.0 | 2065 | 74.0272 | 79.7725 | 85.8279 | 91.8722 | 97.9136
| CavanWind2070RCP6.0 | Cavan | Wind | RCP6.0 | 2070 | 74.13 | 79.9037 | 85.9945 | 92.0687 | 98.1403
| CavanWind2075RCP6.0 | Cavan | Wind | RCP6.0 | 2075 | 74.2768 | 80.0954 | 86.2431 | 92.3665 | 98.4892
| CavanWind2080RCP6.0 | Cavan | Wind | RCP6.0 | 2080 | 74.4236 | 80.2871 | 86.4917 | 92.6644 | 98.838
| CavanWind2085RCP6.0 | Cavan | Wind | RCP6.0 | 2085 | 74.5703 | 80.4788 | 86.7404 | 92.9623 | 99.1868
| CavanWind2090RCP6.0 | Cavan | Wind | RCP6.0 | 2090 | 75.0034 | 81.0263 | 87.4338 | 93.7816 | 100.1332
| CavanWind2095RCP6.0 | Cavan | Wind | RCP6.0 | 2095 | 75.2896 | 81.382 | 87.8787 | 94.303 | 100.7308
| CavanWind2100RCP6.0 | Cavan | Wind | RCP6.0 | 2100 | 75.5759 | 81.7377 | 88.3235 | 94.8245 | 101.3283
| CavanWind2023RCP8.5 | Cavan | Wind | RCP8.5 | 2023 | 73.5868 | 79.1765 | 85.0425 | 90.9318 | 96.8128
| CavanWind2025RCP8.5 | Cavan | Wind | RCP8.5 | 2025 | 73.5966 | 79.2002 | 85.0822 | 90.9833 | 96.8774
| CavanWind2030RCP8.5 | Cavan | Wind | RCP8.5 | 2030 | 73.6064 | 79.2239 | 85.1218 | 91.0349 | 96.942
| CavanWind2035RCP8.5 | Cavan | Wind | RCP8.5 | 2035 | 73.6162 | 79.2476 | 85.1615 | 91.0864 | 97.0066
| CavanWind2040RCP8.5 | Cavan | Wind | RCP8.5 | 2040 | 73.7875 | 79.4663 | 85.4392 | 91.4138 | 97.3845
| CavanWind2045RCP8.5 | Cavan | Wind | RCP8.5 | 2045 | 73.9587 | 79.685 | 85.7168 | 91.7413 | 97.7624
| CavanWind2050RCP8.5 | Cavan | Wind | RCP8.5 | 2050 | 74.3257 | 80.1593 | 86.326 | 92.4658 | 98.6054
| CavanWind2055RCP8.5 | Cavan | Wind | RCP8.5 | 2055 | 74.5214 | 80.4149 | 86.6575 | 92.863 | 99.0706
| CavanWind2060RCP8.5 | Cavan | Wind | RCP8.5 | 2060 | 75.0034 | 81.0263 | 87.4338 | 93.7816 | 100.1332
| CavanWind2065RCP8.5 | Cavan | Wind | RCP8.5 | 2065 | 75.2896 | 81.382 | 87.8787 | 94.303 | 100.7308
| CavanWind2070RCP8.5 | Cavan | Wind | RCP8.5 | 2070 | 75.5783 | 81.7561 | 88.3603 | 94.873 | 101.3962
| CavanWind2075RCP8.5 | Cavan | Wind | RCP8.5 | 2075 | 75.5808 | 81.7746 | 88.3972 | 94.9215 | 101.464
| CavanWind2080RCP8.5 | Cavan | Wind | RCP8.5 | 2080 | 75.5832 | 81.793 | 88.434 | 94.97 | 101.5318
| CavanWind2085RCP8.5 | Cavan | Wind | RCP8.5 | 2085 | 75.7483 | 82.0302 | 88.7655 | 95.3838 | 102.0212
| CavanWind2090RCP8.5 | Cavan | Wind | RCP8.5 | 2090 | 75.9135 | 82.2673 | 89.097 | 95.7976 | 102.5105
| CavanWind2095RCP8.5 | Cavan | Wind | RCP8.5 | 2095 | 75.9135 | 82.2673 | 89.097 | 95.7976 | 102.5105
| CavanWind2100RCP8.5 | Cavan | Wind | RCP8.5 | 2100 | 75.9135 | 82.2673 | 89.097 | 95.7976 | 102.5105
| CentraliaIce Accretion2023RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2023 | 14.379 | 17.2383 | 20.832 | 23.5876 | 26.3277
| CentraliaIce Accretion2025RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2025 | 14.3936 | 17.2673 | 20.8845 | 23.6549 | 26.4115
| CentraliaIce Accretion2030RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2030 | 14.4082 | 17.2964 | 20.937 | 23.7221 | 26.4953
| CentraliaIce Accretion2035RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2035 | 14.4228 | 17.3254 | 20.9895 | 23.7893 | 26.5791
| CentraliaIce Accretion2040RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2040 | 14.4374 | 17.3545 | 21.042 | 23.8566 | 26.6629
| CentraliaIce Accretion2045RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2045 | 14.452 | 17.3835 | 21.0945 | 23.9238 | 26.7467
| CentraliaIce Accretion2050RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2050 | 14.4082 | 17.3707 | 21.1218 | 23.9768 | 26.8304
| CentraliaIce Accretion2055RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2055 | 14.3497 | 17.3289 | 21.0966 | 23.9626 | 26.8304
| CentraliaIce Accretion2060RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2060 | 14.2913 | 17.2871 | 21.0714 | 23.9483 | 26.8304
| CentraliaIce Accretion2065RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2065 | 14.2328 | 17.2452 | 21.0462 | 23.9341 | 26.8304
| CentraliaIce Accretion2070RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2070 | 14.1744 | 17.2034 | 21.021 | 23.9198 | 26.8304
| CentraliaIce Accretion2075RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2075 | 14.1476 | 17.1918 | 21.0315 | 23.9436 | 26.8701
| CentraliaIce Accretion2080RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2080 | 14.1208 | 17.1802 | 21.042 | 23.9673 | 26.9098
| CentraliaIce Accretion2085RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2085 | 14.094 | 17.1685 | 21.0525 | 23.991 | 26.9495
| CentraliaIce Accretion2090RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2090 | 14.0672 | 17.1569 | 21.063 | 24.0148 | 26.9892
| CentraliaIce Accretion2095RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2095 | 14.0404 | 17.1453 | 21.0735 | 24.0385 | 27.0289
| CentraliaIce Accretion2100RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2100 | 14.0136 | 17.1337 | 21.084 | 24.0622 | 27.0686
| CentraliaIce Accretion2023RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2023 | 14.379 | 17.2383 | 20.832 | 23.5876 | 26.3277
| CentraliaIce Accretion2025RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2025 | 14.3936 | 17.2673 | 20.8845 | 23.6549 | 26.4115
| CentraliaIce Accretion2030RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2030 | 14.4082 | 17.2964 | 20.937 | 23.7221 | 26.4953
| CentraliaIce Accretion2035RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2035 | 14.4228 | 17.3254 | 20.9895 | 23.7893 | 26.5791
| CentraliaIce Accretion2040RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2040 | 14.4374 | 17.3545 | 21.042 | 23.8566 | 26.6629
| CentraliaIce Accretion2045RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2045 | 14.452 | 17.3835 | 21.0945 | 23.9238 | 26.7467
| CentraliaIce Accretion2050RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2050 | 14.4082 | 17.3707 | 21.1218 | 23.9768 | 26.8304
| CentraliaIce Accretion2055RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2055 | 14.3497 | 17.3289 | 21.0966 | 23.9626 | 26.8304
| CentraliaIce Accretion2060RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2060 | 14.2913 | 17.2871 | 21.0714 | 23.9483 | 26.8304
| CentraliaIce Accretion2065RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2065 | 14.2328 | 17.2452 | 21.0462 | 23.9341 | 26.8304
| CentraliaIce Accretion2070RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2070 | 14.1744 | 17.2034 | 21.021 | 23.9198 | 26.8304
| CentraliaIce Accretion2075RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2075 | 14.1342 | 17.186 | 21.0367 | 23.9554 | 26.89
| CentraliaIce Accretion2080RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2080 | 14.094 | 17.1685 | 21.0525 | 23.991 | 26.9495
| CentraliaIce Accretion2085RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2085 | 14.0538 | 17.1511 | 21.0682 | 24.0266 | 27.009
| CentraliaIce Accretion2090RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2090 | 13.8383 | 16.9594 | 20.902 | 23.8803 | 26.8745
| CentraliaIce Accretion2095RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2095 | 13.6629 | 16.7851 | 20.72 | 23.6984 | 26.6805
| CentraliaIce Accretion2100RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2100 | 13.4876 | 16.6108 | 20.538 | 23.5164 | 26.4865
| CentraliaIce Accretion2023RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2023 | 14.379 | 17.2383 | 20.832 | 23.5876 | 26.3277
| CentraliaIce Accretion2025RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2025 | 14.4082 | 17.2964 | 20.937 | 23.7221 | 26.4953
| CentraliaIce Accretion2030RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2030 | 14.4374 | 17.3545 | 21.042 | 23.8566 | 26.6629
| CentraliaIce Accretion2035RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2035 | 14.4666 | 17.4126 | 21.147 | 23.991 | 26.8304
| CentraliaIce Accretion2040RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2040 | 14.3692 | 17.3428 | 21.105 | 23.9673 | 26.8304
| CentraliaIce Accretion2045RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2045 | 14.2718 | 17.2731 | 21.063 | 23.9436 | 26.8304
| CentraliaIce Accretion2050RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2050 | 14.1208 | 17.1802 | 21.042 | 23.9673 | 26.9098
| CentraliaIce Accretion2055RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2055 | 14.0672 | 17.1569 | 21.063 | 24.0148 | 26.9892
| CentraliaIce Accretion2060RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2060 | 13.8383 | 16.9594 | 20.902 | 23.8803 | 26.8745
| CentraliaIce Accretion2065RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2065 | 13.6629 | 16.7851 | 20.72 | 23.6984 | 26.6805
| CentraliaIce Accretion2070RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2070 | 13.171 | 16.2564 | 20.139 | 23.0814 | 26.0102
| CentraliaIce Accretion2075RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2075 | 12.8544 | 15.902 | 19.74 | 22.6463 | 25.5339
| CentraliaIce Accretion2080RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2080 | 12.5378 | 15.5476 | 19.341 | 22.2113 | 25.0576
| CentraliaIce Accretion2085RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2085 | 11.8802 | 14.7719 | 18.417 | 21.179 | 23.9198
| CentraliaIce Accretion2090RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2090 | 11.2226 | 13.9963 | 17.493 | 20.1468 | 22.7821
| CentraliaIce Accretion2095RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2095 | 11.2226 | 13.9963 | 17.493 | 20.1468 | 22.7821
| CentraliaIce Accretion2100RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2100 | 11.2226 | 13.9963 | 17.493 | 20.1468 | 22.7821
| CentraliaWind2023RCP4.5 | Centralia | Wind | RCP4.5 | 2023 | 83.7896 | 90.4139 | 97.4304 | 104.4046 | 111.388
| CentraliaWind2025RCP4.5 | Centralia | Wind | RCP4.5 | 2025 | 83.878 | 90.5299 | 97.5824 | 104.5878 | 111.6033
| CentraliaWind2030RCP4.5 | Centralia | Wind | RCP4.5 | 2030 | 83.9664 | 90.646 | 97.7344 | 104.771 | 111.8185
| CentraliaWind2035RCP4.5 | Centralia | Wind | RCP4.5 | 2035 | 84.0548 | 90.762 | 97.8864 | 104.9542 | 112.0337
| CentraliaWind2040RCP4.5 | Centralia | Wind | RCP4.5 | 2040 | 84.1433 | 90.8781 | 98.0384 | 105.1373 | 112.249
| CentraliaWind2045RCP4.5 | Centralia | Wind | RCP4.5 | 2045 | 84.2317 | 90.9942 | 98.1904 | 105.3205 | 112.4642
| CentraliaWind2050RCP4.5 | Centralia | Wind | RCP4.5 | 2050 | 84.3533 | 91.1513 | 98.3942 | 105.5633 | 112.7451
| CentraliaWind2055RCP4.5 | Centralia | Wind | RCP4.5 | 2055 | 84.3864 | 91.1924 | 98.4461 | 105.6229 | 112.8108
| CentraliaWind2060RCP4.5 | Centralia | Wind | RCP4.5 | 2060 | 84.4196 | 91.2334 | 98.4979 | 105.6824 | 112.8764
| CentraliaWind2065RCP4.5 | Centralia | Wind | RCP4.5 | 2065 | 84.4527 | 91.2745 | 98.5498 | 105.742 | 112.9421
| CentraliaWind2070RCP4.5 | Centralia | Wind | RCP4.5 | 2070 | 84.4859 | 91.3156 | 98.6016 | 105.8016 | 113.0077
| CentraliaWind2075RCP4.5 | Centralia | Wind | RCP4.5 | 2075 | 84.5881 | 91.4525 | 98.7808 | 106.0173 | 113.2631
| CentraliaWind2080RCP4.5 | Centralia | Wind | RCP4.5 | 2080 | 84.6904 | 91.5894 | 98.96 | 106.233 | 113.5185
| CentraliaWind2085RCP4.5 | Centralia | Wind | RCP4.5 | 2085 | 84.7926 | 91.7263 | 99.1392 | 106.4487 | 113.7738
| CentraliaWind2090RCP4.5 | Centralia | Wind | RCP4.5 | 2090 | 84.8948 | 91.8632 | 99.3184 | 106.6644 | 114.0292
| CentraliaWind2095RCP4.5 | Centralia | Wind | RCP4.5 | 2095 | 84.9971 | 92.0001 | 99.4976 | 106.8802 | 114.2845
| CentraliaWind2100RCP4.5 | Centralia | Wind | RCP4.5 | 2100 | 85.0993 | 92.137 | 99.6768 | 107.0959 | 114.5399
| CentraliaWind2023RCP6.0 | Centralia | Wind | RCP6.0 | 2023 | 83.7896 | 90.4139 | 97.4304 | 104.4046 | 111.388
| CentraliaWind2025RCP6.0 | Centralia | Wind | RCP6.0 | 2025 | 83.878 | 90.5299 | 97.5824 | 104.5878 | 111.6033
| CentraliaWind2030RCP6.0 | Centralia | Wind | RCP6.0 | 2030 | 83.9664 | 90.646 | 97.7344 | 104.771 | 111.8185
| CentraliaWind2035RCP6.0 | Centralia | Wind | RCP6.0 | 2035 | 84.0548 | 90.762 | 97.8864 | 104.9542 | 112.0337
| CentraliaWind2040RCP6.0 | Centralia | Wind | RCP6.0 | 2040 | 84.1433 | 90.8781 | 98.0384 | 105.1373 | 112.249
| CentraliaWind2045RCP6.0 | Centralia | Wind | RCP6.0 | 2045 | 84.2317 | 90.9942 | 98.1904 | 105.3205 | 112.4642
| CentraliaWind2050RCP6.0 | Centralia | Wind | RCP6.0 | 2050 | 84.3533 | 91.1513 | 98.3942 | 105.5633 | 112.7451
| CentraliaWind2055RCP6.0 | Centralia | Wind | RCP6.0 | 2055 | 84.3864 | 91.1924 | 98.4461 | 105.6229 | 112.8108
| CentraliaWind2060RCP6.0 | Centralia | Wind | RCP6.0 | 2060 | 84.4196 | 91.2334 | 98.4979 | 105.6824 | 112.8764
| CentraliaWind2065RCP6.0 | Centralia | Wind | RCP6.0 | 2065 | 84.4527 | 91.2745 | 98.5498 | 105.742 | 112.9421
| CentraliaWind2070RCP6.0 | Centralia | Wind | RCP6.0 | 2070 | 84.4859 | 91.3156 | 98.6016 | 105.8016 | 113.0077
| CentraliaWind2075RCP6.0 | Centralia | Wind | RCP6.0 | 2075 | 84.6392 | 91.5209 | 98.8704 | 106.1252 | 113.3908
| CentraliaWind2080RCP6.0 | Centralia | Wind | RCP6.0 | 2080 | 84.7926 | 91.7263 | 99.1392 | 106.4487 | 113.7738
| CentraliaWind2085RCP6.0 | Centralia | Wind | RCP6.0 | 2085 | 84.9459 | 91.9316 | 99.408 | 106.7723 | 114.1569
| CentraliaWind2090RCP6.0 | Centralia | Wind | RCP6.0 | 2090 | 85.3977 | 92.4941 | 100.1024 | 107.5855 | 115.0908
| CentraliaWind2095RCP6.0 | Centralia | Wind | RCP6.0 | 2095 | 85.6961 | 92.8512 | 100.528 | 108.0751 | 115.6416
| CentraliaWind2100RCP6.0 | Centralia | Wind | RCP6.0 | 2100 | 85.9946 | 93.2083 | 100.9536 | 108.5648 | 116.1924
| CentraliaWind2023RCP8.5 | Centralia | Wind | RCP8.5 | 2023 | 83.7896 | 90.4139 | 97.4304 | 104.4046 | 111.388
| CentraliaWind2025RCP8.5 | Centralia | Wind | RCP8.5 | 2025 | 83.9664 | 90.646 | 97.7344 | 104.771 | 111.8185
| CentraliaWind2030RCP8.5 | Centralia | Wind | RCP8.5 | 2030 | 84.1433 | 90.8781 | 98.0384 | 105.1373 | 112.249
| CentraliaWind2035RCP8.5 | Centralia | Wind | RCP8.5 | 2035 | 84.3201 | 91.1102 | 98.3424 | 105.5037 | 112.6794
| CentraliaWind2040RCP8.5 | Centralia | Wind | RCP8.5 | 2040 | 84.3754 | 91.1787 | 98.4288 | 105.603 | 112.7889
| CentraliaWind2045RCP8.5 | Centralia | Wind | RCP8.5 | 2045 | 84.4306 | 91.2471 | 98.5152 | 105.7023 | 112.8983
| CentraliaWind2050RCP8.5 | Centralia | Wind | RCP8.5 | 2050 | 84.6904 | 91.5894 | 98.96 | 106.233 | 113.5185
| CentraliaWind2055RCP8.5 | Centralia | Wind | RCP8.5 | 2055 | 84.8948 | 91.8632 | 99.3184 | 106.6644 | 114.0292
| CentraliaWind2060RCP8.5 | Centralia | Wind | RCP8.5 | 2060 | 85.3977 | 92.4941 | 100.1024 | 107.5855 | 115.0908
| CentraliaWind2065RCP8.5 | Centralia | Wind | RCP8.5 | 2065 | 85.6961 | 92.8512 | 100.528 | 108.0751 | 115.6416
| CentraliaWind2070RCP8.5 | Centralia | Wind | RCP8.5 | 2070 | 86.2571 | 93.5535 | 101.408 | 109.1058 | 116.8272
| CentraliaWind2075RCP8.5 | Centralia | Wind | RCP8.5 | 2075 | 86.5196 | 93.8988 | 101.8624 | 109.6468 | 117.462
| CentraliaWind2080RCP8.5 | Centralia | Wind | RCP8.5 | 2080 | 86.7821 | 94.244 | 102.3168 | 110.1877 | 118.0967
| CentraliaWind2085RCP8.5 | Centralia | Wind | RCP8.5 | 2085 | 87.1302 | 94.6859 | 102.8784 | 110.8554 | 118.8683
| CentraliaWind2090RCP8.5 | Centralia | Wind | RCP8.5 | 2090 | 87.4784 | 95.1278 | 103.44 | 111.5231 | 119.6398
| CentraliaWind2095RCP8.5 | Centralia | Wind | RCP8.5 | 2095 | 87.4784 | 95.1278 | 103.44 | 111.5231 | 119.6398
| CentraliaWind2100RCP8.5 | Centralia | Wind | RCP8.5 | 2100 | 87.4784 | 95.1278 | 103.44 | 111.5231 | 119.6398
| ChapleauIce Accretion2023RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2023 | 12.1015 | 14.4486 | 17.408 | 19.671 | 21.9341
| ChapleauIce Accretion2025RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2025 | 12.133 | 14.4792 | 17.4392 | 19.7031 | 21.9662
| ChapleauIce Accretion2030RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2030 | 12.1645 | 14.5098 | 17.4703 | 19.7351 | 21.9983
| ChapleauIce Accretion2035RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2035 | 12.1961 | 14.5404 | 17.5015 | 19.7671 | 22.0305
| ChapleauIce Accretion2040RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2040 | 12.2276 | 14.5709 | 17.5327 | 19.7991 | 22.0626
| ChapleauIce Accretion2045RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2045 | 12.2592 | 14.6015 | 17.5638 | 19.8311 | 22.0947
| ChapleauIce Accretion2050RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2050 | 12.3664 | 14.7224 | 17.7038 | 19.9861 | 22.2639
| ChapleauIce Accretion2055RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2055 | 12.4421 | 14.8127 | 17.8126 | 20.109 | 22.401
| ChapleauIce Accretion2060RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2060 | 12.5179 | 14.903 | 17.9214 | 20.232 | 22.5381
| ChapleauIce Accretion2065RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2065 | 12.5936 | 14.9933 | 18.0302 | 20.3549 | 22.6752
| ChapleauIce Accretion2070RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2070 | 12.6693 | 15.0836 | 18.139 | 20.4779 | 22.8123
| ChapleauIce Accretion2075RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2075 | 12.6653 | 15.0836 | 18.1447 | 20.4875 | 22.8266
| ChapleauIce Accretion2080RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2080 | 12.6614 | 15.0836 | 18.1503 | 20.4971 | 22.8409
| ChapleauIce Accretion2085RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2085 | 12.6574 | 15.0836 | 18.156 | 20.5067 | 22.8551
| ChapleauIce Accretion2090RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2090 | 12.6535 | 15.0836 | 18.1617 | 20.5163 | 22.8694
| ChapleauIce Accretion2095RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2095 | 12.6496 | 15.0836 | 18.1673 | 20.5259 | 22.8837
| ChapleauIce Accretion2100RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2100 | 12.6456 | 15.0836 | 18.173 | 20.5355 | 22.898
| ChapleauIce Accretion2023RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2023 | 12.1015 | 14.4486 | 17.408 | 19.671 | 21.9341
| ChapleauIce Accretion2025RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2025 | 12.133 | 14.4792 | 17.4392 | 19.7031 | 21.9662
| ChapleauIce Accretion2030RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2030 | 12.1645 | 14.5098 | 17.4703 | 19.7351 | 21.9983
| ChapleauIce Accretion2035RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2035 | 12.1961 | 14.5404 | 17.5015 | 19.7671 | 22.0305
| ChapleauIce Accretion2040RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2040 | 12.2276 | 14.5709 | 17.5327 | 19.7991 | 22.0626
| ChapleauIce Accretion2045RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2045 | 12.2592 | 14.6015 | 17.5638 | 19.8311 | 22.0947
| ChapleauIce Accretion2050RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2050 | 12.3664 | 14.7224 | 17.7038 | 19.9861 | 22.2639
| ChapleauIce Accretion2055RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2055 | 12.4421 | 14.8127 | 17.8126 | 20.109 | 22.401
| ChapleauIce Accretion2060RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2060 | 12.5179 | 14.903 | 17.9214 | 20.232 | 22.5381
| ChapleauIce Accretion2065RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2065 | 12.5936 | 14.9933 | 18.0302 | 20.3549 | 22.6752
| ChapleauIce Accretion2070RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2070 | 12.6693 | 15.0836 | 18.139 | 20.4779 | 22.8123
| ChapleauIce Accretion2075RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2075 | 12.6634 | 15.0836 | 18.1475 | 20.4923 | 22.8337
| ChapleauIce Accretion2080RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2080 | 12.6574 | 15.0836 | 18.156 | 20.5067 | 22.8551
| ChapleauIce Accretion2085RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2085 | 12.6515 | 15.0836 | 18.1645 | 20.5211 | 22.8766
| ChapleauIce Accretion2090RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2090 | 12.5155 | 14.9378 | 18.0143 | 20.3626 | 22.7123
| ChapleauIce Accretion2095RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2095 | 12.3854 | 14.792 | 17.8557 | 20.1897 | 22.5267
| ChapleauIce Accretion2100RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2100 | 12.2552 | 14.6462 | 17.697 | 20.0168 | 22.3411
| ChapleauIce Accretion2023RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2023 | 12.1015 | 14.4486 | 17.408 | 19.671 | 21.9341
| ChapleauIce Accretion2025RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2025 | 12.1645 | 14.5098 | 17.4703 | 19.7351 | 21.9983
| ChapleauIce Accretion2030RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2030 | 12.2276 | 14.5709 | 17.5327 | 19.7991 | 22.0626
| ChapleauIce Accretion2035RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2035 | 12.2907 | 14.6321 | 17.595 | 19.8631 | 22.1269
| ChapleauIce Accretion2040RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2040 | 12.4169 | 14.7826 | 17.7763 | 20.068 | 22.3553
| ChapleauIce Accretion2045RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2045 | 12.5431 | 14.9331 | 17.9577 | 20.273 | 22.5838
| ChapleauIce Accretion2050RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2050 | 12.6614 | 15.0836 | 18.1503 | 20.4971 | 22.8409
| ChapleauIce Accretion2055RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2055 | 12.6535 | 15.0836 | 18.1617 | 20.5163 | 22.8694
| ChapleauIce Accretion2060RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2060 | 12.5155 | 14.9378 | 18.0143 | 20.3626 | 22.7123
| ChapleauIce Accretion2065RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2065 | 12.3854 | 14.792 | 17.8557 | 20.1897 | 22.5267
| ChapleauIce Accretion2070RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2070 | 12.2671 | 14.6744 | 17.7367 | 20.068 | 22.4053
| ChapleauIce Accretion2075RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2075 | 12.2789 | 14.7026 | 17.7763 | 20.1193 | 22.4696
| ChapleauIce Accretion2080RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2080 | 12.2907 | 14.7308 | 17.816 | 20.1705 | 22.5338
| ChapleauIce Accretion2085RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2085 | 12.2198 | 14.6673 | 17.7565 | 20.1225 | 22.491
| ChapleauIce Accretion2090RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2090 | 12.1488 | 14.6038 | 17.697 | 20.0744 | 22.4482
| ChapleauIce Accretion2095RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2095 | 12.1488 | 14.6038 | 17.697 | 20.0744 | 22.4482
| ChapleauIce Accretion2100RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2100 | 12.1488 | 14.6038 | 17.697 | 20.0744 | 22.4482
| ChapleauWind2023RCP4.5 | Chapleau | Wind | RCP4.5 | 2023 | 71.3932 | 76.9311 | 82.7708 | 88.5999 | 94.4335
| ChapleauWind2025RCP4.5 | Chapleau | Wind | RCP4.5 | 2025 | 71.4452 | 76.9883 | 82.8337 | 88.6686 | 94.5067
| ChapleauWind2030RCP4.5 | Chapleau | Wind | RCP4.5 | 2030 | 71.4971 | 77.0455 | 82.8965 | 88.7373 | 94.5799
| ChapleauWind2035RCP4.5 | Chapleau | Wind | RCP4.5 | 2035 | 71.549 | 77.1027 | 82.9594 | 88.806 | 94.6532
| ChapleauWind2040RCP4.5 | Chapleau | Wind | RCP4.5 | 2040 | 71.6009 | 77.1599 | 83.0223 | 88.8748 | 94.7264
| ChapleauWind2045RCP4.5 | Chapleau | Wind | RCP4.5 | 2045 | 71.6529 | 77.2171 | 83.0851 | 88.9435 | 94.7996
| ChapleauWind2050RCP4.5 | Chapleau | Wind | RCP4.5 | 2050 | 71.7119 | 77.2651 | 83.1185 | 88.9649 | 94.8093
| ChapleauWind2055RCP4.5 | Chapleau | Wind | RCP4.5 | 2055 | 71.719 | 77.256 | 83.089 | 88.9175 | 94.7457
| ChapleauWind2060RCP4.5 | Chapleau | Wind | RCP4.5 | 2060 | 71.726 | 77.2468 | 83.0594 | 88.8701 | 94.6822
| ChapleauWind2065RCP4.5 | Chapleau | Wind | RCP4.5 | 2065 | 71.7331 | 77.2377 | 83.0299 | 88.8227 | 94.6186
| ChapleauWind2070RCP4.5 | Chapleau | Wind | RCP4.5 | 2070 | 71.7402 | 77.2285 | 83.0004 | 88.7753 | 94.555
| ChapleauWind2075RCP4.5 | Chapleau | Wind | RCP4.5 | 2075 | 71.8417 | 77.3416 | 83.1248 | 88.9128 | 94.7046
| ChapleauWind2080RCP4.5 | Chapleau | Wind | RCP4.5 | 2080 | 71.9432 | 77.4547 | 83.2491 | 89.0503 | 94.8542
| ChapleauWind2085RCP4.5 | Chapleau | Wind | RCP4.5 | 2085 | 72.0447 | 77.5679 | 83.3735 | 89.1877 | 95.0037
| ChapleauWind2090RCP4.5 | Chapleau | Wind | RCP4.5 | 2090 | 72.1461 | 77.681 | 83.4979 | 89.3252 | 95.1533
| ChapleauWind2095RCP4.5 | Chapleau | Wind | RCP4.5 | 2095 | 72.2476 | 77.7941 | 83.6222 | 89.4626 | 95.3029
| ChapleauWind2100RCP4.5 | Chapleau | Wind | RCP4.5 | 2100 | 72.3491 | 77.9072 | 83.7466 | 89.6001 | 95.4524
| ChapleauWind2023RCP6.0 | Chapleau | Wind | RCP6.0 | 2023 | 71.3932 | 76.9311 | 82.7708 | 88.5999 | 94.4335
| ChapleauWind2025RCP6.0 | Chapleau | Wind | RCP6.0 | 2025 | 71.4452 | 76.9883 | 82.8337 | 88.6686 | 94.5067
| ChapleauWind2030RCP6.0 | Chapleau | Wind | RCP6.0 | 2030 | 71.4971 | 77.0455 | 82.8965 | 88.7373 | 94.5799
| ChapleauWind2035RCP6.0 | Chapleau | Wind | RCP6.0 | 2035 | 71.549 | 77.1027 | 82.9594 | 88.806 | 94.6532
| ChapleauWind2040RCP6.0 | Chapleau | Wind | RCP6.0 | 2040 | 71.6009 | 77.1599 | 83.0223 | 88.8748 | 94.7264
| ChapleauWind2045RCP6.0 | Chapleau | Wind | RCP6.0 | 2045 | 71.6529 | 77.2171 | 83.0851 | 88.9435 | 94.7996
| ChapleauWind2050RCP6.0 | Chapleau | Wind | RCP6.0 | 2050 | 71.7119 | 77.2651 | 83.1185 | 88.9649 | 94.8093
| ChapleauWind2055RCP6.0 | Chapleau | Wind | RCP6.0 | 2055 | 71.719 | 77.256 | 83.089 | 88.9175 | 94.7457
| ChapleauWind2060RCP6.0 | Chapleau | Wind | RCP6.0 | 2060 | 71.726 | 77.2468 | 83.0594 | 88.8701 | 94.6822
| ChapleauWind2065RCP6.0 | Chapleau | Wind | RCP6.0 | 2065 | 71.7331 | 77.2377 | 83.0299 | 88.8227 | 94.6186
| ChapleauWind2070RCP6.0 | Chapleau | Wind | RCP6.0 | 2070 | 71.7402 | 77.2285 | 83.0004 | 88.7753 | 94.555
| ChapleauWind2075RCP6.0 | Chapleau | Wind | RCP6.0 | 2075 | 71.8924 | 77.3982 | 83.1869 | 88.9815 | 94.7794
| ChapleauWind2080RCP6.0 | Chapleau | Wind | RCP6.0 | 2080 | 72.0447 | 77.5679 | 83.3735 | 89.1877 | 95.0037
| ChapleauWind2085RCP6.0 | Chapleau | Wind | RCP6.0 | 2085 | 72.1969 | 77.7375 | 83.5601 | 89.3939 | 95.2281
| ChapleauWind2090RCP6.0 | Chapleau | Wind | RCP6.0 | 2090 | 72.5639 | 78.1716 | 84.0773 | 89.9832 | 95.8887
| ChapleauWind2095RCP6.0 | Chapleau | Wind | RCP6.0 | 2095 | 72.7787 | 78.436 | 84.4081 | 90.3664 | 96.3249
| ChapleauWind2100RCP6.0 | Chapleau | Wind | RCP6.0 | 2100 | 72.9935 | 78.7003 | 84.7388 | 90.7495 | 96.7611
| ChapleauWind2023RCP8.5 | Chapleau | Wind | RCP8.5 | 2023 | 71.3932 | 76.9311 | 82.7708 | 88.5999 | 94.4335
| ChapleauWind2025RCP8.5 | Chapleau | Wind | RCP8.5 | 2025 | 71.4971 | 77.0455 | 82.8965 | 88.7373 | 94.5799
| ChapleauWind2030RCP8.5 | Chapleau | Wind | RCP8.5 | 2030 | 71.6009 | 77.1599 | 83.0223 | 88.8748 | 94.7264
| ChapleauWind2035RCP8.5 | Chapleau | Wind | RCP8.5 | 2035 | 71.7048 | 77.2743 | 83.148 | 89.0122 | 94.8729
| ChapleauWind2040RCP8.5 | Chapleau | Wind | RCP8.5 | 2040 | 71.7166 | 77.259 | 83.0988 | 88.9333 | 94.7669
| ChapleauWind2045RCP8.5 | Chapleau | Wind | RCP8.5 | 2045 | 71.7284 | 77.2438 | 83.0496 | 88.8543 | 94.661
| ChapleauWind2050RCP8.5 | Chapleau | Wind | RCP8.5 | 2050 | 71.9432 | 77.4547 | 83.2491 | 89.0503 | 94.8542
| ChapleauWind2055RCP8.5 | Chapleau | Wind | RCP8.5 | 2055 | 72.1461 | 77.681 | 83.4979 | 89.3252 | 95.1533
| ChapleauWind2060RCP8.5 | Chapleau | Wind | RCP8.5 | 2060 | 72.5639 | 78.1716 | 84.0773 | 89.9832 | 95.8887
| ChapleauWind2065RCP8.5 | Chapleau | Wind | RCP8.5 | 2065 | 72.7787 | 78.436 | 84.4081 | 90.3664 | 96.3249
| ChapleauWind2070RCP8.5 | Chapleau | Wind | RCP8.5 | 2070 | 73.1823 | 78.9164 | 84.9821 | 91.0186 | 97.0572
| ChapleauWind2075RCP8.5 | Chapleau | Wind | RCP8.5 | 2075 | 73.3711 | 79.1325 | 85.2253 | 91.2876 | 97.3532
| ChapleauWind2080RCP8.5 | Chapleau | Wind | RCP8.5 | 2080 | 73.5599 | 79.3485 | 85.4686 | 91.5567 | 97.6492
| ChapleauWind2085RCP8.5 | Chapleau | Wind | RCP8.5 | 2085 | 73.6803 | 79.5087 | 85.6777 | 91.8111 | 97.9437
| ChapleauWind2090RCP8.5 | Chapleau | Wind | RCP8.5 | 2090 | 73.8006 | 79.6688 | 85.8868 | 92.0656 | 98.2381
| ChapleauWind2095RCP8.5 | Chapleau | Wind | RCP8.5 | 2095 | 73.8006 | 79.6688 | 85.8868 | 92.0656 | 98.2381
| ChapleauWind2100RCP8.5 | Chapleau | Wind | RCP8.5 | 2100 | 73.8006 | 79.6688 | 85.8868 | 92.0656 | 98.2381
| ChathamIce Accretion2023RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2023 | 19.172 | 22.9844 | 27.804 | 31.4818 | 35.1742
| ChathamIce Accretion2025RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2025 | 19.0518 | 22.8643 | 27.6827 | 31.3552 | 35.0389
| ChathamIce Accretion2030RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2030 | 18.9317 | 22.7442 | 27.5613 | 31.2287 | 34.9037
| ChathamIce Accretion2035RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2035 | 18.8115 | 22.6241 | 27.44 | 31.1021 | 34.7684
| ChathamIce Accretion2040RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2040 | 18.6914 | 22.5041 | 27.3187 | 30.9756 | 34.6332
| ChathamIce Accretion2045RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2045 | 18.5712 | 22.384 | 27.1973 | 30.849 | 34.498
| ChathamIce Accretion2050RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2050 | 18.0107 | 21.7712 | 26.5104 | 30.1023 | 33.6853
| ChathamIce Accretion2055RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2055 | 17.5704 | 21.2785 | 25.9448 | 29.4822 | 33.008
| ChathamIce Accretion2060RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2060 | 17.1301 | 20.7859 | 25.3792 | 28.862 | 32.3306
| ChathamIce Accretion2065RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2065 | 16.6897 | 20.2932 | 24.8136 | 28.2419 | 31.6532
| ChathamIce Accretion2070RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2070 | 16.2494 | 19.8005 | 24.248 | 27.6217 | 30.9758
| ChathamIce Accretion2075RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2075 | 15.824 | 19.3086 | 23.674 | 26.9836 | 30.2702
| ChathamIce Accretion2080RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2080 | 15.3986 | 18.8167 | 23.1 | 26.3456 | 29.5646
| ChathamIce Accretion2085RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2085 | 14.9732 | 18.3247 | 22.526 | 25.7075 | 28.859
| ChathamIce Accretion2090RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2090 | 14.5478 | 17.8328 | 21.952 | 25.0694 | 28.1534
| ChathamIce Accretion2095RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2095 | 14.1224 | 17.3409 | 21.378 | 24.4314 | 27.4478
| ChathamIce Accretion2100RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2100 | 13.697 | 16.849 | 20.804 | 23.7933 | 26.7422
| ChathamIce Accretion2023RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2023 | 19.172 | 22.9844 | 27.804 | 31.4818 | 35.1742
| ChathamIce Accretion2025RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2025 | 19.0518 | 22.8643 | 27.6827 | 31.3552 | 35.0389
| ChathamIce Accretion2030RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2030 | 18.9317 | 22.7442 | 27.5613 | 31.2287 | 34.9037
| ChathamIce Accretion2035RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2035 | 18.8115 | 22.6241 | 27.44 | 31.1021 | 34.7684
| ChathamIce Accretion2040RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2040 | 18.6914 | 22.5041 | 27.3187 | 30.9756 | 34.6332
| ChathamIce Accretion2045RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2045 | 18.5712 | 22.384 | 27.1973 | 30.849 | 34.498
| ChathamIce Accretion2050RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2050 | 18.0107 | 21.7712 | 26.5104 | 30.1023 | 33.6853
| ChathamIce Accretion2055RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2055 | 17.5704 | 21.2785 | 25.9448 | 29.4822 | 33.008
| ChathamIce Accretion2060RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2060 | 17.1301 | 20.7859 | 25.3792 | 28.862 | 32.3306
| ChathamIce Accretion2065RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2065 | 16.6897 | 20.2932 | 24.8136 | 28.2419 | 31.6532
| ChathamIce Accretion2070RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2070 | 16.2494 | 19.8005 | 24.248 | 27.6217 | 30.9758
| ChathamIce Accretion2075RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2075 | 15.6113 | 19.0626 | 23.387 | 26.6646 | 29.9174
| ChathamIce Accretion2080RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2080 | 14.9732 | 18.3247 | 22.526 | 25.7075 | 28.859
| ChathamIce Accretion2085RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2085 | 14.3351 | 17.5869 | 21.665 | 24.7504 | 27.8006
| ChathamIce Accretion2090RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2090 | 12.7229 | 15.687 | 19.3947 | 22.2007 | 24.9665
| ChathamIce Accretion2095RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2095 | 11.7487 | 14.525 | 17.9853 | 20.6082 | 23.1907
| ChathamIce Accretion2100RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2100 | 10.7745 | 13.363 | 16.576 | 19.0156 | 21.415
| ChathamIce Accretion2023RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2023 | 19.172 | 22.9844 | 27.804 | 31.4818 | 35.1742
| ChathamIce Accretion2025RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2025 | 18.9317 | 22.7442 | 27.5613 | 31.2287 | 34.9037
| ChathamIce Accretion2030RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2030 | 18.6914 | 22.5041 | 27.3187 | 30.9756 | 34.6332
| ChathamIce Accretion2035RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2035 | 18.4511 | 22.2639 | 27.076 | 30.7224 | 34.3627
| ChathamIce Accretion2040RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2040 | 17.7172 | 21.4428 | 26.1333 | 29.6889 | 33.2338
| ChathamIce Accretion2045RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2045 | 16.9833 | 20.6216 | 25.1907 | 28.6553 | 32.1048
| ChathamIce Accretion2050RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2050 | 15.3986 | 18.8167 | 23.1 | 26.3456 | 29.5646
| ChathamIce Accretion2055RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2055 | 14.5478 | 17.8328 | 21.952 | 25.0694 | 28.1534
| ChathamIce Accretion2060RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2060 | 12.7229 | 15.687 | 19.3947 | 22.2007 | 24.9665
| ChathamIce Accretion2065RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2065 | 11.7487 | 14.525 | 17.9853 | 20.6082 | 23.1907
| ChathamIce Accretion2070RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2070 | 10.2354 | 12.72 | 15.8013 | 18.1297 | 20.4271
| ChathamIce Accretion2075RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2075 | 9.6964 | 12.0771 | 15.0267 | 17.2438 | 19.4393
| ChathamIce Accretion2080RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2080 | 9.1573 | 11.4341 | 14.252 | 16.3579 | 18.4514
| ChathamIce Accretion2085RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2085 | 8.417 | 10.5393 | 13.174 | 15.1397 | 17.0932
| ChathamIce Accretion2090RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2090 | 7.6766 | 9.6446 | 12.096 | 13.9216 | 15.7349
| ChathamIce Accretion2095RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2095 | 7.6766 | 9.6446 | 12.096 | 13.9216 | 15.7349
| ChathamIce Accretion2100RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2100 | 7.6766 | 9.6446 | 12.096 | 13.9216 | 15.7349
| ChathamWind2023RCP4.5 | Chatham | Wind | RCP4.5 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.368
| ChathamWind2025RCP4.5 | Chatham | Wind | RCP4.5 | 2025 | 85.0909 | 91.6975 | 98.6697 | 105.6307 | 112.5951
| ChathamWind2030RCP4.5 | Chatham | Wind | RCP4.5 | 2030 | 85.1798 | 91.8175 | 98.8297 | 105.8247 | 112.8223
| ChathamWind2035RCP4.5 | Chatham | Wind | RCP4.5 | 2035 | 85.2686 | 91.9375 | 98.9898 | 106.0187 | 113.0495
| ChathamWind2040RCP4.5 | Chatham | Wind | RCP4.5 | 2040 | 85.3575 | 92.0575 | 99.1499 | 106.2127 | 113.2766
| ChathamWind2045RCP4.5 | Chatham | Wind | RCP4.5 | 2045 | 85.4463 | 92.1775 | 99.3099 | 106.4067 | 113.5038
| ChathamWind2050RCP4.5 | Chatham | Wind | RCP4.5 | 2050 | 85.6435 | 92.4415 | 99.6582 | 106.8272 | 113.9969
| ChathamWind2055RCP4.5 | Chatham | Wind | RCP4.5 | 2055 | 85.7518 | 92.5855 | 99.8463 | 107.0537 | 114.2627
| ChathamWind2060RCP4.5 | Chatham | Wind | RCP4.5 | 2060 | 85.8601 | 92.7295 | 100.0345 | 107.2802 | 114.5286
| ChathamWind2065RCP4.5 | Chatham | Wind | RCP4.5 | 2065 | 85.9684 | 92.8735 | 100.2226 | 107.5067 | 114.7945
| ChathamWind2070RCP4.5 | Chatham | Wind | RCP4.5 | 2070 | 86.0768 | 93.0175 | 100.4108 | 107.7332 | 115.0604
| ChathamWind2075RCP4.5 | Chatham | Wind | RCP4.5 | 2075 | 86.2601 | 93.256 | 100.7179 | 108.0967 | 115.485
| ChathamWind2080RCP4.5 | Chatham | Wind | RCP4.5 | 2080 | 86.4435 | 93.4945 | 101.0249 | 108.4602 | 115.9095
| ChathamWind2085RCP4.5 | Chatham | Wind | RCP4.5 | 2085 | 86.6268 | 93.7329 | 101.332 | 108.8237 | 116.334
| ChathamWind2090RCP4.5 | Chatham | Wind | RCP4.5 | 2090 | 86.8101 | 93.9714 | 101.6391 | 109.1872 | 116.7586
| ChathamWind2095RCP4.5 | Chatham | Wind | RCP4.5 | 2095 | 86.9935 | 94.2099 | 101.9461 | 109.5507 | 117.1831
| ChathamWind2100RCP4.5 | Chatham | Wind | RCP4.5 | 2100 | 87.1768 | 94.4484 | 102.2532 | 109.9143 | 117.6076
| ChathamWind2023RCP6.0 | Chatham | Wind | RCP6.0 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.368
| ChathamWind2025RCP6.0 | Chatham | Wind | RCP6.0 | 2025 | 85.0909 | 91.6975 | 98.6697 | 105.6307 | 112.5951
| ChathamWind2030RCP6.0 | Chatham | Wind | RCP6.0 | 2030 | 85.1798 | 91.8175 | 98.8297 | 105.8247 | 112.8223
| ChathamWind2035RCP6.0 | Chatham | Wind | RCP6.0 | 2035 | 85.2686 | 91.9375 | 98.9898 | 106.0187 | 113.0495
| ChathamWind2040RCP6.0 | Chatham | Wind | RCP6.0 | 2040 | 85.3575 | 92.0575 | 99.1499 | 106.2127 | 113.2766
| ChathamWind2045RCP6.0 | Chatham | Wind | RCP6.0 | 2045 | 85.4463 | 92.1775 | 99.3099 | 106.4067 | 113.5038
| ChathamWind2050RCP6.0 | Chatham | Wind | RCP6.0 | 2050 | 85.6435 | 92.4415 | 99.6582 | 106.8272 | 113.9969
| ChathamWind2055RCP6.0 | Chatham | Wind | RCP6.0 | 2055 | 85.7518 | 92.5855 | 99.8463 | 107.0537 | 114.2627
| ChathamWind2060RCP6.0 | Chatham | Wind | RCP6.0 | 2060 | 85.8601 | 92.7295 | 100.0345 | 107.2802 | 114.5286
| ChathamWind2065RCP6.0 | Chatham | Wind | RCP6.0 | 2065 | 85.9684 | 92.8735 | 100.2226 | 107.5067 | 114.7945
| ChathamWind2070RCP6.0 | Chatham | Wind | RCP6.0 | 2070 | 86.0768 | 93.0175 | 100.4108 | 107.7332 | 115.0604
| ChathamWind2075RCP6.0 | Chatham | Wind | RCP6.0 | 2075 | 86.3518 | 93.3752 | 100.8714 | 108.2784 | 115.6972
| ChathamWind2080RCP6.0 | Chatham | Wind | RCP6.0 | 2080 | 86.6268 | 93.7329 | 101.332 | 108.8237 | 116.334
| ChathamWind2085RCP6.0 | Chatham | Wind | RCP6.0 | 2085 | 86.9018 | 94.0907 | 101.7926 | 109.369 | 116.9708
| ChathamWind2090RCP6.0 | Chatham | Wind | RCP6.0 | 2090 | 87.5661 | 94.9375 | 102.8673 | 110.6343 | 118.4381
| ChathamWind2095RCP6.0 | Chatham | Wind | RCP6.0 | 2095 | 87.9554 | 95.4266 | 103.4815 | 111.3543 | 119.2685
| ChathamWind2100RCP6.0 | Chatham | Wind | RCP6.0 | 2100 | 88.3446 | 95.9157 | 104.0956 | 112.0744 | 120.099
| ChathamWind2023RCP8.5 | Chatham | Wind | RCP8.5 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.368
| ChathamWind2025RCP8.5 | Chatham | Wind | RCP8.5 | 2025 | 85.1798 | 91.8175 | 98.8297 | 105.8247 | 112.8223
| ChathamWind2030RCP8.5 | Chatham | Wind | RCP8.5 | 2030 | 85.3575 | 92.0575 | 99.1499 | 106.2127 | 113.2766
| ChathamWind2035RCP8.5 | Chatham | Wind | RCP8.5 | 2035 | 85.5352 | 92.2975 | 99.47 | 106.6007 | 113.731
| ChathamWind2040RCP8.5 | Chatham | Wind | RCP8.5 | 2040 | 85.7157 | 92.5375 | 99.7836 | 106.9782 | 114.1741
| ChathamWind2045RCP8.5 | Chatham | Wind | RCP8.5 | 2045 | 85.8962 | 92.7775 | 100.0972 | 107.3557 | 114.6173
| ChathamWind2050RCP8.5 | Chatham | Wind | RCP8.5 | 2050 | 86.4435 | 93.4945 | 101.0249 | 108.4602 | 115.9095
| ChathamWind2055RCP8.5 | Chatham | Wind | RCP8.5 | 2055 | 86.8101 | 93.9714 | 101.6391 | 109.1872 | 116.7586
| ChathamWind2060RCP8.5 | Chatham | Wind | RCP8.5 | 2060 | 87.5661 | 94.9375 | 102.8673 | 110.6343 | 118.4381
| ChathamWind2065RCP8.5 | Chatham | Wind | RCP8.5 | 2065 | 87.9554 | 95.4266 | 103.4815 | 111.3543 | 119.2685
| ChathamWind2070RCP8.5 | Chatham | Wind | RCP8.5 | 2070 | 88.5251 | 96.1405 | 104.3733 | 112.3994 | 120.4677
| ChathamWind2075RCP8.5 | Chatham | Wind | RCP8.5 | 2075 | 88.7057 | 96.3654 | 104.6509 | 112.7245 | 120.8364
| ChathamWind2080RCP8.5 | Chatham | Wind | RCP8.5 | 2080 | 88.8862 | 96.5902 | 104.9286 | 113.0496 | 121.205
| ChathamWind2085RCP8.5 | Chatham | Wind | RCP8.5 | 2085 | 89.3855 | 97.219 | 105.7224 | 113.9828 | 122.2831
| ChathamWind2090RCP8.5 | Chatham | Wind | RCP8.5 | 2090 | 89.8847 | 97.8479 | 106.5162 | 114.9161 | 123.3612
| ChathamWind2095RCP8.5 | Chatham | Wind | RCP8.5 | 2095 | 89.8847 | 97.8479 | 106.5162 | 114.9161 | 123.3612
| ChathamWind2100RCP8.5 | Chatham | Wind | RCP8.5 | 2100 | 89.8847 | 97.8479 | 106.5162 | 114.9161 | 123.3612
| ChesleyIce Accretion2023RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2023 | 14.5982 | 17.4997 | 21.189 | 23.991 | 26.804
| ChesleyIce Accretion2025RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2025 | 14.603 | 17.5201 | 21.2205 | 24.0345 | 26.8613
| ChesleyIce Accretion2030RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2030 | 14.6079 | 17.5404 | 21.252 | 24.078 | 26.9186
| ChesleyIce Accretion2035RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2035 | 14.6128 | 17.5607 | 21.2835 | 24.1215 | 26.976
| ChesleyIce Accretion2040RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2040 | 14.6176 | 17.5811 | 21.315 | 24.165 | 27.0333
| ChesleyIce Accretion2045RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2045 | 14.6225 | 17.6014 | 21.3465 | 24.2086 | 27.0906
| ChesleyIce Accretion2050RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2050 | 14.6215 | 17.6322 | 21.4158 | 24.309 | 27.222
| ChesleyIce Accretion2055RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2055 | 14.6157 | 17.6426 | 21.4536 | 24.366 | 27.2961
| ChesleyIce Accretion2060RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2060 | 14.6098 | 17.6531 | 21.4914 | 24.4229 | 27.3702
| ChesleyIce Accretion2065RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2065 | 14.604 | 17.6636 | 21.5292 | 24.4799 | 27.4443
| ChesleyIce Accretion2070RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2070 | 14.5982 | 17.674 | 21.567 | 24.5368 | 27.5184
| ChesleyIce Accretion2075RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2075 | 14.5348 | 17.6217 | 21.532 | 24.5091 | 27.5008
| ChesleyIce Accretion2080RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2080 | 14.4715 | 17.5694 | 21.497 | 24.4814 | 27.4831
| ChesleyIce Accretion2085RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2085 | 14.4082 | 17.5172 | 21.462 | 24.4538 | 27.4655
| ChesleyIce Accretion2090RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2090 | 14.3449 | 17.4649 | 21.427 | 24.4261 | 27.4478
| ChesleyIce Accretion2095RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2095 | 14.2815 | 17.4126 | 21.392 | 24.3984 | 27.4302
| ChesleyIce Accretion2100RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2100 | 14.2182 | 17.3603 | 21.357 | 24.3707 | 27.4126
| ChesleyIce Accretion2023RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2023 | 14.5982 | 17.4997 | 21.189 | 23.991 | 26.804
| ChesleyIce Accretion2025RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2025 | 14.603 | 17.5201 | 21.2205 | 24.0345 | 26.8613
| ChesleyIce Accretion2030RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2030 | 14.6079 | 17.5404 | 21.252 | 24.078 | 26.9186
| ChesleyIce Accretion2035RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2035 | 14.6128 | 17.5607 | 21.2835 | 24.1215 | 26.976
| ChesleyIce Accretion2040RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2040 | 14.6176 | 17.5811 | 21.315 | 24.165 | 27.0333
| ChesleyIce Accretion2045RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2045 | 14.6225 | 17.6014 | 21.3465 | 24.2086 | 27.0906
| ChesleyIce Accretion2050RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2050 | 14.6215 | 17.6322 | 21.4158 | 24.309 | 27.222
| ChesleyIce Accretion2055RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2055 | 14.6157 | 17.6426 | 21.4536 | 24.366 | 27.2961
| ChesleyIce Accretion2060RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2060 | 14.6098 | 17.6531 | 21.4914 | 24.4229 | 27.3702
| ChesleyIce Accretion2065RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2065 | 14.604 | 17.6636 | 21.5292 | 24.4799 | 27.4443
| ChesleyIce Accretion2070RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2070 | 14.5982 | 17.674 | 21.567 | 24.5368 | 27.5184
| ChesleyIce Accretion2075RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2075 | 14.5032 | 17.5956 | 21.5145 | 24.4953 | 27.4919
| ChesleyIce Accretion2080RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2080 | 14.4082 | 17.5172 | 21.462 | 24.4538 | 27.4655
| ChesleyIce Accretion2085RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2085 | 14.3132 | 17.4387 | 21.4095 | 24.4122 | 27.439
| ChesleyIce Accretion2090RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2090 | 13.9747 | 17.1046 | 21.07 | 24.0701 | 27.0862
| ChesleyIce Accretion2095RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2095 | 13.7311 | 16.849 | 20.783 | 23.7695 | 26.7599
| ChesleyIce Accretion2100RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2100 | 13.4876 | 16.5934 | 20.496 | 23.469 | 26.4335
| ChesleyIce Accretion2023RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2023 | 14.5982 | 17.4997 | 21.189 | 23.991 | 26.804
| ChesleyIce Accretion2025RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2025 | 14.6079 | 17.5404 | 21.252 | 24.078 | 26.9186
| ChesleyIce Accretion2030RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2030 | 14.6176 | 17.5811 | 21.315 | 24.165 | 27.0333
| ChesleyIce Accretion2035RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2035 | 14.6274 | 17.6217 | 21.378 | 24.2521 | 27.148
| ChesleyIce Accretion2040RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2040 | 14.6176 | 17.6392 | 21.441 | 24.347 | 27.2714
| ChesleyIce Accretion2045RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2045 | 14.6079 | 17.6566 | 21.504 | 24.4419 | 27.3949
| ChesleyIce Accretion2050RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2050 | 14.4715 | 17.5694 | 21.497 | 24.4814 | 27.4831
| ChesleyIce Accretion2055RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2055 | 14.3449 | 17.4649 | 21.427 | 24.4261 | 27.4478
| ChesleyIce Accretion2060RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2060 | 13.9747 | 17.1046 | 21.07 | 24.0701 | 27.0862
| ChesleyIce Accretion2065RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2065 | 13.7311 | 16.849 | 20.783 | 23.7695 | 26.7599
| ChesleyIce Accretion2070RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2070 | 13.0882 | 16.1402 | 19.985 | 22.9074 | 25.825
| ChesleyIce Accretion2075RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2075 | 12.6888 | 15.687 | 19.474 | 22.3457 | 25.2164
| ChesleyIce Accretion2080RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2080 | 12.2893 | 15.2338 | 18.963 | 21.7841 | 24.6078
| ChesleyIce Accretion2085RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2085 | 11.8875 | 14.7894 | 18.459 | 21.2383 | 24.0257
| ChesleyIce Accretion2090RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2090 | 11.4856 | 14.3449 | 17.955 | 20.6926 | 23.4436
| ChesleyIce Accretion2095RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2095 | 11.4856 | 14.3449 | 17.955 | 20.6926 | 23.4436
| ChesleyIce Accretion2100RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2100 | 11.4856 | 14.3449 | 17.955 | 20.6926 | 23.4436
| ChesleyWind2023RCP4.5 | Chesley | Wind | RCP4.5 | 2023 | 83.5906 | 90.1639 | 97.1136 | 104.0245 | 110.9393
| ChesleyWind2025RCP4.5 | Chesley | Wind | RCP4.5 | 2025 | 83.6708 | 90.2621 | 97.2368 | 104.1684 | 111.1053
| ChesleyWind2030RCP4.5 | Chesley | Wind | RCP4.5 | 2030 | 83.7509 | 90.3603 | 97.36 | 104.3122 | 111.2713
| ChesleyWind2035RCP4.5 | Chesley | Wind | RCP4.5 | 2035 | 83.831 | 90.4585 | 97.4832 | 104.456 | 111.4373
| ChesleyWind2040RCP4.5 | Chesley | Wind | RCP4.5 | 2040 | 83.9111 | 90.5567 | 97.6064 | 104.5998 | 111.6033
| ChesleyWind2045RCP4.5 | Chesley | Wind | RCP4.5 | 2045 | 83.9913 | 90.6549 | 97.7296 | 104.7436 | 111.7692
| ChesleyWind2050RCP4.5 | Chesley | Wind | RCP4.5 | 2050 | 84.0847 | 90.7656 | 97.8624 | 104.8956 | 111.9418
| ChesleyWind2055RCP4.5 | Chesley | Wind | RCP4.5 | 2055 | 84.0979 | 90.7781 | 97.872 | 104.9038 | 111.9484
| ChesleyWind2060RCP4.5 | Chesley | Wind | RCP4.5 | 2060 | 84.1112 | 90.7906 | 97.8816 | 104.912 | 111.9549
| ChesleyWind2065RCP4.5 | Chesley | Wind | RCP4.5 | 2065 | 84.1245 | 90.8031 | 97.8912 | 104.9203 | 111.9615
| ChesleyWind2070RCP4.5 | Chesley | Wind | RCP4.5 | 2070 | 84.1377 | 90.8156 | 97.9008 | 104.9285 | 111.9681
| ChesleyWind2075RCP4.5 | Chesley | Wind | RCP4.5 | 2075 | 84.2192 | 90.9213 | 98.0368 | 105.0911 | 112.1559
| ChesleyWind2080RCP4.5 | Chesley | Wind | RCP4.5 | 2080 | 84.3008 | 91.0269 | 98.1728 | 105.2538 | 112.3438
| ChesleyWind2085RCP4.5 | Chesley | Wind | RCP4.5 | 2085 | 84.3823 | 91.1326 | 98.3088 | 105.4164 | 112.5317
| ChesleyWind2090RCP4.5 | Chesley | Wind | RCP4.5 | 2090 | 84.4638 | 91.2382 | 98.4448 | 105.579 | 112.7196
| ChesleyWind2095RCP4.5 | Chesley | Wind | RCP4.5 | 2095 | 84.5453 | 91.3439 | 98.5808 | 105.7417 | 112.9074
| ChesleyWind2100RCP4.5 | Chesley | Wind | RCP4.5 | 2100 | 84.6268 | 91.4495 | 98.7168 | 105.9043 | 113.0953
| ChesleyWind2023RCP6.0 | Chesley | Wind | RCP6.0 | 2023 | 83.5906 | 90.1639 | 97.1136 | 104.0245 | 110.9393
| ChesleyWind2025RCP6.0 | Chesley | Wind | RCP6.0 | 2025 | 83.6708 | 90.2621 | 97.2368 | 104.1684 | 111.1053
| ChesleyWind2030RCP6.0 | Chesley | Wind | RCP6.0 | 2030 | 83.7509 | 90.3603 | 97.36 | 104.3122 | 111.2713
| ChesleyWind2035RCP6.0 | Chesley | Wind | RCP6.0 | 2035 | 83.831 | 90.4585 | 97.4832 | 104.456 | 111.4373
| ChesleyWind2040RCP6.0 | Chesley | Wind | RCP6.0 | 2040 | 83.9111 | 90.5567 | 97.6064 | 104.5998 | 111.6033
| ChesleyWind2045RCP6.0 | Chesley | Wind | RCP6.0 | 2045 | 83.9913 | 90.6549 | 97.7296 | 104.7436 | 111.7692
| ChesleyWind2050RCP6.0 | Chesley | Wind | RCP6.0 | 2050 | 84.0847 | 90.7656 | 97.8624 | 104.8956 | 111.9418
| ChesleyWind2055RCP6.0 | Chesley | Wind | RCP6.0 | 2055 | 84.0979 | 90.7781 | 97.872 | 104.9038 | 111.9484
| ChesleyWind2060RCP6.0 | Chesley | Wind | RCP6.0 | 2060 | 84.1112 | 90.7906 | 97.8816 | 104.912 | 111.9549
| ChesleyWind2065RCP6.0 | Chesley | Wind | RCP6.0 | 2065 | 84.1245 | 90.8031 | 97.8912 | 104.9203 | 111.9615
| ChesleyWind2070RCP6.0 | Chesley | Wind | RCP6.0 | 2070 | 84.1377 | 90.8156 | 97.9008 | 104.9285 | 111.9681
| ChesleyWind2075RCP6.0 | Chesley | Wind | RCP6.0 | 2075 | 84.26 | 90.9741 | 98.1048 | 105.1724 | 112.2499
| ChesleyWind2080RCP6.0 | Chesley | Wind | RCP6.0 | 2080 | 84.3823 | 91.1326 | 98.3088 | 105.4164 | 112.5317
| ChesleyWind2085RCP6.0 | Chesley | Wind | RCP6.0 | 2085 | 84.5045 | 91.291 | 98.5128 | 105.6604 | 112.8135
| ChesleyWind2090RCP6.0 | Chesley | Wind | RCP6.0 | 2090 | 85.0302 | 91.9554 | 99.3472 | 106.6439 | 113.9489
| ChesleyWind2095RCP6.0 | Chesley | Wind | RCP6.0 | 2095 | 85.4336 | 92.4613 | 99.9776 | 107.3835 | 114.8026
| ChesleyWind2100RCP6.0 | Chesley | Wind | RCP6.0 | 2100 | 85.8371 | 92.9673 | 100.608 | 108.1231 | 115.6562
| ChesleyWind2023RCP8.5 | Chesley | Wind | RCP8.5 | 2023 | 83.5906 | 90.1639 | 97.1136 | 104.0245 | 110.9393
| ChesleyWind2025RCP8.5 | Chesley | Wind | RCP8.5 | 2025 | 83.7509 | 90.3603 | 97.36 | 104.3122 | 111.2713
| ChesleyWind2030RCP8.5 | Chesley | Wind | RCP8.5 | 2030 | 83.9111 | 90.5567 | 97.6064 | 104.5998 | 111.6033
| ChesleyWind2035RCP8.5 | Chesley | Wind | RCP8.5 | 2035 | 84.0714 | 90.7531 | 97.8528 | 104.8874 | 111.9352
| ChesleyWind2040RCP8.5 | Chesley | Wind | RCP8.5 | 2040 | 84.0935 | 90.774 | 97.8688 | 104.9011 | 111.9462
| ChesleyWind2045RCP8.5 | Chesley | Wind | RCP8.5 | 2045 | 84.1156 | 90.7948 | 97.8848 | 104.9148 | 111.9571
| ChesleyWind2050RCP8.5 | Chesley | Wind | RCP8.5 | 2050 | 84.3008 | 91.0269 | 98.1728 | 105.2538 | 112.3438
| ChesleyWind2055RCP8.5 | Chesley | Wind | RCP8.5 | 2055 | 84.4638 | 91.2382 | 98.4448 | 105.579 | 112.7196
| ChesleyWind2060RCP8.5 | Chesley | Wind | RCP8.5 | 2060 | 85.0302 | 91.9554 | 99.3472 | 106.6439 | 113.9489
| ChesleyWind2065RCP8.5 | Chesley | Wind | RCP8.5 | 2065 | 85.4336 | 92.4613 | 99.9776 | 107.3835 | 114.8026
| ChesleyWind2070RCP8.5 | Chesley | Wind | RCP8.5 | 2070 | 86.0471 | 93.2232 | 100.9216 | 108.486 | 116.0684
| ChesleyWind2075RCP8.5 | Chesley | Wind | RCP8.5 | 2075 | 86.2571 | 93.4791 | 101.2352 | 108.849 | 116.4806
| ChesleyWind2080RCP8.5 | Chesley | Wind | RCP8.5 | 2080 | 86.4671 | 93.7351 | 101.5488 | 109.2119 | 116.8929
| ChesleyWind2085RCP8.5 | Chesley | Wind | RCP8.5 | 2085 | 86.4878 | 93.744 | 101.5488 | 109.1965 | 116.871
| ChesleyWind2090RCP8.5 | Chesley | Wind | RCP8.5 | 2090 | 86.5085 | 93.7529 | 101.5488 | 109.1811 | 116.8491
| ChesleyWind2095RCP8.5 | Chesley | Wind | RCP8.5 | 2095 | 86.5085 | 93.7529 | 101.5488 | 109.1811 | 116.8491
| ChesleyWind2100RCP8.5 | Chesley | Wind | RCP8.5 | 2100 | 86.5085 | 93.7529 | 101.5488 | 109.1811 | 116.8491
| ClintonIce Accretion2023RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2023 | 14.5105 | 17.4126 | 21.084 | 23.8961 | 26.6981
| ClintonIce Accretion2025RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2025 | 14.603 | 17.5346 | 21.2415 | 24.078 | 26.9054
| ClintonIce Accretion2030RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2030 | 14.6956 | 17.6566 | 21.399 | 24.26 | 27.1127
| ClintonIce Accretion2035RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2035 | 14.7881 | 17.7786 | 21.5565 | 24.4419 | 27.3199
| ClintonIce Accretion2040RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2040 | 14.8807 | 17.9006 | 21.714 | 24.6238 | 27.5272
| ClintonIce Accretion2045RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2045 | 14.9732 | 18.0226 | 21.8715 | 24.8058 | 27.7345
| ClintonIce Accretion2050RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2050 | 15.0716 | 18.1725 | 22.0878 | 25.0684 | 28.0423
| ClintonIce Accretion2055RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2055 | 15.0775 | 18.2004 | 22.1466 | 25.1491 | 28.1429
| ClintonIce Accretion2060RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2060 | 15.0833 | 18.2283 | 22.2054 | 25.2297 | 28.2434
| ClintonIce Accretion2065RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2065 | 15.0891 | 18.2562 | 22.2642 | 25.3104 | 28.344
| ClintonIce Accretion2070RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2070 | 15.095 | 18.2841 | 22.323 | 25.3911 | 28.4445
| ClintonIce Accretion2075RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2075 | 14.9927 | 18.1795 | 22.211 | 25.2764 | 28.3254
| ClintonIce Accretion2080RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2080 | 14.8904 | 18.0749 | 22.099 | 25.1617 | 28.2064
| ClintonIce Accretion2085RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2085 | 14.7881 | 17.9703 | 21.987 | 25.047 | 28.0873
| ClintonIce Accretion2090RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2090 | 14.6858 | 17.8657 | 21.875 | 24.9323 | 27.9682
| ClintonIce Accretion2095RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2095 | 14.5835 | 17.7612 | 21.763 | 24.8176 | 27.8492
| ClintonIce Accretion2100RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2100 | 14.4813 | 17.6566 | 21.651 | 24.7029 | 27.7301
| ClintonIce Accretion2023RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2023 | 14.5105 | 17.4126 | 21.084 | 23.8961 | 26.6981
| ClintonIce Accretion2025RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2025 | 14.603 | 17.5346 | 21.2415 | 24.078 | 26.9054
| ClintonIce Accretion2030RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2030 | 14.6956 | 17.6566 | 21.399 | 24.26 | 27.1127
| ClintonIce Accretion2035RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2035 | 14.7881 | 17.7786 | 21.5565 | 24.4419 | 27.3199
| ClintonIce Accretion2040RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2040 | 14.8807 | 17.9006 | 21.714 | 24.6238 | 27.5272
| ClintonIce Accretion2045RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2045 | 14.9732 | 18.0226 | 21.8715 | 24.8058 | 27.7345
| ClintonIce Accretion2050RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2050 | 15.0716 | 18.1725 | 22.0878 | 25.0684 | 28.0423
| ClintonIce Accretion2055RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2055 | 15.0775 | 18.2004 | 22.1466 | 25.1491 | 28.1429
| ClintonIce Accretion2060RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2060 | 15.0833 | 18.2283 | 22.2054 | 25.2297 | 28.2434
| ClintonIce Accretion2065RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2065 | 15.0891 | 18.2562 | 22.2642 | 25.3104 | 28.344
| ClintonIce Accretion2070RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2070 | 15.095 | 18.2841 | 22.323 | 25.3911 | 28.4445
| ClintonIce Accretion2075RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2075 | 14.9416 | 18.1272 | 22.155 | 25.2191 | 28.2659
| ClintonIce Accretion2080RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2080 | 14.7881 | 17.9703 | 21.987 | 25.047 | 28.0873
| ClintonIce Accretion2085RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2085 | 14.6347 | 17.8135 | 21.819 | 24.875 | 27.9087
| ClintonIce Accretion2090RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2090 | 14.1452 | 17.2847 | 21.231 | 24.2441 | 27.2273
| ClintonIce Accretion2095RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2095 | 13.8091 | 16.9129 | 20.811 | 23.7854 | 26.7246
| ClintonIce Accretion2100RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2100 | 13.473 | 16.5411 | 20.391 | 23.3266 | 26.2219
| ClintonIce Accretion2023RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2023 | 14.5105 | 17.4126 | 21.084 | 23.8961 | 26.6981
| ClintonIce Accretion2025RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2025 | 14.6956 | 17.6566 | 21.399 | 24.26 | 27.1127
| ClintonIce Accretion2030RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2030 | 14.8807 | 17.9006 | 21.714 | 24.6238 | 27.5272
| ClintonIce Accretion2035RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2035 | 15.0658 | 18.1446 | 22.029 | 24.9877 | 27.9418
| ClintonIce Accretion2040RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2040 | 15.0755 | 18.1911 | 22.127 | 25.1222 | 28.1093
| ClintonIce Accretion2045RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2045 | 15.0852 | 18.2376 | 22.225 | 25.2566 | 28.2769
| ClintonIce Accretion2050RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2050 | 14.8904 | 18.0749 | 22.099 | 25.1617 | 28.2064
| ClintonIce Accretion2055RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2055 | 14.6858 | 17.8657 | 21.875 | 24.9323 | 27.9682
| ClintonIce Accretion2060RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2060 | 14.1452 | 17.2847 | 21.231 | 24.2441 | 27.2273
| ClintonIce Accretion2065RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2065 | 13.8091 | 16.9129 | 20.811 | 23.7854 | 26.7246
| ClintonIce Accretion2070RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2070 | 13.02 | 16.0298 | 19.81 | 22.678 | 25.5251
| ClintonIce Accretion2075RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2075 | 12.567 | 15.5185 | 19.229 | 22.0293 | 24.8283
| ClintonIce Accretion2080RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2080 | 12.114 | 15.0072 | 18.648 | 21.3807 | 24.1315
| ClintonIce Accretion2085RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2085 | 11.5149 | 14.31 | 17.8185 | 20.4671 | 23.1128
| ClintonIce Accretion2090RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2090 | 10.9157 | 13.6128 | 16.989 | 19.5535 | 22.0941
| ClintonIce Accretion2095RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2095 | 10.9157 | 13.6128 | 16.989 | 19.5535 | 22.0941
| ClintonIce Accretion2100RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2100 | 10.9157 | 13.6128 | 16.989 | 19.5535 | 22.0941
| ClintonWind2023RCP4.5 | Clinton | Wind | RCP4.5 | 2023 | 86.1344 | 92.8894 | 100.0296 | 107.1482 | 114.2595
| ClintonWind2025RCP4.5 | Clinton | Wind | RCP4.5 | 2025 | 86.2014 | 92.9754 | 100.1402 | 107.2788 | 114.4137
| ClintonWind2030RCP4.5 | Clinton | Wind | RCP4.5 | 2030 | 86.2684 | 93.0613 | 100.2507 | 107.4095 | 114.5679
| ClintonWind2035RCP4.5 | Clinton | Wind | RCP4.5 | 2035 | 86.3353 | 93.1472 | 100.3612 | 107.5401 | 114.7222
| ClintonWind2040RCP4.5 | Clinton | Wind | RCP4.5 | 2040 | 86.4023 | 93.2332 | 100.4718 | 107.6708 | 114.8764
| ClintonWind2045RCP4.5 | Clinton | Wind | RCP4.5 | 2045 | 86.4693 | 93.3191 | 100.5823 | 107.8014 | 115.0307
| ClintonWind2050RCP4.5 | Clinton | Wind | RCP4.5 | 2050 | 86.5567 | 93.4271 | 100.7167 | 107.9575 | 115.212
| ClintonWind2055RCP4.5 | Clinton | Wind | RCP4.5 | 2055 | 86.5773 | 93.4492 | 100.7404 | 107.9829 | 115.2391
| ClintonWind2060RCP4.5 | Clinton | Wind | RCP4.5 | 2060 | 86.5978 | 93.4713 | 100.7642 | 108.0083 | 115.2662
| ClintonWind2065RCP4.5 | Clinton | Wind | RCP4.5 | 2065 | 86.6183 | 93.4934 | 100.7879 | 108.0338 | 115.2933
| ClintonWind2070RCP4.5 | Clinton | Wind | RCP4.5 | 2070 | 86.6388 | 93.5155 | 100.8117 | 108.0592 | 115.3203
| ClintonWind2075RCP4.5 | Clinton | Wind | RCP4.5 | 2075 | 86.7542 | 93.6674 | 101.0097 | 108.2958 | 115.5969
| ClintonWind2080RCP4.5 | Clinton | Wind | RCP4.5 | 2080 | 86.8696 | 93.8193 | 101.2077 | 108.5323 | 115.8734
| ClintonWind2085RCP4.5 | Clinton | Wind | RCP4.5 | 2085 | 86.985 | 93.9712 | 101.4057 | 108.7689 | 116.1499
| ClintonWind2090RCP4.5 | Clinton | Wind | RCP4.5 | 2090 | 87.1004 | 94.1232 | 101.6037 | 109.0055 | 116.4264
| ClintonWind2095RCP4.5 | Clinton | Wind | RCP4.5 | 2095 | 87.2158 | 94.2751 | 101.8017 | 109.2421 | 116.7029
| ClintonWind2100RCP4.5 | Clinton | Wind | RCP4.5 | 2100 | 87.3312 | 94.427 | 101.9997 | 109.4787 | 116.9794
| ClintonWind2023RCP6.0 | Clinton | Wind | RCP6.0 | 2023 | 86.1344 | 92.8894 | 100.0296 | 107.1482 | 114.2595
| ClintonWind2025RCP6.0 | Clinton | Wind | RCP6.0 | 2025 | 86.2014 | 92.9754 | 100.1402 | 107.2788 | 114.4137
| ClintonWind2030RCP6.0 | Clinton | Wind | RCP6.0 | 2030 | 86.2684 | 93.0613 | 100.2507 | 107.4095 | 114.5679
| ClintonWind2035RCP6.0 | Clinton | Wind | RCP6.0 | 2035 | 86.3353 | 93.1472 | 100.3612 | 107.5401 | 114.7222
| ClintonWind2040RCP6.0 | Clinton | Wind | RCP6.0 | 2040 | 86.4023 | 93.2332 | 100.4718 | 107.6708 | 114.8764
| ClintonWind2045RCP6.0 | Clinton | Wind | RCP6.0 | 2045 | 86.4693 | 93.3191 | 100.5823 | 107.8014 | 115.0307
| ClintonWind2050RCP6.0 | Clinton | Wind | RCP6.0 | 2050 | 86.5567 | 93.4271 | 100.7167 | 107.9575 | 115.212
| ClintonWind2055RCP6.0 | Clinton | Wind | RCP6.0 | 2055 | 86.5773 | 93.4492 | 100.7404 | 107.9829 | 115.2391
| ClintonWind2060RCP6.0 | Clinton | Wind | RCP6.0 | 2060 | 86.5978 | 93.4713 | 100.7642 | 108.0083 | 115.2662
| ClintonWind2065RCP6.0 | Clinton | Wind | RCP6.0 | 2065 | 86.6183 | 93.4934 | 100.7879 | 108.0338 | 115.2933
| ClintonWind2070RCP6.0 | Clinton | Wind | RCP6.0 | 2070 | 86.6388 | 93.5155 | 100.8117 | 108.0592 | 115.3203
| ClintonWind2075RCP6.0 | Clinton | Wind | RCP6.0 | 2075 | 86.8119 | 93.7434 | 101.1087 | 108.4141 | 115.7351
| ClintonWind2080RCP6.0 | Clinton | Wind | RCP6.0 | 2080 | 86.985 | 93.9712 | 101.4057 | 108.7689 | 116.1499
| ClintonWind2085RCP6.0 | Clinton | Wind | RCP6.0 | 2085 | 87.1581 | 94.1991 | 101.7027 | 109.1238 | 116.5646
| ClintonWind2090RCP6.0 | Clinton | Wind | RCP6.0 | 2090 | 87.7729 | 94.9794 | 102.6861 | 110.2837 | 117.9011
| ClintonWind2095RCP6.0 | Clinton | Wind | RCP6.0 | 2095 | 88.2146 | 95.5318 | 103.3725 | 111.0888 | 118.8228
| ClintonWind2100RCP6.0 | Clinton | Wind | RCP6.0 | 2100 | 88.6562 | 96.0843 | 104.0589 | 111.8939 | 119.7445
| ClintonWind2023RCP8.5 | Clinton | Wind | RCP8.5 | 2023 | 86.1344 | 92.8894 | 100.0296 | 107.1482 | 114.2595
| ClintonWind2025RCP8.5 | Clinton | Wind | RCP8.5 | 2025 | 86.2684 | 93.0613 | 100.2507 | 107.4095 | 114.5679
| ClintonWind2030RCP8.5 | Clinton | Wind | RCP8.5 | 2030 | 86.4023 | 93.2332 | 100.4718 | 107.6708 | 114.8764
| ClintonWind2035RCP8.5 | Clinton | Wind | RCP8.5 | 2035 | 86.5362 | 93.405 | 100.6929 | 107.9321 | 115.1849
| ClintonWind2040RCP8.5 | Clinton | Wind | RCP8.5 | 2040 | 86.5704 | 93.4418 | 100.7325 | 107.9744 | 115.2301
| ClintonWind2045RCP8.5 | Clinton | Wind | RCP8.5 | 2045 | 86.6046 | 93.4787 | 100.7721 | 108.0168 | 115.2752
| ClintonWind2050RCP8.5 | Clinton | Wind | RCP8.5 | 2050 | 86.8696 | 93.8193 | 101.2077 | 108.5323 | 115.8734
| ClintonWind2055RCP8.5 | Clinton | Wind | RCP8.5 | 2055 | 87.1004 | 94.1232 | 101.6037 | 109.0055 | 116.4264
| ClintonWind2060RCP8.5 | Clinton | Wind | RCP8.5 | 2060 | 87.7729 | 94.9794 | 102.6861 | 110.2837 | 117.9011
| ClintonWind2065RCP8.5 | Clinton | Wind | RCP8.5 | 2065 | 88.2146 | 95.5318 | 103.3725 | 111.0888 | 118.8228
| ClintonWind2070RCP8.5 | Clinton | Wind | RCP8.5 | 2070 | 88.8643 | 96.339 | 104.3757 | 112.2576 | 120.162
| ClintonWind2075RCP8.5 | Clinton | Wind | RCP8.5 | 2075 | 89.0723 | 96.5937 | 104.6925 | 112.6212 | 120.5796
| ClintonWind2080RCP8.5 | Clinton | Wind | RCP8.5 | 2080 | 89.2803 | 96.8484 | 105.0093 | 112.9849 | 120.9972
| ClintonWind2085RCP8.5 | Clinton | Wind | RCP8.5 | 2085 | 89.4171 | 97.0003 | 105.1776 | 113.1703 | 121.2004
| ClintonWind2090RCP8.5 | Clinton | Wind | RCP8.5 | 2090 | 89.5538 | 97.1523 | 105.3459 | 113.3557 | 121.4035
| ClintonWind2095RCP8.5 | Clinton | Wind | RCP8.5 | 2095 | 89.5538 | 97.1523 | 105.3459 | 113.3557 | 121.4035
| ClintonWind2100RCP8.5 | Clinton | Wind | RCP8.5 | 2100 | 89.5538 | 97.1523 | 105.3459 | 113.3557 | 121.4035
| CoboconkIce Accretion2023RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2023 | 17.2396 | 20.584 | 24.825 | 28.0522 | 31.311
| CoboconkIce Accretion2025RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2025 | 17.2251 | 20.5771 | 24.825 | 28.057 | 31.3215
| CoboconkIce Accretion2030RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2030 | 17.2106 | 20.5702 | 24.825 | 28.0617 | 31.332
| CoboconkIce Accretion2035RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2035 | 17.1961 | 20.5633 | 24.825 | 28.0664 | 31.3425
| CoboconkIce Accretion2040RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2040 | 17.1816 | 20.5563 | 24.825 | 28.0711 | 31.353
| CoboconkIce Accretion2045RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2045 | 17.1671 | 20.5494 | 24.825 | 28.0758 | 31.3635
| CoboconkIce Accretion2050RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2050 | 17.1109 | 20.5134 | 24.81 | 28.0748 | 31.374
| CoboconkIce Accretion2055RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2055 | 17.0691 | 20.4844 | 24.795 | 28.0692 | 31.374
| CoboconkIce Accretion2060RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2060 | 17.0274 | 20.4553 | 24.78 | 28.0635 | 31.374
| CoboconkIce Accretion2065RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2065 | 16.9856 | 20.4263 | 24.765 | 28.0579 | 31.374
| CoboconkIce Accretion2070RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2070 | 16.9439 | 20.3972 | 24.75 | 28.0522 | 31.374
| CoboconkIce Accretion2075RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2075 | 17.0134 | 20.4975 | 24.8875 | 28.2217 | 31.5735
| CoboconkIce Accretion2080RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2080 | 17.083 | 20.5978 | 25.025 | 28.3912 | 31.773
| CoboconkIce Accretion2085RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2085 | 17.1526 | 20.6981 | 25.1625 | 28.5607 | 31.9725
| CoboconkIce Accretion2090RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2090 | 17.2222 | 20.7984 | 25.3 | 28.7302 | 32.172
| CoboconkIce Accretion2095RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2095 | 17.2918 | 20.8987 | 25.4375 | 28.8997 | 32.3715
| CoboconkIce Accretion2100RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2100 | 17.3614 | 20.999 | 25.575 | 29.0692 | 32.571
| CoboconkIce Accretion2023RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2023 | 17.2396 | 20.584 | 24.825 | 28.0522 | 31.311
| CoboconkIce Accretion2025RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2025 | 17.2251 | 20.5771 | 24.825 | 28.057 | 31.3215
| CoboconkIce Accretion2030RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2030 | 17.2106 | 20.5702 | 24.825 | 28.0617 | 31.332
| CoboconkIce Accretion2035RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2035 | 17.1961 | 20.5633 | 24.825 | 28.0664 | 31.3425
| CoboconkIce Accretion2040RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2040 | 17.1816 | 20.5563 | 24.825 | 28.0711 | 31.353
| CoboconkIce Accretion2045RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2045 | 17.1671 | 20.5494 | 24.825 | 28.0758 | 31.3635
| CoboconkIce Accretion2050RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2050 | 17.1109 | 20.5134 | 24.81 | 28.0748 | 31.374
| CoboconkIce Accretion2055RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2055 | 17.0691 | 20.4844 | 24.795 | 28.0692 | 31.374
| CoboconkIce Accretion2060RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2060 | 17.0274 | 20.4553 | 24.78 | 28.0635 | 31.374
| CoboconkIce Accretion2065RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2065 | 16.9856 | 20.4263 | 24.765 | 28.0579 | 31.374
| CoboconkIce Accretion2070RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2070 | 16.9439 | 20.3972 | 24.75 | 28.0522 | 31.374
| CoboconkIce Accretion2075RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2075 | 17.0482 | 20.5477 | 24.9563 | 28.3065 | 31.6732
| CoboconkIce Accretion2080RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2080 | 17.1526 | 20.6981 | 25.1625 | 28.5607 | 31.9725
| CoboconkIce Accretion2085RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2085 | 17.257 | 20.8486 | 25.3687 | 28.815 | 32.2717
| CoboconkIce Accretion2090RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2090 | 17.2512 | 20.916 | 25.5333 | 29.0504 | 32.5815
| CoboconkIce Accretion2095RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2095 | 17.141 | 20.833 | 25.4917 | 29.0316 | 32.592
| CoboconkIce Accretion2100RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2100 | 17.0308 | 20.75 | 25.45 | 29.0127 | 32.6025
| CoboconkIce Accretion2023RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2023 | 17.2396 | 20.584 | 24.825 | 28.0522 | 31.311
| CoboconkIce Accretion2025RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2025 | 17.2106 | 20.5702 | 24.825 | 28.0617 | 31.332
| CoboconkIce Accretion2030RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2030 | 17.1816 | 20.5563 | 24.825 | 28.0711 | 31.353
| CoboconkIce Accretion2035RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2035 | 17.1526 | 20.5425 | 24.825 | 28.0805 | 31.374
| CoboconkIce Accretion2040RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2040 | 17.083 | 20.4941 | 24.8 | 28.0711 | 31.374
| CoboconkIce Accretion2045RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2045 | 17.0134 | 20.4457 | 24.775 | 28.0617 | 31.374
| CoboconkIce Accretion2050RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2050 | 17.083 | 20.5978 | 25.025 | 28.3912 | 31.773
| CoboconkIce Accretion2055RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2055 | 17.2222 | 20.7984 | 25.3 | 28.7302 | 32.172
| CoboconkIce Accretion2060RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2060 | 17.2512 | 20.916 | 25.5333 | 29.0504 | 32.5815
| CoboconkIce Accretion2065RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2065 | 17.141 | 20.833 | 25.4917 | 29.0316 | 32.592
| CoboconkIce Accretion2070RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2070 | 16.8105 | 20.5218 | 25.2167 | 28.7773 | 32.3505
| CoboconkIce Accretion2075RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2075 | 16.5901 | 20.2935 | 24.9833 | 28.5419 | 32.0985
| CoboconkIce Accretion2080RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2080 | 16.3698 | 20.0652 | 24.75 | 28.3065 | 31.8465
| CoboconkIce Accretion2085RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2085 | 15.6826 | 19.2871 | 23.85 | 27.3177 | 30.7597
| CoboconkIce Accretion2090RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2090 | 14.9955 | 18.509 | 22.95 | 26.329 | 29.673
| CoboconkIce Accretion2095RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2095 | 14.9955 | 18.509 | 22.95 | 26.329 | 29.673
| CoboconkIce Accretion2100RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2100 | 14.9955 | 18.509 | 22.95 | 26.329 | 29.673
| CoboconkWind2023RCP4.5 | Coboconk | Wind | RCP4.5 | 2023 | 71.0605 | 76.504 | 82.2296 | 87.9594 | 93.6857
| CoboconkWind2025RCP4.5 | Coboconk | Wind | RCP4.5 | 2025 | 71.1147 | 76.5676 | 82.3048 | 88.0442 | 93.7807
| CoboconkWind2030RCP4.5 | Coboconk | Wind | RCP4.5 | 2030 | 71.169 | 76.6311 | 82.3799 | 88.129 | 93.8757
| CoboconkWind2035RCP4.5 | Coboconk | Wind | RCP4.5 | 2035 | 71.2233 | 76.6947 | 82.4551 | 88.2138 | 93.9708
| CoboconkWind2040RCP4.5 | Coboconk | Wind | RCP4.5 | 2040 | 71.2776 | 76.7582 | 82.5303 | 88.2986 | 94.0658
| CoboconkWind2045RCP4.5 | Coboconk | Wind | RCP4.5 | 2045 | 71.3319 | 76.8218 | 82.6054 | 88.3834 | 94.1608
| CoboconkWind2050RCP4.5 | Coboconk | Wind | RCP4.5 | 2050 | 71.4584 | 76.9662 | 82.7692 | 88.5648 | 94.3606
| CoboconkWind2055RCP4.5 | Coboconk | Wind | RCP4.5 | 2055 | 71.5306 | 77.047 | 82.8577 | 88.6613 | 94.4653
| CoboconkWind2060RCP4.5 | Coboconk | Wind | RCP4.5 | 2060 | 71.6028 | 77.1278 | 82.9463 | 88.7578 | 94.57
| CoboconkWind2065RCP4.5 | Coboconk | Wind | RCP4.5 | 2065 | 71.6751 | 77.2087 | 83.0348 | 88.8543 | 94.6747
| CoboconkWind2070RCP4.5 | Coboconk | Wind | RCP4.5 | 2070 | 71.7473 | 77.2895 | 83.1234 | 88.9508 | 94.7794
| CoboconkWind2075RCP4.5 | Coboconk | Wind | RCP4.5 | 2075 | 71.7249 | 77.2666 | 83.0988 | 88.926 | 94.7544
| CoboconkWind2080RCP4.5 | Coboconk | Wind | RCP4.5 | 2080 | 71.7024 | 77.2438 | 83.0742 | 88.9011 | 94.7295
| CoboconkWind2085RCP4.5 | Coboconk | Wind | RCP4.5 | 2085 | 71.68 | 77.2209 | 83.0496 | 88.8762 | 94.7046
| CoboconkWind2090RCP4.5 | Coboconk | Wind | RCP4.5 | 2090 | 71.6576 | 77.198 | 83.025 | 88.8514 | 94.6797
| CoboconkWind2095RCP4.5 | Coboconk | Wind | RCP4.5 | 2095 | 71.6352 | 77.1751 | 83.0004 | 88.8265 | 94.6547
| CoboconkWind2100RCP4.5 | Coboconk | Wind | RCP4.5 | 2100 | 71.6127 | 77.1522 | 82.9758 | 88.8017 | 94.6298
| CoboconkWind2023RCP6.0 | Coboconk | Wind | RCP6.0 | 2023 | 71.0605 | 76.504 | 82.2296 | 87.9594 | 93.6857
| CoboconkWind2025RCP6.0 | Coboconk | Wind | RCP6.0 | 2025 | 71.1147 | 76.5676 | 82.3048 | 88.0442 | 93.7807
| CoboconkWind2030RCP6.0 | Coboconk | Wind | RCP6.0 | 2030 | 71.169 | 76.6311 | 82.3799 | 88.129 | 93.8757
| CoboconkWind2035RCP6.0 | Coboconk | Wind | RCP6.0 | 2035 | 71.2233 | 76.6947 | 82.4551 | 88.2138 | 93.9708
| CoboconkWind2040RCP6.0 | Coboconk | Wind | RCP6.0 | 2040 | 71.2776 | 76.7582 | 82.5303 | 88.2986 | 94.0658
| CoboconkWind2045RCP6.0 | Coboconk | Wind | RCP6.0 | 2045 | 71.3319 | 76.8218 | 82.6054 | 88.3834 | 94.1608
| CoboconkWind2050RCP6.0 | Coboconk | Wind | RCP6.0 | 2050 | 71.4584 | 76.9662 | 82.7692 | 88.5648 | 94.3606
| CoboconkWind2055RCP6.0 | Coboconk | Wind | RCP6.0 | 2055 | 71.5306 | 77.047 | 82.8577 | 88.6613 | 94.4653
| CoboconkWind2060RCP6.0 | Coboconk | Wind | RCP6.0 | 2060 | 71.6028 | 77.1278 | 82.9463 | 88.7578 | 94.57
| CoboconkWind2065RCP6.0 | Coboconk | Wind | RCP6.0 | 2065 | 71.6751 | 77.2087 | 83.0348 | 88.8543 | 94.6747
| CoboconkWind2070RCP6.0 | Coboconk | Wind | RCP6.0 | 2070 | 71.7473 | 77.2895 | 83.1234 | 88.9508 | 94.7794
| CoboconkWind2075RCP6.0 | Coboconk | Wind | RCP6.0 | 2075 | 71.7136 | 77.2552 | 83.0865 | 88.9135 | 94.742
| CoboconkWind2080RCP6.0 | Coboconk | Wind | RCP6.0 | 2080 | 71.68 | 77.2209 | 83.0496 | 88.8762 | 94.7046
| CoboconkWind2085RCP6.0 | Coboconk | Wind | RCP6.0 | 2085 | 71.6464 | 77.1866 | 83.0127 | 88.8389 | 94.6672
| CoboconkWind2090RCP6.0 | Coboconk | Wind | RCP6.0 | 2090 | 71.6647 | 77.2107 | 83.0441 | 88.8777 | 94.7139
| CoboconkWind2095RCP6.0 | Coboconk | Wind | RCP6.0 | 2095 | 71.7166 | 77.2692 | 83.1125 | 88.9537 | 94.7981
| CoboconkWind2100RCP6.0 | Coboconk | Wind | RCP6.0 | 2100 | 71.7685 | 77.3276 | 83.1808 | 89.0298 | 94.8822
| CoboconkWind2023RCP8.5 | Coboconk | Wind | RCP8.5 | 2023 | 71.0605 | 76.504 | 82.2296 | 87.9594 | 93.6857
| CoboconkWind2025RCP8.5 | Coboconk | Wind | RCP8.5 | 2025 | 71.169 | 76.6311 | 82.3799 | 88.129 | 93.8757
| CoboconkWind2030RCP8.5 | Coboconk | Wind | RCP8.5 | 2030 | 71.2776 | 76.7582 | 82.5303 | 88.2986 | 94.0658
| CoboconkWind2035RCP8.5 | Coboconk | Wind | RCP8.5 | 2035 | 71.3862 | 76.8853 | 82.6806 | 88.4682 | 94.2559
| CoboconkWind2040RCP8.5 | Coboconk | Wind | RCP8.5 | 2040 | 71.5065 | 77.0201 | 82.8282 | 88.6291 | 94.4304
| CoboconkWind2045RCP8.5 | Coboconk | Wind | RCP8.5 | 2045 | 71.6269 | 77.1548 | 82.9758 | 88.79 | 94.6049
| CoboconkWind2050RCP8.5 | Coboconk | Wind | RCP8.5 | 2050 | 71.7024 | 77.2438 | 83.0742 | 88.9011 | 94.7295
| CoboconkWind2055RCP8.5 | Coboconk | Wind | RCP8.5 | 2055 | 71.6576 | 77.198 | 83.025 | 88.8514 | 94.6797
| CoboconkWind2060RCP8.5 | Coboconk | Wind | RCP8.5 | 2060 | 71.6647 | 77.2107 | 83.0441 | 88.8777 | 94.7139
| CoboconkWind2065RCP8.5 | Coboconk | Wind | RCP8.5 | 2065 | 71.7166 | 77.2692 | 83.1125 | 88.9537 | 94.7981
| CoboconkWind2070RCP8.5 | Coboconk | Wind | RCP8.5 | 2070 | 71.785 | 77.3404 | 83.1917 | 89.0386 | 94.8884
| CoboconkWind2075RCP8.5 | Coboconk | Wind | RCP8.5 | 2075 | 71.8016 | 77.3531 | 83.2027 | 89.0473 | 94.8947
| CoboconkWind2080RCP8.5 | Coboconk | Wind | RCP8.5 | 2080 | 71.8181 | 77.3658 | 83.2136 | 89.0561 | 94.9009
| CoboconkWind2085RCP8.5 | Coboconk | Wind | RCP8.5 | 2085 | 71.9207 | 77.4802 | 83.3366 | 89.1877 | 95.0411
| CoboconkWind2090RCP8.5 | Coboconk | Wind | RCP8.5 | 2090 | 72.0234 | 77.5946 | 83.4596 | 89.3193 | 95.1813
| CoboconkWind2095RCP8.5 | Coboconk | Wind | RCP8.5 | 2095 | 72.0234 | 77.5946 | 83.4596 | 89.3193 | 95.1813
| CoboconkWind2100RCP8.5 | Coboconk | Wind | RCP8.5 | 2100 | 72.0234 | 77.5946 | 83.4596 | 89.3193 | 95.1813
| CobourgIce Accretion2023RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| CobourgIce Accretion2025RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
| CobourgIce Accretion2030RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| CobourgIce Accretion2035RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
| CobourgIce Accretion2040RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| CobourgIce Accretion2045RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
| CobourgIce Accretion2050RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
| CobourgIce Accretion2055RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
| CobourgIce Accretion2060RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
| CobourgIce Accretion2065RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
| CobourgIce Accretion2070RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
| CobourgIce Accretion2075RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2075 | 16.8859 | 20.3972 | 24.8292 | 28.2123 | 31.5682
| CobourgIce Accretion2080RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2080 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
| CobourgIce Accretion2085RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2085 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
| CobourgIce Accretion2090RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2090 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
| CobourgIce Accretion2095RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2095 | 16.7235 | 20.3142 | 24.8458 | 28.2877 | 31.7152
| CobourgIce Accretion2100RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.2935 | 24.85 | 28.3065 | 31.752
| CobourgIce Accretion2023RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| CobourgIce Accretion2025RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
| CobourgIce Accretion2030RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| CobourgIce Accretion2035RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
| CobourgIce Accretion2040RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| CobourgIce Accretion2045RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
| CobourgIce Accretion2050RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
| CobourgIce Accretion2055RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
| CobourgIce Accretion2060RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
| CobourgIce Accretion2065RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
| CobourgIce Accretion2070RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
| CobourgIce Accretion2075RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2075 | 16.8656 | 20.3869 | 24.8313 | 28.2217 | 31.5866
| CobourgIce Accretion2080RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2080 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
| CobourgIce Accretion2085RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2085 | 16.7438 | 20.3246 | 24.8438 | 28.2782 | 31.6969
| CobourgIce Accretion2090RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2090 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
| CobourgIce Accretion2095RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2095 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
| CobourgIce Accretion2100RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2100 | 15.6565 | 19.173 | 23.6 | 26.9505 | 30.2715
| CobourgIce Accretion2023RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| CobourgIce Accretion2025RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2025 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| CobourgIce Accretion2030RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2030 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| CobourgIce Accretion2035RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2035 | 17.6745 | 21.2272 | 25.725 | 29.154 | 32.571
| CobourgIce Accretion2040RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2040 | 17.4251 | 20.9575 | 25.425 | 28.8338 | 32.2245
| CobourgIce Accretion2045RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2045 | 17.1758 | 20.6877 | 25.125 | 28.5137 | 31.878
| CobourgIce Accretion2050RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2050 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
| CobourgIce Accretion2055RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2055 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
| CobourgIce Accretion2060RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2060 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
| CobourgIce Accretion2065RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2065 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
| CobourgIce Accretion2070RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2070 | 15.2216 | 18.6888 | 23.05 | 26.3478 | 29.631
| CobourgIce Accretion2075RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2075 | 14.7867 | 18.2047 | 22.5 | 25.7452 | 28.9905
| CobourgIce Accretion2080RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2080 | 14.3518 | 17.7205 | 21.95 | 25.1425 | 28.35
| CobourgIce Accretion2085RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2085 | 13.6908 | 16.9424 | 21.025 | 24.0972 | 27.1845
| CobourgIce Accretion2090RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2090 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| CobourgIce Accretion2095RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2095 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| CobourgIce Accretion2100RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2100 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| CobourgWind2023RCP4.5 | Cobourg | Wind | RCP4.5 | 2023 | 86.8663 | 93.5766 | 100.63 | 107.6848 | 114.741
| CobourgWind2025RCP4.5 | Cobourg | Wind | RCP4.5 | 2025 | 86.8332 | 93.5409 | 100.595 | 107.6473 | 114.703
| CobourgWind2030RCP4.5 | Cobourg | Wind | RCP4.5 | 2030 | 86.8001 | 93.5053 | 100.56 | 107.6099 | 114.665
| CobourgWind2035RCP4.5 | Cobourg | Wind | RCP4.5 | 2035 | 86.767 | 93.4697 | 100.525 | 107.5725 | 114.627
| CobourgWind2040RCP4.5 | Cobourg | Wind | RCP4.5 | 2040 | 86.7339 | 93.434 | 100.49 | 107.535 | 114.589
| CobourgWind2045RCP4.5 | Cobourg | Wind | RCP4.5 | 2045 | 86.7008 | 93.3984 | 100.455 | 107.4975 | 114.551
| CobourgWind2050RCP4.5 | Cobourg | Wind | RCP4.5 | 2050 | 86.7903 | 93.5264 | 100.634 | 107.7169 | 114.814
| CobourgWind2055RCP4.5 | Cobourg | Wind | RCP4.5 | 2055 | 86.913 | 93.6901 | 100.848 | 107.9737 | 115.1149
| CobourgWind2060RCP4.5 | Cobourg | Wind | RCP4.5 | 2060 | 87.0356 | 93.8537 | 101.062 | 108.2305 | 115.4159
| CobourgWind2065RCP4.5 | Cobourg | Wind | RCP4.5 | 2065 | 87.1582 | 94.0174 | 101.276 | 108.4873 | 115.7168
| CobourgWind2070RCP4.5 | Cobourg | Wind | RCP4.5 | 2070 | 87.2808 | 94.1811 | 101.49 | 108.7441 | 116.0178
| CobourgWind2075RCP4.5 | Cobourg | Wind | RCP4.5 | 2075 | 87.3427 | 94.2664 | 101.6033 | 108.8814 | 116.1793
| CobourgWind2080RCP4.5 | Cobourg | Wind | RCP4.5 | 2080 | 87.4046 | 94.3516 | 101.7167 | 109.0187 | 116.3408
| CobourgWind2085RCP4.5 | Cobourg | Wind | RCP4.5 | 2085 | 87.4665 | 94.4368 | 101.83 | 109.156 | 116.5023
| CobourgWind2090RCP4.5 | Cobourg | Wind | RCP4.5 | 2090 | 87.5283 | 94.5221 | 101.9433 | 109.2934 | 116.6638
| CobourgWind2095RCP4.5 | Cobourg | Wind | RCP4.5 | 2095 | 87.5902 | 94.6073 | 102.0567 | 109.4307 | 116.8253
| CobourgWind2100RCP4.5 | Cobourg | Wind | RCP4.5 | 2100 | 87.6521 | 94.6926 | 102.17 | 109.568 | 116.9868
| CobourgWind2023RCP6.0 | Cobourg | Wind | RCP6.0 | 2023 | 86.8663 | 93.5766 | 100.63 | 107.6848 | 114.741
| CobourgWind2025RCP6.0 | Cobourg | Wind | RCP6.0 | 2025 | 86.8332 | 93.5409 | 100.595 | 107.6473 | 114.703
| CobourgWind2030RCP6.0 | Cobourg | Wind | RCP6.0 | 2030 | 86.8001 | 93.5053 | 100.56 | 107.6099 | 114.665
| CobourgWind2035RCP6.0 | Cobourg | Wind | RCP6.0 | 2035 | 86.767 | 93.4697 | 100.525 | 107.5725 | 114.627
| CobourgWind2040RCP6.0 | Cobourg | Wind | RCP6.0 | 2040 | 86.7339 | 93.434 | 100.49 | 107.535 | 114.589
| CobourgWind2045RCP6.0 | Cobourg | Wind | RCP6.0 | 2045 | 86.7008 | 93.3984 | 100.455 | 107.4975 | 114.551
| CobourgWind2050RCP6.0 | Cobourg | Wind | RCP6.0 | 2050 | 86.7903 | 93.5264 | 100.634 | 107.7169 | 114.814
| CobourgWind2055RCP6.0 | Cobourg | Wind | RCP6.0 | 2055 | 86.913 | 93.6901 | 100.848 | 107.9737 | 115.1149
| CobourgWind2060RCP6.0 | Cobourg | Wind | RCP6.0 | 2060 | 87.0356 | 93.8537 | 101.062 | 108.2305 | 115.4159
| CobourgWind2065RCP6.0 | Cobourg | Wind | RCP6.0 | 2065 | 87.1582 | 94.0174 | 101.276 | 108.4873 | 115.7168
| CobourgWind2070RCP6.0 | Cobourg | Wind | RCP6.0 | 2070 | 87.2808 | 94.1811 | 101.49 | 108.7441 | 116.0178
| CobourgWind2075RCP6.0 | Cobourg | Wind | RCP6.0 | 2075 | 87.3736 | 94.309 | 101.66 | 108.9501 | 116.26
| CobourgWind2080RCP6.0 | Cobourg | Wind | RCP6.0 | 2080 | 87.4665 | 94.4368 | 101.83 | 109.156 | 116.5023
| CobourgWind2085RCP6.0 | Cobourg | Wind | RCP6.0 | 2085 | 87.5593 | 94.5647 | 102 | 109.362 | 116.7445
| CobourgWind2090RCP6.0 | Cobourg | Wind | RCP6.0 | 2090 | 87.9486 | 95.0522 | 102.61 | 110.0816 | 117.5682
| CobourgWind2095RCP6.0 | Cobourg | Wind | RCP6.0 | 2095 | 88.245 | 95.4118 | 103.05 | 110.5952 | 118.1496
| CobourgWind2100RCP6.0 | Cobourg | Wind | RCP6.0 | 2100 | 88.5415 | 95.7714 | 103.49 | 111.1088 | 118.731
| CobourgWind2023RCP8.5 | Cobourg | Wind | RCP8.5 | 2023 | 86.8663 | 93.5766 | 100.63 | 107.6848 | 114.741
| CobourgWind2025RCP8.5 | Cobourg | Wind | RCP8.5 | 2025 | 86.8001 | 93.5053 | 100.56 | 107.6099 | 114.665
| CobourgWind2030RCP8.5 | Cobourg | Wind | RCP8.5 | 2030 | 86.7339 | 93.434 | 100.49 | 107.535 | 114.589
| CobourgWind2035RCP8.5 | Cobourg | Wind | RCP8.5 | 2035 | 86.6677 | 93.3627 | 100.42 | 107.4601 | 114.513
| CobourgWind2040RCP8.5 | Cobourg | Wind | RCP8.5 | 2040 | 86.8721 | 93.6355 | 100.7767 | 107.8881 | 115.0146
| CobourgWind2045RCP8.5 | Cobourg | Wind | RCP8.5 | 2045 | 87.0764 | 93.9083 | 101.1333 | 108.3161 | 115.5162
| CobourgWind2050RCP8.5 | Cobourg | Wind | RCP8.5 | 2050 | 87.4046 | 94.3516 | 101.7167 | 109.0187 | 116.3408
| CobourgWind2055RCP8.5 | Cobourg | Wind | RCP8.5 | 2055 | 87.5283 | 94.5221 | 101.9433 | 109.2934 | 116.6638
| CobourgWind2060RCP8.5 | Cobourg | Wind | RCP8.5 | 2060 | 87.9486 | 95.0522 | 102.61 | 110.0816 | 117.5682
| CobourgWind2065RCP8.5 | Cobourg | Wind | RCP8.5 | 2065 | 88.245 | 95.4118 | 103.05 | 110.5952 | 118.1496
| CobourgWind2070RCP8.5 | Cobourg | Wind | RCP8.5 | 2070 | 88.4609 | 95.6815 | 103.3867 | 110.9947 | 118.6094
| CobourgWind2075RCP8.5 | Cobourg | Wind | RCP8.5 | 2075 | 88.3803 | 95.5916 | 103.2833 | 110.8805 | 118.4878
| CobourgWind2080RCP8.5 | Cobourg | Wind | RCP8.5 | 2080 | 88.2997 | 95.5017 | 103.18 | 110.7664 | 118.3662
| CobourgWind2085RCP8.5 | Cobourg | Wind | RCP8.5 | 2085 | 88.5113 | 95.8226 | 103.64 | 111.3389 | 119.0559
| CobourgWind2090RCP8.5 | Cobourg | Wind | RCP8.5 | 2090 | 88.7228 | 96.1434 | 104.1 | 111.9113 | 119.7456
| CobourgWind2095RCP8.5 | Cobourg | Wind | RCP8.5 | 2095 | 88.7228 | 96.1434 | 104.1 | 111.9113 | 119.7456
| CobourgWind2100RCP8.5 | Cobourg | Wind | RCP8.5 | 2100 | 88.7228 | 96.1434 | 104.1 | 111.9113 | 119.7456
| CochraneIce Accretion2023RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2023 | 11.8176 | 14.0677 | 16.915 | 19.0947 | 21.2701
| CochraneIce Accretion2025RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2025 | 11.8491 | 14.1029 | 16.9575 | 19.1428 | 21.3236
| CochraneIce Accretion2030RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2030 | 11.8806 | 14.1382 | 17 | 19.1908 | 21.3772
| CochraneIce Accretion2035RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2035 | 11.9122 | 14.1735 | 17.0425 | 19.2388 | 21.4307
| CochraneIce Accretion2040RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2040 | 11.9437 | 14.2088 | 17.085 | 19.2868 | 21.4843
| CochraneIce Accretion2045RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2045 | 11.9753 | 14.244 | 17.1275 | 19.3349 | 21.5378
| CochraneIce Accretion2050RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2050 | 12.0873 | 14.3809 | 17.2992 | 19.5327 | 21.7627
| CochraneIce Accretion2055RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2055 | 12.1677 | 14.4825 | 17.4284 | 19.6826 | 21.9341
| CochraneIce Accretion2060RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2060 | 12.2481 | 14.5841 | 17.5576 | 19.8324 | 22.1054
| CochraneIce Accretion2065RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2065 | 12.3286 | 14.6857 | 17.6868 | 19.9822 | 22.2768
| CochraneIce Accretion2070RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2070 | 12.409 | 14.7873 | 17.816 | 20.1321 | 22.4482
| CochraneIce Accretion2075RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2075 | 12.4307 | 14.8202 | 17.8585 | 20.1833 | 22.5089
| CochraneIce Accretion2080RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2080 | 12.4524 | 14.8531 | 17.901 | 20.2345 | 22.5695
| CochraneIce Accretion2085RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2085 | 12.4741 | 14.8861 | 17.9435 | 20.2858 | 22.6302
| CochraneIce Accretion2090RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2090 | 12.4958 | 14.919 | 17.986 | 20.337 | 22.6909
| CochraneIce Accretion2095RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2095 | 12.5175 | 14.9519 | 18.0285 | 20.3882 | 22.7516
| CochraneIce Accretion2100RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2100 | 12.5391 | 14.9848 | 18.071 | 20.4394 | 22.8123
| CochraneIce Accretion2023RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2023 | 11.8176 | 14.0677 | 16.915 | 19.0947 | 21.2701
| CochraneIce Accretion2025RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2025 | 11.8491 | 14.1029 | 16.9575 | 19.1428 | 21.3236
| CochraneIce Accretion2030RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2030 | 11.8806 | 14.1382 | 17 | 19.1908 | 21.3772
| CochraneIce Accretion2035RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2035 | 11.9122 | 14.1735 | 17.0425 | 19.2388 | 21.4307
| CochraneIce Accretion2040RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2040 | 11.9437 | 14.2088 | 17.085 | 19.2868 | 21.4843
| CochraneIce Accretion2045RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2045 | 11.9753 | 14.244 | 17.1275 | 19.3349 | 21.5378
| CochraneIce Accretion2050RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2050 | 12.0873 | 14.3809 | 17.2992 | 19.5327 | 21.7627
| CochraneIce Accretion2055RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2055 | 12.1677 | 14.4825 | 17.4284 | 19.6826 | 21.9341
| CochraneIce Accretion2060RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2060 | 12.2481 | 14.5841 | 17.5576 | 19.8324 | 22.1054
| CochraneIce Accretion2065RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2065 | 12.3286 | 14.6857 | 17.6868 | 19.9822 | 22.2768
| CochraneIce Accretion2070RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2070 | 12.409 | 14.7873 | 17.816 | 20.1321 | 22.4482
| CochraneIce Accretion2075RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2075 | 12.4416 | 14.8367 | 17.8798 | 20.2089 | 22.5392
| CochraneIce Accretion2080RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2080 | 12.4741 | 14.8861 | 17.9435 | 20.2858 | 22.6302
| CochraneIce Accretion2085RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2085 | 12.5066 | 14.9354 | 18.0072 | 20.3626 | 22.7213
| CochraneIce Accretion2090RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2090 | 12.413 | 14.8531 | 17.935 | 20.2986 | 22.6624
| CochraneIce Accretion2095RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2095 | 12.2868 | 14.7214 | 17.799 | 20.1577 | 22.5124
| CochraneIce Accretion2100RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2100 | 12.1606 | 14.5897 | 17.663 | 20.0168 | 22.3625
| CochraneIce Accretion2023RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2023 | 11.8176 | 14.0677 | 16.915 | 19.0947 | 21.2701
| CochraneIce Accretion2025RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2025 | 11.8806 | 14.1382 | 17 | 19.1908 | 21.3772
| CochraneIce Accretion2030RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2030 | 11.9437 | 14.2088 | 17.085 | 19.2868 | 21.4843
| CochraneIce Accretion2035RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2035 | 12.0068 | 14.2793 | 17.17 | 19.3829 | 21.5914
| CochraneIce Accretion2040RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2040 | 12.1409 | 14.4486 | 17.3853 | 19.6326 | 21.877
| CochraneIce Accretion2045RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2045 | 12.275 | 14.618 | 17.6007 | 19.8823 | 22.1626
| CochraneIce Accretion2050RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2050 | 12.4524 | 14.8531 | 17.901 | 20.2345 | 22.5695
| CochraneIce Accretion2055RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2055 | 12.4958 | 14.919 | 17.986 | 20.337 | 22.6909
| CochraneIce Accretion2060RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2060 | 12.413 | 14.8531 | 17.935 | 20.2986 | 22.6624
| CochraneIce Accretion2065RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2065 | 12.2868 | 14.7214 | 17.799 | 20.1577 | 22.5124
| CochraneIce Accretion2070RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2070 | 12.0778 | 14.5051 | 17.578 | 19.9272 | 22.2697
| CochraneIce Accretion2075RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2075 | 11.995 | 14.4204 | 17.493 | 19.8375 | 22.1768
| CochraneIce Accretion2080RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2080 | 11.9122 | 14.3358 | 17.408 | 19.7479 | 22.084
| CochraneIce Accretion2085RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2085 | 11.859 | 14.3146 | 17.4165 | 19.7863 | 22.1483
| CochraneIce Accretion2090RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2090 | 11.8057 | 14.2934 | 17.425 | 19.8247 | 22.2125
| CochraneIce Accretion2095RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2095 | 11.8057 | 14.2934 | 17.425 | 19.8247 | 22.2125
| CochraneIce Accretion2100RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2100 | 11.8057 | 14.2934 | 17.425 | 19.8247 | 22.2125
| CochraneWind2023RCP4.5 | Cochrane | Wind | RCP4.5 | 2023 | 72.8517 | 78.3778 | 84.1764 | 89.9968 | 95.8175
| CochraneWind2025RCP4.5 | Cochrane | Wind | RCP4.5 | 2025 | 72.9266 | 78.4637 | 84.2744 | 90.1047 | 95.9356
| CochraneWind2030RCP4.5 | Cochrane | Wind | RCP4.5 | 2030 | 73.0016 | 78.5497 | 84.3724 | 90.2126 | 96.0537
| CochraneWind2035RCP4.5 | Cochrane | Wind | RCP4.5 | 2035 | 73.0765 | 78.6356 | 84.4704 | 90.3204 | 96.1718
| CochraneWind2040RCP4.5 | Cochrane | Wind | RCP4.5 | 2040 | 73.1515 | 78.7215 | 84.5684 | 90.4283 | 96.2899
| CochraneWind2045RCP4.5 | Cochrane | Wind | RCP4.5 | 2045 | 73.2264 | 78.8075 | 84.6664 | 90.5361 | 96.408
| CochraneWind2050RCP4.5 | Cochrane | Wind | RCP4.5 | 2050 | 73.3304 | 78.9324 | 84.8148 | 90.7051 | 96.5989
| CochraneWind2055RCP4.5 | Cochrane | Wind | RCP4.5 | 2055 | 73.3594 | 78.9715 | 84.8652 | 90.7662 | 96.6716
| CochraneWind2060RCP4.5 | Cochrane | Wind | RCP4.5 | 2060 | 73.3884 | 79.0106 | 84.9156 | 90.8273 | 96.7444
| CochraneWind2065RCP4.5 | Cochrane | Wind | RCP4.5 | 2065 | 73.4174 | 79.0496 | 84.966 | 90.8885 | 96.8172
| CochraneWind2070RCP4.5 | Cochrane | Wind | RCP4.5 | 2070 | 73.4464 | 79.0887 | 85.0164 | 90.9496 | 96.89
| CochraneWind2075RCP4.5 | Cochrane | Wind | RCP4.5 | 2075 | 73.4996 | 79.1356 | 85.0542 | 90.9825 | 96.9155
| CochraneWind2080RCP4.5 | Cochrane | Wind | RCP4.5 | 2080 | 73.5528 | 79.1824 | 85.092 | 91.0155 | 96.941
| CochraneWind2085RCP4.5 | Cochrane | Wind | RCP4.5 | 2085 | 73.606 | 79.2293 | 85.1298 | 91.0484 | 96.9666
| CochraneWind2090RCP4.5 | Cochrane | Wind | RCP4.5 | 2090 | 73.6592 | 79.2762 | 85.1676 | 91.0814 | 96.9921
| CochraneWind2095RCP4.5 | Cochrane | Wind | RCP4.5 | 2095 | 73.7124 | 79.323 | 85.2054 | 91.1144 | 97.0176
| CochraneWind2100RCP4.5 | Cochrane | Wind | RCP4.5 | 2100 | 73.7656 | 79.3699 | 85.2432 | 91.1473 | 97.0432
| CochraneWind2023RCP6.0 | Cochrane | Wind | RCP6.0 | 2023 | 72.8517 | 78.3778 | 84.1764 | 89.9968 | 95.8175
| CochraneWind2025RCP6.0 | Cochrane | Wind | RCP6.0 | 2025 | 72.9266 | 78.4637 | 84.2744 | 90.1047 | 95.9356
| CochraneWind2030RCP6.0 | Cochrane | Wind | RCP6.0 | 2030 | 73.0016 | 78.5497 | 84.3724 | 90.2126 | 96.0537
| CochraneWind2035RCP6.0 | Cochrane | Wind | RCP6.0 | 2035 | 73.0765 | 78.6356 | 84.4704 | 90.3204 | 96.1718
| CochraneWind2040RCP6.0 | Cochrane | Wind | RCP6.0 | 2040 | 73.1515 | 78.7215 | 84.5684 | 90.4283 | 96.2899
| CochraneWind2045RCP6.0 | Cochrane | Wind | RCP6.0 | 2045 | 73.2264 | 78.8075 | 84.6664 | 90.5361 | 96.408
| CochraneWind2050RCP6.0 | Cochrane | Wind | RCP6.0 | 2050 | 73.3304 | 78.9324 | 84.8148 | 90.7051 | 96.5989
| CochraneWind2055RCP6.0 | Cochrane | Wind | RCP6.0 | 2055 | 73.3594 | 78.9715 | 84.8652 | 90.7662 | 96.6716
| CochraneWind2060RCP6.0 | Cochrane | Wind | RCP6.0 | 2060 | 73.3884 | 79.0106 | 84.9156 | 90.8273 | 96.7444
| CochraneWind2065RCP6.0 | Cochrane | Wind | RCP6.0 | 2065 | 73.4174 | 79.0496 | 84.966 | 90.8885 | 96.8172
| CochraneWind2070RCP6.0 | Cochrane | Wind | RCP6.0 | 2070 | 73.4464 | 79.0887 | 85.0164 | 90.9496 | 96.89
| CochraneWind2075RCP6.0 | Cochrane | Wind | RCP6.0 | 2075 | 73.5262 | 79.159 | 85.0731 | 90.999 | 96.9283
| CochraneWind2080RCP6.0 | Cochrane | Wind | RCP6.0 | 2080 | 73.606 | 79.2293 | 85.1298 | 91.0484 | 96.9666
| CochraneWind2085RCP6.0 | Cochrane | Wind | RCP6.0 | 2085 | 73.6858 | 79.2996 | 85.1865 | 91.0979 | 97.0049
| CochraneWind2090RCP6.0 | Cochrane | Wind | RCP6.0 | 2090 | 73.8816 | 79.4871 | 85.3636 | 91.2671 | 97.1645
| CochraneWind2095RCP6.0 | Cochrane | Wind | RCP6.0 | 2095 | 73.9977 | 79.6043 | 85.484 | 91.387 | 97.2858
| CochraneWind2100RCP6.0 | Cochrane | Wind | RCP6.0 | 2100 | 74.1137 | 79.7215 | 85.6044 | 91.5068 | 97.4071
| CochraneWind2023RCP8.5 | Cochrane | Wind | RCP8.5 | 2023 | 72.8517 | 78.3778 | 84.1764 | 89.9968 | 95.8175
| CochraneWind2025RCP8.5 | Cochrane | Wind | RCP8.5 | 2025 | 73.0016 | 78.5497 | 84.3724 | 90.2126 | 96.0537
| CochraneWind2030RCP8.5 | Cochrane | Wind | RCP8.5 | 2030 | 73.1515 | 78.7215 | 84.5684 | 90.4283 | 96.2899
| CochraneWind2035RCP8.5 | Cochrane | Wind | RCP8.5 | 2035 | 73.3014 | 78.8934 | 84.7644 | 90.644 | 96.5261
| CochraneWind2040RCP8.5 | Cochrane | Wind | RCP8.5 | 2040 | 73.3497 | 78.9585 | 84.8484 | 90.7458 | 96.6474
| CochraneWind2045RCP8.5 | Cochrane | Wind | RCP8.5 | 2045 | 73.3981 | 79.0236 | 84.9324 | 90.8477 | 96.7687
| CochraneWind2050RCP8.5 | Cochrane | Wind | RCP8.5 | 2050 | 73.5528 | 79.1824 | 85.092 | 91.0155 | 96.941
| CochraneWind2055RCP8.5 | Cochrane | Wind | RCP8.5 | 2055 | 73.6592 | 79.2762 | 85.1676 | 91.0814 | 96.9921
| CochraneWind2060RCP8.5 | Cochrane | Wind | RCP8.5 | 2060 | 73.8816 | 79.4871 | 85.3636 | 91.2671 | 97.1645
| CochraneWind2065RCP8.5 | Cochrane | Wind | RCP8.5 | 2065 | 73.9977 | 79.6043 | 85.484 | 91.387 | 97.2858
| CochraneWind2070RCP8.5 | Cochrane | Wind | RCP8.5 | 2070 | 74.2636 | 79.8751 | 85.7556 | 91.6626 | 97.5667
| CochraneWind2075RCP8.5 | Cochrane | Wind | RCP8.5 | 2075 | 74.4135 | 80.0287 | 85.9068 | 91.8184 | 97.7263
| CochraneWind2080RCP8.5 | Cochrane | Wind | RCP8.5 | 2080 | 74.5634 | 80.1824 | 86.058 | 91.9742 | 97.8859
| CochraneWind2085RCP8.5 | Cochrane | Wind | RCP8.5 | 2085 | 74.7303 | 80.4011 | 86.3436 | 92.3113 | 98.2785
| CochraneWind2090RCP8.5 | Cochrane | Wind | RCP8.5 | 2090 | 74.8971 | 80.6198 | 86.6292 | 92.6483 | 98.6711
| CochraneWind2095RCP8.5 | Cochrane | Wind | RCP8.5 | 2095 | 74.8971 | 80.6198 | 86.6292 | 92.6483 | 98.6711
| CochraneWind2100RCP8.5 | Cochrane | Wind | RCP8.5 | 2100 | 74.8971 | 80.6198 | 86.6292 | 92.6483 | 98.6711
| ColborneIce Accretion2023RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| ColborneIce Accretion2025RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
| ColborneIce Accretion2030RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| ColborneIce Accretion2035RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
| ColborneIce Accretion2040RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| ColborneIce Accretion2045RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
| ColborneIce Accretion2050RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
| ColborneIce Accretion2055RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
| ColborneIce Accretion2060RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
| ColborneIce Accretion2065RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
| ColborneIce Accretion2070RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
| ColborneIce Accretion2075RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2075 | 16.8859 | 20.3972 | 24.8292 | 28.2123 | 31.5682
| ColborneIce Accretion2080RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2080 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
| ColborneIce Accretion2085RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2085 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
| ColborneIce Accretion2090RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2090 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
| ColborneIce Accretion2095RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2095 | 16.7235 | 20.3142 | 24.8458 | 28.2877 | 31.7152
| ColborneIce Accretion2100RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.2935 | 24.85 | 28.3065 | 31.752
| ColborneIce Accretion2023RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| ColborneIce Accretion2025RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
| ColborneIce Accretion2030RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| ColborneIce Accretion2035RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
| ColborneIce Accretion2040RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| ColborneIce Accretion2045RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
| ColborneIce Accretion2050RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
| ColborneIce Accretion2055RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
| ColborneIce Accretion2060RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
| ColborneIce Accretion2065RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
| ColborneIce Accretion2070RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
| ColborneIce Accretion2075RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2075 | 16.8656 | 20.3869 | 24.8313 | 28.2217 | 31.5866
| ColborneIce Accretion2080RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2080 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
| ColborneIce Accretion2085RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2085 | 16.7438 | 20.3246 | 24.8438 | 28.2782 | 31.6969
| ColborneIce Accretion2090RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2090 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
| ColborneIce Accretion2095RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2095 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
| ColborneIce Accretion2100RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2100 | 15.6565 | 19.173 | 23.6 | 26.9505 | 30.2715
| ColborneIce Accretion2023RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| ColborneIce Accretion2025RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2025 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| ColborneIce Accretion2030RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2030 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| ColborneIce Accretion2035RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2035 | 17.6745 | 21.2272 | 25.725 | 29.154 | 32.571
| ColborneIce Accretion2040RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2040 | 17.4251 | 20.9575 | 25.425 | 28.8338 | 32.2245
| ColborneIce Accretion2045RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2045 | 17.1758 | 20.6877 | 25.125 | 28.5137 | 31.878
| ColborneIce Accretion2050RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2050 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
| ColborneIce Accretion2055RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2055 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
| ColborneIce Accretion2060RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2060 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
| ColborneIce Accretion2065RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2065 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
| ColborneIce Accretion2070RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2070 | 15.2216 | 18.6888 | 23.05 | 26.3478 | 29.631
| ColborneIce Accretion2075RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2075 | 14.7867 | 18.2047 | 22.5 | 25.7452 | 28.9905
| ColborneIce Accretion2080RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2080 | 14.3518 | 17.7205 | 21.95 | 25.1425 | 28.35
| ColborneIce Accretion2085RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2085 | 13.6908 | 16.9424 | 21.025 | 24.0972 | 27.1845
| ColborneIce Accretion2090RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2090 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| ColborneIce Accretion2095RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2095 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| ColborneIce Accretion2100RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2100 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| ColborneWind2023RCP4.5 | Colborne | Wind | RCP4.5 | 2023 | 85.9977 | 92.6408 | 99.6237 | 106.608 | 113.5936
| ColborneWind2025RCP4.5 | Colborne | Wind | RCP4.5 | 2025 | 85.9649 | 92.6055 | 99.5891 | 106.5709 | 113.556
| ColborneWind2030RCP4.5 | Colborne | Wind | RCP4.5 | 2030 | 85.9321 | 92.5702 | 99.5544 | 106.5338 | 113.5183
| ColborneWind2035RCP4.5 | Colborne | Wind | RCP4.5 | 2035 | 85.8994 | 92.535 | 99.5198 | 106.4967 | 113.4807
| ColborneWind2040RCP4.5 | Colborne | Wind | RCP4.5 | 2040 | 85.8666 | 92.4997 | 99.4851 | 106.4597 | 113.4431
| ColborneWind2045RCP4.5 | Colborne | Wind | RCP4.5 | 2045 | 85.8338 | 92.4644 | 99.4505 | 106.4226 | 113.4055
| ColborneWind2050RCP4.5 | Colborne | Wind | RCP4.5 | 2050 | 85.9224 | 92.5911 | 99.6277 | 106.6397 | 113.6658
| ColborneWind2055RCP4.5 | Colborne | Wind | RCP4.5 | 2055 | 86.0438 | 92.7532 | 99.8395 | 106.894 | 113.9638
| ColborneWind2060RCP4.5 | Colborne | Wind | RCP4.5 | 2060 | 86.1652 | 92.9152 | 100.0514 | 107.1482 | 114.2617
| ColborneWind2065RCP4.5 | Colborne | Wind | RCP4.5 | 2065 | 86.2866 | 93.0772 | 100.2632 | 107.4024 | 114.5597
| ColborneWind2070RCP4.5 | Colborne | Wind | RCP4.5 | 2070 | 86.408 | 93.2393 | 100.4751 | 107.6567 | 114.8576
| ColborneWind2075RCP4.5 | Colborne | Wind | RCP4.5 | 2075 | 86.4693 | 93.3237 | 100.5873 | 107.7926 | 115.0175
| ColborneWind2080RCP4.5 | Colborne | Wind | RCP4.5 | 2080 | 86.5305 | 93.4081 | 100.6995 | 107.9285 | 115.1774
| ColborneWind2085RCP4.5 | Colborne | Wind | RCP4.5 | 2085 | 86.5918 | 93.4925 | 100.8117 | 108.0645 | 115.3373
| ColborneWind2090RCP4.5 | Colborne | Wind | RCP4.5 | 2090 | 86.6531 | 93.5769 | 100.9239 | 108.2004 | 115.4972
| ColborneWind2095RCP4.5 | Colborne | Wind | RCP4.5 | 2095 | 86.7143 | 93.6613 | 101.0361 | 108.3364 | 115.657
| ColborneWind2100RCP4.5 | Colborne | Wind | RCP4.5 | 2100 | 86.7756 | 93.7457 | 101.1483 | 108.4723 | 115.8169
| ColborneWind2023RCP6.0 | Colborne | Wind | RCP6.0 | 2023 | 85.9977 | 92.6408 | 99.6237 | 106.608 | 113.5936
| ColborneWind2025RCP6.0 | Colborne | Wind | RCP6.0 | 2025 | 85.9649 | 92.6055 | 99.5891 | 106.5709 | 113.556
| ColborneWind2030RCP6.0 | Colborne | Wind | RCP6.0 | 2030 | 85.9321 | 92.5702 | 99.5544 | 106.5338 | 113.5183
| ColborneWind2035RCP6.0 | Colborne | Wind | RCP6.0 | 2035 | 85.8994 | 92.535 | 99.5198 | 106.4967 | 113.4807
| ColborneWind2040RCP6.0 | Colborne | Wind | RCP6.0 | 2040 | 85.8666 | 92.4997 | 99.4851 | 106.4597 | 113.4431
| ColborneWind2045RCP6.0 | Colborne | Wind | RCP6.0 | 2045 | 85.8338 | 92.4644 | 99.4505 | 106.4226 | 113.4055
| ColborneWind2050RCP6.0 | Colborne | Wind | RCP6.0 | 2050 | 85.9224 | 92.5911 | 99.6277 | 106.6397 | 113.6658
| ColborneWind2055RCP6.0 | Colborne | Wind | RCP6.0 | 2055 | 86.0438 | 92.7532 | 99.8395 | 106.894 | 113.9638
| ColborneWind2060RCP6.0 | Colborne | Wind | RCP6.0 | 2060 | 86.1652 | 92.9152 | 100.0514 | 107.1482 | 114.2617
| ColborneWind2065RCP6.0 | Colborne | Wind | RCP6.0 | 2065 | 86.2866 | 93.0772 | 100.2632 | 107.4024 | 114.5597
| ColborneWind2070RCP6.0 | Colborne | Wind | RCP6.0 | 2070 | 86.408 | 93.2393 | 100.4751 | 107.6567 | 114.8576
| ColborneWind2075RCP6.0 | Colborne | Wind | RCP6.0 | 2075 | 86.4999 | 93.3659 | 100.6434 | 107.8606 | 115.0974
| ColborneWind2080RCP6.0 | Colborne | Wind | RCP6.0 | 2080 | 86.5918 | 93.4925 | 100.8117 | 108.0645 | 115.3373
| ColborneWind2085RCP6.0 | Colborne | Wind | RCP6.0 | 2085 | 86.6837 | 93.6191 | 100.98 | 108.2684 | 115.5771
| ColborneWind2090RCP6.0 | Colborne | Wind | RCP6.0 | 2090 | 87.0691 | 94.1017 | 101.5839 | 108.9808 | 116.3925
| ColborneWind2095RCP6.0 | Colborne | Wind | RCP6.0 | 2095 | 87.3626 | 94.4577 | 102.0195 | 109.4892 | 116.9681
| ColborneWind2100RCP6.0 | Colborne | Wind | RCP6.0 | 2100 | 87.6561 | 94.8137 | 102.4551 | 109.9977 | 117.5437
| ColborneWind2023RCP8.5 | Colborne | Wind | RCP8.5 | 2023 | 85.9977 | 92.6408 | 99.6237 | 106.608 | 113.5936
| ColborneWind2025RCP8.5 | Colborne | Wind | RCP8.5 | 2025 | 85.9321 | 92.5702 | 99.5544 | 106.5338 | 113.5183
| ColborneWind2030RCP8.5 | Colborne | Wind | RCP8.5 | 2030 | 85.8666 | 92.4997 | 99.4851 | 106.4597 | 113.4431
| ColborneWind2035RCP8.5 | Colborne | Wind | RCP8.5 | 2035 | 85.8011 | 92.4291 | 99.4158 | 106.3855 | 113.3679
| ColborneWind2040RCP8.5 | Colborne | Wind | RCP8.5 | 2040 | 86.0034 | 92.6991 | 99.7689 | 106.8092 | 113.8645
| ColborneWind2045RCP8.5 | Colborne | Wind | RCP8.5 | 2045 | 86.2057 | 92.9692 | 100.122 | 107.2329 | 114.361
| ColborneWind2050RCP8.5 | Colborne | Wind | RCP8.5 | 2050 | 86.5305 | 93.4081 | 100.6995 | 107.9285 | 115.1774
| ColborneWind2055RCP8.5 | Colborne | Wind | RCP8.5 | 2055 | 86.6531 | 93.5769 | 100.9239 | 108.2004 | 115.4972
| ColborneWind2060RCP8.5 | Colborne | Wind | RCP8.5 | 2060 | 87.0691 | 94.1017 | 101.5839 | 108.9808 | 116.3925
| ColborneWind2065RCP8.5 | Colborne | Wind | RCP8.5 | 2065 | 87.3626 | 94.4577 | 102.0195 | 109.4892 | 116.9681
| ColborneWind2070RCP8.5 | Colborne | Wind | RCP8.5 | 2070 | 87.5763 | 94.7247 | 102.3528 | 109.8847 | 117.4233
| ColborneWind2075RCP8.5 | Colborne | Wind | RCP8.5 | 2075 | 87.4965 | 94.6357 | 102.2505 | 109.7717 | 117.3029
| ColborneWind2080RCP8.5 | Colborne | Wind | RCP8.5 | 2080 | 87.4167 | 94.5467 | 102.1482 | 109.6587 | 117.1825
| ColborneWind2085RCP8.5 | Colborne | Wind | RCP8.5 | 2085 | 87.6262 | 94.8643 | 102.6036 | 110.2255 | 117.8653
| ColborneWind2090RCP8.5 | Colborne | Wind | RCP8.5 | 2090 | 87.8356 | 95.182 | 103.059 | 110.7922 | 118.5481
| ColborneWind2095RCP8.5 | Colborne | Wind | RCP8.5 | 2095 | 87.8356 | 95.182 | 103.059 | 110.7922 | 118.5481
| ColborneWind2100RCP8.5 | Colborne | Wind | RCP8.5 | 2100 | 87.8356 | 95.182 | 103.059 | 110.7922 | 118.5481
| CollingwoodIce Accretion2023RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2023 | 14.0422 | 16.8158 | 20.32 | 22.9842 | 25.6536
| CollingwoodIce Accretion2025RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2025 | 14.0399 | 16.8186 | 20.3333 | 23.0068 | 25.683
| CollingwoodIce Accretion2030RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2030 | 14.0375 | 16.8213 | 20.3467 | 23.0294 | 25.7124
| CollingwoodIce Accretion2035RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2035 | 14.0352 | 16.8241 | 20.36 | 23.052 | 25.7418
| CollingwoodIce Accretion2040RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2040 | 14.0329 | 16.8269 | 20.3733 | 23.0746 | 25.7712
| CollingwoodIce Accretion2045RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2045 | 14.0306 | 16.8296 | 20.3867 | 23.0972 | 25.8006
| CollingwoodIce Accretion2050RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2050 | 14.0004 | 16.8158 | 20.392 | 23.1243 | 25.8401
| CollingwoodIce Accretion2055RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2055 | 13.9726 | 16.7992 | 20.384 | 23.1288 | 25.8502
| CollingwoodIce Accretion2060RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2060 | 13.9448 | 16.7826 | 20.376 | 23.1334 | 25.8602
| CollingwoodIce Accretion2065RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2065 | 13.9169 | 16.766 | 20.368 | 23.1379 | 25.8703
| CollingwoodIce Accretion2070RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2070 | 13.8891 | 16.7494 | 20.36 | 23.1424 | 25.8804
| CollingwoodIce Accretion2075RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2075 | 13.8729 | 16.7522 | 20.3867 | 23.1838 | 25.9392
| CollingwoodIce Accretion2080RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2080 | 13.8566 | 16.7549 | 20.4133 | 23.2253 | 25.998
| CollingwoodIce Accretion2085RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2085 | 13.8404 | 16.7577 | 20.44 | 23.2667 | 26.0568
| CollingwoodIce Accretion2090RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2090 | 13.8241 | 16.7605 | 20.4667 | 23.3081 | 26.1156
| CollingwoodIce Accretion2095RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2095 | 13.8079 | 16.7632 | 20.4933 | 23.3496 | 26.1744
| CollingwoodIce Accretion2100RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2100 | 13.7917 | 16.766 | 20.52 | 23.391 | 26.2332
| CollingwoodIce Accretion2023RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2023 | 14.0422 | 16.8158 | 20.32 | 22.9842 | 25.6536
| CollingwoodIce Accretion2025RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2025 | 14.0399 | 16.8186 | 20.3333 | 23.0068 | 25.683
| CollingwoodIce Accretion2030RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2030 | 14.0375 | 16.8213 | 20.3467 | 23.0294 | 25.7124
| CollingwoodIce Accretion2035RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2035 | 14.0352 | 16.8241 | 20.36 | 23.052 | 25.7418
| CollingwoodIce Accretion2040RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2040 | 14.0329 | 16.8269 | 20.3733 | 23.0746 | 25.7712
| CollingwoodIce Accretion2045RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2045 | 14.0306 | 16.8296 | 20.3867 | 23.0972 | 25.8006
| CollingwoodIce Accretion2050RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2050 | 14.0004 | 16.8158 | 20.392 | 23.1243 | 25.8401
| CollingwoodIce Accretion2055RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2055 | 13.9726 | 16.7992 | 20.384 | 23.1288 | 25.8502
| CollingwoodIce Accretion2060RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2060 | 13.9448 | 16.7826 | 20.376 | 23.1334 | 25.8602
| CollingwoodIce Accretion2065RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2065 | 13.9169 | 16.766 | 20.368 | 23.1379 | 25.8703
| CollingwoodIce Accretion2070RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2070 | 13.8891 | 16.7494 | 20.36 | 23.1424 | 25.8804
| CollingwoodIce Accretion2075RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2075 | 13.8647 | 16.7535 | 20.4 | 23.2045 | 25.9686
| CollingwoodIce Accretion2080RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2080 | 13.8404 | 16.7577 | 20.44 | 23.2667 | 26.0568
| CollingwoodIce Accretion2085RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2085 | 13.816 | 16.7618 | 20.48 | 23.3288 | 26.145
| CollingwoodIce Accretion2090RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2090 | 13.6571 | 16.6332 | 20.3933 | 23.2629 | 26.1072
| CollingwoodIce Accretion2095RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2095 | 13.5226 | 16.5004 | 20.2667 | 23.1349 | 25.9812
| CollingwoodIce Accretion2100RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2100 | 13.3881 | 16.3676 | 20.14 | 23.0068 | 25.8552
| CollingwoodIce Accretion2023RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2023 | 14.0422 | 16.8158 | 20.32 | 22.9842 | 25.6536
| CollingwoodIce Accretion2025RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2025 | 14.0375 | 16.8213 | 20.3467 | 23.0294 | 25.7124
| CollingwoodIce Accretion2030RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2030 | 14.0329 | 16.8269 | 20.3733 | 23.0746 | 25.7712
| CollingwoodIce Accretion2035RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2035 | 14.0283 | 16.8324 | 20.4 | 23.1198 | 25.83
| CollingwoodIce Accretion2040RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2040 | 13.9819 | 16.8047 | 20.3867 | 23.1273 | 25.8468
| CollingwoodIce Accretion2045RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2045 | 13.9355 | 16.7771 | 20.3733 | 23.1349 | 25.8636
| CollingwoodIce Accretion2050RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2050 | 13.8566 | 16.7549 | 20.4133 | 23.2253 | 25.998
| CollingwoodIce Accretion2055RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2055 | 13.8241 | 16.7605 | 20.4667 | 23.3081 | 26.1156
| CollingwoodIce Accretion2060RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2060 | 13.6571 | 16.6332 | 20.3933 | 23.2629 | 26.1072
| CollingwoodIce Accretion2065RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2065 | 13.5226 | 16.5004 | 20.2667 | 23.1349 | 25.9812
| CollingwoodIce Accretion2070RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2070 | 13.1283 | 16.0965 | 19.8467 | 22.6979 | 25.536
| CollingwoodIce Accretion2075RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2075 | 12.8685 | 15.8253 | 19.5533 | 22.3891 | 25.2168
| CollingwoodIce Accretion2080RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2080 | 12.6087 | 15.5542 | 19.26 | 22.0802 | 24.8976
| CollingwoodIce Accretion2085RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2085 | 11.9755 | 14.8155 | 18.4 | 21.1197 | 23.8266
| CollingwoodIce Accretion2090RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2090 | 11.3423 | 14.0768 | 17.54 | 20.1592 | 22.7556
| CollingwoodIce Accretion2095RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2095 | 11.3423 | 14.0768 | 17.54 | 20.1592 | 22.7556
| CollingwoodIce Accretion2100RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2100 | 11.3423 | 14.0768 | 17.54 | 20.1592 | 22.7556
| CollingwoodWind2023RCP4.5 | Collingwood | Wind | RCP4.5 | 2023 | 81.1673 | 87.3763 | 93.8966 | 100.4392 | 106.9671
| CollingwoodWind2025RCP4.5 | Collingwood | Wind | RCP4.5 | 2025 | 81.1633 | 87.369 | 93.8856 | 100.4224 | 106.9493
| CollingwoodWind2030RCP4.5 | Collingwood | Wind | RCP4.5 | 2030 | 81.1592 | 87.3617 | 93.8747 | 100.4057 | 106.9314
| CollingwoodWind2035RCP4.5 | Collingwood | Wind | RCP4.5 | 2035 | 81.1552 | 87.3544 | 93.8637 | 100.3889 | 106.9135
| CollingwoodWind2040RCP4.5 | Collingwood | Wind | RCP4.5 | 2040 | 81.1511 | 87.3472 | 93.8527 | 100.3721 | 106.8957
| CollingwoodWind2045RCP4.5 | Collingwood | Wind | RCP4.5 | 2045 | 81.1471 | 87.3399 | 93.8418 | 100.3554 | 106.8778
| CollingwoodWind2050RCP4.5 | Collingwood | Wind | RCP4.5 | 2050 | 81.1381 | 87.3168 | 93.8007 | 100.2984 | 106.8064
| CollingwoodWind2055RCP4.5 | Collingwood | Wind | RCP4.5 | 2055 | 81.1333 | 87.3011 | 93.7706 | 100.2581 | 106.7528
| CollingwoodWind2060RCP4.5 | Collingwood | Wind | RCP4.5 | 2060 | 81.1284 | 87.2854 | 93.7406 | 100.2179 | 106.6992
| CollingwoodWind2065RCP4.5 | Collingwood | Wind | RCP4.5 | 2065 | 81.1235 | 87.2696 | 93.7105 | 100.1777 | 106.6456
| CollingwoodWind2070RCP4.5 | Collingwood | Wind | RCP4.5 | 2070 | 81.1186 | 87.2539 | 93.6804 | 100.1374 | 106.5921
| CollingwoodWind2075RCP4.5 | Collingwood | Wind | RCP4.5 | 2075 | 81.1552 | 87.3078 | 93.7556 | 100.2313 | 106.7028
| CollingwoodWind2080RCP4.5 | Collingwood | Wind | RCP4.5 | 2080 | 81.1917 | 87.3617 | 93.8308 | 100.3252 | 106.8135
| CollingwoodWind2085RCP4.5 | Collingwood | Wind | RCP4.5 | 2085 | 81.2282 | 87.4156 | 93.906 | 100.4191 | 106.9242
| CollingwoodWind2090RCP4.5 | Collingwood | Wind | RCP4.5 | 2090 | 81.2647 | 87.4695 | 93.9812 | 100.5129 | 107.035
| CollingwoodWind2095RCP4.5 | Collingwood | Wind | RCP4.5 | 2095 | 81.3013 | 87.5234 | 94.0564 | 100.6068 | 107.1457
| CollingwoodWind2100RCP4.5 | Collingwood | Wind | RCP4.5 | 2100 | 81.3378 | 87.5774 | 94.1316 | 100.7007 | 107.2564
| CollingwoodWind2023RCP6.0 | Collingwood | Wind | RCP6.0 | 2023 | 81.1673 | 87.3763 | 93.8966 | 100.4392 | 106.9671
| CollingwoodWind2025RCP6.0 | Collingwood | Wind | RCP6.0 | 2025 | 81.1633 | 87.369 | 93.8856 | 100.4224 | 106.9493
| CollingwoodWind2030RCP6.0 | Collingwood | Wind | RCP6.0 | 2030 | 81.1592 | 87.3617 | 93.8747 | 100.4057 | 106.9314
| CollingwoodWind2035RCP6.0 | Collingwood | Wind | RCP6.0 | 2035 | 81.1552 | 87.3544 | 93.8637 | 100.3889 | 106.9135
| CollingwoodWind2040RCP6.0 | Collingwood | Wind | RCP6.0 | 2040 | 81.1511 | 87.3472 | 93.8527 | 100.3721 | 106.8957
| CollingwoodWind2045RCP6.0 | Collingwood | Wind | RCP6.0 | 2045 | 81.1471 | 87.3399 | 93.8418 | 100.3554 | 106.8778
| CollingwoodWind2050RCP6.0 | Collingwood | Wind | RCP6.0 | 2050 | 81.1381 | 87.3168 | 93.8007 | 100.2984 | 106.8064
| CollingwoodWind2055RCP6.0 | Collingwood | Wind | RCP6.0 | 2055 | 81.1333 | 87.3011 | 93.7706 | 100.2581 | 106.7528
| CollingwoodWind2060RCP6.0 | Collingwood | Wind | RCP6.0 | 2060 | 81.1284 | 87.2854 | 93.7406 | 100.2179 | 106.6992
| CollingwoodWind2065RCP6.0 | Collingwood | Wind | RCP6.0 | 2065 | 81.1235 | 87.2696 | 93.7105 | 100.1777 | 106.6456
| CollingwoodWind2070RCP6.0 | Collingwood | Wind | RCP6.0 | 2070 | 81.1186 | 87.2539 | 93.6804 | 100.1374 | 106.5921
| CollingwoodWind2075RCP6.0 | Collingwood | Wind | RCP6.0 | 2075 | 81.1734 | 87.3348 | 93.7932 | 100.2783 | 106.7582
| CollingwoodWind2080RCP6.0 | Collingwood | Wind | RCP6.0 | 2080 | 81.2282 | 87.4156 | 93.906 | 100.4191 | 106.9242
| CollingwoodWind2085RCP6.0 | Collingwood | Wind | RCP6.0 | 2085 | 81.283 | 87.4965 | 94.0188 | 100.5599 | 107.0903
| CollingwoodWind2090RCP6.0 | Collingwood | Wind | RCP6.0 | 2090 | 81.5434 | 87.825 | 94.4324 | 101.0427 | 107.6458
| CollingwoodWind2095RCP6.0 | Collingwood | Wind | RCP6.0 | 2095 | 81.749 | 88.0727 | 94.7332 | 101.3846 | 108.0351
| CollingwoodWind2100RCP6.0 | Collingwood | Wind | RCP6.0 | 2100 | 81.9547 | 88.3204 | 95.034 | 101.7266 | 108.4245
| CollingwoodWind2023RCP8.5 | Collingwood | Wind | RCP8.5 | 2023 | 81.1673 | 87.3763 | 93.8966 | 100.4392 | 106.9671
| CollingwoodWind2025RCP8.5 | Collingwood | Wind | RCP8.5 | 2025 | 81.1592 | 87.3617 | 93.8747 | 100.4057 | 106.9314
| CollingwoodWind2030RCP8.5 | Collingwood | Wind | RCP8.5 | 2030 | 81.1511 | 87.3472 | 93.8527 | 100.3721 | 106.8957
| CollingwoodWind2035RCP8.5 | Collingwood | Wind | RCP8.5 | 2035 | 81.143 | 87.3326 | 93.8308 | 100.3386 | 106.86
| CollingwoodWind2040RCP8.5 | Collingwood | Wind | RCP8.5 | 2040 | 81.1349 | 87.3064 | 93.7807 | 100.2716 | 106.7707
| CollingwoodWind2045RCP8.5 | Collingwood | Wind | RCP8.5 | 2045 | 81.1268 | 87.2801 | 93.7305 | 100.2045 | 106.6814
| CollingwoodWind2050RCP8.5 | Collingwood | Wind | RCP8.5 | 2050 | 81.1917 | 87.3617 | 93.8308 | 100.3252 | 106.8135
| CollingwoodWind2055RCP8.5 | Collingwood | Wind | RCP8.5 | 2055 | 81.2647 | 87.4695 | 93.9812 | 100.5129 | 107.035
| CollingwoodWind2060RCP8.5 | Collingwood | Wind | RCP8.5 | 2060 | 81.5434 | 87.825 | 94.4324 | 101.0427 | 107.6458
| CollingwoodWind2065RCP8.5 | Collingwood | Wind | RCP8.5 | 2065 | 81.749 | 88.0727 | 94.7332 | 101.3846 | 108.0351
| CollingwoodWind2070RCP8.5 | Collingwood | Wind | RCP8.5 | 2070 | 82.0602 | 88.4486 | 95.1875 | 101.9043 | 108.6245
| CollingwoodWind2075RCP8.5 | Collingwood | Wind | RCP8.5 | 2075 | 82.1657 | 88.5769 | 95.3411 | 102.082 | 108.8246
| CollingwoodWind2080RCP8.5 | Collingwood | Wind | RCP8.5 | 2080 | 82.2712 | 88.7051 | 95.4946 | 102.2597 | 109.0246
| CollingwoodWind2085RCP8.5 | Collingwood | Wind | RCP8.5 | 2085 | 82.3727 | 88.8275 | 95.645 | 102.4307 | 109.2175
| CollingwoodWind2090RCP8.5 | Collingwood | Wind | RCP8.5 | 2090 | 82.4741 | 88.9499 | 95.7954 | 102.6017 | 109.4104
| CollingwoodWind2095RCP8.5 | Collingwood | Wind | RCP8.5 | 2095 | 82.4741 | 88.9499 | 95.7954 | 102.6017 | 109.4104
| CollingwoodWind2100RCP8.5 | Collingwood | Wind | RCP8.5 | 2100 | 82.4741 | 88.9499 | 95.7954 | 102.6017 | 109.4104
| CornwallIce Accretion2023RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2023 | 21.0215 | 25.0743 | 30.21 | 34.1373 | 38.0646
| CornwallIce Accretion2025RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2025 | 21.0737 | 25.1531 | 30.325 | 34.2842 | 38.2347
| CornwallIce Accretion2030RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2030 | 21.1259 | 25.232 | 30.44 | 34.4311 | 38.4048
| CornwallIce Accretion2035RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2035 | 21.1781 | 25.3108 | 30.555 | 34.578 | 38.5749
| CornwallIce Accretion2040RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2040 | 21.2303 | 25.3897 | 30.67 | 34.7249 | 38.745
| CornwallIce Accretion2045RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2045 | 21.2825 | 25.4686 | 30.785 | 34.8718 | 38.9151
| CornwallIce Accretion2050RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2050 | 21.3054 | 25.5325 | 30.9 | 35.0187 | 39.1003
| CornwallIce Accretion2055RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2055 | 21.2762 | 25.5175 | 30.9 | 35.0187 | 39.1154
| CornwallIce Accretion2060RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2060 | 21.247 | 25.5026 | 30.9 | 35.0187 | 39.1306
| CornwallIce Accretion2065RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2065 | 21.2177 | 25.4876 | 30.9 | 35.0187 | 39.1457
| CornwallIce Accretion2070RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2070 | 21.1885 | 25.4727 | 30.9 | 35.0187 | 39.1608
| CornwallIce Accretion2075RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2075 | 21.2859 | 25.6138 | 31.1 | 35.2616 | 39.4443
| CornwallIce Accretion2080RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2080 | 21.3834 | 25.7549 | 31.3 | 35.5046 | 39.7278
| CornwallIce Accretion2085RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2085 | 21.4808 | 25.896 | 31.5 | 35.7475 | 40.0113
| CornwallIce Accretion2090RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2090 | 21.5782 | 26.0371 | 31.7 | 35.9905 | 40.2948
| CornwallIce Accretion2095RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2095 | 21.6756 | 26.1782 | 31.9 | 36.2334 | 40.5783
| CornwallIce Accretion2100RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2100 | 21.773 | 26.3193 | 32.1 | 36.4764 | 40.8618
| CornwallIce Accretion2023RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2023 | 21.0215 | 25.0743 | 30.21 | 34.1373 | 38.0646
| CornwallIce Accretion2025RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2025 | 21.0737 | 25.1531 | 30.325 | 34.2842 | 38.2347
| CornwallIce Accretion2030RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2030 | 21.1259 | 25.232 | 30.44 | 34.4311 | 38.4048
| CornwallIce Accretion2035RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2035 | 21.1781 | 25.3108 | 30.555 | 34.578 | 38.5749
| CornwallIce Accretion2040RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2040 | 21.2303 | 25.3897 | 30.67 | 34.7249 | 38.745
| CornwallIce Accretion2045RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2045 | 21.2825 | 25.4686 | 30.785 | 34.8718 | 38.9151
| CornwallIce Accretion2050RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2050 | 21.3054 | 25.5325 | 30.9 | 35.0187 | 39.1003
| CornwallIce Accretion2055RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2055 | 21.2762 | 25.5175 | 30.9 | 35.0187 | 39.1154
| CornwallIce Accretion2060RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2060 | 21.247 | 25.5026 | 30.9 | 35.0187 | 39.1306
| CornwallIce Accretion2065RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2065 | 21.2177 | 25.4876 | 30.9 | 35.0187 | 39.1457
| CornwallIce Accretion2070RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2070 | 21.1885 | 25.4727 | 30.9 | 35.0187 | 39.1608
| CornwallIce Accretion2075RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2075 | 21.3346 | 25.6843 | 31.2 | 35.3831 | 39.586
| CornwallIce Accretion2080RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2080 | 21.4808 | 25.896 | 31.5 | 35.7475 | 40.0113
| CornwallIce Accretion2085RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2085 | 21.6269 | 26.1076 | 31.8 | 36.112 | 40.4365
| CornwallIce Accretion2090RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2090 | 21.6269 | 26.1948 | 31.98 | 36.3634 | 40.761
| CornwallIce Accretion2095RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2095 | 21.4808 | 26.0703 | 31.86 | 36.2504 | 40.6602
| CornwallIce Accretion2100RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2100 | 21.3346 | 25.9458 | 31.74 | 36.1374 | 40.5594
| CornwallIce Accretion2023RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2023 | 21.0215 | 25.0743 | 30.21 | 34.1373 | 38.0646
| CornwallIce Accretion2025RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2025 | 21.1259 | 25.232 | 30.44 | 34.4311 | 38.4048
| CornwallIce Accretion2030RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2030 | 21.2303 | 25.3897 | 30.67 | 34.7249 | 38.745
| CornwallIce Accretion2035RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2035 | 21.3346 | 25.5474 | 30.9 | 35.0187 | 39.0852
| CornwallIce Accretion2040RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2040 | 21.2859 | 25.5225 | 30.9 | 35.0187 | 39.1104
| CornwallIce Accretion2045RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2045 | 21.2372 | 25.4976 | 30.9 | 35.0187 | 39.1356
| CornwallIce Accretion2050RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2050 | 21.3834 | 25.7549 | 31.3 | 35.5046 | 39.7278
| CornwallIce Accretion2055RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2055 | 21.5782 | 26.0371 | 31.7 | 35.9905 | 40.2948
| CornwallIce Accretion2060RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2060 | 21.6269 | 26.1948 | 31.98 | 36.3634 | 40.761
| CornwallIce Accretion2065RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2065 | 21.4808 | 26.0703 | 31.86 | 36.2504 | 40.6602
| CornwallIce Accretion2070RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2070 | 21.0563 | 25.6387 | 31.4 | 35.7758 | 40.1688
| CornwallIce Accretion2075RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2075 | 20.778 | 25.3316 | 31.06 | 35.4142 | 39.7782
| CornwallIce Accretion2080RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2080 | 20.4996 | 25.0245 | 30.72 | 35.0526 | 39.3876
| CornwallIce Accretion2085RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2085 | 19.6333 | 24.0036 | 29.52 | 33.6966 | 37.8756
| CornwallIce Accretion2090RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2090 | 18.767 | 22.9827 | 28.32 | 32.3406 | 36.3636
| CornwallIce Accretion2095RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2095 | 18.767 | 22.9827 | 28.32 | 32.3406 | 36.3636
| CornwallIce Accretion2100RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2100 | 18.767 | 22.9827 | 28.32 | 32.3406 | 36.3636
| CornwallWind2023RCP4.5 | Cornwall | Wind | RCP4.5 | 2023 | 81.8005 | 88.1806 | 94.9024 | 101.616 | 108.3173
| CornwallWind2025RCP4.5 | Cornwall | Wind | RCP4.5 | 2025 | 81.8437 | 88.2214 | 94.9416 | 101.6545 | 108.3548
| CornwallWind2030RCP4.5 | Cornwall | Wind | RCP4.5 | 2030 | 81.887 | 88.2621 | 94.9807 | 101.6931 | 108.3923
| CornwallWind2035RCP4.5 | Cornwall | Wind | RCP4.5 | 2035 | 81.9303 | 88.3029 | 95.0199 | 101.7316 | 108.4298
| CornwallWind2040RCP4.5 | Cornwall | Wind | RCP4.5 | 2040 | 81.9736 | 88.3437 | 95.0591 | 101.7702 | 108.4674
| CornwallWind2045RCP4.5 | Cornwall | Wind | RCP4.5 | 2045 | 82.0169 | 88.3845 | 95.0982 | 101.8088 | 108.5049
| CornwallWind2050RCP4.5 | Cornwall | Wind | RCP4.5 | 2050 | 82.0358 | 88.3956 | 95.1017 | 101.8031 | 108.4931
| CornwallWind2055RCP4.5 | Cornwall | Wind | RCP4.5 | 2055 | 82.0115 | 88.3659 | 95.066 | 101.7588 | 108.4438
| CornwallWind2060RCP4.5 | Cornwall | Wind | RCP4.5 | 2060 | 81.9871 | 88.3362 | 95.0302 | 101.7145 | 108.3945
| CornwallWind2065RCP4.5 | Cornwall | Wind | RCP4.5 | 2065 | 81.9628 | 88.3064 | 94.9945 | 101.6703 | 108.3452
| CornwallWind2070RCP4.5 | Cornwall | Wind | RCP4.5 | 2070 | 81.9384 | 88.2767 | 94.9588 | 101.626 | 108.2959
| CornwallWind2075RCP4.5 | Cornwall | Wind | RCP4.5 | 2075 | 81.9181 | 88.2549 | 94.9353 | 101.6026 | 108.2709
| CornwallWind2080RCP4.5 | Cornwall | Wind | RCP4.5 | 2080 | 81.8979 | 88.233 | 94.9118 | 101.5791 | 108.2459
| CornwallWind2085RCP4.5 | Cornwall | Wind | RCP4.5 | 2085 | 81.8776 | 88.2112 | 94.8883 | 101.5556 | 108.2209
| CornwallWind2090RCP4.5 | Cornwall | Wind | RCP4.5 | 2090 | 81.8573 | 88.1893 | 94.8648 | 101.5322 | 108.1959
| CornwallWind2095RCP4.5 | Cornwall | Wind | RCP4.5 | 2095 | 81.837 | 88.1674 | 94.8413 | 101.5087 | 108.1709
| CornwallWind2100RCP4.5 | Cornwall | Wind | RCP4.5 | 2100 | 81.8167 | 88.1456 | 94.8178 | 101.4852 | 108.1459
| CornwallWind2023RCP6.0 | Cornwall | Wind | RCP6.0 | 2023 | 81.8005 | 88.1806 | 94.9024 | 101.616 | 108.3173
| CornwallWind2025RCP6.0 | Cornwall | Wind | RCP6.0 | 2025 | 81.8437 | 88.2214 | 94.9416 | 101.6545 | 108.3548
| CornwallWind2030RCP6.0 | Cornwall | Wind | RCP6.0 | 2030 | 81.887 | 88.2621 | 94.9807 | 101.6931 | 108.3923
| CornwallWind2035RCP6.0 | Cornwall | Wind | RCP6.0 | 2035 | 81.9303 | 88.3029 | 95.0199 | 101.7316 | 108.4298
| CornwallWind2040RCP6.0 | Cornwall | Wind | RCP6.0 | 2040 | 81.9736 | 88.3437 | 95.0591 | 101.7702 | 108.4674
| CornwallWind2045RCP6.0 | Cornwall | Wind | RCP6.0 | 2045 | 82.0169 | 88.3845 | 95.0982 | 101.8088 | 108.5049
| CornwallWind2050RCP6.0 | Cornwall | Wind | RCP6.0 | 2050 | 82.0358 | 88.3956 | 95.1017 | 101.8031 | 108.4931
| CornwallWind2055RCP6.0 | Cornwall | Wind | RCP6.0 | 2055 | 82.0115 | 88.3659 | 95.066 | 101.7588 | 108.4438
| CornwallWind2060RCP6.0 | Cornwall | Wind | RCP6.0 | 2060 | 81.9871 | 88.3362 | 95.0302 | 101.7145 | 108.3945
| CornwallWind2065RCP6.0 | Cornwall | Wind | RCP6.0 | 2065 | 81.9628 | 88.3064 | 94.9945 | 101.6703 | 108.3452
| CornwallWind2070RCP6.0 | Cornwall | Wind | RCP6.0 | 2070 | 81.9384 | 88.2767 | 94.9588 | 101.626 | 108.2959
| CornwallWind2075RCP6.0 | Cornwall | Wind | RCP6.0 | 2075 | 81.908 | 88.2439 | 94.9235 | 101.5908 | 108.2584
| CornwallWind2080RCP6.0 | Cornwall | Wind | RCP6.0 | 2080 | 81.8776 | 88.2112 | 94.8883 | 101.5556 | 108.2209
| CornwallWind2085RCP6.0 | Cornwall | Wind | RCP6.0 | 2085 | 81.8471 | 88.1784 | 94.853 | 101.5204 | 108.1834
| CornwallWind2090RCP6.0 | Cornwall | Wind | RCP6.0 | 2090 | 81.7653 | 88.0844 | 94.7426 | 101.3981 | 108.0494
| CornwallWind2095RCP6.0 | Cornwall | Wind | RCP6.0 | 2095 | 81.7139 | 88.0232 | 94.6674 | 101.3109 | 107.953
| CornwallWind2100RCP6.0 | Cornwall | Wind | RCP6.0 | 2100 | 81.6625 | 87.962 | 94.5922 | 101.2237 | 107.8565
| CornwallWind2023RCP8.5 | Cornwall | Wind | RCP8.5 | 2023 | 81.8005 | 88.1806 | 94.9024 | 101.616 | 108.3173
| CornwallWind2025RCP8.5 | Cornwall | Wind | RCP8.5 | 2025 | 81.887 | 88.2621 | 94.9807 | 101.6931 | 108.3923
| CornwallWind2030RCP8.5 | Cornwall | Wind | RCP8.5 | 2030 | 81.9736 | 88.3437 | 95.0591 | 101.7702 | 108.4674
| CornwallWind2035RCP8.5 | Cornwall | Wind | RCP8.5 | 2035 | 82.0602 | 88.4253 | 95.1374 | 101.8473 | 108.5424
| CornwallWind2040RCP8.5 | Cornwall | Wind | RCP8.5 | 2040 | 82.0196 | 88.3758 | 95.0779 | 101.7735 | 108.4602
| CornwallWind2045RCP8.5 | Cornwall | Wind | RCP8.5 | 2045 | 81.979 | 88.3263 | 95.0183 | 101.6998 | 108.3781
| CornwallWind2050RCP8.5 | Cornwall | Wind | RCP8.5 | 2050 | 81.8979 | 88.233 | 94.9118 | 101.5791 | 108.2459
| CornwallWind2055RCP8.5 | Cornwall | Wind | RCP8.5 | 2055 | 81.8573 | 88.1893 | 94.8648 | 101.5322 | 108.1959
| CornwallWind2060RCP8.5 | Cornwall | Wind | RCP8.5 | 2060 | 81.7653 | 88.0844 | 94.7426 | 101.3981 | 108.0494
| CornwallWind2065RCP8.5 | Cornwall | Wind | RCP8.5 | 2065 | 81.7139 | 88.0232 | 94.6674 | 101.3109 | 107.953
| CornwallWind2070RCP8.5 | Cornwall | Wind | RCP8.5 | 2070 | 81.8221 | 88.1747 | 94.8711 | 101.559 | 108.2459
| CornwallWind2075RCP8.5 | Cornwall | Wind | RCP8.5 | 2075 | 81.9817 | 88.3874 | 95.1499 | 101.8942 | 108.6352
| CornwallWind2080RCP8.5 | Cornwall | Wind | RCP8.5 | 2080 | 82.1414 | 88.6002 | 95.4288 | 102.2295 | 109.0246
| CornwallWind2085RCP8.5 | Cornwall | Wind | RCP8.5 | 2085 | 82.0196 | 88.421 | 95.1797 | 101.9227 | 108.6549
| CornwallWind2090RCP8.5 | Cornwall | Wind | RCP8.5 | 2090 | 81.8979 | 88.2417 | 94.9306 | 101.616 | 108.2852
| CornwallWind2095RCP8.5 | Cornwall | Wind | RCP8.5 | 2095 | 81.8979 | 88.2417 | 94.9306 | 101.616 | 108.2852
| CornwallWind2100RCP8.5 | Cornwall | Wind | RCP8.5 | 2100 | 81.8979 | 88.2417 | 94.9306 | 101.616 | 108.2852
| CorunnaIce Accretion2023RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2023 | 14.5432 | 17.4931 | 21.208 | 24.0396 | 26.8607
| CorunnaIce Accretion2025RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2025 | 14.5917 | 17.56 | 21.3033 | 24.1515 | 26.9947
| CorunnaIce Accretion2030RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2030 | 14.6401 | 17.627 | 21.3987 | 24.2634 | 27.1286
| CorunnaIce Accretion2035RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2035 | 14.6886 | 17.6939 | 21.494 | 24.3752 | 27.2626
| CorunnaIce Accretion2040RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2040 | 14.7371 | 17.7609 | 21.5893 | 24.4871 | 27.3966
| CorunnaIce Accretion2045RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2045 | 14.7856 | 17.8278 | 21.6847 | 24.599 | 27.5306
| CorunnaIce Accretion2050RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2050 | 14.6167 | 17.6647 | 21.5248 | 24.4374 | 27.3707
| CorunnaIce Accretion2055RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2055 | 14.3993 | 17.4346 | 21.2696 | 24.1639 | 27.0769
| CorunnaIce Accretion2060RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2060 | 14.1819 | 17.2046 | 21.0144 | 23.8905 | 26.7831
| CorunnaIce Accretion2065RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2065 | 13.9645 | 16.9745 | 20.7592 | 23.617 | 26.4892
| CorunnaIce Accretion2070RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2070 | 13.7471 | 16.7444 | 20.504 | 23.3435 | 26.1954
| CorunnaIce Accretion2075RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2075 | 13.5047 | 16.4675 | 20.1813 | 22.9914 | 25.8073
| CorunnaIce Accretion2080RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2080 | 13.2624 | 16.1905 | 19.8587 | 22.6392 | 25.4192
| CorunnaIce Accretion2085RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2085 | 13.02 | 15.9136 | 19.536 | 22.287 | 25.0312
| CorunnaIce Accretion2090RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2090 | 12.7776 | 15.6366 | 19.2133 | 21.9348 | 24.6431
| CorunnaIce Accretion2095RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2095 | 12.5352 | 15.3597 | 18.8907 | 21.5826 | 24.255
| CorunnaIce Accretion2100RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2100 | 12.2928 | 15.0828 | 18.568 | 21.2304 | 23.8669
| CorunnaIce Accretion2023RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2023 | 14.5432 | 17.4931 | 21.208 | 24.0396 | 26.8607
| CorunnaIce Accretion2025RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2025 | 14.5917 | 17.56 | 21.3033 | 24.1515 | 26.9947
| CorunnaIce Accretion2030RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2030 | 14.6401 | 17.627 | 21.3987 | 24.2634 | 27.1286
| CorunnaIce Accretion2035RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2035 | 14.6886 | 17.6939 | 21.494 | 24.3752 | 27.2626
| CorunnaIce Accretion2040RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2040 | 14.7371 | 17.7609 | 21.5893 | 24.4871 | 27.3966
| CorunnaIce Accretion2045RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2045 | 14.7856 | 17.8278 | 21.6847 | 24.599 | 27.5306
| CorunnaIce Accretion2050RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2050 | 14.6167 | 17.6647 | 21.5248 | 24.4374 | 27.3707
| CorunnaIce Accretion2055RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2055 | 14.3993 | 17.4346 | 21.2696 | 24.1639 | 27.0769
| CorunnaIce Accretion2060RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2060 | 14.1819 | 17.2046 | 21.0144 | 23.8905 | 26.7831
| CorunnaIce Accretion2065RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2065 | 13.9645 | 16.9745 | 20.7592 | 23.617 | 26.4892
| CorunnaIce Accretion2070RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2070 | 13.7471 | 16.7444 | 20.504 | 23.3435 | 26.1954
| CorunnaIce Accretion2075RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2075 | 13.3836 | 16.329 | 20.02 | 22.8153 | 25.6133
| CorunnaIce Accretion2080RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2080 | 13.02 | 15.9136 | 19.536 | 22.287 | 25.0312
| CorunnaIce Accretion2085RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2085 | 12.6564 | 15.4982 | 19.052 | 21.7587 | 24.449
| CorunnaIce Accretion2090RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2090 | 11.7774 | 14.4802 | 17.864 | 20.4349 | 22.9891
| CorunnaIce Accretion2095RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2095 | 11.262 | 13.8776 | 17.16 | 19.6394 | 22.1113
| CorunnaIce Accretion2100RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2100 | 10.7466 | 13.275 | 16.456 | 18.8439 | 21.2335
| CorunnaIce Accretion2023RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2023 | 14.5432 | 17.4931 | 21.208 | 24.0396 | 26.8607
| CorunnaIce Accretion2025RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2025 | 14.6401 | 17.627 | 21.3987 | 24.2634 | 27.1286
| CorunnaIce Accretion2030RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2030 | 14.7371 | 17.7609 | 21.5893 | 24.4871 | 27.3966
| CorunnaIce Accretion2035RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2035 | 14.834 | 17.8948 | 21.78 | 24.7108 | 27.6646
| CorunnaIce Accretion2040RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2040 | 14.4717 | 17.5113 | 21.3547 | 24.2551 | 27.1748
| CorunnaIce Accretion2045RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2045 | 14.1094 | 17.1279 | 20.9293 | 23.7993 | 26.6851
| CorunnaIce Accretion2050RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2050 | 13.2624 | 16.1905 | 19.8587 | 22.6392 | 25.4192
| CorunnaIce Accretion2055RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2055 | 12.7776 | 15.6366 | 19.2133 | 21.9348 | 24.6431
| CorunnaIce Accretion2060RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2060 | 11.7774 | 14.4802 | 17.864 | 20.4349 | 22.9891
| CorunnaIce Accretion2065RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2065 | 11.262 | 13.8776 | 17.16 | 19.6394 | 22.1113
| CorunnaIce Accretion2070RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2070 | 10.3231 | 12.7942 | 15.8987 | 18.2307 | 20.559
| CorunnaIce Accretion2075RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2075 | 9.8996 | 12.3133 | 15.3413 | 17.6175 | 19.8845
| CorunnaIce Accretion2080RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2080 | 9.476 | 11.8325 | 14.784 | 17.0042 | 19.21
| CorunnaIce Accretion2085RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2085 | 8.6647 | 10.8647 | 13.596 | 15.6618 | 17.7131
| CorunnaIce Accretion2090RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2090 | 7.8533 | 9.8969 | 12.408 | 14.3194 | 16.2162
| CorunnaIce Accretion2095RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2095 | 7.8533 | 9.8969 | 12.408 | 14.3194 | 16.2162
| CorunnaIce Accretion2100RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2100 | 7.8533 | 9.8969 | 12.408 | 14.3194 | 16.2162
| CorunnaWind2023RCP4.5 | Corunna | Wind | RCP4.5 | 2023 | 85.0444 | 91.6139 | 98.5292 | 105.4367 | 112.3456
| CorunnaWind2025RCP4.5 | Corunna | Wind | RCP4.5 | 2025 | 85.105 | 91.6838 | 98.6109 | 105.5311 | 112.4499
| CorunnaWind2030RCP4.5 | Corunna | Wind | RCP4.5 | 2030 | 85.1657 | 91.7537 | 98.6925 | 105.6255 | 112.5542
| CorunnaWind2035RCP4.5 | Corunna | Wind | RCP4.5 | 2035 | 85.2263 | 91.8236 | 98.7742 | 105.7199 | 112.6584
| CorunnaWind2040RCP4.5 | Corunna | Wind | RCP4.5 | 2040 | 85.287 | 91.8934 | 98.8559 | 105.8142 | 112.7627
| CorunnaWind2045RCP4.5 | Corunna | Wind | RCP4.5 | 2045 | 85.3476 | 91.9633 | 98.9375 | 105.9086 | 112.867
| CorunnaWind2050RCP4.5 | Corunna | Wind | RCP4.5 | 2050 | 85.4083 | 92.0332 | 99.0192 | 106.0009 | 112.9713
| CorunnaWind2055RCP4.5 | Corunna | Wind | RCP4.5 | 2055 | 85.4083 | 92.0332 | 99.0192 | 105.9988 | 112.9713
| CorunnaWind2060RCP4.5 | Corunna | Wind | RCP4.5 | 2060 | 85.4083 | 92.0332 | 99.0192 | 105.9967 | 112.9713
| CorunnaWind2065RCP4.5 | Corunna | Wind | RCP4.5 | 2065 | 85.4083 | 92.0332 | 99.0192 | 105.9946 | 112.9713
| CorunnaWind2070RCP4.5 | Corunna | Wind | RCP4.5 | 2070 | 85.4083 | 92.0332 | 99.0192 | 105.9925 | 112.9713
| CorunnaWind2075RCP4.5 | Corunna | Wind | RCP4.5 | 2075 | 85.538 | 92.1957 | 99.2201 | 106.2284 | 113.2413
| CorunnaWind2080RCP4.5 | Corunna | Wind | RCP4.5 | 2080 | 85.6678 | 92.3582 | 99.421 | 106.4644 | 113.5112
| CorunnaWind2085RCP4.5 | Corunna | Wind | RCP4.5 | 2085 | 85.7975 | 92.5208 | 99.6219 | 106.7003 | 113.7812
| CorunnaWind2090RCP4.5 | Corunna | Wind | RCP4.5 | 2090 | 85.9273 | 92.6833 | 99.8228 | 106.9362 | 114.0512
| CorunnaWind2095RCP4.5 | Corunna | Wind | RCP4.5 | 2095 | 86.057 | 92.8458 | 100.0237 | 107.1722 | 114.3212
| CorunnaWind2100RCP4.5 | Corunna | Wind | RCP4.5 | 2100 | 86.1868 | 93.0084 | 100.2246 | 107.4081 | 114.5912
| CorunnaWind2023RCP6.0 | Corunna | Wind | RCP6.0 | 2023 | 85.0444 | 91.6139 | 98.5292 | 105.4367 | 112.3456
| CorunnaWind2025RCP6.0 | Corunna | Wind | RCP6.0 | 2025 | 85.105 | 91.6838 | 98.6109 | 105.5311 | 112.4499
| CorunnaWind2030RCP6.0 | Corunna | Wind | RCP6.0 | 2030 | 85.1657 | 91.7537 | 98.6925 | 105.6255 | 112.5542
| CorunnaWind2035RCP6.0 | Corunna | Wind | RCP6.0 | 2035 | 85.2263 | 91.8236 | 98.7742 | 105.7199 | 112.6584
| CorunnaWind2040RCP6.0 | Corunna | Wind | RCP6.0 | 2040 | 85.287 | 91.8934 | 98.8559 | 105.8142 | 112.7627
| CorunnaWind2045RCP6.0 | Corunna | Wind | RCP6.0 | 2045 | 85.3476 | 91.9633 | 98.9375 | 105.9086 | 112.867
| CorunnaWind2050RCP6.0 | Corunna | Wind | RCP6.0 | 2050 | 85.4083 | 92.0332 | 99.0192 | 106.0009 | 112.9713
| CorunnaWind2055RCP6.0 | Corunna | Wind | RCP6.0 | 2055 | 85.4083 | 92.0332 | 99.0192 | 105.9988 | 112.9713
| CorunnaWind2060RCP6.0 | Corunna | Wind | RCP6.0 | 2060 | 85.4083 | 92.0332 | 99.0192 | 105.9967 | 112.9713
| CorunnaWind2065RCP6.0 | Corunna | Wind | RCP6.0 | 2065 | 85.4083 | 92.0332 | 99.0192 | 105.9946 | 112.9713
| CorunnaWind2070RCP6.0 | Corunna | Wind | RCP6.0 | 2070 | 85.4083 | 92.0332 | 99.0192 | 105.9925 | 112.9713
| CorunnaWind2075RCP6.0 | Corunna | Wind | RCP6.0 | 2075 | 85.6029 | 92.277 | 99.3205 | 106.3464 | 113.3762
| CorunnaWind2080RCP6.0 | Corunna | Wind | RCP6.0 | 2080 | 85.7975 | 92.5208 | 99.6219 | 106.7003 | 113.7812
| CorunnaWind2085RCP6.0 | Corunna | Wind | RCP6.0 | 2085 | 85.9921 | 92.7646 | 99.9232 | 107.0542 | 114.1862
| CorunnaWind2090RCP6.0 | Corunna | Wind | RCP6.0 | 2090 | 86.4463 | 93.3304 | 100.6264 | 107.8765 | 115.1275
| CorunnaWind2095RCP6.0 | Corunna | Wind | RCP6.0 | 2095 | 86.7058 | 93.6524 | 101.0282 | 108.3448 | 115.6637
| CorunnaWind2100RCP6.0 | Corunna | Wind | RCP6.0 | 2100 | 86.9653 | 93.9745 | 101.43 | 108.8132 | 116.2
| CorunnaWind2023RCP8.5 | Corunna | Wind | RCP8.5 | 2023 | 85.0444 | 91.6139 | 98.5292 | 105.4367 | 112.3456
| CorunnaWind2025RCP8.5 | Corunna | Wind | RCP8.5 | 2025 | 85.1657 | 91.7537 | 98.6925 | 105.6255 | 112.5542
| CorunnaWind2030RCP8.5 | Corunna | Wind | RCP8.5 | 2030 | 85.287 | 91.8934 | 98.8559 | 105.8142 | 112.7627
| CorunnaWind2035RCP8.5 | Corunna | Wind | RCP8.5 | 2035 | 85.4083 | 92.0332 | 99.0192 | 106.003 | 112.9713
| CorunnaWind2040RCP8.5 | Corunna | Wind | RCP8.5 | 2040 | 85.4083 | 92.0332 | 99.0192 | 105.9995 | 112.9713
| CorunnaWind2045RCP8.5 | Corunna | Wind | RCP8.5 | 2045 | 85.4083 | 92.0332 | 99.0192 | 105.996 | 112.9713
| CorunnaWind2050RCP8.5 | Corunna | Wind | RCP8.5 | 2050 | 85.6678 | 92.3582 | 99.421 | 106.4644 | 113.5112
| CorunnaWind2055RCP8.5 | Corunna | Wind | RCP8.5 | 2055 | 85.9273 | 92.6833 | 99.8228 | 106.9362 | 114.0512
| CorunnaWind2060RCP8.5 | Corunna | Wind | RCP8.5 | 2060 | 86.4463 | 93.3304 | 100.6264 | 107.8765 | 115.1275
| CorunnaWind2065RCP8.5 | Corunna | Wind | RCP8.5 | 2065 | 86.7058 | 93.6524 | 101.0282 | 108.3448 | 115.6637
| CorunnaWind2070RCP8.5 | Corunna | Wind | RCP8.5 | 2070 | 87.2474 | 94.3238 | 101.8612 | 109.3131 | 116.7697
| CorunnaWind2075RCP8.5 | Corunna | Wind | RCP8.5 | 2075 | 87.5294 | 94.6732 | 102.2924 | 109.8129 | 117.3395
| CorunnaWind2080RCP8.5 | Corunna | Wind | RCP8.5 | 2080 | 87.8115 | 95.0226 | 102.7236 | 110.3127 | 117.9093
| CorunnaWind2085RCP8.5 | Corunna | Wind | RCP8.5 | 2085 | 87.968 | 95.2367 | 103.0176 | 110.6692 | 118.3394
| CorunnaWind2090RCP8.5 | Corunna | Wind | RCP8.5 | 2090 | 88.1246 | 95.4509 | 103.3116 | 111.0258 | 118.7695
| CorunnaWind2095RCP8.5 | Corunna | Wind | RCP8.5 | 2095 | 88.1246 | 95.4509 | 103.3116 | 111.0258 | 118.7695
| CorunnaWind2100RCP8.5 | Corunna | Wind | RCP8.5 | 2100 | 88.1246 | 95.4509 | 103.3116 | 111.0258 | 118.7695
| Deep RiverIce Accretion2023RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2023 | 13.0012 | 15.5525 | 18.792 | 21.2756 | 23.746
| Deep RiverIce Accretion2025RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2025 | 13.0513 | 15.6123 | 18.861 | 21.3502 | 23.8291
| Deep RiverIce Accretion2030RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2030 | 13.1014 | 15.6721 | 18.93 | 21.4248 | 23.9123
| Deep RiverIce Accretion2035RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2035 | 13.1515 | 15.7318 | 18.999 | 21.4994 | 23.9954
| Deep RiverIce Accretion2040RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2040 | 13.2016 | 15.7916 | 19.068 | 21.574 | 24.0786
| Deep RiverIce Accretion2045RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2045 | 13.2517 | 15.8513 | 19.137 | 21.6485 | 24.1618
| Deep RiverIce Accretion2050RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2050 | 13.2993 | 15.9171 | 19.2276 | 21.7557 | 24.2903
| Deep RiverIce Accretion2055RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2055 | 13.2968 | 15.9231 | 19.2492 | 21.7882 | 24.3356
| Deep RiverIce Accretion2060RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2060 | 13.2943 | 15.929 | 19.2708 | 21.8208 | 24.381
| Deep RiverIce Accretion2065RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2065 | 13.2918 | 15.935 | 19.2924 | 21.8533 | 24.4264
| Deep RiverIce Accretion2070RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2070 | 13.2893 | 15.941 | 19.314 | 21.8858 | 24.4717
| Deep RiverIce Accretion2075RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2075 | 13.2747 | 15.931 | 19.311 | 21.8858 | 24.4717
| Deep RiverIce Accretion2080RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2080 | 13.26 | 15.9211 | 19.308 | 21.8858 | 24.4717
| Deep RiverIce Accretion2085RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2085 | 13.2454 | 15.9111 | 19.305 | 21.8858 | 24.4717
| Deep RiverIce Accretion2090RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2090 | 13.2308 | 15.9011 | 19.302 | 21.8858 | 24.4717
| Deep RiverIce Accretion2095RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2095 | 13.2162 | 15.8912 | 19.299 | 21.8858 | 24.4717
| Deep RiverIce Accretion2100RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2100 | 13.2016 | 15.8812 | 19.296 | 21.8858 | 24.4717
| Deep RiverIce Accretion2023RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2023 | 13.0012 | 15.5525 | 18.792 | 21.2756 | 23.746
| Deep RiverIce Accretion2025RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2025 | 13.0513 | 15.6123 | 18.861 | 21.3502 | 23.8291
| Deep RiverIce Accretion2030RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2030 | 13.1014 | 15.6721 | 18.93 | 21.4248 | 23.9123
| Deep RiverIce Accretion2035RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2035 | 13.1515 | 15.7318 | 18.999 | 21.4994 | 23.9954
| Deep RiverIce Accretion2040RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2040 | 13.2016 | 15.7916 | 19.068 | 21.574 | 24.0786
| Deep RiverIce Accretion2045RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2045 | 13.2517 | 15.8513 | 19.137 | 21.6485 | 24.1618
| Deep RiverIce Accretion2050RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2050 | 13.2993 | 15.9171 | 19.2276 | 21.7557 | 24.2903
| Deep RiverIce Accretion2055RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2055 | 13.2968 | 15.9231 | 19.2492 | 21.7882 | 24.3356
| Deep RiverIce Accretion2060RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2060 | 13.2943 | 15.929 | 19.2708 | 21.8208 | 24.381
| Deep RiverIce Accretion2065RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2065 | 13.2918 | 15.935 | 19.2924 | 21.8533 | 24.4264
| Deep RiverIce Accretion2070RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2070 | 13.2893 | 15.941 | 19.314 | 21.8858 | 24.4717
| Deep RiverIce Accretion2075RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2075 | 13.2673 | 15.926 | 19.3095 | 21.8858 | 24.4717
| Deep RiverIce Accretion2080RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2080 | 13.2454 | 15.9111 | 19.305 | 21.8858 | 24.4717
| Deep RiverIce Accretion2085RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2085 | 13.2235 | 15.8962 | 19.3005 | 21.8858 | 24.4717
| Deep RiverIce Accretion2090RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2090 | 13.2099 | 15.9211 | 19.374 | 22.0011 | 24.6229
| Deep RiverIce Accretion2095RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2095 | 13.2183 | 15.9609 | 19.452 | 22.1164 | 24.7741
| Deep RiverIce Accretion2100RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2100 | 13.2266 | 16.0007 | 19.53 | 22.2316 | 24.9253
| Deep RiverIce Accretion2023RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2023 | 13.0012 | 15.5525 | 18.792 | 21.2756 | 23.746
| Deep RiverIce Accretion2025RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2025 | 13.1014 | 15.6721 | 18.93 | 21.4248 | 23.9123
| Deep RiverIce Accretion2030RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2030 | 13.2016 | 15.7916 | 19.068 | 21.574 | 24.0786
| Deep RiverIce Accretion2035RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2035 | 13.3018 | 15.9111 | 19.206 | 21.7231 | 24.2449
| Deep RiverIce Accretion2040RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2040 | 13.2976 | 15.9211 | 19.242 | 21.7774 | 24.3205
| Deep RiverIce Accretion2045RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2045 | 13.2934 | 15.931 | 19.278 | 21.8316 | 24.3961
| Deep RiverIce Accretion2050RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2050 | 13.26 | 15.9211 | 19.308 | 21.8858 | 24.4717
| Deep RiverIce Accretion2055RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2055 | 13.2308 | 15.9011 | 19.302 | 21.8858 | 24.4717
| Deep RiverIce Accretion2060RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2060 | 13.2099 | 15.9211 | 19.374 | 22.0011 | 24.6229
| Deep RiverIce Accretion2065RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2065 | 13.2183 | 15.9609 | 19.452 | 22.1164 | 24.7741
| Deep RiverIce Accretion2070RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2070 | 13.2016 | 15.9908 | 19.53 | 22.2384 | 24.9404
| Deep RiverIce Accretion2075RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2075 | 13.1765 | 15.9808 | 19.53 | 22.2452 | 24.9556
| Deep RiverIce Accretion2080RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2080 | 13.1515 | 15.9709 | 19.53 | 22.252 | 24.9707
| Deep RiverIce Accretion2085RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2085 | 12.926 | 15.7243 | 19.26 | 21.957 | 24.6532
| Deep RiverIce Accretion2090RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2090 | 12.7006 | 15.4778 | 18.99 | 21.6621 | 24.3356
| Deep RiverIce Accretion2095RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2095 | 12.7006 | 15.4778 | 18.99 | 21.6621 | 24.3356
| Deep RiverIce Accretion2100RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2100 | 12.7006 | 15.4778 | 18.99 | 21.6621 | 24.3356
| Deep RiverWind2023RCP4.5 | Deep River | Wind | RCP4.5 | 2023 | 77.3571 | 83.2997 | 89.5429 | 95.7919 | 102.0383
| Deep RiverWind2025RCP4.5 | Deep River | Wind | RCP4.5 | 2025 | 77.4173 | 83.3604 | 89.6037 | 95.8538 | 102.1026
| Deep RiverWind2030RCP4.5 | Deep River | Wind | RCP4.5 | 2030 | 77.4775 | 83.4211 | 89.6645 | 95.9157 | 102.1668
| Deep RiverWind2035RCP4.5 | Deep River | Wind | RCP4.5 | 2035 | 77.5377 | 83.4818 | 89.7253 | 95.9776 | 102.2311
| Deep RiverWind2040RCP4.5 | Deep River | Wind | RCP4.5 | 2040 | 77.5979 | 83.5425 | 89.7862 | 96.0395 | 102.2954
| Deep RiverWind2045RCP4.5 | Deep River | Wind | RCP4.5 | 2045 | 77.6581 | 83.6032 | 89.847 | 96.1014 | 102.3596
| Deep RiverWind2050RCP4.5 | Deep River | Wind | RCP4.5 | 2050 | 77.7937 | 83.755 | 90.0164 | 96.289 | 102.5639
| Deep RiverWind2055RCP4.5 | Deep River | Wind | RCP4.5 | 2055 | 77.869 | 83.846 | 90.125 | 96.4147 | 102.7039
| Deep RiverWind2060RCP4.5 | Deep River | Wind | RCP4.5 | 2060 | 77.9443 | 83.9371 | 90.2335 | 96.5404 | 102.8439
| Deep RiverWind2065RCP4.5 | Deep River | Wind | RCP4.5 | 2065 | 78.0196 | 84.0281 | 90.3421 | 96.6661 | 102.9839
| Deep RiverWind2070RCP4.5 | Deep River | Wind | RCP4.5 | 2070 | 78.0949 | 84.1192 | 90.4507 | 96.7918 | 103.1239
| Deep RiverWind2075RCP4.5 | Deep River | Wind | RCP4.5 | 2075 | 78.1884 | 84.2336 | 90.5916 | 96.9537 | 103.31
| Deep RiverWind2080RCP4.5 | Deep River | Wind | RCP4.5 | 2080 | 78.2819 | 84.3481 | 90.7325 | 97.1156 | 103.496
| Deep RiverWind2085RCP4.5 | Deep River | Wind | RCP4.5 | 2085 | 78.3754 | 84.4626 | 90.8734 | 97.2774 | 103.682
| Deep RiverWind2090RCP4.5 | Deep River | Wind | RCP4.5 | 2090 | 78.4689 | 84.5771 | 91.0144 | 97.4393 | 103.868
| Deep RiverWind2095RCP4.5 | Deep River | Wind | RCP4.5 | 2095 | 78.5624 | 84.6916 | 91.1553 | 97.6012 | 104.054
| Deep RiverWind2100RCP4.5 | Deep River | Wind | RCP4.5 | 2100 | 78.6559 | 84.8061 | 91.2962 | 97.7631 | 104.24
| Deep RiverWind2023RCP6.0 | Deep River | Wind | RCP6.0 | 2023 | 77.3571 | 83.2997 | 89.5429 | 95.7919 | 102.0383
| Deep RiverWind2025RCP6.0 | Deep River | Wind | RCP6.0 | 2025 | 77.4173 | 83.3604 | 89.6037 | 95.8538 | 102.1026
| Deep RiverWind2030RCP6.0 | Deep River | Wind | RCP6.0 | 2030 | 77.4775 | 83.4211 | 89.6645 | 95.9157 | 102.1668
| Deep RiverWind2035RCP6.0 | Deep River | Wind | RCP6.0 | 2035 | 77.5377 | 83.4818 | 89.7253 | 95.9776 | 102.2311
| Deep RiverWind2040RCP6.0 | Deep River | Wind | RCP6.0 | 2040 | 77.5979 | 83.5425 | 89.7862 | 96.0395 | 102.2954
| Deep RiverWind2045RCP6.0 | Deep River | Wind | RCP6.0 | 2045 | 77.6581 | 83.6032 | 89.847 | 96.1014 | 102.3596
| Deep RiverWind2050RCP6.0 | Deep River | Wind | RCP6.0 | 2050 | 77.7937 | 83.755 | 90.0164 | 96.289 | 102.5639
| Deep RiverWind2055RCP6.0 | Deep River | Wind | RCP6.0 | 2055 | 77.869 | 83.846 | 90.125 | 96.4147 | 102.7039
| Deep RiverWind2060RCP6.0 | Deep River | Wind | RCP6.0 | 2060 | 77.9443 | 83.9371 | 90.2335 | 96.5404 | 102.8439
| Deep RiverWind2065RCP6.0 | Deep River | Wind | RCP6.0 | 2065 | 78.0196 | 84.0281 | 90.3421 | 96.6661 | 102.9839
| Deep RiverWind2070RCP6.0 | Deep River | Wind | RCP6.0 | 2070 | 78.0949 | 84.1192 | 90.4507 | 96.7918 | 103.1239
| Deep RiverWind2075RCP6.0 | Deep River | Wind | RCP6.0 | 2075 | 78.2352 | 84.2909 | 90.6621 | 97.0346 | 103.403
| Deep RiverWind2080RCP6.0 | Deep River | Wind | RCP6.0 | 2080 | 78.3754 | 84.4626 | 90.8734 | 97.2774 | 103.682
| Deep RiverWind2085RCP6.0 | Deep River | Wind | RCP6.0 | 2085 | 78.5157 | 84.6344 | 91.0848 | 97.5203 | 103.961
| Deep RiverWind2090RCP6.0 | Deep River | Wind | RCP6.0 | 2090 | 78.7481 | 84.9303 | 91.4653 | 97.9663 | 104.4767
| Deep RiverWind2095RCP6.0 | Deep River | Wind | RCP6.0 | 2095 | 78.8403 | 85.0545 | 91.6344 | 98.1694 | 104.7135
| Deep RiverWind2100RCP6.0 | Deep River | Wind | RCP6.0 | 2100 | 78.9326 | 85.1786 | 91.8035 | 98.3726 | 104.9502
| Deep RiverWind2023RCP8.5 | Deep River | Wind | RCP8.5 | 2023 | 77.3571 | 83.2997 | 89.5429 | 95.7919 | 102.0383
| Deep RiverWind2025RCP8.5 | Deep River | Wind | RCP8.5 | 2025 | 77.4775 | 83.4211 | 89.6645 | 95.9157 | 102.1668
| Deep RiverWind2030RCP8.5 | Deep River | Wind | RCP8.5 | 2030 | 77.5979 | 83.5425 | 89.7862 | 96.0395 | 102.2954
| Deep RiverWind2035RCP8.5 | Deep River | Wind | RCP8.5 | 2035 | 77.7183 | 83.6639 | 89.9078 | 96.1633 | 102.4239
| Deep RiverWind2040RCP8.5 | Deep River | Wind | RCP8.5 | 2040 | 77.8439 | 83.8157 | 90.0888 | 96.3728 | 102.6572
| Deep RiverWind2045RCP8.5 | Deep River | Wind | RCP8.5 | 2045 | 77.9694 | 83.9674 | 90.2697 | 96.5823 | 102.8906
| Deep RiverWind2050RCP8.5 | Deep River | Wind | RCP8.5 | 2050 | 78.2819 | 84.3481 | 90.7325 | 97.1156 | 103.496
| Deep RiverWind2055RCP8.5 | Deep River | Wind | RCP8.5 | 2055 | 78.4689 | 84.5771 | 91.0144 | 97.4393 | 103.868
| Deep RiverWind2060RCP8.5 | Deep River | Wind | RCP8.5 | 2060 | 78.7481 | 84.9303 | 91.4653 | 97.9663 | 104.4767
| Deep RiverWind2065RCP8.5 | Deep River | Wind | RCP8.5 | 2065 | 78.8403 | 85.0545 | 91.6344 | 98.1694 | 104.7135
| Deep RiverWind2070RCP8.5 | Deep River | Wind | RCP8.5 | 2070 | 78.9556 | 85.1841 | 91.7798 | 98.3313 | 104.8893
| Deep RiverWind2075RCP8.5 | Deep River | Wind | RCP8.5 | 2075 | 78.9787 | 85.1896 | 91.756 | 98.2901 | 104.8285
| Deep RiverWind2080RCP8.5 | Deep River | Wind | RCP8.5 | 2080 | 79.0017 | 85.1952 | 91.7323 | 98.2488 | 104.7676
| Deep RiverWind2085RCP8.5 | Deep River | Wind | RCP8.5 | 2085 | 79.0517 | 85.2531 | 91.799 | 98.3202 | 104.8488
| Deep RiverWind2090RCP8.5 | Deep River | Wind | RCP8.5 | 2090 | 79.1016 | 85.311 | 91.8658 | 98.3916 | 104.9299
| Deep RiverWind2095RCP8.5 | Deep River | Wind | RCP8.5 | 2095 | 79.1016 | 85.311 | 91.8658 | 98.3916 | 104.9299
| Deep RiverWind2100RCP8.5 | Deep River | Wind | RCP8.5 | 2100 | 79.1016 | 85.311 | 91.8658 | 98.3916 | 104.9299
| DeserontoIce Accretion2023RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3347 | 31.5945
| DeserontoIce Accretion2025RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2025 | 17.5121 | 20.8745 | 25.1292 | 28.4007 | 31.668
| DeserontoIce Accretion2030RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2030 | 17.5411 | 20.916 | 25.1833 | 28.4666 | 31.7415
| DeserontoIce Accretion2035RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2035 | 17.5701 | 20.9575 | 25.2375 | 28.5325 | 31.815
| DeserontoIce Accretion2040RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2040 | 17.5991 | 20.999 | 25.2917 | 28.5984 | 31.8885
| DeserontoIce Accretion2045RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2045 | 17.6281 | 21.0405 | 25.3458 | 28.6643 | 31.962
| DeserontoIce Accretion2050RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2050 | 17.584 | 21.0073 | 25.325 | 28.6511 | 31.9536
| DeserontoIce Accretion2055RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2055 | 17.511 | 20.9326 | 25.25 | 28.572 | 31.8717
| DeserontoIce Accretion2060RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2060 | 17.4379 | 20.8579 | 25.175 | 28.4929 | 31.7898
| DeserontoIce Accretion2065RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2065 | 17.3648 | 20.7832 | 25.1 | 28.4138 | 31.7079
| DeserontoIce Accretion2070RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2070 | 17.2918 | 20.7085 | 25.025 | 28.3347 | 31.626
| DeserontoIce Accretion2075RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2075 | 17.3266 | 20.7777 | 25.1375 | 28.476 | 31.7993
| DeserontoIce Accretion2080RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2080 | 17.3614 | 20.8468 | 25.25 | 28.6172 | 31.9725
| DeserontoIce Accretion2085RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2085 | 17.3962 | 20.916 | 25.3625 | 28.7585 | 32.1457
| DeserontoIce Accretion2090RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2090 | 17.4309 | 20.9852 | 25.475 | 28.8997 | 32.319
| DeserontoIce Accretion2095RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2095 | 17.4657 | 21.0543 | 25.5875 | 29.041 | 32.4922
| DeserontoIce Accretion2100RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2100 | 17.5005 | 21.1235 | 25.7 | 29.1822 | 32.6655
| DeserontoIce Accretion2023RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3347 | 31.5945
| DeserontoIce Accretion2025RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2025 | 17.5121 | 20.8745 | 25.1292 | 28.4007 | 31.668
| DeserontoIce Accretion2030RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2030 | 17.5411 | 20.916 | 25.1833 | 28.4666 | 31.7415
| DeserontoIce Accretion2035RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2035 | 17.5701 | 20.9575 | 25.2375 | 28.5325 | 31.815
| DeserontoIce Accretion2040RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2040 | 17.5991 | 20.999 | 25.2917 | 28.5984 | 31.8885
| DeserontoIce Accretion2045RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2045 | 17.6281 | 21.0405 | 25.3458 | 28.6643 | 31.962
| DeserontoIce Accretion2050RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2050 | 17.584 | 21.0073 | 25.325 | 28.6511 | 31.9536
| DeserontoIce Accretion2055RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2055 | 17.511 | 20.9326 | 25.25 | 28.572 | 31.8717
| DeserontoIce Accretion2060RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2060 | 17.4379 | 20.8579 | 25.175 | 28.4929 | 31.7898
| DeserontoIce Accretion2065RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2065 | 17.3648 | 20.7832 | 25.1 | 28.4138 | 31.7079
| DeserontoIce Accretion2070RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2070 | 17.2918 | 20.7085 | 25.025 | 28.3347 | 31.626
| DeserontoIce Accretion2075RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2075 | 17.344 | 20.8122 | 25.1937 | 28.5466 | 31.8859
| DeserontoIce Accretion2080RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2080 | 17.3962 | 20.916 | 25.3625 | 28.7585 | 32.1457
| DeserontoIce Accretion2085RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2085 | 17.4483 | 21.0198 | 25.5312 | 28.9704 | 32.4056
| DeserontoIce Accretion2090RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2090 | 17.315 | 20.9367 | 25.5083 | 28.9845 | 32.466
| DeserontoIce Accretion2095RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2095 | 17.1294 | 20.75 | 25.3167 | 28.7867 | 32.2665
| DeserontoIce Accretion2100RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2100 | 16.9439 | 20.5633 | 25.125 | 28.589 | 32.067
| DeserontoIce Accretion2023RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3347 | 31.5945
| DeserontoIce Accretion2025RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2025 | 17.5411 | 20.916 | 25.1833 | 28.4666 | 31.7415
| DeserontoIce Accretion2030RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2030 | 17.5991 | 20.999 | 25.2917 | 28.5984 | 31.8885
| DeserontoIce Accretion2035RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2035 | 17.6571 | 21.082 | 25.4 | 28.7302 | 32.0355
| DeserontoIce Accretion2040RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2040 | 17.5353 | 20.9575 | 25.275 | 28.5984 | 31.899
| DeserontoIce Accretion2045RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2045 | 17.4135 | 20.833 | 25.15 | 28.4666 | 31.7625
| DeserontoIce Accretion2050RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2050 | 17.3614 | 20.8468 | 25.25 | 28.6172 | 31.9725
| DeserontoIce Accretion2055RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2055 | 17.4309 | 20.9852 | 25.475 | 28.8997 | 32.319
| DeserontoIce Accretion2060RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2060 | 17.315 | 20.9367 | 25.5083 | 28.9845 | 32.466
| DeserontoIce Accretion2065RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2065 | 17.1294 | 20.75 | 25.3167 | 28.7867 | 32.2665
| DeserontoIce Accretion2070RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2070 | 16.6133 | 20.1898 | 24.6917 | 28.1182 | 31.542
| DeserontoIce Accretion2075RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2075 | 16.2828 | 19.8163 | 24.2583 | 27.6473 | 31.017
| DeserontoIce Accretion2080RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2080 | 15.9523 | 19.4428 | 23.825 | 27.1765 | 30.492
| DeserontoIce Accretion2085RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2085 | 15.2825 | 18.6542 | 22.8875 | 26.1171 | 29.3265
| DeserontoIce Accretion2090RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2090 | 14.6128 | 17.8657 | 21.95 | 25.0577 | 28.161
| DeserontoIce Accretion2095RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2095 | 14.6128 | 17.8657 | 21.95 | 25.0577 | 28.161
| DeserontoIce Accretion2100RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2100 | 14.6128 | 17.8657 | 21.95 | 25.0577 | 28.161
| DeserontoWind2023RCP4.5 | Deseronto | Wind | RCP4.5 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.3568
| DeserontoWind2025RCP4.5 | Deseronto | Wind | RCP4.5 | 2025 | 85.0176 | 91.5972 | 98.5341 | 105.4647 | 112.3885
| DeserontoWind2030RCP4.5 | Deseronto | Wind | RCP4.5 | 2030 | 85.0331 | 91.617 | 98.5586 | 105.4927 | 112.4201
| DeserontoWind2035RCP4.5 | Deseronto | Wind | RCP4.5 | 2035 | 85.0486 | 91.6367 | 98.5831 | 105.5206 | 112.4518
| DeserontoWind2040RCP4.5 | Deseronto | Wind | RCP4.5 | 2040 | 85.0641 | 91.6565 | 98.6076 | 105.5486 | 112.4834
| DeserontoWind2045RCP4.5 | Deseronto | Wind | RCP4.5 | 2045 | 85.0796 | 91.6762 | 98.6321 | 105.5765 | 112.5151
| DeserontoWind2050RCP4.5 | Deseronto | Wind | RCP4.5 | 2050 | 85.1747 | 91.7944 | 98.7781 | 105.745 | 112.7076
| DeserontoWind2055RCP4.5 | Deseronto | Wind | RCP4.5 | 2055 | 85.2542 | 91.8928 | 98.8996 | 105.8855 | 112.8685
| DeserontoWind2060RCP4.5 | Deseronto | Wind | RCP4.5 | 2060 | 85.3338 | 91.9912 | 99.0212 | 106.026 | 113.0294
| DeserontoWind2065RCP4.5 | Deseronto | Wind | RCP4.5 | 2065 | 85.4133 | 92.0897 | 99.1427 | 106.1666 | 113.1902
| DeserontoWind2070RCP4.5 | Deseronto | Wind | RCP4.5 | 2070 | 85.4929 | 92.1881 | 99.2642 | 106.3071 | 113.3511
| DeserontoWind2075RCP4.5 | Deseronto | Wind | RCP4.5 | 2075 | 85.5549 | 92.2671 | 99.3638 | 106.4259 | 113.4889
| DeserontoWind2080RCP4.5 | Deseronto | Wind | RCP4.5 | 2080 | 85.617 | 92.3461 | 99.4635 | 106.5448 | 113.6267
| DeserontoWind2085RCP4.5 | Deseronto | Wind | RCP4.5 | 2085 | 85.679 | 92.4251 | 99.5631 | 106.6636 | 113.7645
| DeserontoWind2090RCP4.5 | Deseronto | Wind | RCP4.5 | 2090 | 85.7411 | 92.5041 | 99.6627 | 106.7824 | 113.9023
| DeserontoWind2095RCP4.5 | Deseronto | Wind | RCP4.5 | 2095 | 85.8032 | 92.5831 | 99.7624 | 106.9013 | 114.0401
| DeserontoWind2100RCP4.5 | Deseronto | Wind | RCP4.5 | 2100 | 85.8652 | 92.662 | 99.862 | 107.0201 | 114.1778
| DeserontoWind2023RCP6.0 | Deseronto | Wind | RCP6.0 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.3568
| DeserontoWind2025RCP6.0 | Deseronto | Wind | RCP6.0 | 2025 | 85.0176 | 91.5972 | 98.5341 | 105.4647 | 112.3885
| DeserontoWind2030RCP6.0 | Deseronto | Wind | RCP6.0 | 2030 | 85.0331 | 91.617 | 98.5586 | 105.4927 | 112.4201
| DeserontoWind2035RCP6.0 | Deseronto | Wind | RCP6.0 | 2035 | 85.0486 | 91.6367 | 98.5831 | 105.5206 | 112.4518
| DeserontoWind2040RCP6.0 | Deseronto | Wind | RCP6.0 | 2040 | 85.0641 | 91.6565 | 98.6076 | 105.5486 | 112.4834
| DeserontoWind2045RCP6.0 | Deseronto | Wind | RCP6.0 | 2045 | 85.0796 | 91.6762 | 98.6321 | 105.5765 | 112.5151
| DeserontoWind2050RCP6.0 | Deseronto | Wind | RCP6.0 | 2050 | 85.1747 | 91.7944 | 98.7781 | 105.745 | 112.7076
| DeserontoWind2055RCP6.0 | Deseronto | Wind | RCP6.0 | 2055 | 85.2542 | 91.8928 | 98.8996 | 105.8855 | 112.8685
| DeserontoWind2060RCP6.0 | Deseronto | Wind | RCP6.0 | 2060 | 85.3338 | 91.9912 | 99.0212 | 106.026 | 113.0294
| DeserontoWind2065RCP6.0 | Deseronto | Wind | RCP6.0 | 2065 | 85.4133 | 92.0897 | 99.1427 | 106.1666 | 113.1902
| DeserontoWind2070RCP6.0 | Deseronto | Wind | RCP6.0 | 2070 | 85.4929 | 92.1881 | 99.2642 | 106.3071 | 113.3511
| DeserontoWind2075RCP6.0 | Deseronto | Wind | RCP6.0 | 2075 | 85.586 | 92.3066 | 99.4136 | 106.4853 | 113.5578
| DeserontoWind2080RCP6.0 | Deseronto | Wind | RCP6.0 | 2080 | 85.679 | 92.4251 | 99.5631 | 106.6636 | 113.7645
| DeserontoWind2085RCP6.0 | Deseronto | Wind | RCP6.0 | 2085 | 85.7721 | 92.5436 | 99.7125 | 106.8419 | 113.9712
| DeserontoWind2090RCP6.0 | Deseronto | Wind | RCP6.0 | 2090 | 86.0091 | 92.817 | 100.0253 | 107.1914 | 114.3603
| DeserontoWind2095RCP6.0 | Deseronto | Wind | RCP6.0 | 2095 | 86.1529 | 92.9719 | 100.1887 | 107.3627 | 114.5428
| DeserontoWind2100RCP6.0 | Deseronto | Wind | RCP6.0 | 2100 | 86.2968 | 93.1269 | 100.352 | 107.5339 | 114.7253
| DeserontoWind2023RCP8.5 | Deseronto | Wind | RCP8.5 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.3568
| DeserontoWind2025RCP8.5 | Deseronto | Wind | RCP8.5 | 2025 | 85.0331 | 91.617 | 98.5586 | 105.4927 | 112.4201
| DeserontoWind2030RCP8.5 | Deseronto | Wind | RCP8.5 | 2030 | 85.0641 | 91.6565 | 98.6076 | 105.5486 | 112.4834
| DeserontoWind2035RCP8.5 | Deseronto | Wind | RCP8.5 | 2035 | 85.0952 | 91.696 | 98.6566 | 105.6045 | 112.5467
| DeserontoWind2040RCP8.5 | Deseronto | Wind | RCP8.5 | 2040 | 85.2277 | 91.86 | 98.8591 | 105.8387 | 112.8149
| DeserontoWind2045RCP8.5 | Deseronto | Wind | RCP8.5 | 2045 | 85.3603 | 92.0241 | 99.0617 | 106.0729 | 113.083
| DeserontoWind2050RCP8.5 | Deseronto | Wind | RCP8.5 | 2050 | 85.617 | 92.3461 | 99.4635 | 106.5448 | 113.6267
| DeserontoWind2055RCP8.5 | Deseronto | Wind | RCP8.5 | 2055 | 85.7411 | 92.5041 | 99.6627 | 106.7824 | 113.9023
| DeserontoWind2060RCP8.5 | Deseronto | Wind | RCP8.5 | 2060 | 86.0091 | 92.817 | 100.0253 | 107.1914 | 114.3603
| DeserontoWind2065RCP8.5 | Deseronto | Wind | RCP8.5 | 2065 | 86.1529 | 92.9719 | 100.1887 | 107.3627 | 114.5428
| DeserontoWind2070RCP8.5 | Deseronto | Wind | RCP8.5 | 2070 | 86.3081 | 93.142 | 100.3749 | 107.5619 | 114.7588
| DeserontoWind2075RCP8.5 | Deseronto | Wind | RCP8.5 | 2075 | 86.3193 | 93.1572 | 100.3977 | 107.5899 | 114.7923
| DeserontoWind2080RCP8.5 | Deseronto | Wind | RCP8.5 | 2080 | 86.3306 | 93.1724 | 100.4206 | 107.6178 | 114.8258
| DeserontoWind2085RCP8.5 | Deseronto | Wind | RCP8.5 | 2085 | 86.4279 | 93.3091 | 100.6117 | 107.8538 | 115.1051
| DeserontoWind2090RCP8.5 | Deseronto | Wind | RCP8.5 | 2090 | 86.5253 | 93.4458 | 100.8028 | 108.0897 | 115.3844
| DeserontoWind2095RCP8.5 | Deseronto | Wind | RCP8.5 | 2095 | 86.5253 | 93.4458 | 100.8028 | 108.0897 | 115.3844
| DeserontoWind2100RCP8.5 | Deseronto | Wind | RCP8.5 | 2100 | 86.5253 | 93.4458 | 100.8028 | 108.0897 | 115.3844
| DorchesterIce Accretion2023RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2023 | 21.9553 | 26.3475 | 31.904 | 36.1238 | 40.3603
| DorchesterIce Accretion2025RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2025 | 21.8254 | 26.2059 | 31.7493 | 35.9611 | 40.1856
| DorchesterIce Accretion2030RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2030 | 21.6956 | 26.0642 | 31.5947 | 35.7984 | 40.0109
| DorchesterIce Accretion2035RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2035 | 21.5657 | 25.9226 | 31.44 | 35.6357 | 39.8362
| DorchesterIce Accretion2040RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2040 | 21.4358 | 25.7809 | 31.2853 | 35.473 | 39.6614
| DorchesterIce Accretion2045RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2045 | 21.3059 | 25.6393 | 31.1307 | 35.3102 | 39.4867
| DorchesterIce Accretion2050RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2050 | 20.7618 | 25.0408 | 30.4576 | 34.5834 | 38.6991
| DorchesterIce Accretion2055RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2055 | 20.3477 | 24.5839 | 29.9392 | 34.0193 | 38.0863
| DorchesterIce Accretion2060RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2060 | 19.9335 | 24.1271 | 29.4208 | 33.4552 | 37.4734
| DorchesterIce Accretion2065RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2065 | 19.5193 | 23.6703 | 28.9024 | 32.8911 | 36.8605
| DorchesterIce Accretion2070RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2070 | 19.1052 | 23.2134 | 28.384 | 32.327 | 36.2477
| DorchesterIce Accretion2075RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2075 | 18.9604 | 23.0674 | 28.2347 | 32.1703 | 36.0864
| DorchesterIce Accretion2080RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2080 | 18.8157 | 22.9213 | 28.0853 | 32.0137 | 35.9251
| DorchesterIce Accretion2085RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2085 | 18.6709 | 22.7752 | 27.936 | 31.857 | 35.7638
| DorchesterIce Accretion2090RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2090 | 18.5262 | 22.6291 | 27.7867 | 31.7003 | 35.6026
| DorchesterIce Accretion2095RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2095 | 18.3815 | 22.483 | 27.6373 | 31.5436 | 35.4413
| DorchesterIce Accretion2100RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2100 | 18.2367 | 22.337 | 27.488 | 31.3869 | 35.28
| DorchesterIce Accretion2023RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2023 | 21.9553 | 26.3475 | 31.904 | 36.1238 | 40.3603
| DorchesterIce Accretion2025RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2025 | 21.8254 | 26.2059 | 31.7493 | 35.9611 | 40.1856
| DorchesterIce Accretion2030RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2030 | 21.6956 | 26.0642 | 31.5947 | 35.7984 | 40.0109
| DorchesterIce Accretion2035RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2035 | 21.5657 | 25.9226 | 31.44 | 35.6357 | 39.8362
| DorchesterIce Accretion2040RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2040 | 21.4358 | 25.7809 | 31.2853 | 35.473 | 39.6614
| DorchesterIce Accretion2045RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2045 | 21.3059 | 25.6393 | 31.1307 | 35.3102 | 39.4867
| DorchesterIce Accretion2050RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2050 | 20.7618 | 25.0408 | 30.4576 | 34.5834 | 38.6991
| DorchesterIce Accretion2055RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2055 | 20.3477 | 24.5839 | 29.9392 | 34.0193 | 38.0863
| DorchesterIce Accretion2060RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2060 | 19.9335 | 24.1271 | 29.4208 | 33.4552 | 37.4734
| DorchesterIce Accretion2065RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2065 | 19.5193 | 23.6703 | 28.9024 | 32.8911 | 36.8605
| DorchesterIce Accretion2070RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2070 | 19.1052 | 23.2134 | 28.384 | 32.327 | 36.2477
| DorchesterIce Accretion2075RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2075 | 18.888 | 22.9943 | 28.16 | 32.092 | 36.0058
| DorchesterIce Accretion2080RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2080 | 18.6709 | 22.7752 | 27.936 | 31.857 | 35.7638
| DorchesterIce Accretion2085RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2085 | 18.4538 | 22.5561 | 27.712 | 31.6219 | 35.5219
| DorchesterIce Accretion2090RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2090 | 17.7172 | 21.7526 | 26.8267 | 30.6637 | 34.487
| DorchesterIce Accretion2095RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2095 | 17.1976 | 21.1683 | 26.1653 | 29.9405 | 33.6941
| DorchesterIce Accretion2100RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2100 | 16.678 | 20.584 | 25.504 | 29.2173 | 32.9011
| DorchesterIce Accretion2023RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2023 | 21.9553 | 26.3475 | 31.904 | 36.1238 | 40.3603
| DorchesterIce Accretion2025RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2025 | 21.6956 | 26.0642 | 31.5947 | 35.7984 | 40.0109
| DorchesterIce Accretion2030RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2030 | 21.4358 | 25.7809 | 31.2853 | 35.473 | 39.6614
| DorchesterIce Accretion2035RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2035 | 21.176 | 25.4976 | 30.976 | 35.1475 | 39.312
| DorchesterIce Accretion2040RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2040 | 20.4857 | 24.7362 | 30.112 | 34.2074 | 38.2906
| DorchesterIce Accretion2045RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2045 | 19.7954 | 23.9748 | 29.248 | 33.2672 | 37.2691
| DorchesterIce Accretion2050RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2050 | 18.8157 | 22.9213 | 28.0853 | 32.0137 | 35.9251
| DorchesterIce Accretion2055RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2055 | 18.5262 | 22.6291 | 27.7867 | 31.7003 | 35.6026
| DorchesterIce Accretion2060RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2060 | 17.7172 | 21.7526 | 26.8267 | 30.6637 | 34.487
| DorchesterIce Accretion2065RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2065 | 17.1976 | 21.1683 | 26.1653 | 29.9405 | 33.6941
| DorchesterIce Accretion2070RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2070 | 16.344 | 20.2299 | 25.12 | 28.7954 | 32.4576
| DorchesterIce Accretion2075RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2075 | 16.01 | 19.8757 | 24.736 | 28.3735 | 32.0141
| DorchesterIce Accretion2080RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2080 | 15.676 | 19.5216 | 24.352 | 27.9517 | 31.5706
| DorchesterIce Accretion2085RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2085 | 14.6851 | 18.353 | 22.944 | 26.3787 | 29.8166
| DorchesterIce Accretion2090RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2090 | 13.6943 | 17.1843 | 21.536 | 24.8058 | 28.0627
| DorchesterIce Accretion2095RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2095 | 13.6943 | 17.1843 | 21.536 | 24.8058 | 28.0627
| DorchesterIce Accretion2100RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2100 | 13.6943 | 17.1843 | 21.536 | 24.8058 | 28.0627
| DorchesterWind2023RCP4.5 | Dorchester | Wind | RCP4.5 | 2023 | 88.7974 | 95.7896 | 103.1934 | 110.5588 | 117.9312
| DorchesterWind2025RCP4.5 | Dorchester | Wind | RCP4.5 | 2025 | 88.909 | 95.9382 | 103.3889 | 110.7935 | 118.2064
| DorchesterWind2030RCP4.5 | Dorchester | Wind | RCP4.5 | 2030 | 89.0205 | 96.0869 | 103.5844 | 111.0281 | 118.4816
| DorchesterWind2035RCP4.5 | Dorchester | Wind | RCP4.5 | 2035 | 89.1321 | 96.2355 | 103.7799 | 111.2628 | 118.7568
| DorchesterWind2040RCP4.5 | Dorchester | Wind | RCP4.5 | 2040 | 89.2437 | 96.3841 | 103.9754 | 111.4974 | 119.032
| DorchesterWind2045RCP4.5 | Dorchester | Wind | RCP4.5 | 2045 | 89.3552 | 96.5327 | 104.1709 | 111.7321 | 119.3072
| DorchesterWind2050RCP4.5 | Dorchester | Wind | RCP4.5 | 2050 | 89.5196 | 96.7553 | 104.4684 | 112.0933 | 119.7335
| DorchesterWind2055RCP4.5 | Dorchester | Wind | RCP4.5 | 2055 | 89.5725 | 96.8293 | 104.5704 | 112.2199 | 119.8847
| DorchesterWind2060RCP4.5 | Dorchester | Wind | RCP4.5 | 2060 | 89.6253 | 96.9033 | 104.6724 | 112.3465 | 120.0358
| DorchesterWind2065RCP4.5 | Dorchester | Wind | RCP4.5 | 2065 | 89.6782 | 96.9773 | 104.7744 | 112.4731 | 120.187
| DorchesterWind2070RCP4.5 | Dorchester | Wind | RCP4.5 | 2070 | 89.731 | 97.0513 | 104.8764 | 112.5997 | 120.3382
| DorchesterWind2075RCP4.5 | Dorchester | Wind | RCP4.5 | 2075 | 89.8866 | 97.2536 | 105.1382 | 112.9108 | 120.7006
| DorchesterWind2080RCP4.5 | Dorchester | Wind | RCP4.5 | 2080 | 90.0422 | 97.456 | 105.4 | 113.2218 | 121.063
| DorchesterWind2085RCP4.5 | Dorchester | Wind | RCP4.5 | 2085 | 90.1978 | 97.6584 | 105.6618 | 113.5329 | 121.4254
| DorchesterWind2090RCP4.5 | Dorchester | Wind | RCP4.5 | 2090 | 90.3534 | 97.8607 | 105.9236 | 113.8439 | 121.7878
| DorchesterWind2095RCP4.5 | Dorchester | Wind | RCP4.5 | 2095 | 90.509 | 98.0631 | 106.1854 | 114.155 | 122.1502
| DorchesterWind2100RCP4.5 | Dorchester | Wind | RCP4.5 | 2100 | 90.6646 | 98.2655 | 106.4472 | 114.466 | 122.5126
| DorchesterWind2023RCP6.0 | Dorchester | Wind | RCP6.0 | 2023 | 88.7974 | 95.7896 | 103.1934 | 110.5588 | 117.9312
| DorchesterWind2025RCP6.0 | Dorchester | Wind | RCP6.0 | 2025 | 88.909 | 95.9382 | 103.3889 | 110.7935 | 118.2064
| DorchesterWind2030RCP6.0 | Dorchester | Wind | RCP6.0 | 2030 | 89.0205 | 96.0869 | 103.5844 | 111.0281 | 118.4816
| DorchesterWind2035RCP6.0 | Dorchester | Wind | RCP6.0 | 2035 | 89.1321 | 96.2355 | 103.7799 | 111.2628 | 118.7568
| DorchesterWind2040RCP6.0 | Dorchester | Wind | RCP6.0 | 2040 | 89.2437 | 96.3841 | 103.9754 | 111.4974 | 119.032
| DorchesterWind2045RCP6.0 | Dorchester | Wind | RCP6.0 | 2045 | 89.3552 | 96.5327 | 104.1709 | 111.7321 | 119.3072
| DorchesterWind2050RCP6.0 | Dorchester | Wind | RCP6.0 | 2050 | 89.5196 | 96.7553 | 104.4684 | 112.0933 | 119.7335
| DorchesterWind2055RCP6.0 | Dorchester | Wind | RCP6.0 | 2055 | 89.5725 | 96.8293 | 104.5704 | 112.2199 | 119.8847
| DorchesterWind2060RCP6.0 | Dorchester | Wind | RCP6.0 | 2060 | 89.6253 | 96.9033 | 104.6724 | 112.3465 | 120.0358
| DorchesterWind2065RCP6.0 | Dorchester | Wind | RCP6.0 | 2065 | 89.6782 | 96.9773 | 104.7744 | 112.4731 | 120.187
| DorchesterWind2070RCP6.0 | Dorchester | Wind | RCP6.0 | 2070 | 89.731 | 97.0513 | 104.8764 | 112.5997 | 120.3382
| DorchesterWind2075RCP6.0 | Dorchester | Wind | RCP6.0 | 2075 | 89.9644 | 97.3548 | 105.2691 | 113.0663 | 120.8818
| DorchesterWind2080RCP6.0 | Dorchester | Wind | RCP6.0 | 2080 | 90.1978 | 97.6584 | 105.6618 | 113.5329 | 121.4254
| DorchesterWind2085RCP6.0 | Dorchester | Wind | RCP6.0 | 2085 | 90.4312 | 97.9619 | 106.0545 | 113.9995 | 121.969
| DorchesterWind2090RCP6.0 | Dorchester | Wind | RCP6.0 | 2090 | 91.0492 | 98.7556 | 107.0626 | 115.19 | 123.3498
| DorchesterWind2095RCP6.0 | Dorchester | Wind | RCP6.0 | 2095 | 91.4338 | 99.2457 | 107.678 | 115.914 | 124.187
| DorchesterWind2100RCP6.0 | Dorchester | Wind | RCP6.0 | 2100 | 91.8184 | 99.7358 | 108.2934 | 116.6379 | 125.0243
| DorchesterWind2023RCP8.5 | Dorchester | Wind | RCP8.5 | 2023 | 88.7974 | 95.7896 | 103.1934 | 110.5588 | 117.9312
| DorchesterWind2025RCP8.5 | Dorchester | Wind | RCP8.5 | 2025 | 89.0205 | 96.0869 | 103.5844 | 111.0281 | 118.4816
| DorchesterWind2030RCP8.5 | Dorchester | Wind | RCP8.5 | 2030 | 89.2437 | 96.3841 | 103.9754 | 111.4974 | 119.032
| DorchesterWind2035RCP8.5 | Dorchester | Wind | RCP8.5 | 2035 | 89.4668 | 96.6813 | 104.3664 | 111.9667 | 119.5824
| DorchesterWind2040RCP8.5 | Dorchester | Wind | RCP8.5 | 2040 | 89.5549 | 96.8046 | 104.5364 | 112.1777 | 119.8343
| DorchesterWind2045RCP8.5 | Dorchester | Wind | RCP8.5 | 2045 | 89.6429 | 96.9279 | 104.7064 | 112.3887 | 120.0862
| DorchesterWind2050RCP8.5 | Dorchester | Wind | RCP8.5 | 2050 | 90.0422 | 97.456 | 105.4 | 113.2218 | 121.063
| DorchesterWind2055RCP8.5 | Dorchester | Wind | RCP8.5 | 2055 | 90.3534 | 97.8607 | 105.9236 | 113.8439 | 121.7878
| DorchesterWind2060RCP8.5 | Dorchester | Wind | RCP8.5 | 2060 | 91.0492 | 98.7556 | 107.0626 | 115.19 | 123.3498
| DorchesterWind2065RCP8.5 | Dorchester | Wind | RCP8.5 | 2065 | 91.4338 | 99.2457 | 107.678 | 115.914 | 124.187
| DorchesterWind2070RCP8.5 | Dorchester | Wind | RCP8.5 | 2070 | 92.0562 | 100.033 | 108.6708 | 117.0854 | 125.5398
| DorchesterWind2075RCP8.5 | Dorchester | Wind | RCP8.5 | 2075 | 92.294 | 100.3303 | 109.0482 | 117.5329 | 126.0553
| DorchesterWind2080RCP8.5 | Dorchester | Wind | RCP8.5 | 2080 | 92.5318 | 100.6275 | 109.4256 | 117.9803 | 126.5708
| DorchesterWind2085RCP8.5 | Dorchester | Wind | RCP8.5 | 2085 | 92.937 | 101.1634 | 110.1294 | 118.8207 | 127.5592
| DorchesterWind2090RCP8.5 | Dorchester | Wind | RCP8.5 | 2090 | 93.3421 | 101.6994 | 110.8332 | 119.6611 | 128.5475
| DorchesterWind2095RCP8.5 | Dorchester | Wind | RCP8.5 | 2095 | 93.3421 | 101.6994 | 110.8332 | 119.6611 | 128.5475
| DorchesterWind2100RCP8.5 | Dorchester | Wind | RCP8.5 | 2100 | 93.3421 | 101.6994 | 110.8332 | 119.6611 | 128.5475
| DorionIce Accretion2023RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2023 | 11.7793 | 14.0901 | 17.024 | 19.2552 | 21.4906
| DorionIce Accretion2025RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2025 | 11.7904 | 14.1011 | 17.032 | 19.2612 | 21.4973
| DorionIce Accretion2030RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2030 | 11.8016 | 14.1122 | 17.04 | 19.2673 | 21.504
| DorionIce Accretion2035RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2035 | 11.8127 | 14.1233 | 17.048 | 19.2733 | 21.5107
| DorionIce Accretion2040RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2040 | 11.8238 | 14.1343 | 17.056 | 19.2793 | 21.5174
| DorionIce Accretion2045RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2045 | 11.835 | 14.1454 | 17.064 | 19.2853 | 21.5242
| DorionIce Accretion2050RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2050 | 11.8862 | 14.199 | 17.1232 | 19.3492 | 21.5914
| DorionIce Accretion2055RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2055 | 11.9262 | 14.2415 | 17.1744 | 19.4071 | 21.6518
| DorionIce Accretion2060RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2060 | 11.9663 | 14.284 | 17.2256 | 19.4649 | 21.7123
| DorionIce Accretion2065RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2065 | 12.0064 | 14.3265 | 17.2768 | 19.5228 | 21.7728
| DorionIce Accretion2070RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2070 | 12.0465 | 14.369 | 17.328 | 19.5806 | 21.8333
| DorionIce Accretion2075RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2075 | 12.0762 | 14.411 | 17.384 | 19.6469 | 21.9106
| DorionIce Accretion2080RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2080 | 12.1059 | 14.4531 | 17.44 | 19.7132 | 21.9878
| DorionIce Accretion2085RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2085 | 12.1356 | 14.4951 | 17.496 | 19.7795 | 22.0651
| DorionIce Accretion2090RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2090 | 12.1652 | 14.5372 | 17.552 | 19.8458 | 22.1424
| DorionIce Accretion2095RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2095 | 12.1949 | 14.5792 | 17.608 | 19.9121 | 22.2197
| DorionIce Accretion2100RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2100 | 12.2246 | 14.6213 | 17.664 | 19.9784 | 22.297
| DorionIce Accretion2023RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2023 | 11.7793 | 14.0901 | 17.024 | 19.2552 | 21.4906
| DorionIce Accretion2025RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2025 | 11.7904 | 14.1011 | 17.032 | 19.2612 | 21.4973
| DorionIce Accretion2030RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2030 | 11.8016 | 14.1122 | 17.04 | 19.2673 | 21.504
| DorionIce Accretion2035RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2035 | 11.8127 | 14.1233 | 17.048 | 19.2733 | 21.5107
| DorionIce Accretion2040RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2040 | 11.8238 | 14.1343 | 17.056 | 19.2793 | 21.5174
| DorionIce Accretion2045RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2045 | 11.835 | 14.1454 | 17.064 | 19.2853 | 21.5242
| DorionIce Accretion2050RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2050 | 11.8862 | 14.199 | 17.1232 | 19.3492 | 21.5914
| DorionIce Accretion2055RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2055 | 11.9262 | 14.2415 | 17.1744 | 19.4071 | 21.6518
| DorionIce Accretion2060RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2060 | 11.9663 | 14.284 | 17.2256 | 19.4649 | 21.7123
| DorionIce Accretion2065RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2065 | 12.0064 | 14.3265 | 17.2768 | 19.5228 | 21.7728
| DorionIce Accretion2070RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2070 | 12.0465 | 14.369 | 17.328 | 19.5806 | 21.8333
| DorionIce Accretion2075RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2075 | 12.091 | 14.432 | 17.412 | 19.6801 | 21.9492
| DorionIce Accretion2080RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2080 | 12.1356 | 14.4951 | 17.496 | 19.7795 | 22.0651
| DorionIce Accretion2085RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2085 | 12.1801 | 14.5582 | 17.58 | 19.879 | 22.181
| DorionIce Accretion2090RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2090 | 12.2358 | 14.6434 | 17.7013 | 20.0266 | 22.3574
| DorionIce Accretion2095RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2095 | 12.2469 | 14.6655 | 17.7387 | 20.0748 | 22.4179
| DorionIce Accretion2100RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2100 | 12.258 | 14.6877 | 17.776 | 20.123 | 22.4784
| DorionIce Accretion2023RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2023 | 11.7793 | 14.0901 | 17.024 | 19.2552 | 21.4906
| DorionIce Accretion2025RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2025 | 11.8016 | 14.1122 | 17.04 | 19.2673 | 21.504
| DorionIce Accretion2030RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2030 | 11.8238 | 14.1343 | 17.056 | 19.2793 | 21.5174
| DorionIce Accretion2035RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2035 | 11.8461 | 14.1565 | 17.072 | 19.2914 | 21.5309
| DorionIce Accretion2040RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2040 | 11.9129 | 14.2273 | 17.1573 | 19.3878 | 21.6317
| DorionIce Accretion2045RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2045 | 11.9797 | 14.2981 | 17.2427 | 19.4842 | 21.7325
| DorionIce Accretion2050RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2050 | 12.1059 | 14.4531 | 17.44 | 19.7132 | 21.9878
| DorionIce Accretion2055RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2055 | 12.1652 | 14.5372 | 17.552 | 19.8458 | 22.1424
| DorionIce Accretion2060RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2060 | 12.2358 | 14.6434 | 17.7013 | 20.0266 | 22.3574
| DorionIce Accretion2065RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2065 | 12.2469 | 14.6655 | 17.7387 | 20.0748 | 22.4179
| DorionIce Accretion2070RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2070 | 12.2246 | 14.67 | 17.7707 | 20.1291 | 22.4918
| DorionIce Accretion2075RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2075 | 12.1912 | 14.6523 | 17.7653 | 20.1351 | 22.5053
| DorionIce Accretion2080RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2080 | 12.1578 | 14.6346 | 17.76 | 20.1411 | 22.5187
| DorionIce Accretion2085RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2085 | 11.8628 | 14.2826 | 17.344 | 19.671 | 21.9946
| DorionIce Accretion2090RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2090 | 11.5677 | 13.9307 | 16.928 | 19.201 | 21.4704
| DorionIce Accretion2095RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2095 | 11.5677 | 13.9307 | 16.928 | 19.201 | 21.4704
| DorionIce Accretion2100RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2100 | 11.5677 | 13.9307 | 16.928 | 19.201 | 21.4704
| DorionWind2023RCP4.5 | Dorion | Wind | RCP4.5 | 2023 | 81.4514 | 87.7085 | 94.282 | 100.8616 | 107.4493
| DorionWind2025RCP4.5 | Dorion | Wind | RCP4.5 | 2025 | 81.6719 | 87.9868 | 94.6345 | 101.2757 | 107.9262
| DorionWind2030RCP4.5 | Dorion | Wind | RCP4.5 | 2030 | 81.8924 | 88.2651 | 94.987 | 101.6897 | 108.4031
| DorionWind2035RCP4.5 | Dorion | Wind | RCP4.5 | 2035 | 82.1129 | 88.5433 | 95.3395 | 102.1038 | 108.8799
| DorionWind2040RCP4.5 | Dorion | Wind | RCP4.5 | 2040 | 82.3335 | 88.8216 | 95.692 | 102.5178 | 109.3568
| DorionWind2045RCP4.5 | Dorion | Wind | RCP4.5 | 2045 | 82.554 | 89.0999 | 96.0445 | 102.9319 | 109.8336
| DorionWind2050RCP4.5 | Dorion | Wind | RCP4.5 | 2050 | 82.9141 | 89.5426 | 96.5869 | 103.5612 | 110.5505
| DorionWind2055RCP4.5 | Dorion | Wind | RCP4.5 | 2055 | 83.0537 | 89.7069 | 96.7768 | 103.7764 | 110.7906
| DorionWind2060RCP4.5 | Dorion | Wind | RCP4.5 | 2060 | 83.1933 | 89.8713 | 96.9666 | 103.9917 | 111.0306
| DorionWind2065RCP4.5 | Dorion | Wind | RCP4.5 | 2065 | 83.3329 | 90.0356 | 97.1565 | 104.2069 | 111.2707
| DorionWind2070RCP4.5 | Dorion | Wind | RCP4.5 | 2070 | 83.4725 | 90.2 | 97.3464 | 104.4222 | 111.5107
| DorionWind2075RCP4.5 | Dorion | Wind | RCP4.5 | 2075 | 83.4982 | 90.2131 | 97.3448 | 104.4071 | 111.4839
| DorionWind2080RCP4.5 | Dorion | Wind | RCP4.5 | 2080 | 83.5239 | 90.2262 | 97.3433 | 104.392 | 111.4571
| DorionWind2085RCP4.5 | Dorion | Wind | RCP4.5 | 2085 | 83.5496 | 90.2393 | 97.3417 | 104.3769 | 111.4303
| DorionWind2090RCP4.5 | Dorion | Wind | RCP4.5 | 2090 | 83.5753 | 90.2524 | 97.3401 | 104.3618 | 111.4035
| DorionWind2095RCP4.5 | Dorion | Wind | RCP4.5 | 2095 | 83.601 | 90.2655 | 97.3386 | 104.3467 | 111.3767
| DorionWind2100RCP4.5 | Dorion | Wind | RCP4.5 | 2100 | 83.6267 | 90.2786 | 97.337 | 104.3316 | 111.35
| DorionWind2023RCP6.0 | Dorion | Wind | RCP6.0 | 2023 | 81.4514 | 87.7085 | 94.282 | 100.8616 | 107.4493
| DorionWind2025RCP6.0 | Dorion | Wind | RCP6.0 | 2025 | 81.6719 | 87.9868 | 94.6345 | 101.2757 | 107.9262
| DorionWind2030RCP6.0 | Dorion | Wind | RCP6.0 | 2030 | 81.8924 | 88.2651 | 94.987 | 101.6897 | 108.4031
| DorionWind2035RCP6.0 | Dorion | Wind | RCP6.0 | 2035 | 82.1129 | 88.5433 | 95.3395 | 102.1038 | 108.8799
| DorionWind2040RCP6.0 | Dorion | Wind | RCP6.0 | 2040 | 82.3335 | 88.8216 | 95.692 | 102.5178 | 109.3568
| DorionWind2045RCP6.0 | Dorion | Wind | RCP6.0 | 2045 | 82.554 | 89.0999 | 96.0445 | 102.9319 | 109.8336
| DorionWind2050RCP6.0 | Dorion | Wind | RCP6.0 | 2050 | 82.9141 | 89.5426 | 96.5869 | 103.5612 | 110.5505
| DorionWind2055RCP6.0 | Dorion | Wind | RCP6.0 | 2055 | 83.0537 | 89.7069 | 96.7768 | 103.7764 | 110.7906
| DorionWind2060RCP6.0 | Dorion | Wind | RCP6.0 | 2060 | 83.1933 | 89.8713 | 96.9666 | 103.9917 | 111.0306
| DorionWind2065RCP6.0 | Dorion | Wind | RCP6.0 | 2065 | 83.3329 | 90.0356 | 97.1565 | 104.2069 | 111.2707
| DorionWind2070RCP6.0 | Dorion | Wind | RCP6.0 | 2070 | 83.4725 | 90.2 | 97.3464 | 104.4222 | 111.5107
| DorionWind2075RCP6.0 | Dorion | Wind | RCP6.0 | 2075 | 83.5111 | 90.2196 | 97.3441 | 104.3995 | 111.4705
| DorionWind2080RCP6.0 | Dorion | Wind | RCP6.0 | 2080 | 83.5496 | 90.2393 | 97.3417 | 104.3769 | 111.4303
| DorionWind2085RCP6.0 | Dorion | Wind | RCP6.0 | 2085 | 83.5882 | 90.259 | 97.3393 | 104.3543 | 111.3901
| DorionWind2090RCP6.0 | Dorion | Wind | RCP6.0 | 2090 | 83.6592 | 90.3019 | 97.3495 | 104.3383 | 111.3464
| DorionWind2095RCP6.0 | Dorion | Wind | RCP6.0 | 2095 | 83.6917 | 90.3253 | 97.3621 | 104.345 | 111.3428
| DorionWind2100RCP6.0 | Dorion | Wind | RCP6.0 | 2100 | 83.7241 | 90.3486 | 97.3746 | 104.3518 | 111.3392
| DorionWind2023RCP8.5 | Dorion | Wind | RCP8.5 | 2023 | 81.4514 | 87.7085 | 94.282 | 100.8616 | 107.4493
| DorionWind2025RCP8.5 | Dorion | Wind | RCP8.5 | 2025 | 81.8924 | 88.2651 | 94.987 | 101.6897 | 108.4031
| DorionWind2030RCP8.5 | Dorion | Wind | RCP8.5 | 2030 | 82.3335 | 88.8216 | 95.692 | 102.5178 | 109.3568
| DorionWind2035RCP8.5 | Dorion | Wind | RCP8.5 | 2035 | 82.7745 | 89.3782 | 96.397 | 103.346 | 110.3105
| DorionWind2040RCP8.5 | Dorion | Wind | RCP8.5 | 2040 | 83.0071 | 89.6521 | 96.7135 | 103.7047 | 110.7106
| DorionWind2045RCP8.5 | Dorion | Wind | RCP8.5 | 2045 | 83.2398 | 89.926 | 97.0299 | 104.0634 | 111.1106
| DorionWind2050RCP8.5 | Dorion | Wind | RCP8.5 | 2050 | 83.5239 | 90.2262 | 97.3433 | 104.392 | 111.4571
| DorionWind2055RCP8.5 | Dorion | Wind | RCP8.5 | 2055 | 83.5753 | 90.2524 | 97.3401 | 104.3618 | 111.4035
| DorionWind2060RCP8.5 | Dorion | Wind | RCP8.5 | 2060 | 83.6592 | 90.3019 | 97.3495 | 104.3383 | 111.3464
| DorionWind2065RCP8.5 | Dorion | Wind | RCP8.5 | 2065 | 83.6917 | 90.3253 | 97.3621 | 104.345 | 111.3428
| DorionWind2070RCP8.5 | Dorion | Wind | RCP8.5 | 2070 | 83.9054 | 90.5788 | 97.6597 | 104.687 | 111.725
| DorionWind2075RCP8.5 | Dorion | Wind | RCP8.5 | 2075 | 84.0867 | 90.809 | 97.9449 | 105.0223 | 112.1108
| DorionWind2080RCP8.5 | Dorion | Wind | RCP8.5 | 2080 | 84.2679 | 91.0392 | 98.23 | 105.3576 | 112.4966
| DorionWind2085RCP8.5 | Dorion | Wind | RCP8.5 | 2085 | 84.6332 | 91.5069 | 98.8222 | 106.0566 | 113.3056
| DorionWind2090RCP8.5 | Dorion | Wind | RCP8.5 | 2090 | 84.9984 | 91.9746 | 99.4144 | 106.7556 | 114.1147
| DorionWind2095RCP8.5 | Dorion | Wind | RCP8.5 | 2095 | 84.9984 | 91.9746 | 99.4144 | 106.7556 | 114.1147
| DorionWind2100RCP8.5 | Dorion | Wind | RCP8.5 | 2100 | 84.9984 | 91.9746 | 99.4144 | 106.7556 | 114.1147
| DresdenIce Accretion2023RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2023 | 17.1178 | 20.5218 | 24.825 | 28.1087 | 31.4055
| DresdenIce Accretion2025RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2025 | 17.0105 | 20.4145 | 24.7167 | 27.9957 | 31.2847
| DresdenIce Accretion2030RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2030 | 16.9033 | 20.3073 | 24.6083 | 27.8827 | 31.164
| DresdenIce Accretion2035RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2035 | 16.796 | 20.2001 | 24.5 | 27.7697 | 31.0433
| DresdenIce Accretion2040RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2040 | 16.6887 | 20.0929 | 24.3917 | 27.6567 | 30.9225
| DresdenIce Accretion2045RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2045 | 16.5814 | 19.9857 | 24.2833 | 27.5437 | 30.8018
| DresdenIce Accretion2050RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2050 | 16.081 | 19.4386 | 23.67 | 26.877 | 30.0762
| DresdenIce Accretion2055RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2055 | 15.6879 | 18.9987 | 23.165 | 26.3233 | 29.4714
| DresdenIce Accretion2060RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2060 | 15.2947 | 18.5588 | 22.66 | 25.7696 | 28.8666
| DresdenIce Accretion2065RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2065 | 14.9015 | 18.1189 | 22.155 | 25.2159 | 28.2618
| DresdenIce Accretion2070RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2070 | 14.5084 | 17.679 | 21.65 | 24.6622 | 27.657
| DresdenIce Accretion2075RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2075 | 14.1286 | 17.2398 | 21.1375 | 24.0925 | 27.027
| DresdenIce Accretion2080RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2080 | 13.7488 | 16.8006 | 20.625 | 23.5228 | 26.397
| DresdenIce Accretion2085RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2085 | 13.3689 | 16.3614 | 20.1125 | 22.9531 | 25.767
| DresdenIce Accretion2090RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2090 | 12.9891 | 15.9222 | 19.6 | 22.3834 | 25.137
| DresdenIce Accretion2095RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2095 | 12.6093 | 15.483 | 19.0875 | 21.8137 | 24.507
| DresdenIce Accretion2100RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2100 | 12.2295 | 15.0437 | 18.575 | 21.244 | 23.877
| DresdenIce Accretion2023RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2023 | 17.1178 | 20.5218 | 24.825 | 28.1087 | 31.4055
| DresdenIce Accretion2025RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2025 | 17.0105 | 20.4145 | 24.7167 | 27.9957 | 31.2847
| DresdenIce Accretion2030RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2030 | 16.9033 | 20.3073 | 24.6083 | 27.8827 | 31.164
| DresdenIce Accretion2035RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2035 | 16.796 | 20.2001 | 24.5 | 27.7697 | 31.0433
| DresdenIce Accretion2040RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2040 | 16.6887 | 20.0929 | 24.3917 | 27.6567 | 30.9225
| DresdenIce Accretion2045RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2045 | 16.5814 | 19.9857 | 24.2833 | 27.5437 | 30.8018
| DresdenIce Accretion2050RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2050 | 16.081 | 19.4386 | 23.67 | 26.877 | 30.0762
| DresdenIce Accretion2055RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2055 | 15.6879 | 18.9987 | 23.165 | 26.3233 | 29.4714
| DresdenIce Accretion2060RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2060 | 15.2947 | 18.5588 | 22.66 | 25.7696 | 28.8666
| DresdenIce Accretion2065RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2065 | 14.9015 | 18.1189 | 22.155 | 25.2159 | 28.2618
| DresdenIce Accretion2070RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2070 | 14.5084 | 17.679 | 21.65 | 24.6622 | 27.657
| DresdenIce Accretion2075RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2075 | 13.9387 | 17.0202 | 20.8812 | 23.8077 | 26.712
| DresdenIce Accretion2080RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2080 | 13.3689 | 16.3614 | 20.1125 | 22.9531 | 25.767
| DresdenIce Accretion2085RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2085 | 12.7992 | 15.7026 | 19.3438 | 22.0986 | 24.822
| DresdenIce Accretion2090RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2090 | 11.3597 | 14.0062 | 17.3167 | 19.8221 | 22.2915
| DresdenIce Accretion2095RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2095 | 10.4899 | 12.9687 | 16.0583 | 18.4002 | 20.706
| DresdenIce Accretion2100RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2100 | 9.6201 | 11.9312 | 14.8 | 16.9782 | 19.1205
| DresdenIce Accretion2023RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2023 | 17.1178 | 20.5218 | 24.825 | 28.1087 | 31.4055
| DresdenIce Accretion2025RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2025 | 16.9033 | 20.3073 | 24.6083 | 27.8827 | 31.164
| DresdenIce Accretion2030RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2030 | 16.6887 | 20.0929 | 24.3917 | 27.6567 | 30.9225
| DresdenIce Accretion2035RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2035 | 16.4742 | 19.8785 | 24.175 | 27.4307 | 30.681
| DresdenIce Accretion2040RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2040 | 15.8189 | 19.1453 | 23.3333 | 26.5079 | 29.673
| DresdenIce Accretion2045RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2045 | 15.1636 | 18.4122 | 22.4917 | 25.5851 | 28.665
| DresdenIce Accretion2050RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2050 | 13.7488 | 16.8006 | 20.625 | 23.5228 | 26.397
| DresdenIce Accretion2055RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2055 | 12.9891 | 15.9222 | 19.6 | 22.3834 | 25.137
| DresdenIce Accretion2060RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2060 | 11.3597 | 14.0062 | 17.3167 | 19.8221 | 22.2915
| DresdenIce Accretion2065RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2065 | 10.4899 | 12.9687 | 16.0583 | 18.4002 | 20.706
| DresdenIce Accretion2070RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2070 | 9.1388 | 11.3572 | 14.1083 | 16.1872 | 18.2385
| DresdenIce Accretion2075RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2075 | 8.6575 | 10.7831 | 13.4167 | 15.3962 | 17.3565
| DresdenIce Accretion2080RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2080 | 8.1762 | 10.209 | 12.725 | 14.6052 | 16.4745
| DresdenIce Accretion2085RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2085 | 7.5151 | 9.4101 | 11.7625 | 13.5176 | 15.2617
| DresdenIce Accretion2090RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2090 | 6.8541 | 8.6113 | 10.8 | 12.43 | 14.049
| DresdenIce Accretion2095RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2095 | 6.8541 | 8.6113 | 10.8 | 12.43 | 14.049
| DresdenIce Accretion2100RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2100 | 6.8541 | 8.6113 | 10.8 | 12.43 | 14.049
| DresdenWind2023RCP4.5 | Dresden | Wind | RCP4.5 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.368
| DresdenWind2025RCP4.5 | Dresden | Wind | RCP4.5 | 2025 | 85.0909 | 91.6975 | 98.6697 | 105.6307 | 112.5951
| DresdenWind2030RCP4.5 | Dresden | Wind | RCP4.5 | 2030 | 85.1798 | 91.8175 | 98.8297 | 105.8247 | 112.8223
| DresdenWind2035RCP4.5 | Dresden | Wind | RCP4.5 | 2035 | 85.2686 | 91.9375 | 98.9898 | 106.0187 | 113.0495
| DresdenWind2040RCP4.5 | Dresden | Wind | RCP4.5 | 2040 | 85.3575 | 92.0575 | 99.1499 | 106.2127 | 113.2766
| DresdenWind2045RCP4.5 | Dresden | Wind | RCP4.5 | 2045 | 85.4463 | 92.1775 | 99.3099 | 106.4067 | 113.5038
| DresdenWind2050RCP4.5 | Dresden | Wind | RCP4.5 | 2050 | 85.6435 | 92.4415 | 99.6582 | 106.8272 | 113.9969
| DresdenWind2055RCP4.5 | Dresden | Wind | RCP4.5 | 2055 | 85.7518 | 92.5855 | 99.8463 | 107.0537 | 114.2627
| DresdenWind2060RCP4.5 | Dresden | Wind | RCP4.5 | 2060 | 85.8601 | 92.7295 | 100.0345 | 107.2802 | 114.5286
| DresdenWind2065RCP4.5 | Dresden | Wind | RCP4.5 | 2065 | 85.9684 | 92.8735 | 100.2226 | 107.5067 | 114.7945
| DresdenWind2070RCP4.5 | Dresden | Wind | RCP4.5 | 2070 | 86.0768 | 93.0175 | 100.4108 | 107.7332 | 115.0604
| DresdenWind2075RCP4.5 | Dresden | Wind | RCP4.5 | 2075 | 86.2601 | 93.256 | 100.7179 | 108.0967 | 115.485
| DresdenWind2080RCP4.5 | Dresden | Wind | RCP4.5 | 2080 | 86.4435 | 93.4945 | 101.0249 | 108.4602 | 115.9095
| DresdenWind2085RCP4.5 | Dresden | Wind | RCP4.5 | 2085 | 86.6268 | 93.7329 | 101.332 | 108.8237 | 116.334
| DresdenWind2090RCP4.5 | Dresden | Wind | RCP4.5 | 2090 | 86.8101 | 93.9714 | 101.6391 | 109.1872 | 116.7586
| DresdenWind2095RCP4.5 | Dresden | Wind | RCP4.5 | 2095 | 86.9935 | 94.2099 | 101.9461 | 109.5507 | 117.1831
| DresdenWind2100RCP4.5 | Dresden | Wind | RCP4.5 | 2100 | 87.1768 | 94.4484 | 102.2532 | 109.9143 | 117.6076
| DresdenWind2023RCP6.0 | Dresden | Wind | RCP6.0 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.368
| DresdenWind2025RCP6.0 | Dresden | Wind | RCP6.0 | 2025 | 85.0909 | 91.6975 | 98.6697 | 105.6307 | 112.5951
| DresdenWind2030RCP6.0 | Dresden | Wind | RCP6.0 | 2030 | 85.1798 | 91.8175 | 98.8297 | 105.8247 | 112.8223
| DresdenWind2035RCP6.0 | Dresden | Wind | RCP6.0 | 2035 | 85.2686 | 91.9375 | 98.9898 | 106.0187 | 113.0495
| DresdenWind2040RCP6.0 | Dresden | Wind | RCP6.0 | 2040 | 85.3575 | 92.0575 | 99.1499 | 106.2127 | 113.2766
| DresdenWind2045RCP6.0 | Dresden | Wind | RCP6.0 | 2045 | 85.4463 | 92.1775 | 99.3099 | 106.4067 | 113.5038
| DresdenWind2050RCP6.0 | Dresden | Wind | RCP6.0 | 2050 | 85.6435 | 92.4415 | 99.6582 | 106.8272 | 113.9969
| DresdenWind2055RCP6.0 | Dresden | Wind | RCP6.0 | 2055 | 85.7518 | 92.5855 | 99.8463 | 107.0537 | 114.2627
| DresdenWind2060RCP6.0 | Dresden | Wind | RCP6.0 | 2060 | 85.8601 | 92.7295 | 100.0345 | 107.2802 | 114.5286
| DresdenWind2065RCP6.0 | Dresden | Wind | RCP6.0 | 2065 | 85.9684 | 92.8735 | 100.2226 | 107.5067 | 114.7945
| DresdenWind2070RCP6.0 | Dresden | Wind | RCP6.0 | 2070 | 86.0768 | 93.0175 | 100.4108 | 107.7332 | 115.0604
| DresdenWind2075RCP6.0 | Dresden | Wind | RCP6.0 | 2075 | 86.3518 | 93.3752 | 100.8714 | 108.2784 | 115.6972
| DresdenWind2080RCP6.0 | Dresden | Wind | RCP6.0 | 2080 | 86.6268 | 93.7329 | 101.332 | 108.8237 | 116.334
| DresdenWind2085RCP6.0 | Dresden | Wind | RCP6.0 | 2085 | 86.9018 | 94.0907 | 101.7926 | 109.369 | 116.9708
| DresdenWind2090RCP6.0 | Dresden | Wind | RCP6.0 | 2090 | 87.5661 | 94.9375 | 102.8673 | 110.6343 | 118.4381
| DresdenWind2095RCP6.0 | Dresden | Wind | RCP6.0 | 2095 | 87.9554 | 95.4266 | 103.4815 | 111.3543 | 119.2685
| DresdenWind2100RCP6.0 | Dresden | Wind | RCP6.0 | 2100 | 88.3446 | 95.9157 | 104.0956 | 112.0744 | 120.099
| DresdenWind2023RCP8.5 | Dresden | Wind | RCP8.5 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.368
| DresdenWind2025RCP8.5 | Dresden | Wind | RCP8.5 | 2025 | 85.1798 | 91.8175 | 98.8297 | 105.8247 | 112.8223
| DresdenWind2030RCP8.5 | Dresden | Wind | RCP8.5 | 2030 | 85.3575 | 92.0575 | 99.1499 | 106.2127 | 113.2766
| DresdenWind2035RCP8.5 | Dresden | Wind | RCP8.5 | 2035 | 85.5352 | 92.2975 | 99.47 | 106.6007 | 113.731
| DresdenWind2040RCP8.5 | Dresden | Wind | RCP8.5 | 2040 | 85.7157 | 92.5375 | 99.7836 | 106.9782 | 114.1741
| DresdenWind2045RCP8.5 | Dresden | Wind | RCP8.5 | 2045 | 85.8962 | 92.7775 | 100.0972 | 107.3557 | 114.6173
| DresdenWind2050RCP8.5 | Dresden | Wind | RCP8.5 | 2050 | 86.4435 | 93.4945 | 101.0249 | 108.4602 | 115.9095
| DresdenWind2055RCP8.5 | Dresden | Wind | RCP8.5 | 2055 | 86.8101 | 93.9714 | 101.6391 | 109.1872 | 116.7586
| DresdenWind2060RCP8.5 | Dresden | Wind | RCP8.5 | 2060 | 87.5661 | 94.9375 | 102.8673 | 110.6343 | 118.4381
| DresdenWind2065RCP8.5 | Dresden | Wind | RCP8.5 | 2065 | 87.9554 | 95.4266 | 103.4815 | 111.3543 | 119.2685
| DresdenWind2070RCP8.5 | Dresden | Wind | RCP8.5 | 2070 | 88.5251 | 96.1405 | 104.3733 | 112.3994 | 120.4677
| DresdenWind2075RCP8.5 | Dresden | Wind | RCP8.5 | 2075 | 88.7057 | 96.3654 | 104.6509 | 112.7245 | 120.8364
| DresdenWind2080RCP8.5 | Dresden | Wind | RCP8.5 | 2080 | 88.8862 | 96.5902 | 104.9286 | 113.0496 | 121.205
| DresdenWind2085RCP8.5 | Dresden | Wind | RCP8.5 | 2085 | 89.3855 | 97.219 | 105.7224 | 113.9828 | 122.2831
| DresdenWind2090RCP8.5 | Dresden | Wind | RCP8.5 | 2090 | 89.8847 | 97.8479 | 106.5162 | 114.9161 | 123.3612
| DresdenWind2095RCP8.5 | Dresden | Wind | RCP8.5 | 2095 | 89.8847 | 97.8479 | 106.5162 | 114.9161 | 123.3612
| DresdenWind2100RCP8.5 | Dresden | Wind | RCP8.5 | 2100 | 89.8847 | 97.8479 | 106.5162 | 114.9161 | 123.3612
| DrydenIce Accretion2023RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2023 | 10.3458 | 12.3637 | 14.924 | 16.8799 | 18.8219
| DrydenIce Accretion2025RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2025 | 10.3767 | 12.4005 | 14.9683 | 16.93 | 18.8777
| DrydenIce Accretion2030RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2030 | 10.4075 | 12.4373 | 15.0127 | 16.9801 | 18.9336
| DrydenIce Accretion2035RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2035 | 10.4384 | 12.4741 | 15.057 | 17.0302 | 18.9895
| DrydenIce Accretion2040RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2040 | 10.4692 | 12.5109 | 15.1013 | 17.0803 | 19.0453
| DrydenIce Accretion2045RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2045 | 10.5001 | 12.5477 | 15.1457 | 17.1304 | 19.1012
| DrydenIce Accretion2050RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2050 | 10.5387 | 12.5891 | 15.19 | 17.1774 | 19.1535
| DrydenIce Accretion2055RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2055 | 10.5465 | 12.5938 | 15.19 | 17.1742 | 19.15
| DrydenIce Accretion2060RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2060 | 10.5543 | 12.5984 | 15.19 | 17.171 | 19.1465
| DrydenIce Accretion2065RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2065 | 10.5621 | 12.6031 | 15.19 | 17.1679 | 19.1429
| DrydenIce Accretion2070RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2070 | 10.5699 | 12.6077 | 15.19 | 17.1647 | 19.1394
| DrydenIce Accretion2075RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2075 | 10.5585 | 12.5922 | 15.1713 | 17.1436 | 19.1159
| DrydenIce Accretion2080RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2080 | 10.5472 | 12.5767 | 15.1527 | 17.1225 | 19.0924
| DrydenIce Accretion2085RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2085 | 10.5358 | 12.5612 | 15.134 | 17.1014 | 19.0688
| DrydenIce Accretion2090RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2090 | 10.5244 | 12.5457 | 15.1153 | 17.0803 | 19.0453
| DrydenIce Accretion2095RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2095 | 10.5131 | 12.5302 | 15.0967 | 17.0592 | 19.0218
| DrydenIce Accretion2100RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2100 | 10.5017 | 12.5147 | 15.078 | 17.0381 | 18.9983
| DrydenIce Accretion2023RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2023 | 10.3458 | 12.3637 | 14.924 | 16.8799 | 18.8219
| DrydenIce Accretion2025RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2025 | 10.3767 | 12.4005 | 14.9683 | 16.93 | 18.8777
| DrydenIce Accretion2030RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2030 | 10.4075 | 12.4373 | 15.0127 | 16.9801 | 18.9336
| DrydenIce Accretion2035RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2035 | 10.4384 | 12.4741 | 15.057 | 17.0302 | 18.9895
| DrydenIce Accretion2040RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2040 | 10.4692 | 12.5109 | 15.1013 | 17.0803 | 19.0453
| DrydenIce Accretion2045RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2045 | 10.5001 | 12.5477 | 15.1457 | 17.1304 | 19.1012
| DrydenIce Accretion2050RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2050 | 10.5387 | 12.5891 | 15.19 | 17.1774 | 19.1535
| DrydenIce Accretion2055RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2055 | 10.5465 | 12.5938 | 15.19 | 17.1742 | 19.15
| DrydenIce Accretion2060RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2060 | 10.5543 | 12.5984 | 15.19 | 17.171 | 19.1465
| DrydenIce Accretion2065RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2065 | 10.5621 | 12.6031 | 15.19 | 17.1679 | 19.1429
| DrydenIce Accretion2070RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2070 | 10.5699 | 12.6077 | 15.19 | 17.1647 | 19.1394
| DrydenIce Accretion2075RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2075 | 10.5529 | 12.5845 | 15.162 | 17.1331 | 19.1041
| DrydenIce Accretion2080RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2080 | 10.5358 | 12.5612 | 15.134 | 17.1014 | 19.0688
| DrydenIce Accretion2085RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2085 | 10.5188 | 12.538 | 15.106 | 17.0698 | 19.0336
| DrydenIce Accretion2090RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2090 | 10.5374 | 12.5612 | 15.134 | 17.1014 | 19.0688
| DrydenIce Accretion2095RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2095 | 10.5731 | 12.6077 | 15.19 | 17.1647 | 19.1394
| DrydenIce Accretion2100RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2100 | 10.6089 | 12.6542 | 15.246 | 17.228 | 19.21
| DrydenIce Accretion2023RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2023 | 10.3458 | 12.3637 | 14.924 | 16.8799 | 18.8219
| DrydenIce Accretion2025RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2025 | 10.4075 | 12.4373 | 15.0127 | 16.9801 | 18.9336
| DrydenIce Accretion2030RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2030 | 10.4692 | 12.5109 | 15.1013 | 17.0803 | 19.0453
| DrydenIce Accretion2035RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2035 | 10.5309 | 12.5845 | 15.19 | 17.1805 | 19.157
| DrydenIce Accretion2040RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2040 | 10.5439 | 12.5922 | 15.19 | 17.1752 | 19.1512
| DrydenIce Accretion2045RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2045 | 10.5569 | 12.6 | 15.19 | 17.17 | 19.1453
| DrydenIce Accretion2050RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2050 | 10.5472 | 12.5767 | 15.1527 | 17.1225 | 19.0924
| DrydenIce Accretion2055RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2055 | 10.5244 | 12.5457 | 15.1153 | 17.0803 | 19.0453
| DrydenIce Accretion2060RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2060 | 10.5374 | 12.5612 | 15.134 | 17.1014 | 19.0688
| DrydenIce Accretion2065RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2065 | 10.5731 | 12.6077 | 15.19 | 17.1647 | 19.1394
| DrydenIce Accretion2070RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2070 | 10.7095 | 12.7859 | 15.4187 | 17.4336 | 19.4452
| DrydenIce Accretion2075RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2075 | 10.8102 | 12.9176 | 15.5913 | 17.6393 | 19.6804
| DrydenIce Accretion2080RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2080 | 10.9109 | 13.0493 | 15.764 | 17.845 | 19.9156
| DrydenIce Accretion2085RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2085 | 10.6868 | 12.7762 | 15.428 | 17.4574 | 19.4746
| DrydenIce Accretion2090RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2090 | 10.4627 | 12.5031 | 15.092 | 17.0698 | 19.0336
| DrydenIce Accretion2095RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2095 | 10.4627 | 12.5031 | 15.092 | 17.0698 | 19.0336
| DrydenIce Accretion2100RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2100 | 10.4627 | 12.5031 | 15.092 | 17.0698 | 19.0336
| DrydenWind2023RCP4.5 | Dryden | Wind | RCP4.5 | 2023 | 72.4672 | 78.0497 | 83.9328 | 89.8171 | 95.693
| DrydenWind2025RCP4.5 | Dryden | Wind | RCP4.5 | 2025 | 72.5035 | 78.0809 | 83.9538 | 89.8306 | 95.7009
| DrydenWind2030RCP4.5 | Dryden | Wind | RCP4.5 | 2030 | 72.5398 | 78.1122 | 83.9748 | 89.844 | 95.7089
| DrydenWind2035RCP4.5 | Dryden | Wind | RCP4.5 | 2035 | 72.576 | 78.1434 | 83.9958 | 89.8575 | 95.7169
| DrydenWind2040RCP4.5 | Dryden | Wind | RCP4.5 | 2040 | 72.6123 | 78.1747 | 84.0168 | 89.871 | 95.7249
| DrydenWind2045RCP4.5 | Dryden | Wind | RCP4.5 | 2045 | 72.6486 | 78.2059 | 84.0378 | 89.8845 | 95.7329
| DrydenWind2050RCP4.5 | Dryden | Wind | RCP4.5 | 2050 | 72.7777 | 78.3434 | 84.1831 | 90.0382 | 95.8941
| DrydenWind2055RCP4.5 | Dryden | Wind | RCP4.5 | 2055 | 72.8705 | 78.4497 | 84.3074 | 90.1784 | 96.0473
| DrydenWind2060RCP4.5 | Dryden | Wind | RCP4.5 | 2060 | 72.9634 | 78.5559 | 84.4318 | 90.3186 | 96.2005
| DrydenWind2065RCP4.5 | Dryden | Wind | RCP4.5 | 2065 | 73.0562 | 78.6622 | 84.5561 | 90.4588 | 96.3537
| DrydenWind2070RCP4.5 | Dryden | Wind | RCP4.5 | 2070 | 73.1491 | 78.7684 | 84.6804 | 90.599 | 96.5069
| DrydenWind2075RCP4.5 | Dryden | Wind | RCP4.5 | 2075 | 73.2216 | 78.8504 | 84.7742 | 90.7024 | 96.6218
| DrydenWind2080RCP4.5 | Dryden | Wind | RCP4.5 | 2080 | 73.2941 | 78.9324 | 84.868 | 90.8058 | 96.7368
| DrydenWind2085RCP4.5 | Dryden | Wind | RCP4.5 | 2085 | 73.3666 | 79.0145 | 84.9618 | 90.9091 | 96.8517
| DrydenWind2090RCP4.5 | Dryden | Wind | RCP4.5 | 2090 | 73.4392 | 79.0965 | 85.0556 | 91.0125 | 96.9666
| DrydenWind2095RCP4.5 | Dryden | Wind | RCP4.5 | 2095 | 73.5117 | 79.1785 | 85.1494 | 91.1158 | 97.0815
| DrydenWind2100RCP4.5 | Dryden | Wind | RCP4.5 | 2100 | 73.5842 | 79.2606 | 85.2432 | 91.2192 | 97.1964
| DrydenWind2023RCP6.0 | Dryden | Wind | RCP6.0 | 2023 | 72.4672 | 78.0497 | 83.9328 | 89.8171 | 95.693
| DrydenWind2025RCP6.0 | Dryden | Wind | RCP6.0 | 2025 | 72.5035 | 78.0809 | 83.9538 | 89.8306 | 95.7009
| DrydenWind2030RCP6.0 | Dryden | Wind | RCP6.0 | 2030 | 72.5398 | 78.1122 | 83.9748 | 89.844 | 95.7089
| DrydenWind2035RCP6.0 | Dryden | Wind | RCP6.0 | 2035 | 72.576 | 78.1434 | 83.9958 | 89.8575 | 95.7169
| DrydenWind2040RCP6.0 | Dryden | Wind | RCP6.0 | 2040 | 72.6123 | 78.1747 | 84.0168 | 89.871 | 95.7249
| DrydenWind2045RCP6.0 | Dryden | Wind | RCP6.0 | 2045 | 72.6486 | 78.2059 | 84.0378 | 89.8845 | 95.7329
| DrydenWind2050RCP6.0 | Dryden | Wind | RCP6.0 | 2050 | 72.7777 | 78.3434 | 84.1831 | 90.0382 | 95.8941
| DrydenWind2055RCP6.0 | Dryden | Wind | RCP6.0 | 2055 | 72.8705 | 78.4497 | 84.3074 | 90.1784 | 96.0473
| DrydenWind2060RCP6.0 | Dryden | Wind | RCP6.0 | 2060 | 72.9634 | 78.5559 | 84.4318 | 90.3186 | 96.2005
| DrydenWind2065RCP6.0 | Dryden | Wind | RCP6.0 | 2065 | 73.0562 | 78.6622 | 84.5561 | 90.4588 | 96.3537
| DrydenWind2070RCP6.0 | Dryden | Wind | RCP6.0 | 2070 | 73.1491 | 78.7684 | 84.6804 | 90.599 | 96.5069
| DrydenWind2075RCP6.0 | Dryden | Wind | RCP6.0 | 2075 | 73.2578 | 78.8914 | 84.8211 | 90.7541 | 96.6793
| DrydenWind2080RCP6.0 | Dryden | Wind | RCP6.0 | 2080 | 73.3666 | 79.0145 | 84.9618 | 90.9091 | 96.8517
| DrydenWind2085RCP6.0 | Dryden | Wind | RCP6.0 | 2085 | 73.4754 | 79.1375 | 85.1025 | 91.0642 | 97.024
| DrydenWind2090RCP6.0 | Dryden | Wind | RCP6.0 | 2090 | 73.8091 | 79.5626 | 85.638 | 91.6926 | 97.7518
| DrydenWind2095RCP6.0 | Dryden | Wind | RCP6.0 | 2095 | 74.0339 | 79.8647 | 86.0328 | 92.1659 | 98.3072
| DrydenWind2100RCP6.0 | Dryden | Wind | RCP6.0 | 2100 | 74.2588 | 80.1667 | 86.4276 | 92.6393 | 98.8626
| DrydenWind2023RCP8.5 | Dryden | Wind | RCP8.5 | 2023 | 72.4672 | 78.0497 | 83.9328 | 89.8171 | 95.693
| DrydenWind2025RCP8.5 | Dryden | Wind | RCP8.5 | 2025 | 72.5398 | 78.1122 | 83.9748 | 89.844 | 95.7089
| DrydenWind2030RCP8.5 | Dryden | Wind | RCP8.5 | 2030 | 72.6123 | 78.1747 | 84.0168 | 89.871 | 95.7249
| DrydenWind2035RCP8.5 | Dryden | Wind | RCP8.5 | 2035 | 72.6848 | 78.2372 | 84.0588 | 89.898 | 95.7408
| DrydenWind2040RCP8.5 | Dryden | Wind | RCP8.5 | 2040 | 72.8396 | 78.4143 | 84.266 | 90.1317 | 95.9962
| DrydenWind2045RCP8.5 | Dryden | Wind | RCP8.5 | 2045 | 72.9943 | 78.5913 | 84.4732 | 90.3654 | 96.2516
| DrydenWind2050RCP8.5 | Dryden | Wind | RCP8.5 | 2050 | 73.2941 | 78.9324 | 84.868 | 90.8058 | 96.7368
| DrydenWind2055RCP8.5 | Dryden | Wind | RCP8.5 | 2055 | 73.4392 | 79.0965 | 85.0556 | 91.0125 | 96.9666
| DrydenWind2060RCP8.5 | Dryden | Wind | RCP8.5 | 2060 | 73.8091 | 79.5626 | 85.638 | 91.6926 | 97.7518
| DrydenWind2065RCP8.5 | Dryden | Wind | RCP8.5 | 2065 | 74.0339 | 79.8647 | 86.0328 | 92.1659 | 98.3072
| DrydenWind2070RCP8.5 | Dryden | Wind | RCP8.5 | 2070 | 74.4643 | 80.4193 | 86.7356 | 92.9988 | 99.2712
| DrydenWind2075RCP8.5 | Dryden | Wind | RCP8.5 | 2075 | 74.6698 | 80.6719 | 87.0436 | 93.3584 | 99.6798
| DrydenWind2080RCP8.5 | Dryden | Wind | RCP8.5 | 2080 | 74.8753 | 80.9245 | 87.3516 | 93.7179 | 100.0884
| DrydenWind2085RCP8.5 | Dryden | Wind | RCP8.5 | 2085 | 75.1038 | 81.2136 | 87.717 | 94.1448 | 100.5815
| DrydenWind2090RCP8.5 | Dryden | Wind | RCP8.5 | 2090 | 75.3323 | 81.5026 | 88.0824 | 94.5717 | 101.0747
| DrydenWind2095RCP8.5 | Dryden | Wind | RCP8.5 | 2095 | 75.3323 | 81.5026 | 88.0824 | 94.5717 | 101.0747
| DrydenWind2100RCP8.5 | Dryden | Wind | RCP8.5 | 2100 | 75.3323 | 81.5026 | 88.0824 | 94.5717 | 101.0747
| DundalkIce Accretion2023RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2023 | 15.4005 | 18.4791 | 22.396 | 25.3821 | 28.3576
| DundalkIce Accretion2025RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2025 | 15.4209 | 18.5156 | 22.451 | 25.4525 | 28.4407
| DundalkIce Accretion2030RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2030 | 15.4413 | 18.5522 | 22.506 | 25.5229 | 28.5239
| DundalkIce Accretion2035RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2035 | 15.4617 | 18.5887 | 22.561 | 25.5934 | 28.607
| DundalkIce Accretion2040RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2040 | 15.4821 | 18.6252 | 22.616 | 25.6638 | 28.6902
| DundalkIce Accretion2045RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2045 | 15.5025 | 18.6617 | 22.671 | 25.7342 | 28.7734
| DundalkIce Accretion2050RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2050 | 15.4893 | 18.6727 | 22.7128 | 25.7997 | 28.8676
| DundalkIce Accretion2055RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2055 | 15.4556 | 18.6471 | 22.6996 | 25.7947 | 28.8787
| DundalkIce Accretion2060RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2060 | 15.4219 | 18.6215 | 22.6864 | 25.7898 | 28.8898
| DundalkIce Accretion2065RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2065 | 15.3882 | 18.596 | 22.6732 | 25.7848 | 28.9009
| DundalkIce Accretion2070RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2070 | 15.3545 | 18.5704 | 22.66 | 25.7798 | 28.912
| DundalkIce Accretion2075RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2075 | 15.3341 | 18.5735 | 22.6893 | 25.8295 | 28.9813
| DundalkIce Accretion2080RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2080 | 15.3137 | 18.5765 | 22.7187 | 25.8793 | 29.0506
| DundalkIce Accretion2085RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2085 | 15.2933 | 18.5795 | 22.748 | 25.929 | 29.1199
| DundalkIce Accretion2090RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2090 | 15.2729 | 18.5826 | 22.7773 | 25.9787 | 29.1892
| DundalkIce Accretion2095RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2095 | 15.2525 | 18.5856 | 22.8067 | 26.0284 | 29.2585
| DundalkIce Accretion2100RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2100 | 15.2321 | 18.5887 | 22.836 | 26.0781 | 29.3278
| DundalkIce Accretion2023RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2023 | 15.4005 | 18.4791 | 22.396 | 25.3821 | 28.3576
| DundalkIce Accretion2025RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2025 | 15.4209 | 18.5156 | 22.451 | 25.4525 | 28.4407
| DundalkIce Accretion2030RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2030 | 15.4413 | 18.5522 | 22.506 | 25.5229 | 28.5239
| DundalkIce Accretion2035RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2035 | 15.4617 | 18.5887 | 22.561 | 25.5934 | 28.607
| DundalkIce Accretion2040RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2040 | 15.4821 | 18.6252 | 22.616 | 25.6638 | 28.6902
| DundalkIce Accretion2045RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2045 | 15.5025 | 18.6617 | 22.671 | 25.7342 | 28.7734
| DundalkIce Accretion2050RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2050 | 15.4893 | 18.6727 | 22.7128 | 25.7997 | 28.8676
| DundalkIce Accretion2055RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2055 | 15.4556 | 18.6471 | 22.6996 | 25.7947 | 28.8787
| DundalkIce Accretion2060RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2060 | 15.4219 | 18.6215 | 22.6864 | 25.7898 | 28.8898
| DundalkIce Accretion2065RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2065 | 15.3882 | 18.596 | 22.6732 | 25.7848 | 28.9009
| DundalkIce Accretion2070RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2070 | 15.3545 | 18.5704 | 22.66 | 25.7798 | 28.912
| DundalkIce Accretion2075RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2075 | 15.3239 | 18.575 | 22.704 | 25.8544 | 29.0159
| DundalkIce Accretion2080RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2080 | 15.2933 | 18.5795 | 22.748 | 25.929 | 29.1199
| DundalkIce Accretion2085RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2085 | 15.2627 | 18.5841 | 22.792 | 26.0036 | 29.2238
| DundalkIce Accretion2090RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2090 | 15.0331 | 18.3939 | 22.6453 | 25.8875 | 29.1245
| DundalkIce Accretion2095RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2095 | 14.834 | 18.1991 | 22.4547 | 25.697 | 28.9212
| DundalkIce Accretion2100RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2100 | 14.635 | 18.0044 | 22.264 | 25.5064 | 28.7179
| DundalkIce Accretion2023RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2023 | 15.4005 | 18.4791 | 22.396 | 25.3821 | 28.3576
| DundalkIce Accretion2025RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2025 | 15.4413 | 18.5522 | 22.506 | 25.5229 | 28.5239
| DundalkIce Accretion2030RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2030 | 15.4821 | 18.6252 | 22.616 | 25.6638 | 28.6902
| DundalkIce Accretion2035RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2035 | 15.5229 | 18.6982 | 22.726 | 25.8047 | 28.8565
| DundalkIce Accretion2040RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2040 | 15.4668 | 18.6556 | 22.704 | 25.7964 | 28.875
| DundalkIce Accretion2045RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2045 | 15.4107 | 18.613 | 22.682 | 25.7881 | 28.8935
| DundalkIce Accretion2050RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2050 | 15.3137 | 18.5765 | 22.7187 | 25.8793 | 29.0506
| DundalkIce Accretion2055RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2055 | 15.2729 | 18.5826 | 22.7773 | 25.9787 | 29.1892
| DundalkIce Accretion2060RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2060 | 15.0331 | 18.3939 | 22.6453 | 25.8875 | 29.1245
| DundalkIce Accretion2065RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2065 | 14.834 | 18.1991 | 22.4547 | 25.697 | 28.9212
| DundalkIce Accretion2070RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2070 | 14.2778 | 17.6087 | 21.8167 | 25.0174 | 28.2005
| DundalkIce Accretion2075RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2075 | 13.9206 | 17.2131 | 21.3693 | 24.5285 | 27.683
| DundalkIce Accretion2080RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2080 | 13.5634 | 16.8175 | 20.922 | 24.0396 | 27.1656
| DundalkIce Accretion2085RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2085 | 12.9817 | 16.1601 | 20.174 | 23.2192 | 26.2647
| DundalkIce Accretion2090RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2090 | 12.4 | 15.5027 | 19.426 | 22.3989 | 25.3638
| DundalkIce Accretion2095RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2095 | 12.4 | 15.5027 | 19.426 | 22.3989 | 25.3638
| DundalkIce Accretion2100RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2100 | 12.4 | 15.5027 | 19.426 | 22.3989 | 25.3638
| DundalkWind2023RCP4.5 | Dundalk | Wind | RCP4.5 | 2023 | 81.4271 | 87.7172 | 94.3384 | 100.9521 | 107.5672
| DundalkWind2025RCP4.5 | Dundalk | Wind | RCP4.5 | 2025 | 81.4352 | 87.7318 | 94.3619 | 100.9823 | 107.6065
| DundalkWind2030RCP4.5 | Dundalk | Wind | RCP4.5 | 2030 | 81.4433 | 87.7464 | 94.3854 | 101.0125 | 107.6458
| DundalkWind2035RCP4.5 | Dundalk | Wind | RCP4.5 | 2035 | 81.4514 | 87.7609 | 94.4089 | 101.0427 | 107.6851
| DundalkWind2040RCP4.5 | Dundalk | Wind | RCP4.5 | 2040 | 81.4596 | 87.7755 | 94.4324 | 101.0728 | 107.7244
| DundalkWind2045RCP4.5 | Dundalk | Wind | RCP4.5 | 2045 | 81.4677 | 87.7901 | 94.4559 | 101.103 | 107.7637
| DundalkWind2050RCP4.5 | Dundalk | Wind | RCP4.5 | 2050 | 81.531 | 87.8641 | 94.5433 | 101.2016 | 107.8758
| DundalkWind2055RCP4.5 | Dundalk | Wind | RCP4.5 | 2055 | 81.5862 | 87.9235 | 94.6072 | 101.27 | 107.9487
| DundalkWind2060RCP4.5 | Dundalk | Wind | RCP4.5 | 2060 | 81.6414 | 87.983 | 94.6712 | 101.3384 | 108.0216
| DundalkWind2065RCP4.5 | Dundalk | Wind | RCP4.5 | 2065 | 81.6966 | 88.0424 | 94.7351 | 101.4068 | 108.0944
| DundalkWind2070RCP4.5 | Dundalk | Wind | RCP4.5 | 2070 | 81.7518 | 88.1019 | 94.799 | 101.4752 | 108.1673
| DundalkWind2075RCP4.5 | Dundalk | Wind | RCP4.5 | 2075 | 81.8207 | 88.1951 | 94.9243 | 101.6294 | 108.3477
| DundalkWind2080RCP4.5 | Dundalk | Wind | RCP4.5 | 2080 | 81.8897 | 88.2884 | 95.0497 | 101.7836 | 108.5281
| DundalkWind2085RCP4.5 | Dundalk | Wind | RCP4.5 | 2085 | 81.9587 | 88.3816 | 95.175 | 101.9378 | 108.7085
| DundalkWind2090RCP4.5 | Dundalk | Wind | RCP4.5 | 2090 | 82.0277 | 88.4749 | 95.3003 | 102.0921 | 108.8888
| DundalkWind2095RCP4.5 | Dundalk | Wind | RCP4.5 | 2095 | 82.0967 | 88.5681 | 95.4257 | 102.2463 | 109.0692
| DundalkWind2100RCP4.5 | Dundalk | Wind | RCP4.5 | 2100 | 82.1657 | 88.6614 | 95.551 | 102.4005 | 109.2496
| DundalkWind2023RCP6.0 | Dundalk | Wind | RCP6.0 | 2023 | 81.4271 | 87.7172 | 94.3384 | 100.9521 | 107.5672
| DundalkWind2025RCP6.0 | Dundalk | Wind | RCP6.0 | 2025 | 81.4352 | 87.7318 | 94.3619 | 100.9823 | 107.6065
| DundalkWind2030RCP6.0 | Dundalk | Wind | RCP6.0 | 2030 | 81.4433 | 87.7464 | 94.3854 | 101.0125 | 107.6458
| DundalkWind2035RCP6.0 | Dundalk | Wind | RCP6.0 | 2035 | 81.4514 | 87.7609 | 94.4089 | 101.0427 | 107.6851
| DundalkWind2040RCP6.0 | Dundalk | Wind | RCP6.0 | 2040 | 81.4596 | 87.7755 | 94.4324 | 101.0728 | 107.7244
| DundalkWind2045RCP6.0 | Dundalk | Wind | RCP6.0 | 2045 | 81.4677 | 87.7901 | 94.4559 | 101.103 | 107.7637
| DundalkWind2050RCP6.0 | Dundalk | Wind | RCP6.0 | 2050 | 81.531 | 87.8641 | 94.5433 | 101.2016 | 107.8758
| DundalkWind2055RCP6.0 | Dundalk | Wind | RCP6.0 | 2055 | 81.5862 | 87.9235 | 94.6072 | 101.27 | 107.9487
| DundalkWind2060RCP6.0 | Dundalk | Wind | RCP6.0 | 2060 | 81.6414 | 87.983 | 94.6712 | 101.3384 | 108.0216
| DundalkWind2065RCP6.0 | Dundalk | Wind | RCP6.0 | 2065 | 81.6966 | 88.0424 | 94.7351 | 101.4068 | 108.0944
| DundalkWind2070RCP6.0 | Dundalk | Wind | RCP6.0 | 2070 | 81.7518 | 88.1019 | 94.799 | 101.4752 | 108.1673
| DundalkWind2075RCP6.0 | Dundalk | Wind | RCP6.0 | 2075 | 81.8552 | 88.2417 | 94.987 | 101.7065 | 108.4379
| DundalkWind2080RCP6.0 | Dundalk | Wind | RCP6.0 | 2080 | 81.9587 | 88.3816 | 95.175 | 101.9378 | 108.7085
| DundalkWind2085RCP6.0 | Dundalk | Wind | RCP6.0 | 2085 | 82.0622 | 88.5215 | 95.363 | 102.1692 | 108.979
| DundalkWind2090RCP6.0 | Dundalk | Wind | RCP6.0 | 2090 | 82.5526 | 89.1393 | 96.1369 | 103.0811 | 110.0247
| DundalkWind2095RCP6.0 | Dundalk | Wind | RCP6.0 | 2095 | 82.9395 | 89.6172 | 96.7229 | 103.7617 | 110.7999
| DundalkWind2100RCP6.0 | Dundalk | Wind | RCP6.0 | 2100 | 83.3264 | 90.0951 | 97.3088 | 104.4423 | 111.575
| DundalkWind2023RCP8.5 | Dundalk | Wind | RCP8.5 | 2023 | 81.4271 | 87.7172 | 94.3384 | 100.9521 | 107.5672
| DundalkWind2025RCP8.5 | Dundalk | Wind | RCP8.5 | 2025 | 81.4433 | 87.7464 | 94.3854 | 101.0125 | 107.6458
| DundalkWind2030RCP8.5 | Dundalk | Wind | RCP8.5 | 2030 | 81.4596 | 87.7755 | 94.4324 | 101.0728 | 107.7244
| DundalkWind2035RCP8.5 | Dundalk | Wind | RCP8.5 | 2035 | 81.4758 | 87.8046 | 94.4794 | 101.1332 | 107.803
| DundalkWind2040RCP8.5 | Dundalk | Wind | RCP8.5 | 2040 | 81.5678 | 87.9037 | 94.5859 | 101.2472 | 107.9244
| DundalkWind2045RCP8.5 | Dundalk | Wind | RCP8.5 | 2045 | 81.6598 | 88.0028 | 94.6925 | 101.3612 | 108.0459
| DundalkWind2050RCP8.5 | Dundalk | Wind | RCP8.5 | 2050 | 81.8897 | 88.2884 | 95.0497 | 101.7836 | 108.5281
| DundalkWind2055RCP8.5 | Dundalk | Wind | RCP8.5 | 2055 | 82.0277 | 88.4749 | 95.3003 | 102.0921 | 108.8888
| DundalkWind2060RCP8.5 | Dundalk | Wind | RCP8.5 | 2060 | 82.5526 | 89.1393 | 96.1369 | 103.0811 | 110.0247
| DundalkWind2065RCP8.5 | Dundalk | Wind | RCP8.5 | 2065 | 82.9395 | 89.6172 | 96.7229 | 103.7617 | 110.7999
| DundalkWind2070RCP8.5 | Dundalk | Wind | RCP8.5 | 2070 | 83.5401 | 90.369 | 97.6597 | 104.8513 | 112.0501
| DundalkWind2075RCP8.5 | Dundalk | Wind | RCP8.5 | 2075 | 83.7539 | 90.6429 | 98.0107 | 105.2603 | 112.5251
| DundalkWind2080RCP8.5 | Dundalk | Wind | RCP8.5 | 2080 | 83.9676 | 90.9168 | 98.3616 | 105.6693 | 113.0002
| DundalkWind2085RCP8.5 | Dundalk | Wind | RCP8.5 | 2085 | 84.1462 | 91.1354 | 98.6295 | 105.9811 | 113.3592
| DundalkWind2090RCP8.5 | Dundalk | Wind | RCP8.5 | 2090 | 84.3248 | 91.3539 | 98.8974 | 106.2929 | 113.7182
| DundalkWind2095RCP8.5 | Dundalk | Wind | RCP8.5 | 2095 | 84.3248 | 91.3539 | 98.8974 | 106.2929 | 113.7182
| DundalkWind2100RCP8.5 | Dundalk | Wind | RCP8.5 | 2100 | 84.3248 | 91.3539 | 98.8974 | 106.2929 | 113.7182
| DunnvilleIce Accretion2023RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
| DunnvilleIce Accretion2025RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2025 | 21.9182 | 26.3121 | 31.8773 | 36.1299 | 40.3738
| DunnvilleIce Accretion2030RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2030 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
| DunnvilleIce Accretion2035RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2035 | 21.7104 | 26.0819 | 31.632 | 35.8526 | 40.0781
| DunnvilleIce Accretion2040RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2040 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
| DunnvilleIce Accretion2045RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2045 | 21.5026 | 25.8517 | 31.3867 | 35.5754 | 39.7824
| DunnvilleIce Accretion2050RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2050 | 20.9221 | 25.2001 | 30.6368 | 34.7425 | 38.8765
| DunnvilleIce Accretion2055RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2055 | 20.4456 | 24.6636 | 30.0096 | 34.0483 | 38.1185
| DunnvilleIce Accretion2060RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2060 | 19.9691 | 24.1271 | 29.3824 | 33.354 | 37.3605
| DunnvilleIce Accretion2065RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2065 | 19.4926 | 23.5906 | 28.7552 | 32.6597 | 36.6025
| DunnvilleIce Accretion2070RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2070 | 19.0161 | 23.0541 | 28.128 | 31.9654 | 35.8445
| DunnvilleIce Accretion2075RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2075 | 18.8379 | 22.8682 | 27.9307 | 31.7605 | 35.6294
| DunnvilleIce Accretion2080RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2080 | 18.6598 | 22.6822 | 27.7333 | 31.5556 | 35.4144
| DunnvilleIce Accretion2085RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2085 | 18.4817 | 22.4963 | 27.536 | 31.3507 | 35.1994
| DunnvilleIce Accretion2090RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2090 | 18.3035 | 22.3104 | 27.3387 | 31.1458 | 34.9843
| DunnvilleIce Accretion2095RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2095 | 18.1254 | 22.1245 | 27.1413 | 30.9409 | 34.7693
| DunnvilleIce Accretion2100RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2100 | 17.9473 | 21.9386 | 26.944 | 30.736 | 34.5542
| DunnvilleIce Accretion2023RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
| DunnvilleIce Accretion2025RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2025 | 21.9182 | 26.3121 | 31.8773 | 36.1299 | 40.3738
| DunnvilleIce Accretion2030RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2030 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
| DunnvilleIce Accretion2035RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2035 | 21.7104 | 26.0819 | 31.632 | 35.8526 | 40.0781
| DunnvilleIce Accretion2040RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2040 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
| DunnvilleIce Accretion2045RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2045 | 21.5026 | 25.8517 | 31.3867 | 35.5754 | 39.7824
| DunnvilleIce Accretion2050RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2050 | 20.9221 | 25.2001 | 30.6368 | 34.7425 | 38.8765
| DunnvilleIce Accretion2055RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2055 | 20.4456 | 24.6636 | 30.0096 | 34.0483 | 38.1185
| DunnvilleIce Accretion2060RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2060 | 19.9691 | 24.1271 | 29.3824 | 33.354 | 37.3605
| DunnvilleIce Accretion2065RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2065 | 19.4926 | 23.5906 | 28.7552 | 32.6597 | 36.6025
| DunnvilleIce Accretion2070RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2070 | 19.0161 | 23.0541 | 28.128 | 31.9654 | 35.8445
| DunnvilleIce Accretion2075RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2075 | 18.7489 | 22.7752 | 27.832 | 31.6581 | 35.5219
| DunnvilleIce Accretion2080RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2080 | 18.4817 | 22.4963 | 27.536 | 31.3507 | 35.1994
| DunnvilleIce Accretion2085RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2085 | 18.2145 | 22.2174 | 27.24 | 31.0434 | 34.8768
| DunnvilleIce Accretion2090RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2090 | 17.2199 | 21.1063 | 25.9733 | 29.6633 | 33.3581
| DunnvilleIce Accretion2095RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2095 | 16.4925 | 20.2741 | 25.0027 | 28.5905 | 32.1619
| DunnvilleIce Accretion2100RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2100 | 15.7651 | 19.4419 | 24.032 | 27.5178 | 30.9658
| DunnvilleIce Accretion2023RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
| DunnvilleIce Accretion2025RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2025 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
| DunnvilleIce Accretion2030RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2030 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
| DunnvilleIce Accretion2035RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2035 | 21.3987 | 25.7366 | 31.264 | 35.4368 | 39.6346
| DunnvilleIce Accretion2040RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2040 | 20.6045 | 24.8425 | 30.2187 | 34.2797 | 38.3712
| DunnvilleIce Accretion2045RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2045 | 19.8103 | 23.9483 | 29.1733 | 33.1226 | 37.1078
| DunnvilleIce Accretion2050RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2050 | 18.6598 | 22.6822 | 27.7333 | 31.5556 | 35.4144
| DunnvilleIce Accretion2055RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2055 | 18.3035 | 22.3104 | 27.3387 | 31.1458 | 34.9843
| DunnvilleIce Accretion2060RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2060 | 17.2199 | 21.1063 | 25.9733 | 29.6633 | 33.3581
| DunnvilleIce Accretion2065RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2065 | 16.4925 | 20.2741 | 25.0027 | 28.5905 | 32.1619
| DunnvilleIce Accretion2070RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2070 | 15.4014 | 19.0258 | 23.5627 | 26.9995 | 30.4013
| DunnvilleIce Accretion2075RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2075 | 15.0377 | 18.6097 | 23.0933 | 26.4812 | 29.8368
| DunnvilleIce Accretion2080RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2080 | 14.674 | 18.1936 | 22.624 | 25.9629 | 29.2723
| DunnvilleIce Accretion2085RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2085 | 13.8501 | 17.2242 | 21.456 | 24.643 | 27.8006
| DunnvilleIce Accretion2090RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2090 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
| DunnvilleIce Accretion2095RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2095 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
| DunnvilleIce Accretion2100RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2100 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
| DunnvilleWind2023RCP4.5 | Dunnville | Wind | RCP4.5 | 2023 | 88.9824 | 96.0647 | 103.581 | 111.05 | 118.5126
| DunnvilleWind2025RCP4.5 | Dunnville | Wind | RCP4.5 | 2025 | 88.953 | 96.0347 | 103.5487 | 111.0154 | 118.4758
| DunnvilleWind2030RCP4.5 | Dunnville | Wind | RCP4.5 | 2030 | 88.9237 | 96.0046 | 103.5164 | 110.9808 | 118.4389
| DunnvilleWind2035RCP4.5 | Dunnville | Wind | RCP4.5 | 2035 | 88.8943 | 95.9746 | 103.4841 | 110.9463 | 118.4021
| DunnvilleWind2040RCP4.5 | Dunnville | Wind | RCP4.5 | 2040 | 88.8649 | 95.9446 | 103.4518 | 110.9117 | 118.3653
| DunnvilleWind2045RCP4.5 | Dunnville | Wind | RCP4.5 | 2045 | 88.8356 | 95.9145 | 103.4195 | 110.8771 | 118.3285
| DunnvilleWind2050RCP4.5 | Dunnville | Wind | RCP4.5 | 2050 | 88.8644 | 95.9585 | 103.4831 | 110.9539 | 118.4219
| DunnvilleWind2055RCP4.5 | Dunnville | Wind | RCP4.5 | 2055 | 88.9225 | 96.0325 | 103.579 | 111.0652 | 118.5521
| DunnvilleWind2060RCP4.5 | Dunnville | Wind | RCP4.5 | 2060 | 88.9806 | 96.1065 | 103.6748 | 111.1766 | 118.6823
| DunnvilleWind2065RCP4.5 | Dunnville | Wind | RCP4.5 | 2065 | 89.0388 | 96.1805 | 103.7707 | 111.2879 | 118.8126
| DunnvilleWind2070RCP4.5 | Dunnville | Wind | RCP4.5 | 2070 | 89.0969 | 96.2544 | 103.8666 | 111.3992 | 118.9428
| DunnvilleWind2075RCP4.5 | Dunnville | Wind | RCP4.5 | 2075 | 89.1791 | 96.3699 | 104.0247 | 111.592 | 119.1734
| DunnvilleWind2080RCP4.5 | Dunnville | Wind | RCP4.5 | 2080 | 89.2613 | 96.4853 | 104.1828 | 111.7848 | 119.4041
| DunnvilleWind2085RCP4.5 | Dunnville | Wind | RCP4.5 | 2085 | 89.3435 | 96.6007 | 104.3409 | 111.9776 | 119.6347
| DunnvilleWind2090RCP4.5 | Dunnville | Wind | RCP4.5 | 2090 | 89.4257 | 96.7161 | 104.499 | 112.1705 | 119.8653
| DunnvilleWind2095RCP4.5 | Dunnville | Wind | RCP4.5 | 2095 | 89.5079 | 96.8315 | 104.6571 | 112.3633 | 120.0959
| DunnvilleWind2100RCP4.5 | Dunnville | Wind | RCP4.5 | 2100 | 89.5901 | 96.9469 | 104.8152 | 112.5561 | 120.3265
| DunnvilleWind2023RCP6.0 | Dunnville | Wind | RCP6.0 | 2023 | 88.9824 | 96.0647 | 103.581 | 111.05 | 118.5126
| DunnvilleWind2025RCP6.0 | Dunnville | Wind | RCP6.0 | 2025 | 88.953 | 96.0347 | 103.5487 | 111.0154 | 118.4758
| DunnvilleWind2030RCP6.0 | Dunnville | Wind | RCP6.0 | 2030 | 88.9237 | 96.0046 | 103.5164 | 110.9808 | 118.4389
| DunnvilleWind2035RCP6.0 | Dunnville | Wind | RCP6.0 | 2035 | 88.8943 | 95.9746 | 103.4841 | 110.9463 | 118.4021
| DunnvilleWind2040RCP6.0 | Dunnville | Wind | RCP6.0 | 2040 | 88.8649 | 95.9446 | 103.4518 | 110.9117 | 118.3653
| DunnvilleWind2045RCP6.0 | Dunnville | Wind | RCP6.0 | 2045 | 88.8356 | 95.9145 | 103.4195 | 110.8771 | 118.3285
| DunnvilleWind2050RCP6.0 | Dunnville | Wind | RCP6.0 | 2050 | 88.8644 | 95.9585 | 103.4831 | 110.9539 | 118.4219
| DunnvilleWind2055RCP6.0 | Dunnville | Wind | RCP6.0 | 2055 | 88.9225 | 96.0325 | 103.579 | 111.0652 | 118.5521
| DunnvilleWind2060RCP6.0 | Dunnville | Wind | RCP6.0 | 2060 | 88.9806 | 96.1065 | 103.6748 | 111.1766 | 118.6823
| DunnvilleWind2065RCP6.0 | Dunnville | Wind | RCP6.0 | 2065 | 89.0388 | 96.1805 | 103.7707 | 111.2879 | 118.8126
| DunnvilleWind2070RCP6.0 | Dunnville | Wind | RCP6.0 | 2070 | 89.0969 | 96.2544 | 103.8666 | 111.3992 | 118.9428
| DunnvilleWind2075RCP6.0 | Dunnville | Wind | RCP6.0 | 2075 | 89.2202 | 96.4276 | 104.1038 | 111.6884 | 119.2887
| DunnvilleWind2080RCP6.0 | Dunnville | Wind | RCP6.0 | 2080 | 89.3435 | 96.6007 | 104.3409 | 111.9776 | 119.6347
| DunnvilleWind2085RCP6.0 | Dunnville | Wind | RCP6.0 | 2085 | 89.4668 | 96.7738 | 104.5781 | 112.2669 | 119.9806
| DunnvilleWind2090RCP6.0 | Dunnville | Wind | RCP6.0 | 2090 | 89.778 | 97.1872 | 105.1178 | 112.9162 | 120.7452
| DunnvilleWind2095RCP6.0 | Dunnville | Wind | RCP6.0 | 2095 | 89.9659 | 97.4275 | 105.4204 | 113.2764 | 121.1638
| DunnvilleWind2100RCP6.0 | Dunnville | Wind | RCP6.0 | 2100 | 90.1538 | 97.6679 | 105.723 | 113.6366 | 121.5824
| DunnvilleWind2023RCP8.5 | Dunnville | Wind | RCP8.5 | 2023 | 88.9824 | 96.0647 | 103.581 | 111.05 | 118.5126
| DunnvilleWind2025RCP8.5 | Dunnville | Wind | RCP8.5 | 2025 | 88.9237 | 96.0046 | 103.5164 | 110.9808 | 118.4389
| DunnvilleWind2030RCP8.5 | Dunnville | Wind | RCP8.5 | 2030 | 88.8649 | 95.9446 | 103.4518 | 110.9117 | 118.3653
| DunnvilleWind2035RCP8.5 | Dunnville | Wind | RCP8.5 | 2035 | 88.8062 | 95.8845 | 103.3872 | 110.8426 | 118.2916
| DunnvilleWind2040RCP8.5 | Dunnville | Wind | RCP8.5 | 2040 | 88.9031 | 96.0078 | 103.547 | 111.0281 | 118.5087
| DunnvilleWind2045RCP8.5 | Dunnville | Wind | RCP8.5 | 2045 | 89 | 96.1311 | 103.7068 | 111.2137 | 118.7258
| DunnvilleWind2050RCP8.5 | Dunnville | Wind | RCP8.5 | 2050 | 89.2613 | 96.4853 | 104.1828 | 111.7848 | 119.4041
| DunnvilleWind2055RCP8.5 | Dunnville | Wind | RCP8.5 | 2055 | 89.4257 | 96.7161 | 104.499 | 112.1705 | 119.8653
| DunnvilleWind2060RCP8.5 | Dunnville | Wind | RCP8.5 | 2060 | 89.778 | 97.1872 | 105.1178 | 112.9162 | 120.7452
| DunnvilleWind2065RCP8.5 | Dunnville | Wind | RCP8.5 | 2065 | 89.9659 | 97.4275 | 105.4204 | 113.2764 | 121.1638
| DunnvilleWind2070RCP8.5 | Dunnville | Wind | RCP8.5 | 2070 | 90.2154 | 97.7722 | 105.8896 | 113.8548 | 121.8459
| DunnvilleWind2075RCP8.5 | Dunnville | Wind | RCP8.5 | 2075 | 90.2771 | 97.8765 | 106.0562 | 114.0731 | 122.1095
| DunnvilleWind2080RCP8.5 | Dunnville | Wind | RCP8.5 | 2080 | 90.3387 | 97.9809 | 106.2228 | 114.2914 | 122.3731
| DunnvilleWind2085RCP8.5 | Dunnville | Wind | RCP8.5 | 2085 | 90.4048 | 98.09 | 106.3809 | 114.4879 | 122.6173
| DunnvilleWind2090RCP8.5 | Dunnville | Wind | RCP8.5 | 2090 | 90.4709 | 98.1991 | 106.539 | 114.6843 | 122.8614
| DunnvilleWind2095RCP8.5 | Dunnville | Wind | RCP8.5 | 2095 | 90.4709 | 98.1991 | 106.539 | 114.6843 | 122.8614
| DunnvilleWind2100RCP8.5 | Dunnville | Wind | RCP8.5 | 2100 | 90.4709 | 98.1991 | 106.539 | 114.6843 | 122.8614
| DurhamIce Accretion2023RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2023 | 15.2933 | 18.333 | 22.198 | 25.1335 | 28.0804
| DurhamIce Accretion2025RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2025 | 15.2984 | 18.3543 | 22.231 | 25.179 | 28.1404
| DurhamIce Accretion2030RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2030 | 15.3035 | 18.3756 | 22.264 | 25.2246 | 28.2005
| DurhamIce Accretion2035RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2035 | 15.3086 | 18.3969 | 22.297 | 25.2702 | 28.2605
| DurhamIce Accretion2040RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2040 | 15.3137 | 18.4183 | 22.33 | 25.3158 | 28.3206
| DurhamIce Accretion2045RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2045 | 15.3188 | 18.4396 | 22.363 | 25.3613 | 28.3807
| DurhamIce Accretion2050RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2050 | 15.3178 | 18.4718 | 22.4356 | 25.4666 | 28.5183
| DurhamIce Accretion2055RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2055 | 15.3117 | 18.4828 | 22.4752 | 25.5262 | 28.596
| DurhamIce Accretion2060RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2060 | 15.3056 | 18.4937 | 22.5148 | 25.5859 | 28.6736
| DurhamIce Accretion2065RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2065 | 15.2994 | 18.5047 | 22.5544 | 25.6456 | 28.7512
| DurhamIce Accretion2070RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2070 | 15.2933 | 18.5156 | 22.594 | 25.7052 | 28.8288
| DurhamIce Accretion2075RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2075 | 15.227 | 18.4609 | 22.5573 | 25.6762 | 28.8103
| DurhamIce Accretion2080RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2080 | 15.1606 | 18.4061 | 22.5207 | 25.6472 | 28.7918
| DurhamIce Accretion2085RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2085 | 15.0943 | 18.3513 | 22.484 | 25.6182 | 28.7734
| DurhamIce Accretion2090RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2090 | 15.028 | 18.2965 | 22.4473 | 25.5892 | 28.7549
| DurhamIce Accretion2095RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2095 | 14.9616 | 18.2417 | 22.4107 | 25.5602 | 28.7364
| DurhamIce Accretion2100RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2100 | 14.8953 | 18.187 | 22.374 | 25.5312 | 28.7179
| DurhamIce Accretion2023RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2023 | 15.2933 | 18.333 | 22.198 | 25.1335 | 28.0804
| DurhamIce Accretion2025RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2025 | 15.2984 | 18.3543 | 22.231 | 25.179 | 28.1404
| DurhamIce Accretion2030RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2030 | 15.3035 | 18.3756 | 22.264 | 25.2246 | 28.2005
| DurhamIce Accretion2035RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2035 | 15.3086 | 18.3969 | 22.297 | 25.2702 | 28.2605
| DurhamIce Accretion2040RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2040 | 15.3137 | 18.4183 | 22.33 | 25.3158 | 28.3206
| DurhamIce Accretion2045RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2045 | 15.3188 | 18.4396 | 22.363 | 25.3613 | 28.3807
| DurhamIce Accretion2050RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2050 | 15.3178 | 18.4718 | 22.4356 | 25.4666 | 28.5183
| DurhamIce Accretion2055RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2055 | 15.3117 | 18.4828 | 22.4752 | 25.5262 | 28.596
| DurhamIce Accretion2060RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2060 | 15.3056 | 18.4937 | 22.5148 | 25.5859 | 28.6736
| DurhamIce Accretion2065RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2065 | 15.2994 | 18.5047 | 22.5544 | 25.6456 | 28.7512
| DurhamIce Accretion2070RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2070 | 15.2933 | 18.5156 | 22.594 | 25.7052 | 28.8288
| DurhamIce Accretion2075RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2075 | 15.1938 | 18.4335 | 22.539 | 25.6617 | 28.8011
| DurhamIce Accretion2080RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2080 | 15.0943 | 18.3513 | 22.484 | 25.6182 | 28.7734
| DurhamIce Accretion2085RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2085 | 14.9948 | 18.2691 | 22.429 | 25.5747 | 28.7456
| DurhamIce Accretion2090RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2090 | 14.6401 | 17.9191 | 22.0733 | 25.2163 | 28.376
| DurhamIce Accretion2095RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2095 | 14.385 | 17.6513 | 21.7727 | 24.9014 | 28.0342
| DurhamIce Accretion2100RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2100 | 14.1299 | 17.3835 | 21.472 | 24.5865 | 27.6923
| DurhamIce Accretion2023RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2023 | 15.2933 | 18.333 | 22.198 | 25.1335 | 28.0804
| DurhamIce Accretion2025RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2025 | 15.3035 | 18.3756 | 22.264 | 25.2246 | 28.2005
| DurhamIce Accretion2030RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2030 | 15.3137 | 18.4183 | 22.33 | 25.3158 | 28.3206
| DurhamIce Accretion2035RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2035 | 15.3239 | 18.4609 | 22.396 | 25.4069 | 28.4407
| DurhamIce Accretion2040RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2040 | 15.3137 | 18.4791 | 22.462 | 25.5064 | 28.5701
| DurhamIce Accretion2045RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2045 | 15.3035 | 18.4974 | 22.528 | 25.6058 | 28.6994
| DurhamIce Accretion2050RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2050 | 15.1606 | 18.4061 | 22.5207 | 25.6472 | 28.7918
| DurhamIce Accretion2055RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2055 | 15.028 | 18.2965 | 22.4473 | 25.5892 | 28.7549
| DurhamIce Accretion2060RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2060 | 14.6401 | 17.9191 | 22.0733 | 25.2163 | 28.376
| DurhamIce Accretion2065RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2065 | 14.385 | 17.6513 | 21.7727 | 24.9014 | 28.0342
| DurhamIce Accretion2070RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2070 | 13.7114 | 16.9088 | 20.9367 | 23.9982 | 27.0547
| DurhamIce Accretion2075RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2075 | 13.293 | 16.434 | 20.4013 | 23.4098 | 26.4172
| DurhamIce Accretion2080RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2080 | 12.8745 | 15.9592 | 19.866 | 22.8215 | 25.7796
| DurhamIce Accretion2085RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2085 | 12.4536 | 15.4936 | 19.338 | 22.2497 | 25.1698
| DurhamIce Accretion2090RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2090 | 12.0326 | 15.028 | 18.81 | 21.6779 | 24.5599
| DurhamIce Accretion2095RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2095 | 12.0326 | 15.028 | 18.81 | 21.6779 | 24.5599
| DurhamIce Accretion2100RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2100 | 12.0326 | 15.028 | 18.81 | 21.6779 | 24.5599
| DurhamWind2023RCP4.5 | Durham | Wind | RCP4.5 | 2023 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2506
| DurhamWind2025RCP4.5 | Durham | Wind | RCP4.5 | 2025 | 85.4139 | 92.1425 | 99.2626 | 106.3385 | 113.42
| DurhamWind2030RCP4.5 | Durham | Wind | RCP4.5 | 2030 | 85.4957 | 92.2428 | 99.3883 | 106.4853 | 113.5894
| DurhamWind2035RCP4.5 | Durham | Wind | RCP4.5 | 2035 | 85.5775 | 92.343 | 99.5141 | 106.6321 | 113.7589
| DurhamWind2040RCP4.5 | Durham | Wind | RCP4.5 | 2040 | 85.6593 | 92.4433 | 99.6399 | 106.7789 | 113.9283
| DurhamWind2045RCP4.5 | Durham | Wind | RCP4.5 | 2045 | 85.7411 | 92.5436 | 99.7656 | 106.9257 | 114.0978
| DurhamWind2050RCP4.5 | Durham | Wind | RCP4.5 | 2050 | 85.8364 | 92.6566 | 99.9012 | 107.0809 | 114.2739
| DurhamWind2055RCP4.5 | Durham | Wind | RCP4.5 | 2055 | 85.85 | 92.6693 | 99.911 | 107.0893 | 114.2806
| DurhamWind2060RCP4.5 | Durham | Wind | RCP4.5 | 2060 | 85.8635 | 92.6821 | 99.9208 | 107.0977 | 114.2873
| DurhamWind2065RCP4.5 | Durham | Wind | RCP4.5 | 2065 | 85.8771 | 92.6948 | 99.9306 | 107.1061 | 114.294
| DurhamWind2070RCP4.5 | Durham | Wind | RCP4.5 | 2070 | 85.8906 | 92.7076 | 99.9404 | 107.1145 | 114.3007
| DurhamWind2075RCP4.5 | Durham | Wind | RCP4.5 | 2075 | 85.9738 | 92.8155 | 100.0792 | 107.2805 | 114.4925
| DurhamWind2080RCP4.5 | Durham | Wind | RCP4.5 | 2080 | 86.057 | 92.9233 | 100.2181 | 107.4465 | 114.6843
| DurhamWind2085RCP4.5 | Durham | Wind | RCP4.5 | 2085 | 86.1402 | 93.0312 | 100.3569 | 107.6126 | 114.8761
| DurhamWind2090RCP4.5 | Durham | Wind | RCP4.5 | 2090 | 86.2234 | 93.139 | 100.4957 | 107.7786 | 115.0679
| DurhamWind2095RCP4.5 | Durham | Wind | RCP4.5 | 2095 | 86.3067 | 93.2469 | 100.6346 | 107.9446 | 115.2597
| DurhamWind2100RCP4.5 | Durham | Wind | RCP4.5 | 2100 | 86.3899 | 93.3547 | 100.7734 | 108.1107 | 115.4514
| DurhamWind2023RCP6.0 | Durham | Wind | RCP6.0 | 2023 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2506
| DurhamWind2025RCP6.0 | Durham | Wind | RCP6.0 | 2025 | 85.4139 | 92.1425 | 99.2626 | 106.3385 | 113.42
| DurhamWind2030RCP6.0 | Durham | Wind | RCP6.0 | 2030 | 85.4957 | 92.2428 | 99.3883 | 106.4853 | 113.5894
| DurhamWind2035RCP6.0 | Durham | Wind | RCP6.0 | 2035 | 85.5775 | 92.343 | 99.5141 | 106.6321 | 113.7589
| DurhamWind2040RCP6.0 | Durham | Wind | RCP6.0 | 2040 | 85.6593 | 92.4433 | 99.6399 | 106.7789 | 113.9283
| DurhamWind2045RCP6.0 | Durham | Wind | RCP6.0 | 2045 | 85.7411 | 92.5436 | 99.7656 | 106.9257 | 114.0978
| DurhamWind2050RCP6.0 | Durham | Wind | RCP6.0 | 2050 | 85.8364 | 92.6566 | 99.9012 | 107.0809 | 114.2739
| DurhamWind2055RCP6.0 | Durham | Wind | RCP6.0 | 2055 | 85.85 | 92.6693 | 99.911 | 107.0893 | 114.2806
| DurhamWind2060RCP6.0 | Durham | Wind | RCP6.0 | 2060 | 85.8635 | 92.6821 | 99.9208 | 107.0977 | 114.2873
| DurhamWind2065RCP6.0 | Durham | Wind | RCP6.0 | 2065 | 85.8771 | 92.6948 | 99.9306 | 107.1061 | 114.294
| DurhamWind2070RCP6.0 | Durham | Wind | RCP6.0 | 2070 | 85.8906 | 92.7076 | 99.9404 | 107.1145 | 114.3007
| DurhamWind2075RCP6.0 | Durham | Wind | RCP6.0 | 2075 | 86.0154 | 92.8694 | 100.1487 | 107.3635 | 114.5884
| DurhamWind2080RCP6.0 | Durham | Wind | RCP6.0 | 2080 | 86.1402 | 93.0312 | 100.3569 | 107.6126 | 114.8761
| DurhamWind2085RCP6.0 | Durham | Wind | RCP6.0 | 2085 | 86.265 | 93.1929 | 100.5652 | 107.8616 | 115.1638
| DurhamWind2090RCP6.0 | Durham | Wind | RCP6.0 | 2090 | 86.8017 | 93.8712 | 101.4169 | 108.8657 | 116.3229
| DurhamWind2095RCP6.0 | Durham | Wind | RCP6.0 | 2095 | 87.2135 | 94.3876 | 102.0605 | 109.6206 | 117.1943
| DurhamWind2100RCP6.0 | Durham | Wind | RCP6.0 | 2100 | 87.6253 | 94.9041 | 102.704 | 110.3756 | 118.0657
| DurhamWind2023RCP8.5 | Durham | Wind | RCP8.5 | 2023 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2506
| DurhamWind2025RCP8.5 | Durham | Wind | RCP8.5 | 2025 | 85.4957 | 92.2428 | 99.3883 | 106.4853 | 113.5894
| DurhamWind2030RCP8.5 | Durham | Wind | RCP8.5 | 2030 | 85.6593 | 92.4433 | 99.6399 | 106.7789 | 113.9283
| DurhamWind2035RCP8.5 | Durham | Wind | RCP8.5 | 2035 | 85.8229 | 92.6438 | 99.8914 | 107.0725 | 114.2672
| DurhamWind2040RCP8.5 | Durham | Wind | RCP8.5 | 2040 | 85.8455 | 92.6651 | 99.9077 | 107.0865 | 114.2784
| DurhamWind2045RCP8.5 | Durham | Wind | RCP8.5 | 2045 | 85.868 | 92.6863 | 99.9241 | 107.1005 | 114.2896
| DurhamWind2050RCP8.5 | Durham | Wind | RCP8.5 | 2050 | 86.057 | 92.9233 | 100.2181 | 107.4465 | 114.6843
| DurhamWind2055RCP8.5 | Durham | Wind | RCP8.5 | 2055 | 86.2234 | 93.139 | 100.4957 | 107.7786 | 115.0679
| DurhamWind2060RCP8.5 | Durham | Wind | RCP8.5 | 2060 | 86.8017 | 93.8712 | 101.4169 | 108.8657 | 116.3229
| DurhamWind2065RCP8.5 | Durham | Wind | RCP8.5 | 2065 | 87.2135 | 94.3876 | 102.0605 | 109.6206 | 117.1943
| DurhamWind2070RCP8.5 | Durham | Wind | RCP8.5 | 2070 | 87.8397 | 95.1653 | 103.0241 | 110.7461 | 118.4865
| DurhamWind2075RCP8.5 | Durham | Wind | RCP8.5 | 2075 | 88.0541 | 95.4266 | 103.3443 | 111.1166 | 118.9073
| DurhamWind2080RCP8.5 | Durham | Wind | RCP8.5 | 2080 | 88.2685 | 95.6879 | 103.6644 | 111.4872 | 119.3281
| DurhamWind2085RCP8.5 | Durham | Wind | RCP8.5 | 2085 | 88.2896 | 95.697 | 103.6644 | 111.4714 | 119.3058
| DurhamWind2090RCP8.5 | Durham | Wind | RCP8.5 | 2090 | 88.3108 | 95.7061 | 103.6644 | 111.4557 | 119.2834
| DurhamWind2095RCP8.5 | Durham | Wind | RCP8.5 | 2095 | 88.3108 | 95.7061 | 103.6644 | 111.4557 | 119.2834
| DurhamWind2100RCP8.5 | Durham | Wind | RCP8.5 | 2100 | 88.3108 | 95.7061 | 103.6644 | 111.4557 | 119.2834
| DuttonIce Accretion2023RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2023 | 20.5831 | 24.7008 | 29.91 | 33.8661 | 37.8378
| DuttonIce Accretion2025RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2025 | 20.4614 | 24.568 | 29.765 | 33.7135 | 37.674
| DuttonIce Accretion2030RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2030 | 20.3396 | 24.4352 | 29.62 | 33.561 | 37.5102
| DuttonIce Accretion2035RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2035 | 20.2178 | 24.3024 | 29.475 | 33.4085 | 37.3464
| DuttonIce Accretion2040RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2040 | 20.096 | 24.1696 | 29.33 | 33.2559 | 37.1826
| DuttonIce Accretion2045RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2045 | 19.9743 | 24.0368 | 29.185 | 33.1033 | 37.0188
| DuttonIce Accretion2050RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2050 | 19.4642 | 23.4757 | 28.554 | 32.422 | 36.2804
| DuttonIce Accretion2055RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2055 | 19.0759 | 23.0474 | 28.068 | 31.8931 | 35.7059
| DuttonIce Accretion2060RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2060 | 18.6876 | 22.6192 | 27.582 | 31.3643 | 35.1313
| DuttonIce Accretion2065RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2065 | 18.2994 | 22.1909 | 27.096 | 30.8354 | 34.5568
| DuttonIce Accretion2070RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2070 | 17.9111 | 21.7626 | 26.61 | 30.3066 | 33.9822
| DuttonIce Accretion2075RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2075 | 17.7754 | 21.6257 | 26.47 | 30.1597 | 33.831
| DuttonIce Accretion2080RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2080 | 17.6397 | 21.4887 | 26.33 | 30.0128 | 33.6798
| DuttonIce Accretion2085RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2085 | 17.504 | 21.3517 | 26.19 | 29.8659 | 33.5286
| DuttonIce Accretion2090RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2090 | 17.3683 | 21.2148 | 26.05 | 29.719 | 33.3774
| DuttonIce Accretion2095RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2095 | 17.2326 | 21.0778 | 25.91 | 29.5721 | 33.2262
| DuttonIce Accretion2100RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2100 | 17.0969 | 20.9409 | 25.77 | 29.4252 | 33.075
| DuttonIce Accretion2023RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2023 | 20.5831 | 24.7008 | 29.91 | 33.8661 | 37.8378
| DuttonIce Accretion2025RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2025 | 20.4614 | 24.568 | 29.765 | 33.7135 | 37.674
| DuttonIce Accretion2030RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2030 | 20.3396 | 24.4352 | 29.62 | 33.561 | 37.5102
| DuttonIce Accretion2035RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2035 | 20.2178 | 24.3024 | 29.475 | 33.4085 | 37.3464
| DuttonIce Accretion2040RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2040 | 20.096 | 24.1696 | 29.33 | 33.2559 | 37.1826
| DuttonIce Accretion2045RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2045 | 19.9743 | 24.0368 | 29.185 | 33.1033 | 37.0188
| DuttonIce Accretion2050RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2050 | 19.4642 | 23.4757 | 28.554 | 32.422 | 36.2804
| DuttonIce Accretion2055RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2055 | 19.0759 | 23.0474 | 28.068 | 31.8931 | 35.7059
| DuttonIce Accretion2060RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2060 | 18.6876 | 22.6192 | 27.582 | 31.3643 | 35.1313
| DuttonIce Accretion2065RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2065 | 18.2994 | 22.1909 | 27.096 | 30.8354 | 34.5568
| DuttonIce Accretion2070RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2070 | 17.9111 | 21.7626 | 26.61 | 30.3066 | 33.9822
| DuttonIce Accretion2075RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2075 | 17.7075 | 21.5572 | 26.4 | 30.0862 | 33.7554
| DuttonIce Accretion2080RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2080 | 17.504 | 21.3517 | 26.19 | 29.8659 | 33.5286
| DuttonIce Accretion2085RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2085 | 17.3005 | 21.1463 | 25.98 | 29.6456 | 33.3018
| DuttonIce Accretion2090RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2090 | 16.6098 | 20.3931 | 25.15 | 28.7472 | 32.3316
| DuttonIce Accretion2095RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2095 | 16.1228 | 19.8453 | 24.53 | 28.0692 | 31.5882
| DuttonIce Accretion2100RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2100 | 15.6357 | 19.2975 | 23.91 | 27.3912 | 30.8448
| DuttonIce Accretion2023RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2023 | 20.5831 | 24.7008 | 29.91 | 33.8661 | 37.8378
| DuttonIce Accretion2025RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2025 | 20.3396 | 24.4352 | 29.62 | 33.561 | 37.5102
| DuttonIce Accretion2030RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2030 | 20.096 | 24.1696 | 29.33 | 33.2559 | 37.1826
| DuttonIce Accretion2035RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2035 | 19.8525 | 23.904 | 29.04 | 32.9508 | 36.855
| DuttonIce Accretion2040RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2040 | 19.2054 | 23.1902 | 28.23 | 32.0694 | 35.8974
| DuttonIce Accretion2045RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2045 | 18.5582 | 22.4764 | 27.42 | 31.188 | 34.9398
| DuttonIce Accretion2050RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2050 | 17.6397 | 21.4887 | 26.33 | 30.0128 | 33.6798
| DuttonIce Accretion2055RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2055 | 17.3683 | 21.2148 | 26.05 | 29.719 | 33.3774
| DuttonIce Accretion2060RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2060 | 16.6098 | 20.3931 | 25.15 | 28.7472 | 32.3316
| DuttonIce Accretion2065RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2065 | 16.1228 | 19.8453 | 24.53 | 28.0692 | 31.5882
| DuttonIce Accretion2070RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2070 | 15.3225 | 18.9655 | 23.55 | 26.9957 | 30.429
| DuttonIce Accretion2075RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2075 | 15.0094 | 18.6335 | 23.19 | 26.6002 | 30.0132
| DuttonIce Accretion2080RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2080 | 14.6963 | 18.3015 | 22.83 | 26.2047 | 29.5974
| DuttonIce Accretion2085RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2085 | 13.7673 | 17.2059 | 21.51 | 24.73 | 27.9531
| DuttonIce Accretion2090RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2090 | 12.8384 | 16.1103 | 20.19 | 23.2554 | 26.3088
| DuttonIce Accretion2095RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2095 | 12.8384 | 16.1103 | 20.19 | 23.2554 | 26.3088
| DuttonIce Accretion2100RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2100 | 12.8384 | 16.1103 | 20.19 | 23.2554 | 26.3088
| DuttonWind2023RCP4.5 | Dutton | Wind | RCP4.5 | 2023 | 87.0563 | 93.9114 | 101.17 | 108.391 | 115.6188
| DuttonWind2025RCP4.5 | Dutton | Wind | RCP4.5 | 2025 | 87.1657 | 94.0571 | 101.3617 | 108.621 | 115.8886
| DuttonWind2030RCP4.5 | Dutton | Wind | RCP4.5 | 2030 | 87.275 | 94.2028 | 101.5533 | 108.8511 | 116.1584
| DuttonWind2035RCP4.5 | Dutton | Wind | RCP4.5 | 2035 | 87.3844 | 94.3485 | 101.745 | 109.0811 | 116.4282
| DuttonWind2040RCP4.5 | Dutton | Wind | RCP4.5 | 2040 | 87.4938 | 94.4942 | 101.9367 | 109.3112 | 116.698
| DuttonWind2045RCP4.5 | Dutton | Wind | RCP4.5 | 2045 | 87.6032 | 94.6399 | 102.1283 | 109.5412 | 116.9678
| DuttonWind2050RCP4.5 | Dutton | Wind | RCP4.5 | 2050 | 87.7644 | 94.8581 | 102.42 | 109.8954 | 117.3858
| DuttonWind2055RCP4.5 | Dutton | Wind | RCP4.5 | 2055 | 87.8162 | 94.9307 | 102.52 | 110.0195 | 117.534
| DuttonWind2060RCP4.5 | Dutton | Wind | RCP4.5 | 2060 | 87.868 | 95.0032 | 102.62 | 110.1437 | 117.6822
| DuttonWind2065RCP4.5 | Dutton | Wind | RCP4.5 | 2065 | 87.9198 | 95.0758 | 102.72 | 110.2678 | 117.8304
| DuttonWind2070RCP4.5 | Dutton | Wind | RCP4.5 | 2070 | 87.9716 | 95.1483 | 102.82 | 110.3919 | 117.9786
| DuttonWind2075RCP4.5 | Dutton | Wind | RCP4.5 | 2075 | 88.1241 | 95.3467 | 103.0767 | 110.6969 | 118.3339
| DuttonWind2080RCP4.5 | Dutton | Wind | RCP4.5 | 2080 | 88.2767 | 95.5451 | 103.3333 | 111.0018 | 118.6892
| DuttonWind2085RCP4.5 | Dutton | Wind | RCP4.5 | 2085 | 88.4292 | 95.7435 | 103.59 | 111.3067 | 119.0445
| DuttonWind2090RCP4.5 | Dutton | Wind | RCP4.5 | 2090 | 88.5818 | 95.9419 | 103.8467 | 111.6117 | 119.3998
| DuttonWind2095RCP4.5 | Dutton | Wind | RCP4.5 | 2095 | 88.7343 | 96.1403 | 104.1033 | 111.9167 | 119.7551
| DuttonWind2100RCP4.5 | Dutton | Wind | RCP4.5 | 2100 | 88.8869 | 96.3387 | 104.36 | 112.2216 | 120.1104
| DuttonWind2023RCP6.0 | Dutton | Wind | RCP6.0 | 2023 | 87.0563 | 93.9114 | 101.17 | 108.391 | 115.6188
| DuttonWind2025RCP6.0 | Dutton | Wind | RCP6.0 | 2025 | 87.1657 | 94.0571 | 101.3617 | 108.621 | 115.8886
| DuttonWind2030RCP6.0 | Dutton | Wind | RCP6.0 | 2030 | 87.275 | 94.2028 | 101.5533 | 108.8511 | 116.1584
| DuttonWind2035RCP6.0 | Dutton | Wind | RCP6.0 | 2035 | 87.3844 | 94.3485 | 101.745 | 109.0811 | 116.4282
| DuttonWind2040RCP6.0 | Dutton | Wind | RCP6.0 | 2040 | 87.4938 | 94.4942 | 101.9367 | 109.3112 | 116.698
| DuttonWind2045RCP6.0 | Dutton | Wind | RCP6.0 | 2045 | 87.6032 | 94.6399 | 102.1283 | 109.5412 | 116.9678
| DuttonWind2050RCP6.0 | Dutton | Wind | RCP6.0 | 2050 | 87.7644 | 94.8581 | 102.42 | 109.8954 | 117.3858
| DuttonWind2055RCP6.0 | Dutton | Wind | RCP6.0 | 2055 | 87.8162 | 94.9307 | 102.52 | 110.0195 | 117.534
| DuttonWind2060RCP6.0 | Dutton | Wind | RCP6.0 | 2060 | 87.868 | 95.0032 | 102.62 | 110.1437 | 117.6822
| DuttonWind2065RCP6.0 | Dutton | Wind | RCP6.0 | 2065 | 87.9198 | 95.0758 | 102.72 | 110.2678 | 117.8304
| DuttonWind2070RCP6.0 | Dutton | Wind | RCP6.0 | 2070 | 87.9716 | 95.1483 | 102.82 | 110.3919 | 117.9786
| DuttonWind2075RCP6.0 | Dutton | Wind | RCP6.0 | 2075 | 88.2004 | 95.4459 | 103.205 | 110.8493 | 118.5115
| DuttonWind2080RCP6.0 | Dutton | Wind | RCP6.0 | 2080 | 88.4292 | 95.7435 | 103.59 | 111.3067 | 119.0445
| DuttonWind2085RCP6.0 | Dutton | Wind | RCP6.0 | 2085 | 88.6581 | 96.0411 | 103.975 | 111.7642 | 119.5774
| DuttonWind2090RCP6.0 | Dutton | Wind | RCP6.0 | 2090 | 89.2639 | 96.8192 | 104.9633 | 112.9314 | 120.9312
| DuttonWind2095RCP6.0 | Dutton | Wind | RCP6.0 | 2095 | 89.641 | 97.2997 | 105.5667 | 113.6411 | 121.752
| DuttonWind2100RCP6.0 | Dutton | Wind | RCP6.0 | 2100 | 90.018 | 97.7802 | 106.17 | 114.3509 | 122.5728
| DuttonWind2023RCP8.5 | Dutton | Wind | RCP8.5 | 2023 | 87.0563 | 93.9114 | 101.17 | 108.391 | 115.6188
| DuttonWind2025RCP8.5 | Dutton | Wind | RCP8.5 | 2025 | 87.275 | 94.2028 | 101.5533 | 108.8511 | 116.1584
| DuttonWind2030RCP8.5 | Dutton | Wind | RCP8.5 | 2030 | 87.4938 | 94.4942 | 101.9367 | 109.3112 | 116.698
| DuttonWind2035RCP8.5 | Dutton | Wind | RCP8.5 | 2035 | 87.7125 | 94.7856 | 102.32 | 109.7713 | 117.2376
| DuttonWind2040RCP8.5 | Dutton | Wind | RCP8.5 | 2040 | 87.7989 | 94.9065 | 102.4867 | 109.9782 | 117.4846
| DuttonWind2045RCP8.5 | Dutton | Wind | RCP8.5 | 2045 | 87.8852 | 95.0274 | 102.6533 | 110.185 | 117.7316
| DuttonWind2050RCP8.5 | Dutton | Wind | RCP8.5 | 2050 | 88.2767 | 95.5451 | 103.3333 | 111.0018 | 118.6892
| DuttonWind2055RCP8.5 | Dutton | Wind | RCP8.5 | 2055 | 88.5818 | 95.9419 | 103.8467 | 111.6117 | 119.3998
| DuttonWind2060RCP8.5 | Dutton | Wind | RCP8.5 | 2060 | 89.2639 | 96.8192 | 104.9633 | 112.9314 | 120.9312
| DuttonWind2065RCP8.5 | Dutton | Wind | RCP8.5 | 2065 | 89.641 | 97.2997 | 105.5667 | 113.6411 | 121.752
| DuttonWind2070RCP8.5 | Dutton | Wind | RCP8.5 | 2070 | 90.2512 | 98.0716 | 106.54 | 114.7896 | 123.0782
| DuttonWind2075RCP8.5 | Dutton | Wind | RCP8.5 | 2075 | 90.4843 | 98.363 | 106.91 | 115.2283 | 123.5836
| DuttonWind2080RCP8.5 | Dutton | Wind | RCP8.5 | 2080 | 90.7175 | 98.6544 | 107.28 | 115.667 | 124.089
| DuttonWind2085RCP8.5 | Dutton | Wind | RCP8.5 | 2085 | 91.1147 | 99.1799 | 107.97 | 116.4909 | 125.058
| DuttonWind2090RCP8.5 | Dutton | Wind | RCP8.5 | 2090 | 91.5119 | 99.7053 | 108.66 | 117.3148 | 126.027
| DuttonWind2095RCP8.5 | Dutton | Wind | RCP8.5 | 2095 | 91.5119 | 99.7053 | 108.66 | 117.3148 | 126.027
| DuttonWind2100RCP8.5 | Dutton | Wind | RCP8.5 | 2100 | 91.5119 | 99.7053 | 108.66 | 117.3148 | 126.027
| EarltonIce Accretion2023RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2023 | 14.7519 | 17.6458 | 21.32 | 24.1142 | 26.9136
| EarltonIce Accretion2025RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2025 | 14.7311 | 17.6209 | 21.2867 | 24.0765 | 26.8716
| EarltonIce Accretion2030RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2030 | 14.7102 | 17.596 | 21.2533 | 24.0389 | 26.8296
| EarltonIce Accretion2035RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2035 | 14.6893 | 17.5711 | 21.22 | 24.0012 | 26.7876
| EarltonIce Accretion2040RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2040 | 14.6684 | 17.5462 | 21.1867 | 23.9635 | 26.7456
| EarltonIce Accretion2045RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2045 | 14.6476 | 17.5213 | 21.1533 | 23.9259 | 26.7036
| EarltonIce Accretion2050RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2050 | 14.635 | 17.5064 | 21.128 | 23.8972 | 26.6717
| EarltonIce Accretion2055RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2055 | 14.6434 | 17.5163 | 21.136 | 23.9063 | 26.6818
| EarltonIce Accretion2060RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2060 | 14.6517 | 17.5263 | 21.144 | 23.9153 | 26.6918
| EarltonIce Accretion2065RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2065 | 14.6601 | 17.5362 | 21.152 | 23.9244 | 26.7019
| EarltonIce Accretion2070RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2070 | 14.6684 | 17.5462 | 21.16 | 23.9334 | 26.712
| EarltonIce Accretion2075RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2075 | 14.7055 | 17.5988 | 21.2367 | 24.0276 | 26.8212
| EarltonIce Accretion2080RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2080 | 14.7427 | 17.6513 | 21.3133 | 24.1217 | 26.9304
| EarltonIce Accretion2085RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2085 | 14.7798 | 17.7039 | 21.39 | 24.2159 | 27.0396
| EarltonIce Accretion2090RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2090 | 14.8169 | 17.7565 | 21.4667 | 24.3101 | 27.1488
| EarltonIce Accretion2095RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2095 | 14.854 | 17.809 | 21.5433 | 24.4042 | 27.258
| EarltonIce Accretion2100RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2100 | 14.8911 | 17.8616 | 21.62 | 24.4984 | 27.3672
| EarltonIce Accretion2023RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2023 | 14.7519 | 17.6458 | 21.32 | 24.1142 | 26.9136
| EarltonIce Accretion2025RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2025 | 14.7311 | 17.6209 | 21.2867 | 24.0765 | 26.8716
| EarltonIce Accretion2030RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2030 | 14.7102 | 17.596 | 21.2533 | 24.0389 | 26.8296
| EarltonIce Accretion2035RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2035 | 14.6893 | 17.5711 | 21.22 | 24.0012 | 26.7876
| EarltonIce Accretion2040RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2040 | 14.6684 | 17.5462 | 21.1867 | 23.9635 | 26.7456
| EarltonIce Accretion2045RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2045 | 14.6476 | 17.5213 | 21.1533 | 23.9259 | 26.7036
| EarltonIce Accretion2050RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2050 | 14.635 | 17.5064 | 21.128 | 23.8972 | 26.6717
| EarltonIce Accretion2055RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2055 | 14.6434 | 17.5163 | 21.136 | 23.9063 | 26.6818
| EarltonIce Accretion2060RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2060 | 14.6517 | 17.5263 | 21.144 | 23.9153 | 26.6918
| EarltonIce Accretion2065RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2065 | 14.6601 | 17.5362 | 21.152 | 23.9244 | 26.7019
| EarltonIce Accretion2070RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2070 | 14.6684 | 17.5462 | 21.16 | 23.9334 | 26.712
| EarltonIce Accretion2075RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2075 | 14.7241 | 17.625 | 21.275 | 24.0746 | 26.8758
| EarltonIce Accretion2080RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2080 | 14.7798 | 17.7039 | 21.39 | 24.2159 | 27.0396
| EarltonIce Accretion2085RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2085 | 14.8354 | 17.7828 | 21.505 | 24.3571 | 27.2034
| EarltonIce Accretion2090RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2090 | 14.9375 | 17.9225 | 21.7067 | 24.6039 | 27.4848
| EarltonIce Accretion2095RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2095 | 14.9839 | 17.9833 | 21.7933 | 24.7093 | 27.6024
| EarltonIce Accretion2100RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2100 | 15.0303 | 18.0442 | 21.88 | 24.8148 | 27.72
| EarltonIce Accretion2023RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2023 | 14.7519 | 17.6458 | 21.32 | 24.1142 | 26.9136
| EarltonIce Accretion2025RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2025 | 14.7102 | 17.596 | 21.2533 | 24.0389 | 26.8296
| EarltonIce Accretion2030RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2030 | 14.6684 | 17.5462 | 21.1867 | 23.9635 | 26.7456
| EarltonIce Accretion2035RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2035 | 14.6267 | 17.4964 | 21.12 | 23.8882 | 26.6616
| EarltonIce Accretion2040RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2040 | 14.6406 | 17.513 | 21.1333 | 23.9033 | 26.6784
| EarltonIce Accretion2045RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2045 | 14.6545 | 17.5296 | 21.1467 | 23.9183 | 26.6952
| EarltonIce Accretion2050RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2050 | 14.7427 | 17.6513 | 21.3133 | 24.1217 | 26.9304
| EarltonIce Accretion2055RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2055 | 14.8169 | 17.7565 | 21.4667 | 24.3101 | 27.1488
| EarltonIce Accretion2060RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2060 | 14.9375 | 17.9225 | 21.7067 | 24.6039 | 27.4848
| EarltonIce Accretion2065RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2065 | 14.9839 | 17.9833 | 21.7933 | 24.7093 | 27.6024
| EarltonIce Accretion2070RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2070 | 14.8633 | 17.8616 | 21.6667 | 24.5737 | 27.4596
| EarltonIce Accretion2075RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2075 | 14.6963 | 17.679 | 21.4533 | 24.3327 | 27.1992
| EarltonIce Accretion2080RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2080 | 14.5293 | 17.4964 | 21.24 | 24.0916 | 26.9388
| EarltonIce Accretion2085RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2085 | 14.5641 | 17.5711 | 21.36 | 24.2611 | 27.1404
| EarltonIce Accretion2090RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2090 | 14.5989 | 17.6458 | 21.48 | 24.4306 | 27.342
| EarltonIce Accretion2095RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2095 | 14.5989 | 17.6458 | 21.48 | 24.4306 | 27.342
| EarltonIce Accretion2100RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2100 | 14.5989 | 17.6458 | 21.48 | 24.4306 | 27.342
| EarltonWind2023RCP4.5 | Earlton | Wind | RCP4.5 | 2023 | 76.1156 | 81.9218 | 88.0088 | 94.1129 | 100.2197
| EarltonWind2025RCP4.5 | Earlton | Wind | RCP4.5 | 2025 | 76.122 | 81.9259 | 88.0132 | 94.1176 | 100.223
| EarltonWind2030RCP4.5 | Earlton | Wind | RCP4.5 | 2030 | 76.1283 | 81.93 | 88.0176 | 94.1223 | 100.2264
| EarltonWind2035RCP4.5 | Earlton | Wind | RCP4.5 | 2035 | 76.1346 | 81.9341 | 88.022 | 94.127 | 100.2297
| EarltonWind2040RCP4.5 | Earlton | Wind | RCP4.5 | 2040 | 76.141 | 81.9382 | 88.0264 | 94.1318 | 100.2331
| EarltonWind2045RCP4.5 | Earlton | Wind | RCP4.5 | 2045 | 76.1473 | 81.9423 | 88.0308 | 94.1365 | 100.2364
| EarltonWind2050RCP4.5 | Earlton | Wind | RCP4.5 | 2050 | 76.1551 | 81.9448 | 88.0246 | 94.1261 | 100.2197
| EarltonWind2055RCP4.5 | Earlton | Wind | RCP4.5 | 2055 | 76.1567 | 81.9431 | 88.0141 | 94.111 | 100.1996
| EarltonWind2060RCP4.5 | Earlton | Wind | RCP4.5 | 2060 | 76.1582 | 81.9415 | 88.0035 | 94.096 | 100.1796
| EarltonWind2065RCP4.5 | Earlton | Wind | RCP4.5 | 2065 | 76.1597 | 81.9398 | 87.993 | 94.0809 | 100.1595
| EarltonWind2070RCP4.5 | Earlton | Wind | RCP4.5 | 2070 | 76.1612 | 81.9382 | 87.9824 | 94.0658 | 100.1394
| EarltonWind2075RCP4.5 | Earlton | Wind | RCP4.5 | 2075 | 76.2182 | 82.0078 | 88.0689 | 94.1647 | 100.2514
| EarltonWind2080RCP4.5 | Earlton | Wind | RCP4.5 | 2080 | 76.2752 | 82.0773 | 88.1555 | 94.2636 | 100.3635
| EarltonWind2085RCP4.5 | Earlton | Wind | RCP4.5 | 2085 | 76.3322 | 82.1469 | 88.242 | 94.3624 | 100.4755
| EarltonWind2090RCP4.5 | Earlton | Wind | RCP4.5 | 2090 | 76.3892 | 82.2165 | 88.3285 | 94.4613 | 100.5875
| EarltonWind2095RCP4.5 | Earlton | Wind | RCP4.5 | 2095 | 76.4462 | 82.286 | 88.4151 | 94.5602 | 100.6995
| EarltonWind2100RCP4.5 | Earlton | Wind | RCP4.5 | 2100 | 76.5032 | 82.3556 | 88.5016 | 94.659 | 100.8116
| EarltonWind2023RCP6.0 | Earlton | Wind | RCP6.0 | 2023 | 76.1156 | 81.9218 | 88.0088 | 94.1129 | 100.2197
| EarltonWind2025RCP6.0 | Earlton | Wind | RCP6.0 | 2025 | 76.122 | 81.9259 | 88.0132 | 94.1176 | 100.223
| EarltonWind2030RCP6.0 | Earlton | Wind | RCP6.0 | 2030 | 76.1283 | 81.93 | 88.0176 | 94.1223 | 100.2264
| EarltonWind2035RCP6.0 | Earlton | Wind | RCP6.0 | 2035 | 76.1346 | 81.9341 | 88.022 | 94.127 | 100.2297
| EarltonWind2040RCP6.0 | Earlton | Wind | RCP6.0 | 2040 | 76.141 | 81.9382 | 88.0264 | 94.1318 | 100.2331
| EarltonWind2045RCP6.0 | Earlton | Wind | RCP6.0 | 2045 | 76.1473 | 81.9423 | 88.0308 | 94.1365 | 100.2364
| EarltonWind2050RCP6.0 | Earlton | Wind | RCP6.0 | 2050 | 76.1551 | 81.9448 | 88.0246 | 94.1261 | 100.2197
| EarltonWind2055RCP6.0 | Earlton | Wind | RCP6.0 | 2055 | 76.1567 | 81.9431 | 88.0141 | 94.111 | 100.1996
| EarltonWind2060RCP6.0 | Earlton | Wind | RCP6.0 | 2060 | 76.1582 | 81.9415 | 88.0035 | 94.096 | 100.1796
| EarltonWind2065RCP6.0 | Earlton | Wind | RCP6.0 | 2065 | 76.1597 | 81.9398 | 87.993 | 94.0809 | 100.1595
| EarltonWind2070RCP6.0 | Earlton | Wind | RCP6.0 | 2070 | 76.1612 | 81.9382 | 87.9824 | 94.0658 | 100.1394
| EarltonWind2075RCP6.0 | Earlton | Wind | RCP6.0 | 2075 | 76.2467 | 82.0426 | 88.1122 | 94.2141 | 100.3075
| EarltonWind2080RCP6.0 | Earlton | Wind | RCP6.0 | 2080 | 76.3322 | 82.1469 | 88.242 | 94.3624 | 100.4755
| EarltonWind2085RCP6.0 | Earlton | Wind | RCP6.0 | 2085 | 76.4177 | 82.2512 | 88.3718 | 94.5107 | 100.6435
| EarltonWind2090RCP6.0 | Earlton | Wind | RCP6.0 | 2090 | 76.493 | 82.331 | 88.4576 | 94.6026 | 100.7413
| EarltonWind2095RCP6.0 | Earlton | Wind | RCP6.0 | 2095 | 76.4829 | 82.3065 | 88.4136 | 94.5461 | 100.6711
| EarltonWind2100RCP6.0 | Earlton | Wind | RCP6.0 | 2100 | 76.4728 | 82.2819 | 88.3696 | 94.4896 | 100.6009
| EarltonWind2023RCP8.5 | Earlton | Wind | RCP8.5 | 2023 | 76.1156 | 81.9218 | 88.0088 | 94.1129 | 100.2197
| EarltonWind2025RCP8.5 | Earlton | Wind | RCP8.5 | 2025 | 76.1283 | 81.93 | 88.0176 | 94.1223 | 100.2264
| EarltonWind2030RCP8.5 | Earlton | Wind | RCP8.5 | 2030 | 76.141 | 81.9382 | 88.0264 | 94.1318 | 100.2331
| EarltonWind2035RCP8.5 | Earlton | Wind | RCP8.5 | 2035 | 76.1536 | 81.9464 | 88.0352 | 94.1412 | 100.2397
| EarltonWind2040RCP8.5 | Earlton | Wind | RCP8.5 | 2040 | 76.1562 | 81.9437 | 88.0176 | 94.1161 | 100.2063
| EarltonWind2045RCP8.5 | Earlton | Wind | RCP8.5 | 2045 | 76.1587 | 81.9409 | 88 | 94.0909 | 100.1729
| EarltonWind2050RCP8.5 | Earlton | Wind | RCP8.5 | 2050 | 76.2752 | 82.0773 | 88.1555 | 94.2636 | 100.3635
| EarltonWind2055RCP8.5 | Earlton | Wind | RCP8.5 | 2055 | 76.3892 | 82.2165 | 88.3285 | 94.4613 | 100.5875
| EarltonWind2060RCP8.5 | Earlton | Wind | RCP8.5 | 2060 | 76.493 | 82.331 | 88.4576 | 94.6026 | 100.7413
| EarltonWind2065RCP8.5 | Earlton | Wind | RCP8.5 | 2065 | 76.4829 | 82.3065 | 88.4136 | 94.5461 | 100.6711
| EarltonWind2070RCP8.5 | Earlton | Wind | RCP8.5 | 2070 | 76.5488 | 82.3665 | 88.4635 | 94.59 | 100.7112
| EarltonWind2075RCP8.5 | Earlton | Wind | RCP8.5 | 2075 | 76.6247 | 82.4511 | 88.5573 | 94.6904 | 100.8216
| EarltonWind2080RCP8.5 | Earlton | Wind | RCP8.5 | 2080 | 76.7007 | 82.5356 | 88.6512 | 94.7909 | 100.932
| EarltonWind2085RCP8.5 | Earlton | Wind | RCP8.5 | 2085 | 76.8299 | 82.7075 | 88.8756 | 95.0592 | 101.248
| EarltonWind2090RCP8.5 | Earlton | Wind | RCP8.5 | 2090 | 76.9591 | 82.8794 | 89.1 | 95.3276 | 101.564
| EarltonWind2095RCP8.5 | Earlton | Wind | RCP8.5 | 2095 | 76.9591 | 82.8794 | 89.1 | 95.3276 | 101.564
| EarltonWind2100RCP8.5 | Earlton | Wind | RCP8.5 | 2100 | 76.9591 | 82.8794 | 89.1 | 95.3276 | 101.564
| EdisonIce Accretion2023RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2023 | 10.2679 | 12.2591 | 14.784 | 16.7217 | 18.6455
| EdisonIce Accretion2025RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2025 | 10.2793 | 12.2727 | 14.8003 | 16.7402 | 18.6661
| EdisonIce Accretion2030RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2030 | 10.2906 | 12.2862 | 14.8167 | 16.7587 | 18.6866
| EdisonIce Accretion2035RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2035 | 10.302 | 12.2998 | 14.833 | 16.7771 | 18.7072
| EdisonIce Accretion2040RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2040 | 10.3134 | 12.3133 | 14.8493 | 16.7956 | 18.7278
| EdisonIce Accretion2045RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2045 | 10.3247 | 12.3269 | 14.8657 | 16.814 | 18.7484
| EdisonIce Accretion2050RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2050 | 10.3809 | 12.3916 | 14.9408 | 16.8958 | 18.8395
| EdisonIce Accretion2055RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2055 | 10.4257 | 12.4427 | 14.9996 | 16.959 | 18.9101
| EdisonIce Accretion2060RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2060 | 10.4705 | 12.4938 | 15.0584 | 17.0223 | 18.9806
| EdisonIce Accretion2065RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2065 | 10.5153 | 12.545 | 15.1172 | 17.0856 | 19.0512
| EdisonIce Accretion2070RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2070 | 10.5602 | 12.5961 | 15.176 | 17.1489 | 19.1218
| EdisonIce Accretion2075RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2075 | 10.591 | 12.6348 | 15.2227 | 17.2016 | 19.1806
| EdisonIce Accretion2080RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2080 | 10.6219 | 12.6735 | 15.2693 | 17.2543 | 19.2394
| EdisonIce Accretion2085RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2085 | 10.6527 | 12.7123 | 15.316 | 17.3071 | 19.2982
| EdisonIce Accretion2090RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2090 | 10.6836 | 12.751 | 15.3627 | 17.3598 | 19.357
| EdisonIce Accretion2095RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2095 | 10.7144 | 12.7897 | 15.4093 | 17.4125 | 19.4158
| EdisonIce Accretion2100RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2100 | 10.7453 | 12.8285 | 15.456 | 17.4653 | 19.4746
| EdisonIce Accretion2023RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2023 | 10.2679 | 12.2591 | 14.784 | 16.7217 | 18.6455
| EdisonIce Accretion2025RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2025 | 10.2793 | 12.2727 | 14.8003 | 16.7402 | 18.6661
| EdisonIce Accretion2030RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2030 | 10.2906 | 12.2862 | 14.8167 | 16.7587 | 18.6866
| EdisonIce Accretion2035RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2035 | 10.302 | 12.2998 | 14.833 | 16.7771 | 18.7072
| EdisonIce Accretion2040RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2040 | 10.3134 | 12.3133 | 14.8493 | 16.7956 | 18.7278
| EdisonIce Accretion2045RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2045 | 10.3247 | 12.3269 | 14.8657 | 16.814 | 18.7484
| EdisonIce Accretion2050RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2050 | 10.3809 | 12.3916 | 14.9408 | 16.8958 | 18.8395
| EdisonIce Accretion2055RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2055 | 10.4257 | 12.4427 | 14.9996 | 16.959 | 18.9101
| EdisonIce Accretion2060RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2060 | 10.4705 | 12.4938 | 15.0584 | 17.0223 | 18.9806
| EdisonIce Accretion2065RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2065 | 10.5153 | 12.545 | 15.1172 | 17.0856 | 19.0512
| EdisonIce Accretion2070RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2070 | 10.5602 | 12.5961 | 15.176 | 17.1489 | 19.1218
| EdisonIce Accretion2075RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2075 | 10.6064 | 12.6542 | 15.246 | 17.228 | 19.21
| EdisonIce Accretion2080RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2080 | 10.6527 | 12.7123 | 15.316 | 17.3071 | 19.2982
| EdisonIce Accretion2085RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2085 | 10.699 | 12.7704 | 15.386 | 17.3862 | 19.3864
| EdisonIce Accretion2090RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2090 | 10.7453 | 12.8246 | 15.4513 | 17.4547 | 19.4628
| EdisonIce Accretion2095RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2095 | 10.7453 | 12.8207 | 15.4467 | 17.4442 | 19.451
| EdisonIce Accretion2100RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2100 | 10.7453 | 12.8169 | 15.442 | 17.4336 | 19.4393
| EdisonIce Accretion2023RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2023 | 10.2679 | 12.2591 | 14.784 | 16.7217 | 18.6455
| EdisonIce Accretion2025RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2025 | 10.2906 | 12.2862 | 14.8167 | 16.7587 | 18.6866
| EdisonIce Accretion2030RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2030 | 10.3134 | 12.3133 | 14.8493 | 16.7956 | 18.7278
| EdisonIce Accretion2035RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2035 | 10.3361 | 12.3404 | 14.882 | 16.8325 | 18.769
| EdisonIce Accretion2040RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2040 | 10.4108 | 12.4257 | 14.98 | 16.9379 | 18.8866
| EdisonIce Accretion2045RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2045 | 10.4855 | 12.5109 | 15.078 | 17.0434 | 19.0042
| EdisonIce Accretion2050RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2050 | 10.6219 | 12.6735 | 15.2693 | 17.2543 | 19.2394
| EdisonIce Accretion2055RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2055 | 10.6836 | 12.751 | 15.3627 | 17.3598 | 19.357
| EdisonIce Accretion2060RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2060 | 10.7453 | 12.8246 | 15.4513 | 17.4547 | 19.4628
| EdisonIce Accretion2065RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2065 | 10.7453 | 12.8207 | 15.4467 | 17.4442 | 19.451
| EdisonIce Accretion2070RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2070 | 10.7485 | 12.8246 | 15.456 | 17.4547 | 19.4687
| EdisonIce Accretion2075RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2075 | 10.7518 | 12.8324 | 15.47 | 17.4758 | 19.4981
| EdisonIce Accretion2080RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2080 | 10.755 | 12.8401 | 15.484 | 17.4969 | 19.5275
| EdisonIce Accretion2085RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2085 | 10.5212 | 12.5554 | 15.134 | 17.1014 | 19.0777
| EdisonIce Accretion2090RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2090 | 10.2874 | 12.2707 | 14.784 | 16.7059 | 18.6278
| EdisonIce Accretion2095RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2095 | 10.2874 | 12.2707 | 14.784 | 16.7059 | 18.6278
| EdisonIce Accretion2100RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2100 | 10.2874 | 12.2707 | 14.784 | 16.7059 | 18.6278
| EdisonWind2023RCP4.5 | Edison | Wind | RCP4.5 | 2023 | 73.9171 | 79.6982 | 85.8075 | 91.8868 | 97.9659
| EdisonWind2025RCP4.5 | Edison | Wind | RCP4.5 | 2025 | 73.9465 | 79.7167 | 85.8103 | 91.8792 | 97.9481
| EdisonWind2030RCP4.5 | Edison | Wind | RCP4.5 | 2030 | 73.9758 | 79.7351 | 85.8132 | 91.8716 | 97.9304
| EdisonWind2035RCP4.5 | Edison | Wind | RCP4.5 | 2035 | 74.0052 | 79.7535 | 85.816 | 91.864 | 97.9126
| EdisonWind2040RCP4.5 | Edison | Wind | RCP4.5 | 2040 | 74.0346 | 79.772 | 85.8188 | 91.8565 | 97.8948
| EdisonWind2045RCP4.5 | Edison | Wind | RCP4.5 | 2045 | 74.0639 | 79.7904 | 85.8217 | 91.8489 | 97.8771
| EdisonWind2050RCP4.5 | Edison | Wind | RCP4.5 | 2050 | 74.1902 | 79.9259 | 85.9656 | 92.0032 | 98.0434
| EdisonWind2055RCP4.5 | Edison | Wind | RCP4.5 | 2055 | 74.287 | 80.0429 | 86.1067 | 92.1651 | 98.2275
| EdisonWind2060RCP4.5 | Edison | Wind | RCP4.5 | 2060 | 74.3839 | 80.1599 | 86.2478 | 92.327 | 98.4116
| EdisonWind2065RCP4.5 | Edison | Wind | RCP4.5 | 2065 | 74.4808 | 80.2769 | 86.3889 | 92.4889 | 98.5957
| EdisonWind2070RCP4.5 | Edison | Wind | RCP4.5 | 2070 | 74.5777 | 80.3938 | 86.53 | 92.6508 | 98.7799
| EdisonWind2075RCP4.5 | Edison | Wind | RCP4.5 | 2075 | 74.6156 | 80.4373 | 86.581 | 92.7084 | 98.8428
| EdisonWind2080RCP4.5 | Edison | Wind | RCP4.5 | 2080 | 74.6535 | 80.4808 | 86.632 | 92.766 | 98.9058
| EdisonWind2085RCP4.5 | Edison | Wind | RCP4.5 | 2085 | 74.6914 | 80.5243 | 86.683 | 92.8236 | 98.9688
| EdisonWind2090RCP4.5 | Edison | Wind | RCP4.5 | 2090 | 74.7294 | 80.5678 | 86.734 | 92.8812 | 99.0318
| EdisonWind2095RCP4.5 | Edison | Wind | RCP4.5 | 2095 | 74.7673 | 80.6112 | 86.785 | 92.9388 | 99.0948
| EdisonWind2100RCP4.5 | Edison | Wind | RCP4.5 | 2100 | 74.8052 | 80.6547 | 86.836 | 92.9964 | 99.1578
| EdisonWind2023RCP6.0 | Edison | Wind | RCP6.0 | 2023 | 73.9171 | 79.6982 | 85.8075 | 91.8868 | 97.9659
| EdisonWind2025RCP6.0 | Edison | Wind | RCP6.0 | 2025 | 73.9465 | 79.7167 | 85.8103 | 91.8792 | 97.9481
| EdisonWind2030RCP6.0 | Edison | Wind | RCP6.0 | 2030 | 73.9758 | 79.7351 | 85.8132 | 91.8716 | 97.9304
| EdisonWind2035RCP6.0 | Edison | Wind | RCP6.0 | 2035 | 74.0052 | 79.7535 | 85.816 | 91.864 | 97.9126
| EdisonWind2040RCP6.0 | Edison | Wind | RCP6.0 | 2040 | 74.0346 | 79.772 | 85.8188 | 91.8565 | 97.8948
| EdisonWind2045RCP6.0 | Edison | Wind | RCP6.0 | 2045 | 74.0639 | 79.7904 | 85.8217 | 91.8489 | 97.8771
| EdisonWind2050RCP6.0 | Edison | Wind | RCP6.0 | 2050 | 74.1902 | 79.9259 | 85.9656 | 92.0032 | 98.0434
| EdisonWind2055RCP6.0 | Edison | Wind | RCP6.0 | 2055 | 74.287 | 80.0429 | 86.1067 | 92.1651 | 98.2275
| EdisonWind2060RCP6.0 | Edison | Wind | RCP6.0 | 2060 | 74.3839 | 80.1599 | 86.2478 | 92.327 | 98.4116
| EdisonWind2065RCP6.0 | Edison | Wind | RCP6.0 | 2065 | 74.4808 | 80.2769 | 86.3889 | 92.4889 | 98.5957
| EdisonWind2070RCP6.0 | Edison | Wind | RCP6.0 | 2070 | 74.5777 | 80.3938 | 86.53 | 92.6508 | 98.7799
| EdisonWind2075RCP6.0 | Edison | Wind | RCP6.0 | 2075 | 74.6346 | 80.4591 | 86.6065 | 92.7372 | 98.8743
| EdisonWind2080RCP6.0 | Edison | Wind | RCP6.0 | 2080 | 74.6914 | 80.5243 | 86.683 | 92.8236 | 98.9688
| EdisonWind2085RCP6.0 | Edison | Wind | RCP6.0 | 2085 | 74.7483 | 80.5895 | 86.7595 | 92.91 | 99.0633
| EdisonWind2090RCP6.0 | Edison | Wind | RCP6.0 | 2090 | 75.0376 | 80.963 | 87.2355 | 93.4754 | 99.7166
| EdisonWind2095RCP6.0 | Edison | Wind | RCP6.0 | 2095 | 75.2701 | 81.2713 | 87.635 | 93.9544 | 100.2753
| EdisonWind2100RCP6.0 | Edison | Wind | RCP6.0 | 2100 | 75.5025 | 81.5796 | 88.0345 | 94.4334 | 100.8341
| EdisonWind2023RCP8.5 | Edison | Wind | RCP8.5 | 2023 | 73.9171 | 79.6982 | 85.8075 | 91.8868 | 97.9659
| EdisonWind2025RCP8.5 | Edison | Wind | RCP8.5 | 2025 | 73.9758 | 79.7351 | 85.8132 | 91.8716 | 97.9304
| EdisonWind2030RCP8.5 | Edison | Wind | RCP8.5 | 2030 | 74.0346 | 79.772 | 85.8188 | 91.8565 | 97.8948
| EdisonWind2035RCP8.5 | Edison | Wind | RCP8.5 | 2035 | 74.0933 | 79.8089 | 85.8245 | 91.8413 | 97.8593
| EdisonWind2040RCP8.5 | Edison | Wind | RCP8.5 | 2040 | 74.2547 | 80.0039 | 86.0597 | 92.1111 | 98.1662
| EdisonWind2045RCP8.5 | Edison | Wind | RCP8.5 | 2045 | 74.4162 | 80.1989 | 86.2948 | 92.3809 | 98.473
| EdisonWind2050RCP8.5 | Edison | Wind | RCP8.5 | 2050 | 74.6535 | 80.4808 | 86.632 | 92.766 | 98.9058
| EdisonWind2055RCP8.5 | Edison | Wind | RCP8.5 | 2055 | 74.7294 | 80.5678 | 86.734 | 92.8812 | 99.0318
| EdisonWind2060RCP8.5 | Edison | Wind | RCP8.5 | 2060 | 75.0376 | 80.963 | 87.2355 | 93.4754 | 99.7166
| EdisonWind2065RCP8.5 | Edison | Wind | RCP8.5 | 2065 | 75.2701 | 81.2713 | 87.635 | 93.9544 | 100.2753
| EdisonWind2070RCP8.5 | Edison | Wind | RCP8.5 | 2070 | 75.6909 | 81.7957 | 88.2838 | 94.7093 | 101.141
| EdisonWind2075RCP8.5 | Edison | Wind | RCP8.5 | 2075 | 75.8792 | 82.0117 | 88.5332 | 94.9851 | 101.4478
| EdisonWind2080RCP8.5 | Edison | Wind | RCP8.5 | 2080 | 76.0676 | 82.2278 | 88.7825 | 95.261 | 101.7547
| EdisonWind2085RCP8.5 | Edison | Wind | RCP8.5 | 2085 | 76.3318 | 82.5519 | 89.1863 | 95.7294 | 102.2828
| EdisonWind2090RCP8.5 | Edison | Wind | RCP8.5 | 2090 | 76.5961 | 82.876 | 89.59 | 96.1978 | 102.8109
| EdisonWind2095RCP8.5 | Edison | Wind | RCP8.5 | 2095 | 76.5961 | 82.876 | 89.59 | 96.1978 | 102.8109
| EdisonWind2100RCP8.5 | Edison | Wind | RCP8.5 | 2100 | 76.5961 | 82.876 | 89.59 | 96.1978 | 102.8109
| Elliot Lake Ice Accretion2023RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2023 | 15.3086 | 18.2783 | 22.066 | 24.9346 | 27.8309
| Elliot Lake Ice Accretion2025RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2025 | 15.2576 | 18.2204 | 22 | 24.8641 | 27.7523
| Elliot Lake Ice Accretion2030RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2030 | 15.2066 | 18.1626 | 21.934 | 24.7937 | 27.6738
| Elliot Lake Ice Accretion2035RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2035 | 15.1555 | 18.1048 | 21.868 | 24.7233 | 27.5953
| Elliot Lake Ice Accretion2040RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2040 | 15.1045 | 18.047 | 21.802 | 24.6528 | 27.5167
| Elliot Lake Ice Accretion2045RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2045 | 15.0535 | 17.9891 | 21.736 | 24.5824 | 27.4382
| Elliot Lake Ice Accretion2050RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2050 | 15.1739 | 18.1504 | 21.9472 | 24.8351 | 27.7255
| Elliot Lake Ice Accretion2055RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2055 | 15.3454 | 18.3696 | 22.2244 | 25.1583 | 28.0914
| Elliot Lake Ice Accretion2060RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2060 | 15.5168 | 18.5887 | 22.5016 | 25.4815 | 28.4574
| Elliot Lake Ice Accretion2065RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2065 | 15.6883 | 18.8078 | 22.7788 | 25.8047 | 28.8233
| Elliot Lake Ice Accretion2070RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2070 | 15.8597 | 19.0269 | 23.056 | 26.1279 | 29.1892
| Elliot Lake Ice Accretion2075RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2075 | 15.8521 | 19.0269 | 23.0633 | 26.1403 | 29.2076
| Elliot Lake Ice Accretion2080RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2080 | 15.8444 | 19.0269 | 23.0707 | 26.1527 | 29.2261
| Elliot Lake Ice Accretion2085RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2085 | 15.8368 | 19.0269 | 23.078 | 26.1651 | 29.2446
| Elliot Lake Ice Accretion2090RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2090 | 15.8291 | 19.0269 | 23.0853 | 26.1776 | 29.2631
| Elliot Lake Ice Accretion2095RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2095 | 15.8215 | 19.0269 | 23.0927 | 26.19 | 29.2816
| Elliot Lake Ice Accretion2100RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2100 | 15.8138 | 19.0269 | 23.1 | 26.2024 | 29.3
| Elliot Lake Ice Accretion2023RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2023 | 15.3086 | 18.2783 | 22.066 | 24.9346 | 27.8309
| Elliot Lake Ice Accretion2025RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2025 | 15.2576 | 18.2204 | 22 | 24.8641 | 27.7523
| Elliot Lake Ice Accretion2030RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2030 | 15.2066 | 18.1626 | 21.934 | 24.7937 | 27.6738
| Elliot Lake Ice Accretion2035RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2035 | 15.1555 | 18.1048 | 21.868 | 24.7233 | 27.5953
| Elliot Lake Ice Accretion2040RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2040 | 15.1045 | 18.047 | 21.802 | 24.6528 | 27.5167
| Elliot Lake Ice Accretion2045RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2045 | 15.0535 | 17.9891 | 21.736 | 24.5824 | 27.4382
| Elliot Lake Ice Accretion2050RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2050 | 15.1739 | 18.1504 | 21.9472 | 24.8351 | 27.7255
| Elliot Lake Ice Accretion2055RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2055 | 15.3454 | 18.3696 | 22.2244 | 25.1583 | 28.0914
| Elliot Lake Ice Accretion2060RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2060 | 15.5168 | 18.5887 | 22.5016 | 25.4815 | 28.4574
| Elliot Lake Ice Accretion2065RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2065 | 15.6883 | 18.8078 | 22.7788 | 25.8047 | 28.8233
| Elliot Lake Ice Accretion2070RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2070 | 15.8597 | 19.0269 | 23.056 | 26.1279 | 29.1892
| Elliot Lake Ice Accretion2075RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2075 | 15.8482 | 19.0269 | 23.067 | 26.1465 | 29.2169
| Elliot Lake Ice Accretion2080RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2080 | 15.8368 | 19.0269 | 23.078 | 26.1651 | 29.2446
| Elliot Lake Ice Accretion2085RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2085 | 15.8253 | 19.0269 | 23.089 | 26.1838 | 29.2723
| Elliot Lake Ice Accretion2090RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2090 | 15.8903 | 19.1487 | 23.276 | 26.4262 | 29.568
| Elliot Lake Ice Accretion2095RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2095 | 15.9669 | 19.2704 | 23.452 | 26.6499 | 29.836
| Elliot Lake Ice Accretion2100RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2100 | 16.0434 | 19.3921 | 23.628 | 26.8737 | 30.1039
| Elliot Lake Ice Accretion2023RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2023 | 15.3086 | 18.2783 | 22.066 | 24.9346 | 27.8309
| Elliot Lake Ice Accretion2025RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2025 | 15.2066 | 18.1626 | 21.934 | 24.7937 | 27.6738
| Elliot Lake Ice Accretion2030RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2030 | 15.1045 | 18.047 | 21.802 | 24.6528 | 27.5167
| Elliot Lake Ice Accretion2035RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2035 | 15.0024 | 17.9313 | 21.67 | 24.512 | 27.3596
| Elliot Lake Ice Accretion2040RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2040 | 15.2882 | 18.2965 | 22.132 | 25.0506 | 27.9695
| Elliot Lake Ice Accretion2045RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2045 | 15.574 | 18.6617 | 22.594 | 25.5892 | 28.5793
| Elliot Lake Ice Accretion2050RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2050 | 15.8444 | 19.0269 | 23.0707 | 26.1527 | 29.2261
| Elliot Lake Ice Accretion2055RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2055 | 15.8291 | 19.0269 | 23.0853 | 26.1776 | 29.2631
| Elliot Lake Ice Accretion2060RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2060 | 15.8903 | 19.1487 | 23.276 | 26.4262 | 29.568
| Elliot Lake Ice Accretion2065RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2065 | 15.9669 | 19.2704 | 23.452 | 26.6499 | 29.836
| Elliot Lake Ice Accretion2070RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2070 | 15.6913 | 18.9965 | 23.1807 | 26.3765 | 29.5588
| Elliot Lake Ice Accretion2075RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2075 | 15.3392 | 18.6009 | 22.7333 | 25.8793 | 29.0136
| Elliot Lake Ice Accretion2080RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2080 | 14.9871 | 18.2052 | 22.286 | 25.3821 | 28.4684
| Elliot Lake Ice Accretion2085RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2085 | 15.0101 | 18.26 | 22.374 | 25.4939 | 28.607
| Elliot Lake Ice Accretion2090RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2090 | 15.0331 | 18.3148 | 22.462 | 25.6058 | 28.7456
| Elliot Lake Ice Accretion2095RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2095 | 15.0331 | 18.3148 | 22.462 | 25.6058 | 28.7456
| Elliot Lake Ice Accretion2100RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2100 | 15.0331 | 18.3148 | 22.462 | 25.6058 | 28.7456
| Elliot Lake Wind2023RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2023 | 76.8375 | 82.8057 | 89.0912 | 95.3747 | 101.6543
| Elliot Lake Wind2025RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2025 | 76.9021 | 82.8739 | 89.1645 | 95.4516 | 101.7345
| Elliot Lake Wind2030RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2030 | 76.9667 | 82.9421 | 89.2379 | 95.5285 | 101.8148
| Elliot Lake Wind2035RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2035 | 77.0313 | 83.0103 | 89.3112 | 95.6054 | 101.895
| Elliot Lake Wind2040RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2040 | 77.0959 | 83.0785 | 89.3845 | 95.6823 | 101.9753
| Elliot Lake Wind2045RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2045 | 77.1604 | 83.1467 | 89.4579 | 95.7592 | 102.0555
| Elliot Lake Wind2050RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2050 | 77.2843 | 83.2755 | 89.591 | 95.8982 | 102.2
| Elliot Lake Wind2055RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2055 | 77.3436 | 83.336 | 89.6509 | 95.9603 | 102.2642
| Elliot Lake Wind2060RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2060 | 77.4028 | 83.3966 | 89.7107 | 96.0225 | 102.3284
| Elliot Lake Wind2065RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2065 | 77.4621 | 83.4572 | 89.7706 | 96.0846 | 102.3926
| Elliot Lake Wind2070RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2070 | 77.5214 | 83.5177 | 89.8304 | 96.1468 | 102.4568
| Elliot Lake Wind2075RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2075 | 77.5492 | 83.5532 | 89.8759 | 96.2001 | 102.5187
| Elliot Lake Wind2080RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2080 | 77.5771 | 83.5886 | 89.9213 | 96.2535 | 102.5805
| Elliot Lake Wind2085RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2085 | 77.605 | 83.6241 | 89.9668 | 96.3068 | 102.6424
| Elliot Lake Wind2090RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2090 | 77.6328 | 83.6596 | 90.0123 | 96.3602 | 102.7043
| Elliot Lake Wind2095RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2095 | 77.6607 | 83.695 | 90.0577 | 96.4136 | 102.7661
| Elliot Lake Wind2100RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2100 | 77.6886 | 83.7305 | 90.1032 | 96.4669 | 102.828
| Elliot Lake Wind2023RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2023 | 76.8375 | 82.8057 | 89.0912 | 95.3747 | 101.6543
| Elliot Lake Wind2025RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2025 | 76.9021 | 82.8739 | 89.1645 | 95.4516 | 101.7345
| Elliot Lake Wind2030RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2030 | 76.9667 | 82.9421 | 89.2379 | 95.5285 | 101.8148
| Elliot Lake Wind2035RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2035 | 77.0313 | 83.0103 | 89.3112 | 95.6054 | 101.895
| Elliot Lake Wind2040RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2040 | 77.0959 | 83.0785 | 89.3845 | 95.6823 | 101.9753
| Elliot Lake Wind2045RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2045 | 77.1604 | 83.1467 | 89.4579 | 95.7592 | 102.0555
| Elliot Lake Wind2050RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2050 | 77.2843 | 83.2755 | 89.591 | 95.8982 | 102.2
| Elliot Lake Wind2055RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2055 | 77.3436 | 83.336 | 89.6509 | 95.9603 | 102.2642
| Elliot Lake Wind2060RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2060 | 77.4028 | 83.3966 | 89.7107 | 96.0225 | 102.3284
| Elliot Lake Wind2065RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2065 | 77.4621 | 83.4572 | 89.7706 | 96.0846 | 102.3926
| Elliot Lake Wind2070RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2070 | 77.5214 | 83.5177 | 89.8304 | 96.1468 | 102.4568
| Elliot Lake Wind2075RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2075 | 77.5632 | 83.5709 | 89.8986 | 96.2268 | 102.5496
| Elliot Lake Wind2080RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2080 | 77.605 | 83.6241 | 89.9668 | 96.3068 | 102.6424
| Elliot Lake Wind2085RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2085 | 77.6468 | 83.6773 | 90.035 | 96.3869 | 102.7352
| Elliot Lake Wind2090RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2090 | 77.9165 | 84.0142 | 90.4523 | 96.8687 | 103.2861
| Elliot Lake Wind2095RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2095 | 78.1445 | 84.2979 | 90.8013 | 97.2704 | 103.7443
| Elliot Lake Wind2100RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2100 | 78.3724 | 84.5816 | 91.1504 | 97.6722 | 104.2024
| Elliot Lake Wind2023RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2023 | 76.8375 | 82.8057 | 89.0912 | 95.3747 | 101.6543
| Elliot Lake Wind2025RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2025 | 76.9667 | 82.9421 | 89.2379 | 95.5285 | 101.8148
| Elliot Lake Wind2030RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2030 | 77.0959 | 83.0785 | 89.3845 | 95.6823 | 101.9753
| Elliot Lake Wind2035RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2035 | 77.225 | 83.2149 | 89.5312 | 95.836 | 102.1358
| Elliot Lake Wind2040RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2040 | 77.3238 | 83.3158 | 89.6309 | 95.9396 | 102.2428
| Elliot Lake Wind2045RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2045 | 77.4226 | 83.4168 | 89.7307 | 96.0432 | 102.3498
| Elliot Lake Wind2050RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2050 | 77.5771 | 83.5886 | 89.9213 | 96.2535 | 102.5805
| Elliot Lake Wind2055RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2055 | 77.6328 | 83.6596 | 90.0123 | 96.3602 | 102.7043
| Elliot Lake Wind2060RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2060 | 77.9165 | 84.0142 | 90.4523 | 96.8687 | 103.2861
| Elliot Lake Wind2065RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2065 | 78.1445 | 84.2979 | 90.8013 | 97.2704 | 103.7443
| Elliot Lake Wind2070RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2070 | 78.6865 | 84.9745 | 91.6403 | 98.2465 | 104.8612
| Elliot Lake Wind2075RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2075 | 79.0006 | 85.3673 | 92.1301 | 98.8209 | 105.5199
| Elliot Lake Wind2080RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2080 | 79.3147 | 85.7601 | 92.62 | 99.3953 | 106.1787
| Elliot Lake Wind2085RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2085 | 79.516 | 85.9566 | 92.8048 | 99.5742 | 106.3542
| Elliot Lake Wind2090RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2090 | 79.7174 | 86.153 | 92.9896 | 99.7531 | 106.5298
| Elliot Lake Wind2095RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2095 | 79.7174 | 86.153 | 92.9896 | 99.7531 | 106.5298
| Elliot Lake Wind2100RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2100 | 79.7174 | 86.153 | 92.9896 | 99.7531 | 106.5298
| ElmvaleIce Accretion2023RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2023 | 14.3059 | 17.1163 | 20.664 | 23.374 | 26.0631
| ElmvaleIce Accretion2025RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2025 | 14.301 | 17.1134 | 20.6675 | 23.382 | 26.0807
| ElmvaleIce Accretion2030RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2030 | 14.2962 | 17.1105 | 20.671 | 23.3899 | 26.0984
| ElmvaleIce Accretion2035RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2035 | 14.2913 | 17.1075 | 20.6745 | 23.3978 | 26.116
| ElmvaleIce Accretion2040RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2040 | 14.2864 | 17.1046 | 20.678 | 23.4057 | 26.1337
| ElmvaleIce Accretion2045RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2045 | 14.2815 | 17.1017 | 20.6815 | 23.4136 | 26.1513
| ElmvaleIce Accretion2050RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2050 | 14.2387 | 17.0709 | 20.6682 | 23.412 | 26.1636
| ElmvaleIce Accretion2055RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2055 | 14.2007 | 17.0431 | 20.6514 | 23.4025 | 26.1584
| ElmvaleIce Accretion2060RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2060 | 14.1627 | 17.0152 | 20.6346 | 23.393 | 26.1531
| ElmvaleIce Accretion2065RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2065 | 14.1247 | 16.9873 | 20.6178 | 23.3835 | 26.1478
| ElmvaleIce Accretion2070RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2070 | 14.0867 | 16.9594 | 20.601 | 23.374 | 26.1425
| ElmvaleIce Accretion2075RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2075 | 14.0867 | 16.9797 | 20.6465 | 23.4373 | 26.2219
| ElmvaleIce Accretion2080RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2080 | 14.0867 | 17.0001 | 20.692 | 23.5006 | 26.3012
| ElmvaleIce Accretion2085RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2085 | 14.0867 | 17.0204 | 20.7375 | 23.5639 | 26.3806
| ElmvaleIce Accretion2090RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2090 | 14.0867 | 17.0407 | 20.783 | 23.6272 | 26.46
| ElmvaleIce Accretion2095RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2095 | 14.0867 | 17.0611 | 20.8285 | 23.6904 | 26.5394
| ElmvaleIce Accretion2100RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2100 | 14.0867 | 17.0814 | 20.874 | 23.7537 | 26.6188
| ElmvaleIce Accretion2023RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2023 | 14.3059 | 17.1163 | 20.664 | 23.374 | 26.0631
| ElmvaleIce Accretion2025RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2025 | 14.301 | 17.1134 | 20.6675 | 23.382 | 26.0807
| ElmvaleIce Accretion2030RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2030 | 14.2962 | 17.1105 | 20.671 | 23.3899 | 26.0984
| ElmvaleIce Accretion2035RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2035 | 14.2913 | 17.1075 | 20.6745 | 23.3978 | 26.116
| ElmvaleIce Accretion2040RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2040 | 14.2864 | 17.1046 | 20.678 | 23.4057 | 26.1337
| ElmvaleIce Accretion2045RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2045 | 14.2815 | 17.1017 | 20.6815 | 23.4136 | 26.1513
| ElmvaleIce Accretion2050RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2050 | 14.2387 | 17.0709 | 20.6682 | 23.412 | 26.1636
| ElmvaleIce Accretion2055RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2055 | 14.2007 | 17.0431 | 20.6514 | 23.4025 | 26.1584
| ElmvaleIce Accretion2060RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2060 | 14.1627 | 17.0152 | 20.6346 | 23.393 | 26.1531
| ElmvaleIce Accretion2065RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2065 | 14.1247 | 16.9873 | 20.6178 | 23.3835 | 26.1478
| ElmvaleIce Accretion2070RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2070 | 14.0867 | 16.9594 | 20.601 | 23.374 | 26.1425
| ElmvaleIce Accretion2075RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2075 | 14.0867 | 16.9899 | 20.6692 | 23.469 | 26.2615
| ElmvaleIce Accretion2080RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2080 | 14.0867 | 17.0204 | 20.7375 | 23.5639 | 26.3806
| ElmvaleIce Accretion2085RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2085 | 14.0867 | 17.0509 | 20.8057 | 23.6588 | 26.4997
| ElmvaleIce Accretion2090RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2090 | 13.926 | 16.9187 | 20.713 | 23.5876 | 26.46
| ElmvaleIce Accretion2095RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2095 | 13.7652 | 16.756 | 20.552 | 23.4215 | 26.3012
| ElmvaleIce Accretion2100RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2100 | 13.6045 | 16.5934 | 20.391 | 23.2554 | 26.1425
| ElmvaleIce Accretion2023RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2023 | 14.3059 | 17.1163 | 20.664 | 23.374 | 26.0631
| ElmvaleIce Accretion2025RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2025 | 14.2962 | 17.1105 | 20.671 | 23.3899 | 26.0984
| ElmvaleIce Accretion2030RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2030 | 14.2864 | 17.1046 | 20.678 | 23.4057 | 26.1337
| ElmvaleIce Accretion2035RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2035 | 14.2767 | 17.0988 | 20.685 | 23.4215 | 26.1689
| ElmvaleIce Accretion2040RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2040 | 14.2134 | 17.0524 | 20.657 | 23.4057 | 26.1601
| ElmvaleIce Accretion2045RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2045 | 14.15 | 17.0059 | 20.629 | 23.3899 | 26.1513
| ElmvaleIce Accretion2050RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2050 | 14.0867 | 17.0001 | 20.692 | 23.5006 | 26.3012
| ElmvaleIce Accretion2055RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2055 | 14.0867 | 17.0407 | 20.783 | 23.6272 | 26.46
| ElmvaleIce Accretion2060RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2060 | 13.926 | 16.9187 | 20.713 | 23.5876 | 26.46
| ElmvaleIce Accretion2065RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2065 | 13.7652 | 16.756 | 20.552 | 23.4215 | 26.3012
| ElmvaleIce Accretion2070RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2070 | 13.3707 | 16.361 | 20.146 | 23.0102 | 25.8867
| ElmvaleIce Accretion2075RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2075 | 13.1369 | 16.1286 | 19.901 | 22.765 | 25.6309
| ElmvaleIce Accretion2080RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2080 | 12.9031 | 15.8962 | 19.656 | 22.5198 | 25.3751
| ElmvaleIce Accretion2085RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2085 | 12.304 | 15.199 | 18.8475 | 21.618 | 24.3697
| ElmvaleIce Accretion2090RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2090 | 11.7048 | 14.5018 | 18.039 | 20.7163 | 23.3642
| ElmvaleIce Accretion2095RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2095 | 11.7048 | 14.5018 | 18.039 | 20.7163 | 23.3642
| ElmvaleIce Accretion2100RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2100 | 11.7048 | 14.5018 | 18.039 | 20.7163 | 23.3642
| ElmvaleWind2023RCP4.5 | Elmvale | Wind | RCP4.5 | 2023 | 77.2419 | 83.2087 | 89.4895 | 95.7728 | 102.0485
| ElmvaleWind2025RCP4.5 | Elmvale | Wind | RCP4.5 | 2025 | 77.2636 | 83.2363 | 89.5251 | 95.8141 | 102.0975
| ElmvaleWind2030RCP4.5 | Elmvale | Wind | RCP4.5 | 2030 | 77.2854 | 83.2639 | 89.5607 | 95.8553 | 102.1465
| ElmvaleWind2035RCP4.5 | Elmvale | Wind | RCP4.5 | 2035 | 77.3072 | 83.2915 | 89.5963 | 95.8966 | 102.1956
| ElmvaleWind2040RCP4.5 | Elmvale | Wind | RCP4.5 | 2040 | 77.329 | 83.319 | 89.6319 | 95.9379 | 102.2446
| ElmvaleWind2045RCP4.5 | Elmvale | Wind | RCP4.5 | 2045 | 77.3507 | 83.3466 | 89.6675 | 95.9791 | 102.2937
| ElmvaleWind2050RCP4.5 | Elmvale | Wind | RCP4.5 | 2050 | 77.4939 | 83.5149 | 89.8651 | 96.2013 | 102.5436
| ElmvaleWind2055RCP4.5 | Elmvale | Wind | RCP4.5 | 2055 | 77.6154 | 83.6556 | 90.0271 | 96.3823 | 102.7445
| ElmvaleWind2060RCP4.5 | Elmvale | Wind | RCP4.5 | 2060 | 77.7368 | 83.7963 | 90.189 | 96.5632 | 102.9454
| ElmvaleWind2065RCP4.5 | Elmvale | Wind | RCP4.5 | 2065 | 77.8582 | 83.9371 | 90.351 | 96.7442 | 103.1463
| ElmvaleWind2070RCP4.5 | Elmvale | Wind | RCP4.5 | 2070 | 77.9796 | 84.0778 | 90.513 | 96.9251 | 103.3472
| ElmvaleWind2075RCP4.5 | Elmvale | Wind | RCP4.5 | 2075 | 78.0385 | 84.155 | 90.6139 | 97.0457 | 103.4858
| ElmvaleWind2080RCP4.5 | Elmvale | Wind | RCP4.5 | 2080 | 78.0975 | 84.2323 | 90.7147 | 97.1663 | 103.6245
| ElmvaleWind2085RCP4.5 | Elmvale | Wind | RCP4.5 | 2085 | 78.1564 | 84.3095 | 90.8156 | 97.287 | 103.7631
| ElmvaleWind2090RCP4.5 | Elmvale | Wind | RCP4.5 | 2090 | 78.2153 | 84.3868 | 90.9165 | 97.4076 | 103.9018
| ElmvaleWind2095RCP4.5 | Elmvale | Wind | RCP4.5 | 2095 | 78.2742 | 84.464 | 91.0173 | 97.5282 | 104.0405
| ElmvaleWind2100RCP4.5 | Elmvale | Wind | RCP4.5 | 2100 | 78.3331 | 84.5413 | 91.1182 | 97.6488 | 104.1791
| ElmvaleWind2023RCP6.0 | Elmvale | Wind | RCP6.0 | 2023 | 77.2419 | 83.2087 | 89.4895 | 95.7728 | 102.0485
| ElmvaleWind2025RCP6.0 | Elmvale | Wind | RCP6.0 | 2025 | 77.2636 | 83.2363 | 89.5251 | 95.8141 | 102.0975
| ElmvaleWind2030RCP6.0 | Elmvale | Wind | RCP6.0 | 2030 | 77.2854 | 83.2639 | 89.5607 | 95.8553 | 102.1465
| ElmvaleWind2035RCP6.0 | Elmvale | Wind | RCP6.0 | 2035 | 77.3072 | 83.2915 | 89.5963 | 95.8966 | 102.1956
| ElmvaleWind2040RCP6.0 | Elmvale | Wind | RCP6.0 | 2040 | 77.329 | 83.319 | 89.6319 | 95.9379 | 102.2446
| ElmvaleWind2045RCP6.0 | Elmvale | Wind | RCP6.0 | 2045 | 77.3507 | 83.3466 | 89.6675 | 95.9791 | 102.2937
| ElmvaleWind2050RCP6.0 | Elmvale | Wind | RCP6.0 | 2050 | 77.4939 | 83.5149 | 89.8651 | 96.2013 | 102.5436
| ElmvaleWind2055RCP6.0 | Elmvale | Wind | RCP6.0 | 2055 | 77.6154 | 83.6556 | 90.0271 | 96.3823 | 102.7445
| ElmvaleWind2060RCP6.0 | Elmvale | Wind | RCP6.0 | 2060 | 77.7368 | 83.7963 | 90.189 | 96.5632 | 102.9454
| ElmvaleWind2065RCP6.0 | Elmvale | Wind | RCP6.0 | 2065 | 77.8582 | 83.9371 | 90.351 | 96.7442 | 103.1463
| ElmvaleWind2070RCP6.0 | Elmvale | Wind | RCP6.0 | 2070 | 77.9796 | 84.0778 | 90.513 | 96.9251 | 103.3472
| ElmvaleWind2075RCP6.0 | Elmvale | Wind | RCP6.0 | 2075 | 78.068 | 84.1936 | 90.6643 | 97.106 | 103.5551
| ElmvaleWind2080RCP6.0 | Elmvale | Wind | RCP6.0 | 2080 | 78.1564 | 84.3095 | 90.8156 | 97.287 | 103.7631
| ElmvaleWind2085RCP6.0 | Elmvale | Wind | RCP6.0 | 2085 | 78.2448 | 84.4254 | 90.9669 | 97.4679 | 103.9711
| ElmvaleWind2090RCP6.0 | Elmvale | Wind | RCP6.0 | 2090 | 78.6124 | 84.8779 | 91.5217 | 98.1123 | 104.7067
| ElmvaleWind2095RCP6.0 | Elmvale | Wind | RCP6.0 | 2095 | 78.8916 | 85.2145 | 91.9251 | 98.5757 | 105.2343
| ElmvaleWind2100RCP6.0 | Elmvale | Wind | RCP6.0 | 2100 | 79.1708 | 85.5511 | 92.3286 | 99.0392 | 105.7619
| ElmvaleWind2023RCP8.5 | Elmvale | Wind | RCP8.5 | 2023 | 77.2419 | 83.2087 | 89.4895 | 95.7728 | 102.0485
| ElmvaleWind2025RCP8.5 | Elmvale | Wind | RCP8.5 | 2025 | 77.2854 | 83.2639 | 89.5607 | 95.8553 | 102.1465
| ElmvaleWind2030RCP8.5 | Elmvale | Wind | RCP8.5 | 2030 | 77.329 | 83.319 | 89.6319 | 95.9379 | 102.2446
| ElmvaleWind2035RCP8.5 | Elmvale | Wind | RCP8.5 | 2035 | 77.3725 | 83.3742 | 89.7031 | 96.0204 | 102.3427
| ElmvaleWind2040RCP8.5 | Elmvale | Wind | RCP8.5 | 2040 | 77.5749 | 83.6087 | 89.9731 | 96.322 | 102.6775
| ElmvaleWind2045RCP8.5 | Elmvale | Wind | RCP8.5 | 2045 | 77.7773 | 83.8433 | 90.243 | 96.6235 | 103.0123
| ElmvaleWind2050RCP8.5 | Elmvale | Wind | RCP8.5 | 2050 | 78.0975 | 84.2323 | 90.7147 | 97.1663 | 103.6245
| ElmvaleWind2055RCP8.5 | Elmvale | Wind | RCP8.5 | 2055 | 78.2153 | 84.3868 | 90.9165 | 97.4076 | 103.9018
| ElmvaleWind2060RCP8.5 | Elmvale | Wind | RCP8.5 | 2060 | 78.6124 | 84.8779 | 91.5217 | 98.1123 | 104.7067
| ElmvaleWind2065RCP8.5 | Elmvale | Wind | RCP8.5 | 2065 | 78.8916 | 85.2145 | 91.9251 | 98.5757 | 105.2343
| ElmvaleWind2070RCP8.5 | Elmvale | Wind | RCP8.5 | 2070 | 79.3194 | 85.7304 | 92.5511 | 99.2963 | 106.0528
| ElmvaleWind2075RCP8.5 | Elmvale | Wind | RCP8.5 | 2075 | 79.468 | 85.9097 | 92.7736 | 99.5534 | 106.3436
| ElmvaleWind2080RCP8.5 | Elmvale | Wind | RCP8.5 | 2080 | 79.6165 | 86.0891 | 92.9961 | 99.8106 | 106.6345
| ElmvaleWind2085RCP8.5 | Elmvale | Wind | RCP8.5 | 2085 | 79.6473 | 86.1222 | 93.0273 | 99.8439 | 106.6649
| ElmvaleWind2090RCP8.5 | Elmvale | Wind | RCP8.5 | 2090 | 79.678 | 86.1553 | 93.0584 | 99.8772 | 106.6953
| ElmvaleWind2095RCP8.5 | Elmvale | Wind | RCP8.5 | 2095 | 79.678 | 86.1553 | 93.0584 | 99.8772 | 106.6953
| ElmvaleWind2100RCP8.5 | Elmvale | Wind | RCP8.5 | 2100 | 79.678 | 86.1553 | 93.0584 | 99.8772 | 106.6953
| EmbroIce Accretion2023RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
| EmbroIce Accretion2025RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2025 | 20.3952 | 24.4642 | 29.605 | 33.5328 | 37.4661
| EmbroIce Accretion2030RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2030 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
| EmbroIce Accretion2035RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2035 | 20.3117 | 24.3895 | 29.535 | 33.4763 | 37.4031
| EmbroIce Accretion2040RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2040 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
| EmbroIce Accretion2045RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2045 | 20.2282 | 24.3148 | 29.465 | 33.4198 | 37.3401
| EmbroIce Accretion2050RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2050 | 20.0571 | 24.153 | 29.316 | 33.2762 | 37.2028
| EmbroIce Accretion2055RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2055 | 19.9276 | 24.0285 | 29.202 | 33.161 | 37.0969
| EmbroIce Accretion2060RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2060 | 19.7982 | 23.904 | 29.088 | 33.0457 | 36.9911
| EmbroIce Accretion2065RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2065 | 19.6688 | 23.7795 | 28.974 | 32.9305 | 36.8852
| EmbroIce Accretion2070RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2070 | 19.5394 | 23.655 | 28.86 | 32.8152 | 36.7794
| EmbroIce Accretion2075RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2075 | 19.4837 | 23.6135 | 28.84 | 32.8095 | 36.7857
| EmbroIce Accretion2080RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2080 | 19.428 | 23.572 | 28.82 | 32.8039 | 36.792
| EmbroIce Accretion2085RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2085 | 19.3724 | 23.5305 | 28.8 | 32.7982 | 36.7983
| EmbroIce Accretion2090RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2090 | 19.3167 | 23.489 | 28.78 | 32.7926 | 36.8046
| EmbroIce Accretion2095RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2095 | 19.261 | 23.4475 | 28.76 | 32.7869 | 36.8109
| EmbroIce Accretion2100RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2100 | 19.2054 | 23.406 | 28.74 | 32.7813 | 36.8172
| EmbroIce Accretion2023RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
| EmbroIce Accretion2025RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2025 | 20.3952 | 24.4642 | 29.605 | 33.5328 | 37.4661
| EmbroIce Accretion2030RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2030 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
| EmbroIce Accretion2035RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2035 | 20.3117 | 24.3895 | 29.535 | 33.4763 | 37.4031
| EmbroIce Accretion2040RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2040 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
| EmbroIce Accretion2045RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2045 | 20.2282 | 24.3148 | 29.465 | 33.4198 | 37.3401
| EmbroIce Accretion2050RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2050 | 20.0571 | 24.153 | 29.316 | 33.2762 | 37.2028
| EmbroIce Accretion2055RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2055 | 19.9276 | 24.0285 | 29.202 | 33.161 | 37.0969
| EmbroIce Accretion2060RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2060 | 19.7982 | 23.904 | 29.088 | 33.0457 | 36.9911
| EmbroIce Accretion2065RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2065 | 19.6688 | 23.7795 | 28.974 | 32.9305 | 36.8852
| EmbroIce Accretion2070RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2070 | 19.5394 | 23.655 | 28.86 | 32.8152 | 36.7794
| EmbroIce Accretion2075RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2075 | 19.4559 | 23.5927 | 28.83 | 32.8067 | 36.7888
| EmbroIce Accretion2080RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2080 | 19.3724 | 23.5305 | 28.8 | 32.7982 | 36.7983
| EmbroIce Accretion2085RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2085 | 19.2889 | 23.4682 | 28.77 | 32.7898 | 36.8077
| EmbroIce Accretion2090RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2090 | 18.7739 | 22.9412 | 28.21 | 32.2163 | 36.1998
| EmbroIce Accretion2095RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2095 | 18.3425 | 22.4764 | 27.68 | 31.6513 | 35.5824
| EmbroIce Accretion2100RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2100 | 17.9111 | 22.0116 | 27.15 | 31.0863 | 34.965
| EmbroIce Accretion2023RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
| EmbroIce Accretion2025RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2025 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
| EmbroIce Accretion2030RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2030 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
| EmbroIce Accretion2035RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2035 | 20.1865 | 24.2775 | 29.43 | 33.3915 | 37.3086
| EmbroIce Accretion2040RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2040 | 19.9708 | 24.07 | 29.24 | 33.1994 | 37.1322
| EmbroIce Accretion2045RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2045 | 19.7551 | 23.8625 | 29.05 | 33.0073 | 36.9558
| EmbroIce Accretion2050RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2050 | 19.428 | 23.572 | 28.82 | 32.8039 | 36.792
| EmbroIce Accretion2055RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2055 | 19.3167 | 23.489 | 28.78 | 32.7926 | 36.8046
| EmbroIce Accretion2060RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2060 | 18.7739 | 22.9412 | 28.21 | 32.2163 | 36.1998
| EmbroIce Accretion2065RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2065 | 18.3425 | 22.4764 | 27.68 | 31.6513 | 35.5824
| EmbroIce Accretion2070RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2070 | 17.5353 | 21.6049 | 26.71 | 30.6117 | 34.461
| EmbroIce Accretion2075RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2075 | 17.1596 | 21.1982 | 26.27 | 30.1371 | 33.957
| EmbroIce Accretion2080RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2080 | 16.7838 | 20.7915 | 25.83 | 29.6625 | 33.453
| EmbroIce Accretion2085RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2085 | 15.8549 | 19.7208 | 24.57 | 28.2387 | 31.9032
| EmbroIce Accretion2090RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2090 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
| EmbroIce Accretion2095RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2095 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
| EmbroIce Accretion2100RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2100 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
| EmbroWind2023RCP4.5 | Embro | Wind | RCP4.5 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
| EmbroWind2025RCP4.5 | Embro | Wind | RCP4.5 | 2025 | 87.206 | 94.102 | 101.4083 | 108.6746 | 115.9494
| EmbroWind2030RCP4.5 | Embro | Wind | RCP4.5 | 2030 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
| EmbroWind2035RCP4.5 | Embro | Wind | RCP4.5 | 2035 | 87.3672 | 94.316 | 101.685 | 109.0063 | 116.337
| EmbroWind2040RCP4.5 | Embro | Wind | RCP4.5 | 2040 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
| EmbroWind2045RCP4.5 | Embro | Wind | RCP4.5 | 2045 | 87.5283 | 94.5299 | 101.9617 | 109.338 | 116.7246
| EmbroWind2050RCP4.5 | Embro | Wind | RCP4.5 | 2050 | 87.678 | 94.7205 | 102.206 | 109.6258 | 117.0575
| EmbroWind2055RCP4.5 | Embro | Wind | RCP4.5 | 2055 | 87.7471 | 94.8042 | 102.312 | 109.7478 | 117.1966
| EmbroWind2060RCP4.5 | Embro | Wind | RCP4.5 | 2060 | 87.8162 | 94.8879 | 102.418 | 109.8697 | 117.3356
| EmbroWind2065RCP4.5 | Embro | Wind | RCP4.5 | 2065 | 87.8852 | 94.9716 | 102.524 | 109.9917 | 117.4747
| EmbroWind2070RCP4.5 | Embro | Wind | RCP4.5 | 2070 | 87.9543 | 95.0553 | 102.63 | 110.1137 | 117.6138
| EmbroWind2075RCP4.5 | Embro | Wind | RCP4.5 | 2075 | 88.0407 | 95.1746 | 102.7917 | 110.3117 | 117.8494
| EmbroWind2080RCP4.5 | Embro | Wind | RCP4.5 | 2080 | 88.127 | 95.294 | 102.9533 | 110.5096 | 118.085
| EmbroWind2085RCP4.5 | Embro | Wind | RCP4.5 | 2085 | 88.2134 | 95.4134 | 103.115 | 110.7075 | 118.3206
| EmbroWind2090RCP4.5 | Embro | Wind | RCP4.5 | 2090 | 88.2997 | 95.5327 | 103.2767 | 110.9055 | 118.5562
| EmbroWind2095RCP4.5 | Embro | Wind | RCP4.5 | 2095 | 88.3861 | 95.6521 | 103.4383 | 111.1034 | 118.7918
| EmbroWind2100RCP4.5 | Embro | Wind | RCP4.5 | 2100 | 88.4724 | 95.7714 | 103.6 | 111.3014 | 119.0274
| EmbroWind2023RCP6.0 | Embro | Wind | RCP6.0 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
| EmbroWind2025RCP6.0 | Embro | Wind | RCP6.0 | 2025 | 87.206 | 94.102 | 101.4083 | 108.6746 | 115.9494
| EmbroWind2030RCP6.0 | Embro | Wind | RCP6.0 | 2030 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
| EmbroWind2035RCP6.0 | Embro | Wind | RCP6.0 | 2035 | 87.3672 | 94.316 | 101.685 | 109.0063 | 116.337
| EmbroWind2040RCP6.0 | Embro | Wind | RCP6.0 | 2040 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
| EmbroWind2045RCP6.0 | Embro | Wind | RCP6.0 | 2045 | 87.5283 | 94.5299 | 101.9617 | 109.338 | 116.7246
| EmbroWind2050RCP6.0 | Embro | Wind | RCP6.0 | 2050 | 87.678 | 94.7205 | 102.206 | 109.6258 | 117.0575
| EmbroWind2055RCP6.0 | Embro | Wind | RCP6.0 | 2055 | 87.7471 | 94.8042 | 102.312 | 109.7478 | 117.1966
| EmbroWind2060RCP6.0 | Embro | Wind | RCP6.0 | 2060 | 87.8162 | 94.8879 | 102.418 | 109.8697 | 117.3356
| EmbroWind2065RCP6.0 | Embro | Wind | RCP6.0 | 2065 | 87.8852 | 94.9716 | 102.524 | 109.9917 | 117.4747
| EmbroWind2070RCP6.0 | Embro | Wind | RCP6.0 | 2070 | 87.9543 | 95.0553 | 102.63 | 110.1137 | 117.6138
| EmbroWind2075RCP6.0 | Embro | Wind | RCP6.0 | 2075 | 88.0838 | 95.2343 | 102.8725 | 110.4106 | 117.9672
| EmbroWind2080RCP6.0 | Embro | Wind | RCP6.0 | 2080 | 88.2134 | 95.4134 | 103.115 | 110.7075 | 118.3206
| EmbroWind2085RCP6.0 | Embro | Wind | RCP6.0 | 2085 | 88.3429 | 95.5924 | 103.3575 | 111.0045 | 118.674
| EmbroWind2090RCP6.0 | Embro | Wind | RCP6.0 | 2090 | 88.8264 | 96.2271 | 104.18 | 111.9862 | 119.8216
| EmbroWind2095RCP6.0 | Embro | Wind | RCP6.0 | 2095 | 89.1805 | 96.6828 | 104.76 | 112.671 | 120.6158
| EmbroWind2100RCP6.0 | Embro | Wind | RCP6.0 | 2100 | 89.5345 | 97.1385 | 105.34 | 113.3558 | 121.41
| EmbroWind2023RCP8.5 | Embro | Wind | RCP8.5 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
| EmbroWind2025RCP8.5 | Embro | Wind | RCP8.5 | 2025 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
| EmbroWind2030RCP8.5 | Embro | Wind | RCP8.5 | 2030 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
| EmbroWind2035RCP8.5 | Embro | Wind | RCP8.5 | 2035 | 87.6089 | 94.6368 | 102.1 | 109.5038 | 116.9184
| EmbroWind2040RCP8.5 | Embro | Wind | RCP8.5 | 2040 | 87.7241 | 94.7763 | 102.2767 | 109.7071 | 117.1502
| EmbroWind2045RCP8.5 | Embro | Wind | RCP8.5 | 2045 | 87.8392 | 94.9158 | 102.4533 | 109.9104 | 117.382
| EmbroWind2050RCP8.5 | Embro | Wind | RCP8.5 | 2050 | 88.127 | 95.294 | 102.9533 | 110.5096 | 118.085
| EmbroWind2055RCP8.5 | Embro | Wind | RCP8.5 | 2055 | 88.2997 | 95.5327 | 103.2767 | 110.9055 | 118.5562
| EmbroWind2060RCP8.5 | Embro | Wind | RCP8.5 | 2060 | 88.8264 | 96.2271 | 104.18 | 111.9862 | 119.8216
| EmbroWind2065RCP8.5 | Embro | Wind | RCP8.5 | 2065 | 89.1805 | 96.6828 | 104.76 | 112.671 | 120.6158
| EmbroWind2070RCP8.5 | Embro | Wind | RCP8.5 | 2070 | 89.759 | 97.4392 | 105.7367 | 113.8337 | 121.9724
| EmbroWind2075RCP8.5 | Embro | Wind | RCP8.5 | 2075 | 89.9835 | 97.7399 | 106.1333 | 114.3117 | 122.5348
| EmbroWind2080RCP8.5 | Embro | Wind | RCP8.5 | 2080 | 90.208 | 98.0406 | 106.53 | 114.7896 | 123.0972
| EmbroWind2085RCP8.5 | Embro | Wind | RCP8.5 | 2085 | 90.6484 | 98.6172 | 107.285 | 115.6937 | 124.1517
| EmbroWind2090RCP8.5 | Embro | Wind | RCP8.5 | 2090 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
| EmbroWind2095RCP8.5 | Embro | Wind | RCP8.5 | 2095 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
| EmbroWind2100RCP8.5 | Embro | Wind | RCP8.5 | 2100 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
| EnglehartIce Accretion2023RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2023 | 14.6545 | 17.5296 | 21.16 | 23.9334 | 26.712
| EnglehartIce Accretion2025RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2025 | 14.6638 | 17.5407 | 21.1733 | 23.9522 | 26.733
| EnglehartIce Accretion2030RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2030 | 14.6731 | 17.5517 | 21.1867 | 23.9711 | 26.754
| EnglehartIce Accretion2035RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2035 | 14.6824 | 17.5628 | 21.2 | 23.9899 | 26.775
| EnglehartIce Accretion2040RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2040 | 14.6916 | 17.5739 | 21.2133 | 24.0087 | 26.796
| EnglehartIce Accretion2045RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2045 | 14.7009 | 17.5849 | 21.2267 | 24.0276 | 26.817
| EnglehartIce Accretion2050RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2050 | 14.816 | 17.7321 | 21.416 | 24.2498 | 27.0698
| EnglehartIce Accretion2055RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2055 | 14.9217 | 17.8682 | 21.592 | 24.4532 | 27.3017
| EnglehartIce Accretion2060RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2060 | 15.0275 | 18.0044 | 21.768 | 24.6566 | 27.5335
| EnglehartIce Accretion2065RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2065 | 15.1333 | 18.1405 | 21.944 | 24.86 | 27.7654
| EnglehartIce Accretion2070RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2070 | 15.239 | 18.2766 | 22.12 | 25.0634 | 27.9972
| EnglehartIce Accretion2075RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2075 | 15.3249 | 18.39 | 22.2667 | 25.2367 | 28.1988
| EnglehartIce Accretion2080RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2080 | 15.4107 | 18.5035 | 22.4133 | 25.4099 | 28.4004
| EnglehartIce Accretion2085RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2085 | 15.4965 | 18.6169 | 22.56 | 25.5832 | 28.602
| EnglehartIce Accretion2090RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2090 | 15.5823 | 18.7303 | 22.7067 | 25.7565 | 28.8036
| EnglehartIce Accretion2095RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2095 | 15.6681 | 18.8438 | 22.8533 | 25.9297 | 29.0052
| EnglehartIce Accretion2100RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2100 | 15.754 | 18.9572 | 23 | 26.103 | 29.2068
| EnglehartIce Accretion2023RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2023 | 14.6545 | 17.5296 | 21.16 | 23.9334 | 26.712
| EnglehartIce Accretion2025RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2025 | 14.6638 | 17.5407 | 21.1733 | 23.9522 | 26.733
| EnglehartIce Accretion2030RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2030 | 14.6731 | 17.5517 | 21.1867 | 23.9711 | 26.754
| EnglehartIce Accretion2035RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2035 | 14.6824 | 17.5628 | 21.2 | 23.9899 | 26.775
| EnglehartIce Accretion2040RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2040 | 14.6916 | 17.5739 | 21.2133 | 24.0087 | 26.796
| EnglehartIce Accretion2045RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2045 | 14.7009 | 17.5849 | 21.2267 | 24.0276 | 26.817
| EnglehartIce Accretion2050RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2050 | 14.816 | 17.7321 | 21.416 | 24.2498 | 27.0698
| EnglehartIce Accretion2055RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2055 | 14.9217 | 17.8682 | 21.592 | 24.4532 | 27.3017
| EnglehartIce Accretion2060RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2060 | 15.0275 | 18.0044 | 21.768 | 24.6566 | 27.5335
| EnglehartIce Accretion2065RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2065 | 15.1333 | 18.1405 | 21.944 | 24.86 | 27.7654
| EnglehartIce Accretion2070RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2070 | 15.239 | 18.2766 | 22.12 | 25.0634 | 27.9972
| EnglehartIce Accretion2075RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2075 | 15.3678 | 18.4467 | 22.34 | 25.3233 | 28.2996
| EnglehartIce Accretion2080RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2080 | 15.4965 | 18.6169 | 22.56 | 25.5832 | 28.602
| EnglehartIce Accretion2085RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2085 | 15.6252 | 18.787 | 22.78 | 25.8431 | 28.9044
| EnglehartIce Accretion2090RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2090 | 15.7586 | 18.9793 | 23.0467 | 26.1633 | 29.274
| EnglehartIce Accretion2095RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2095 | 15.7632 | 19.0015 | 23.0933 | 26.2235 | 29.3412
| EnglehartIce Accretion2100RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2100 | 15.7679 | 19.0236 | 23.14 | 26.2838 | 29.4084
| EnglehartIce Accretion2023RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2023 | 14.6545 | 17.5296 | 21.16 | 23.9334 | 26.712
| EnglehartIce Accretion2025RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2025 | 14.6731 | 17.5517 | 21.1867 | 23.9711 | 26.754
| EnglehartIce Accretion2030RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2030 | 14.6916 | 17.5739 | 21.2133 | 24.0087 | 26.796
| EnglehartIce Accretion2035RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2035 | 14.7102 | 17.596 | 21.24 | 24.0464 | 26.838
| EnglehartIce Accretion2040RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2040 | 14.8865 | 17.8229 | 21.5333 | 24.3854 | 27.2244
| EnglehartIce Accretion2045RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2045 | 15.0627 | 18.0497 | 21.8267 | 24.7244 | 27.6108
| EnglehartIce Accretion2050RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2050 | 15.4107 | 18.5035 | 22.4133 | 25.4099 | 28.4004
| EnglehartIce Accretion2055RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2055 | 15.5823 | 18.7303 | 22.7067 | 25.7565 | 28.8036
| EnglehartIce Accretion2060RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2060 | 15.7586 | 18.9793 | 23.0467 | 26.1633 | 29.274
| EnglehartIce Accretion2065RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2065 | 15.7632 | 19.0015 | 23.0933 | 26.2235 | 29.3412
| EnglehartIce Accretion2070RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2070 | 15.5359 | 18.7469 | 22.8067 | 25.9071 | 28.9968
| EnglehartIce Accretion2075RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2075 | 15.304 | 18.4703 | 22.4733 | 25.5305 | 28.5852
| EnglehartIce Accretion2080RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2080 | 15.072 | 18.1936 | 22.14 | 25.1538 | 28.1736
| EnglehartIce Accretion2085RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2085 | 14.8841 | 18.0027 | 21.94 | 24.9391 | 27.9468
| EnglehartIce Accretion2090RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2090 | 14.6963 | 17.8118 | 21.74 | 24.7244 | 27.72
| EnglehartIce Accretion2095RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2095 | 14.6963 | 17.8118 | 21.74 | 24.7244 | 27.72
| EnglehartIce Accretion2100RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2100 | 14.6963 | 17.8118 | 21.74 | 24.7244 | 27.72
| EnglehartWind2023RCP4.5 | Englehart | Wind | RCP4.5 | 2023 | 73.004 | 78.6043 | 84.4788 | 90.3654 | 96.258
| EnglehartWind2025RCP4.5 | Englehart | Wind | RCP4.5 | 2025 | 73.0668 | 78.6707 | 84.553 | 90.4447 | 96.3425
| EnglehartWind2030RCP4.5 | Englehart | Wind | RCP4.5 | 2030 | 73.1297 | 78.7371 | 84.6272 | 90.5241 | 96.4271
| EnglehartWind2035RCP4.5 | Englehart | Wind | RCP4.5 | 2035 | 73.1926 | 78.8036 | 84.7014 | 90.6035 | 96.5117
| EnglehartWind2040RCP4.5 | Englehart | Wind | RCP4.5 | 2040 | 73.2554 | 78.87 | 84.7756 | 90.6829 | 96.5963
| EnglehartWind2045RCP4.5 | Englehart | Wind | RCP4.5 | 2045 | 73.3183 | 78.9364 | 84.8498 | 90.7623 | 96.6809
| EnglehartWind2050RCP4.5 | Englehart | Wind | RCP4.5 | 2050 | 73.4 | 79.0168 | 84.929 | 90.8417 | 96.7578
| EnglehartWind2055RCP4.5 | Englehart | Wind | RCP4.5 | 2055 | 73.4189 | 79.0309 | 84.9341 | 90.8417 | 96.7502
| EnglehartWind2060RCP4.5 | Englehart | Wind | RCP4.5 | 2060 | 73.4377 | 79.0449 | 84.9391 | 90.8417 | 96.7425
| EnglehartWind2065RCP4.5 | Englehart | Wind | RCP4.5 | 2065 | 73.4566 | 79.059 | 84.9442 | 90.8417 | 96.7348
| EnglehartWind2070RCP4.5 | Englehart | Wind | RCP4.5 | 2070 | 73.4754 | 79.0731 | 84.9492 | 90.8417 | 96.7272
| EnglehartWind2075RCP4.5 | Englehart | Wind | RCP4.5 | 2075 | 73.5165 | 79.1225 | 85.008 | 90.9091 | 96.8038
| EnglehartWind2080RCP4.5 | Englehart | Wind | RCP4.5 | 2080 | 73.5577 | 79.172 | 85.0668 | 90.9765 | 96.8804
| EnglehartWind2085RCP4.5 | Englehart | Wind | RCP4.5 | 2085 | 73.5988 | 79.2215 | 85.1256 | 91.0439 | 96.957
| EnglehartWind2090RCP4.5 | Englehart | Wind | RCP4.5 | 2090 | 73.6399 | 79.271 | 85.1844 | 91.1114 | 97.0336
| EnglehartWind2095RCP4.5 | Englehart | Wind | RCP4.5 | 2095 | 73.681 | 79.3204 | 85.2432 | 91.1788 | 97.1102
| EnglehartWind2100RCP4.5 | Englehart | Wind | RCP4.5 | 2100 | 73.7221 | 79.3699 | 85.302 | 91.2462 | 97.1868
| EnglehartWind2023RCP6.0 | Englehart | Wind | RCP6.0 | 2023 | 73.004 | 78.6043 | 84.4788 | 90.3654 | 96.258
| EnglehartWind2025RCP6.0 | Englehart | Wind | RCP6.0 | 2025 | 73.0668 | 78.6707 | 84.553 | 90.4447 | 96.3425
| EnglehartWind2030RCP6.0 | Englehart | Wind | RCP6.0 | 2030 | 73.1297 | 78.7371 | 84.6272 | 90.5241 | 96.4271
| EnglehartWind2035RCP6.0 | Englehart | Wind | RCP6.0 | 2035 | 73.1926 | 78.8036 | 84.7014 | 90.6035 | 96.5117
| EnglehartWind2040RCP6.0 | Englehart | Wind | RCP6.0 | 2040 | 73.2554 | 78.87 | 84.7756 | 90.6829 | 96.5963
| EnglehartWind2045RCP6.0 | Englehart | Wind | RCP6.0 | 2045 | 73.3183 | 78.9364 | 84.8498 | 90.7623 | 96.6809
| EnglehartWind2050RCP6.0 | Englehart | Wind | RCP6.0 | 2050 | 73.4 | 79.0168 | 84.929 | 90.8417 | 96.7578
| EnglehartWind2055RCP6.0 | Englehart | Wind | RCP6.0 | 2055 | 73.4189 | 79.0309 | 84.9341 | 90.8417 | 96.7502
| EnglehartWind2060RCP6.0 | Englehart | Wind | RCP6.0 | 2060 | 73.4377 | 79.0449 | 84.9391 | 90.8417 | 96.7425
| EnglehartWind2065RCP6.0 | Englehart | Wind | RCP6.0 | 2065 | 73.4566 | 79.059 | 84.9442 | 90.8417 | 96.7348
| EnglehartWind2070RCP6.0 | Englehart | Wind | RCP6.0 | 2070 | 73.4754 | 79.0731 | 84.9492 | 90.8417 | 96.7272
| EnglehartWind2075RCP6.0 | Englehart | Wind | RCP6.0 | 2075 | 73.5371 | 79.1473 | 85.0374 | 90.9428 | 96.8421
| EnglehartWind2080RCP6.0 | Englehart | Wind | RCP6.0 | 2080 | 73.5988 | 79.2215 | 85.1256 | 91.0439 | 96.957
| EnglehartWind2085RCP6.0 | Englehart | Wind | RCP6.0 | 2085 | 73.6604 | 79.2957 | 85.2138 | 91.1451 | 97.0719
| EnglehartWind2090RCP6.0 | Englehart | Wind | RCP6.0 | 2090 | 73.7632 | 79.409 | 85.3412 | 91.2851 | 97.2283
| EnglehartWind2095RCP6.0 | Englehart | Wind | RCP6.0 | 2095 | 73.8043 | 79.448 | 85.3804 | 91.3241 | 97.2698
| EnglehartWind2100RCP6.0 | Englehart | Wind | RCP6.0 | 2100 | 73.8454 | 79.4871 | 85.4196 | 91.363 | 97.3113
| EnglehartWind2023RCP8.5 | Englehart | Wind | RCP8.5 | 2023 | 73.004 | 78.6043 | 84.4788 | 90.3654 | 96.258
| EnglehartWind2025RCP8.5 | Englehart | Wind | RCP8.5 | 2025 | 73.1297 | 78.7371 | 84.6272 | 90.5241 | 96.4271
| EnglehartWind2030RCP8.5 | Englehart | Wind | RCP8.5 | 2030 | 73.2554 | 78.87 | 84.7756 | 90.6829 | 96.5963
| EnglehartWind2035RCP8.5 | Englehart | Wind | RCP8.5 | 2035 | 73.3812 | 79.0028 | 84.924 | 90.8417 | 96.7655
| EnglehartWind2040RCP8.5 | Englehart | Wind | RCP8.5 | 2040 | 73.4126 | 79.0262 | 84.9324 | 90.8417 | 96.7527
| EnglehartWind2045RCP8.5 | Englehart | Wind | RCP8.5 | 2045 | 73.444 | 79.0496 | 84.9408 | 90.8417 | 96.7399
| EnglehartWind2050RCP8.5 | Englehart | Wind | RCP8.5 | 2050 | 73.5577 | 79.172 | 85.0668 | 90.9765 | 96.8804
| EnglehartWind2055RCP8.5 | Englehart | Wind | RCP8.5 | 2055 | 73.6399 | 79.271 | 85.1844 | 91.1114 | 97.0336
| EnglehartWind2060RCP8.5 | Englehart | Wind | RCP8.5 | 2060 | 73.7632 | 79.409 | 85.3412 | 91.2851 | 97.2283
| EnglehartWind2065RCP8.5 | Englehart | Wind | RCP8.5 | 2065 | 73.8043 | 79.448 | 85.3804 | 91.3241 | 97.2698
| EnglehartWind2070RCP8.5 | Englehart | Wind | RCP8.5 | 2070 | 73.959 | 79.6017 | 85.5344 | 91.4799 | 97.4262
| EnglehartWind2075RCP8.5 | Englehart | Wind | RCP8.5 | 2075 | 74.0726 | 79.7163 | 85.6492 | 91.5967 | 97.5411
| EnglehartWind2080RCP8.5 | Englehart | Wind | RCP8.5 | 2080 | 74.1863 | 79.8308 | 85.764 | 91.7136 | 97.656
| EnglehartWind2085RCP8.5 | Englehart | Wind | RCP8.5 | 2085 | 74.1863 | 79.8425 | 85.7892 | 91.7495 | 97.7039
| EnglehartWind2090RCP8.5 | Englehart | Wind | RCP8.5 | 2090 | 74.1863 | 79.8543 | 85.8144 | 91.7855 | 97.7518
| EnglehartWind2095RCP8.5 | Englehart | Wind | RCP8.5 | 2095 | 74.1863 | 79.8543 | 85.8144 | 91.7855 | 97.7518
| EnglehartWind2100RCP8.5 | Englehart | Wind | RCP8.5 | 2100 | 74.1863 | 79.8543 | 85.8144 | 91.7855 | 97.7518
| EspanolaIce Accretion2023RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2023 | 15.7066 | 18.8261 | 22.792 | 25.8295 | 28.8288
| EspanolaIce Accretion2025RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2025 | 15.6888 | 18.8169 | 22.792 | 25.8337 | 28.8427
| EspanolaIce Accretion2030RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2030 | 15.6709 | 18.8078 | 22.792 | 25.8378 | 28.8565
| EspanolaIce Accretion2035RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2035 | 15.6531 | 18.7987 | 22.792 | 25.842 | 28.8704
| EspanolaIce Accretion2040RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2040 | 15.6352 | 18.7895 | 22.792 | 25.8461 | 28.8842
| EspanolaIce Accretion2045RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2045 | 15.6173 | 18.7804 | 22.792 | 25.8503 | 28.8981
| EspanolaIce Accretion2050RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2050 | 15.6607 | 18.8626 | 22.924 | 26.0185 | 29.106
| EspanolaIce Accretion2055RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2055 | 15.7219 | 18.9539 | 23.056 | 26.1826 | 29.3
| EspanolaIce Accretion2060RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2060 | 15.7832 | 19.0452 | 23.188 | 26.3466 | 29.4941
| EspanolaIce Accretion2065RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2065 | 15.8444 | 19.1365 | 23.32 | 26.5107 | 29.6881
| EspanolaIce Accretion2070RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2070 | 15.9057 | 19.2278 | 23.452 | 26.6748 | 29.8822
| EspanolaIce Accretion2075RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2075 | 15.7781 | 19.0847 | 23.287 | 26.4925 | 29.6835
| EspanolaIce Accretion2080RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2080 | 15.6505 | 18.9417 | 23.122 | 26.3102 | 29.4848
| EspanolaIce Accretion2085RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2085 | 15.5229 | 18.7987 | 22.957 | 26.1279 | 29.2862
| EspanolaIce Accretion2090RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2090 | 15.3954 | 18.6556 | 22.792 | 25.9456 | 29.0875
| EspanolaIce Accretion2095RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2095 | 15.2678 | 18.5126 | 22.627 | 25.7632 | 28.8889
| EspanolaIce Accretion2100RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2100 | 15.1402 | 18.3696 | 22.462 | 25.5809 | 28.6902
| EspanolaIce Accretion2023RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2023 | 15.7066 | 18.8261 | 22.792 | 25.8295 | 28.8288
| EspanolaIce Accretion2025RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2025 | 15.6888 | 18.8169 | 22.792 | 25.8337 | 28.8427
| EspanolaIce Accretion2030RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2030 | 15.6709 | 18.8078 | 22.792 | 25.8378 | 28.8565
| EspanolaIce Accretion2035RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2035 | 15.6531 | 18.7987 | 22.792 | 25.842 | 28.8704
| EspanolaIce Accretion2040RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2040 | 15.6352 | 18.7895 | 22.792 | 25.8461 | 28.8842
| EspanolaIce Accretion2045RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2045 | 15.6173 | 18.7804 | 22.792 | 25.8503 | 28.8981
| EspanolaIce Accretion2050RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2050 | 15.6607 | 18.8626 | 22.924 | 26.0185 | 29.106
| EspanolaIce Accretion2055RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2055 | 15.7219 | 18.9539 | 23.056 | 26.1826 | 29.3
| EspanolaIce Accretion2060RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2060 | 15.7832 | 19.0452 | 23.188 | 26.3466 | 29.4941
| EspanolaIce Accretion2065RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2065 | 15.8444 | 19.1365 | 23.32 | 26.5107 | 29.6881
| EspanolaIce Accretion2070RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2070 | 15.9057 | 19.2278 | 23.452 | 26.6748 | 29.8822
| EspanolaIce Accretion2075RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2075 | 15.7143 | 19.0132 | 23.2045 | 26.4013 | 29.5842
| EspanolaIce Accretion2080RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2080 | 15.5229 | 18.7987 | 22.957 | 26.1279 | 29.2862
| EspanolaIce Accretion2085RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2085 | 15.3316 | 18.5841 | 22.7095 | 25.8544 | 28.9882
| EspanolaIce Accretion2090RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2090 | 15.1351 | 18.3939 | 22.5207 | 25.6638 | 28.7918
| EspanolaIce Accretion2095RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2095 | 15.13 | 18.4183 | 22.5793 | 25.7467 | 28.8935
| EspanolaIce Accretion2100RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2100 | 15.1249 | 18.4426 | 22.638 | 25.8295 | 28.9951
| EspanolaIce Accretion2023RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2023 | 15.7066 | 18.8261 | 22.792 | 25.8295 | 28.8288
| EspanolaIce Accretion2025RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2025 | 15.6709 | 18.8078 | 22.792 | 25.8378 | 28.8565
| EspanolaIce Accretion2030RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2030 | 15.6352 | 18.7895 | 22.792 | 25.8461 | 28.8842
| EspanolaIce Accretion2035RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2035 | 15.5995 | 18.7713 | 22.792 | 25.8544 | 28.912
| EspanolaIce Accretion2040RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2040 | 15.7015 | 18.9234 | 23.012 | 26.1279 | 29.2354
| EspanolaIce Accretion2045RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2045 | 15.8036 | 19.0756 | 23.232 | 26.4013 | 29.5588
| EspanolaIce Accretion2050RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2050 | 15.6505 | 18.9417 | 23.122 | 26.3102 | 29.4848
| EspanolaIce Accretion2055RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2055 | 15.3954 | 18.6556 | 22.792 | 25.9456 | 29.0875
| EspanolaIce Accretion2060RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2060 | 15.1351 | 18.3939 | 22.5207 | 25.6638 | 28.7918
| EspanolaIce Accretion2065RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2065 | 15.13 | 18.4183 | 22.5793 | 25.7467 | 28.8935
| EspanolaIce Accretion2070RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2070 | 14.6248 | 17.8583 | 21.9487 | 25.0589 | 28.145
| EspanolaIce Accretion2075RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2075 | 14.1247 | 17.274 | 21.2593 | 24.2882 | 27.295
| EspanolaIce Accretion2080RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2080 | 13.6247 | 16.6896 | 20.57 | 23.5176 | 26.4449
| EspanolaIce Accretion2085RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2085 | 13.3185 | 16.361 | 20.207 | 23.1198 | 26.0291
| EspanolaIce Accretion2090RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2090 | 13.0123 | 16.0323 | 19.844 | 22.722 | 25.6133
| EspanolaIce Accretion2095RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2095 | 13.0123 | 16.0323 | 19.844 | 22.722 | 25.6133
| EspanolaIce Accretion2100RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2100 | 13.0123 | 16.0323 | 19.844 | 22.722 | 25.6133
| EspanolaWind2023RCP4.5 | Espanola | Wind | RCP4.5 | 2023 | 81.9141 | 88.233 | 94.893 | 101.5456 | 108.1887
| EspanolaWind2025RCP4.5 | Espanola | Wind | RCP4.5 | 2025 | 82.0237 | 88.3612 | 95.0418 | 101.7149 | 108.3781
| EspanolaWind2030RCP4.5 | Espanola | Wind | RCP4.5 | 2030 | 82.1332 | 88.4894 | 95.1907 | 101.8842 | 108.5674
| EspanolaWind2035RCP4.5 | Espanola | Wind | RCP4.5 | 2035 | 82.2428 | 88.6177 | 95.3395 | 102.0535 | 108.7567
| EspanolaWind2040RCP4.5 | Espanola | Wind | RCP4.5 | 2040 | 82.3524 | 88.7459 | 95.4883 | 102.2228 | 108.946
| EspanolaWind2045RCP4.5 | Espanola | Wind | RCP4.5 | 2045 | 82.462 | 88.8741 | 95.6372 | 102.3921 | 109.1353
| EspanolaWind2050RCP4.5 | Espanola | Wind | RCP4.5 | 2050 | 82.6771 | 89.1264 | 95.9326 | 102.7264 | 109.5111
| EspanolaWind2055RCP4.5 | Espanola | Wind | RCP4.5 | 2055 | 82.7826 | 89.2506 | 96.0793 | 102.8913 | 109.6975
| EspanolaWind2060RCP4.5 | Espanola | Wind | RCP4.5 | 2060 | 82.8881 | 89.3747 | 96.2259 | 103.0563 | 109.884
| EspanolaWind2065RCP4.5 | Espanola | Wind | RCP4.5 | 2065 | 82.9936 | 89.4988 | 96.3726 | 103.2212 | 110.0705
| EspanolaWind2070RCP4.5 | Espanola | Wind | RCP4.5 | 2070 | 83.0991 | 89.623 | 96.5192 | 103.3862 | 110.2569
| EspanolaWind2075RCP4.5 | Espanola | Wind | RCP4.5 | 2075 | 83.1465 | 89.6827 | 96.5944 | 103.475 | 110.3587
| EspanolaWind2080RCP4.5 | Espanola | Wind | RCP4.5 | 2080 | 83.1938 | 89.7425 | 96.6696 | 103.5639 | 110.4605
| EspanolaWind2085RCP4.5 | Espanola | Wind | RCP4.5 | 2085 | 83.2412 | 89.8022 | 96.7448 | 103.6527 | 110.5623
| EspanolaWind2090RCP4.5 | Espanola | Wind | RCP4.5 | 2090 | 83.2885 | 89.8619 | 96.82 | 103.7416 | 110.6641
| EspanolaWind2095RCP4.5 | Espanola | Wind | RCP4.5 | 2095 | 83.3359 | 89.9217 | 96.8952 | 103.8304 | 110.7659
| EspanolaWind2100RCP4.5 | Espanola | Wind | RCP4.5 | 2100 | 83.3832 | 89.9814 | 96.9704 | 103.9193 | 110.8677
| EspanolaWind2023RCP6.0 | Espanola | Wind | RCP6.0 | 2023 | 81.9141 | 88.233 | 94.893 | 101.5456 | 108.1887
| EspanolaWind2025RCP6.0 | Espanola | Wind | RCP6.0 | 2025 | 82.0237 | 88.3612 | 95.0418 | 101.7149 | 108.3781
| EspanolaWind2030RCP6.0 | Espanola | Wind | RCP6.0 | 2030 | 82.1332 | 88.4894 | 95.1907 | 101.8842 | 108.5674
| EspanolaWind2035RCP6.0 | Espanola | Wind | RCP6.0 | 2035 | 82.2428 | 88.6177 | 95.3395 | 102.0535 | 108.7567
| EspanolaWind2040RCP6.0 | Espanola | Wind | RCP6.0 | 2040 | 82.3524 | 88.7459 | 95.4883 | 102.2228 | 108.946
| EspanolaWind2045RCP6.0 | Espanola | Wind | RCP6.0 | 2045 | 82.462 | 88.8741 | 95.6372 | 102.3921 | 109.1353
| EspanolaWind2050RCP6.0 | Espanola | Wind | RCP6.0 | 2050 | 82.6771 | 89.1264 | 95.9326 | 102.7264 | 109.5111
| EspanolaWind2055RCP6.0 | Espanola | Wind | RCP6.0 | 2055 | 82.7826 | 89.2506 | 96.0793 | 102.8913 | 109.6975
| EspanolaWind2060RCP6.0 | Espanola | Wind | RCP6.0 | 2060 | 82.8881 | 89.3747 | 96.2259 | 103.0563 | 109.884
| EspanolaWind2065RCP6.0 | Espanola | Wind | RCP6.0 | 2065 | 82.9936 | 89.4988 | 96.3726 | 103.2212 | 110.0705
| EspanolaWind2070RCP6.0 | Espanola | Wind | RCP6.0 | 2070 | 83.0991 | 89.623 | 96.5192 | 103.3862 | 110.2569
| EspanolaWind2075RCP6.0 | Espanola | Wind | RCP6.0 | 2075 | 83.1702 | 89.7126 | 96.632 | 103.5195 | 110.4096
| EspanolaWind2080RCP6.0 | Espanola | Wind | RCP6.0 | 2080 | 83.2412 | 89.8022 | 96.7448 | 103.6527 | 110.5623
| EspanolaWind2085RCP6.0 | Espanola | Wind | RCP6.0 | 2085 | 83.3122 | 89.8918 | 96.8576 | 103.786 | 110.715
| EspanolaWind2090RCP6.0 | Espanola | Wind | RCP6.0 | 2090 | 83.6673 | 90.3398 | 97.4247 | 104.4523 | 111.4821
| EspanolaWind2095RCP6.0 | Espanola | Wind | RCP6.0 | 2095 | 83.9514 | 90.6983 | 97.8791 | 104.9854 | 112.0965
| EspanolaWind2100RCP6.0 | Espanola | Wind | RCP6.0 | 2100 | 84.2355 | 91.0567 | 98.3334 | 105.5185 | 112.7109
| EspanolaWind2023RCP8.5 | Espanola | Wind | RCP8.5 | 2023 | 81.9141 | 88.233 | 94.893 | 101.5456 | 108.1887
| EspanolaWind2025RCP8.5 | Espanola | Wind | RCP8.5 | 2025 | 82.1332 | 88.4894 | 95.1907 | 101.8842 | 108.5674
| EspanolaWind2030RCP8.5 | Espanola | Wind | RCP8.5 | 2030 | 82.3524 | 88.7459 | 95.4883 | 102.2228 | 108.946
| EspanolaWind2035RCP8.5 | Espanola | Wind | RCP8.5 | 2035 | 82.5715 | 89.0023 | 95.786 | 102.5614 | 109.3246
| EspanolaWind2040RCP8.5 | Espanola | Wind | RCP8.5 | 2040 | 82.7474 | 89.2092 | 96.0304 | 102.8363 | 109.6354
| EspanolaWind2045RCP8.5 | Espanola | Wind | RCP8.5 | 2045 | 82.9233 | 89.4161 | 96.2748 | 103.1113 | 109.9462
| EspanolaWind2050RCP8.5 | Espanola | Wind | RCP8.5 | 2050 | 83.1938 | 89.7425 | 96.6696 | 103.5639 | 110.4605
| EspanolaWind2055RCP8.5 | Espanola | Wind | RCP8.5 | 2055 | 83.2885 | 89.8619 | 96.82 | 103.7416 | 110.6641
| EspanolaWind2060RCP8.5 | Espanola | Wind | RCP8.5 | 2060 | 83.6673 | 90.3398 | 97.4247 | 104.4523 | 111.4821
| EspanolaWind2065RCP8.5 | Espanola | Wind | RCP8.5 | 2065 | 83.9514 | 90.6983 | 97.8791 | 104.9854 | 112.0965
| EspanolaWind2070RCP8.5 | Espanola | Wind | RCP8.5 | 2070 | 84.4817 | 91.351 | 98.6843 | 105.9208 | 113.1645
| EspanolaWind2075RCP8.5 | Espanola | Wind | RCP8.5 | 2075 | 84.7279 | 91.6453 | 99.0353 | 106.3231 | 113.6182
| EspanolaWind2080RCP8.5 | Espanola | Wind | RCP8.5 | 2080 | 84.9741 | 91.9396 | 99.3862 | 106.7254 | 114.0718
| EspanolaWind2085RCP8.5 | Espanola | Wind | RCP8.5 | 2085 | 85.3353 | 92.3942 | 99.9549 | 107.3893 | 114.8327
| EspanolaWind2090RCP8.5 | Espanola | Wind | RCP8.5 | 2090 | 85.6965 | 92.8488 | 100.5236 | 108.0531 | 115.5935
| EspanolaWind2095RCP8.5 | Espanola | Wind | RCP8.5 | 2095 | 85.6965 | 92.8488 | 100.5236 | 108.0531 | 115.5935
| EspanolaWind2100RCP8.5 | Espanola | Wind | RCP8.5 | 2100 | 85.6965 | 92.8488 | 100.5236 | 108.0531 | 115.5935
| EtobicokeIce Accretion2023RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
| EtobicokeIce Accretion2025RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2025 | 17.4222 | 20.9229 | 25.3542 | 28.7444 | 32.1247
| EtobicokeIce Accretion2030RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2030 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
| EtobicokeIce Accretion2035RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2035 | 17.5092 | 21.0612 | 25.5625 | 28.9986 | 32.4292
| EtobicokeIce Accretion2040RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2040 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
| EtobicokeIce Accretion2045RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2045 | 17.5962 | 21.1996 | 25.7708 | 29.2529 | 32.7338
| EtobicokeIce Accretion2050RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2050 | 17.5214 | 21.1484 | 25.745 | 29.2444 | 32.7411
| EtobicokeIce Accretion2055RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2055 | 17.4031 | 21.0281 | 25.615 | 29.1088 | 32.5962
| EtobicokeIce Accretion2060RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2060 | 17.2848 | 20.9077 | 25.485 | 28.9732 | 32.4513
| EtobicokeIce Accretion2065RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2065 | 17.1665 | 20.7873 | 25.355 | 28.8376 | 32.3064
| EtobicokeIce Accretion2070RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2070 | 17.0482 | 20.667 | 25.225 | 28.702 | 32.1615
| EtobicokeIce Accretion2075RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2075 | 17.0105 | 20.6497 | 25.2333 | 28.7255 | 32.2035
| EtobicokeIce Accretion2080RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2080 | 16.9728 | 20.6324 | 25.2417 | 28.7491 | 32.2455
| EtobicokeIce Accretion2085RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2085 | 16.9352 | 20.6151 | 25.25 | 28.7726 | 32.2875
| EtobicokeIce Accretion2090RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2090 | 16.8975 | 20.5978 | 25.2583 | 28.7962 | 32.3295
| EtobicokeIce Accretion2095RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2095 | 16.8598 | 20.5805 | 25.2667 | 28.8197 | 32.3715
| EtobicokeIce Accretion2100RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2100 | 16.8221 | 20.5633 | 25.275 | 28.8432 | 32.4135
| EtobicokeIce Accretion2023RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
| EtobicokeIce Accretion2025RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2025 | 17.4222 | 20.9229 | 25.3542 | 28.7444 | 32.1247
| EtobicokeIce Accretion2030RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2030 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
| EtobicokeIce Accretion2035RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2035 | 17.5092 | 21.0612 | 25.5625 | 28.9986 | 32.4292
| EtobicokeIce Accretion2040RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2040 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
| EtobicokeIce Accretion2045RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2045 | 17.5962 | 21.1996 | 25.7708 | 29.2529 | 32.7338
| EtobicokeIce Accretion2050RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2050 | 17.5214 | 21.1484 | 25.745 | 29.2444 | 32.7411
| EtobicokeIce Accretion2055RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2055 | 17.4031 | 21.0281 | 25.615 | 29.1088 | 32.5962
| EtobicokeIce Accretion2060RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2060 | 17.2848 | 20.9077 | 25.485 | 28.9732 | 32.4513
| EtobicokeIce Accretion2065RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2065 | 17.1665 | 20.7873 | 25.355 | 28.8376 | 32.3064
| EtobicokeIce Accretion2070RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2070 | 17.0482 | 20.667 | 25.225 | 28.702 | 32.1615
| EtobicokeIce Accretion2075RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2075 | 16.9917 | 20.6411 | 25.2375 | 28.7373 | 32.2245
| EtobicokeIce Accretion2080RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2080 | 16.9352 | 20.6151 | 25.25 | 28.7726 | 32.2875
| EtobicokeIce Accretion2085RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2085 | 16.8786 | 20.5892 | 25.2625 | 28.8079 | 32.3505
| EtobicokeIce Accretion2090RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2090 | 16.5147 | 20.2382 | 24.925 | 28.4854 | 32.0355
| EtobicokeIce Accretion2095RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2095 | 16.2074 | 19.9131 | 24.575 | 28.1276 | 31.6575
| EtobicokeIce Accretion2100RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2100 | 15.9001 | 19.588 | 24.225 | 27.7697 | 31.2795
| EtobicokeIce Accretion2023RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
| EtobicokeIce Accretion2025RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2025 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
| EtobicokeIce Accretion2030RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2030 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
| EtobicokeIce Accretion2035RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2035 | 17.6397 | 21.2687 | 25.875 | 29.38 | 32.886
| EtobicokeIce Accretion2040RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2040 | 17.4425 | 21.0682 | 25.6583 | 29.154 | 32.6445
| EtobicokeIce Accretion2045RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2045 | 17.2454 | 20.8676 | 25.4417 | 28.928 | 32.403
| EtobicokeIce Accretion2050RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2050 | 16.9728 | 20.6324 | 25.2417 | 28.7491 | 32.2455
| EtobicokeIce Accretion2055RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2055 | 16.8975 | 20.5978 | 25.2583 | 28.7962 | 32.3295
| EtobicokeIce Accretion2060RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2060 | 16.5147 | 20.2382 | 24.925 | 28.4854 | 32.0355
| EtobicokeIce Accretion2065RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2065 | 16.2074 | 19.9131 | 24.575 | 28.1276 | 31.6575
| EtobicokeIce Accretion2070RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2070 | 15.5116 | 19.173 | 23.775 | 27.2801 | 30.765
| EtobicokeIce Accretion2075RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2075 | 15.1231 | 18.758 | 23.325 | 26.7904 | 30.2505
| EtobicokeIce Accretion2080RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2080 | 14.7345 | 18.343 | 22.875 | 26.3007 | 29.736
| EtobicokeIce Accretion2085RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2085 | 13.9691 | 17.4404 | 21.8 | 25.1001 | 28.3972
| EtobicokeIce Accretion2090RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2090 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
| EtobicokeIce Accretion2095RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2095 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
| EtobicokeIce Accretion2100RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2100 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
| EtobicokeWind2023RCP4.5 | Etobicoke | Wind | RCP4.5 | 2023 | 84.9344 | 91.4772 | 98.3626 | 105.248 | 112.1334
| EtobicokeWind2025RCP4.5 | Etobicoke | Wind | RCP4.5 | 2025 | 84.9612 | 91.5152 | 98.4149 | 105.3126 | 112.2116
| EtobicokeWind2030RCP4.5 | Etobicoke | Wind | RCP4.5 | 2030 | 84.988 | 91.5532 | 98.4671 | 105.3773 | 112.2898
| EtobicokeWind2035RCP4.5 | Etobicoke | Wind | RCP4.5 | 2035 | 85.0148 | 91.5911 | 98.5194 | 105.442 | 112.368
| EtobicokeWind2040RCP4.5 | Etobicoke | Wind | RCP4.5 | 2040 | 85.0416 | 91.6291 | 98.5717 | 105.5066 | 112.4462
| EtobicokeWind2045RCP4.5 | Etobicoke | Wind | RCP4.5 | 2045 | 85.0684 | 91.6671 | 98.6239 | 105.5713 | 112.5244
| EtobicokeWind2050RCP4.5 | Etobicoke | Wind | RCP4.5 | 2050 | 85.151 | 91.7579 | 98.7252 | 105.6821 | 112.645
| EtobicokeWind2055RCP4.5 | Etobicoke | Wind | RCP4.5 | 2055 | 85.2069 | 91.8108 | 98.7742 | 105.7282 | 112.6875
| EtobicokeWind2060RCP4.5 | Etobicoke | Wind | RCP4.5 | 2060 | 85.2627 | 91.8637 | 98.8232 | 105.7744 | 112.7299
| EtobicokeWind2065RCP4.5 | Etobicoke | Wind | RCP4.5 | 2065 | 85.3186 | 91.9165 | 98.8722 | 105.8205 | 112.7724
| EtobicokeWind2070RCP4.5 | Etobicoke | Wind | RCP4.5 | 2070 | 85.3744 | 91.9694 | 98.9212 | 105.8667 | 112.8149
| EtobicokeWind2075RCP4.5 | Etobicoke | Wind | RCP4.5 | 2075 | 85.4562 | 92.0818 | 99.0715 | 106.0484 | 113.029
| EtobicokeWind2080RCP4.5 | Etobicoke | Wind | RCP4.5 | 2080 | 85.538 | 92.1942 | 99.2217 | 106.2302 | 113.2431
| EtobicokeWind2085RCP4.5 | Etobicoke | Wind | RCP4.5 | 2085 | 85.6198 | 92.3066 | 99.372 | 106.4119 | 113.4572
| EtobicokeWind2090RCP4.5 | Etobicoke | Wind | RCP4.5 | 2090 | 85.7016 | 92.419 | 99.5223 | 106.5937 | 113.6714
| EtobicokeWind2095RCP4.5 | Etobicoke | Wind | RCP4.5 | 2095 | 85.7834 | 92.5314 | 99.6725 | 106.7754 | 113.8855
| EtobicokeWind2100RCP4.5 | Etobicoke | Wind | RCP4.5 | 2100 | 85.8652 | 92.6438 | 99.8228 | 106.9572 | 114.0996
| EtobicokeWind2023RCP6.0 | Etobicoke | Wind | RCP6.0 | 2023 | 84.9344 | 91.4772 | 98.3626 | 105.248 | 112.1334
| EtobicokeWind2025RCP6.0 | Etobicoke | Wind | RCP6.0 | 2025 | 84.9612 | 91.5152 | 98.4149 | 105.3126 | 112.2116
| EtobicokeWind2030RCP6.0 | Etobicoke | Wind | RCP6.0 | 2030 | 84.988 | 91.5532 | 98.4671 | 105.3773 | 112.2898
| EtobicokeWind2035RCP6.0 | Etobicoke | Wind | RCP6.0 | 2035 | 85.0148 | 91.5911 | 98.5194 | 105.442 | 112.368
| EtobicokeWind2040RCP6.0 | Etobicoke | Wind | RCP6.0 | 2040 | 85.0416 | 91.6291 | 98.5717 | 105.5066 | 112.4462
| EtobicokeWind2045RCP6.0 | Etobicoke | Wind | RCP6.0 | 2045 | 85.0684 | 91.6671 | 98.6239 | 105.5713 | 112.5244
| EtobicokeWind2050RCP6.0 | Etobicoke | Wind | RCP6.0 | 2050 | 85.151 | 91.7579 | 98.7252 | 105.6821 | 112.645
| EtobicokeWind2055RCP6.0 | Etobicoke | Wind | RCP6.0 | 2055 | 85.2069 | 91.8108 | 98.7742 | 105.7282 | 112.6875
| EtobicokeWind2060RCP6.0 | Etobicoke | Wind | RCP6.0 | 2060 | 85.2627 | 91.8637 | 98.8232 | 105.7744 | 112.7299
| EtobicokeWind2065RCP6.0 | Etobicoke | Wind | RCP6.0 | 2065 | 85.3186 | 91.9165 | 98.8722 | 105.8205 | 112.7724
| EtobicokeWind2070RCP6.0 | Etobicoke | Wind | RCP6.0 | 2070 | 85.3744 | 91.9694 | 98.9212 | 105.8667 | 112.8149
| EtobicokeWind2075RCP6.0 | Etobicoke | Wind | RCP6.0 | 2075 | 85.4971 | 92.138 | 99.1466 | 106.1393 | 113.1361
| EtobicokeWind2080RCP6.0 | Etobicoke | Wind | RCP6.0 | 2080 | 85.6198 | 92.3066 | 99.372 | 106.4119 | 113.4572
| EtobicokeWind2085RCP6.0 | Etobicoke | Wind | RCP6.0 | 2085 | 85.7425 | 92.4752 | 99.5974 | 106.6846 | 113.7784
| EtobicokeWind2090RCP6.0 | Etobicoke | Wind | RCP6.0 | 2090 | 86.1501 | 92.9962 | 100.2573 | 107.464 | 114.6806
| EtobicokeWind2095RCP6.0 | Etobicoke | Wind | RCP6.0 | 2095 | 86.435 | 93.3486 | 100.6917 | 107.9708 | 115.2615
| EtobicokeWind2100RCP6.0 | Etobicoke | Wind | RCP6.0 | 2100 | 86.7199 | 93.701 | 101.1262 | 108.4777 | 115.8425
| EtobicokeWind2023RCP8.5 | Etobicoke | Wind | RCP8.5 | 2023 | 84.9344 | 91.4772 | 98.3626 | 105.248 | 112.1334
| EtobicokeWind2025RCP8.5 | Etobicoke | Wind | RCP8.5 | 2025 | 84.988 | 91.5532 | 98.4671 | 105.3773 | 112.2898
| EtobicokeWind2030RCP8.5 | Etobicoke | Wind | RCP8.5 | 2030 | 85.0416 | 91.6291 | 98.5717 | 105.5066 | 112.4462
| EtobicokeWind2035RCP8.5 | Etobicoke | Wind | RCP8.5 | 2035 | 85.0952 | 91.7051 | 98.6762 | 105.636 | 112.6026
| EtobicokeWind2040RCP8.5 | Etobicoke | Wind | RCP8.5 | 2040 | 85.1882 | 91.7932 | 98.7579 | 105.7129 | 112.6733
| EtobicokeWind2045RCP8.5 | Etobicoke | Wind | RCP8.5 | 2045 | 85.2813 | 91.8813 | 98.8395 | 105.7898 | 112.7441
| EtobicokeWind2050RCP8.5 | Etobicoke | Wind | RCP8.5 | 2050 | 85.538 | 92.1942 | 99.2217 | 106.2302 | 113.2431
| EtobicokeWind2055RCP8.5 | Etobicoke | Wind | RCP8.5 | 2055 | 85.7016 | 92.419 | 99.5223 | 106.5937 | 113.6714
| EtobicokeWind2060RCP8.5 | Etobicoke | Wind | RCP8.5 | 2060 | 86.1501 | 92.9962 | 100.2573 | 107.464 | 114.6806
| EtobicokeWind2065RCP8.5 | Etobicoke | Wind | RCP8.5 | 2065 | 86.435 | 93.3486 | 100.6917 | 107.9708 | 115.2615
| EtobicokeWind2070RCP8.5 | Etobicoke | Wind | RCP8.5 | 2070 | 86.9371 | 93.9927 | 101.5117 | 108.9425 | 116.3862
| EtobicokeWind2075RCP8.5 | Etobicoke | Wind | RCP8.5 | 2075 | 87.1543 | 94.2843 | 101.8971 | 109.4074 | 116.9299
| EtobicokeWind2080RCP8.5 | Etobicoke | Wind | RCP8.5 | 2080 | 87.3715 | 94.576 | 102.2826 | 109.8723 | 117.4736
| EtobicokeWind2085RCP8.5 | Etobicoke | Wind | RCP8.5 | 2085 | 87.4815 | 94.7218 | 102.4786 | 110.103 | 117.7473
| EtobicokeWind2090RCP8.5 | Etobicoke | Wind | RCP8.5 | 2090 | 87.5915 | 94.8676 | 102.6746 | 110.3337 | 118.021
| EtobicokeWind2095RCP8.5 | Etobicoke | Wind | RCP8.5 | 2095 | 87.5915 | 94.8676 | 102.6746 | 110.3337 | 118.021
| EtobicokeWind2100RCP8.5 | Etobicoke | Wind | RCP8.5 | 2100 | 87.5915 | 94.8676 | 102.6746 | 110.3337 | 118.021
| ExeterIce Accretion2023RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2023 | 15.0637 | 18.0591 | 21.824 | 24.7108 | 27.5814
| ExeterIce Accretion2025RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2025 | 15.079 | 18.0896 | 21.879 | 24.7813 | 27.6692
| ExeterIce Accretion2030RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2030 | 15.0943 | 18.12 | 21.934 | 24.8517 | 27.757
| ExeterIce Accretion2035RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2035 | 15.1096 | 18.1504 | 21.989 | 24.9221 | 27.8447
| ExeterIce Accretion2040RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2040 | 15.1249 | 18.1809 | 22.044 | 24.9926 | 27.9325
| ExeterIce Accretion2045RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2045 | 15.1402 | 18.2113 | 22.099 | 25.063 | 28.0203
| ExeterIce Accretion2050RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2050 | 15.0943 | 18.1979 | 22.1276 | 25.1185 | 28.1081
| ExeterIce Accretion2055RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2055 | 15.0331 | 18.1541 | 22.1012 | 25.1036 | 28.1081
| ExeterIce Accretion2060RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2060 | 14.9718 | 18.1103 | 22.0748 | 25.0887 | 28.1081
| ExeterIce Accretion2065RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2065 | 14.9106 | 18.0664 | 22.0484 | 25.0738 | 28.1081
| ExeterIce Accretion2070RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2070 | 14.8494 | 18.0226 | 22.022 | 25.0589 | 28.1081
| ExeterIce Accretion2075RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2075 | 14.8213 | 18.0104 | 22.033 | 25.0837 | 28.1497
| ExeterIce Accretion2080RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2080 | 14.7932 | 17.9983 | 22.044 | 25.1086 | 28.1912
| ExeterIce Accretion2085RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2085 | 14.7652 | 17.9861 | 22.055 | 25.1335 | 28.2328
| ExeterIce Accretion2090RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2090 | 14.7371 | 17.9739 | 22.066 | 25.1583 | 28.2744
| ExeterIce Accretion2095RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2095 | 14.709 | 17.9618 | 22.077 | 25.1832 | 28.316
| ExeterIce Accretion2100RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2100 | 14.681 | 17.9496 | 22.088 | 25.208 | 28.3576
| ExeterIce Accretion2023RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2023 | 15.0637 | 18.0591 | 21.824 | 24.7108 | 27.5814
| ExeterIce Accretion2025RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2025 | 15.079 | 18.0896 | 21.879 | 24.7813 | 27.6692
| ExeterIce Accretion2030RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2030 | 15.0943 | 18.12 | 21.934 | 24.8517 | 27.757
| ExeterIce Accretion2035RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2035 | 15.1096 | 18.1504 | 21.989 | 24.9221 | 27.8447
| ExeterIce Accretion2040RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2040 | 15.1249 | 18.1809 | 22.044 | 24.9926 | 27.9325
| ExeterIce Accretion2045RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2045 | 15.1402 | 18.2113 | 22.099 | 25.063 | 28.0203
| ExeterIce Accretion2050RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2050 | 15.0943 | 18.1979 | 22.1276 | 25.1185 | 28.1081
| ExeterIce Accretion2055RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2055 | 15.0331 | 18.1541 | 22.1012 | 25.1036 | 28.1081
| ExeterIce Accretion2060RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2060 | 14.9718 | 18.1103 | 22.0748 | 25.0887 | 28.1081
| ExeterIce Accretion2065RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2065 | 14.9106 | 18.0664 | 22.0484 | 25.0738 | 28.1081
| ExeterIce Accretion2070RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2070 | 14.8494 | 18.0226 | 22.022 | 25.0589 | 28.1081
| ExeterIce Accretion2075RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2075 | 14.8073 | 18.0044 | 22.0385 | 25.0962 | 28.1704
| ExeterIce Accretion2080RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2080 | 14.7652 | 17.9861 | 22.055 | 25.1335 | 28.2328
| ExeterIce Accretion2085RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2085 | 14.7231 | 17.9678 | 22.0715 | 25.1707 | 28.2952
| ExeterIce Accretion2090RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2090 | 14.4973 | 17.767 | 21.8973 | 25.0174 | 28.1543
| ExeterIce Accretion2095RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2095 | 14.3136 | 17.5844 | 21.7067 | 24.8269 | 27.951
| ExeterIce Accretion2100RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2100 | 14.1299 | 17.4018 | 21.516 | 24.6363 | 27.7477
| ExeterIce Accretion2023RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2023 | 15.0637 | 18.0591 | 21.824 | 24.7108 | 27.5814
| ExeterIce Accretion2025RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2025 | 15.0943 | 18.12 | 21.934 | 24.8517 | 27.757
| ExeterIce Accretion2030RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2030 | 15.1249 | 18.1809 | 22.044 | 24.9926 | 27.9325
| ExeterIce Accretion2035RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2035 | 15.1555 | 18.2417 | 22.154 | 25.1335 | 28.1081
| ExeterIce Accretion2040RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2040 | 15.0535 | 18.1687 | 22.11 | 25.1086 | 28.1081
| ExeterIce Accretion2045RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2045 | 14.9514 | 18.0957 | 22.066 | 25.0837 | 28.1081
| ExeterIce Accretion2050RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2050 | 14.7932 | 17.9983 | 22.044 | 25.1086 | 28.1912
| ExeterIce Accretion2055RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2055 | 14.7371 | 17.9739 | 22.066 | 25.1583 | 28.2744
| ExeterIce Accretion2060RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2060 | 14.4973 | 17.767 | 21.8973 | 25.0174 | 28.1543
| ExeterIce Accretion2065RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2065 | 14.3136 | 17.5844 | 21.7067 | 24.8269 | 27.951
| ExeterIce Accretion2070RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2070 | 13.7982 | 17.0305 | 21.098 | 24.1805 | 27.2488
| ExeterIce Accretion2075RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2075 | 13.4665 | 16.6592 | 20.68 | 23.7247 | 26.7498
| ExeterIce Accretion2080RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2080 | 13.1348 | 16.2879 | 20.262 | 23.269 | 26.2508
| ExeterIce Accretion2085RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2085 | 12.4459 | 15.4753 | 19.294 | 22.1875 | 25.0589
| ExeterIce Accretion2090RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2090 | 11.757 | 14.6628 | 18.326 | 21.1061 | 23.8669
| ExeterIce Accretion2095RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2095 | 11.757 | 14.6628 | 18.326 | 21.1061 | 23.8669
| ExeterIce Accretion2100RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2100 | 11.757 | 14.6628 | 18.326 | 21.1061 | 23.8669
| ExeterWind2023RCP4.5 | Exeter | Wind | RCP4.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| ExeterWind2025RCP4.5 | Exeter | Wind | RCP4.5 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
| ExeterWind2030RCP4.5 | Exeter | Wind | RCP4.5 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| ExeterWind2035RCP4.5 | Exeter | Wind | RCP4.5 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
| ExeterWind2040RCP4.5 | Exeter | Wind | RCP4.5 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| ExeterWind2045RCP4.5 | Exeter | Wind | RCP4.5 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
| ExeterWind2050RCP4.5 | Exeter | Wind | RCP4.5 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
| ExeterWind2055RCP4.5 | Exeter | Wind | RCP4.5 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
| ExeterWind2060RCP4.5 | Exeter | Wind | RCP4.5 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
| ExeterWind2065RCP4.5 | Exeter | Wind | RCP4.5 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
| ExeterWind2070RCP4.5 | Exeter | Wind | RCP4.5 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
| ExeterWind2075RCP4.5 | Exeter | Wind | RCP4.5 | 2075 | 86.3504 | 93.3577 | 100.8387 | 108.226 | 115.6228
| ExeterWind2080RCP4.5 | Exeter | Wind | RCP4.5 | 2080 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
| ExeterWind2085RCP4.5 | Exeter | Wind | RCP4.5 | 2085 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
| ExeterWind2090RCP4.5 | Exeter | Wind | RCP4.5 | 2090 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
| ExeterWind2095RCP4.5 | Exeter | Wind | RCP4.5 | 2095 | 86.7678 | 93.9167 | 101.5705 | 109.1068 | 116.6655
| ExeterWind2100RCP4.5 | Exeter | Wind | RCP4.5 | 2100 | 86.8722 | 94.0565 | 101.7534 | 109.327 | 116.9262
| ExeterWind2023RCP6.0 | Exeter | Wind | RCP6.0 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| ExeterWind2025RCP6.0 | Exeter | Wind | RCP6.0 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
| ExeterWind2030RCP6.0 | Exeter | Wind | RCP6.0 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| ExeterWind2035RCP6.0 | Exeter | Wind | RCP6.0 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
| ExeterWind2040RCP6.0 | Exeter | Wind | RCP6.0 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| ExeterWind2045RCP6.0 | Exeter | Wind | RCP6.0 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
| ExeterWind2050RCP6.0 | Exeter | Wind | RCP6.0 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
| ExeterWind2055RCP6.0 | Exeter | Wind | RCP6.0 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
| ExeterWind2060RCP6.0 | Exeter | Wind | RCP6.0 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
| ExeterWind2065RCP6.0 | Exeter | Wind | RCP6.0 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
| ExeterWind2070RCP6.0 | Exeter | Wind | RCP6.0 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
| ExeterWind2075RCP6.0 | Exeter | Wind | RCP6.0 | 2075 | 86.4026 | 93.4276 | 100.9302 | 108.3361 | 115.7531
| ExeterWind2080RCP6.0 | Exeter | Wind | RCP6.0 | 2080 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
| ExeterWind2085RCP6.0 | Exeter | Wind | RCP6.0 | 2085 | 86.7157 | 93.8469 | 101.479 | 108.9967 | 116.5351
| ExeterWind2090RCP6.0 | Exeter | Wind | RCP6.0 | 2090 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
| ExeterWind2095RCP6.0 | Exeter | Wind | RCP6.0 | 2095 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
| ExeterWind2100RCP6.0 | Exeter | Wind | RCP6.0 | 2100 | 87.7861 | 95.1502 | 103.0568 | 110.8265 | 118.6131
| ExeterWind2023RCP8.5 | Exeter | Wind | RCP8.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| ExeterWind2025RCP8.5 | Exeter | Wind | RCP8.5 | 2025 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| ExeterWind2030RCP8.5 | Exeter | Wind | RCP8.5 | 2030 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| ExeterWind2035RCP8.5 | Exeter | Wind | RCP8.5 | 2035 | 86.0768 | 93.0084 | 100.3912 | 107.7017 | 115.0269
| ExeterWind2040RCP8.5 | Exeter | Wind | RCP8.5 | 2040 | 86.1332 | 93.0782 | 100.4794 | 107.8031 | 115.1386
| ExeterWind2045RCP8.5 | Exeter | Wind | RCP8.5 | 2045 | 86.1896 | 93.1481 | 100.5676 | 107.9044 | 115.2504
| ExeterWind2050RCP8.5 | Exeter | Wind | RCP8.5 | 2050 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
| ExeterWind2055RCP8.5 | Exeter | Wind | RCP8.5 | 2055 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
| ExeterWind2060RCP8.5 | Exeter | Wind | RCP8.5 | 2060 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
| ExeterWind2065RCP8.5 | Exeter | Wind | RCP8.5 | 2065 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
| ExeterWind2070RCP8.5 | Exeter | Wind | RCP8.5 | 2070 | 88.0541 | 95.5026 | 103.5207 | 111.3788 | 119.2611
| ExeterWind2075RCP8.5 | Exeter | Wind | RCP8.5 | 2075 | 88.322 | 95.855 | 103.9845 | 111.9311 | 119.9091
| ExeterWind2080RCP8.5 | Exeter | Wind | RCP8.5 | 2080 | 88.59 | 96.2074 | 104.4484 | 112.4833 | 120.5571
| ExeterWind2085RCP8.5 | Exeter | Wind | RCP8.5 | 2085 | 88.9454 | 96.6585 | 105.0217 | 113.1649 | 121.3447
| ExeterWind2090RCP8.5 | Exeter | Wind | RCP8.5 | 2090 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| ExeterWind2095RCP8.5 | Exeter | Wind | RCP8.5 | 2095 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| ExeterWind2100RCP8.5 | Exeter | Wind | RCP8.5 | 2100 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| Fenelon FallsIce Accretion2023RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2023 | 17.2396 | 20.584 | 24.825 | 28.0522 | 31.311
| Fenelon FallsIce Accretion2025RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2025 | 17.2251 | 20.5771 | 24.825 | 28.057 | 31.3215
| Fenelon FallsIce Accretion2030RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2030 | 17.2106 | 20.5702 | 24.825 | 28.0617 | 31.332
| Fenelon FallsIce Accretion2035RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2035 | 17.1961 | 20.5633 | 24.825 | 28.0664 | 31.3425
| Fenelon FallsIce Accretion2040RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2040 | 17.1816 | 20.5563 | 24.825 | 28.0711 | 31.353
| Fenelon FallsIce Accretion2045RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2045 | 17.1671 | 20.5494 | 24.825 | 28.0758 | 31.3635
| Fenelon FallsIce Accretion2050RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2050 | 17.1109 | 20.5134 | 24.81 | 28.0748 | 31.374
| Fenelon FallsIce Accretion2055RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2055 | 17.0691 | 20.4844 | 24.795 | 28.0692 | 31.374
| Fenelon FallsIce Accretion2060RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2060 | 17.0274 | 20.4553 | 24.78 | 28.0635 | 31.374
| Fenelon FallsIce Accretion2065RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2065 | 16.9856 | 20.4263 | 24.765 | 28.0579 | 31.374
| Fenelon FallsIce Accretion2070RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2070 | 16.9439 | 20.3972 | 24.75 | 28.0522 | 31.374
| Fenelon FallsIce Accretion2075RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2075 | 17.0134 | 20.4975 | 24.8875 | 28.2217 | 31.5735
| Fenelon FallsIce Accretion2080RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2080 | 17.083 | 20.5978 | 25.025 | 28.3912 | 31.773
| Fenelon FallsIce Accretion2085RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2085 | 17.1526 | 20.6981 | 25.1625 | 28.5607 | 31.9725
| Fenelon FallsIce Accretion2090RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2090 | 17.2222 | 20.7984 | 25.3 | 28.7302 | 32.172
| Fenelon FallsIce Accretion2095RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2095 | 17.2918 | 20.8987 | 25.4375 | 28.8997 | 32.3715
| Fenelon FallsIce Accretion2100RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2100 | 17.3614 | 20.999 | 25.575 | 29.0692 | 32.571
| Fenelon FallsIce Accretion2023RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2023 | 17.2396 | 20.584 | 24.825 | 28.0522 | 31.311
| Fenelon FallsIce Accretion2025RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2025 | 17.2251 | 20.5771 | 24.825 | 28.057 | 31.3215
| Fenelon FallsIce Accretion2030RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2030 | 17.2106 | 20.5702 | 24.825 | 28.0617 | 31.332
| Fenelon FallsIce Accretion2035RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2035 | 17.1961 | 20.5633 | 24.825 | 28.0664 | 31.3425
| Fenelon FallsIce Accretion2040RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2040 | 17.1816 | 20.5563 | 24.825 | 28.0711 | 31.353
| Fenelon FallsIce Accretion2045RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2045 | 17.1671 | 20.5494 | 24.825 | 28.0758 | 31.3635
| Fenelon FallsIce Accretion2050RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2050 | 17.1109 | 20.5134 | 24.81 | 28.0748 | 31.374
| Fenelon FallsIce Accretion2055RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2055 | 17.0691 | 20.4844 | 24.795 | 28.0692 | 31.374
| Fenelon FallsIce Accretion2060RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2060 | 17.0274 | 20.4553 | 24.78 | 28.0635 | 31.374
| Fenelon FallsIce Accretion2065RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2065 | 16.9856 | 20.4263 | 24.765 | 28.0579 | 31.374
| Fenelon FallsIce Accretion2070RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2070 | 16.9439 | 20.3972 | 24.75 | 28.0522 | 31.374
| Fenelon FallsIce Accretion2075RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2075 | 17.0482 | 20.5477 | 24.9563 | 28.3065 | 31.6732
| Fenelon FallsIce Accretion2080RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2080 | 17.1526 | 20.6981 | 25.1625 | 28.5607 | 31.9725
| Fenelon FallsIce Accretion2085RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2085 | 17.257 | 20.8486 | 25.3687 | 28.815 | 32.2717
| Fenelon FallsIce Accretion2090RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2090 | 17.2512 | 20.916 | 25.5333 | 29.0504 | 32.5815
| Fenelon FallsIce Accretion2095RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2095 | 17.141 | 20.833 | 25.4917 | 29.0316 | 32.592
| Fenelon FallsIce Accretion2100RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2100 | 17.0308 | 20.75 | 25.45 | 29.0127 | 32.6025
| Fenelon FallsIce Accretion2023RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2023 | 17.2396 | 20.584 | 24.825 | 28.0522 | 31.311
| Fenelon FallsIce Accretion2025RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2025 | 17.2106 | 20.5702 | 24.825 | 28.0617 | 31.332
| Fenelon FallsIce Accretion2030RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2030 | 17.1816 | 20.5563 | 24.825 | 28.0711 | 31.353
| Fenelon FallsIce Accretion2035RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2035 | 17.1526 | 20.5425 | 24.825 | 28.0805 | 31.374
| Fenelon FallsIce Accretion2040RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2040 | 17.083 | 20.4941 | 24.8 | 28.0711 | 31.374
| Fenelon FallsIce Accretion2045RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2045 | 17.0134 | 20.4457 | 24.775 | 28.0617 | 31.374
| Fenelon FallsIce Accretion2050RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2050 | 17.083 | 20.5978 | 25.025 | 28.3912 | 31.773
| Fenelon FallsIce Accretion2055RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2055 | 17.2222 | 20.7984 | 25.3 | 28.7302 | 32.172
| Fenelon FallsIce Accretion2060RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2060 | 17.2512 | 20.916 | 25.5333 | 29.0504 | 32.5815
| Fenelon FallsIce Accretion2065RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2065 | 17.141 | 20.833 | 25.4917 | 29.0316 | 32.592
| Fenelon FallsIce Accretion2070RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2070 | 16.8105 | 20.5218 | 25.2167 | 28.7773 | 32.3505
| Fenelon FallsIce Accretion2075RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2075 | 16.5901 | 20.2935 | 24.9833 | 28.5419 | 32.0985
| Fenelon FallsIce Accretion2080RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2080 | 16.3698 | 20.0652 | 24.75 | 28.3065 | 31.8465
| Fenelon FallsIce Accretion2085RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2085 | 15.6826 | 19.2871 | 23.85 | 27.3177 | 30.7597
| Fenelon FallsIce Accretion2090RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2090 | 14.9955 | 18.509 | 22.95 | 26.329 | 29.673
| Fenelon FallsIce Accretion2095RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2095 | 14.9955 | 18.509 | 22.95 | 26.329 | 29.673
| Fenelon FallsIce Accretion2100RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2100 | 14.9955 | 18.509 | 22.95 | 26.329 | 29.673
| Fenelon FallsWind2023RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2023 | 72.7936 | 78.37 | 84.2352 | 90.1047 | 95.9707
| Fenelon FallsWind2025RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2025 | 72.8492 | 78.4351 | 84.3122 | 90.1916 | 96.068
| Fenelon FallsWind2030RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2030 | 72.9049 | 78.5002 | 84.3892 | 90.2785 | 96.1654
| Fenelon FallsWind2035RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2035 | 72.9605 | 78.5653 | 84.4662 | 90.3654 | 96.2627
| Fenelon FallsWind2040RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2040 | 73.0161 | 78.6304 | 84.5432 | 90.4522 | 96.3601
| Fenelon FallsWind2045RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2045 | 73.0717 | 78.6955 | 84.6202 | 90.5391 | 96.4575
| Fenelon FallsWind2050RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2050 | 73.2013 | 78.8434 | 84.7879 | 90.7249 | 96.6621
| Fenelon FallsWind2055RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2055 | 73.2753 | 78.9262 | 84.8786 | 90.8237 | 96.7693
| Fenelon FallsWind2060RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2060 | 73.3492 | 79.009 | 84.9694 | 90.9226 | 96.8766
| Fenelon FallsWind2065RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2065 | 73.4232 | 79.0918 | 85.0601 | 91.0215 | 96.9838
| Fenelon FallsWind2070RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2070 | 73.4972 | 79.1746 | 85.1508 | 91.1203 | 97.0911
| Fenelon FallsWind2075RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2075 | 73.4742 | 79.1512 | 85.1256 | 91.0949 | 97.0655
| Fenelon FallsWind2080RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2080 | 73.4513 | 79.1277 | 85.1004 | 91.0694 | 97.04
| Fenelon FallsWind2085RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2085 | 73.4283 | 79.1043 | 85.0752 | 91.0439 | 97.0145
| Fenelon FallsWind2090RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2090 | 73.4053 | 79.0809 | 85.05 | 91.0185 | 96.9889
| Fenelon FallsWind2095RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2095 | 73.3824 | 79.0574 | 85.0248 | 90.993 | 96.9634
| Fenelon FallsWind2100RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2100 | 73.3594 | 79.034 | 84.9996 | 90.9675 | 96.9378
| Fenelon FallsWind2023RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2023 | 72.7936 | 78.37 | 84.2352 | 90.1047 | 95.9707
| Fenelon FallsWind2025RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2025 | 72.8492 | 78.4351 | 84.3122 | 90.1916 | 96.068
| Fenelon FallsWind2030RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2030 | 72.9049 | 78.5002 | 84.3892 | 90.2785 | 96.1654
| Fenelon FallsWind2035RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2035 | 72.9605 | 78.5653 | 84.4662 | 90.3654 | 96.2627
| Fenelon FallsWind2040RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2040 | 73.0161 | 78.6304 | 84.5432 | 90.4522 | 96.3601
| Fenelon FallsWind2045RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2045 | 73.0717 | 78.6955 | 84.6202 | 90.5391 | 96.4575
| Fenelon FallsWind2050RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2050 | 73.2013 | 78.8434 | 84.7879 | 90.7249 | 96.6621
| Fenelon FallsWind2055RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2055 | 73.2753 | 78.9262 | 84.8786 | 90.8237 | 96.7693
| Fenelon FallsWind2060RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2060 | 73.3492 | 79.009 | 84.9694 | 90.9226 | 96.8766
| Fenelon FallsWind2065RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2065 | 73.4232 | 79.0918 | 85.0601 | 91.0215 | 96.9838
| Fenelon FallsWind2070RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2070 | 73.4972 | 79.1746 | 85.1508 | 91.1203 | 97.0911
| Fenelon FallsWind2075RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2075 | 73.4628 | 79.1395 | 85.113 | 91.0821 | 97.0528
| Fenelon FallsWind2080RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2080 | 73.4283 | 79.1043 | 85.0752 | 91.0439 | 97.0145
| Fenelon FallsWind2085RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2085 | 73.3938 | 79.0692 | 85.0374 | 91.0057 | 96.9762
| Fenelon FallsWind2090RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2090 | 73.4126 | 79.0939 | 85.0696 | 91.0454 | 97.024
| Fenelon FallsWind2095RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2095 | 73.4658 | 79.1538 | 85.1396 | 91.1233 | 97.1102
| Fenelon FallsWind2100RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2100 | 73.519 | 79.2137 | 85.2096 | 91.2012 | 97.1964
| Fenelon FallsWind2023RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2023 | 72.7936 | 78.37 | 84.2352 | 90.1047 | 95.9707
| Fenelon FallsWind2025RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2025 | 72.9049 | 78.5002 | 84.3892 | 90.2785 | 96.1654
| Fenelon FallsWind2030RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2030 | 73.0161 | 78.6304 | 84.5432 | 90.4522 | 96.3601
| Fenelon FallsWind2035RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2035 | 73.1273 | 78.7606 | 84.6972 | 90.626 | 96.5548
| Fenelon FallsWind2040RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2040 | 73.2506 | 78.8986 | 84.8484 | 90.7908 | 96.7336
| Fenelon FallsWind2045RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2045 | 73.3739 | 79.0366 | 84.9996 | 90.9556 | 96.9123
| Fenelon FallsWind2050RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2050 | 73.4513 | 79.1277 | 85.1004 | 91.0694 | 97.04
| Fenelon FallsWind2055RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2055 | 73.4053 | 79.0809 | 85.05 | 91.0185 | 96.9889
| Fenelon FallsWind2060RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2060 | 73.4126 | 79.0939 | 85.0696 | 91.0454 | 97.024
| Fenelon FallsWind2065RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2065 | 73.4658 | 79.1538 | 85.1396 | 91.1233 | 97.1102
| Fenelon FallsWind2070RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2070 | 73.5359 | 79.2267 | 85.2208 | 91.2102 | 97.2028
| Fenelon FallsWind2075RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2075 | 73.5528 | 79.2397 | 85.232 | 91.2192 | 97.2092
| Fenelon FallsWind2080RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2080 | 73.5697 | 79.2527 | 85.2432 | 91.2282 | 97.2156
| Fenelon FallsWind2085RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2085 | 73.6749 | 79.3699 | 85.3692 | 91.363 | 97.3592
| Fenelon FallsWind2090RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2090 | 73.7801 | 79.4871 | 85.4952 | 91.4978 | 97.5028
| Fenelon FallsWind2095RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2095 | 73.7801 | 79.4871 | 85.4952 | 91.4978 | 97.5028
| Fenelon FallsWind2100RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2100 | 73.7801 | 79.4871 | 85.4952 | 91.4978 | 97.5028
| FergusIce Accretion2023RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2023 | 16.6001 | 19.92 | 24.12 | 27.337 | 30.5424
| FergusIce Accretion2025RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2025 | 16.6279 | 19.9665 | 24.188 | 27.4228 | 30.6432
| FergusIce Accretion2030RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2030 | 16.6558 | 20.013 | 24.256 | 27.5087 | 30.744
| FergusIce Accretion2035RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2035 | 16.6836 | 20.0594 | 24.324 | 27.5946 | 30.8448
| FergusIce Accretion2040RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2040 | 16.7114 | 20.1059 | 24.392 | 27.6805 | 30.9456
| FergusIce Accretion2045RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2045 | 16.7393 | 20.1524 | 24.46 | 27.7664 | 31.0464
| FergusIce Accretion2050RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2050 | 16.7137 | 20.1511 | 24.4896 | 27.8197 | 31.123
| FergusIce Accretion2055RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2055 | 16.6602 | 20.1033 | 24.4512 | 27.7872 | 31.0988
| FergusIce Accretion2060RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2060 | 16.6068 | 20.0555 | 24.4128 | 27.7546 | 31.0746
| FergusIce Accretion2065RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2065 | 16.5533 | 20.0076 | 24.3744 | 27.7221 | 31.0504
| FergusIce Accretion2070RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2070 | 16.4999 | 19.9598 | 24.336 | 27.6895 | 31.0262
| FergusIce Accretion2075RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2075 | 16.4693 | 19.9532 | 24.356 | 27.7257 | 31.0817
| FergusIce Accretion2080RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2080 | 16.4387 | 19.9466 | 24.376 | 27.7618 | 31.1371
| FergusIce Accretion2085RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2085 | 16.4081 | 19.9399 | 24.396 | 27.798 | 31.1926
| FergusIce Accretion2090RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2090 | 16.3774 | 19.9333 | 24.416 | 27.8342 | 31.248
| FergusIce Accretion2095RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2095 | 16.3468 | 19.9266 | 24.436 | 27.8703 | 31.3034
| FergusIce Accretion2100RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2100 | 16.3162 | 19.92 | 24.456 | 27.9065 | 31.3589
| FergusIce Accretion2023RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2023 | 16.6001 | 19.92 | 24.12 | 27.337 | 30.5424
| FergusIce Accretion2025RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2025 | 16.6279 | 19.9665 | 24.188 | 27.4228 | 30.6432
| FergusIce Accretion2030RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2030 | 16.6558 | 20.013 | 24.256 | 27.5087 | 30.744
| FergusIce Accretion2035RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2035 | 16.6836 | 20.0594 | 24.324 | 27.5946 | 30.8448
| FergusIce Accretion2040RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2040 | 16.7114 | 20.1059 | 24.392 | 27.6805 | 30.9456
| FergusIce Accretion2045RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2045 | 16.7393 | 20.1524 | 24.46 | 27.7664 | 31.0464
| FergusIce Accretion2050RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2050 | 16.7137 | 20.1511 | 24.4896 | 27.8197 | 31.123
| FergusIce Accretion2055RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2055 | 16.6602 | 20.1033 | 24.4512 | 27.7872 | 31.0988
| FergusIce Accretion2060RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2060 | 16.6068 | 20.0555 | 24.4128 | 27.7546 | 31.0746
| FergusIce Accretion2065RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2065 | 16.5533 | 20.0076 | 24.3744 | 27.7221 | 31.0504
| FergusIce Accretion2070RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2070 | 16.4999 | 19.9598 | 24.336 | 27.6895 | 31.0262
| FergusIce Accretion2075RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2075 | 16.454 | 19.9499 | 24.366 | 27.7438 | 31.1094
| FergusIce Accretion2080RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2080 | 16.4081 | 19.9399 | 24.396 | 27.798 | 31.1926
| FergusIce Accretion2085RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2085 | 16.3621 | 19.93 | 24.426 | 27.8522 | 31.2757
| FergusIce Accretion2090RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2090 | 16.0212 | 19.6079 | 24.128 | 27.563 | 31.0061
| FergusIce Accretion2095RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2095 | 15.7261 | 19.2958 | 23.8 | 27.2194 | 30.6533
| FergusIce Accretion2100RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2100 | 15.4311 | 18.9838 | 23.472 | 26.8759 | 30.3005
| FergusIce Accretion2023RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2023 | 16.6001 | 19.92 | 24.12 | 27.337 | 30.5424
| FergusIce Accretion2025RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2025 | 16.6558 | 20.013 | 24.256 | 27.5087 | 30.744
| FergusIce Accretion2030RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2030 | 16.7114 | 20.1059 | 24.392 | 27.6805 | 30.9456
| FergusIce Accretion2035RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2035 | 16.7671 | 20.1989 | 24.528 | 27.8522 | 31.1472
| FergusIce Accretion2040RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2040 | 16.678 | 20.1192 | 24.464 | 27.798 | 31.1069
| FergusIce Accretion2045RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2045 | 16.589 | 20.0395 | 24.4 | 27.7438 | 31.0666
| FergusIce Accretion2050RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2050 | 16.4387 | 19.9466 | 24.376 | 27.7618 | 31.1371
| FergusIce Accretion2055RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2055 | 16.3774 | 19.9333 | 24.416 | 27.8342 | 31.248
| FergusIce Accretion2060RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2060 | 16.0212 | 19.6079 | 24.128 | 27.563 | 31.0061
| FergusIce Accretion2065RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2065 | 15.7261 | 19.2958 | 23.8 | 27.2194 | 30.6533
| FergusIce Accretion2070RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2070 | 15.0247 | 18.5455 | 22.992 | 26.3697 | 29.7461
| FergusIce Accretion2075RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2075 | 14.6183 | 18.1073 | 22.512 | 25.8634 | 29.1917
| FergusIce Accretion2080RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2080 | 14.212 | 17.669 | 22.032 | 25.3572 | 28.6373
| FergusIce Accretion2085RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2085 | 13.4187 | 16.7328 | 20.916 | 24.0826 | 27.2311
| FergusIce Accretion2090RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2090 | 12.6254 | 15.7966 | 19.8 | 22.8079 | 25.825
| FergusIce Accretion2095RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2095 | 12.6254 | 15.7966 | 19.8 | 22.8079 | 25.825
| FergusIce Accretion2100RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2100 | 12.6254 | 15.7966 | 19.8 | 22.8079 | 25.825
| FergusWind2023RCP4.5 | Fergus | Wind | RCP4.5 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
| FergusWind2025RCP4.5 | Fergus | Wind | RCP4.5 | 2025 | 81.5488 | 87.8469 | 94.481 | 101.1097 | 107.7494
| FergusWind2030RCP4.5 | Fergus | Wind | RCP4.5 | 2030 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
| FergusWind2035RCP4.5 | Fergus | Wind | RCP4.5 | 2035 | 81.6625 | 88.0013 | 94.6909 | 101.3645 | 108.0494
| FergusWind2040RCP4.5 | Fergus | Wind | RCP4.5 | 2040 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
| FergusWind2045RCP4.5 | Fergus | Wind | RCP4.5 | 2045 | 81.7761 | 88.1558 | 94.9008 | 101.6193 | 108.3495
| FergusWind2050RCP4.5 | Fergus | Wind | RCP4.5 | 2050 | 81.8962 | 88.3099 | 95.096 | 101.8513 | 108.6174
| FergusWind2055RCP4.5 | Fergus | Wind | RCP4.5 | 2055 | 81.9595 | 88.3869 | 95.1863 | 101.9559 | 108.7353
| FergusWind2060RCP4.5 | Fergus | Wind | RCP4.5 | 2060 | 82.0229 | 88.4638 | 95.2765 | 102.0605 | 108.8531
| FergusWind2065RCP4.5 | Fergus | Wind | RCP4.5 | 2065 | 82.0862 | 88.5407 | 95.3668 | 102.1651 | 108.971
| FergusWind2070RCP4.5 | Fergus | Wind | RCP4.5 | 2070 | 82.1495 | 88.6177 | 95.457 | 102.2697 | 109.0889
| FergusWind2075RCP4.5 | Fergus | Wind | RCP4.5 | 2075 | 82.2185 | 88.7167 | 95.598 | 102.4424 | 109.2961
| FergusWind2080RCP4.5 | Fergus | Wind | RCP4.5 | 2080 | 82.2875 | 88.8158 | 95.739 | 102.6151 | 109.5032
| FergusWind2085RCP4.5 | Fergus | Wind | RCP4.5 | 2085 | 82.3564 | 88.9149 | 95.88 | 102.7877 | 109.7104
| FergusWind2090RCP4.5 | Fergus | Wind | RCP4.5 | 2090 | 82.4254 | 89.014 | 96.021 | 102.9604 | 109.9176
| FergusWind2095RCP4.5 | Fergus | Wind | RCP4.5 | 2095 | 82.4944 | 89.113 | 96.162 | 103.1331 | 110.1248
| FergusWind2100RCP4.5 | Fergus | Wind | RCP4.5 | 2100 | 82.5634 | 89.2121 | 96.303 | 103.3057 | 110.3319
| FergusWind2023RCP6.0 | Fergus | Wind | RCP6.0 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
| FergusWind2025RCP6.0 | Fergus | Wind | RCP6.0 | 2025 | 81.5488 | 87.8469 | 94.481 | 101.1097 | 107.7494
| FergusWind2030RCP6.0 | Fergus | Wind | RCP6.0 | 2030 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
| FergusWind2035RCP6.0 | Fergus | Wind | RCP6.0 | 2035 | 81.6625 | 88.0013 | 94.6909 | 101.3645 | 108.0494
| FergusWind2040RCP6.0 | Fergus | Wind | RCP6.0 | 2040 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
| FergusWind2045RCP6.0 | Fergus | Wind | RCP6.0 | 2045 | 81.7761 | 88.1558 | 94.9008 | 101.6193 | 108.3495
| FergusWind2050RCP6.0 | Fergus | Wind | RCP6.0 | 2050 | 81.8962 | 88.3099 | 95.096 | 101.8513 | 108.6174
| FergusWind2055RCP6.0 | Fergus | Wind | RCP6.0 | 2055 | 81.9595 | 88.3869 | 95.1863 | 101.9559 | 108.7353
| FergusWind2060RCP6.0 | Fergus | Wind | RCP6.0 | 2060 | 82.0229 | 88.4638 | 95.2765 | 102.0605 | 108.8531
| FergusWind2065RCP6.0 | Fergus | Wind | RCP6.0 | 2065 | 82.0862 | 88.5407 | 95.3668 | 102.1651 | 108.971
| FergusWind2070RCP6.0 | Fergus | Wind | RCP6.0 | 2070 | 82.1495 | 88.6177 | 95.457 | 102.2697 | 109.0889
| FergusWind2075RCP6.0 | Fergus | Wind | RCP6.0 | 2075 | 82.253 | 88.7663 | 95.6685 | 102.5287 | 109.3996
| FergusWind2080RCP6.0 | Fergus | Wind | RCP6.0 | 2080 | 82.3564 | 88.9149 | 95.88 | 102.7877 | 109.7104
| FergusWind2085RCP6.0 | Fergus | Wind | RCP6.0 | 2085 | 82.4599 | 89.0635 | 96.0915 | 103.0467 | 110.0212
| FergusWind2090RCP6.0 | Fergus | Wind | RCP6.0 | 2090 | 82.8421 | 89.5618 | 96.7385 | 103.8187 | 110.9213
| FergusWind2095RCP6.0 | Fergus | Wind | RCP6.0 | 2095 | 83.1208 | 89.9115 | 97.1741 | 104.3316 | 111.5107
| FergusWind2100RCP6.0 | Fergus | Wind | RCP6.0 | 2100 | 83.3995 | 90.2612 | 97.6096 | 104.8446 | 112.1001
| FergusWind2023RCP8.5 | Fergus | Wind | RCP8.5 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
| FergusWind2025RCP8.5 | Fergus | Wind | RCP8.5 | 2025 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
| FergusWind2030RCP8.5 | Fergus | Wind | RCP8.5 | 2030 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
| FergusWind2035RCP8.5 | Fergus | Wind | RCP8.5 | 2035 | 81.8329 | 88.233 | 95.0058 | 101.7467 | 108.4995
| FergusWind2040RCP8.5 | Fergus | Wind | RCP8.5 | 2040 | 81.9384 | 88.3612 | 95.1562 | 101.9211 | 108.696
| FergusWind2045RCP8.5 | Fergus | Wind | RCP8.5 | 2045 | 82.044 | 88.4894 | 95.3066 | 102.0954 | 108.8924
| FergusWind2050RCP8.5 | Fergus | Wind | RCP8.5 | 2050 | 82.2875 | 88.8158 | 95.739 | 102.6151 | 109.5032
| FergusWind2055RCP8.5 | Fergus | Wind | RCP8.5 | 2055 | 82.4254 | 89.014 | 96.021 | 102.9604 | 109.9176
| FergusWind2060RCP8.5 | Fergus | Wind | RCP8.5 | 2060 | 82.8421 | 89.5618 | 96.7385 | 103.8187 | 110.9213
| FergusWind2065RCP8.5 | Fergus | Wind | RCP8.5 | 2065 | 83.1208 | 89.9115 | 97.1741 | 104.3316 | 111.5107
| FergusWind2070RCP8.5 | Fergus | Wind | RCP8.5 | 2070 | 83.6457 | 90.5933 | 98.0451 | 105.371 | 112.718
| FergusWind2075RCP8.5 | Fergus | Wind | RCP8.5 | 2075 | 83.8919 | 90.9255 | 98.4807 | 105.8973 | 113.336
| FergusWind2080RCP8.5 | Fergus | Wind | RCP8.5 | 2080 | 84.1381 | 91.2577 | 98.9162 | 106.4237 | 113.9539
| FergusWind2085RCP8.5 | Fergus | Wind | RCP8.5 | 2085 | 84.3775 | 91.5768 | 99.3392 | 106.9266 | 114.5433
| FergusWind2090RCP8.5 | Fergus | Wind | RCP8.5 | 2090 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
| FergusWind2095RCP8.5 | Fergus | Wind | RCP8.5 | 2095 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
| FergusWind2100RCP8.5 | Fergus | Wind | RCP8.5 | 2100 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
| ForestIce Accretion2023RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2023 | 14.7422 | 17.6939 | 21.428 | 24.2634 | 27.1102
| ForestIce Accretion2025RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2025 | 14.6835 | 17.6361 | 21.3693 | 24.2054 | 27.0501
| ForestIce Accretion2030RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2030 | 14.6248 | 17.5783 | 21.3107 | 24.1473 | 26.99
| ForestIce Accretion2035RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2035 | 14.5661 | 17.5205 | 21.252 | 24.0893 | 26.93
| ForestIce Accretion2040RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2040 | 14.5075 | 17.4626 | 21.1933 | 24.0313 | 26.8699
| ForestIce Accretion2045RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2045 | 14.4488 | 17.4048 | 21.1347 | 23.9733 | 26.8099
| ForestIce Accretion2050RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2050 | 14.1207 | 17.0475 | 20.7328 | 23.5424 | 26.3451
| ForestIce Accretion2055RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2055 | 13.8512 | 16.7481 | 20.3896 | 23.1695 | 25.9404
| ForestIce Accretion2060RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2060 | 13.5818 | 16.4486 | 20.0464 | 22.7966 | 25.5357
| ForestIce Accretion2065RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2065 | 13.3124 | 16.1491 | 19.7032 | 22.4237 | 25.131
| ForestIce Accretion2070RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2070 | 13.0429 | 15.8497 | 19.36 | 22.0508 | 24.7262
| ForestIce Accretion2075RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2075 | 12.9205 | 15.7219 | 19.228 | 21.9099 | 24.5784
| ForestIce Accretion2080RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2080 | 12.798 | 15.594 | 19.096 | 21.7691 | 24.4306
| ForestIce Accretion2085RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2085 | 12.6755 | 15.4662 | 18.964 | 21.6282 | 24.2827
| ForestIce Accretion2090RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2090 | 12.5531 | 15.3384 | 18.832 | 21.4873 | 24.1349
| ForestIce Accretion2095RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2095 | 12.4306 | 15.2106 | 18.7 | 21.3465 | 23.987
| ForestIce Accretion2100RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2100 | 12.3081 | 15.0828 | 18.568 | 21.2056 | 23.8392
| ForestIce Accretion2023RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2023 | 14.7422 | 17.6939 | 21.428 | 24.2634 | 27.1102
| ForestIce Accretion2025RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2025 | 14.6835 | 17.6361 | 21.3693 | 24.2054 | 27.0501
| ForestIce Accretion2030RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2030 | 14.6248 | 17.5783 | 21.3107 | 24.1473 | 26.99
| ForestIce Accretion2035RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2035 | 14.5661 | 17.5205 | 21.252 | 24.0893 | 26.93
| ForestIce Accretion2040RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2040 | 14.5075 | 17.4626 | 21.1933 | 24.0313 | 26.8699
| ForestIce Accretion2045RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2045 | 14.4488 | 17.4048 | 21.1347 | 23.9733 | 26.8099
| ForestIce Accretion2050RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2050 | 14.1207 | 17.0475 | 20.7328 | 23.5424 | 26.3451
| ForestIce Accretion2055RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2055 | 13.8512 | 16.7481 | 20.3896 | 23.1695 | 25.9404
| ForestIce Accretion2060RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2060 | 13.5818 | 16.4486 | 20.0464 | 22.7966 | 25.5357
| ForestIce Accretion2065RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2065 | 13.3124 | 16.1491 | 19.7032 | 22.4237 | 25.131
| ForestIce Accretion2070RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2070 | 13.0429 | 15.8497 | 19.36 | 22.0508 | 24.7262
| ForestIce Accretion2075RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2075 | 12.8592 | 15.6579 | 19.162 | 21.8395 | 24.5045
| ForestIce Accretion2080RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2080 | 12.6755 | 15.4662 | 18.964 | 21.6282 | 24.2827
| ForestIce Accretion2085RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2085 | 12.4918 | 15.2745 | 18.766 | 21.4169 | 24.061
| ForestIce Accretion2090RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2090 | 11.9356 | 14.6628 | 18.084 | 20.6669 | 23.2478
| ForestIce Accretion2095RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2095 | 11.5631 | 14.2428 | 17.6 | 20.1283 | 22.6565
| ForestIce Accretion2100RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2100 | 11.1906 | 13.8228 | 17.116 | 19.5897 | 22.0651
| ForestIce Accretion2023RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2023 | 14.7422 | 17.6939 | 21.428 | 24.2634 | 27.1102
| ForestIce Accretion2025RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2025 | 14.6248 | 17.5783 | 21.3107 | 24.1473 | 26.99
| ForestIce Accretion2030RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2030 | 14.5075 | 17.4626 | 21.1933 | 24.0313 | 26.8699
| ForestIce Accretion2035RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2035 | 14.3901 | 17.347 | 21.076 | 23.9153 | 26.7498
| ForestIce Accretion2040RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2040 | 13.941 | 16.8479 | 20.504 | 23.2938 | 26.0753
| ForestIce Accretion2045RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2045 | 13.492 | 16.3488 | 19.932 | 22.6723 | 25.4008
| ForestIce Accretion2050RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2050 | 12.798 | 15.594 | 19.096 | 21.7691 | 24.4306
| ForestIce Accretion2055RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2055 | 12.5531 | 15.3384 | 18.832 | 21.4873 | 24.1349
| ForestIce Accretion2060RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2060 | 11.9356 | 14.6628 | 18.084 | 20.6669 | 23.2478
| ForestIce Accretion2065RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2065 | 11.5631 | 14.2428 | 17.6 | 20.1283 | 22.6565
| ForestIce Accretion2070RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2070 | 10.8997 | 13.5063 | 16.7567 | 19.2085 | 21.6493
| ForestIce Accretion2075RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2075 | 10.6089 | 13.1898 | 16.3973 | 18.8273 | 21.2335
| ForestIce Accretion2080RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2080 | 10.318 | 12.8733 | 16.038 | 18.4461 | 20.8177
| ForestIce Accretion2085RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2085 | 9.6138 | 12.0333 | 15.037 | 17.3026 | 19.5565
| ForestIce Accretion2090RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2090 | 8.9096 | 11.1934 | 14.036 | 16.159 | 18.2952
| ForestIce Accretion2095RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2095 | 8.9096 | 11.1934 | 14.036 | 16.159 | 18.2952
| ForestIce Accretion2100RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2100 | 8.9096 | 11.1934 | 14.036 | 16.159 | 18.2952
| ForestWind2023RCP4.5 | Forest | Wind | RCP4.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
| ForestWind2025RCP4.5 | Forest | Wind | RCP4.5 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
| ForestWind2030RCP4.5 | Forest | Wind | RCP4.5 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
| ForestWind2035RCP4.5 | Forest | Wind | RCP4.5 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
| ForestWind2040RCP4.5 | Forest | Wind | RCP4.5 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
| ForestWind2045RCP4.5 | Forest | Wind | RCP4.5 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
| ForestWind2050RCP4.5 | Forest | Wind | RCP4.5 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
| ForestWind2055RCP4.5 | Forest | Wind | RCP4.5 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
| ForestWind2060RCP4.5 | Forest | Wind | RCP4.5 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
| ForestWind2065RCP4.5 | Forest | Wind | RCP4.5 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
| ForestWind2070RCP4.5 | Forest | Wind | RCP4.5 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
| ForestWind2075RCP4.5 | Forest | Wind | RCP4.5 | 2075 | 85.7411 | 92.542 | 99.746 | 106.9048 | 114.0736
| ForestWind2080RCP4.5 | Forest | Wind | RCP4.5 | 2080 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
| ForestWind2085RCP4.5 | Forest | Wind | RCP4.5 | 2085 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
| ForestWind2090RCP4.5 | Forest | Wind | RCP4.5 | 2090 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
| ForestWind2095RCP4.5 | Forest | Wind | RCP4.5 | 2095 | 86.3278 | 93.3015 | 100.7326 | 108.0792 | 115.444
| ForestWind2100RCP4.5 | Forest | Wind | RCP4.5 | 2100 | 86.4745 | 93.4914 | 100.9792 | 108.3728 | 115.7866
| ForestWind2023RCP6.0 | Forest | Wind | RCP6.0 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
| ForestWind2025RCP6.0 | Forest | Wind | RCP6.0 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
| ForestWind2030RCP6.0 | Forest | Wind | RCP6.0 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
| ForestWind2035RCP6.0 | Forest | Wind | RCP6.0 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
| ForestWind2040RCP6.0 | Forest | Wind | RCP6.0 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
| ForestWind2045RCP6.0 | Forest | Wind | RCP6.0 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
| ForestWind2050RCP6.0 | Forest | Wind | RCP6.0 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
| ForestWind2055RCP6.0 | Forest | Wind | RCP6.0 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
| ForestWind2060RCP6.0 | Forest | Wind | RCP6.0 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
| ForestWind2065RCP6.0 | Forest | Wind | RCP6.0 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
| ForestWind2070RCP6.0 | Forest | Wind | RCP6.0 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
| ForestWind2075RCP6.0 | Forest | Wind | RCP6.0 | 2075 | 85.8144 | 92.637 | 99.8693 | 107.0516 | 114.2449
| ForestWind2080RCP6.0 | Forest | Wind | RCP6.0 | 2080 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
| ForestWind2085RCP6.0 | Forest | Wind | RCP6.0 | 2085 | 86.2545 | 93.2066 | 100.6093 | 107.9324 | 115.2727
| ForestWind2090RCP6.0 | Forest | Wind | RCP6.0 | 2090 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
| ForestWind2095RCP6.0 | Forest | Wind | RCP6.0 | 2095 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
| ForestWind2100RCP6.0 | Forest | Wind | RCP6.0 | 2100 | 87.5746 | 94.8494 | 102.6452 | 110.3127 | 117.9987
| ForestWind2023RCP8.5 | Forest | Wind | RCP8.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
| ForestWind2025RCP8.5 | Forest | Wind | RCP8.5 | 2025 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
| ForestWind2030RCP8.5 | Forest | Wind | RCP8.5 | 2030 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
| ForestWind2035RCP8.5 | Forest | Wind | RCP8.5 | 2035 | 85.586 | 92.3248 | 99.4504 | 106.5378 | 113.6304
| ForestWind2040RCP8.5 | Forest | Wind | RCP8.5 | 2040 | 85.5888 | 92.3339 | 99.4667 | 106.5622 | 113.6639
| ForestWind2045RCP8.5 | Forest | Wind | RCP8.5 | 2045 | 85.5916 | 92.343 | 99.4831 | 106.5867 | 113.6974
| ForestWind2050RCP8.5 | Forest | Wind | RCP8.5 | 2050 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
| ForestWind2055RCP8.5 | Forest | Wind | RCP8.5 | 2055 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
| ForestWind2060RCP8.5 | Forest | Wind | RCP8.5 | 2060 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
| ForestWind2065RCP8.5 | Forest | Wind | RCP8.5 | 2065 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
| ForestWind2070RCP8.5 | Forest | Wind | RCP8.5 | 2070 | 87.882 | 95.2383 | 103.1385 | 110.8929 | 118.669
| ForestWind2075RCP8.5 | Forest | Wind | RCP8.5 | 2075 | 88.1895 | 95.6271 | 103.6317 | 111.4732 | 119.3393
| ForestWind2080RCP8.5 | Forest | Wind | RCP8.5 | 2080 | 88.4969 | 96.016 | 104.125 | 112.0534 | 120.0096
| ForestWind2085RCP8.5 | Forest | Wind | RCP8.5 | 2085 | 88.8396 | 96.4489 | 104.664 | 112.6826 | 120.7358
| ForestWind2090RCP8.5 | Forest | Wind | RCP8.5 | 2090 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
| ForestWind2095RCP8.5 | Forest | Wind | RCP8.5 | 2095 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
| ForestWind2100RCP8.5 | Forest | Wind | RCP8.5 | 2100 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
| Fort ErieIce Accretion2023RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2023 | 20.7501 | 24.8253 | 29.97 | 33.9339 | 37.8378
| Fort ErieIce Accretion2025RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2025 | 20.7084 | 24.7838 | 29.935 | 33.8943 | 37.8
| Fort ErieIce Accretion2030RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2030 | 20.6666 | 24.7423 | 29.9 | 33.8548 | 37.7622
| Fort ErieIce Accretion2035RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2035 | 20.6249 | 24.7008 | 29.865 | 33.8152 | 37.7244
| Fort ErieIce Accretion2040RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2040 | 20.5831 | 24.6593 | 29.83 | 33.7757 | 37.6866
| Fort ErieIce Accretion2045RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2045 | 20.5414 | 24.6178 | 29.795 | 33.7361 | 37.6488
| Fort ErieIce Accretion2050RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2050 | 20.1531 | 24.1879 | 29.31 | 33.2017 | 37.0742
| Fort ErieIce Accretion2055RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2055 | 19.8066 | 23.7994 | 28.86 | 32.7067 | 36.5375
| Fort ErieIce Accretion2060RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2060 | 19.46 | 23.411 | 28.41 | 32.2118 | 36.0007
| Fort ErieIce Accretion2065RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2065 | 19.1135 | 23.0225 | 27.96 | 31.7168 | 35.464
| Fort ErieIce Accretion2070RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2070 | 18.767 | 22.6341 | 27.51 | 31.2219 | 34.9272
| Fort ErieIce Accretion2075RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2075 | 18.6139 | 22.4806 | 27.355 | 31.0637 | 34.7634
| Fort ErieIce Accretion2080RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2080 | 18.4608 | 22.327 | 27.2 | 30.9055 | 34.5996
| Fort ErieIce Accretion2085RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2085 | 18.3077 | 22.1734 | 27.045 | 30.7473 | 34.4358
| Fort ErieIce Accretion2090RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2090 | 18.1546 | 22.0199 | 26.89 | 30.5891 | 34.272
| Fort ErieIce Accretion2095RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2095 | 18.0015 | 21.8663 | 26.735 | 30.4309 | 34.1082
| Fort ErieIce Accretion2100RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2100 | 17.8485 | 21.7128 | 26.58 | 30.2727 | 33.9444
| Fort ErieIce Accretion2023RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2023 | 20.7501 | 24.8253 | 29.97 | 33.9339 | 37.8378
| Fort ErieIce Accretion2025RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2025 | 20.7084 | 24.7838 | 29.935 | 33.8943 | 37.8
| Fort ErieIce Accretion2030RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2030 | 20.6666 | 24.7423 | 29.9 | 33.8548 | 37.7622
| Fort ErieIce Accretion2035RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2035 | 20.6249 | 24.7008 | 29.865 | 33.8152 | 37.7244
| Fort ErieIce Accretion2040RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2040 | 20.5831 | 24.6593 | 29.83 | 33.7757 | 37.6866
| Fort ErieIce Accretion2045RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2045 | 20.5414 | 24.6178 | 29.795 | 33.7361 | 37.6488
| Fort ErieIce Accretion2050RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2050 | 20.1531 | 24.1879 | 29.31 | 33.2017 | 37.0742
| Fort ErieIce Accretion2055RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2055 | 19.8066 | 23.7994 | 28.86 | 32.7067 | 36.5375
| Fort ErieIce Accretion2060RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2060 | 19.46 | 23.411 | 28.41 | 32.2118 | 36.0007
| Fort ErieIce Accretion2065RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2065 | 19.1135 | 23.0225 | 27.96 | 31.7168 | 35.464
| Fort ErieIce Accretion2070RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2070 | 18.767 | 22.6341 | 27.51 | 31.2219 | 34.9272
| Fort ErieIce Accretion2075RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2075 | 18.5373 | 22.4038 | 27.2775 | 30.9846 | 34.6815
| Fort ErieIce Accretion2080RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2080 | 18.3077 | 22.1734 | 27.045 | 30.7473 | 34.4358
| Fort ErieIce Accretion2085RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2085 | 18.0781 | 21.9431 | 26.8125 | 30.51 | 34.1901
| Fort ErieIce Accretion2090RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2090 | 17.2848 | 21.082 | 25.85 | 29.4704 | 33.075
| Fort ErieIce Accretion2095RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2095 | 16.7212 | 20.4512 | 25.12 | 28.6681 | 32.2056
| Fort ErieIce Accretion2100RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2100 | 16.1575 | 19.8204 | 24.39 | 27.8658 | 31.3362
| Fort ErieIce Accretion2023RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2023 | 20.7501 | 24.8253 | 29.97 | 33.9339 | 37.8378
| Fort ErieIce Accretion2025RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2025 | 20.6666 | 24.7423 | 29.9 | 33.8548 | 37.7622
| Fort ErieIce Accretion2030RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2030 | 20.5831 | 24.6593 | 29.83 | 33.7757 | 37.6866
| Fort ErieIce Accretion2035RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2035 | 20.4996 | 24.5763 | 29.76 | 33.6966 | 37.611
| Fort ErieIce Accretion2040RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2040 | 19.9221 | 23.9289 | 29.01 | 32.8717 | 36.7164
| Fort ErieIce Accretion2045RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2045 | 19.3445 | 23.2815 | 28.26 | 32.0468 | 35.8218
| Fort ErieIce Accretion2050RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2050 | 18.4608 | 22.327 | 27.2 | 30.9055 | 34.5996
| Fort ErieIce Accretion2055RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2055 | 18.1546 | 22.0199 | 26.89 | 30.5891 | 34.272
| Fort ErieIce Accretion2060RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2060 | 17.2848 | 21.082 | 25.85 | 29.4704 | 33.075
| Fort ErieIce Accretion2065RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2065 | 16.7212 | 20.4512 | 25.12 | 28.6681 | 32.2056
| Fort ErieIce Accretion2070RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2070 | 15.9418 | 19.588 | 24.14 | 27.6059 | 31.0464
| Fort ErieIce Accretion2075RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2075 | 15.7261 | 19.3556 | 23.89 | 27.346 | 30.7566
| Fort ErieIce Accretion2080RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2080 | 15.5104 | 19.1232 | 23.64 | 27.0861 | 30.4668
| Fort ErieIce Accretion2085RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2085 | 14.8946 | 18.426 | 22.83 | 26.1878 | 29.484
| Fort ErieIce Accretion2090RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2090 | 14.2788 | 17.7288 | 22.02 | 25.2894 | 28.5012
| Fort ErieIce Accretion2095RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2095 | 14.2788 | 17.7288 | 22.02 | 25.2894 | 28.5012
| Fort ErieIce Accretion2100RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2100 | 14.2788 | 17.7288 | 22.02 | 25.2894 | 28.5012
| Fort ErieWind2023RCP4.5 | Fort Erie | Wind | RCP4.5 | 2023 | 89.1233 | 96.1501 | 103.581 | 110.9736 | 118.373
| Fort ErieWind2025RCP4.5 | Fort Erie | Wind | RCP4.5 | 2025 | 89.1204 | 96.1533 | 103.5929 | 110.9917 | 118.3982
| Fort ErieWind2030RCP4.5 | Fort Erie | Wind | RCP4.5 | 2030 | 89.1174 | 96.1564 | 103.6048 | 111.0099 | 118.4234
| Fort ErieWind2035RCP4.5 | Fort Erie | Wind | RCP4.5 | 2035 | 89.1145 | 96.1596 | 103.6167 | 111.0281 | 118.4486
| Fort ErieWind2040RCP4.5 | Fort Erie | Wind | RCP4.5 | 2040 | 89.1116 | 96.1627 | 103.6286 | 111.0463 | 118.4738
| Fort ErieWind2045RCP4.5 | Fort Erie | Wind | RCP4.5 | 2045 | 89.1086 | 96.1659 | 103.6405 | 111.0645 | 118.499
| Fort ErieWind2050RCP4.5 | Fort Erie | Wind | RCP4.5 | 2050 | 89.1074 | 96.1823 | 103.683 | 111.1263 | 118.58
| Fort ErieWind2055RCP4.5 | Fort Erie | Wind | RCP4.5 | 2055 | 89.1092 | 96.1956 | 103.7136 | 111.17 | 118.6358
| Fort ErieWind2060RCP4.5 | Fort Erie | Wind | RCP4.5 | 2060 | 89.111 | 96.2089 | 103.7442 | 111.2137 | 118.6916
| Fort ErieWind2065RCP4.5 | Fort Erie | Wind | RCP4.5 | 2065 | 89.1127 | 96.2222 | 103.7748 | 111.2573 | 118.7475
| Fort ErieWind2070RCP4.5 | Fort Erie | Wind | RCP4.5 | 2070 | 89.1145 | 96.2355 | 103.8054 | 111.301 | 118.8033
| Fort ErieWind2075RCP4.5 | Fort Erie | Wind | RCP4.5 | 2075 | 89.135 | 96.2671 | 103.8513 | 111.3592 | 118.873
| Fort ErieWind2080RCP4.5 | Fort Erie | Wind | RCP4.5 | 2080 | 89.1556 | 96.2987 | 103.8972 | 111.4174 | 118.9428
| Fort ErieWind2085RCP4.5 | Fort Erie | Wind | RCP4.5 | 2085 | 89.1761 | 96.3303 | 103.9431 | 111.4756 | 119.0126
| Fort ErieWind2090RCP4.5 | Fort Erie | Wind | RCP4.5 | 2090 | 89.1967 | 96.3619 | 103.989 | 111.5338 | 119.0823
| Fort ErieWind2095RCP4.5 | Fort Erie | Wind | RCP4.5 | 2095 | 89.2172 | 96.3936 | 104.0349 | 111.592 | 119.1521
| Fort ErieWind2100RCP4.5 | Fort Erie | Wind | RCP4.5 | 2100 | 89.2378 | 96.4252 | 104.0808 | 111.6502 | 119.2219
| Fort ErieWind2023RCP6.0 | Fort Erie | Wind | RCP6.0 | 2023 | 89.1233 | 96.1501 | 103.581 | 110.9736 | 118.373
| Fort ErieWind2025RCP6.0 | Fort Erie | Wind | RCP6.0 | 2025 | 89.1204 | 96.1533 | 103.5929 | 110.9917 | 118.3982
| Fort ErieWind2030RCP6.0 | Fort Erie | Wind | RCP6.0 | 2030 | 89.1174 | 96.1564 | 103.6048 | 111.0099 | 118.4234
| Fort ErieWind2035RCP6.0 | Fort Erie | Wind | RCP6.0 | 2035 | 89.1145 | 96.1596 | 103.6167 | 111.0281 | 118.4486
| Fort ErieWind2040RCP6.0 | Fort Erie | Wind | RCP6.0 | 2040 | 89.1116 | 96.1627 | 103.6286 | 111.0463 | 118.4738
| Fort ErieWind2045RCP6.0 | Fort Erie | Wind | RCP6.0 | 2045 | 89.1086 | 96.1659 | 103.6405 | 111.0645 | 118.499
| Fort ErieWind2050RCP6.0 | Fort Erie | Wind | RCP6.0 | 2050 | 89.1074 | 96.1823 | 103.683 | 111.1263 | 118.58
| Fort ErieWind2055RCP6.0 | Fort Erie | Wind | RCP6.0 | 2055 | 89.1092 | 96.1956 | 103.7136 | 111.17 | 118.6358
| Fort ErieWind2060RCP6.0 | Fort Erie | Wind | RCP6.0 | 2060 | 89.111 | 96.2089 | 103.7442 | 111.2137 | 118.6916
| Fort ErieWind2065RCP6.0 | Fort Erie | Wind | RCP6.0 | 2065 | 89.1127 | 96.2222 | 103.7748 | 111.2573 | 118.7475
| Fort ErieWind2070RCP6.0 | Fort Erie | Wind | RCP6.0 | 2070 | 89.1145 | 96.2355 | 103.8054 | 111.301 | 118.8033
| Fort ErieWind2075RCP6.0 | Fort Erie | Wind | RCP6.0 | 2075 | 89.1453 | 96.2829 | 103.8743 | 111.3883 | 118.9079
| Fort ErieWind2080RCP6.0 | Fort Erie | Wind | RCP6.0 | 2080 | 89.1761 | 96.3303 | 103.9431 | 111.4756 | 119.0126
| Fort ErieWind2085RCP6.0 | Fort Erie | Wind | RCP6.0 | 2085 | 89.207 | 96.3778 | 104.0119 | 111.5629 | 119.1172
| Fort ErieWind2090RCP6.0 | Fort Erie | Wind | RCP6.0 | 2090 | 89.3406 | 96.5706 | 104.2746 | 111.8867 | 119.5087
| Fort ErieWind2095RCP6.0 | Fort Erie | Wind | RCP6.0 | 2095 | 89.4433 | 96.7161 | 104.4684 | 112.1232 | 119.7955
| Fort ErieWind2100RCP6.0 | Fort Erie | Wind | RCP6.0 | 2100 | 89.5461 | 96.8615 | 104.6622 | 112.3596 | 120.0824
| Fort ErieWind2023RCP8.5 | Fort Erie | Wind | RCP8.5 | 2023 | 89.1233 | 96.1501 | 103.581 | 110.9736 | 118.373
| Fort ErieWind2025RCP8.5 | Fort Erie | Wind | RCP8.5 | 2025 | 89.1174 | 96.1564 | 103.6048 | 111.0099 | 118.4234
| Fort ErieWind2030RCP8.5 | Fort Erie | Wind | RCP8.5 | 2030 | 89.1116 | 96.1627 | 103.6286 | 111.0463 | 118.4738
| Fort ErieWind2035RCP8.5 | Fort Erie | Wind | RCP8.5 | 2035 | 89.1057 | 96.1691 | 103.6524 | 111.0827 | 118.5242
| Fort ErieWind2040RCP8.5 | Fort Erie | Wind | RCP8.5 | 2040 | 89.1086 | 96.1912 | 103.7034 | 111.1555 | 118.6172
| Fort ErieWind2045RCP8.5 | Fort Erie | Wind | RCP8.5 | 2045 | 89.1116 | 96.2133 | 103.7544 | 111.2282 | 118.7103
| Fort ErieWind2050RCP8.5 | Fort Erie | Wind | RCP8.5 | 2050 | 89.1556 | 96.2987 | 103.8972 | 111.4174 | 118.9428
| Fort ErieWind2055RCP8.5 | Fort Erie | Wind | RCP8.5 | 2055 | 89.1967 | 96.3619 | 103.989 | 111.5338 | 119.0823
| Fort ErieWind2060RCP8.5 | Fort Erie | Wind | RCP8.5 | 2060 | 89.3406 | 96.5706 | 104.2746 | 111.8867 | 119.5087
| Fort ErieWind2065RCP8.5 | Fort Erie | Wind | RCP8.5 | 2065 | 89.4433 | 96.7161 | 104.4684 | 112.1232 | 119.7955
| Fort ErieWind2070RCP8.5 | Fort Erie | Wind | RCP8.5 | 2070 | 89.549 | 96.8868 | 104.72 | 112.4433 | 120.187
| Fort ErieWind2075RCP8.5 | Fort Erie | Wind | RCP8.5 | 2075 | 89.5519 | 96.9121 | 104.7778 | 112.527 | 120.2917
| Fort ErieWind2080RCP8.5 | Fort Erie | Wind | RCP8.5 | 2080 | 89.5549 | 96.9374 | 104.8356 | 112.6107 | 120.3963
| Fort ErieWind2085RCP8.5 | Fort Erie | Wind | RCP8.5 | 2085 | 89.5901 | 97.0465 | 105.0345 | 112.8835 | 120.7452
| Fort ErieWind2090RCP8.5 | Fort Erie | Wind | RCP8.5 | 2090 | 89.6253 | 97.1556 | 105.2334 | 113.1564 | 121.094
| Fort ErieWind2095RCP8.5 | Fort Erie | Wind | RCP8.5 | 2095 | 89.6253 | 97.1556 | 105.2334 | 113.1564 | 121.094
| Fort ErieWind2100RCP8.5 | Fort Erie | Wind | RCP8.5 | 2100 | 89.6253 | 97.1556 | 105.2334 | 113.1564 | 121.094
| Fort Erie (Ridgeway)Ice Accretion2023RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2023 | 20.7501 | 24.8253 | 29.97 | 33.9339 | 37.8378
| Fort Erie (Ridgeway)Ice Accretion2025RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2025 | 20.7084 | 24.7838 | 29.935 | 33.8943 | 37.8
| Fort Erie (Ridgeway)Ice Accretion2030RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2030 | 20.6666 | 24.7423 | 29.9 | 33.8548 | 37.7622
| Fort Erie (Ridgeway)Ice Accretion2035RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2035 | 20.6249 | 24.7008 | 29.865 | 33.8152 | 37.7244
| Fort Erie (Ridgeway)Ice Accretion2040RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2040 | 20.5831 | 24.6593 | 29.83 | 33.7757 | 37.6866
| Fort Erie (Ridgeway)Ice Accretion2045RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2045 | 20.5414 | 24.6178 | 29.795 | 33.7361 | 37.6488
| Fort Erie (Ridgeway)Ice Accretion2050RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2050 | 20.1531 | 24.1879 | 29.31 | 33.2017 | 37.0742
| Fort Erie (Ridgeway)Ice Accretion2055RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2055 | 19.8066 | 23.7994 | 28.86 | 32.7067 | 36.5375
| Fort Erie (Ridgeway)Ice Accretion2060RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2060 | 19.46 | 23.411 | 28.41 | 32.2118 | 36.0007
| Fort Erie (Ridgeway)Ice Accretion2065RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2065 | 19.1135 | 23.0225 | 27.96 | 31.7168 | 35.464
| Fort Erie (Ridgeway)Ice Accretion2070RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2070 | 18.767 | 22.6341 | 27.51 | 31.2219 | 34.9272
| Fort Erie (Ridgeway)Ice Accretion2075RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2075 | 18.6139 | 22.4806 | 27.355 | 31.0637 | 34.7634
| Fort Erie (Ridgeway)Ice Accretion2080RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2080 | 18.4608 | 22.327 | 27.2 | 30.9055 | 34.5996
| Fort Erie (Ridgeway)Ice Accretion2085RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2085 | 18.3077 | 22.1734 | 27.045 | 30.7473 | 34.4358
| Fort Erie (Ridgeway)Ice Accretion2090RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2090 | 18.1546 | 22.0199 | 26.89 | 30.5891 | 34.272
| Fort Erie (Ridgeway)Ice Accretion2095RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2095 | 18.0015 | 21.8663 | 26.735 | 30.4309 | 34.1082
| Fort Erie (Ridgeway)Ice Accretion2100RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2100 | 17.8485 | 21.7128 | 26.58 | 30.2727 | 33.9444
| Fort Erie (Ridgeway)Ice Accretion2023RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2023 | 20.7501 | 24.8253 | 29.97 | 33.9339 | 37.8378
| Fort Erie (Ridgeway)Ice Accretion2025RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2025 | 20.7084 | 24.7838 | 29.935 | 33.8943 | 37.8
| Fort Erie (Ridgeway)Ice Accretion2030RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2030 | 20.6666 | 24.7423 | 29.9 | 33.8548 | 37.7622
| Fort Erie (Ridgeway)Ice Accretion2035RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2035 | 20.6249 | 24.7008 | 29.865 | 33.8152 | 37.7244
| Fort Erie (Ridgeway)Ice Accretion2040RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2040 | 20.5831 | 24.6593 | 29.83 | 33.7757 | 37.6866
| Fort Erie (Ridgeway)Ice Accretion2045RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2045 | 20.5414 | 24.6178 | 29.795 | 33.7361 | 37.6488
| Fort Erie (Ridgeway)Ice Accretion2050RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2050 | 20.1531 | 24.1879 | 29.31 | 33.2017 | 37.0742
| Fort Erie (Ridgeway)Ice Accretion2055RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2055 | 19.8066 | 23.7994 | 28.86 | 32.7067 | 36.5375
| Fort Erie (Ridgeway)Ice Accretion2060RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2060 | 19.46 | 23.411 | 28.41 | 32.2118 | 36.0007
| Fort Erie (Ridgeway)Ice Accretion2065RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2065 | 19.1135 | 23.0225 | 27.96 | 31.7168 | 35.464
| Fort Erie (Ridgeway)Ice Accretion2070RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2070 | 18.767 | 22.6341 | 27.51 | 31.2219 | 34.9272
| Fort Erie (Ridgeway)Ice Accretion2075RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2075 | 18.5373 | 22.4038 | 27.2775 | 30.9846 | 34.6815
| Fort Erie (Ridgeway)Ice Accretion2080RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2080 | 18.3077 | 22.1734 | 27.045 | 30.7473 | 34.4358
| Fort Erie (Ridgeway)Ice Accretion2085RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2085 | 18.0781 | 21.9431 | 26.8125 | 30.51 | 34.1901
| Fort Erie (Ridgeway)Ice Accretion2090RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2090 | 17.2848 | 21.082 | 25.85 | 29.4704 | 33.075
| Fort Erie (Ridgeway)Ice Accretion2095RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2095 | 16.7212 | 20.4512 | 25.12 | 28.6681 | 32.2056
| Fort Erie (Ridgeway)Ice Accretion2100RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2100 | 16.1575 | 19.8204 | 24.39 | 27.8658 | 31.3362
| Fort Erie (Ridgeway)Ice Accretion2023RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2023 | 20.7501 | 24.8253 | 29.97 | 33.9339 | 37.8378
| Fort Erie (Ridgeway)Ice Accretion2025RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2025 | 20.6666 | 24.7423 | 29.9 | 33.8548 | 37.7622
| Fort Erie (Ridgeway)Ice Accretion2030RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2030 | 20.5831 | 24.6593 | 29.83 | 33.7757 | 37.6866
| Fort Erie (Ridgeway)Ice Accretion2035RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2035 | 20.4996 | 24.5763 | 29.76 | 33.6966 | 37.611
| Fort Erie (Ridgeway)Ice Accretion2040RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2040 | 19.9221 | 23.9289 | 29.01 | 32.8717 | 36.7164
| Fort Erie (Ridgeway)Ice Accretion2045RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2045 | 19.3445 | 23.2815 | 28.26 | 32.0468 | 35.8218
| Fort Erie (Ridgeway)Ice Accretion2050RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2050 | 18.4608 | 22.327 | 27.2 | 30.9055 | 34.5996
| Fort Erie (Ridgeway)Ice Accretion2055RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2055 | 18.1546 | 22.0199 | 26.89 | 30.5891 | 34.272
| Fort Erie (Ridgeway)Ice Accretion2060RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2060 | 17.2848 | 21.082 | 25.85 | 29.4704 | 33.075
| Fort Erie (Ridgeway)Ice Accretion2065RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2065 | 16.7212 | 20.4512 | 25.12 | 28.6681 | 32.2056
| Fort Erie (Ridgeway)Ice Accretion2070RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2070 | 15.9418 | 19.588 | 24.14 | 27.6059 | 31.0464
| Fort Erie (Ridgeway)Ice Accretion2075RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2075 | 15.7261 | 19.3556 | 23.89 | 27.346 | 30.7566
| Fort Erie (Ridgeway)Ice Accretion2080RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2080 | 15.5104 | 19.1232 | 23.64 | 27.0861 | 30.4668
| Fort Erie (Ridgeway)Ice Accretion2085RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2085 | 14.8946 | 18.426 | 22.83 | 26.1878 | 29.484
| Fort Erie (Ridgeway)Ice Accretion2090RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2090 | 14.2788 | 17.7288 | 22.02 | 25.2894 | 28.5012
| Fort Erie (Ridgeway)Ice Accretion2095RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2095 | 14.2788 | 17.7288 | 22.02 | 25.2894 | 28.5012
| Fort Erie (Ridgeway)Ice Accretion2100RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2100 | 14.2788 | 17.7288 | 22.02 | 25.2894 | 28.5012
| Fort Erie (Ridgeway)Wind2023RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2023 | 89.1233 | 96.1501 | 103.581 | 110.9736 | 118.373
| Fort Erie (Ridgeway)Wind2025RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2025 | 89.1204 | 96.1533 | 103.5929 | 110.9917 | 118.3982
| Fort Erie (Ridgeway)Wind2030RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2030 | 89.1174 | 96.1564 | 103.6048 | 111.0099 | 118.4234
| Fort Erie (Ridgeway)Wind2035RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2035 | 89.1145 | 96.1596 | 103.6167 | 111.0281 | 118.4486
| Fort Erie (Ridgeway)Wind2040RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2040 | 89.1116 | 96.1627 | 103.6286 | 111.0463 | 118.4738
| Fort Erie (Ridgeway)Wind2045RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2045 | 89.1086 | 96.1659 | 103.6405 | 111.0645 | 118.499
| Fort Erie (Ridgeway)Wind2050RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2050 | 89.1074 | 96.1823 | 103.683 | 111.1263 | 118.58
| Fort Erie (Ridgeway)Wind2055RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2055 | 89.1092 | 96.1956 | 103.7136 | 111.17 | 118.6358
| Fort Erie (Ridgeway)Wind2060RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2060 | 89.111 | 96.2089 | 103.7442 | 111.2137 | 118.6916
| Fort Erie (Ridgeway)Wind2065RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2065 | 89.1127 | 96.2222 | 103.7748 | 111.2573 | 118.7475
| Fort Erie (Ridgeway)Wind2070RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2070 | 89.1145 | 96.2355 | 103.8054 | 111.301 | 118.8033
| Fort Erie (Ridgeway)Wind2075RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2075 | 89.135 | 96.2671 | 103.8513 | 111.3592 | 118.873
| Fort Erie (Ridgeway)Wind2080RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2080 | 89.1556 | 96.2987 | 103.8972 | 111.4174 | 118.9428
| Fort Erie (Ridgeway)Wind2085RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2085 | 89.1761 | 96.3303 | 103.9431 | 111.4756 | 119.0126
| Fort Erie (Ridgeway)Wind2090RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2090 | 89.1967 | 96.3619 | 103.989 | 111.5338 | 119.0823
| Fort Erie (Ridgeway)Wind2095RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2095 | 89.2172 | 96.3936 | 104.0349 | 111.592 | 119.1521
| Fort Erie (Ridgeway)Wind2100RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2100 | 89.2378 | 96.4252 | 104.0808 | 111.6502 | 119.2219
| Fort Erie (Ridgeway)Wind2023RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2023 | 89.1233 | 96.1501 | 103.581 | 110.9736 | 118.373
| Fort Erie (Ridgeway)Wind2025RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2025 | 89.1204 | 96.1533 | 103.5929 | 110.9917 | 118.3982
| Fort Erie (Ridgeway)Wind2030RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2030 | 89.1174 | 96.1564 | 103.6048 | 111.0099 | 118.4234
| Fort Erie (Ridgeway)Wind2035RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2035 | 89.1145 | 96.1596 | 103.6167 | 111.0281 | 118.4486
| Fort Erie (Ridgeway)Wind2040RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2040 | 89.1116 | 96.1627 | 103.6286 | 111.0463 | 118.4738
| Fort Erie (Ridgeway)Wind2045RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2045 | 89.1086 | 96.1659 | 103.6405 | 111.0645 | 118.499
| Fort Erie (Ridgeway)Wind2050RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2050 | 89.1074 | 96.1823 | 103.683 | 111.1263 | 118.58
| Fort Erie (Ridgeway)Wind2055RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2055 | 89.1092 | 96.1956 | 103.7136 | 111.17 | 118.6358
| Fort Erie (Ridgeway)Wind2060RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2060 | 89.111 | 96.2089 | 103.7442 | 111.2137 | 118.6916
| Fort Erie (Ridgeway)Wind2065RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2065 | 89.1127 | 96.2222 | 103.7748 | 111.2573 | 118.7475
| Fort Erie (Ridgeway)Wind2070RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2070 | 89.1145 | 96.2355 | 103.8054 | 111.301 | 118.8033
| Fort Erie (Ridgeway)Wind2075RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2075 | 89.1453 | 96.2829 | 103.8743 | 111.3883 | 118.9079
| Fort Erie (Ridgeway)Wind2080RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2080 | 89.1761 | 96.3303 | 103.9431 | 111.4756 | 119.0126
| Fort Erie (Ridgeway)Wind2085RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2085 | 89.207 | 96.3778 | 104.0119 | 111.5629 | 119.1172
| Fort Erie (Ridgeway)Wind2090RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2090 | 89.3406 | 96.5706 | 104.2746 | 111.8867 | 119.5087
| Fort Erie (Ridgeway)Wind2095RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2095 | 89.4433 | 96.7161 | 104.4684 | 112.1232 | 119.7955
| Fort Erie (Ridgeway)Wind2100RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2100 | 89.5461 | 96.8615 | 104.6622 | 112.3596 | 120.0824
| Fort Erie (Ridgeway)Wind2023RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2023 | 89.1233 | 96.1501 | 103.581 | 110.9736 | 118.373
| Fort Erie (Ridgeway)Wind2025RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2025 | 89.1174 | 96.1564 | 103.6048 | 111.0099 | 118.4234
| Fort Erie (Ridgeway)Wind2030RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2030 | 89.1116 | 96.1627 | 103.6286 | 111.0463 | 118.4738
| Fort Erie (Ridgeway)Wind2035RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2035 | 89.1057 | 96.1691 | 103.6524 | 111.0827 | 118.5242
| Fort Erie (Ridgeway)Wind2040RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2040 | 89.1086 | 96.1912 | 103.7034 | 111.1555 | 118.6172
| Fort Erie (Ridgeway)Wind2045RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2045 | 89.1116 | 96.2133 | 103.7544 | 111.2282 | 118.7103
| Fort Erie (Ridgeway)Wind2050RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2050 | 89.1556 | 96.2987 | 103.8972 | 111.4174 | 118.9428
| Fort Erie (Ridgeway)Wind2055RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2055 | 89.1967 | 96.3619 | 103.989 | 111.5338 | 119.0823
| Fort Erie (Ridgeway)Wind2060RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2060 | 89.3406 | 96.5706 | 104.2746 | 111.8867 | 119.5087
| Fort Erie (Ridgeway)Wind2065RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2065 | 89.4433 | 96.7161 | 104.4684 | 112.1232 | 119.7955
| Fort Erie (Ridgeway)Wind2070RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2070 | 89.549 | 96.8868 | 104.72 | 112.4433 | 120.187
| Fort Erie (Ridgeway)Wind2075RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2075 | 89.5519 | 96.9121 | 104.7778 | 112.527 | 120.2917
| Fort Erie (Ridgeway)Wind2080RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2080 | 89.5549 | 96.9374 | 104.8356 | 112.6107 | 120.3963
| Fort Erie (Ridgeway)Wind2085RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2085 | 89.5901 | 97.0465 | 105.0345 | 112.8835 | 120.7452
| Fort Erie (Ridgeway)Wind2090RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2090 | 89.6253 | 97.1556 | 105.2334 | 113.1564 | 121.094
| Fort Erie (Ridgeway)Wind2095RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2095 | 89.6253 | 97.1556 | 105.2334 | 113.1564 | 121.094
| Fort Erie (Ridgeway)Wind2100RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2100 | 89.6253 | 97.1556 | 105.2334 | 113.1564 | 121.094
| Fort FrancesIce Accretion2023RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2023 | 10.7717 | 12.7986 | 15.375 | 17.3398 | 19.3158
| Fort FrancesIce Accretion2025RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2025 | 10.8048 | 12.8297 | 15.4075 | 17.3737 | 19.3504
| Fort FrancesIce Accretion2030RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2030 | 10.8378 | 12.8608 | 15.44 | 17.4076 | 19.3851
| Fort FrancesIce Accretion2035RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2035 | 10.8709 | 12.892 | 15.4725 | 17.4415 | 19.4198
| Fort FrancesIce Accretion2040RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2040 | 10.9039 | 12.9231 | 15.505 | 17.4754 | 19.4544
| Fort FrancesIce Accretion2045RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2045 | 10.937 | 12.9542 | 15.5375 | 17.5093 | 19.489
| Fort FrancesIce Accretion2050RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2050 | 11.0807 | 13.1223 | 15.738 | 17.7365 | 19.7392
| Fort FrancesIce Accretion2055RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2055 | 11.1913 | 13.2592 | 15.906 | 17.9297 | 19.9546
| Fort FrancesIce Accretion2060RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2060 | 11.3019 | 13.3962 | 16.074 | 18.1229 | 20.1701
| Fort FrancesIce Accretion2065RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2065 | 11.4126 | 13.5331 | 16.242 | 18.3162 | 20.3855
| Fort FrancesIce Accretion2070RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2070 | 11.5232 | 13.6701 | 16.41 | 18.5094 | 20.601
| Fort FrancesIce Accretion2075RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2075 | 11.5197 | 13.668 | 16.405 | 18.5038 | 20.5978
| Fort FrancesIce Accretion2080RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2080 | 11.5163 | 13.6659 | 16.4 | 18.4981 | 20.5947
| Fort FrancesIce Accretion2085RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2085 | 11.5128 | 13.6639 | 16.395 | 18.4924 | 20.5915
| Fort FrancesIce Accretion2090RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2090 | 11.5093 | 13.6618 | 16.39 | 18.4868 | 20.5884
| Fort FrancesIce Accretion2095RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2095 | 11.5058 | 13.6597 | 16.385 | 18.4811 | 20.5852
| Fort FrancesIce Accretion2100RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2100 | 11.5023 | 13.6576 | 16.38 | 18.4755 | 20.5821
| Fort FrancesIce Accretion2023RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2023 | 10.7717 | 12.7986 | 15.375 | 17.3398 | 19.3158
| Fort FrancesIce Accretion2025RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2025 | 10.8048 | 12.8297 | 15.4075 | 17.3737 | 19.3504
| Fort FrancesIce Accretion2030RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2030 | 10.8378 | 12.8608 | 15.44 | 17.4076 | 19.3851
| Fort FrancesIce Accretion2035RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2035 | 10.8709 | 12.892 | 15.4725 | 17.4415 | 19.4198
| Fort FrancesIce Accretion2040RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2040 | 10.9039 | 12.9231 | 15.505 | 17.4754 | 19.4544
| Fort FrancesIce Accretion2045RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2045 | 10.937 | 12.9542 | 15.5375 | 17.5093 | 19.489
| Fort FrancesIce Accretion2050RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2050 | 11.0807 | 13.1223 | 15.738 | 17.7365 | 19.7392
| Fort FrancesIce Accretion2055RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2055 | 11.1913 | 13.2592 | 15.906 | 17.9297 | 19.9546
| Fort FrancesIce Accretion2060RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2060 | 11.3019 | 13.3962 | 16.074 | 18.1229 | 20.1701
| Fort FrancesIce Accretion2065RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2065 | 11.4126 | 13.5331 | 16.242 | 18.3162 | 20.3855
| Fort FrancesIce Accretion2070RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2070 | 11.5232 | 13.6701 | 16.41 | 18.5094 | 20.601
| Fort FrancesIce Accretion2075RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2075 | 11.518 | 13.667 | 16.4025 | 18.5009 | 20.5963
| Fort FrancesIce Accretion2080RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2080 | 11.5128 | 13.6639 | 16.395 | 18.4924 | 20.5915
| Fort FrancesIce Accretion2085RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2085 | 11.5076 | 13.6608 | 16.3875 | 18.484 | 20.5868
| Fort FrancesIce Accretion2090RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2090 | 11.4919 | 13.6452 | 16.365 | 18.4585 | 20.5632
| Fort FrancesIce Accretion2095RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2095 | 11.4815 | 13.6327 | 16.35 | 18.4416 | 20.5443
| Fort FrancesIce Accretion2100RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2100 | 11.471 | 13.6203 | 16.335 | 18.4246 | 20.5254
| Fort FrancesIce Accretion2023RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2023 | 10.7717 | 12.7986 | 15.375 | 17.3398 | 19.3158
| Fort FrancesIce Accretion2025RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2025 | 10.8378 | 12.8608 | 15.44 | 17.4076 | 19.3851
| Fort FrancesIce Accretion2030RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2030 | 10.9039 | 12.9231 | 15.505 | 17.4754 | 19.4544
| Fort FrancesIce Accretion2035RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2035 | 10.97 | 12.9853 | 15.57 | 17.5432 | 19.5237
| Fort FrancesIce Accretion2040RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2040 | 11.1544 | 13.2136 | 15.85 | 17.8653 | 19.8828
| Fort FrancesIce Accretion2045RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2045 | 11.3388 | 13.4418 | 16.13 | 18.1873 | 20.2419
| Fort FrancesIce Accretion2050RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2050 | 11.5163 | 13.6659 | 16.4 | 18.4981 | 20.5947
| Fort FrancesIce Accretion2055RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2055 | 11.5093 | 13.6618 | 16.39 | 18.4868 | 20.5884
| Fort FrancesIce Accretion2060RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2060 | 11.4919 | 13.6452 | 16.365 | 18.4585 | 20.5632
| Fort FrancesIce Accretion2065RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2065 | 11.4815 | 13.6327 | 16.35 | 18.4416 | 20.5443
| Fort FrancesIce Accretion2070RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2070 | 11.311 | 13.4336 | 16.115 | 18.1761 | 20.2482
| Fort FrancesIce Accretion2075RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2075 | 11.1509 | 13.2468 | 15.895 | 17.9274 | 19.971
| Fort FrancesIce Accretion2080RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2080 | 10.9909 | 13.06 | 15.675 | 17.6788 | 19.6938
| Fort FrancesIce Accretion2085RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2085 | 10.7508 | 12.7737 | 15.345 | 17.3144 | 19.2874
| Fort FrancesIce Accretion2090RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2090 | 10.5108 | 12.4873 | 15.015 | 16.95 | 18.8811
| Fort FrancesIce Accretion2095RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2095 | 10.5108 | 12.4873 | 15.015 | 16.95 | 18.8811
| Fort FrancesIce Accretion2100RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2100 | 10.5108 | 12.4873 | 15.015 | 16.95 | 18.8811
| Fort FrancesWind2023RCP4.5 | Fort Frances | Wind | RCP4.5 | 2023 | 72.3947 | 77.9872 | 83.8824 | 89.7721 | 95.6547
| Fort FrancesWind2025RCP4.5 | Fort Frances | Wind | RCP4.5 | 2025 | 72.3802 | 77.9573 | 83.832 | 89.7047 | 95.5701
| Fort FrancesWind2030RCP4.5 | Fort Frances | Wind | RCP4.5 | 2030 | 72.3657 | 77.9273 | 83.7816 | 89.6373 | 95.4855
| Fort FrancesWind2035RCP4.5 | Fort Frances | Wind | RCP4.5 | 2035 | 72.3512 | 77.8974 | 83.7312 | 89.5699 | 95.4009
| Fort FrancesWind2040RCP4.5 | Fort Frances | Wind | RCP4.5 | 2040 | 72.3367 | 77.8674 | 83.6808 | 89.5025 | 95.3163
| Fort FrancesWind2045RCP4.5 | Fort Frances | Wind | RCP4.5 | 2045 | 72.3222 | 77.8375 | 83.6304 | 89.4351 | 95.2317
| Fort FrancesWind2050RCP4.5 | Fort Frances | Wind | RCP4.5 | 2050 | 72.4672 | 78.0044 | 83.8236 | 89.6499 | 95.4708
| Fort FrancesWind2055RCP4.5 | Fort Frances | Wind | RCP4.5 | 2055 | 72.6268 | 78.2012 | 84.0672 | 89.9321 | 95.7945
| Fort FrancesWind2060RCP4.5 | Fort Frances | Wind | RCP4.5 | 2060 | 72.7864 | 78.3981 | 84.3108 | 90.2144 | 96.1181
| Fort FrancesWind2065RCP4.5 | Fort Frances | Wind | RCP4.5 | 2065 | 72.946 | 78.595 | 84.5544 | 90.4966 | 96.4418
| Fort FrancesWind2070RCP4.5 | Fort Frances | Wind | RCP4.5 | 2070 | 73.1055 | 78.7918 | 84.798 | 90.7788 | 96.7655
| Fort FrancesWind2075RCP4.5 | Fort Frances | Wind | RCP4.5 | 2075 | 73.201 | 78.909 | 84.9408 | 90.9466 | 96.957
| Fort FrancesWind2080RCP4.5 | Fort Frances | Wind | RCP4.5 | 2080 | 73.2965 | 79.0262 | 85.0836 | 91.1144 | 97.1485
| Fort FrancesWind2085RCP4.5 | Fort Frances | Wind | RCP4.5 | 2085 | 73.392 | 79.1434 | 85.2264 | 91.2821 | 97.34
| Fort FrancesWind2090RCP4.5 | Fort Frances | Wind | RCP4.5 | 2090 | 73.4875 | 79.2606 | 85.3692 | 91.4499 | 97.5316
| Fort FrancesWind2095RCP4.5 | Fort Frances | Wind | RCP4.5 | 2095 | 73.583 | 79.3777 | 85.512 | 91.6177 | 97.7231
| Fort FrancesWind2100RCP4.5 | Fort Frances | Wind | RCP4.5 | 2100 | 73.6785 | 79.4949 | 85.6548 | 91.7855 | 97.9146
| Fort FrancesWind2023RCP6.0 | Fort Frances | Wind | RCP6.0 | 2023 | 72.3947 | 77.9872 | 83.8824 | 89.7721 | 95.6547
| Fort FrancesWind2025RCP6.0 | Fort Frances | Wind | RCP6.0 | 2025 | 72.3802 | 77.9573 | 83.832 | 89.7047 | 95.5701
| Fort FrancesWind2030RCP6.0 | Fort Frances | Wind | RCP6.0 | 2030 | 72.3657 | 77.9273 | 83.7816 | 89.6373 | 95.4855
| Fort FrancesWind2035RCP6.0 | Fort Frances | Wind | RCP6.0 | 2035 | 72.3512 | 77.8974 | 83.7312 | 89.5699 | 95.4009
| Fort FrancesWind2040RCP6.0 | Fort Frances | Wind | RCP6.0 | 2040 | 72.3367 | 77.8674 | 83.6808 | 89.5025 | 95.3163
| Fort FrancesWind2045RCP6.0 | Fort Frances | Wind | RCP6.0 | 2045 | 72.3222 | 77.8375 | 83.6304 | 89.4351 | 95.2317
| Fort FrancesWind2050RCP6.0 | Fort Frances | Wind | RCP6.0 | 2050 | 72.4672 | 78.0044 | 83.8236 | 89.6499 | 95.4708
| Fort FrancesWind2055RCP6.0 | Fort Frances | Wind | RCP6.0 | 2055 | 72.6268 | 78.2012 | 84.0672 | 89.9321 | 95.7945
| Fort FrancesWind2060RCP6.0 | Fort Frances | Wind | RCP6.0 | 2060 | 72.7864 | 78.3981 | 84.3108 | 90.2144 | 96.1181
| Fort FrancesWind2065RCP6.0 | Fort Frances | Wind | RCP6.0 | 2065 | 72.946 | 78.595 | 84.5544 | 90.4966 | 96.4418
| Fort FrancesWind2070RCP6.0 | Fort Frances | Wind | RCP6.0 | 2070 | 73.1055 | 78.7918 | 84.798 | 90.7788 | 96.7655
| Fort FrancesWind2075RCP6.0 | Fort Frances | Wind | RCP6.0 | 2075 | 73.2488 | 78.9676 | 85.0122 | 91.0305 | 97.0528
| Fort FrancesWind2080RCP6.0 | Fort Frances | Wind | RCP6.0 | 2080 | 73.392 | 79.1434 | 85.2264 | 91.2821 | 97.34
| Fort FrancesWind2085RCP6.0 | Fort Frances | Wind | RCP6.0 | 2085 | 73.5353 | 79.3191 | 85.4406 | 91.5338 | 97.6273
| Fort FrancesWind2090RCP6.0 | Fort Frances | Wind | RCP6.0 | 2090 | 73.9155 | 79.81 | 86.0664 | 92.2738 | 98.486
| Fort FrancesWind2095RCP6.0 | Fort Frances | Wind | RCP6.0 | 2095 | 74.1524 | 80.1251 | 86.478 | 92.7622 | 99.0573
| Fort FrancesWind2100RCP6.0 | Fort Frances | Wind | RCP6.0 | 2100 | 74.3894 | 80.4402 | 86.8896 | 93.2505 | 99.6287
| Fort FrancesWind2023RCP8.5 | Fort Frances | Wind | RCP8.5 | 2023 | 72.3947 | 77.9872 | 83.8824 | 89.7721 | 95.6547
| Fort FrancesWind2025RCP8.5 | Fort Frances | Wind | RCP8.5 | 2025 | 72.3657 | 77.9273 | 83.7816 | 89.6373 | 95.4855
| Fort FrancesWind2030RCP8.5 | Fort Frances | Wind | RCP8.5 | 2030 | 72.3367 | 77.8674 | 83.6808 | 89.5025 | 95.3163
| Fort FrancesWind2035RCP8.5 | Fort Frances | Wind | RCP8.5 | 2035 | 72.3077 | 77.8075 | 83.58 | 89.3677 | 95.1471
| Fort FrancesWind2040RCP8.5 | Fort Frances | Wind | RCP8.5 | 2040 | 72.5736 | 78.1356 | 83.986 | 89.8381 | 95.6866
| Fort FrancesWind2045RCP8.5 | Fort Frances | Wind | RCP8.5 | 2045 | 72.8396 | 78.4637 | 84.392 | 90.3084 | 96.226
| Fort FrancesWind2050RCP8.5 | Fort Frances | Wind | RCP8.5 | 2050 | 73.2965 | 79.0262 | 85.0836 | 91.1144 | 97.1485
| Fort FrancesWind2055RCP8.5 | Fort Frances | Wind | RCP8.5 | 2055 | 73.4875 | 79.2606 | 85.3692 | 91.4499 | 97.5316
| Fort FrancesWind2060RCP8.5 | Fort Frances | Wind | RCP8.5 | 2060 | 73.9155 | 79.81 | 86.0664 | 92.2738 | 98.486
| Fort FrancesWind2065RCP8.5 | Fort Frances | Wind | RCP8.5 | 2065 | 74.1524 | 80.1251 | 86.478 | 92.7622 | 99.0573
| Fort FrancesWind2070RCP8.5 | Fort Frances | Wind | RCP8.5 | 2070 | 74.4885 | 80.5599 | 87.0324 | 93.4183 | 99.817
| Fort FrancesWind2075RCP8.5 | Fort Frances | Wind | RCP8.5 | 2075 | 74.5876 | 80.6797 | 87.1752 | 93.5861 | 100.0054
| Fort FrancesWind2080RCP8.5 | Fort Frances | Wind | RCP8.5 | 2080 | 74.6867 | 80.7995 | 87.318 | 93.7538 | 100.1937
| Fort FrancesWind2085RCP8.5 | Fort Frances | Wind | RCP8.5 | 2085 | 74.879 | 81.0261 | 87.5868 | 94.0594 | 100.5384
| Fort FrancesWind2090RCP8.5 | Fort Frances | Wind | RCP8.5 | 2090 | 75.0712 | 81.2526 | 87.8556 | 94.365 | 100.8832
| Fort FrancesWind2095RCP8.5 | Fort Frances | Wind | RCP8.5 | 2095 | 75.0712 | 81.2526 | 87.8556 | 94.365 | 100.8832
| Fort FrancesWind2100RCP8.5 | Fort Frances | Wind | RCP8.5 | 2100 | 75.0712 | 81.2526 | 87.8556 | 94.365 | 100.8832
| GananoqueIce Accretion2023RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2023 | 20.8754 | 24.8751 | 29.97 | 33.8661 | 37.7244
| GananoqueIce Accretion2025RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2025 | 20.9624 | 24.9954 | 30.13 | 34.0525 | 37.9449
| GananoqueIce Accretion2030RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2030 | 21.0493 | 25.1158 | 30.29 | 34.239 | 38.1654
| GananoqueIce Accretion2035RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2035 | 21.1363 | 25.2362 | 30.45 | 34.4254 | 38.3859
| GananoqueIce Accretion2040RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2040 | 21.2233 | 25.3565 | 30.61 | 34.6119 | 38.6064
| GananoqueIce Accretion2045RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2045 | 21.3103 | 25.4768 | 30.77 | 34.7983 | 38.8269
| GananoqueIce Accretion2050RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2050 | 21.2804 | 25.4777 | 30.804 | 34.856 | 38.9189
| GananoqueIce Accretion2055RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2055 | 21.1635 | 25.3582 | 30.678 | 34.7272 | 38.7904
| GananoqueIce Accretion2060RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2060 | 21.0466 | 25.2386 | 30.552 | 34.5983 | 38.6618
| GananoqueIce Accretion2065RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2065 | 20.9297 | 25.1191 | 30.426 | 34.4695 | 38.5333
| GananoqueIce Accretion2070RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2070 | 20.8128 | 24.9996 | 30.3 | 34.3407 | 38.4048
| GananoqueIce Accretion2075RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2075 | 20.8267 | 25.0452 | 30.38 | 34.448 | 38.5371
| GananoqueIce Accretion2080RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2080 | 20.8406 | 25.0909 | 30.46 | 34.5554 | 38.6694
| GananoqueIce Accretion2085RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2085 | 20.8545 | 25.1365 | 30.54 | 34.6628 | 38.8017
| GananoqueIce Accretion2090RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2090 | 20.8684 | 25.1822 | 30.62 | 34.7701 | 38.934
| GananoqueIce Accretion2095RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2095 | 20.8823 | 25.2278 | 30.7 | 34.8774 | 39.0663
| GananoqueIce Accretion2100RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2100 | 20.8963 | 25.2735 | 30.78 | 34.9848 | 39.1986
| GananoqueIce Accretion2023RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2023 | 20.8754 | 24.8751 | 29.97 | 33.8661 | 37.7244
| GananoqueIce Accretion2025RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2025 | 20.9624 | 24.9954 | 30.13 | 34.0525 | 37.9449
| GananoqueIce Accretion2030RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2030 | 21.0493 | 25.1158 | 30.29 | 34.239 | 38.1654
| GananoqueIce Accretion2035RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2035 | 21.1363 | 25.2362 | 30.45 | 34.4254 | 38.3859
| GananoqueIce Accretion2040RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2040 | 21.2233 | 25.3565 | 30.61 | 34.6119 | 38.6064
| GananoqueIce Accretion2045RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2045 | 21.3103 | 25.4768 | 30.77 | 34.7983 | 38.8269
| GananoqueIce Accretion2050RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2050 | 21.2804 | 25.4777 | 30.804 | 34.856 | 38.9189
| GananoqueIce Accretion2055RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2055 | 21.1635 | 25.3582 | 30.678 | 34.7272 | 38.7904
| GananoqueIce Accretion2060RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2060 | 21.0466 | 25.2386 | 30.552 | 34.5983 | 38.6618
| GananoqueIce Accretion2065RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2065 | 20.9297 | 25.1191 | 30.426 | 34.4695 | 38.5333
| GananoqueIce Accretion2070RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2070 | 20.8128 | 24.9996 | 30.3 | 34.3407 | 38.4048
| GananoqueIce Accretion2075RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2075 | 20.8336 | 25.0681 | 30.42 | 34.5017 | 38.6032
| GananoqueIce Accretion2080RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2080 | 20.8545 | 25.1365 | 30.54 | 34.6628 | 38.8017
| GananoqueIce Accretion2085RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2085 | 20.8754 | 25.205 | 30.66 | 34.8238 | 39.0001
| GananoqueIce Accretion2090RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2090 | 20.5414 | 24.8751 | 30.34 | 34.4989 | 38.6694
| GananoqueIce Accretion2095RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2095 | 20.1865 | 24.4767 | 29.9 | 34.013 | 38.1402
| GananoqueIce Accretion2100RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2100 | 19.8316 | 24.0783 | 29.46 | 33.5271 | 37.611
| GananoqueIce Accretion2023RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2023 | 20.8754 | 24.8751 | 29.97 | 33.8661 | 37.7244
| GananoqueIce Accretion2025RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2025 | 21.0493 | 25.1158 | 30.29 | 34.239 | 38.1654
| GananoqueIce Accretion2030RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2030 | 21.2233 | 25.3565 | 30.61 | 34.6119 | 38.6064
| GananoqueIce Accretion2035RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2035 | 21.3973 | 25.5972 | 30.93 | 34.9848 | 39.0474
| GananoqueIce Accretion2040RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2040 | 21.2024 | 25.398 | 30.72 | 34.7701 | 38.8332
| GananoqueIce Accretion2045RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2045 | 21.0076 | 25.1988 | 30.51 | 34.5554 | 38.619
| GananoqueIce Accretion2050RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2050 | 20.8406 | 25.0909 | 30.46 | 34.5554 | 38.6694
| GananoqueIce Accretion2055RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2055 | 20.8684 | 25.1822 | 30.62 | 34.7701 | 38.934
| GananoqueIce Accretion2060RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2060 | 20.5414 | 24.8751 | 30.34 | 34.4989 | 38.6694
| GananoqueIce Accretion2065RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2065 | 20.1865 | 24.4767 | 29.9 | 34.013 | 38.1402
| GananoqueIce Accretion2070RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2070 | 19.5463 | 23.7795 | 29.13 | 33.1881 | 37.2456
| GananoqueIce Accretion2075RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2075 | 19.261 | 23.4807 | 28.8 | 32.8491 | 36.8802
| GananoqueIce Accretion2080RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2080 | 18.9757 | 23.1819 | 28.47 | 32.5101 | 36.5148
| GananoqueIce Accretion2085RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2085 | 18.266 | 22.3477 | 27.48 | 31.3914 | 35.2674
| GananoqueIce Accretion2090RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2090 | 17.5562 | 21.5136 | 26.49 | 30.2727 | 34.02
| GananoqueIce Accretion2095RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2095 | 17.5562 | 21.5136 | 26.49 | 30.2727 | 34.02
| GananoqueIce Accretion2100RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2100 | 17.5562 | 21.5136 | 26.49 | 30.2727 | 34.02
| GananoqueWind2023RCP4.5 | Gananoque | Wind | RCP4.5 | 2023 | 86.1755 | 92.721 | 99.6 | 106.4971 | 113.3958
| GananoqueWind2025RCP4.5 | Gananoque | Wind | RCP4.5 | 2025 | 86.1597 | 92.6931 | 99.5533 | 106.4365 | 113.3198
| GananoqueWind2030RCP4.5 | Gananoque | Wind | RCP4.5 | 2030 | 86.1439 | 92.6652 | 99.5067 | 106.3758 | 113.2438
| GananoqueWind2035RCP4.5 | Gananoque | Wind | RCP4.5 | 2035 | 86.1281 | 92.6373 | 99.46 | 106.3152 | 113.1678
| GananoqueWind2040RCP4.5 | Gananoque | Wind | RCP4.5 | 2040 | 86.1122 | 92.6094 | 99.4133 | 106.2546 | 113.0918
| GananoqueWind2045RCP4.5 | Gananoque | Wind | RCP4.5 | 2045 | 86.0964 | 92.5815 | 99.3667 | 106.1939 | 113.0158
| GananoqueWind2050RCP4.5 | Gananoque | Wind | RCP4.5 | 2050 | 86.1894 | 92.6857 | 99.482 | 106.3195 | 113.1518
| GananoqueWind2055RCP4.5 | Gananoque | Wind | RCP4.5 | 2055 | 86.2982 | 92.8177 | 99.644 | 106.5057 | 113.3639
| GananoqueWind2060RCP4.5 | Gananoque | Wind | RCP4.5 | 2060 | 86.407 | 92.9498 | 99.806 | 106.6918 | 113.5759
| GananoqueWind2065RCP4.5 | Gananoque | Wind | RCP4.5 | 2065 | 86.5158 | 93.0818 | 99.968 | 106.878 | 113.788
| GananoqueWind2070RCP4.5 | Gananoque | Wind | RCP4.5 | 2070 | 86.6246 | 93.2139 | 100.13 | 107.0642 | 114
| GananoqueWind2075RCP4.5 | Gananoque | Wind | RCP4.5 | 2075 | 86.7426 | 93.3751 | 100.3433 | 107.321 | 114.3002
| GananoqueWind2080RCP4.5 | Gananoque | Wind | RCP4.5 | 2080 | 86.8606 | 93.5363 | 100.5567 | 107.5778 | 114.6004
| GananoqueWind2085RCP4.5 | Gananoque | Wind | RCP4.5 | 2085 | 86.9786 | 93.6975 | 100.77 | 107.8346 | 114.9006
| GananoqueWind2090RCP4.5 | Gananoque | Wind | RCP4.5 | 2090 | 87.0966 | 93.8587 | 100.9833 | 108.0914 | 115.2008
| GananoqueWind2095RCP4.5 | Gananoque | Wind | RCP4.5 | 2095 | 87.2146 | 94.0199 | 101.1967 | 108.3482 | 115.501
| GananoqueWind2100RCP4.5 | Gananoque | Wind | RCP4.5 | 2100 | 87.3326 | 94.1811 | 101.41 | 108.605 | 115.8012
| GananoqueWind2023RCP6.0 | Gananoque | Wind | RCP6.0 | 2023 | 86.1755 | 92.721 | 99.6 | 106.4971 | 113.3958
| GananoqueWind2025RCP6.0 | Gananoque | Wind | RCP6.0 | 2025 | 86.1597 | 92.6931 | 99.5533 | 106.4365 | 113.3198
| GananoqueWind2030RCP6.0 | Gananoque | Wind | RCP6.0 | 2030 | 86.1439 | 92.6652 | 99.5067 | 106.3758 | 113.2438
| GananoqueWind2035RCP6.0 | Gananoque | Wind | RCP6.0 | 2035 | 86.1281 | 92.6373 | 99.46 | 106.3152 | 113.1678
| GananoqueWind2040RCP6.0 | Gananoque | Wind | RCP6.0 | 2040 | 86.1122 | 92.6094 | 99.4133 | 106.2546 | 113.0918
| GananoqueWind2045RCP6.0 | Gananoque | Wind | RCP6.0 | 2045 | 86.0964 | 92.5815 | 99.3667 | 106.1939 | 113.0158
| GananoqueWind2050RCP6.0 | Gananoque | Wind | RCP6.0 | 2050 | 86.1894 | 92.6857 | 99.482 | 106.3195 | 113.1518
| GananoqueWind2055RCP6.0 | Gananoque | Wind | RCP6.0 | 2055 | 86.2982 | 92.8177 | 99.644 | 106.5057 | 113.3639
| GananoqueWind2060RCP6.0 | Gananoque | Wind | RCP6.0 | 2060 | 86.407 | 92.9498 | 99.806 | 106.6918 | 113.5759
| GananoqueWind2065RCP6.0 | Gananoque | Wind | RCP6.0 | 2065 | 86.5158 | 93.0818 | 99.968 | 106.878 | 113.788
| GananoqueWind2070RCP6.0 | Gananoque | Wind | RCP6.0 | 2070 | 86.6246 | 93.2139 | 100.13 | 107.0642 | 114
| GananoqueWind2075RCP6.0 | Gananoque | Wind | RCP6.0 | 2075 | 86.8016 | 93.4557 | 100.45 | 107.4494 | 114.4503
| GananoqueWind2080RCP6.0 | Gananoque | Wind | RCP6.0 | 2080 | 86.9786 | 93.6975 | 100.77 | 107.8346 | 114.9006
| GananoqueWind2085RCP6.0 | Gananoque | Wind | RCP6.0 | 2085 | 87.1556 | 93.9393 | 101.09 | 108.2198 | 115.3509
| GananoqueWind2090RCP6.0 | Gananoque | Wind | RCP6.0 | 2090 | 87.5312 | 94.4384 | 101.7433 | 109.0045 | 116.2648
| GananoqueWind2095RCP6.0 | Gananoque | Wind | RCP6.0 | 2095 | 87.7298 | 94.6957 | 102.0767 | 109.4039 | 116.7284
| GananoqueWind2100RCP6.0 | Gananoque | Wind | RCP6.0 | 2100 | 87.9284 | 94.953 | 102.41 | 109.8034 | 117.192
| GananoqueWind2023RCP8.5 | Gananoque | Wind | RCP8.5 | 2023 | 86.1755 | 92.721 | 99.6 | 106.4971 | 113.3958
| GananoqueWind2025RCP8.5 | Gananoque | Wind | RCP8.5 | 2025 | 86.1439 | 92.6652 | 99.5067 | 106.3758 | 113.2438
| GananoqueWind2030RCP8.5 | Gananoque | Wind | RCP8.5 | 2030 | 86.1122 | 92.6094 | 99.4133 | 106.2546 | 113.0918
| GananoqueWind2035RCP8.5 | Gananoque | Wind | RCP8.5 | 2035 | 86.0806 | 92.5536 | 99.32 | 106.1333 | 112.9398
| GananoqueWind2040RCP8.5 | Gananoque | Wind | RCP8.5 | 2040 | 86.2619 | 92.7737 | 99.59 | 106.4436 | 113.2932
| GananoqueWind2045RCP8.5 | Gananoque | Wind | RCP8.5 | 2045 | 86.4432 | 92.9938 | 99.86 | 106.7539 | 113.6466
| GananoqueWind2050RCP8.5 | Gananoque | Wind | RCP8.5 | 2050 | 86.8606 | 93.5363 | 100.5567 | 107.5778 | 114.6004
| GananoqueWind2055RCP8.5 | Gananoque | Wind | RCP8.5 | 2055 | 87.0966 | 93.8587 | 100.9833 | 108.0914 | 115.2008
| GananoqueWind2060RCP8.5 | Gananoque | Wind | RCP8.5 | 2060 | 87.5312 | 94.4384 | 101.7433 | 109.0045 | 116.2648
| GananoqueWind2065RCP8.5 | Gananoque | Wind | RCP8.5 | 2065 | 87.7298 | 94.6957 | 102.0767 | 109.4039 | 116.7284
| GananoqueWind2070RCP8.5 | Gananoque | Wind | RCP8.5 | 2070 | 88.0004 | 95.0584 | 102.5567 | 109.9853 | 117.4086
| GananoqueWind2075RCP8.5 | Gananoque | Wind | RCP8.5 | 2075 | 88.0723 | 95.1638 | 102.7033 | 110.1672 | 117.6252
| GananoqueWind2080RCP8.5 | Gananoque | Wind | RCP8.5 | 2080 | 88.1443 | 95.2692 | 102.85 | 110.3491 | 117.8418
| GananoqueWind2085RCP8.5 | Gananoque | Wind | RCP8.5 | 2085 | 88.3127 | 95.5017 | 103.165 | 110.7289 | 118.2978
| GananoqueWind2090RCP8.5 | Gananoque | Wind | RCP8.5 | 2090 | 88.481 | 95.7342 | 103.48 | 111.1088 | 118.7538
| GananoqueWind2095RCP8.5 | Gananoque | Wind | RCP8.5 | 2095 | 88.481 | 95.7342 | 103.48 | 111.1088 | 118.7538
| GananoqueWind2100RCP8.5 | Gananoque | Wind | RCP8.5 | 2100 | 88.481 | 95.7342 | 103.48 | 111.1088 | 118.7538
| GeraldtonIce Accretion2023RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2023 | 10.7091 | 12.7737 | 15.39 | 17.3907 | 19.3914
| GeraldtonIce Accretion2025RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2025 | 10.7961 | 12.8774 | 15.5175 | 17.5348 | 19.552
| GeraldtonIce Accretion2030RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2030 | 10.883 | 12.9812 | 15.645 | 17.6788 | 19.7127
| GeraldtonIce Accretion2035RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2035 | 10.97 | 13.0849 | 15.7725 | 17.8229 | 19.8733
| GeraldtonIce Accretion2040RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2040 | 11.057 | 13.1887 | 15.9 | 17.967 | 20.034
| GeraldtonIce Accretion2045RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2045 | 11.144 | 13.2925 | 16.0275 | 18.1111 | 20.1946
| GeraldtonIce Accretion2050RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2050 | 11.2748 | 13.4485 | 16.215 | 18.3229 | 20.4309
| GeraldtonIce Accretion2055RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2055 | 11.3186 | 13.5008 | 16.275 | 18.3907 | 20.5065
| GeraldtonIce Accretion2060RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2060 | 11.3625 | 13.5531 | 16.335 | 18.4585 | 20.5821
| GeraldtonIce Accretion2065RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2065 | 11.4063 | 13.6054 | 16.395 | 18.5263 | 20.6577
| GeraldtonIce Accretion2070RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2070 | 11.4501 | 13.6576 | 16.455 | 18.5941 | 20.7333
| GeraldtonIce Accretion2075RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2075 | 11.4971 | 13.7178 | 16.53 | 18.6817 | 20.8309
| GeraldtonIce Accretion2080RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2080 | 11.5441 | 13.778 | 16.605 | 18.7693 | 20.9286
| GeraldtonIce Accretion2085RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2085 | 11.5911 | 13.8382 | 16.68 | 18.8569 | 21.0262
| GeraldtonIce Accretion2090RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2090 | 11.638 | 13.8983 | 16.755 | 18.9444 | 21.1239
| GeraldtonIce Accretion2095RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2095 | 11.685 | 13.9585 | 16.83 | 19.032 | 21.2216
| GeraldtonIce Accretion2100RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2100 | 11.732 | 14.0187 | 16.905 | 19.1196 | 21.3192
| GeraldtonIce Accretion2023RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2023 | 10.7091 | 12.7737 | 15.39 | 17.3907 | 19.3914
| GeraldtonIce Accretion2025RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2025 | 10.7961 | 12.8774 | 15.5175 | 17.5348 | 19.552
| GeraldtonIce Accretion2030RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2030 | 10.883 | 12.9812 | 15.645 | 17.6788 | 19.7127
| GeraldtonIce Accretion2035RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2035 | 10.97 | 13.0849 | 15.7725 | 17.8229 | 19.8733
| GeraldtonIce Accretion2040RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2040 | 11.057 | 13.1887 | 15.9 | 17.967 | 20.034
| GeraldtonIce Accretion2045RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2045 | 11.144 | 13.2925 | 16.0275 | 18.1111 | 20.1946
| GeraldtonIce Accretion2050RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2050 | 11.2748 | 13.4485 | 16.215 | 18.3229 | 20.4309
| GeraldtonIce Accretion2055RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2055 | 11.3186 | 13.5008 | 16.275 | 18.3907 | 20.5065
| GeraldtonIce Accretion2060RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2060 | 11.3625 | 13.5531 | 16.335 | 18.4585 | 20.5821
| GeraldtonIce Accretion2065RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2065 | 11.4063 | 13.6054 | 16.395 | 18.5263 | 20.6577
| GeraldtonIce Accretion2070RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2070 | 11.4501 | 13.6576 | 16.455 | 18.5941 | 20.7333
| GeraldtonIce Accretion2075RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2075 | 11.5206 | 13.7479 | 16.5675 | 18.7255 | 20.8798
| GeraldtonIce Accretion2080RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2080 | 11.5911 | 13.8382 | 16.68 | 18.8569 | 21.0262
| GeraldtonIce Accretion2085RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2085 | 11.6615 | 13.9284 | 16.7925 | 18.9882 | 21.1727
| GeraldtonIce Accretion2090RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2090 | 11.6206 | 13.8776 | 16.73 | 18.9162 | 21.0924
| GeraldtonIce Accretion2095RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2095 | 11.5093 | 13.7365 | 16.555 | 18.7128 | 20.8656
| GeraldtonIce Accretion2100RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2100 | 11.398 | 13.5954 | 16.38 | 18.5094 | 20.6388
| GeraldtonIce Accretion2023RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2023 | 10.7091 | 12.7737 | 15.39 | 17.3907 | 19.3914
| GeraldtonIce Accretion2025RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2025 | 10.883 | 12.9812 | 15.645 | 17.6788 | 19.7127
| GeraldtonIce Accretion2030RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2030 | 11.057 | 13.1887 | 15.9 | 17.967 | 20.034
| GeraldtonIce Accretion2035RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2035 | 11.231 | 13.3962 | 16.155 | 18.2551 | 20.3553
| GeraldtonIce Accretion2040RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2040 | 11.304 | 13.4833 | 16.255 | 18.3681 | 20.4813
| GeraldtonIce Accretion2045RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2045 | 11.3771 | 13.5705 | 16.355 | 18.4811 | 20.6073
| GeraldtonIce Accretion2050RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2050 | 11.5441 | 13.778 | 16.605 | 18.7693 | 20.9286
| GeraldtonIce Accretion2055RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2055 | 11.638 | 13.8983 | 16.755 | 18.9444 | 21.1239
| GeraldtonIce Accretion2060RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2060 | 11.6206 | 13.8776 | 16.73 | 18.9162 | 21.0924
| GeraldtonIce Accretion2065RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2065 | 11.5093 | 13.7365 | 16.555 | 18.7128 | 20.8656
| GeraldtonIce Accretion2070RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2070 | 11.3701 | 13.5705 | 16.36 | 18.4924 | 20.6262
| GeraldtonIce Accretion2075RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2075 | 11.3423 | 13.5456 | 16.34 | 18.4755 | 20.6136
| GeraldtonIce Accretion2080RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2080 | 11.3145 | 13.5207 | 16.32 | 18.4585 | 20.601
| GeraldtonIce Accretion2085RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2085 | 11.0587 | 13.2343 | 15.9825 | 18.0857 | 20.1852
| GeraldtonIce Accretion2090RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2090 | 10.803 | 12.948 | 15.645 | 17.7127 | 19.7694
| GeraldtonIce Accretion2095RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2095 | 10.803 | 12.948 | 15.645 | 17.7127 | 19.7694
| GeraldtonIce Accretion2100RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2100 | 10.803 | 12.948 | 15.645 | 17.7127 | 19.7694
| GeraldtonWind2023RCP4.5 | Geraldton | Wind | RCP4.5 | 2023 | 73.6162 | 79.2634 | 85.204 | 91.141 | 97.0841
| GeraldtonWind2025RCP4.5 | Geraldton | Wind | RCP4.5 | 2025 | 73.7324 | 79.3991 | 85.3641 | 91.3229 | 97.2876
| GeraldtonWind2030RCP4.5 | Geraldton | Wind | RCP4.5 | 2030 | 73.8486 | 79.5348 | 85.5242 | 91.5048 | 97.4911
| GeraldtonWind2035RCP4.5 | Geraldton | Wind | RCP4.5 | 2035 | 73.9648 | 79.6705 | 85.6842 | 91.6867 | 97.6946
| GeraldtonWind2040RCP4.5 | Geraldton | Wind | RCP4.5 | 2040 | 74.081 | 79.8062 | 85.8443 | 91.8686 | 97.8981
| GeraldtonWind2045RCP4.5 | Geraldton | Wind | RCP4.5 | 2045 | 74.1972 | 79.9419 | 86.0044 | 92.0505 | 98.1016
| GeraldtonWind2050RCP4.5 | Geraldton | Wind | RCP4.5 | 2050 | 74.4588 | 80.2563 | 86.3838 | 92.4871 | 98.5957
| GeraldtonWind2055RCP4.5 | Geraldton | Wind | RCP4.5 | 2055 | 74.6041 | 80.435 | 86.6031 | 92.7417 | 98.8864
| GeraldtonWind2060RCP4.5 | Geraldton | Wind | RCP4.5 | 2060 | 74.7494 | 80.6136 | 86.8224 | 92.9964 | 99.1771
| GeraldtonWind2065RCP4.5 | Geraldton | Wind | RCP4.5 | 2065 | 74.8948 | 80.7923 | 87.0417 | 93.251 | 99.4678
| GeraldtonWind2070RCP4.5 | Geraldton | Wind | RCP4.5 | 2070 | 75.0401 | 80.9709 | 87.261 | 93.5057 | 99.7585
| GeraldtonWind2075RCP4.5 | Geraldton | Wind | RCP4.5 | 2075 | 75.1049 | 81.0434 | 87.3403 | 93.5921 | 99.8522
| GeraldtonWind2080RCP4.5 | Geraldton | Wind | RCP4.5 | 2080 | 75.1697 | 81.1158 | 87.4197 | 93.6785 | 99.9459
| GeraldtonWind2085RCP4.5 | Geraldton | Wind | RCP4.5 | 2085 | 75.2346 | 81.1883 | 87.499 | 93.7649 | 100.0396
| GeraldtonWind2090RCP4.5 | Geraldton | Wind | RCP4.5 | 2090 | 75.2994 | 81.2608 | 87.5783 | 93.8513 | 100.1332
| GeraldtonWind2095RCP4.5 | Geraldton | Wind | RCP4.5 | 2095 | 75.3642 | 81.3332 | 87.6577 | 93.9377 | 100.2269
| GeraldtonWind2100RCP4.5 | Geraldton | Wind | RCP4.5 | 2100 | 75.4291 | 81.4057 | 87.737 | 94.0241 | 100.3206
| GeraldtonWind2023RCP6.0 | Geraldton | Wind | RCP6.0 | 2023 | 73.6162 | 79.2634 | 85.204 | 91.141 | 97.0841
| GeraldtonWind2025RCP6.0 | Geraldton | Wind | RCP6.0 | 2025 | 73.7324 | 79.3991 | 85.3641 | 91.3229 | 97.2876
| GeraldtonWind2030RCP6.0 | Geraldton | Wind | RCP6.0 | 2030 | 73.8486 | 79.5348 | 85.5242 | 91.5048 | 97.4911
| GeraldtonWind2035RCP6.0 | Geraldton | Wind | RCP6.0 | 2035 | 73.9648 | 79.6705 | 85.6842 | 91.6867 | 97.6946
| GeraldtonWind2040RCP6.0 | Geraldton | Wind | RCP6.0 | 2040 | 74.081 | 79.8062 | 85.8443 | 91.8686 | 97.8981
| GeraldtonWind2045RCP6.0 | Geraldton | Wind | RCP6.0 | 2045 | 74.1972 | 79.9419 | 86.0044 | 92.0505 | 98.1016
| GeraldtonWind2050RCP6.0 | Geraldton | Wind | RCP6.0 | 2050 | 74.4588 | 80.2563 | 86.3838 | 92.4871 | 98.5957
| GeraldtonWind2055RCP6.0 | Geraldton | Wind | RCP6.0 | 2055 | 74.6041 | 80.435 | 86.6031 | 92.7417 | 98.8864
| GeraldtonWind2060RCP6.0 | Geraldton | Wind | RCP6.0 | 2060 | 74.7494 | 80.6136 | 86.8224 | 92.9964 | 99.1771
| GeraldtonWind2065RCP6.0 | Geraldton | Wind | RCP6.0 | 2065 | 74.8948 | 80.7923 | 87.0417 | 93.251 | 99.4678
| GeraldtonWind2070RCP6.0 | Geraldton | Wind | RCP6.0 | 2070 | 75.0401 | 80.9709 | 87.261 | 93.5057 | 99.7585
| GeraldtonWind2075RCP6.0 | Geraldton | Wind | RCP6.0 | 2075 | 75.1373 | 81.0796 | 87.38 | 93.6353 | 99.8991
| GeraldtonWind2080RCP6.0 | Geraldton | Wind | RCP6.0 | 2080 | 75.2346 | 81.1883 | 87.499 | 93.7649 | 100.0396
| GeraldtonWind2085RCP6.0 | Geraldton | Wind | RCP6.0 | 2085 | 75.3318 | 81.297 | 87.618 | 93.8945 | 100.1801
| GeraldtonWind2090RCP6.0 | Geraldton | Wind | RCP6.0 | 2090 | 75.4878 | 81.4847 | 87.8447 | 94.1545 | 100.4724
| GeraldtonWind2095RCP6.0 | Geraldton | Wind | RCP6.0 | 2095 | 75.5465 | 81.5638 | 87.9523 | 94.2848 | 100.6242
| GeraldtonWind2100RCP6.0 | Geraldton | Wind | RCP6.0 | 2100 | 75.6052 | 81.6428 | 88.06 | 94.4152 | 100.776
| GeraldtonWind2023RCP8.5 | Geraldton | Wind | RCP8.5 | 2023 | 73.6162 | 79.2634 | 85.204 | 91.141 | 97.0841
| GeraldtonWind2025RCP8.5 | Geraldton | Wind | RCP8.5 | 2025 | 73.8486 | 79.5348 | 85.5242 | 91.5048 | 97.4911
| GeraldtonWind2030RCP8.5 | Geraldton | Wind | RCP8.5 | 2030 | 74.081 | 79.8062 | 85.8443 | 91.8686 | 97.8981
| GeraldtonWind2035RCP8.5 | Geraldton | Wind | RCP8.5 | 2035 | 74.3135 | 80.0776 | 86.1645 | 92.2324 | 98.305
| GeraldtonWind2040RCP8.5 | Geraldton | Wind | RCP8.5 | 2040 | 74.5557 | 80.3754 | 86.53 | 92.6568 | 98.7895
| GeraldtonWind2045RCP8.5 | Geraldton | Wind | RCP8.5 | 2045 | 74.7979 | 80.6732 | 86.8955 | 93.0813 | 99.2741
| GeraldtonWind2050RCP8.5 | Geraldton | Wind | RCP8.5 | 2050 | 75.1697 | 81.1158 | 87.4197 | 93.6785 | 99.9459
| GeraldtonWind2055RCP8.5 | Geraldton | Wind | RCP8.5 | 2055 | 75.2994 | 81.2608 | 87.5783 | 93.8513 | 100.1332
| GeraldtonWind2060RCP8.5 | Geraldton | Wind | RCP8.5 | 2060 | 75.4878 | 81.4847 | 87.8447 | 94.1545 | 100.4724
| GeraldtonWind2065RCP8.5 | Geraldton | Wind | RCP8.5 | 2065 | 75.5465 | 81.5638 | 87.9523 | 94.2848 | 100.6242
| GeraldtonWind2070RCP8.5 | Geraldton | Wind | RCP8.5 | 2070 | 75.5857 | 81.6033 | 87.9948 | 94.3303 | 100.6726
| GeraldtonWind2075RCP8.5 | Geraldton | Wind | RCP8.5 | 2075 | 75.5661 | 81.5638 | 87.9297 | 94.2454 | 100.5693
| GeraldtonWind2080RCP8.5 | Geraldton | Wind | RCP8.5 | 2080 | 75.5465 | 81.5243 | 87.8645 | 94.1605 | 100.4659
| GeraldtonWind2085RCP8.5 | Geraldton | Wind | RCP8.5 | 2085 | 75.8071 | 81.8681 | 88.315 | 94.6971 | 101.0909
| GeraldtonWind2090RCP8.5 | Geraldton | Wind | RCP8.5 | 2090 | 76.0676 | 82.212 | 88.7655 | 95.2337 | 101.7159
| GeraldtonWind2095RCP8.5 | Geraldton | Wind | RCP8.5 | 2095 | 76.0676 | 82.212 | 88.7655 | 95.2337 | 101.7159
| GeraldtonWind2100RCP8.5 | Geraldton | Wind | RCP8.5 | 2100 | 76.0676 | 82.212 | 88.7655 | 95.2337 | 101.7159
| GlencoeIce Accretion2023RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2023 | 17.4226 | 20.911 | 25.324 | 28.6749 | 32.0393
| GlencoeIce Accretion2025RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2025 | 17.3532 | 20.8427 | 25.2547 | 28.6063 | 31.9683
| GlencoeIce Accretion2030RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2030 | 17.2839 | 20.7743 | 25.1853 | 28.5378 | 31.8973
| GlencoeIce Accretion2035RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2035 | 17.2145 | 20.706 | 25.116 | 28.4692 | 31.8263
| GlencoeIce Accretion2040RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2040 | 17.1452 | 20.6377 | 25.0467 | 28.4007 | 31.7554
| GlencoeIce Accretion2045RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2045 | 17.0758 | 20.5693 | 24.9773 | 28.3321 | 31.6844
| GlencoeIce Accretion2050RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2050 | 16.6881 | 20.1471 | 24.5024 | 27.8229 | 31.1351
| GlencoeIce Accretion2055RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2055 | 16.3696 | 19.7932 | 24.0968 | 27.3822 | 30.6568
| GlencoeIce Accretion2060RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2060 | 16.0512 | 19.4393 | 23.6912 | 26.9415 | 30.1785
| GlencoeIce Accretion2065RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2065 | 15.7328 | 19.0854 | 23.2856 | 26.5008 | 29.7002
| GlencoeIce Accretion2070RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2070 | 15.4144 | 18.7314 | 22.88 | 26.0601 | 29.2219
| GlencoeIce Accretion2075RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2075 | 15.2696 | 18.5804 | 22.724 | 25.8936 | 29.0472
| GlencoeIce Accretion2080RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2080 | 15.1249 | 18.4293 | 22.568 | 25.7271 | 28.8725
| GlencoeIce Accretion2085RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2085 | 14.9802 | 18.2783 | 22.412 | 25.5606 | 28.6978
| GlencoeIce Accretion2090RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2090 | 14.8354 | 18.1272 | 22.256 | 25.3941 | 28.523
| GlencoeIce Accretion2095RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2095 | 14.6907 | 17.9761 | 22.1 | 25.2276 | 28.3483
| GlencoeIce Accretion2100RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2100 | 14.546 | 17.8251 | 21.944 | 25.0611 | 28.1736
| GlencoeIce Accretion2023RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2023 | 17.4226 | 20.911 | 25.324 | 28.6749 | 32.0393
| GlencoeIce Accretion2025RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2025 | 17.3532 | 20.8427 | 25.2547 | 28.6063 | 31.9683
| GlencoeIce Accretion2030RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2030 | 17.2839 | 20.7743 | 25.1853 | 28.5378 | 31.8973
| GlencoeIce Accretion2035RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2035 | 17.2145 | 20.706 | 25.116 | 28.4692 | 31.8263
| GlencoeIce Accretion2040RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2040 | 17.1452 | 20.6377 | 25.0467 | 28.4007 | 31.7554
| GlencoeIce Accretion2045RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2045 | 17.0758 | 20.5693 | 24.9773 | 28.3321 | 31.6844
| GlencoeIce Accretion2050RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2050 | 16.6881 | 20.1471 | 24.5024 | 27.8229 | 31.1351
| GlencoeIce Accretion2055RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2055 | 16.3696 | 19.7932 | 24.0968 | 27.3822 | 30.6568
| GlencoeIce Accretion2060RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2060 | 16.0512 | 19.4393 | 23.6912 | 26.9415 | 30.1785
| GlencoeIce Accretion2065RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2065 | 15.7328 | 19.0854 | 23.2856 | 26.5008 | 29.7002
| GlencoeIce Accretion2070RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2070 | 15.4144 | 18.7314 | 22.88 | 26.0601 | 29.2219
| GlencoeIce Accretion2075RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2075 | 15.1973 | 18.5048 | 22.646 | 25.8103 | 28.9598
| GlencoeIce Accretion2080RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2080 | 14.9802 | 18.2783 | 22.412 | 25.5606 | 28.6978
| GlencoeIce Accretion2085RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2085 | 14.7631 | 18.0517 | 22.178 | 25.3109 | 28.4357
| GlencoeIce Accretion2090RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2090 | 14.1057 | 17.3287 | 21.372 | 24.4246 | 27.4747
| GlencoeIce Accretion2095RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2095 | 13.6655 | 16.8324 | 20.8 | 23.788 | 26.7758
| GlencoeIce Accretion2100RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2100 | 13.2253 | 16.3361 | 20.228 | 23.1514 | 26.077
| GlencoeIce Accretion2023RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2023 | 17.4226 | 20.911 | 25.324 | 28.6749 | 32.0393
| GlencoeIce Accretion2025RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2025 | 17.2839 | 20.7743 | 25.1853 | 28.5378 | 31.8973
| GlencoeIce Accretion2030RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2030 | 17.1452 | 20.6377 | 25.0467 | 28.4007 | 31.7554
| GlencoeIce Accretion2035RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2035 | 17.0065 | 20.501 | 24.908 | 28.2636 | 31.6134
| GlencoeIce Accretion2040RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2040 | 16.4758 | 19.9111 | 24.232 | 27.5291 | 30.8162
| GlencoeIce Accretion2045RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2045 | 15.9451 | 19.3213 | 23.556 | 26.7946 | 30.0191
| GlencoeIce Accretion2050RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2050 | 15.1249 | 18.4293 | 22.568 | 25.7271 | 28.8725
| GlencoeIce Accretion2055RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2055 | 14.8354 | 18.1272 | 22.256 | 25.3941 | 28.523
| GlencoeIce Accretion2060RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2060 | 14.1057 | 17.3287 | 21.372 | 24.4246 | 27.4747
| GlencoeIce Accretion2065RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2065 | 13.6655 | 16.8324 | 20.8 | 23.788 | 26.7758
| GlencoeIce Accretion2070RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2070 | 12.8815 | 15.962 | 19.8033 | 22.7009 | 25.5856
| GlencoeIce Accretion2075RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2075 | 12.5378 | 15.588 | 19.3787 | 22.2505 | 25.0942
| GlencoeIce Accretion2080RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2080 | 12.194 | 15.2139 | 18.954 | 21.8 | 24.6028
| GlencoeIce Accretion2085RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2085 | 11.3618 | 14.2212 | 17.771 | 20.4485 | 23.1122
| GlencoeIce Accretion2090RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2090 | 10.5295 | 13.2285 | 16.588 | 19.097 | 21.6216
| GlencoeIce Accretion2095RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2095 | 10.5295 | 13.2285 | 16.588 | 19.097 | 21.6216
| GlencoeIce Accretion2100RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2100 | 10.5295 | 13.2285 | 16.588 | 19.097 | 21.6216
| GlencoeWind2023RCP4.5 | Glencoe | Wind | RCP4.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
| GlencoeWind2025RCP4.5 | Glencoe | Wind | RCP4.5 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
| GlencoeWind2030RCP4.5 | Glencoe | Wind | RCP4.5 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
| GlencoeWind2035RCP4.5 | Glencoe | Wind | RCP4.5 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
| GlencoeWind2040RCP4.5 | Glencoe | Wind | RCP4.5 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
| GlencoeWind2045RCP4.5 | Glencoe | Wind | RCP4.5 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
| GlencoeWind2050RCP4.5 | Glencoe | Wind | RCP4.5 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
| GlencoeWind2055RCP4.5 | Glencoe | Wind | RCP4.5 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
| GlencoeWind2060RCP4.5 | Glencoe | Wind | RCP4.5 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
| GlencoeWind2065RCP4.5 | Glencoe | Wind | RCP4.5 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
| GlencoeWind2070RCP4.5 | Glencoe | Wind | RCP4.5 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
| GlencoeWind2075RCP4.5 | Glencoe | Wind | RCP4.5 | 2075 | 85.7411 | 92.542 | 99.746 | 106.9048 | 114.0736
| GlencoeWind2080RCP4.5 | Glencoe | Wind | RCP4.5 | 2080 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
| GlencoeWind2085RCP4.5 | Glencoe | Wind | RCP4.5 | 2085 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
| GlencoeWind2090RCP4.5 | Glencoe | Wind | RCP4.5 | 2090 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
| GlencoeWind2095RCP4.5 | Glencoe | Wind | RCP4.5 | 2095 | 86.3278 | 93.3015 | 100.7326 | 108.0792 | 115.444
| GlencoeWind2100RCP4.5 | Glencoe | Wind | RCP4.5 | 2100 | 86.4745 | 93.4914 | 100.9792 | 108.3728 | 115.7866
| GlencoeWind2023RCP6.0 | Glencoe | Wind | RCP6.0 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
| GlencoeWind2025RCP6.0 | Glencoe | Wind | RCP6.0 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
| GlencoeWind2030RCP6.0 | Glencoe | Wind | RCP6.0 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
| GlencoeWind2035RCP6.0 | Glencoe | Wind | RCP6.0 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
| GlencoeWind2040RCP6.0 | Glencoe | Wind | RCP6.0 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
| GlencoeWind2045RCP6.0 | Glencoe | Wind | RCP6.0 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
| GlencoeWind2050RCP6.0 | Glencoe | Wind | RCP6.0 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
| GlencoeWind2055RCP6.0 | Glencoe | Wind | RCP6.0 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
| GlencoeWind2060RCP6.0 | Glencoe | Wind | RCP6.0 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
| GlencoeWind2065RCP6.0 | Glencoe | Wind | RCP6.0 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
| GlencoeWind2070RCP6.0 | Glencoe | Wind | RCP6.0 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
| GlencoeWind2075RCP6.0 | Glencoe | Wind | RCP6.0 | 2075 | 85.8144 | 92.637 | 99.8693 | 107.0516 | 114.2449
| GlencoeWind2080RCP6.0 | Glencoe | Wind | RCP6.0 | 2080 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
| GlencoeWind2085RCP6.0 | Glencoe | Wind | RCP6.0 | 2085 | 86.2545 | 93.2066 | 100.6093 | 107.9324 | 115.2727
| GlencoeWind2090RCP6.0 | Glencoe | Wind | RCP6.0 | 2090 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
| GlencoeWind2095RCP6.0 | Glencoe | Wind | RCP6.0 | 2095 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
| GlencoeWind2100RCP6.0 | Glencoe | Wind | RCP6.0 | 2100 | 87.5746 | 94.8494 | 102.6452 | 110.3127 | 117.9987
| GlencoeWind2023RCP8.5 | Glencoe | Wind | RCP8.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
| GlencoeWind2025RCP8.5 | Glencoe | Wind | RCP8.5 | 2025 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
| GlencoeWind2030RCP8.5 | Glencoe | Wind | RCP8.5 | 2030 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
| GlencoeWind2035RCP8.5 | Glencoe | Wind | RCP8.5 | 2035 | 85.586 | 92.3248 | 99.4504 | 106.5378 | 113.6304
| GlencoeWind2040RCP8.5 | Glencoe | Wind | RCP8.5 | 2040 | 85.5888 | 92.3339 | 99.4667 | 106.5622 | 113.6639
| GlencoeWind2045RCP8.5 | Glencoe | Wind | RCP8.5 | 2045 | 85.5916 | 92.343 | 99.4831 | 106.5867 | 113.6974
| GlencoeWind2050RCP8.5 | Glencoe | Wind | RCP8.5 | 2050 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
| GlencoeWind2055RCP8.5 | Glencoe | Wind | RCP8.5 | 2055 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
| GlencoeWind2060RCP8.5 | Glencoe | Wind | RCP8.5 | 2060 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
| GlencoeWind2065RCP8.5 | Glencoe | Wind | RCP8.5 | 2065 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
| GlencoeWind2070RCP8.5 | Glencoe | Wind | RCP8.5 | 2070 | 87.882 | 95.2383 | 103.1385 | 110.8929 | 118.669
| GlencoeWind2075RCP8.5 | Glencoe | Wind | RCP8.5 | 2075 | 88.1895 | 95.6271 | 103.6317 | 111.4732 | 119.3393
| GlencoeWind2080RCP8.5 | Glencoe | Wind | RCP8.5 | 2080 | 88.4969 | 96.016 | 104.125 | 112.0534 | 120.0096
| GlencoeWind2085RCP8.5 | Glencoe | Wind | RCP8.5 | 2085 | 88.8396 | 96.4489 | 104.664 | 112.6826 | 120.7358
| GlencoeWind2090RCP8.5 | Glencoe | Wind | RCP8.5 | 2090 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
| GlencoeWind2095RCP8.5 | Glencoe | Wind | RCP8.5 | 2095 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
| GlencoeWind2100RCP8.5 | Glencoe | Wind | RCP8.5 | 2100 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
| GoderichIce Accretion2023RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2023 | 13.8195 | 16.5834 | 20.08 | 22.7582 | 25.4268
| GoderichIce Accretion2025RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2025 | 13.9076 | 16.6996 | 20.23 | 22.9315 | 25.6242
| GoderichIce Accretion2030RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2030 | 13.9958 | 16.8158 | 20.38 | 23.1047 | 25.8216
| GoderichIce Accretion2035RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2035 | 14.0839 | 16.932 | 20.53 | 23.278 | 26.019
| GoderichIce Accretion2040RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2040 | 14.1721 | 17.0482 | 20.68 | 23.4513 | 26.2164
| GoderichIce Accretion2045RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2045 | 14.2602 | 17.1644 | 20.83 | 23.6245 | 26.4138
| GoderichIce Accretion2050RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2050 | 14.3539 | 17.3072 | 21.036 | 23.8746 | 26.707
| GoderichIce Accretion2055RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2055 | 14.3595 | 17.3337 | 21.092 | 23.9515 | 26.8027
| GoderichIce Accretion2060RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2060 | 14.365 | 17.3603 | 21.148 | 24.0283 | 26.8985
| GoderichIce Accretion2065RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2065 | 14.3706 | 17.3868 | 21.204 | 24.1052 | 26.9942
| GoderichIce Accretion2070RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2070 | 14.3762 | 17.4134 | 21.26 | 24.182 | 27.09
| GoderichIce Accretion2075RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2075 | 14.2788 | 17.3138 | 21.1533 | 24.0728 | 26.9766
| GoderichIce Accretion2080RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2080 | 14.1813 | 17.2142 | 21.0467 | 23.9635 | 26.8632
| GoderichIce Accretion2085RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2085 | 14.0839 | 17.1146 | 20.94 | 23.8543 | 26.7498
| GoderichIce Accretion2090RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2090 | 13.9865 | 17.015 | 20.8333 | 23.7451 | 26.6364
| GoderichIce Accretion2095RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2095 | 13.8891 | 16.9154 | 20.7267 | 23.6358 | 26.523
| GoderichIce Accretion2100RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2100 | 13.7917 | 16.8158 | 20.62 | 23.5266 | 26.4096
| GoderichIce Accretion2023RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2023 | 13.8195 | 16.5834 | 20.08 | 22.7582 | 25.4268
| GoderichIce Accretion2025RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2025 | 13.9076 | 16.6996 | 20.23 | 22.9315 | 25.6242
| GoderichIce Accretion2030RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2030 | 13.9958 | 16.8158 | 20.38 | 23.1047 | 25.8216
| GoderichIce Accretion2035RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2035 | 14.0839 | 16.932 | 20.53 | 23.278 | 26.019
| GoderichIce Accretion2040RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2040 | 14.1721 | 17.0482 | 20.68 | 23.4513 | 26.2164
| GoderichIce Accretion2045RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2045 | 14.2602 | 17.1644 | 20.83 | 23.6245 | 26.4138
| GoderichIce Accretion2050RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2050 | 14.3539 | 17.3072 | 21.036 | 23.8746 | 26.707
| GoderichIce Accretion2055RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2055 | 14.3595 | 17.3337 | 21.092 | 23.9515 | 26.8027
| GoderichIce Accretion2060RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2060 | 14.365 | 17.3603 | 21.148 | 24.0283 | 26.8985
| GoderichIce Accretion2065RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2065 | 14.3706 | 17.3868 | 21.204 | 24.1052 | 26.9942
| GoderichIce Accretion2070RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2070 | 14.3762 | 17.4134 | 21.26 | 24.182 | 27.09
| GoderichIce Accretion2075RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2075 | 14.2301 | 17.264 | 21.1 | 24.0181 | 26.9199
| GoderichIce Accretion2080RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2080 | 14.0839 | 17.1146 | 20.94 | 23.8543 | 26.7498
| GoderichIce Accretion2085RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2085 | 13.9378 | 16.9652 | 20.78 | 23.6904 | 26.5797
| GoderichIce Accretion2090RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2090 | 13.4716 | 16.4617 | 20.22 | 23.0897 | 25.9308
| GoderichIce Accretion2095RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2095 | 13.1515 | 16.1075 | 19.82 | 22.6527 | 25.452
| GoderichIce Accretion2100RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2100 | 12.8314 | 15.7534 | 19.42 | 22.2158 | 24.9732
| GoderichIce Accretion2023RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2023 | 13.8195 | 16.5834 | 20.08 | 22.7582 | 25.4268
| GoderichIce Accretion2025RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2025 | 13.9958 | 16.8158 | 20.38 | 23.1047 | 25.8216
| GoderichIce Accretion2030RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2030 | 14.1721 | 17.0482 | 20.68 | 23.4513 | 26.2164
| GoderichIce Accretion2035RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2035 | 14.3483 | 17.2806 | 20.98 | 23.7978 | 26.6112
| GoderichIce Accretion2040RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2040 | 14.3576 | 17.3249 | 21.0733 | 23.9259 | 26.7708
| GoderichIce Accretion2045RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2045 | 14.3669 | 17.3691 | 21.1667 | 24.0539 | 26.9304
| GoderichIce Accretion2050RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2050 | 14.1813 | 17.2142 | 21.0467 | 23.9635 | 26.8632
| GoderichIce Accretion2055RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2055 | 13.9865 | 17.015 | 20.8333 | 23.7451 | 26.6364
| GoderichIce Accretion2060RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2060 | 13.4716 | 16.4617 | 20.22 | 23.0897 | 25.9308
| GoderichIce Accretion2065RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2065 | 13.1515 | 16.1075 | 19.82 | 22.6527 | 25.452
| GoderichIce Accretion2070RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2070 | 12.4 | 15.2665 | 18.8667 | 21.5981 | 24.3096
| GoderichIce Accretion2075RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2075 | 11.9686 | 14.7795 | 18.3133 | 20.9803 | 23.646
| GoderichIce Accretion2080RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2080 | 11.5371 | 14.2926 | 17.76 | 20.3626 | 22.9824
| GoderichIce Accretion2085RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2085 | 10.9665 | 13.6286 | 16.97 | 19.4925 | 22.0122
| GoderichIce Accretion2090RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2090 | 10.3959 | 12.9646 | 16.18 | 18.6224 | 21.042
| GoderichIce Accretion2095RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2095 | 10.3959 | 12.9646 | 16.18 | 18.6224 | 21.042
| GoderichIce Accretion2100RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2100 | 10.3959 | 12.9646 | 16.18 | 18.6224 | 21.042
| GoderichWind2023RCP4.5 | Goderich | Wind | RCP4.5 | 2023 | 86.1344 | 92.8894 | 100.0296 | 107.1482 | 114.2595
| GoderichWind2025RCP4.5 | Goderich | Wind | RCP4.5 | 2025 | 86.2014 | 92.9754 | 100.1402 | 107.2788 | 114.4137
| GoderichWind2030RCP4.5 | Goderich | Wind | RCP4.5 | 2030 | 86.2684 | 93.0613 | 100.2507 | 107.4095 | 114.5679
| GoderichWind2035RCP4.5 | Goderich | Wind | RCP4.5 | 2035 | 86.3353 | 93.1472 | 100.3612 | 107.5401 | 114.7222
| GoderichWind2040RCP4.5 | Goderich | Wind | RCP4.5 | 2040 | 86.4023 | 93.2332 | 100.4718 | 107.6708 | 114.8764
| GoderichWind2045RCP4.5 | Goderich | Wind | RCP4.5 | 2045 | 86.4693 | 93.3191 | 100.5823 | 107.8014 | 115.0307
| GoderichWind2050RCP4.5 | Goderich | Wind | RCP4.5 | 2050 | 86.5567 | 93.4271 | 100.7167 | 107.9575 | 115.212
| GoderichWind2055RCP4.5 | Goderich | Wind | RCP4.5 | 2055 | 86.5773 | 93.4492 | 100.7404 | 107.9829 | 115.2391
| GoderichWind2060RCP4.5 | Goderich | Wind | RCP4.5 | 2060 | 86.5978 | 93.4713 | 100.7642 | 108.0083 | 115.2662
| GoderichWind2065RCP4.5 | Goderich | Wind | RCP4.5 | 2065 | 86.6183 | 93.4934 | 100.7879 | 108.0338 | 115.2933
| GoderichWind2070RCP4.5 | Goderich | Wind | RCP4.5 | 2070 | 86.6388 | 93.5155 | 100.8117 | 108.0592 | 115.3203
| GoderichWind2075RCP4.5 | Goderich | Wind | RCP4.5 | 2075 | 86.7542 | 93.6674 | 101.0097 | 108.2958 | 115.5969
| GoderichWind2080RCP4.5 | Goderich | Wind | RCP4.5 | 2080 | 86.8696 | 93.8193 | 101.2077 | 108.5323 | 115.8734
| GoderichWind2085RCP4.5 | Goderich | Wind | RCP4.5 | 2085 | 86.985 | 93.9712 | 101.4057 | 108.7689 | 116.1499
| GoderichWind2090RCP4.5 | Goderich | Wind | RCP4.5 | 2090 | 87.1004 | 94.1232 | 101.6037 | 109.0055 | 116.4264
| GoderichWind2095RCP4.5 | Goderich | Wind | RCP4.5 | 2095 | 87.2158 | 94.2751 | 101.8017 | 109.2421 | 116.7029
| GoderichWind2100RCP4.5 | Goderich | Wind | RCP4.5 | 2100 | 87.3312 | 94.427 | 101.9997 | 109.4787 | 116.9794
| GoderichWind2023RCP6.0 | Goderich | Wind | RCP6.0 | 2023 | 86.1344 | 92.8894 | 100.0296 | 107.1482 | 114.2595
| GoderichWind2025RCP6.0 | Goderich | Wind | RCP6.0 | 2025 | 86.2014 | 92.9754 | 100.1402 | 107.2788 | 114.4137
| GoderichWind2030RCP6.0 | Goderich | Wind | RCP6.0 | 2030 | 86.2684 | 93.0613 | 100.2507 | 107.4095 | 114.5679
| GoderichWind2035RCP6.0 | Goderich | Wind | RCP6.0 | 2035 | 86.3353 | 93.1472 | 100.3612 | 107.5401 | 114.7222
| GoderichWind2040RCP6.0 | Goderich | Wind | RCP6.0 | 2040 | 86.4023 | 93.2332 | 100.4718 | 107.6708 | 114.8764
| GoderichWind2045RCP6.0 | Goderich | Wind | RCP6.0 | 2045 | 86.4693 | 93.3191 | 100.5823 | 107.8014 | 115.0307
| GoderichWind2050RCP6.0 | Goderich | Wind | RCP6.0 | 2050 | 86.5567 | 93.4271 | 100.7167 | 107.9575 | 115.212
| GoderichWind2055RCP6.0 | Goderich | Wind | RCP6.0 | 2055 | 86.5773 | 93.4492 | 100.7404 | 107.9829 | 115.2391
| GoderichWind2060RCP6.0 | Goderich | Wind | RCP6.0 | 2060 | 86.5978 | 93.4713 | 100.7642 | 108.0083 | 115.2662
| GoderichWind2065RCP6.0 | Goderich | Wind | RCP6.0 | 2065 | 86.6183 | 93.4934 | 100.7879 | 108.0338 | 115.2933
| GoderichWind2070RCP6.0 | Goderich | Wind | RCP6.0 | 2070 | 86.6388 | 93.5155 | 100.8117 | 108.0592 | 115.3203
| GoderichWind2075RCP6.0 | Goderich | Wind | RCP6.0 | 2075 | 86.8119 | 93.7434 | 101.1087 | 108.4141 | 115.7351
| GoderichWind2080RCP6.0 | Goderich | Wind | RCP6.0 | 2080 | 86.985 | 93.9712 | 101.4057 | 108.7689 | 116.1499
| GoderichWind2085RCP6.0 | Goderich | Wind | RCP6.0 | 2085 | 87.1581 | 94.1991 | 101.7027 | 109.1238 | 116.5646
| GoderichWind2090RCP6.0 | Goderich | Wind | RCP6.0 | 2090 | 87.7729 | 94.9794 | 102.6861 | 110.2837 | 117.9011
| GoderichWind2095RCP6.0 | Goderich | Wind | RCP6.0 | 2095 | 88.2146 | 95.5318 | 103.3725 | 111.0888 | 118.8228
| GoderichWind2100RCP6.0 | Goderich | Wind | RCP6.0 | 2100 | 88.6562 | 96.0843 | 104.0589 | 111.8939 | 119.7445
| GoderichWind2023RCP8.5 | Goderich | Wind | RCP8.5 | 2023 | 86.1344 | 92.8894 | 100.0296 | 107.1482 | 114.2595
| GoderichWind2025RCP8.5 | Goderich | Wind | RCP8.5 | 2025 | 86.2684 | 93.0613 | 100.2507 | 107.4095 | 114.5679
| GoderichWind2030RCP8.5 | Goderich | Wind | RCP8.5 | 2030 | 86.4023 | 93.2332 | 100.4718 | 107.6708 | 114.8764
| GoderichWind2035RCP8.5 | Goderich | Wind | RCP8.5 | 2035 | 86.5362 | 93.405 | 100.6929 | 107.9321 | 115.1849
| GoderichWind2040RCP8.5 | Goderich | Wind | RCP8.5 | 2040 | 86.5704 | 93.4418 | 100.7325 | 107.9744 | 115.2301
| GoderichWind2045RCP8.5 | Goderich | Wind | RCP8.5 | 2045 | 86.6046 | 93.4787 | 100.7721 | 108.0168 | 115.2752
| GoderichWind2050RCP8.5 | Goderich | Wind | RCP8.5 | 2050 | 86.8696 | 93.8193 | 101.2077 | 108.5323 | 115.8734
| GoderichWind2055RCP8.5 | Goderich | Wind | RCP8.5 | 2055 | 87.1004 | 94.1232 | 101.6037 | 109.0055 | 116.4264
| GoderichWind2060RCP8.5 | Goderich | Wind | RCP8.5 | 2060 | 87.7729 | 94.9794 | 102.6861 | 110.2837 | 117.9011
| GoderichWind2065RCP8.5 | Goderich | Wind | RCP8.5 | 2065 | 88.2146 | 95.5318 | 103.3725 | 111.0888 | 118.8228
| GoderichWind2070RCP8.5 | Goderich | Wind | RCP8.5 | 2070 | 88.8643 | 96.339 | 104.3757 | 112.2576 | 120.162
| GoderichWind2075RCP8.5 | Goderich | Wind | RCP8.5 | 2075 | 89.0723 | 96.5937 | 104.6925 | 112.6212 | 120.5796
| GoderichWind2080RCP8.5 | Goderich | Wind | RCP8.5 | 2080 | 89.2803 | 96.8484 | 105.0093 | 112.9849 | 120.9972
| GoderichWind2085RCP8.5 | Goderich | Wind | RCP8.5 | 2085 | 89.4171 | 97.0003 | 105.1776 | 113.1703 | 121.2004
| GoderichWind2090RCP8.5 | Goderich | Wind | RCP8.5 | 2090 | 89.5538 | 97.1523 | 105.3459 | 113.3557 | 121.4035
| GoderichWind2095RCP8.5 | Goderich | Wind | RCP8.5 | 2095 | 89.5538 | 97.1523 | 105.3459 | 113.3557 | 121.4035
| GoderichWind2100RCP8.5 | Goderich | Wind | RCP8.5 | 2100 | 89.5538 | 97.1523 | 105.3459 | 113.3557 | 121.4035
| Gore BayIce Accretion2023RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2023 | 15.6454 | 18.7165 | 22.594 | 25.5809 | 28.5516
| Gore BayIce Accretion2025RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2025 | 15.6148 | 18.6952 | 22.5793 | 25.5727 | 28.547
| Gore BayIce Accretion2030RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2030 | 15.5842 | 18.6739 | 22.5647 | 25.5644 | 28.5424
| Gore BayIce Accretion2035RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2035 | 15.5536 | 18.6526 | 22.55 | 25.5561 | 28.5377
| Gore BayIce Accretion2040RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2040 | 15.5229 | 18.6313 | 22.5353 | 25.5478 | 28.5331
| Gore BayIce Accretion2045RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2045 | 15.4923 | 18.61 | 22.5207 | 25.5395 | 28.5285
| Gore BayIce Accretion2050RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2050 | 15.5842 | 18.7494 | 22.7172 | 25.7798 | 28.8122
| Gore BayIce Accretion2055RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2055 | 15.7066 | 18.9101 | 22.9284 | 26.0284 | 29.1005
| Gore BayIce Accretion2060RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2060 | 15.8291 | 19.0707 | 23.1396 | 26.277 | 29.3887
| Gore BayIce Accretion2065RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2065 | 15.9516 | 19.2314 | 23.3508 | 26.5256 | 29.677
| Gore BayIce Accretion2070RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2070 | 16.074 | 19.3921 | 23.562 | 26.7742 | 29.9653
| Gore BayIce Accretion2075RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2075 | 15.972 | 19.2795 | 23.4447 | 26.6416 | 29.8267
| Gore BayIce Accretion2080RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2080 | 15.8699 | 19.1669 | 23.3273 | 26.509 | 29.6881
| Gore BayIce Accretion2085RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2085 | 15.7679 | 19.0543 | 23.21 | 26.3765 | 29.5495
| Gore BayIce Accretion2090RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2090 | 15.6658 | 18.9417 | 23.0927 | 26.2439 | 29.4109
| Gore BayIce Accretion2095RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2095 | 15.5638 | 18.8291 | 22.9753 | 26.1113 | 29.2723
| Gore BayIce Accretion2100RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2100 | 15.4617 | 18.7165 | 22.858 | 25.9787 | 29.1337
| Gore BayIce Accretion2023RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2023 | 15.6454 | 18.7165 | 22.594 | 25.5809 | 28.5516
| Gore BayIce Accretion2025RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2025 | 15.6148 | 18.6952 | 22.5793 | 25.5727 | 28.547
| Gore BayIce Accretion2030RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2030 | 15.5842 | 18.6739 | 22.5647 | 25.5644 | 28.5424
| Gore BayIce Accretion2035RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2035 | 15.5536 | 18.6526 | 22.55 | 25.5561 | 28.5377
| Gore BayIce Accretion2040RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2040 | 15.5229 | 18.6313 | 22.5353 | 25.5478 | 28.5331
| Gore BayIce Accretion2045RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2045 | 15.4923 | 18.61 | 22.5207 | 25.5395 | 28.5285
| Gore BayIce Accretion2050RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2050 | 15.5842 | 18.7494 | 22.7172 | 25.7798 | 28.8122
| Gore BayIce Accretion2055RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2055 | 15.7066 | 18.9101 | 22.9284 | 26.0284 | 29.1005
| Gore BayIce Accretion2060RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2060 | 15.8291 | 19.0707 | 23.1396 | 26.277 | 29.3887
| Gore BayIce Accretion2065RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2065 | 15.9516 | 19.2314 | 23.3508 | 26.5256 | 29.677
| Gore BayIce Accretion2070RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2070 | 16.074 | 19.3921 | 23.562 | 26.7742 | 29.9653
| Gore BayIce Accretion2075RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2075 | 15.921 | 19.2232 | 23.386 | 26.5753 | 29.7574
| Gore BayIce Accretion2080RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2080 | 15.7679 | 19.0543 | 23.21 | 26.3765 | 29.5495
| Gore BayIce Accretion2085RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2085 | 15.6148 | 18.8854 | 23.034 | 26.1776 | 29.3416
| Gore BayIce Accretion2090RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2090 | 15.5025 | 18.7835 | 22.9533 | 26.103 | 29.2723
| Gore BayIce Accretion2095RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2095 | 15.5433 | 18.8504 | 23.0487 | 26.2273 | 29.4109
| Gore BayIce Accretion2100RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2100 | 15.5842 | 18.9174 | 23.144 | 26.3516 | 29.5495
| Gore BayIce Accretion2023RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2023 | 15.6454 | 18.7165 | 22.594 | 25.5809 | 28.5516
| Gore BayIce Accretion2025RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2025 | 15.5842 | 18.6739 | 22.5647 | 25.5644 | 28.5424
| Gore BayIce Accretion2030RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2030 | 15.5229 | 18.6313 | 22.5353 | 25.5478 | 28.5331
| Gore BayIce Accretion2035RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2035 | 15.4617 | 18.5887 | 22.506 | 25.5312 | 28.5239
| Gore BayIce Accretion2040RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2040 | 15.6658 | 18.8565 | 22.858 | 25.9456 | 29.0044
| Gore BayIce Accretion2045RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2045 | 15.8699 | 19.1243 | 23.21 | 26.3599 | 29.4848
| Gore BayIce Accretion2050RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2050 | 15.8699 | 19.1669 | 23.3273 | 26.509 | 29.6881
| Gore BayIce Accretion2055RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2055 | 15.6658 | 18.9417 | 23.0927 | 26.2439 | 29.4109
| Gore BayIce Accretion2060RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2060 | 15.5025 | 18.7835 | 22.9533 | 26.103 | 29.2723
| Gore BayIce Accretion2065RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2065 | 15.5433 | 18.8504 | 23.0487 | 26.2273 | 29.4109
| Gore BayIce Accretion2070RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2070 | 15.0586 | 18.3087 | 22.418 | 25.5395 | 28.6532
| Gore BayIce Accretion2075RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2075 | 14.533 | 17.7 | 21.692 | 24.7274 | 27.757
| Gore BayIce Accretion2080RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2080 | 14.0074 | 17.0914 | 20.966 | 23.9153 | 26.8607
| Gore BayIce Accretion2085RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2085 | 13.7012 | 16.7535 | 20.592 | 23.5051 | 26.4172
| Gore BayIce Accretion2090RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2090 | 13.395 | 16.4157 | 20.218 | 23.0949 | 25.9736
| Gore BayIce Accretion2095RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2095 | 13.395 | 16.4157 | 20.218 | 23.0949 | 25.9736
| Gore BayIce Accretion2100RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2100 | 13.395 | 16.4157 | 20.218 | 23.0949 | 25.9736
| Gore BayWind2023RCP4.5 | Gore Bay | Wind | RCP4.5 | 2023 | 82.605 | 88.9773 | 95.684 | 102.4022 | 109.1014
| Gore BayWind2025RCP4.5 | Gore Bay | Wind | RCP4.5 | 2025 | 82.7062 | 89.0966 | 95.8249 | 102.5598 | 109.2801
| Gore BayWind2030RCP4.5 | Gore Bay | Wind | RCP4.5 | 2030 | 82.8074 | 89.2158 | 95.9658 | 102.7173 | 109.4588
| Gore BayWind2035RCP4.5 | Gore Bay | Wind | RCP4.5 | 2035 | 82.9086 | 89.3351 | 96.1068 | 102.8749 | 109.6375
| Gore BayWind2040RCP4.5 | Gore Bay | Wind | RCP4.5 | 2040 | 83.0097 | 89.4544 | 96.2477 | 103.0324 | 109.8162
| Gore BayWind2045RCP4.5 | Gore Bay | Wind | RCP4.5 | 2045 | 83.1109 | 89.5736 | 96.3886 | 103.19 | 109.9949
| Gore BayWind2050RCP4.5 | Gore Bay | Wind | RCP4.5 | 2050 | 83.281 | 89.7777 | 96.6321 | 103.4675 | 110.3079
| Gore BayWind2055RCP4.5 | Gore Bay | Wind | RCP4.5 | 2055 | 83.3499 | 89.8626 | 96.7347 | 103.5874 | 110.4422
| Gore BayWind2060RCP4.5 | Gore Bay | Wind | RCP4.5 | 2060 | 83.4188 | 89.9474 | 96.8373 | 103.7074 | 110.5765
| Gore BayWind2065RCP4.5 | Gore Bay | Wind | RCP4.5 | 2065 | 83.4877 | 90.0322 | 96.9399 | 103.8273 | 110.7108
| Gore BayWind2070RCP4.5 | Gore Bay | Wind | RCP4.5 | 2070 | 83.5566 | 90.117 | 97.0425 | 103.9473 | 110.8451
| Gore BayWind2075RCP4.5 | Gore Bay | Wind | RCP4.5 | 2075 | 83.6072 | 90.1877 | 97.1391 | 104.0642 | 110.984
| Gore BayWind2080RCP4.5 | Gore Bay | Wind | RCP4.5 | 2080 | 83.6578 | 90.2584 | 97.2357 | 104.1811 | 111.123
| Gore BayWind2085RCP4.5 | Gore Bay | Wind | RCP4.5 | 2085 | 83.7084 | 90.329 | 97.3323 | 104.298 | 111.262
| Gore BayWind2090RCP4.5 | Gore Bay | Wind | RCP4.5 | 2090 | 83.7589 | 90.3997 | 97.4288 | 104.4149 | 111.401
| Gore BayWind2095RCP4.5 | Gore Bay | Wind | RCP4.5 | 2095 | 83.8095 | 90.4704 | 97.5254 | 104.5318 | 111.54
| Gore BayWind2100RCP4.5 | Gore Bay | Wind | RCP4.5 | 2100 | 83.8601 | 90.5411 | 97.622 | 104.6487 | 111.679
| Gore BayWind2023RCP6.0 | Gore Bay | Wind | RCP6.0 | 2023 | 82.605 | 88.9773 | 95.684 | 102.4022 | 109.1014
| Gore BayWind2025RCP6.0 | Gore Bay | Wind | RCP6.0 | 2025 | 82.7062 | 89.0966 | 95.8249 | 102.5598 | 109.2801
| Gore BayWind2030RCP6.0 | Gore Bay | Wind | RCP6.0 | 2030 | 82.8074 | 89.2158 | 95.9658 | 102.7173 | 109.4588
| Gore BayWind2035RCP6.0 | Gore Bay | Wind | RCP6.0 | 2035 | 82.9086 | 89.3351 | 96.1068 | 102.8749 | 109.6375
| Gore BayWind2040RCP6.0 | Gore Bay | Wind | RCP6.0 | 2040 | 83.0097 | 89.4544 | 96.2477 | 103.0324 | 109.8162
| Gore BayWind2045RCP6.0 | Gore Bay | Wind | RCP6.0 | 2045 | 83.1109 | 89.5736 | 96.3886 | 103.19 | 109.9949
| Gore BayWind2050RCP6.0 | Gore Bay | Wind | RCP6.0 | 2050 | 83.281 | 89.7777 | 96.6321 | 103.4675 | 110.3079
| Gore BayWind2055RCP6.0 | Gore Bay | Wind | RCP6.0 | 2055 | 83.3499 | 89.8626 | 96.7347 | 103.5874 | 110.4422
| Gore BayWind2060RCP6.0 | Gore Bay | Wind | RCP6.0 | 2060 | 83.4188 | 89.9474 | 96.8373 | 103.7074 | 110.5765
| Gore BayWind2065RCP6.0 | Gore Bay | Wind | RCP6.0 | 2065 | 83.4877 | 90.0322 | 96.9399 | 103.8273 | 110.7108
| Gore BayWind2070RCP6.0 | Gore Bay | Wind | RCP6.0 | 2070 | 83.5566 | 90.117 | 97.0425 | 103.9473 | 110.8451
| Gore BayWind2075RCP6.0 | Gore Bay | Wind | RCP6.0 | 2075 | 83.6325 | 90.223 | 97.1874 | 104.1226 | 111.0535
| Gore BayWind2080RCP6.0 | Gore Bay | Wind | RCP6.0 | 2080 | 83.7084 | 90.329 | 97.3323 | 104.298 | 111.262
| Gore BayWind2085RCP6.0 | Gore Bay | Wind | RCP6.0 | 2085 | 83.7842 | 90.4351 | 97.4771 | 104.4733 | 111.4705
| Gore BayWind2090RCP6.0 | Gore Bay | Wind | RCP6.0 | 2090 | 84.0652 | 90.8032 | 97.9577 | 105.0451 | 112.141
| Gore BayWind2095RCP6.0 | Gore Bay | Wind | RCP6.0 | 2095 | 84.2703 | 91.0653 | 98.2933 | 105.4415 | 112.6031
| Gore BayWind2100RCP6.0 | Gore Bay | Wind | RCP6.0 | 2100 | 84.4753 | 91.3274 | 98.629 | 105.838 | 113.0652
| Gore BayWind2023RCP8.5 | Gore Bay | Wind | RCP8.5 | 2023 | 82.605 | 88.9773 | 95.684 | 102.4022 | 109.1014
| Gore BayWind2025RCP8.5 | Gore Bay | Wind | RCP8.5 | 2025 | 82.8074 | 89.2158 | 95.9658 | 102.7173 | 109.4588
| Gore BayWind2030RCP8.5 | Gore Bay | Wind | RCP8.5 | 2030 | 83.0097 | 89.4544 | 96.2477 | 103.0324 | 109.8162
| Gore BayWind2035RCP8.5 | Gore Bay | Wind | RCP8.5 | 2035 | 83.2121 | 89.6929 | 96.5295 | 103.3476 | 110.1736
| Gore BayWind2040RCP8.5 | Gore Bay | Wind | RCP8.5 | 2040 | 83.3269 | 89.8343 | 96.7005 | 103.5475 | 110.3974
| Gore BayWind2045RCP8.5 | Gore Bay | Wind | RCP8.5 | 2045 | 83.4418 | 89.9756 | 96.8715 | 103.7474 | 110.6212
| Gore BayWind2050RCP8.5 | Gore Bay | Wind | RCP8.5 | 2050 | 83.6578 | 90.2584 | 97.2357 | 104.1811 | 111.123
| Gore BayWind2055RCP8.5 | Gore Bay | Wind | RCP8.5 | 2055 | 83.7589 | 90.3997 | 97.4288 | 104.4149 | 111.401
| Gore BayWind2060RCP8.5 | Gore Bay | Wind | RCP8.5 | 2060 | 84.0652 | 90.8032 | 97.9577 | 105.0451 | 112.141
| Gore BayWind2065RCP8.5 | Gore Bay | Wind | RCP8.5 | 2065 | 84.2703 | 91.0653 | 98.2933 | 105.4415 | 112.6031
| Gore BayWind2070RCP8.5 | Gore Bay | Wind | RCP8.5 | 2070 | 84.7324 | 91.6572 | 99.0438 | 106.3259 | 113.6284
| Gore BayWind2075RCP8.5 | Gore Bay | Wind | RCP8.5 | 2075 | 84.9894 | 91.9871 | 99.4587 | 106.8138 | 114.1915
| Gore BayWind2080RCP8.5 | Gore Bay | Wind | RCP8.5 | 2080 | 85.2464 | 92.3169 | 99.8735 | 107.3017 | 114.7547
| Gore BayWind2085RCP8.5 | Gore Bay | Wind | RCP8.5 | 2085 | 85.5664 | 92.7233 | 100.3912 | 107.9116 | 115.4586
| Gore BayWind2090RCP8.5 | Gore Bay | Wind | RCP8.5 | 2090 | 85.8863 | 93.1297 | 100.909 | 108.5215 | 116.1626
| Gore BayWind2095RCP8.5 | Gore Bay | Wind | RCP8.5 | 2095 | 85.8863 | 93.1297 | 100.909 | 108.5215 | 116.1626
| Gore BayWind2100RCP8.5 | Gore Bay | Wind | RCP8.5 | 2100 | 85.8863 | 93.1297 | 100.909 | 108.5215 | 116.1626
| GrahamIce Accretion2023RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2023 | 10.6464 | 12.7114 | 15.33 | 17.3229 | 19.3347
| GrahamIce Accretion2025RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2025 | 10.7195 | 12.8007 | 15.44 | 17.45 | 19.4764
| GrahamIce Accretion2030RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2030 | 10.7926 | 12.8899 | 15.55 | 17.5771 | 19.6182
| GrahamIce Accretion2035RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2035 | 10.8656 | 12.9791 | 15.66 | 17.7043 | 19.7599
| GrahamIce Accretion2040RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2040 | 10.9387 | 13.0683 | 15.77 | 17.8314 | 19.9017
| GrahamIce Accretion2045RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2045 | 11.0118 | 13.1576 | 15.88 | 17.9585 | 20.0434
| GrahamIce Accretion2050RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2050 | 11.0473 | 13.1945 | 15.918 | 18.0009 | 20.0869
| GrahamIce Accretion2055RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2055 | 11.0097 | 13.1422 | 15.846 | 17.9161 | 19.9886
| GrahamIce Accretion2060RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2060 | 10.9721 | 13.0899 | 15.774 | 17.8314 | 19.8904
| GrahamIce Accretion2065RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2065 | 10.9345 | 13.0376 | 15.702 | 17.7466 | 19.7921
| GrahamIce Accretion2070RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2070 | 10.897 | 12.9853 | 15.63 | 17.6619 | 19.6938
| GrahamIce Accretion2075RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2075 | 10.9561 | 13.058 | 15.72 | 17.7636 | 19.8072
| GrahamIce Accretion2080RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2080 | 11.0152 | 13.1306 | 15.81 | 17.8653 | 19.9206
| GrahamIce Accretion2085RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2085 | 11.0744 | 13.2032 | 15.9 | 17.967 | 20.034
| GrahamIce Accretion2090RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2090 | 11.1335 | 13.2759 | 15.99 | 18.0687 | 20.1474
| GrahamIce Accretion2095RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2095 | 11.1927 | 13.3485 | 16.08 | 18.1704 | 20.2608
| GrahamIce Accretion2100RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2100 | 11.2518 | 13.4211 | 16.17 | 18.2721 | 20.3742
| GrahamIce Accretion2023RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2023 | 10.6464 | 12.7114 | 15.33 | 17.3229 | 19.3347
| GrahamIce Accretion2025RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2025 | 10.7195 | 12.8007 | 15.44 | 17.45 | 19.4764
| GrahamIce Accretion2030RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2030 | 10.7926 | 12.8899 | 15.55 | 17.5771 | 19.6182
| GrahamIce Accretion2035RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2035 | 10.8656 | 12.9791 | 15.66 | 17.7043 | 19.7599
| GrahamIce Accretion2040RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2040 | 10.9387 | 13.0683 | 15.77 | 17.8314 | 19.9017
| GrahamIce Accretion2045RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2045 | 11.0118 | 13.1576 | 15.88 | 17.9585 | 20.0434
| GrahamIce Accretion2050RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2050 | 11.0473 | 13.1945 | 15.918 | 18.0009 | 20.0869
| GrahamIce Accretion2055RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2055 | 11.0097 | 13.1422 | 15.846 | 17.9161 | 19.9886
| GrahamIce Accretion2060RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2060 | 10.9721 | 13.0899 | 15.774 | 17.8314 | 19.8904
| GrahamIce Accretion2065RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2065 | 10.9345 | 13.0376 | 15.702 | 17.7466 | 19.7921
| GrahamIce Accretion2070RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2070 | 10.897 | 12.9853 | 15.63 | 17.6619 | 19.6938
| GrahamIce Accretion2075RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2075 | 10.9857 | 13.0943 | 15.765 | 17.8145 | 19.8639
| GrahamIce Accretion2080RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2080 | 11.0744 | 13.2032 | 15.9 | 17.967 | 20.034
| GrahamIce Accretion2085RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2085 | 11.1631 | 13.3122 | 16.035 | 18.1196 | 20.2041
| GrahamIce Accretion2090RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2090 | 11.1857 | 13.3422 | 16.075 | 18.1648 | 20.2545
| GrahamIce Accretion2095RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2095 | 11.1196 | 13.2634 | 15.98 | 18.0574 | 20.1348
| GrahamIce Accretion2100RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2100 | 11.0535 | 13.1845 | 15.885 | 17.95 | 20.0151
| GrahamIce Accretion2023RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2023 | 10.6464 | 12.7114 | 15.33 | 17.3229 | 19.3347
| GrahamIce Accretion2025RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2025 | 10.7926 | 12.8899 | 15.55 | 17.5771 | 19.6182
| GrahamIce Accretion2030RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2030 | 10.9387 | 13.0683 | 15.77 | 17.8314 | 19.9017
| GrahamIce Accretion2035RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2035 | 11.0848 | 13.2468 | 15.99 | 18.0856 | 20.1852
| GrahamIce Accretion2040RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2040 | 11.0222 | 13.1596 | 15.87 | 17.9444 | 20.0214
| GrahamIce Accretion2045RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2045 | 10.9596 | 13.0725 | 15.75 | 17.8031 | 19.8576
| GrahamIce Accretion2050RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2050 | 11.0152 | 13.1306 | 15.81 | 17.8653 | 19.9206
| GrahamIce Accretion2055RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2055 | 11.1335 | 13.2759 | 15.99 | 18.0687 | 20.1474
| GrahamIce Accretion2060RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2060 | 11.1857 | 13.3422 | 16.075 | 18.1648 | 20.2545
| GrahamIce Accretion2065RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2065 | 11.1196 | 13.2634 | 15.98 | 18.0574 | 20.1348
| GrahamIce Accretion2070RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2070 | 11.0779 | 13.226 | 15.95 | 18.0291 | 20.1096
| GrahamIce Accretion2075RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2075 | 11.1022 | 13.2675 | 16.015 | 18.1082 | 20.2041
| GrahamIce Accretion2080RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2080 | 11.1266 | 13.309 | 16.08 | 18.1873 | 20.2986
| GrahamIce Accretion2085RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2085 | 10.85 | 12.9916 | 15.705 | 17.7721 | 19.845
| GrahamIce Accretion2090RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2090 | 10.5734 | 12.6741 | 15.33 | 17.3568 | 19.3914
| GrahamIce Accretion2095RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2095 | 10.5734 | 12.6741 | 15.33 | 17.3568 | 19.3914
| GrahamIce Accretion2100RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2100 | 10.5734 | 12.6741 | 15.33 | 17.3568 | 19.3914
| GrahamWind2023RCP4.5 | Graham | Wind | RCP4.5 | 2023 | 72.6486 | 78.2841 | 84.2184 | 90.1496 | 96.076
| GrahamWind2025RCP4.5 | Graham | Wind | RCP4.5 | 2025 | 72.7163 | 78.3622 | 84.3122 | 90.2545 | 96.1941
| GrahamWind2030RCP4.5 | Graham | Wind | RCP4.5 | 2030 | 72.784 | 78.4403 | 84.406 | 90.3594 | 96.3122
| GrahamWind2035RCP4.5 | Graham | Wind | RCP4.5 | 2035 | 72.8517 | 78.5184 | 84.4998 | 90.4642 | 96.4303
| GrahamWind2040RCP4.5 | Graham | Wind | RCP4.5 | 2040 | 72.9194 | 78.5965 | 84.5936 | 90.5691 | 96.5484
| GrahamWind2045RCP4.5 | Graham | Wind | RCP4.5 | 2045 | 72.9871 | 78.6747 | 84.6874 | 90.6739 | 96.6665
| GrahamWind2050RCP4.5 | Graham | Wind | RCP4.5 | 2050 | 73.1041 | 78.82 | 84.8669 | 90.8831 | 96.9072
| GrahamWind2055RCP4.5 | Graham | Wind | RCP4.5 | 2055 | 73.1534 | 78.8871 | 84.9526 | 90.9873 | 97.0298
| GrahamWind2060RCP4.5 | Graham | Wind | RCP4.5 | 2060 | 73.2027 | 78.9543 | 85.0382 | 91.0916 | 97.1524
| GrahamWind2065RCP4.5 | Graham | Wind | RCP4.5 | 2065 | 73.252 | 79.0215 | 85.1239 | 91.1958 | 97.2749
| GrahamWind2070RCP4.5 | Graham | Wind | RCP4.5 | 2070 | 73.3014 | 79.0887 | 85.2096 | 91.3001 | 97.3975
| GrahamWind2075RCP4.5 | Graham | Wind | RCP4.5 | 2075 | 73.3981 | 79.2033 | 85.3454 | 91.4544 | 97.5699
| GrahamWind2080RCP4.5 | Graham | Wind | RCP4.5 | 2080 | 73.4948 | 79.3178 | 85.4812 | 91.6087 | 97.7422
| GrahamWind2085RCP4.5 | Graham | Wind | RCP4.5 | 2085 | 73.5915 | 79.4324 | 85.617 | 91.763 | 97.9146
| GrahamWind2090RCP4.5 | Graham | Wind | RCP4.5 | 2090 | 73.6882 | 79.547 | 85.7528 | 91.9173 | 98.087
| GrahamWind2095RCP4.5 | Graham | Wind | RCP4.5 | 2095 | 73.7849 | 79.6616 | 85.8886 | 92.0716 | 98.2593
| GrahamWind2100RCP4.5 | Graham | Wind | RCP4.5 | 2100 | 73.8816 | 79.7761 | 86.0244 | 92.2259 | 98.4317
| GrahamWind2023RCP6.0 | Graham | Wind | RCP6.0 | 2023 | 72.6486 | 78.2841 | 84.2184 | 90.1496 | 96.076
| GrahamWind2025RCP6.0 | Graham | Wind | RCP6.0 | 2025 | 72.7163 | 78.3622 | 84.3122 | 90.2545 | 96.1941
| GrahamWind2030RCP6.0 | Graham | Wind | RCP6.0 | 2030 | 72.784 | 78.4403 | 84.406 | 90.3594 | 96.3122
| GrahamWind2035RCP6.0 | Graham | Wind | RCP6.0 | 2035 | 72.8517 | 78.5184 | 84.4998 | 90.4642 | 96.4303
| GrahamWind2040RCP6.0 | Graham | Wind | RCP6.0 | 2040 | 72.9194 | 78.5965 | 84.5936 | 90.5691 | 96.5484
| GrahamWind2045RCP6.0 | Graham | Wind | RCP6.0 | 2045 | 72.9871 | 78.6747 | 84.6874 | 90.6739 | 96.6665
| GrahamWind2050RCP6.0 | Graham | Wind | RCP6.0 | 2050 | 73.1041 | 78.82 | 84.8669 | 90.8831 | 96.9072
| GrahamWind2055RCP6.0 | Graham | Wind | RCP6.0 | 2055 | 73.1534 | 78.8871 | 84.9526 | 90.9873 | 97.0298
| GrahamWind2060RCP6.0 | Graham | Wind | RCP6.0 | 2060 | 73.2027 | 78.9543 | 85.0382 | 91.0916 | 97.1524
| GrahamWind2065RCP6.0 | Graham | Wind | RCP6.0 | 2065 | 73.252 | 79.0215 | 85.1239 | 91.1958 | 97.2749
| GrahamWind2070RCP6.0 | Graham | Wind | RCP6.0 | 2070 | 73.3014 | 79.0887 | 85.2096 | 91.3001 | 97.3975
| GrahamWind2075RCP6.0 | Graham | Wind | RCP6.0 | 2075 | 73.4464 | 79.2606 | 85.4133 | 91.5315 | 97.656
| GrahamWind2080RCP6.0 | Graham | Wind | RCP6.0 | 2080 | 73.5915 | 79.4324 | 85.617 | 91.763 | 97.9146
| GrahamWind2085RCP6.0 | Graham | Wind | RCP6.0 | 2085 | 73.7366 | 79.6043 | 85.8207 | 91.9944 | 98.1732
| GrahamWind2090RCP6.0 | Graham | Wind | RCP6.0 | 2090 | 73.9783 | 79.9089 | 86.2064 | 92.4476 | 98.6934
| GrahamWind2095RCP6.0 | Graham | Wind | RCP6.0 | 2095 | 74.075 | 80.0418 | 86.3884 | 92.6693 | 98.9552
| GrahamWind2100RCP6.0 | Graham | Wind | RCP6.0 | 2100 | 74.1718 | 80.1746 | 86.5704 | 92.891 | 99.2169
| GrahamWind2023RCP8.5 | Graham | Wind | RCP8.5 | 2023 | 72.6486 | 78.2841 | 84.2184 | 90.1496 | 96.076
| GrahamWind2025RCP8.5 | Graham | Wind | RCP8.5 | 2025 | 72.784 | 78.4403 | 84.406 | 90.3594 | 96.3122
| GrahamWind2030RCP8.5 | Graham | Wind | RCP8.5 | 2030 | 72.9194 | 78.5965 | 84.5936 | 90.5691 | 96.5484
| GrahamWind2035RCP8.5 | Graham | Wind | RCP8.5 | 2035 | 73.0548 | 78.7528 | 84.7812 | 90.7788 | 96.7846
| GrahamWind2040RCP8.5 | Graham | Wind | RCP8.5 | 2040 | 73.137 | 78.8647 | 84.924 | 90.9526 | 96.9889
| GrahamWind2045RCP8.5 | Graham | Wind | RCP8.5 | 2045 | 73.2192 | 78.9767 | 85.0668 | 91.1263 | 97.1932
| GrahamWind2050RCP8.5 | Graham | Wind | RCP8.5 | 2050 | 73.4948 | 79.3178 | 85.4812 | 91.6087 | 97.7422
| GrahamWind2055RCP8.5 | Graham | Wind | RCP8.5 | 2055 | 73.6882 | 79.547 | 85.7528 | 91.9173 | 98.087
| GrahamWind2060RCP8.5 | Graham | Wind | RCP8.5 | 2060 | 73.9783 | 79.9089 | 86.2064 | 92.4476 | 98.6934
| GrahamWind2065RCP8.5 | Graham | Wind | RCP8.5 | 2065 | 74.075 | 80.0418 | 86.3884 | 92.6693 | 98.9552
| GrahamWind2070RCP8.5 | Graham | Wind | RCP8.5 | 2070 | 74.3942 | 80.4324 | 86.87 | 93.2295 | 99.5936
| GrahamWind2075RCP8.5 | Graham | Wind | RCP8.5 | 2075 | 74.6166 | 80.6901 | 87.1696 | 93.5681 | 99.9702
| GrahamWind2080RCP8.5 | Graham | Wind | RCP8.5 | 2080 | 74.8391 | 80.9479 | 87.4692 | 93.9066 | 100.3469
| GrahamWind2085RCP8.5 | Graham | Wind | RCP8.5 | 2085 | 74.8282 | 80.905 | 87.3894 | 93.7943 | 100.2081
| GrahamWind2090RCP8.5 | Graham | Wind | RCP8.5 | 2090 | 74.8173 | 80.862 | 87.3096 | 93.6819 | 100.0692
| GrahamWind2095RCP8.5 | Graham | Wind | RCP8.5 | 2095 | 74.8173 | 80.862 | 87.3096 | 93.6819 | 100.0692
| GrahamWind2100RCP8.5 | Graham | Wind | RCP8.5 | 2100 | 74.8173 | 80.862 | 87.3096 | 93.6819 | 100.0692
| Gravenhurst (Muskoka Airport)Ice Accretion2023RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2023 | 14.3351 | 17.0988 | 20.601 | 23.2791 | 25.9837
| Gravenhurst (Muskoka Airport)Ice Accretion2025RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2025 | 14.3181 | 17.0872 | 20.594 | 23.2791 | 25.9837
| Gravenhurst (Muskoka Airport)Ice Accretion2030RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2030 | 14.301 | 17.0756 | 20.587 | 23.2791 | 25.9837
| Gravenhurst (Muskoka Airport)Ice Accretion2035RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2035 | 14.284 | 17.064 | 20.58 | 23.2791 | 25.9837
| Gravenhurst (Muskoka Airport)Ice Accretion2040RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2040 | 14.2669 | 17.0524 | 20.573 | 23.2791 | 25.9837
| Gravenhurst (Muskoka Airport)Ice Accretion2045RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2045 | 14.2499 | 17.0407 | 20.566 | 23.2791 | 25.9837
| Gravenhurst (Muskoka Airport)Ice Accretion2050RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2050 | 14.2299 | 17.0396 | 20.5926 | 23.3218 | 26.0419
| Gravenhurst (Muskoka Airport)Ice Accretion2055RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2055 | 14.227 | 17.05 | 20.6262 | 23.3646 | 26.1001
| Gravenhurst (Muskoka Airport)Ice Accretion2060RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2060 | 14.2241 | 17.0605 | 20.6598 | 23.4073 | 26.1584
| Gravenhurst (Muskoka Airport)Ice Accretion2065RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2065 | 14.2211 | 17.0709 | 20.6934 | 23.45 | 26.2166
| Gravenhurst (Muskoka Airport)Ice Accretion2070RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2070 | 14.2182 | 17.0814 | 20.727 | 23.4927 | 26.2748
| Gravenhurst (Muskoka Airport)Ice Accretion2075RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2075 | 14.2596 | 17.1482 | 20.8215 | 23.6074 | 26.4115
| Gravenhurst (Muskoka Airport)Ice Accretion2080RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2080 | 14.301 | 17.215 | 20.916 | 23.7221 | 26.5482
| Gravenhurst (Muskoka Airport)Ice Accretion2085RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2085 | 14.3424 | 17.2818 | 21.0105 | 23.8368 | 26.6849
| Gravenhurst (Muskoka Airport)Ice Accretion2090RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2090 | 14.3838 | 17.3487 | 21.105 | 23.9515 | 26.8216
| Gravenhurst (Muskoka Airport)Ice Accretion2095RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2095 | 14.4252 | 17.4155 | 21.1995 | 24.0662 | 26.9583
| Gravenhurst (Muskoka Airport)Ice Accretion2100RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2100 | 14.4666 | 17.4823 | 21.294 | 24.1809 | 27.095
| Gravenhurst (Muskoka Airport)Ice Accretion2023RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2023 | 14.3351 | 17.0988 | 20.601 | 23.2791 | 25.9837
| Gravenhurst (Muskoka Airport)Ice Accretion2025RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2025 | 14.3181 | 17.0872 | 20.594 | 23.2791 | 25.9837
| Gravenhurst (Muskoka Airport)Ice Accretion2030RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2030 | 14.301 | 17.0756 | 20.587 | 23.2791 | 25.9837
| Gravenhurst (Muskoka Airport)Ice Accretion2035RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2035 | 14.284 | 17.064 | 20.58 | 23.2791 | 25.9837
| Gravenhurst (Muskoka Airport)Ice Accretion2040RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2040 | 14.2669 | 17.0524 | 20.573 | 23.2791 | 25.9837
| Gravenhurst (Muskoka Airport)Ice Accretion2045RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2045 | 14.2499 | 17.0407 | 20.566 | 23.2791 | 25.9837
| Gravenhurst (Muskoka Airport)Ice Accretion2050RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2050 | 14.2299 | 17.0396 | 20.5926 | 23.3218 | 26.0419
| Gravenhurst (Muskoka Airport)Ice Accretion2055RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2055 | 14.227 | 17.05 | 20.6262 | 23.3646 | 26.1001
| Gravenhurst (Muskoka Airport)Ice Accretion2060RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2060 | 14.2241 | 17.0605 | 20.6598 | 23.4073 | 26.1584
| Gravenhurst (Muskoka Airport)Ice Accretion2065RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2065 | 14.2211 | 17.0709 | 20.6934 | 23.45 | 26.2166
| Gravenhurst (Muskoka Airport)Ice Accretion2070RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2070 | 14.2182 | 17.0814 | 20.727 | 23.4927 | 26.2748
| Gravenhurst (Muskoka Airport)Ice Accretion2075RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2075 | 14.2803 | 17.1816 | 20.8687 | 23.6647 | 26.4798
| Gravenhurst (Muskoka Airport)Ice Accretion2080RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2080 | 14.3424 | 17.2818 | 21.0105 | 23.8368 | 26.6849
| Gravenhurst (Muskoka Airport)Ice Accretion2085RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2085 | 14.4045 | 17.3821 | 21.1523 | 24.0088 | 26.89
| Gravenhurst (Muskoka Airport)Ice Accretion2090RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2090 | 14.4423 | 17.4939 | 21.35 | 24.2758 | 27.2185
| Gravenhurst (Muskoka Airport)Ice Accretion2095RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2095 | 14.4179 | 17.5055 | 21.406 | 24.3707 | 27.342
| Gravenhurst (Muskoka Airport)Ice Accretion2100RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2100 | 14.3936 | 17.5171 | 21.462 | 24.4656 | 27.4655
| Gravenhurst (Muskoka Airport)Ice Accretion2023RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2023 | 14.3351 | 17.0988 | 20.601 | 23.2791 | 25.9837
| Gravenhurst (Muskoka Airport)Ice Accretion2025RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2025 | 14.301 | 17.0756 | 20.587 | 23.2791 | 25.9837
| Gravenhurst (Muskoka Airport)Ice Accretion2030RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2030 | 14.2669 | 17.0524 | 20.573 | 23.2791 | 25.9837
| Gravenhurst (Muskoka Airport)Ice Accretion2035RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2035 | 14.2328 | 17.0291 | 20.559 | 23.2791 | 25.9837
| Gravenhurst (Muskoka Airport)Ice Accretion2040RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2040 | 14.228 | 17.0465 | 20.615 | 23.3503 | 26.0807
| Gravenhurst (Muskoka Airport)Ice Accretion2045RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2045 | 14.2231 | 17.064 | 20.671 | 23.4215 | 26.1778
| Gravenhurst (Muskoka Airport)Ice Accretion2050RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2050 | 14.301 | 17.215 | 20.916 | 23.7221 | 26.5482
| Gravenhurst (Muskoka Airport)Ice Accretion2055RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2055 | 14.3838 | 17.3487 | 21.105 | 23.9515 | 26.8216
| Gravenhurst (Muskoka Airport)Ice Accretion2060RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2060 | 14.4423 | 17.4939 | 21.35 | 24.2758 | 27.2185
| Gravenhurst (Muskoka Airport)Ice Accretion2065RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2065 | 14.4179 | 17.5055 | 21.406 | 24.3707 | 27.342
| Gravenhurst (Muskoka Airport)Ice Accretion2070RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2070 | 14.1305 | 17.2383 | 21.161 | 24.1413 | 27.1215
| Gravenhurst (Muskoka Airport)Ice Accretion2075RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2075 | 13.8675 | 16.9594 | 20.86 | 23.817 | 26.7775
| Gravenhurst (Muskoka Airport)Ice Accretion2080RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2080 | 13.6045 | 16.6805 | 20.559 | 23.4927 | 26.4335
| Gravenhurst (Muskoka Airport)Ice Accretion2085RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2085 | 13.0565 | 16.0617 | 19.845 | 22.7096 | 25.5736
| Gravenhurst (Muskoka Airport)Ice Accretion2090RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2090 | 12.5085 | 15.443 | 19.131 | 21.9265 | 24.7136
| Gravenhurst (Muskoka Airport)Ice Accretion2095RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2095 | 12.5085 | 15.443 | 19.131 | 21.9265 | 24.7136
| Gravenhurst (Muskoka Airport)Ice Accretion2100RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2100 | 12.5085 | 15.443 | 19.131 | 21.9265 | 24.7136
| Gravenhurst (Muskoka Airport)Wind2023RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2023 | 77.3418 | 83.3328 | 89.6497 | 95.9537 | 102.2615
| Gravenhurst (Muskoka Airport)Wind2025RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2025 | 77.4212 | 83.428 | 89.7624 | 96.0823 | 102.4053
| Gravenhurst (Muskoka Airport)Wind2030RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2030 | 77.5006 | 83.5232 | 89.8752 | 96.2109 | 102.549
| Gravenhurst (Muskoka Airport)Wind2035RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2035 | 77.58 | 83.6184 | 89.9879 | 96.3394 | 102.6927
| Gravenhurst (Muskoka Airport)Wind2040RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2040 | 77.6594 | 83.7136 | 90.1006 | 96.468 | 102.8365
| Gravenhurst (Muskoka Airport)Wind2045RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2045 | 77.7388 | 83.8088 | 90.2134 | 96.5966 | 102.9802
| Gravenhurst (Muskoka Airport)Wind2050RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2050 | 77.9289 | 84.0364 | 90.4863 | 96.9099 | 103.335
| Gravenhurst (Muskoka Airport)Wind2055RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2055 | 78.0396 | 84.1688 | 90.6465 | 97.0946 | 103.546
| Gravenhurst (Muskoka Airport)Wind2060RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2060 | 78.1502 | 84.3012 | 90.8067 | 97.2793 | 103.7571
| Gravenhurst (Muskoka Airport)Wind2065RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2065 | 78.2609 | 84.4337 | 90.9669 | 97.4641 | 103.9681
| Gravenhurst (Muskoka Airport)Wind2070RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2070 | 78.3716 | 84.5661 | 91.1271 | 97.6488 | 104.1791
| Gravenhurst (Muskoka Airport)Wind2075RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2075 | 78.4061 | 84.6158 | 91.1968 | 97.7345 | 104.2806
| Gravenhurst (Muskoka Airport)Wind2080RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2080 | 78.4407 | 84.6654 | 91.2665 | 97.8203 | 104.382
| Gravenhurst (Muskoka Airport)Wind2085RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2085 | 78.4753 | 84.7151 | 91.3363 | 97.906 | 104.4835
| Gravenhurst (Muskoka Airport)Wind2090RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2090 | 78.5099 | 84.7648 | 91.406 | 97.9917 | 104.585
| Gravenhurst (Muskoka Airport)Wind2095RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2095 | 78.5445 | 84.8144 | 91.4757 | 98.0774 | 104.6864
| Gravenhurst (Muskoka Airport)Wind2100RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2100 | 78.5791 | 84.8641 | 91.5454 | 98.1631 | 104.7879
| Gravenhurst (Muskoka Airport)Wind2023RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2023 | 77.3418 | 83.3328 | 89.6497 | 95.9537 | 102.2615
| Gravenhurst (Muskoka Airport)Wind2025RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2025 | 77.4212 | 83.428 | 89.7624 | 96.0823 | 102.4053
| Gravenhurst (Muskoka Airport)Wind2030RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2030 | 77.5006 | 83.5232 | 89.8752 | 96.2109 | 102.549
| Gravenhurst (Muskoka Airport)Wind2035RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2035 | 77.58 | 83.6184 | 89.9879 | 96.3394 | 102.6927
| Gravenhurst (Muskoka Airport)Wind2040RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2040 | 77.6594 | 83.7136 | 90.1006 | 96.468 | 102.8365
| Gravenhurst (Muskoka Airport)Wind2045RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2045 | 77.7388 | 83.8088 | 90.2134 | 96.5966 | 102.9802
| Gravenhurst (Muskoka Airport)Wind2050RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2050 | 77.9289 | 84.0364 | 90.4863 | 96.9099 | 103.335
| Gravenhurst (Muskoka Airport)Wind2055RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2055 | 78.0396 | 84.1688 | 90.6465 | 97.0946 | 103.546
| Gravenhurst (Muskoka Airport)Wind2060RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2060 | 78.1502 | 84.3012 | 90.8067 | 97.2793 | 103.7571
| Gravenhurst (Muskoka Airport)Wind2065RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2065 | 78.2609 | 84.4337 | 90.9669 | 97.4641 | 103.9681
| Gravenhurst (Muskoka Airport)Wind2070RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2070 | 78.3716 | 84.5661 | 91.1271 | 97.6488 | 104.1791
| Gravenhurst (Muskoka Airport)Wind2075RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2075 | 78.4234 | 84.6406 | 91.2317 | 97.7774 | 104.3313
| Gravenhurst (Muskoka Airport)Wind2080RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2080 | 78.4753 | 84.7151 | 91.3363 | 97.906 | 104.4835
| Gravenhurst (Muskoka Airport)Wind2085RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2085 | 78.5272 | 84.7896 | 91.4408 | 98.0345 | 104.6357
| Gravenhurst (Muskoka Airport)Wind2090RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2090 | 78.6943 | 85.0186 | 91.7442 | 98.4012 | 105.0652
| Gravenhurst (Muskoka Airport)Wind2095RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2095 | 78.8096 | 85.1731 | 91.9429 | 98.6392 | 105.3425
| Gravenhurst (Muskoka Airport)Wind2100RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2100 | 78.9249 | 85.3276 | 92.1417 | 98.8773 | 105.6199
| Gravenhurst (Muskoka Airport)Wind2023RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2023 | 77.3418 | 83.3328 | 89.6497 | 95.9537 | 102.2615
| Gravenhurst (Muskoka Airport)Wind2025RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2025 | 77.5006 | 83.5232 | 89.8752 | 96.2109 | 102.549
| Gravenhurst (Muskoka Airport)Wind2030RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2030 | 77.6594 | 83.7136 | 90.1006 | 96.468 | 102.8365
| Gravenhurst (Muskoka Airport)Wind2035RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2035 | 77.8182 | 83.9039 | 90.3261 | 96.7251 | 103.1239
| Gravenhurst (Muskoka Airport)Wind2040RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2040 | 78.0027 | 84.1247 | 90.5931 | 97.033 | 103.4757
| Gravenhurst (Muskoka Airport)Wind2045RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2045 | 78.1871 | 84.3454 | 90.8601 | 97.3409 | 103.8274
| Gravenhurst (Muskoka Airport)Wind2050RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2050 | 78.4407 | 84.6654 | 91.2665 | 97.8203 | 104.382
| Gravenhurst (Muskoka Airport)Wind2055RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2055 | 78.5099 | 84.7648 | 91.406 | 97.9917 | 104.585
| Gravenhurst (Muskoka Airport)Wind2060RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2060 | 78.6943 | 85.0186 | 91.7442 | 98.4012 | 105.0652
| Gravenhurst (Muskoka Airport)Wind2065RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2065 | 78.8096 | 85.1731 | 91.9429 | 98.6392 | 105.3425
| Gravenhurst (Muskoka Airport)Wind2070RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2070 | 78.9121 | 85.3221 | 92.1476 | 98.89 | 105.6435
| Gravenhurst (Muskoka Airport)Wind2075RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2075 | 78.8993 | 85.3166 | 92.1536 | 98.9027 | 105.6672
| Gravenhurst (Muskoka Airport)Wind2080RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2080 | 78.8865 | 85.311 | 92.1595 | 98.9154 | 105.6909
| Gravenhurst (Muskoka Airport)Wind2085RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2085 | 78.9864 | 85.4393 | 92.3286 | 99.1154 | 105.9242
| Gravenhurst (Muskoka Airport)Wind2090RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2090 | 79.0863 | 85.5676 | 92.4977 | 99.3154 | 106.1576
| Gravenhurst (Muskoka Airport)Wind2095RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2095 | 79.0863 | 85.5676 | 92.4977 | 99.3154 | 106.1576
| Gravenhurst (Muskoka Airport)Wind2100RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2100 | 79.0863 | 85.5676 | 92.4977 | 99.3154 | 106.1576
| GrimsbyIce Accretion2023RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2023 | 20.6458 | 24.7755 | 30 | 34.0017 | 37.989
| GrimsbyIce Accretion2025RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2025 | 20.5483 | 24.6676 | 29.885 | 33.8717 | 37.8504
| GrimsbyIce Accretion2030RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2030 | 20.4509 | 24.5597 | 29.77 | 33.7418 | 37.7118
| GrimsbyIce Accretion2035RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2035 | 20.3535 | 24.4518 | 29.655 | 33.6118 | 37.5732
| GrimsbyIce Accretion2040RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2040 | 20.2561 | 24.3439 | 29.54 | 33.4819 | 37.4346
| GrimsbyIce Accretion2045RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2045 | 20.1587 | 24.236 | 29.425 | 33.352 | 37.296
| GrimsbyIce Accretion2050RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2050 | 19.6145 | 23.6251 | 28.722 | 32.5711 | 36.4468
| GrimsbyIce Accretion2055RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2055 | 19.1678 | 23.1221 | 28.134 | 31.9202 | 35.7361
| GrimsbyIce Accretion2060RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2060 | 18.721 | 22.6192 | 27.546 | 31.2694 | 35.0255
| GrimsbyIce Accretion2065RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2065 | 18.2743 | 22.1162 | 26.958 | 30.6185 | 34.3148
| GrimsbyIce Accretion2070RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2070 | 17.8276 | 21.6132 | 26.37 | 29.9676 | 33.6042
| GrimsbyIce Accretion2075RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2075 | 17.6606 | 21.4389 | 26.185 | 29.7755 | 33.4026
| GrimsbyIce Accretion2080RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2080 | 17.4936 | 21.2646 | 26 | 29.5834 | 33.201
| GrimsbyIce Accretion2085RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2085 | 17.3266 | 21.0903 | 25.815 | 29.3913 | 32.9994
| GrimsbyIce Accretion2090RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2090 | 17.1596 | 20.916 | 25.63 | 29.1992 | 32.7978
| GrimsbyIce Accretion2095RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2095 | 16.9926 | 20.7417 | 25.445 | 29.0071 | 32.5962
| GrimsbyIce Accretion2100RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2100 | 16.8256 | 20.5674 | 25.26 | 28.815 | 32.3946
| GrimsbyIce Accretion2023RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2023 | 20.6458 | 24.7755 | 30 | 34.0017 | 37.989
| GrimsbyIce Accretion2025RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2025 | 20.5483 | 24.6676 | 29.885 | 33.8717 | 37.8504
| GrimsbyIce Accretion2030RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2030 | 20.4509 | 24.5597 | 29.77 | 33.7418 | 37.7118
| GrimsbyIce Accretion2035RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2035 | 20.3535 | 24.4518 | 29.655 | 33.6118 | 37.5732
| GrimsbyIce Accretion2040RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2040 | 20.2561 | 24.3439 | 29.54 | 33.4819 | 37.4346
| GrimsbyIce Accretion2045RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2045 | 20.1587 | 24.236 | 29.425 | 33.352 | 37.296
| GrimsbyIce Accretion2050RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2050 | 19.6145 | 23.6251 | 28.722 | 32.5711 | 36.4468
| GrimsbyIce Accretion2055RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2055 | 19.1678 | 23.1221 | 28.134 | 31.9202 | 35.7361
| GrimsbyIce Accretion2060RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2060 | 18.721 | 22.6192 | 27.546 | 31.2694 | 35.0255
| GrimsbyIce Accretion2065RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2065 | 18.2743 | 22.1162 | 26.958 | 30.6185 | 34.3148
| GrimsbyIce Accretion2070RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2070 | 17.8276 | 21.6132 | 26.37 | 29.9676 | 33.6042
| GrimsbyIce Accretion2075RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2075 | 17.5771 | 21.3517 | 26.0925 | 29.6794 | 33.3018
| GrimsbyIce Accretion2080RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2080 | 17.3266 | 21.0903 | 25.815 | 29.3913 | 32.9994
| GrimsbyIce Accretion2085RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2085 | 17.0761 | 20.8288 | 25.5375 | 29.1031 | 32.697
| GrimsbyIce Accretion2090RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2090 | 16.1436 | 19.7872 | 24.35 | 27.8093 | 31.2732
| GrimsbyIce Accretion2095RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2095 | 15.4617 | 19.007 | 23.44 | 26.8036 | 30.1518
| GrimsbyIce Accretion2100RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2100 | 14.7798 | 18.2268 | 22.53 | 25.7979 | 29.0304
| GrimsbyIce Accretion2023RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2023 | 20.6458 | 24.7755 | 30 | 34.0017 | 37.989
| GrimsbyIce Accretion2025RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2025 | 20.4509 | 24.5597 | 29.77 | 33.7418 | 37.7118
| GrimsbyIce Accretion2030RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2030 | 20.2561 | 24.3439 | 29.54 | 33.4819 | 37.4346
| GrimsbyIce Accretion2035RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2035 | 20.0612 | 24.1281 | 29.31 | 33.222 | 37.1574
| GrimsbyIce Accretion2040RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2040 | 19.3167 | 23.2898 | 28.33 | 32.1372 | 35.973
| GrimsbyIce Accretion2045RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2045 | 18.5721 | 22.4515 | 27.35 | 31.0524 | 34.7886
| GrimsbyIce Accretion2050RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2050 | 17.4936 | 21.2646 | 26 | 29.5834 | 33.201
| GrimsbyIce Accretion2055RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2055 | 17.1596 | 20.916 | 25.63 | 29.1992 | 32.7978
| GrimsbyIce Accretion2060RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2060 | 16.1436 | 19.7872 | 24.35 | 27.8093 | 31.2732
| GrimsbyIce Accretion2065RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2065 | 15.4617 | 19.007 | 23.44 | 26.8036 | 30.1518
| GrimsbyIce Accretion2070RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2070 | 14.4388 | 17.8367 | 22.09 | 25.312 | 28.5012
| GrimsbyIce Accretion2075RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2075 | 14.0978 | 17.4466 | 21.65 | 24.8261 | 27.972
| GrimsbyIce Accretion2080RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2080 | 13.7569 | 17.0565 | 21.21 | 24.3402 | 27.4428
| GrimsbyIce Accretion2085RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2085 | 12.9845 | 16.1476 | 20.115 | 23.1029 | 26.0631
| GrimsbyIce Accretion2090RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2090 | 12.2121 | 15.2388 | 19.02 | 21.8655 | 24.6834
| GrimsbyIce Accretion2095RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2095 | 12.2121 | 15.2388 | 19.02 | 21.8655 | 24.6834
| GrimsbyIce Accretion2100RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2100 | 12.2121 | 15.2388 | 19.02 | 21.8655 | 24.6834
| GrimsbyWind2023RCP4.5 | Grimsby | Wind | RCP4.5 | 2023 | 87.2376 | 94.1811 | 101.55 | 108.8725 | 116.1888
| GrimsbyWind2025RCP4.5 | Grimsby | Wind | RCP4.5 | 2025 | 87.2088 | 94.1517 | 101.5183 | 108.8386 | 116.1527
| GrimsbyWind2030RCP4.5 | Grimsby | Wind | RCP4.5 | 2030 | 87.1801 | 94.1222 | 101.4867 | 108.8047 | 116.1166
| GrimsbyWind2035RCP4.5 | Grimsby | Wind | RCP4.5 | 2035 | 87.1513 | 94.0927 | 101.455 | 108.7708 | 116.0805
| GrimsbyWind2040RCP4.5 | Grimsby | Wind | RCP4.5 | 2040 | 87.1225 | 94.0633 | 101.4233 | 108.737 | 116.0444
| GrimsbyWind2045RCP4.5 | Grimsby | Wind | RCP4.5 | 2045 | 87.0937 | 94.0338 | 101.3917 | 108.7031 | 116.0083
| GrimsbyWind2050RCP4.5 | Grimsby | Wind | RCP4.5 | 2050 | 87.1219 | 94.0769 | 101.454 | 108.7783 | 116.0999
| GrimsbyWind2055RCP4.5 | Grimsby | Wind | RCP4.5 | 2055 | 87.1789 | 94.1495 | 101.548 | 108.8875 | 116.2276
| GrimsbyWind2060RCP4.5 | Grimsby | Wind | RCP4.5 | 2060 | 87.2359 | 94.222 | 101.642 | 108.9966 | 116.3552
| GrimsbyWind2065RCP4.5 | Grimsby | Wind | RCP4.5 | 2065 | 87.2929 | 94.2946 | 101.736 | 109.1058 | 116.4829
| GrimsbyWind2070RCP4.5 | Grimsby | Wind | RCP4.5 | 2070 | 87.3499 | 94.3671 | 101.83 | 109.2149 | 116.6106
| GrimsbyWind2075RCP4.5 | Grimsby | Wind | RCP4.5 | 2075 | 87.4305 | 94.4802 | 101.985 | 109.4039 | 116.8367
| GrimsbyWind2080RCP4.5 | Grimsby | Wind | RCP4.5 | 2080 | 87.5111 | 94.5934 | 102.14 | 109.593 | 117.0628
| GrimsbyWind2085RCP4.5 | Grimsby | Wind | RCP4.5 | 2085 | 87.5917 | 94.7065 | 102.295 | 109.782 | 117.2889
| GrimsbyWind2090RCP4.5 | Grimsby | Wind | RCP4.5 | 2090 | 87.6722 | 94.8197 | 102.45 | 109.971 | 117.515
| GrimsbyWind2095RCP4.5 | Grimsby | Wind | RCP4.5 | 2095 | 87.7528 | 94.9329 | 102.605 | 110.1601 | 117.7411
| GrimsbyWind2100RCP4.5 | Grimsby | Wind | RCP4.5 | 2100 | 87.8334 | 95.046 | 102.76 | 110.3491 | 117.9672
| GrimsbyWind2023RCP6.0 | Grimsby | Wind | RCP6.0 | 2023 | 87.2376 | 94.1811 | 101.55 | 108.8725 | 116.1888
| GrimsbyWind2025RCP6.0 | Grimsby | Wind | RCP6.0 | 2025 | 87.2088 | 94.1517 | 101.5183 | 108.8386 | 116.1527
| GrimsbyWind2030RCP6.0 | Grimsby | Wind | RCP6.0 | 2030 | 87.1801 | 94.1222 | 101.4867 | 108.8047 | 116.1166
| GrimsbyWind2035RCP6.0 | Grimsby | Wind | RCP6.0 | 2035 | 87.1513 | 94.0927 | 101.455 | 108.7708 | 116.0805
| GrimsbyWind2040RCP6.0 | Grimsby | Wind | RCP6.0 | 2040 | 87.1225 | 94.0633 | 101.4233 | 108.737 | 116.0444
| GrimsbyWind2045RCP6.0 | Grimsby | Wind | RCP6.0 | 2045 | 87.0937 | 94.0338 | 101.3917 | 108.7031 | 116.0083
| GrimsbyWind2050RCP6.0 | Grimsby | Wind | RCP6.0 | 2050 | 87.1219 | 94.0769 | 101.454 | 108.7783 | 116.0999
| GrimsbyWind2055RCP6.0 | Grimsby | Wind | RCP6.0 | 2055 | 87.1789 | 94.1495 | 101.548 | 108.8875 | 116.2276
| GrimsbyWind2060RCP6.0 | Grimsby | Wind | RCP6.0 | 2060 | 87.2359 | 94.222 | 101.642 | 108.9966 | 116.3552
| GrimsbyWind2065RCP6.0 | Grimsby | Wind | RCP6.0 | 2065 | 87.2929 | 94.2946 | 101.736 | 109.1058 | 116.4829
| GrimsbyWind2070RCP6.0 | Grimsby | Wind | RCP6.0 | 2070 | 87.3499 | 94.3671 | 101.83 | 109.2149 | 116.6106
| GrimsbyWind2075RCP6.0 | Grimsby | Wind | RCP6.0 | 2075 | 87.4708 | 94.5368 | 102.0625 | 109.4985 | 116.9497
| GrimsbyWind2080RCP6.0 | Grimsby | Wind | RCP6.0 | 2080 | 87.5917 | 94.7065 | 102.295 | 109.782 | 117.2889
| GrimsbyWind2085RCP6.0 | Grimsby | Wind | RCP6.0 | 2085 | 87.7125 | 94.8763 | 102.5275 | 110.0656 | 117.628
| GrimsbyWind2090RCP6.0 | Grimsby | Wind | RCP6.0 | 2090 | 88.0176 | 95.2816 | 103.0567 | 110.7022 | 118.3776
| GrimsbyWind2095RCP6.0 | Grimsby | Wind | RCP6.0 | 2095 | 88.2019 | 95.5172 | 103.3533 | 111.0553 | 118.788
| GrimsbyWind2100RCP6.0 | Grimsby | Wind | RCP6.0 | 2100 | 88.3861 | 95.7528 | 103.65 | 111.4084 | 119.1984
| GrimsbyWind2023RCP8.5 | Grimsby | Wind | RCP8.5 | 2023 | 87.2376 | 94.1811 | 101.55 | 108.8725 | 116.1888
| GrimsbyWind2025RCP8.5 | Grimsby | Wind | RCP8.5 | 2025 | 87.1801 | 94.1222 | 101.4867 | 108.8047 | 116.1166
| GrimsbyWind2030RCP8.5 | Grimsby | Wind | RCP8.5 | 2030 | 87.1225 | 94.0633 | 101.4233 | 108.737 | 116.0444
| GrimsbyWind2035RCP8.5 | Grimsby | Wind | RCP8.5 | 2035 | 87.0649 | 94.0044 | 101.36 | 108.6692 | 115.9722
| GrimsbyWind2040RCP8.5 | Grimsby | Wind | RCP8.5 | 2040 | 87.1599 | 94.1253 | 101.5167 | 108.8511 | 116.185
| GrimsbyWind2045RCP8.5 | Grimsby | Wind | RCP8.5 | 2045 | 87.2549 | 94.2462 | 101.6733 | 109.033 | 116.3978
| GrimsbyWind2050RCP8.5 | Grimsby | Wind | RCP8.5 | 2050 | 87.5111 | 94.5934 | 102.14 | 109.593 | 117.0628
| GrimsbyWind2055RCP8.5 | Grimsby | Wind | RCP8.5 | 2055 | 87.6722 | 94.8197 | 102.45 | 109.971 | 117.515
| GrimsbyWind2060RCP8.5 | Grimsby | Wind | RCP8.5 | 2060 | 88.0176 | 95.2816 | 103.0567 | 110.7022 | 118.3776
| GrimsbyWind2065RCP8.5 | Grimsby | Wind | RCP8.5 | 2065 | 88.2019 | 95.5172 | 103.3533 | 111.0553 | 118.788
| GrimsbyWind2070RCP8.5 | Grimsby | Wind | RCP8.5 | 2070 | 88.4465 | 95.8551 | 103.8133 | 111.6224 | 119.4568
| GrimsbyWind2075RCP8.5 | Grimsby | Wind | RCP8.5 | 2075 | 88.5069 | 95.9574 | 103.9767 | 111.8364 | 119.7152
| GrimsbyWind2080RCP8.5 | Grimsby | Wind | RCP8.5 | 2080 | 88.5674 | 96.0597 | 104.14 | 112.0504 | 119.9736
| GrimsbyWind2085RCP8.5 | Grimsby | Wind | RCP8.5 | 2085 | 88.6322 | 96.1666 | 104.295 | 112.243 | 120.213
| GrimsbyWind2090RCP8.5 | Grimsby | Wind | RCP8.5 | 2090 | 88.6969 | 96.2736 | 104.45 | 112.4356 | 120.4524
| GrimsbyWind2095RCP8.5 | Grimsby | Wind | RCP8.5 | 2095 | 88.6969 | 96.2736 | 104.45 | 112.4356 | 120.4524
| GrimsbyWind2100RCP8.5 | Grimsby | Wind | RCP8.5 | 2100 | 88.6969 | 96.2736 | 104.45 | 112.4356 | 120.4524
| GuelphIce Accretion2023RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
| GuelphIce Accretion2025RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2025 | 17.3208 | 20.7984 | 25.1958 | 28.5655 | 31.92
| GuelphIce Accretion2030RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2030 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
| GuelphIce Accretion2035RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2035 | 17.3788 | 20.8953 | 25.3375 | 28.7444 | 32.13
| GuelphIce Accretion2040RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2040 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
| GuelphIce Accretion2045RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2045 | 17.4367 | 20.9921 | 25.4792 | 28.9233 | 32.34
| GuelphIce Accretion2050RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2050 | 17.4101 | 20.9907 | 25.51 | 28.9788 | 32.4198
| GuelphIce Accretion2055RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2055 | 17.3544 | 20.9409 | 25.47 | 28.9449 | 32.3946
| GuelphIce Accretion2060RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2060 | 17.2987 | 20.8911 | 25.43 | 28.911 | 32.3694
| GuelphIce Accretion2065RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2065 | 17.2431 | 20.8413 | 25.39 | 28.8771 | 32.3442
| GuelphIce Accretion2070RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2070 | 17.1874 | 20.7915 | 25.35 | 28.8432 | 32.319
| GuelphIce Accretion2075RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2075 | 17.1555 | 20.7846 | 25.3708 | 28.8809 | 32.3768
| GuelphIce Accretion2080RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2080 | 17.1236 | 20.7777 | 25.3917 | 28.9186 | 32.4345
| GuelphIce Accretion2085RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2085 | 17.0917 | 20.7707 | 25.4125 | 28.9562 | 32.4922
| GuelphIce Accretion2090RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2090 | 17.0598 | 20.7638 | 25.4333 | 28.9939 | 32.55
| GuelphIce Accretion2095RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2095 | 17.0279 | 20.7569 | 25.4542 | 29.0316 | 32.6077
| GuelphIce Accretion2100RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2100 | 16.996 | 20.75 | 25.475 | 29.0692 | 32.6655
| GuelphIce Accretion2023RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
| GuelphIce Accretion2025RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2025 | 17.3208 | 20.7984 | 25.1958 | 28.5655 | 31.92
| GuelphIce Accretion2030RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2030 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
| GuelphIce Accretion2035RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2035 | 17.3788 | 20.8953 | 25.3375 | 28.7444 | 32.13
| GuelphIce Accretion2040RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2040 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
| GuelphIce Accretion2045RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2045 | 17.4367 | 20.9921 | 25.4792 | 28.9233 | 32.34
| GuelphIce Accretion2050RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2050 | 17.4101 | 20.9907 | 25.51 | 28.9788 | 32.4198
| GuelphIce Accretion2055RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2055 | 17.3544 | 20.9409 | 25.47 | 28.9449 | 32.3946
| GuelphIce Accretion2060RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2060 | 17.2987 | 20.8911 | 25.43 | 28.911 | 32.3694
| GuelphIce Accretion2065RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2065 | 17.2431 | 20.8413 | 25.39 | 28.8771 | 32.3442
| GuelphIce Accretion2070RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2070 | 17.1874 | 20.7915 | 25.35 | 28.8432 | 32.319
| GuelphIce Accretion2075RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2075 | 17.1396 | 20.7811 | 25.3813 | 28.8997 | 32.4056
| GuelphIce Accretion2080RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2080 | 17.0917 | 20.7707 | 25.4125 | 28.9562 | 32.4922
| GuelphIce Accretion2085RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2085 | 17.0439 | 20.7604 | 25.4437 | 29.0127 | 32.5789
| GuelphIce Accretion2090RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2090 | 16.6887 | 20.4249 | 25.1333 | 28.7114 | 32.298
| GuelphIce Accretion2095RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2095 | 16.3814 | 20.0998 | 24.7917 | 28.3536 | 31.9305
| GuelphIce Accretion2100RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2100 | 16.074 | 19.7747 | 24.45 | 27.9957 | 31.563
| GuelphIce Accretion2023RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
| GuelphIce Accretion2025RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2025 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
| GuelphIce Accretion2030RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2030 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
| GuelphIce Accretion2035RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2035 | 17.4657 | 21.0405 | 25.55 | 29.0127 | 32.445
| GuelphIce Accretion2040RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2040 | 17.373 | 20.9575 | 25.4833 | 28.9562 | 32.403
| GuelphIce Accretion2045RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2045 | 17.2802 | 20.8745 | 25.4167 | 28.8997 | 32.361
| GuelphIce Accretion2050RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2050 | 17.1236 | 20.7777 | 25.3917 | 28.9186 | 32.4345
| GuelphIce Accretion2055RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2055 | 17.0598 | 20.7638 | 25.4333 | 28.9939 | 32.55
| GuelphIce Accretion2060RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2060 | 16.6887 | 20.4249 | 25.1333 | 28.7114 | 32.298
| GuelphIce Accretion2065RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2065 | 16.3814 | 20.0998 | 24.7917 | 28.3536 | 31.9305
| GuelphIce Accretion2070RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2070 | 15.6507 | 19.3182 | 23.95 | 27.4684 | 30.9855
| GuelphIce Accretion2075RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2075 | 15.2274 | 18.8617 | 23.45 | 26.9411 | 30.408
| GuelphIce Accretion2080RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2080 | 14.8041 | 18.4052 | 22.95 | 26.4137 | 29.8305
| GuelphIce Accretion2085RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2085 | 13.9778 | 17.43 | 21.7875 | 25.086 | 28.3657
| GuelphIce Accretion2090RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2090 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
| GuelphIce Accretion2095RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2095 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
| GuelphIce Accretion2100RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2100 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
| GuelphWind2023RCP4.5 | Guelph | Wind | RCP4.5 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
| GuelphWind2025RCP4.5 | Guelph | Wind | RCP4.5 | 2025 | 81.5488 | 87.8469 | 94.481 | 101.1097 | 107.7494
| GuelphWind2030RCP4.5 | Guelph | Wind | RCP4.5 | 2030 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
| GuelphWind2035RCP4.5 | Guelph | Wind | RCP4.5 | 2035 | 81.6625 | 88.0013 | 94.6909 | 101.3645 | 108.0494
| GuelphWind2040RCP4.5 | Guelph | Wind | RCP4.5 | 2040 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
| GuelphWind2045RCP4.5 | Guelph | Wind | RCP4.5 | 2045 | 81.7761 | 88.1558 | 94.9008 | 101.6193 | 108.3495
| GuelphWind2050RCP4.5 | Guelph | Wind | RCP4.5 | 2050 | 81.8962 | 88.3099 | 95.096 | 101.8513 | 108.6174
| GuelphWind2055RCP4.5 | Guelph | Wind | RCP4.5 | 2055 | 81.9595 | 88.3869 | 95.1863 | 101.9559 | 108.7353
| GuelphWind2060RCP4.5 | Guelph | Wind | RCP4.5 | 2060 | 82.0229 | 88.4638 | 95.2765 | 102.0605 | 108.8531
| GuelphWind2065RCP4.5 | Guelph | Wind | RCP4.5 | 2065 | 82.0862 | 88.5407 | 95.3668 | 102.1651 | 108.971
| GuelphWind2070RCP4.5 | Guelph | Wind | RCP4.5 | 2070 | 82.1495 | 88.6177 | 95.457 | 102.2697 | 109.0889
| GuelphWind2075RCP4.5 | Guelph | Wind | RCP4.5 | 2075 | 82.2185 | 88.7167 | 95.598 | 102.4424 | 109.2961
| GuelphWind2080RCP4.5 | Guelph | Wind | RCP4.5 | 2080 | 82.2875 | 88.8158 | 95.739 | 102.6151 | 109.5032
| GuelphWind2085RCP4.5 | Guelph | Wind | RCP4.5 | 2085 | 82.3564 | 88.9149 | 95.88 | 102.7877 | 109.7104
| GuelphWind2090RCP4.5 | Guelph | Wind | RCP4.5 | 2090 | 82.4254 | 89.014 | 96.021 | 102.9604 | 109.9176
| GuelphWind2095RCP4.5 | Guelph | Wind | RCP4.5 | 2095 | 82.4944 | 89.113 | 96.162 | 103.1331 | 110.1248
| GuelphWind2100RCP4.5 | Guelph | Wind | RCP4.5 | 2100 | 82.5634 | 89.2121 | 96.303 | 103.3057 | 110.3319
| GuelphWind2023RCP6.0 | Guelph | Wind | RCP6.0 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
| GuelphWind2025RCP6.0 | Guelph | Wind | RCP6.0 | 2025 | 81.5488 | 87.8469 | 94.481 | 101.1097 | 107.7494
| GuelphWind2030RCP6.0 | Guelph | Wind | RCP6.0 | 2030 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
| GuelphWind2035RCP6.0 | Guelph | Wind | RCP6.0 | 2035 | 81.6625 | 88.0013 | 94.6909 | 101.3645 | 108.0494
| GuelphWind2040RCP6.0 | Guelph | Wind | RCP6.0 | 2040 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
| GuelphWind2045RCP6.0 | Guelph | Wind | RCP6.0 | 2045 | 81.7761 | 88.1558 | 94.9008 | 101.6193 | 108.3495
| GuelphWind2050RCP6.0 | Guelph | Wind | RCP6.0 | 2050 | 81.8962 | 88.3099 | 95.096 | 101.8513 | 108.6174
| GuelphWind2055RCP6.0 | Guelph | Wind | RCP6.0 | 2055 | 81.9595 | 88.3869 | 95.1863 | 101.9559 | 108.7353
| GuelphWind2060RCP6.0 | Guelph | Wind | RCP6.0 | 2060 | 82.0229 | 88.4638 | 95.2765 | 102.0605 | 108.8531
| GuelphWind2065RCP6.0 | Guelph | Wind | RCP6.0 | 2065 | 82.0862 | 88.5407 | 95.3668 | 102.1651 | 108.971
| GuelphWind2070RCP6.0 | Guelph | Wind | RCP6.0 | 2070 | 82.1495 | 88.6177 | 95.457 | 102.2697 | 109.0889
| GuelphWind2075RCP6.0 | Guelph | Wind | RCP6.0 | 2075 | 82.253 | 88.7663 | 95.6685 | 102.5287 | 109.3996
| GuelphWind2080RCP6.0 | Guelph | Wind | RCP6.0 | 2080 | 82.3564 | 88.9149 | 95.88 | 102.7877 | 109.7104
| GuelphWind2085RCP6.0 | Guelph | Wind | RCP6.0 | 2085 | 82.4599 | 89.0635 | 96.0915 | 103.0467 | 110.0212
| GuelphWind2090RCP6.0 | Guelph | Wind | RCP6.0 | 2090 | 82.8421 | 89.5618 | 96.7385 | 103.8187 | 110.9213
| GuelphWind2095RCP6.0 | Guelph | Wind | RCP6.0 | 2095 | 83.1208 | 89.9115 | 97.1741 | 104.3316 | 111.5107
| GuelphWind2100RCP6.0 | Guelph | Wind | RCP6.0 | 2100 | 83.3995 | 90.2612 | 97.6096 | 104.8446 | 112.1001
| GuelphWind2023RCP8.5 | Guelph | Wind | RCP8.5 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
| GuelphWind2025RCP8.5 | Guelph | Wind | RCP8.5 | 2025 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
| GuelphWind2030RCP8.5 | Guelph | Wind | RCP8.5 | 2030 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
| GuelphWind2035RCP8.5 | Guelph | Wind | RCP8.5 | 2035 | 81.8329 | 88.233 | 95.0058 | 101.7467 | 108.4995
| GuelphWind2040RCP8.5 | Guelph | Wind | RCP8.5 | 2040 | 81.9384 | 88.3612 | 95.1562 | 101.9211 | 108.696
| GuelphWind2045RCP8.5 | Guelph | Wind | RCP8.5 | 2045 | 82.044 | 88.4894 | 95.3066 | 102.0954 | 108.8924
| GuelphWind2050RCP8.5 | Guelph | Wind | RCP8.5 | 2050 | 82.2875 | 88.8158 | 95.739 | 102.6151 | 109.5032
| GuelphWind2055RCP8.5 | Guelph | Wind | RCP8.5 | 2055 | 82.4254 | 89.014 | 96.021 | 102.9604 | 109.9176
| GuelphWind2060RCP8.5 | Guelph | Wind | RCP8.5 | 2060 | 82.8421 | 89.5618 | 96.7385 | 103.8187 | 110.9213
| GuelphWind2065RCP8.5 | Guelph | Wind | RCP8.5 | 2065 | 83.1208 | 89.9115 | 97.1741 | 104.3316 | 111.5107
| GuelphWind2070RCP8.5 | Guelph | Wind | RCP8.5 | 2070 | 83.6457 | 90.5933 | 98.0451 | 105.371 | 112.718
| GuelphWind2075RCP8.5 | Guelph | Wind | RCP8.5 | 2075 | 83.8919 | 90.9255 | 98.4807 | 105.8973 | 113.336
| GuelphWind2080RCP8.5 | Guelph | Wind | RCP8.5 | 2080 | 84.1381 | 91.2577 | 98.9162 | 106.4237 | 113.9539
| GuelphWind2085RCP8.5 | Guelph | Wind | RCP8.5 | 2085 | 84.3775 | 91.5768 | 99.3392 | 106.9266 | 114.5433
| GuelphWind2090RCP8.5 | Guelph | Wind | RCP8.5 | 2090 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
| GuelphWind2095RCP8.5 | Guelph | Wind | RCP8.5 | 2095 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
| GuelphWind2100RCP8.5 | Guelph | Wind | RCP8.5 | 2100 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
| GuthrieIce Accretion2023RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2023 | 15.6684 | 18.7464 | 22.632 | 25.6001 | 28.5453
| GuthrieIce Accretion2025RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2025 | 15.663 | 18.7432 | 22.6358 | 25.6088 | 28.5646
| GuthrieIce Accretion2030RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2030 | 15.6577 | 18.74 | 22.6397 | 25.6175 | 28.5839
| GuthrieIce Accretion2035RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2035 | 15.6524 | 18.7368 | 22.6435 | 25.6261 | 28.6033
| GuthrieIce Accretion2040RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2040 | 15.647 | 18.7337 | 22.6473 | 25.6348 | 28.6226
| GuthrieIce Accretion2045RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2045 | 15.6417 | 18.7305 | 22.6512 | 25.6435 | 28.6419
| GuthrieIce Accretion2050RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2050 | 15.5947 | 18.6967 | 22.6366 | 25.6417 | 28.6554
| GuthrieIce Accretion2055RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2055 | 15.5531 | 18.6662 | 22.6182 | 25.6313 | 28.6496
| GuthrieIce Accretion2060RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2060 | 15.5115 | 18.6357 | 22.5998 | 25.6209 | 28.6438
| GuthrieIce Accretion2065RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2065 | 15.4699 | 18.6051 | 22.5814 | 25.6105 | 28.638
| GuthrieIce Accretion2070RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2070 | 15.4283 | 18.5746 | 22.563 | 25.6001 | 28.6322
| GuthrieIce Accretion2075RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2075 | 15.4283 | 18.5968 | 22.6128 | 25.6695 | 28.7192
| GuthrieIce Accretion2080RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2080 | 15.4283 | 18.6191 | 22.6627 | 25.7388 | 28.8061
| GuthrieIce Accretion2085RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2085 | 15.4283 | 18.6414 | 22.7125 | 25.8081 | 28.8931
| GuthrieIce Accretion2090RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2090 | 15.4283 | 18.6637 | 22.7623 | 25.8774 | 28.98
| GuthrieIce Accretion2095RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2095 | 15.4283 | 18.6859 | 22.8122 | 25.9467 | 29.0669
| GuthrieIce Accretion2100RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2100 | 15.4283 | 18.7082 | 22.862 | 26.016 | 29.1539
| GuthrieIce Accretion2023RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2023 | 15.6684 | 18.7464 | 22.632 | 25.6001 | 28.5453
| GuthrieIce Accretion2025RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2025 | 15.663 | 18.7432 | 22.6358 | 25.6088 | 28.5646
| GuthrieIce Accretion2030RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2030 | 15.6577 | 18.74 | 22.6397 | 25.6175 | 28.5839
| GuthrieIce Accretion2035RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2035 | 15.6524 | 18.7368 | 22.6435 | 25.6261 | 28.6033
| GuthrieIce Accretion2040RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2040 | 15.647 | 18.7337 | 22.6473 | 25.6348 | 28.6226
| GuthrieIce Accretion2045RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2045 | 15.6417 | 18.7305 | 22.6512 | 25.6435 | 28.6419
| GuthrieIce Accretion2050RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2050 | 15.5947 | 18.6967 | 22.6366 | 25.6417 | 28.6554
| GuthrieIce Accretion2055RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2055 | 15.5531 | 18.6662 | 22.6182 | 25.6313 | 28.6496
| GuthrieIce Accretion2060RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2060 | 15.5115 | 18.6357 | 22.5998 | 25.6209 | 28.6438
| GuthrieIce Accretion2065RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2065 | 15.4699 | 18.6051 | 22.5814 | 25.6105 | 28.638
| GuthrieIce Accretion2070RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2070 | 15.4283 | 18.5746 | 22.563 | 25.6001 | 28.6322
| GuthrieIce Accretion2075RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2075 | 15.4283 | 18.608 | 22.6377 | 25.7041 | 28.7627
| GuthrieIce Accretion2080RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2080 | 15.4283 | 18.6414 | 22.7125 | 25.8081 | 28.8931
| GuthrieIce Accretion2085RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2085 | 15.4283 | 18.6748 | 22.7873 | 25.912 | 29.0235
| GuthrieIce Accretion2090RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2090 | 15.2523 | 18.53 | 22.6857 | 25.8341 | 28.98
| GuthrieIce Accretion2095RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2095 | 15.0762 | 18.3519 | 22.5093 | 25.6521 | 28.8061
| GuthrieIce Accretion2100RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2100 | 14.9002 | 18.1737 | 22.333 | 25.4702 | 28.6322
| GuthrieIce Accretion2023RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2023 | 15.6684 | 18.7464 | 22.632 | 25.6001 | 28.5453
| GuthrieIce Accretion2025RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2025 | 15.6577 | 18.74 | 22.6397 | 25.6175 | 28.5839
| GuthrieIce Accretion2030RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2030 | 15.647 | 18.7337 | 22.6473 | 25.6348 | 28.6226
| GuthrieIce Accretion2035RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2035 | 15.6364 | 18.7273 | 22.655 | 25.6521 | 28.6612
| GuthrieIce Accretion2040RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2040 | 15.567 | 18.6764 | 22.6243 | 25.6348 | 28.6516
| GuthrieIce Accretion2045RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2045 | 15.4977 | 18.6255 | 22.5937 | 25.6175 | 28.6419
| GuthrieIce Accretion2050RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2050 | 15.4283 | 18.6191 | 22.6627 | 25.7388 | 28.8061
| GuthrieIce Accretion2055RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2055 | 15.4283 | 18.6637 | 22.7623 | 25.8774 | 28.98
| GuthrieIce Accretion2060RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2060 | 15.2523 | 18.53 | 22.6857 | 25.8341 | 28.98
| GuthrieIce Accretion2065RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2065 | 15.0762 | 18.3519 | 22.5093 | 25.6521 | 28.8061
| GuthrieIce Accretion2070RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2070 | 14.6441 | 17.9191 | 22.0647 | 25.2016 | 28.3521
| GuthrieIce Accretion2075RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2075 | 14.388 | 17.6646 | 21.7963 | 24.9331 | 28.072
| GuthrieIce Accretion2080RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2080 | 14.1319 | 17.4101 | 21.528 | 24.6645 | 27.7918
| GuthrieIce Accretion2085RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2085 | 13.4758 | 16.6465 | 20.6425 | 23.6769 | 26.6906
| GuthrieIce Accretion2090RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2090 | 12.8196 | 15.8829 | 19.757 | 22.6893 | 25.5893
| GuthrieIce Accretion2095RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2095 | 12.8196 | 15.8829 | 19.757 | 22.6893 | 25.5893
| GuthrieIce Accretion2100RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2100 | 12.8196 | 15.8829 | 19.757 | 22.6893 | 25.5893
| GuthrieWind2023RCP4.5 | Guthrie | Wind | RCP4.5 | 2023 | 74.6382 | 80.4039 | 86.473 | 92.5445 | 98.6086
| GuthrieWind2025RCP4.5 | Guthrie | Wind | RCP4.5 | 2025 | 74.6593 | 80.4306 | 86.5074 | 92.5844 | 98.656
| GuthrieWind2030RCP4.5 | Guthrie | Wind | RCP4.5 | 2030 | 74.6803 | 80.4572 | 86.5418 | 92.6243 | 98.7034
| GuthrieWind2035RCP4.5 | Guthrie | Wind | RCP4.5 | 2035 | 74.7013 | 80.4839 | 86.5762 | 92.6641 | 98.7508
| GuthrieWind2040RCP4.5 | Guthrie | Wind | RCP4.5 | 2040 | 74.7224 | 80.5105 | 86.6106 | 92.704 | 98.7982
| GuthrieWind2045RCP4.5 | Guthrie | Wind | RCP4.5 | 2045 | 74.7434 | 80.5372 | 86.645 | 92.7439 | 98.8456
| GuthrieWind2050RCP4.5 | Guthrie | Wind | RCP4.5 | 2050 | 74.8818 | 80.6998 | 86.8359 | 92.9586 | 99.0871
| GuthrieWind2055RCP4.5 | Guthrie | Wind | RCP4.5 | 2055 | 74.9991 | 80.8358 | 86.9924 | 93.1334 | 99.2812
| GuthrieWind2060RCP4.5 | Guthrie | Wind | RCP4.5 | 2060 | 75.1164 | 80.9718 | 87.149 | 93.3083 | 99.4753
| GuthrieWind2065RCP4.5 | Guthrie | Wind | RCP4.5 | 2065 | 75.2338 | 81.1077 | 87.3055 | 93.4831 | 99.6694
| GuthrieWind2070RCP4.5 | Guthrie | Wind | RCP4.5 | 2070 | 75.3511 | 81.2437 | 87.462 | 93.658 | 99.8635
| GuthrieWind2075RCP4.5 | Guthrie | Wind | RCP4.5 | 2075 | 75.408 | 81.3183 | 87.5595 | 93.7745 | 99.9975
| GuthrieWind2080RCP4.5 | Guthrie | Wind | RCP4.5 | 2080 | 75.465 | 81.393 | 87.6569 | 93.8911 | 100.1315
| GuthrieWind2085RCP4.5 | Guthrie | Wind | RCP4.5 | 2085 | 75.5219 | 81.4676 | 87.7544 | 94.0076 | 100.2655
| GuthrieWind2090RCP4.5 | Guthrie | Wind | RCP4.5 | 2090 | 75.5788 | 81.5423 | 87.8519 | 94.1242 | 100.3995
| GuthrieWind2095RCP4.5 | Guthrie | Wind | RCP4.5 | 2095 | 75.6358 | 81.6169 | 87.9493 | 94.2407 | 100.5335
| GuthrieWind2100RCP4.5 | Guthrie | Wind | RCP4.5 | 2100 | 75.6927 | 81.6916 | 88.0468 | 94.3573 | 100.6675
| GuthrieWind2023RCP6.0 | Guthrie | Wind | RCP6.0 | 2023 | 74.6382 | 80.4039 | 86.473 | 92.5445 | 98.6086
| GuthrieWind2025RCP6.0 | Guthrie | Wind | RCP6.0 | 2025 | 74.6593 | 80.4306 | 86.5074 | 92.5844 | 98.656
| GuthrieWind2030RCP6.0 | Guthrie | Wind | RCP6.0 | 2030 | 74.6803 | 80.4572 | 86.5418 | 92.6243 | 98.7034
| GuthrieWind2035RCP6.0 | Guthrie | Wind | RCP6.0 | 2035 | 74.7013 | 80.4839 | 86.5762 | 92.6641 | 98.7508
| GuthrieWind2040RCP6.0 | Guthrie | Wind | RCP6.0 | 2040 | 74.7224 | 80.5105 | 86.6106 | 92.704 | 98.7982
| GuthrieWind2045RCP6.0 | Guthrie | Wind | RCP6.0 | 2045 | 74.7434 | 80.5372 | 86.645 | 92.7439 | 98.8456
| GuthrieWind2050RCP6.0 | Guthrie | Wind | RCP6.0 | 2050 | 74.8818 | 80.6998 | 86.8359 | 92.9586 | 99.0871
| GuthrieWind2055RCP6.0 | Guthrie | Wind | RCP6.0 | 2055 | 74.9991 | 80.8358 | 86.9924 | 93.1334 | 99.2812
| GuthrieWind2060RCP6.0 | Guthrie | Wind | RCP6.0 | 2060 | 75.1164 | 80.9718 | 87.149 | 93.3083 | 99.4753
| GuthrieWind2065RCP6.0 | Guthrie | Wind | RCP6.0 | 2065 | 75.2338 | 81.1077 | 87.3055 | 93.4831 | 99.6694
| GuthrieWind2070RCP6.0 | Guthrie | Wind | RCP6.0 | 2070 | 75.3511 | 81.2437 | 87.462 | 93.658 | 99.8635
| GuthrieWind2075RCP6.0 | Guthrie | Wind | RCP6.0 | 2075 | 75.4365 | 81.3557 | 87.6082 | 93.8328 | 100.0645
| GuthrieWind2080RCP6.0 | Guthrie | Wind | RCP6.0 | 2080 | 75.5219 | 81.4676 | 87.7544 | 94.0076 | 100.2655
| GuthrieWind2085RCP6.0 | Guthrie | Wind | RCP6.0 | 2085 | 75.6073 | 81.5796 | 87.9006 | 94.1825 | 100.4665
| GuthrieWind2090RCP6.0 | Guthrie | Wind | RCP6.0 | 2090 | 75.9625 | 82.0168 | 88.4367 | 94.8051 | 101.1773
| GuthrieWind2095RCP6.0 | Guthrie | Wind | RCP6.0 | 2095 | 76.2323 | 82.3421 | 88.8265 | 95.253 | 101.6871
| GuthrieWind2100RCP6.0 | Guthrie | Wind | RCP6.0 | 2100 | 76.5021 | 82.6673 | 89.2164 | 95.7008 | 102.1969
| GuthrieWind2023RCP8.5 | Guthrie | Wind | RCP8.5 | 2023 | 74.6382 | 80.4039 | 86.473 | 92.5445 | 98.6086
| GuthrieWind2025RCP8.5 | Guthrie | Wind | RCP8.5 | 2025 | 74.6803 | 80.4572 | 86.5418 | 92.6243 | 98.7034
| GuthrieWind2030RCP8.5 | Guthrie | Wind | RCP8.5 | 2030 | 74.7224 | 80.5105 | 86.6106 | 92.704 | 98.7982
| GuthrieWind2035RCP8.5 | Guthrie | Wind | RCP8.5 | 2035 | 74.7645 | 80.5639 | 86.6794 | 92.7838 | 98.8929
| GuthrieWind2040RCP8.5 | Guthrie | Wind | RCP8.5 | 2040 | 74.96 | 80.7905 | 86.9403 | 93.0752 | 99.2165
| GuthrieWind2045RCP8.5 | Guthrie | Wind | RCP8.5 | 2045 | 75.1556 | 81.0171 | 87.2011 | 93.3666 | 99.54
| GuthrieWind2050RCP8.5 | Guthrie | Wind | RCP8.5 | 2050 | 75.465 | 81.393 | 87.6569 | 93.8911 | 100.1315
| GuthrieWind2055RCP8.5 | Guthrie | Wind | RCP8.5 | 2055 | 75.5788 | 81.5423 | 87.8519 | 94.1242 | 100.3995
| GuthrieWind2060RCP8.5 | Guthrie | Wind | RCP8.5 | 2060 | 75.9625 | 82.0168 | 88.4367 | 94.8051 | 101.1773
| GuthrieWind2065RCP8.5 | Guthrie | Wind | RCP8.5 | 2065 | 76.2323 | 82.3421 | 88.8265 | 95.253 | 101.6871
| GuthrieWind2070RCP8.5 | Guthrie | Wind | RCP8.5 | 2070 | 76.6457 | 82.8406 | 89.4314 | 95.9493 | 102.4779
| GuthrieWind2075RCP8.5 | Guthrie | Wind | RCP8.5 | 2075 | 76.7893 | 83.0139 | 89.6464 | 96.1977 | 102.759
| GuthrieWind2080RCP8.5 | Guthrie | Wind | RCP8.5 | 2080 | 76.9328 | 83.1872 | 89.8614 | 96.4462 | 103.04
| GuthrieWind2085RCP8.5 | Guthrie | Wind | RCP8.5 | 2085 | 76.9625 | 83.2192 | 89.8915 | 96.4784 | 103.0695
| GuthrieWind2090RCP8.5 | Guthrie | Wind | RCP8.5 | 2090 | 76.9922 | 83.2512 | 89.9216 | 96.5106 | 103.0989
| GuthrieWind2095RCP8.5 | Guthrie | Wind | RCP8.5 | 2095 | 76.9922 | 83.2512 | 89.9216 | 96.5106 | 103.0989
| GuthrieWind2100RCP8.5 | Guthrie | Wind | RCP8.5 | 2100 | 76.9922 | 83.2512 | 89.9216 | 96.5106 | 103.0989
| HaileyburyIce Accretion2023RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2023 | 14.7519 | 17.6458 | 21.32 | 24.1142 | 26.9136
| HaileyburyIce Accretion2025RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2025 | 14.7311 | 17.6209 | 21.2867 | 24.0765 | 26.8716
| HaileyburyIce Accretion2030RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2030 | 14.7102 | 17.596 | 21.2533 | 24.0389 | 26.8296
| HaileyburyIce Accretion2035RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2035 | 14.6893 | 17.5711 | 21.22 | 24.0012 | 26.7876
| HaileyburyIce Accretion2040RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2040 | 14.6684 | 17.5462 | 21.1867 | 23.9635 | 26.7456
| HaileyburyIce Accretion2045RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2045 | 14.6476 | 17.5213 | 21.1533 | 23.9259 | 26.7036
| HaileyburyIce Accretion2050RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2050 | 14.635 | 17.5064 | 21.128 | 23.8972 | 26.6717
| HaileyburyIce Accretion2055RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2055 | 14.6434 | 17.5163 | 21.136 | 23.9063 | 26.6818
| HaileyburyIce Accretion2060RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2060 | 14.6517 | 17.5263 | 21.144 | 23.9153 | 26.6918
| HaileyburyIce Accretion2065RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2065 | 14.6601 | 17.5362 | 21.152 | 23.9244 | 26.7019
| HaileyburyIce Accretion2070RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2070 | 14.6684 | 17.5462 | 21.16 | 23.9334 | 26.712
| HaileyburyIce Accretion2075RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2075 | 14.7055 | 17.5988 | 21.2367 | 24.0276 | 26.8212
| HaileyburyIce Accretion2080RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2080 | 14.7427 | 17.6513 | 21.3133 | 24.1217 | 26.9304
| HaileyburyIce Accretion2085RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2085 | 14.7798 | 17.7039 | 21.39 | 24.2159 | 27.0396
| HaileyburyIce Accretion2090RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2090 | 14.8169 | 17.7565 | 21.4667 | 24.3101 | 27.1488
| HaileyburyIce Accretion2095RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2095 | 14.854 | 17.809 | 21.5433 | 24.4042 | 27.258
| HaileyburyIce Accretion2100RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2100 | 14.8911 | 17.8616 | 21.62 | 24.4984 | 27.3672
| HaileyburyIce Accretion2023RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2023 | 14.7519 | 17.6458 | 21.32 | 24.1142 | 26.9136
| HaileyburyIce Accretion2025RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2025 | 14.7311 | 17.6209 | 21.2867 | 24.0765 | 26.8716
| HaileyburyIce Accretion2030RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2030 | 14.7102 | 17.596 | 21.2533 | 24.0389 | 26.8296
| HaileyburyIce Accretion2035RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2035 | 14.6893 | 17.5711 | 21.22 | 24.0012 | 26.7876
| HaileyburyIce Accretion2040RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2040 | 14.6684 | 17.5462 | 21.1867 | 23.9635 | 26.7456
| HaileyburyIce Accretion2045RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2045 | 14.6476 | 17.5213 | 21.1533 | 23.9259 | 26.7036
| HaileyburyIce Accretion2050RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2050 | 14.635 | 17.5064 | 21.128 | 23.8972 | 26.6717
| HaileyburyIce Accretion2055RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2055 | 14.6434 | 17.5163 | 21.136 | 23.9063 | 26.6818
| HaileyburyIce Accretion2060RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2060 | 14.6517 | 17.5263 | 21.144 | 23.9153 | 26.6918
| HaileyburyIce Accretion2065RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2065 | 14.6601 | 17.5362 | 21.152 | 23.9244 | 26.7019
| HaileyburyIce Accretion2070RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2070 | 14.6684 | 17.5462 | 21.16 | 23.9334 | 26.712
| HaileyburyIce Accretion2075RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2075 | 14.7241 | 17.625 | 21.275 | 24.0746 | 26.8758
| HaileyburyIce Accretion2080RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2080 | 14.7798 | 17.7039 | 21.39 | 24.2159 | 27.0396
| HaileyburyIce Accretion2085RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2085 | 14.8354 | 17.7828 | 21.505 | 24.3571 | 27.2034
| HaileyburyIce Accretion2090RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2090 | 14.9375 | 17.9225 | 21.7067 | 24.6039 | 27.4848
| HaileyburyIce Accretion2095RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2095 | 14.9839 | 17.9833 | 21.7933 | 24.7093 | 27.6024
| HaileyburyIce Accretion2100RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2100 | 15.0303 | 18.0442 | 21.88 | 24.8148 | 27.72
| HaileyburyIce Accretion2023RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2023 | 14.7519 | 17.6458 | 21.32 | 24.1142 | 26.9136
| HaileyburyIce Accretion2025RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2025 | 14.7102 | 17.596 | 21.2533 | 24.0389 | 26.8296
| HaileyburyIce Accretion2030RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2030 | 14.6684 | 17.5462 | 21.1867 | 23.9635 | 26.7456
| HaileyburyIce Accretion2035RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2035 | 14.6267 | 17.4964 | 21.12 | 23.8882 | 26.6616
| HaileyburyIce Accretion2040RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2040 | 14.6406 | 17.513 | 21.1333 | 23.9033 | 26.6784
| HaileyburyIce Accretion2045RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2045 | 14.6545 | 17.5296 | 21.1467 | 23.9183 | 26.6952
| HaileyburyIce Accretion2050RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2050 | 14.7427 | 17.6513 | 21.3133 | 24.1217 | 26.9304
| HaileyburyIce Accretion2055RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2055 | 14.8169 | 17.7565 | 21.4667 | 24.3101 | 27.1488
| HaileyburyIce Accretion2060RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2060 | 14.9375 | 17.9225 | 21.7067 | 24.6039 | 27.4848
| HaileyburyIce Accretion2065RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2065 | 14.9839 | 17.9833 | 21.7933 | 24.7093 | 27.6024
| HaileyburyIce Accretion2070RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2070 | 14.8633 | 17.8616 | 21.6667 | 24.5737 | 27.4596
| HaileyburyIce Accretion2075RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2075 | 14.6963 | 17.679 | 21.4533 | 24.3327 | 27.1992
| HaileyburyIce Accretion2080RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2080 | 14.5293 | 17.4964 | 21.24 | 24.0916 | 26.9388
| HaileyburyIce Accretion2085RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2085 | 14.5641 | 17.5711 | 21.36 | 24.2611 | 27.1404
| HaileyburyIce Accretion2090RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2090 | 14.5989 | 17.6458 | 21.48 | 24.4306 | 27.342
| HaileyburyIce Accretion2095RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2095 | 14.5989 | 17.6458 | 21.48 | 24.4306 | 27.342
| HaileyburyIce Accretion2100RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2100 | 14.5989 | 17.6458 | 21.48 | 24.4306 | 27.342
| HaileyburyWind2023RCP4.5 | Haileybury | Wind | RCP4.5 | 2023 | 76.1156 | 81.9218 | 88.0088 | 94.1129 | 100.2197
| HaileyburyWind2025RCP4.5 | Haileybury | Wind | RCP4.5 | 2025 | 76.122 | 81.9259 | 88.0132 | 94.1176 | 100.223
| HaileyburyWind2030RCP4.5 | Haileybury | Wind | RCP4.5 | 2030 | 76.1283 | 81.93 | 88.0176 | 94.1223 | 100.2264
| HaileyburyWind2035RCP4.5 | Haileybury | Wind | RCP4.5 | 2035 | 76.1346 | 81.9341 | 88.022 | 94.127 | 100.2297
| HaileyburyWind2040RCP4.5 | Haileybury | Wind | RCP4.5 | 2040 | 76.141 | 81.9382 | 88.0264 | 94.1318 | 100.2331
| HaileyburyWind2045RCP4.5 | Haileybury | Wind | RCP4.5 | 2045 | 76.1473 | 81.9423 | 88.0308 | 94.1365 | 100.2364
| HaileyburyWind2050RCP4.5 | Haileybury | Wind | RCP4.5 | 2050 | 76.1551 | 81.9448 | 88.0246 | 94.1261 | 100.2197
| HaileyburyWind2055RCP4.5 | Haileybury | Wind | RCP4.5 | 2055 | 76.1567 | 81.9431 | 88.0141 | 94.111 | 100.1996
| HaileyburyWind2060RCP4.5 | Haileybury | Wind | RCP4.5 | 2060 | 76.1582 | 81.9415 | 88.0035 | 94.096 | 100.1796
| HaileyburyWind2065RCP4.5 | Haileybury | Wind | RCP4.5 | 2065 | 76.1597 | 81.9398 | 87.993 | 94.0809 | 100.1595
| HaileyburyWind2070RCP4.5 | Haileybury | Wind | RCP4.5 | 2070 | 76.1612 | 81.9382 | 87.9824 | 94.0658 | 100.1394
| HaileyburyWind2075RCP4.5 | Haileybury | Wind | RCP4.5 | 2075 | 76.2182 | 82.0078 | 88.0689 | 94.1647 | 100.2514
| HaileyburyWind2080RCP4.5 | Haileybury | Wind | RCP4.5 | 2080 | 76.2752 | 82.0773 | 88.1555 | 94.2636 | 100.3635
| HaileyburyWind2085RCP4.5 | Haileybury | Wind | RCP4.5 | 2085 | 76.3322 | 82.1469 | 88.242 | 94.3624 | 100.4755
| HaileyburyWind2090RCP4.5 | Haileybury | Wind | RCP4.5 | 2090 | 76.3892 | 82.2165 | 88.3285 | 94.4613 | 100.5875
| HaileyburyWind2095RCP4.5 | Haileybury | Wind | RCP4.5 | 2095 | 76.4462 | 82.286 | 88.4151 | 94.5602 | 100.6995
| HaileyburyWind2100RCP4.5 | Haileybury | Wind | RCP4.5 | 2100 | 76.5032 | 82.3556 | 88.5016 | 94.659 | 100.8116
| HaileyburyWind2023RCP6.0 | Haileybury | Wind | RCP6.0 | 2023 | 76.1156 | 81.9218 | 88.0088 | 94.1129 | 100.2197
| HaileyburyWind2025RCP6.0 | Haileybury | Wind | RCP6.0 | 2025 | 76.122 | 81.9259 | 88.0132 | 94.1176 | 100.223
| HaileyburyWind2030RCP6.0 | Haileybury | Wind | RCP6.0 | 2030 | 76.1283 | 81.93 | 88.0176 | 94.1223 | 100.2264
| HaileyburyWind2035RCP6.0 | Haileybury | Wind | RCP6.0 | 2035 | 76.1346 | 81.9341 | 88.022 | 94.127 | 100.2297
| HaileyburyWind2040RCP6.0 | Haileybury | Wind | RCP6.0 | 2040 | 76.141 | 81.9382 | 88.0264 | 94.1318 | 100.2331
| HaileyburyWind2045RCP6.0 | Haileybury | Wind | RCP6.0 | 2045 | 76.1473 | 81.9423 | 88.0308 | 94.1365 | 100.2364
| HaileyburyWind2050RCP6.0 | Haileybury | Wind | RCP6.0 | 2050 | 76.1551 | 81.9448 | 88.0246 | 94.1261 | 100.2197
| HaileyburyWind2055RCP6.0 | Haileybury | Wind | RCP6.0 | 2055 | 76.1567 | 81.9431 | 88.0141 | 94.111 | 100.1996
| HaileyburyWind2060RCP6.0 | Haileybury | Wind | RCP6.0 | 2060 | 76.1582 | 81.9415 | 88.0035 | 94.096 | 100.1796
| HaileyburyWind2065RCP6.0 | Haileybury | Wind | RCP6.0 | 2065 | 76.1597 | 81.9398 | 87.993 | 94.0809 | 100.1595
| HaileyburyWind2070RCP6.0 | Haileybury | Wind | RCP6.0 | 2070 | 76.1612 | 81.9382 | 87.9824 | 94.0658 | 100.1394
| HaileyburyWind2075RCP6.0 | Haileybury | Wind | RCP6.0 | 2075 | 76.2467 | 82.0426 | 88.1122 | 94.2141 | 100.3075
| HaileyburyWind2080RCP6.0 | Haileybury | Wind | RCP6.0 | 2080 | 76.3322 | 82.1469 | 88.242 | 94.3624 | 100.4755
| HaileyburyWind2085RCP6.0 | Haileybury | Wind | RCP6.0 | 2085 | 76.4177 | 82.2512 | 88.3718 | 94.5107 | 100.6435
| HaileyburyWind2090RCP6.0 | Haileybury | Wind | RCP6.0 | 2090 | 76.493 | 82.331 | 88.4576 | 94.6026 | 100.7413
| HaileyburyWind2095RCP6.0 | Haileybury | Wind | RCP6.0 | 2095 | 76.4829 | 82.3065 | 88.4136 | 94.5461 | 100.6711
| HaileyburyWind2100RCP6.0 | Haileybury | Wind | RCP6.0 | 2100 | 76.4728 | 82.2819 | 88.3696 | 94.4896 | 100.6009
| HaileyburyWind2023RCP8.5 | Haileybury | Wind | RCP8.5 | 2023 | 76.1156 | 81.9218 | 88.0088 | 94.1129 | 100.2197
| HaileyburyWind2025RCP8.5 | Haileybury | Wind | RCP8.5 | 2025 | 76.1283 | 81.93 | 88.0176 | 94.1223 | 100.2264
| HaileyburyWind2030RCP8.5 | Haileybury | Wind | RCP8.5 | 2030 | 76.141 | 81.9382 | 88.0264 | 94.1318 | 100.2331
| HaileyburyWind2035RCP8.5 | Haileybury | Wind | RCP8.5 | 2035 | 76.1536 | 81.9464 | 88.0352 | 94.1412 | 100.2397
| HaileyburyWind2040RCP8.5 | Haileybury | Wind | RCP8.5 | 2040 | 76.1562 | 81.9437 | 88.0176 | 94.1161 | 100.2063
| HaileyburyWind2045RCP8.5 | Haileybury | Wind | RCP8.5 | 2045 | 76.1587 | 81.9409 | 88 | 94.0909 | 100.1729
| HaileyburyWind2050RCP8.5 | Haileybury | Wind | RCP8.5 | 2050 | 76.2752 | 82.0773 | 88.1555 | 94.2636 | 100.3635
| HaileyburyWind2055RCP8.5 | Haileybury | Wind | RCP8.5 | 2055 | 76.3892 | 82.2165 | 88.3285 | 94.4613 | 100.5875
| HaileyburyWind2060RCP8.5 | Haileybury | Wind | RCP8.5 | 2060 | 76.493 | 82.331 | 88.4576 | 94.6026 | 100.7413
| HaileyburyWind2065RCP8.5 | Haileybury | Wind | RCP8.5 | 2065 | 76.4829 | 82.3065 | 88.4136 | 94.5461 | 100.6711
| HaileyburyWind2070RCP8.5 | Haileybury | Wind | RCP8.5 | 2070 | 76.5488 | 82.3665 | 88.4635 | 94.59 | 100.7112
| HaileyburyWind2075RCP8.5 | Haileybury | Wind | RCP8.5 | 2075 | 76.6247 | 82.4511 | 88.5573 | 94.6904 | 100.8216
| HaileyburyWind2080RCP8.5 | Haileybury | Wind | RCP8.5 | 2080 | 76.7007 | 82.5356 | 88.6512 | 94.7909 | 100.932
| HaileyburyWind2085RCP8.5 | Haileybury | Wind | RCP8.5 | 2085 | 76.8299 | 82.7075 | 88.8756 | 95.0592 | 101.248
| HaileyburyWind2090RCP8.5 | Haileybury | Wind | RCP8.5 | 2090 | 76.9591 | 82.8794 | 89.1 | 95.3276 | 101.564
| HaileyburyWind2095RCP8.5 | Haileybury | Wind | RCP8.5 | 2095 | 76.9591 | 82.8794 | 89.1 | 95.3276 | 101.564
| HaileyburyWind2100RCP8.5 | Haileybury | Wind | RCP8.5 | 2100 | 76.9591 | 82.8794 | 89.1 | 95.3276 | 101.564
| Haldimand (Caledonia)Ice Accretion2023RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2023 | 23.2802 | 27.9096 | 33.796 | 38.2663 | 42.7543
| Haldimand (Caledonia)Ice Accretion2025RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2025 | 23.1619 | 27.7826 | 33.6543 | 38.119 | 42.5972
| Haldimand (Caledonia)Ice Accretion2030RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2030 | 23.0436 | 27.6556 | 33.5127 | 37.9718 | 42.4402
| Haldimand (Caledonia)Ice Accretion2035RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2035 | 22.9253 | 27.5286 | 33.371 | 37.8245 | 42.2831
| Haldimand (Caledonia)Ice Accretion2040RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2040 | 22.8071 | 27.4016 | 33.2293 | 37.6772 | 42.126
| Haldimand (Caledonia)Ice Accretion2045RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2045 | 22.6888 | 27.2746 | 33.0877 | 37.5299 | 41.9689
| Haldimand (Caledonia)Ice Accretion2050RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2050 | 22.2534 | 26.8034 | 32.572 | 36.9754 | 41.3749
| Haldimand (Caledonia)Ice Accretion2055RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2055 | 21.9364 | 26.4591 | 32.198 | 36.5682 | 40.9379
| Haldimand (Caledonia)Ice Accretion2060RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2060 | 21.6194 | 26.1148 | 31.824 | 36.1609 | 40.5009
| Haldimand (Caledonia)Ice Accretion2065RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2065 | 21.3024 | 25.7705 | 31.45 | 35.7537 | 40.064
| Haldimand (Caledonia)Ice Accretion2070RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2070 | 20.9853 | 25.4262 | 31.076 | 35.3464 | 39.627
| Haldimand (Caledonia)Ice Accretion2075RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2075 | 20.8828 | 25.3369 | 30.9967 | 35.276 | 39.5556
| Haldimand (Caledonia)Ice Accretion2080RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2080 | 20.7803 | 25.2475 | 30.9173 | 35.2055 | 39.4842
| Haldimand (Caledonia)Ice Accretion2085RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2085 | 20.6778 | 25.1581 | 30.838 | 35.1351 | 39.4128
| Haldimand (Caledonia)Ice Accretion2090RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2090 | 20.5752 | 25.0688 | 30.7587 | 35.0647 | 39.3414
| Haldimand (Caledonia)Ice Accretion2095RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2095 | 20.4727 | 24.9794 | 30.6793 | 34.9942 | 39.27
| Haldimand (Caledonia)Ice Accretion2100RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2100 | 20.3702 | 24.89 | 30.6 | 34.9238 | 39.1986
| Haldimand (Caledonia)Ice Accretion2023RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2023 | 23.2802 | 27.9096 | 33.796 | 38.2663 | 42.7543
| Haldimand (Caledonia)Ice Accretion2025RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2025 | 23.1619 | 27.7826 | 33.6543 | 38.119 | 42.5972
| Haldimand (Caledonia)Ice Accretion2030RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2030 | 23.0436 | 27.6556 | 33.5127 | 37.9718 | 42.4402
| Haldimand (Caledonia)Ice Accretion2035RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2035 | 22.9253 | 27.5286 | 33.371 | 37.8245 | 42.2831
| Haldimand (Caledonia)Ice Accretion2040RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2040 | 22.8071 | 27.4016 | 33.2293 | 37.6772 | 42.126
| Haldimand (Caledonia)Ice Accretion2045RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2045 | 22.6888 | 27.2746 | 33.0877 | 37.5299 | 41.9689
| Haldimand (Caledonia)Ice Accretion2050RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2050 | 22.2534 | 26.8034 | 32.572 | 36.9754 | 41.3749
| Haldimand (Caledonia)Ice Accretion2055RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2055 | 21.9364 | 26.4591 | 32.198 | 36.5682 | 40.9379
| Haldimand (Caledonia)Ice Accretion2060RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2060 | 21.6194 | 26.1148 | 31.824 | 36.1609 | 40.5009
| Haldimand (Caledonia)Ice Accretion2065RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2065 | 21.3024 | 25.7705 | 31.45 | 35.7537 | 40.064
| Haldimand (Caledonia)Ice Accretion2070RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2070 | 20.9853 | 25.4262 | 31.076 | 35.3464 | 39.627
| Haldimand (Caledonia)Ice Accretion2075RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2075 | 20.8315 | 25.2922 | 30.957 | 35.2407 | 39.5199
| Haldimand (Caledonia)Ice Accretion2080RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2080 | 20.6778 | 25.1581 | 30.838 | 35.1351 | 39.4128
| Haldimand (Caledonia)Ice Accretion2085RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2085 | 20.524 | 25.0241 | 30.719 | 35.0294 | 39.3057
| Haldimand (Caledonia)Ice Accretion2090RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2090 | 19.6999 | 24.1281 | 29.716 | 33.9505 | 38.1419
| Haldimand (Caledonia)Ice Accretion2095RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2095 | 19.0295 | 23.3662 | 28.832 | 32.9772 | 37.0852
| Haldimand (Caledonia)Ice Accretion2100RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2100 | 18.3592 | 22.6042 | 27.948 | 32.0039 | 36.0284
| Haldimand (Caledonia)Ice Accretion2023RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2023 | 23.2802 | 27.9096 | 33.796 | 38.2663 | 42.7543
| Haldimand (Caledonia)Ice Accretion2025RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2025 | 23.0436 | 27.6556 | 33.5127 | 37.9718 | 42.4402
| Haldimand (Caledonia)Ice Accretion2030RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2030 | 22.8071 | 27.4016 | 33.2293 | 37.6772 | 42.126
| Haldimand (Caledonia)Ice Accretion2035RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2035 | 22.5705 | 27.1476 | 32.946 | 37.3827 | 41.8118
| Haldimand (Caledonia)Ice Accretion2040RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2040 | 22.0421 | 26.5738 | 32.3227 | 36.7039 | 41.0836
| Haldimand (Caledonia)Ice Accretion2045RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2045 | 21.5137 | 26 | 31.6993 | 36.0252 | 40.3553
| Haldimand (Caledonia)Ice Accretion2050RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2050 | 20.7803 | 25.2475 | 30.9173 | 35.2055 | 39.4842
| Haldimand (Caledonia)Ice Accretion2055RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2055 | 20.5752 | 25.0688 | 30.7587 | 35.0647 | 39.3414
| Haldimand (Caledonia)Ice Accretion2060RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2060 | 19.6999 | 24.1281 | 29.716 | 33.9505 | 38.1419
| Haldimand (Caledonia)Ice Accretion2065RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2065 | 19.0295 | 23.3662 | 28.832 | 32.9772 | 37.0852
| Haldimand (Caledonia)Ice Accretion2070RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2070 | 17.9255 | 22.1245 | 27.4153 | 31.4148 | 35.4001
| Haldimand (Caledonia)Ice Accretion2075RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2075 | 17.4917 | 21.6447 | 26.8827 | 30.8256 | 34.7718
| Haldimand (Caledonia)Ice Accretion2080RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2080 | 17.058 | 21.165 | 26.35 | 30.2365 | 34.1435
| Haldimand (Caledonia)Ice Accretion2085RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2085 | 15.8987 | 19.8104 | 24.701 | 28.3924 | 32.0872
| Haldimand (Caledonia)Ice Accretion2090RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2090 | 14.7394 | 18.4559 | 23.052 | 26.5482 | 30.0308
| Haldimand (Caledonia)Ice Accretion2095RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2095 | 14.7394 | 18.4559 | 23.052 | 26.5482 | 30.0308
| Haldimand (Caledonia)Ice Accretion2100RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2100 | 14.7394 | 18.4559 | 23.052 | 26.5482 | 30.0308
| Haldimand (Caledonia)Wind2023RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2023 | 87.6216 | 94.4654 | 101.6969 | 108.9021 | 116.1072
| Haldimand (Caledonia)Wind2025RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2025 | 87.6405 | 94.4983 | 101.7474 | 108.967 | 116.1878
| Haldimand (Caledonia)Wind2030RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2030 | 87.6594 | 94.5312 | 101.7979 | 109.0318 | 116.2684
| Haldimand (Caledonia)Wind2035RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2035 | 87.6783 | 94.564 | 101.8484 | 109.0967 | 116.349
| Haldimand (Caledonia)Wind2040RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2040 | 87.6972 | 94.5969 | 101.8989 | 109.1615 | 116.4296
| Haldimand (Caledonia)Wind2045RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2045 | 87.7161 | 94.6298 | 101.9494 | 109.2263 | 116.5102
| Haldimand (Caledonia)Wind2050RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2050 | 87.8083 | 94.7585 | 102.1231 | 109.4403 | 116.7658
| Haldimand (Caledonia)Wind2055RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2055 | 87.8815 | 94.8543 | 102.2463 | 109.5895 | 116.9408
| Haldimand (Caledonia)Wind2060RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2060 | 87.9548 | 94.9501 | 102.3696 | 109.7386 | 117.1158
| Haldimand (Caledonia)Wind2065RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2065 | 88.028 | 95.0459 | 102.4928 | 109.8877 | 117.2908
| Haldimand (Caledonia)Wind2070RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2070 | 88.1013 | 95.1417 | 102.616 | 110.0369 | 117.4658
| Haldimand (Caledonia)Wind2075RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2075 | 88.2103 | 95.2873 | 102.8062 | 110.2638 | 117.7326
| Haldimand (Caledonia)Wind2080RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2080 | 88.3193 | 95.4329 | 102.9964 | 110.4908 | 117.9993
| Haldimand (Caledonia)Wind2085RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2085 | 88.4283 | 95.5785 | 103.1867 | 110.7177 | 118.2661
| Haldimand (Caledonia)Wind2090RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2090 | 88.5373 | 95.7241 | 103.3769 | 110.9447 | 118.5328
| Haldimand (Caledonia)Wind2095RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2095 | 88.6464 | 95.8697 | 103.5671 | 111.1716 | 118.7995
| Haldimand (Caledonia)Wind2100RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2100 | 88.7554 | 96.0152 | 103.7573 | 111.3986 | 119.0663
| Haldimand (Caledonia)Wind2023RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2023 | 87.6216 | 94.4654 | 101.6969 | 108.9021 | 116.1072
| Haldimand (Caledonia)Wind2025RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2025 | 87.6405 | 94.4983 | 101.7474 | 108.967 | 116.1878
| Haldimand (Caledonia)Wind2030RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2030 | 87.6594 | 94.5312 | 101.7979 | 109.0318 | 116.2684
| Haldimand (Caledonia)Wind2035RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2035 | 87.6783 | 94.564 | 101.8484 | 109.0967 | 116.349
| Haldimand (Caledonia)Wind2040RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2040 | 87.6972 | 94.5969 | 101.8989 | 109.1615 | 116.4296
| Haldimand (Caledonia)Wind2045RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2045 | 87.7161 | 94.6298 | 101.9494 | 109.2263 | 116.5102
| Haldimand (Caledonia)Wind2050RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2050 | 87.8083 | 94.7585 | 102.1231 | 109.4403 | 116.7658
| Haldimand (Caledonia)Wind2055RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2055 | 87.8815 | 94.8543 | 102.2463 | 109.5895 | 116.9408
| Haldimand (Caledonia)Wind2060RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2060 | 87.9548 | 94.9501 | 102.3696 | 109.7386 | 117.1158
| Haldimand (Caledonia)Wind2065RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2065 | 88.028 | 95.0459 | 102.4928 | 109.8877 | 117.2908
| Haldimand (Caledonia)Wind2070RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2070 | 88.1013 | 95.1417 | 102.616 | 110.0369 | 117.4658
| Haldimand (Caledonia)Wind2075RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2075 | 88.2648 | 95.3601 | 102.9013 | 110.3773 | 117.8659
| Haldimand (Caledonia)Wind2080RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2080 | 88.4283 | 95.5785 | 103.1867 | 110.7177 | 118.2661
| Haldimand (Caledonia)Wind2085RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2085 | 88.5919 | 95.7969 | 103.472 | 111.0581 | 118.6662
| Haldimand (Caledonia)Wind2090RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2090 | 89.0781 | 96.4254 | 104.2825 | 112.0218 | 119.7878
| Haldimand (Caledonia)Wind2095RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2095 | 89.4007 | 96.8356 | 104.8077 | 112.645 | 120.5094
| Haldimand (Caledonia)Wind2100RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2100 | 89.7234 | 97.2457 | 105.3329 | 113.2682 | 121.2309
| Haldimand (Caledonia)Wind2023RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2023 | 87.6216 | 94.4654 | 101.6969 | 108.9021 | 116.1072
| Haldimand (Caledonia)Wind2025RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2025 | 87.6594 | 94.5312 | 101.7979 | 109.0318 | 116.2684
| Haldimand (Caledonia)Wind2030RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2030 | 87.6972 | 94.5969 | 101.8989 | 109.1615 | 116.4296
| Haldimand (Caledonia)Wind2035RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2035 | 87.735 | 94.6627 | 101.9999 | 109.2912 | 116.5908
| Haldimand (Caledonia)Wind2040RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2040 | 87.8571 | 94.8223 | 102.2053 | 109.5398 | 116.8825
| Haldimand (Caledonia)Wind2045RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2045 | 87.9792 | 94.982 | 102.4106 | 109.7883 | 117.1741
| Haldimand (Caledonia)Wind2050RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2050 | 88.3193 | 95.4329 | 102.9964 | 110.4908 | 117.9993
| Haldimand (Caledonia)Wind2055RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2055 | 88.5373 | 95.7241 | 103.3769 | 110.9447 | 118.5328
| Haldimand (Caledonia)Wind2060RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2060 | 89.0781 | 96.4254 | 104.2825 | 112.0218 | 119.7878
| Haldimand (Caledonia)Wind2065RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2065 | 89.4007 | 96.8356 | 104.8077 | 112.645 | 120.5094
| Haldimand (Caledonia)Wind2070RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2070 | 89.9037 | 97.4962 | 105.6763 | 113.686 | 121.726
| Haldimand (Caledonia)Wind2075RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2075 | 90.0839 | 97.7467 | 106.0197 | 114.1039 | 122.2211
| Haldimand (Caledonia)Wind2080RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2080 | 90.2641 | 97.9972 | 106.3631 | 114.5218 | 122.7162
| Haldimand (Caledonia)Wind2085RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2085 | 90.5389 | 98.3682 | 106.8479 | 115.1108 | 123.4071
| Haldimand (Caledonia)Wind2090RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2090 | 90.8136 | 98.7392 | 107.3327 | 115.6997 | 124.0979
| Haldimand (Caledonia)Wind2095RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2095 | 90.8136 | 98.7392 | 107.3327 | 115.6997 | 124.0979
| Haldimand (Caledonia)Wind2100RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2100 | 90.8136 | 98.7392 | 107.3327 | 115.6997 | 124.0979
| Haldimand (Hagersville)Ice Accretion2023RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2023 | 23.2802 | 27.9096 | 33.796 | 38.2663 | 42.7543
| Haldimand (Hagersville)Ice Accretion2025RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2025 | 23.1619 | 27.7826 | 33.6543 | 38.119 | 42.5972
| Haldimand (Hagersville)Ice Accretion2030RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2030 | 23.0436 | 27.6556 | 33.5127 | 37.9718 | 42.4402
| Haldimand (Hagersville)Ice Accretion2035RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2035 | 22.9253 | 27.5286 | 33.371 | 37.8245 | 42.2831
| Haldimand (Hagersville)Ice Accretion2040RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2040 | 22.8071 | 27.4016 | 33.2293 | 37.6772 | 42.126
| Haldimand (Hagersville)Ice Accretion2045RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2045 | 22.6888 | 27.2746 | 33.0877 | 37.5299 | 41.9689
| Haldimand (Hagersville)Ice Accretion2050RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2050 | 22.2534 | 26.8034 | 32.572 | 36.9754 | 41.3749
| Haldimand (Hagersville)Ice Accretion2055RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2055 | 21.9364 | 26.4591 | 32.198 | 36.5682 | 40.9379
| Haldimand (Hagersville)Ice Accretion2060RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2060 | 21.6194 | 26.1148 | 31.824 | 36.1609 | 40.5009
| Haldimand (Hagersville)Ice Accretion2065RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2065 | 21.3024 | 25.7705 | 31.45 | 35.7537 | 40.064
| Haldimand (Hagersville)Ice Accretion2070RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2070 | 20.9853 | 25.4262 | 31.076 | 35.3464 | 39.627
| Haldimand (Hagersville)Ice Accretion2075RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2075 | 20.8828 | 25.3369 | 30.9967 | 35.276 | 39.5556
| Haldimand (Hagersville)Ice Accretion2080RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2080 | 20.7803 | 25.2475 | 30.9173 | 35.2055 | 39.4842
| Haldimand (Hagersville)Ice Accretion2085RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2085 | 20.6778 | 25.1581 | 30.838 | 35.1351 | 39.4128
| Haldimand (Hagersville)Ice Accretion2090RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2090 | 20.5752 | 25.0688 | 30.7587 | 35.0647 | 39.3414
| Haldimand (Hagersville)Ice Accretion2095RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2095 | 20.4727 | 24.9794 | 30.6793 | 34.9942 | 39.27
| Haldimand (Hagersville)Ice Accretion2100RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2100 | 20.3702 | 24.89 | 30.6 | 34.9238 | 39.1986
| Haldimand (Hagersville)Ice Accretion2023RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2023 | 23.2802 | 27.9096 | 33.796 | 38.2663 | 42.7543
| Haldimand (Hagersville)Ice Accretion2025RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2025 | 23.1619 | 27.7826 | 33.6543 | 38.119 | 42.5972
| Haldimand (Hagersville)Ice Accretion2030RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2030 | 23.0436 | 27.6556 | 33.5127 | 37.9718 | 42.4402
| Haldimand (Hagersville)Ice Accretion2035RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2035 | 22.9253 | 27.5286 | 33.371 | 37.8245 | 42.2831
| Haldimand (Hagersville)Ice Accretion2040RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2040 | 22.8071 | 27.4016 | 33.2293 | 37.6772 | 42.126
| Haldimand (Hagersville)Ice Accretion2045RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2045 | 22.6888 | 27.2746 | 33.0877 | 37.5299 | 41.9689
| Haldimand (Hagersville)Ice Accretion2050RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2050 | 22.2534 | 26.8034 | 32.572 | 36.9754 | 41.3749
| Haldimand (Hagersville)Ice Accretion2055RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2055 | 21.9364 | 26.4591 | 32.198 | 36.5682 | 40.9379
| Haldimand (Hagersville)Ice Accretion2060RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2060 | 21.6194 | 26.1148 | 31.824 | 36.1609 | 40.5009
| Haldimand (Hagersville)Ice Accretion2065RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2065 | 21.3024 | 25.7705 | 31.45 | 35.7537 | 40.064
| Haldimand (Hagersville)Ice Accretion2070RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2070 | 20.9853 | 25.4262 | 31.076 | 35.3464 | 39.627
| Haldimand (Hagersville)Ice Accretion2075RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2075 | 20.8315 | 25.2922 | 30.957 | 35.2407 | 39.5199
| Haldimand (Hagersville)Ice Accretion2080RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2080 | 20.6778 | 25.1581 | 30.838 | 35.1351 | 39.4128
| Haldimand (Hagersville)Ice Accretion2085RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2085 | 20.524 | 25.0241 | 30.719 | 35.0294 | 39.3057
| Haldimand (Hagersville)Ice Accretion2090RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2090 | 19.6999 | 24.1281 | 29.716 | 33.9505 | 38.1419
| Haldimand (Hagersville)Ice Accretion2095RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2095 | 19.0295 | 23.3662 | 28.832 | 32.9772 | 37.0852
| Haldimand (Hagersville)Ice Accretion2100RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2100 | 18.3592 | 22.6042 | 27.948 | 32.0039 | 36.0284
| Haldimand (Hagersville)Ice Accretion2023RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2023 | 23.2802 | 27.9096 | 33.796 | 38.2663 | 42.7543
| Haldimand (Hagersville)Ice Accretion2025RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2025 | 23.0436 | 27.6556 | 33.5127 | 37.9718 | 42.4402
| Haldimand (Hagersville)Ice Accretion2030RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2030 | 22.8071 | 27.4016 | 33.2293 | 37.6772 | 42.126
| Haldimand (Hagersville)Ice Accretion2035RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2035 | 22.5705 | 27.1476 | 32.946 | 37.3827 | 41.8118
| Haldimand (Hagersville)Ice Accretion2040RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2040 | 22.0421 | 26.5738 | 32.3227 | 36.7039 | 41.0836
| Haldimand (Hagersville)Ice Accretion2045RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2045 | 21.5137 | 26 | 31.6993 | 36.0252 | 40.3553
| Haldimand (Hagersville)Ice Accretion2050RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2050 | 20.7803 | 25.2475 | 30.9173 | 35.2055 | 39.4842
| Haldimand (Hagersville)Ice Accretion2055RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2055 | 20.5752 | 25.0688 | 30.7587 | 35.0647 | 39.3414
| Haldimand (Hagersville)Ice Accretion2060RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2060 | 19.6999 | 24.1281 | 29.716 | 33.9505 | 38.1419
| Haldimand (Hagersville)Ice Accretion2065RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2065 | 19.0295 | 23.3662 | 28.832 | 32.9772 | 37.0852
| Haldimand (Hagersville)Ice Accretion2070RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2070 | 17.9255 | 22.1245 | 27.4153 | 31.4148 | 35.4001
| Haldimand (Hagersville)Ice Accretion2075RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2075 | 17.4917 | 21.6447 | 26.8827 | 30.8256 | 34.7718
| Haldimand (Hagersville)Ice Accretion2080RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2080 | 17.058 | 21.165 | 26.35 | 30.2365 | 34.1435
| Haldimand (Hagersville)Ice Accretion2085RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2085 | 15.8987 | 19.8104 | 24.701 | 28.3924 | 32.0872
| Haldimand (Hagersville)Ice Accretion2090RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2090 | 14.7394 | 18.4559 | 23.052 | 26.5482 | 30.0308
| Haldimand (Hagersville)Ice Accretion2095RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2095 | 14.7394 | 18.4559 | 23.052 | 26.5482 | 30.0308
| Haldimand (Hagersville)Ice Accretion2100RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2100 | 14.7394 | 18.4559 | 23.052 | 26.5482 | 30.0308
| Haldimand (Hagersville)Wind2023RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2023 | 87.6216 | 94.4654 | 101.6969 | 108.9021 | 116.1072
| Haldimand (Hagersville)Wind2025RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2025 | 87.6405 | 94.4983 | 101.7474 | 108.967 | 116.1878
| Haldimand (Hagersville)Wind2030RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2030 | 87.6594 | 94.5312 | 101.7979 | 109.0318 | 116.2684
| Haldimand (Hagersville)Wind2035RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2035 | 87.6783 | 94.564 | 101.8484 | 109.0967 | 116.349
| Haldimand (Hagersville)Wind2040RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2040 | 87.6972 | 94.5969 | 101.8989 | 109.1615 | 116.4296
| Haldimand (Hagersville)Wind2045RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2045 | 87.7161 | 94.6298 | 101.9494 | 109.2263 | 116.5102
| Haldimand (Hagersville)Wind2050RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2050 | 87.8083 | 94.7585 | 102.1231 | 109.4403 | 116.7658
| Haldimand (Hagersville)Wind2055RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2055 | 87.8815 | 94.8543 | 102.2463 | 109.5895 | 116.9408
| Haldimand (Hagersville)Wind2060RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2060 | 87.9548 | 94.9501 | 102.3696 | 109.7386 | 117.1158
| Haldimand (Hagersville)Wind2065RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2065 | 88.028 | 95.0459 | 102.4928 | 109.8877 | 117.2908
| Haldimand (Hagersville)Wind2070RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2070 | 88.1013 | 95.1417 | 102.616 | 110.0369 | 117.4658
| Haldimand (Hagersville)Wind2075RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2075 | 88.2103 | 95.2873 | 102.8062 | 110.2638 | 117.7326
| Haldimand (Hagersville)Wind2080RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2080 | 88.3193 | 95.4329 | 102.9964 | 110.4908 | 117.9993
| Haldimand (Hagersville)Wind2085RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2085 | 88.4283 | 95.5785 | 103.1867 | 110.7177 | 118.2661
| Haldimand (Hagersville)Wind2090RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2090 | 88.5373 | 95.7241 | 103.3769 | 110.9447 | 118.5328
| Haldimand (Hagersville)Wind2095RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2095 | 88.6464 | 95.8697 | 103.5671 | 111.1716 | 118.7995
| Haldimand (Hagersville)Wind2100RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2100 | 88.7554 | 96.0152 | 103.7573 | 111.3986 | 119.0663
| Haldimand (Hagersville)Wind2023RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2023 | 87.6216 | 94.4654 | 101.6969 | 108.9021 | 116.1072
| Haldimand (Hagersville)Wind2025RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2025 | 87.6405 | 94.4983 | 101.7474 | 108.967 | 116.1878
| Haldimand (Hagersville)Wind2030RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2030 | 87.6594 | 94.5312 | 101.7979 | 109.0318 | 116.2684
| Haldimand (Hagersville)Wind2035RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2035 | 87.6783 | 94.564 | 101.8484 | 109.0967 | 116.349
| Haldimand (Hagersville)Wind2040RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2040 | 87.6972 | 94.5969 | 101.8989 | 109.1615 | 116.4296
| Haldimand (Hagersville)Wind2045RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2045 | 87.7161 | 94.6298 | 101.9494 | 109.2263 | 116.5102
| Haldimand (Hagersville)Wind2050RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2050 | 87.8083 | 94.7585 | 102.1231 | 109.4403 | 116.7658
| Haldimand (Hagersville)Wind2055RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2055 | 87.8815 | 94.8543 | 102.2463 | 109.5895 | 116.9408
| Haldimand (Hagersville)Wind2060RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2060 | 87.9548 | 94.9501 | 102.3696 | 109.7386 | 117.1158
| Haldimand (Hagersville)Wind2065RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2065 | 88.028 | 95.0459 | 102.4928 | 109.8877 | 117.2908
| Haldimand (Hagersville)Wind2070RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2070 | 88.1013 | 95.1417 | 102.616 | 110.0369 | 117.4658
| Haldimand (Hagersville)Wind2075RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2075 | 88.2648 | 95.3601 | 102.9013 | 110.3773 | 117.8659
| Haldimand (Hagersville)Wind2080RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2080 | 88.4283 | 95.5785 | 103.1867 | 110.7177 | 118.2661
| Haldimand (Hagersville)Wind2085RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2085 | 88.5919 | 95.7969 | 103.472 | 111.0581 | 118.6662
| Haldimand (Hagersville)Wind2090RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2090 | 89.0781 | 96.4254 | 104.2825 | 112.0218 | 119.7878
| Haldimand (Hagersville)Wind2095RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2095 | 89.4007 | 96.8356 | 104.8077 | 112.645 | 120.5094
| Haldimand (Hagersville)Wind2100RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2100 | 89.7234 | 97.2457 | 105.3329 | 113.2682 | 121.2309
| Haldimand (Hagersville)Wind2023RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2023 | 87.6216 | 94.4654 | 101.6969 | 108.9021 | 116.1072
| Haldimand (Hagersville)Wind2025RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2025 | 87.6594 | 94.5312 | 101.7979 | 109.0318 | 116.2684
| Haldimand (Hagersville)Wind2030RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2030 | 87.6972 | 94.5969 | 101.8989 | 109.1615 | 116.4296
| Haldimand (Hagersville)Wind2035RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2035 | 87.735 | 94.6627 | 101.9999 | 109.2912 | 116.5908
| Haldimand (Hagersville)Wind2040RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2040 | 87.8571 | 94.8223 | 102.2053 | 109.5398 | 116.8825
| Haldimand (Hagersville)Wind2045RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2045 | 87.9792 | 94.982 | 102.4106 | 109.7883 | 117.1741
| Haldimand (Hagersville)Wind2050RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2050 | 88.3193 | 95.4329 | 102.9964 | 110.4908 | 117.9993
| Haldimand (Hagersville)Wind2055RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2055 | 88.5373 | 95.7241 | 103.3769 | 110.9447 | 118.5328
| Haldimand (Hagersville)Wind2060RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2060 | 89.0781 | 96.4254 | 104.2825 | 112.0218 | 119.7878
| Haldimand (Hagersville)Wind2065RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2065 | 89.4007 | 96.8356 | 104.8077 | 112.645 | 120.5094
| Haldimand (Hagersville)Wind2070RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2070 | 89.9037 | 97.4962 | 105.6763 | 113.686 | 121.726
| Haldimand (Hagersville)Wind2075RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2075 | 90.0839 | 97.7467 | 106.0197 | 114.1039 | 122.2211
| Haldimand (Hagersville)Wind2080RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2080 | 90.2641 | 97.9972 | 106.3631 | 114.5218 | 122.7162
| Haldimand (Hagersville)Wind2085RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2085 | 90.5389 | 98.3682 | 106.8479 | 115.1108 | 123.4071
| Haldimand (Hagersville)Wind2090RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2090 | 90.8136 | 98.7392 | 107.3327 | 115.6997 | 124.0979
| Haldimand (Hagersville)Wind2095RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2095 | 90.8136 | 98.7392 | 107.3327 | 115.6997 | 124.0979
| Haldimand (Hagersville)Wind2100RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2100 | 90.8136 | 98.7392 | 107.3327 | 115.6997 | 124.0979
| HaliburtonIce Accretion2023RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2023 | 16.8569 | 20.0652 | 24.125 | 27.233 | 30.366
| HaliburtonIce Accretion2025RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2025 | 16.8395 | 20.041 | 24.0917 | 27.1953 | 30.3188
| HaliburtonIce Accretion2030RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2030 | 16.8221 | 20.0168 | 24.0583 | 27.1577 | 30.2715
| HaliburtonIce Accretion2035RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2035 | 16.8047 | 19.9926 | 24.025 | 27.12 | 30.2242
| HaliburtonIce Accretion2040RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2040 | 16.7873 | 19.9684 | 23.9917 | 27.0823 | 30.177
| HaliburtonIce Accretion2045RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2045 | 16.7699 | 19.9442 | 23.9583 | 27.0447 | 30.1298
| HaliburtonIce Accretion2050RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2050 | 16.749 | 19.9324 | 23.965 | 27.0635 | 30.1581
| HaliburtonIce Accretion2055RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2055 | 16.7455 | 19.9449 | 24.005 | 27.12 | 30.2337
| HaliburtonIce Accretion2060RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2060 | 16.7421 | 19.9573 | 24.045 | 27.1765 | 30.3093
| HaliburtonIce Accretion2065RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2065 | 16.7386 | 19.9698 | 24.085 | 27.233 | 30.3849
| HaliburtonIce Accretion2070RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2070 | 16.7351 | 19.9823 | 24.125 | 27.2895 | 30.4605
| HaliburtonIce Accretion2075RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2075 | 16.8134 | 20.0929 | 24.2708 | 27.4637 | 30.66
| HaliburtonIce Accretion2080RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2080 | 16.8917 | 20.2036 | 24.4167 | 27.6379 | 30.8595
| HaliburtonIce Accretion2085RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2085 | 16.9699 | 20.3143 | 24.5625 | 27.8121 | 31.059
| HaliburtonIce Accretion2090RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2090 | 17.0482 | 20.4249 | 24.7083 | 27.9863 | 31.2585
| HaliburtonIce Accretion2095RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2095 | 17.1265 | 20.5356 | 24.8542 | 28.1605 | 31.458
| HaliburtonIce Accretion2100RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2100 | 17.2048 | 20.6462 | 25 | 28.3347 | 31.6575
| HaliburtonIce Accretion2023RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2023 | 16.8569 | 20.0652 | 24.125 | 27.233 | 30.366
| HaliburtonIce Accretion2025RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2025 | 16.8395 | 20.041 | 24.0917 | 27.1953 | 30.3188
| HaliburtonIce Accretion2030RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2030 | 16.8221 | 20.0168 | 24.0583 | 27.1577 | 30.2715
| HaliburtonIce Accretion2035RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2035 | 16.8047 | 19.9926 | 24.025 | 27.12 | 30.2242
| HaliburtonIce Accretion2040RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2040 | 16.7873 | 19.9684 | 23.9917 | 27.0823 | 30.177
| HaliburtonIce Accretion2045RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2045 | 16.7699 | 19.9442 | 23.9583 | 27.0447 | 30.1298
| HaliburtonIce Accretion2050RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2050 | 16.749 | 19.9324 | 23.965 | 27.0635 | 30.1581
| HaliburtonIce Accretion2055RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2055 | 16.7455 | 19.9449 | 24.005 | 27.12 | 30.2337
| HaliburtonIce Accretion2060RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2060 | 16.7421 | 19.9573 | 24.045 | 27.1765 | 30.3093
| HaliburtonIce Accretion2065RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2065 | 16.7386 | 19.9698 | 24.085 | 27.233 | 30.3849
| HaliburtonIce Accretion2070RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2070 | 16.7351 | 19.9823 | 24.125 | 27.2895 | 30.4605
| HaliburtonIce Accretion2075RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2075 | 16.8525 | 20.1483 | 24.3438 | 27.5508 | 30.7597
| HaliburtonIce Accretion2080RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2080 | 16.9699 | 20.3143 | 24.5625 | 27.8121 | 31.059
| HaliburtonIce Accretion2085RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2085 | 17.0874 | 20.4802 | 24.7812 | 28.0734 | 31.3582
| HaliburtonIce Accretion2090RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2090 | 17.3034 | 20.8053 | 25.2417 | 28.6361 | 32.0145
| HaliburtonIce Accretion2095RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2095 | 17.402 | 20.9644 | 25.4833 | 28.9374 | 32.3715
| HaliburtonIce Accretion2100RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2100 | 17.5005 | 21.1235 | 25.725 | 29.2387 | 32.7285
| HaliburtonIce Accretion2023RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2023 | 16.8569 | 20.0652 | 24.125 | 27.233 | 30.366
| HaliburtonIce Accretion2025RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2025 | 16.8221 | 20.0168 | 24.0583 | 27.1577 | 30.2715
| HaliburtonIce Accretion2030RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2030 | 16.7873 | 19.9684 | 23.9917 | 27.0823 | 30.177
| HaliburtonIce Accretion2035RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2035 | 16.7525 | 19.92 | 23.925 | 27.007 | 30.0825
| HaliburtonIce Accretion2040RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2040 | 16.7467 | 19.9407 | 23.9917 | 27.1012 | 30.2085
| HaliburtonIce Accretion2045RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2045 | 16.7409 | 19.9615 | 24.0583 | 27.1953 | 30.3345
| HaliburtonIce Accretion2050RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2050 | 16.8917 | 20.2036 | 24.4167 | 27.6379 | 30.8595
| HaliburtonIce Accretion2055RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2055 | 17.0482 | 20.4249 | 24.7083 | 27.9863 | 31.2585
| HaliburtonIce Accretion2060RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2060 | 17.3034 | 20.8053 | 25.2417 | 28.6361 | 32.0145
| HaliburtonIce Accretion2065RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2065 | 17.402 | 20.9644 | 25.4833 | 28.9374 | 32.3715
| HaliburtonIce Accretion2070RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2070 | 17.373 | 20.999 | 25.6 | 29.1163 | 32.613
| HaliburtonIce Accretion2075RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2075 | 17.2454 | 20.8745 | 25.475 | 28.9939 | 32.4975
| HaliburtonIce Accretion2080RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2080 | 17.1178 | 20.75 | 25.35 | 28.8715 | 32.382
| HaliburtonIce Accretion2085RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2085 | 16.6916 | 20.2831 | 24.8375 | 28.3065 | 31.7677
| HaliburtonIce Accretion2090RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2090 | 16.2654 | 19.8163 | 24.325 | 27.7415 | 31.1535
| HaliburtonIce Accretion2095RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2095 | 16.2654 | 19.8163 | 24.325 | 27.7415 | 31.1535
| HaliburtonIce Accretion2100RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2100 | 16.2654 | 19.8163 | 24.325 | 27.7415 | 31.1535
| HaliburtonWind2023RCP4.5 | Haliburton | Wind | RCP4.5 | 2023 | 69.5414 | 74.9134 | 80.576 | 86.2334 | 91.884
| HaliburtonWind2025RCP4.5 | Haliburton | Wind | RCP4.5 | 2025 | 69.6266 | 75.0287 | 80.728 | 86.4161 | 92.0998
| HaliburtonWind2030RCP4.5 | Haliburton | Wind | RCP4.5 | 2030 | 69.7118 | 75.144 | 80.88 | 86.5987 | 92.3157
| HaliburtonWind2035RCP4.5 | Haliburton | Wind | RCP4.5 | 2035 | 69.797 | 75.2593 | 81.032 | 86.7813 | 92.5315
| HaliburtonWind2040RCP4.5 | Haliburton | Wind | RCP4.5 | 2040 | 69.8822 | 75.3746 | 81.184 | 86.9639 | 92.7474
| HaliburtonWind2045RCP4.5 | Haliburton | Wind | RCP4.5 | 2045 | 69.9674 | 75.49 | 81.336 | 87.1465 | 92.9632
| HaliburtonWind2050RCP4.5 | Haliburton | Wind | RCP4.5 | 2050 | 70.0498 | 75.5949 | 81.4672 | 87.3 | 93.1407
| HaliburtonWind2055RCP4.5 | Haliburton | Wind | RCP4.5 | 2055 | 70.0471 | 75.5844 | 81.4464 | 87.2709 | 93.1024
| HaliburtonWind2060RCP4.5 | Haliburton | Wind | RCP4.5 | 2060 | 70.0443 | 75.574 | 81.4256 | 87.2418 | 93.0641
| HaliburtonWind2065RCP4.5 | Haliburton | Wind | RCP4.5 | 2065 | 70.0415 | 75.5636 | 81.4048 | 87.2127 | 93.0258
| HaliburtonWind2070RCP4.5 | Haliburton | Wind | RCP4.5 | 2070 | 70.0388 | 75.5532 | 81.384 | 87.1836 | 92.9875
| HaliburtonWind2075RCP4.5 | Haliburton | Wind | RCP4.5 | 2075 | 69.9996 | 75.5024 | 81.32 | 87.1094 | 92.9009
| HaliburtonWind2080RCP4.5 | Haliburton | Wind | RCP4.5 | 2080 | 69.9605 | 75.4515 | 81.256 | 87.0352 | 92.8142
| HaliburtonWind2085RCP4.5 | Haliburton | Wind | RCP4.5 | 2085 | 69.9214 | 75.4007 | 81.192 | 86.961 | 92.7276
| HaliburtonWind2090RCP4.5 | Haliburton | Wind | RCP4.5 | 2090 | 69.8822 | 75.3498 | 81.128 | 86.8869 | 92.641
| HaliburtonWind2095RCP4.5 | Haliburton | Wind | RCP4.5 | 2095 | 69.8431 | 75.299 | 81.064 | 86.8127 | 92.5543
| HaliburtonWind2100RCP4.5 | Haliburton | Wind | RCP4.5 | 2100 | 69.8039 | 75.2482 | 81 | 86.7385 | 92.4677
| HaliburtonWind2023RCP6.0 | Haliburton | Wind | RCP6.0 | 2023 | 69.5414 | 74.9134 | 80.576 | 86.2334 | 91.884
| HaliburtonWind2025RCP6.0 | Haliburton | Wind | RCP6.0 | 2025 | 69.6266 | 75.0287 | 80.728 | 86.4161 | 92.0998
| HaliburtonWind2030RCP6.0 | Haliburton | Wind | RCP6.0 | 2030 | 69.7118 | 75.144 | 80.88 | 86.5987 | 92.3157
| HaliburtonWind2035RCP6.0 | Haliburton | Wind | RCP6.0 | 2035 | 69.797 | 75.2593 | 81.032 | 86.7813 | 92.5315
| HaliburtonWind2040RCP6.0 | Haliburton | Wind | RCP6.0 | 2040 | 69.8822 | 75.3746 | 81.184 | 86.9639 | 92.7474
| HaliburtonWind2045RCP6.0 | Haliburton | Wind | RCP6.0 | 2045 | 69.9674 | 75.49 | 81.336 | 87.1465 | 92.9632
| HaliburtonWind2050RCP6.0 | Haliburton | Wind | RCP6.0 | 2050 | 70.0498 | 75.5949 | 81.4672 | 87.3 | 93.1407
| HaliburtonWind2055RCP6.0 | Haliburton | Wind | RCP6.0 | 2055 | 70.0471 | 75.5844 | 81.4464 | 87.2709 | 93.1024
| HaliburtonWind2060RCP6.0 | Haliburton | Wind | RCP6.0 | 2060 | 70.0443 | 75.574 | 81.4256 | 87.2418 | 93.0641
| HaliburtonWind2065RCP6.0 | Haliburton | Wind | RCP6.0 | 2065 | 70.0415 | 75.5636 | 81.4048 | 87.2127 | 93.0258
| HaliburtonWind2070RCP6.0 | Haliburton | Wind | RCP6.0 | 2070 | 70.0388 | 75.5532 | 81.384 | 87.1836 | 92.9875
| HaliburtonWind2075RCP6.0 | Haliburton | Wind | RCP6.0 | 2075 | 69.9801 | 75.4769 | 81.288 | 87.0723 | 92.8576
| HaliburtonWind2080RCP6.0 | Haliburton | Wind | RCP6.0 | 2080 | 69.9214 | 75.4007 | 81.192 | 86.961 | 92.7276
| HaliburtonWind2085RCP6.0 | Haliburton | Wind | RCP6.0 | 2085 | 69.8626 | 75.3244 | 81.096 | 86.8498 | 92.5976
| HaliburtonWind2090RCP6.0 | Haliburton | Wind | RCP6.0 | 2090 | 69.7302 | 75.1465 | 80.8613 | 86.5673 | 92.267
| HaliburtonWind2095RCP6.0 | Haliburton | Wind | RCP6.0 | 2095 | 69.6566 | 75.0448 | 80.7227 | 86.3961 | 92.0664
| HaliburtonWind2100RCP6.0 | Haliburton | Wind | RCP6.0 | 2100 | 69.5829 | 74.9431 | 80.584 | 86.2249 | 91.8658
| HaliburtonWind2023RCP8.5 | Haliburton | Wind | RCP8.5 | 2023 | 69.5414 | 74.9134 | 80.576 | 86.2334 | 91.884
| HaliburtonWind2025RCP8.5 | Haliburton | Wind | RCP8.5 | 2025 | 69.7118 | 75.144 | 80.88 | 86.5987 | 92.3157
| HaliburtonWind2030RCP8.5 | Haliburton | Wind | RCP8.5 | 2030 | 69.8822 | 75.3746 | 81.184 | 86.9639 | 92.7474
| HaliburtonWind2035RCP8.5 | Haliburton | Wind | RCP8.5 | 2035 | 70.0526 | 75.6053 | 81.488 | 87.3291 | 93.179
| HaliburtonWind2040RCP8.5 | Haliburton | Wind | RCP8.5 | 2040 | 70.048 | 75.5879 | 81.4533 | 87.2806 | 93.1152
| HaliburtonWind2045RCP8.5 | Haliburton | Wind | RCP8.5 | 2045 | 70.0434 | 75.5706 | 81.4187 | 87.2321 | 93.0514
| HaliburtonWind2050RCP8.5 | Haliburton | Wind | RCP8.5 | 2050 | 69.9605 | 75.4515 | 81.256 | 87.0352 | 92.8142
| HaliburtonWind2055RCP8.5 | Haliburton | Wind | RCP8.5 | 2055 | 69.8822 | 75.3498 | 81.128 | 86.8869 | 92.641
| HaliburtonWind2060RCP8.5 | Haliburton | Wind | RCP8.5 | 2060 | 69.7302 | 75.1465 | 80.8613 | 86.5673 | 92.267
| HaliburtonWind2065RCP8.5 | Haliburton | Wind | RCP8.5 | 2065 | 69.6566 | 75.0448 | 80.7227 | 86.3961 | 92.0664
| HaliburtonWind2070RCP8.5 | Haliburton | Wind | RCP8.5 | 2070 | 69.5944 | 74.9382 | 80.5547 | 86.1764 | 91.7989
| HaliburtonWind2075RCP8.5 | Haliburton | Wind | RCP8.5 | 2075 | 69.6059 | 74.9332 | 80.5253 | 86.1279 | 91.732
| HaliburtonWind2080RCP8.5 | Haliburton | Wind | RCP8.5 | 2080 | 69.6174 | 74.9282 | 80.496 | 86.0794 | 91.6651
| HaliburtonWind2085RCP8.5 | Haliburton | Wind | RCP8.5 | 2085 | 69.8316 | 75.1961 | 80.832 | 86.4731 | 92.1166
| HaliburtonWind2090RCP8.5 | Haliburton | Wind | RCP8.5 | 2090 | 70.0457 | 75.4639 | 81.168 | 86.8669 | 92.568
| HaliburtonWind2095RCP8.5 | Haliburton | Wind | RCP8.5 | 2095 | 70.0457 | 75.4639 | 81.168 | 86.8669 | 92.568
| HaliburtonWind2100RCP8.5 | Haliburton | Wind | RCP8.5 | 2100 | 70.0457 | 75.4639 | 81.168 | 86.8669 | 92.568
| Halton Hills (Georgetown)Ice Accretion2023RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| Halton Hills (Georgetown)Ice Accretion2025RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
| Halton Hills (Georgetown)Ice Accretion2030RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| Halton Hills (Georgetown)Ice Accretion2035RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
| Halton Hills (Georgetown)Ice Accretion2040RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| Halton Hills (Georgetown)Ice Accretion2045RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
| Halton Hills (Georgetown)Ice Accretion2050RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
| Halton Hills (Georgetown)Ice Accretion2055RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
| Halton Hills (Georgetown)Ice Accretion2060RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
| Halton Hills (Georgetown)Ice Accretion2065RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
| Halton Hills (Georgetown)Ice Accretion2070RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
| Halton Hills (Georgetown)Ice Accretion2075RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2075 | 15.5377 | 18.8894 | 23.1125 | 26.329 | 29.5313
| Halton Hills (Georgetown)Ice Accretion2080RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2080 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
| Halton Hills (Georgetown)Ice Accretion2085RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2085 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
| Halton Hills (Georgetown)Ice Accretion2090RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2090 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
| Halton Hills (Georgetown)Ice Accretion2095RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2095 | 15.3405 | 18.7511 | 23.0625 | 26.329 | 29.5942
| Halton Hills (Georgetown)Ice Accretion2100RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2100 | 15.2912 | 18.7165 | 23.05 | 26.329 | 29.61
| Halton Hills (Georgetown)Ice Accretion2023RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| Halton Hills (Georgetown)Ice Accretion2025RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
| Halton Hills (Georgetown)Ice Accretion2030RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| Halton Hills (Georgetown)Ice Accretion2035RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
| Halton Hills (Georgetown)Ice Accretion2040RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| Halton Hills (Georgetown)Ice Accretion2045RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
| Halton Hills (Georgetown)Ice Accretion2050RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
| Halton Hills (Georgetown)Ice Accretion2055RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
| Halton Hills (Georgetown)Ice Accretion2060RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
| Halton Hills (Georgetown)Ice Accretion2065RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
| Halton Hills (Georgetown)Ice Accretion2070RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
| Halton Hills (Georgetown)Ice Accretion2075RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2075 | 15.513 | 18.8721 | 23.1062 | 26.329 | 29.5391
| Halton Hills (Georgetown)Ice Accretion2080RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2080 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
| Halton Hills (Georgetown)Ice Accretion2085RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2085 | 15.3652 | 18.7684 | 23.0688 | 26.329 | 29.5864
| Halton Hills (Georgetown)Ice Accretion2090RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2090 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
| Halton Hills (Georgetown)Ice Accretion2095RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2095 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
| Halton Hills (Georgetown)Ice Accretion2100RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2100 | 14.2127 | 17.596 | 21.825 | 25.0577 | 28.2555
| Halton Hills (Georgetown)Ice Accretion2023RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| Halton Hills (Georgetown)Ice Accretion2025RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2025 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| Halton Hills (Georgetown)Ice Accretion2030RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2030 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| Halton Hills (Georgetown)Ice Accretion2035RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2035 | 16.6133 | 20.0652 | 24.425 | 27.7415 | 31.059
| Halton Hills (Georgetown)Ice Accretion2040RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2040 | 16.2712 | 19.6848 | 23.9917 | 27.2707 | 30.5445
| Halton Hills (Georgetown)Ice Accretion2045RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2045 | 15.9291 | 19.3044 | 23.5583 | 26.7998 | 30.03
| Halton Hills (Georgetown)Ice Accretion2050RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2050 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
| Halton Hills (Georgetown)Ice Accretion2055RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2055 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
| Halton Hills (Georgetown)Ice Accretion2060RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2060 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
| Halton Hills (Georgetown)Ice Accretion2065RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2065 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
| Halton Hills (Georgetown)Ice Accretion2070RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2070 | 13.8125 | 17.1464 | 21.325 | 24.5022 | 27.657
| Halton Hills (Georgetown)Ice Accretion2075RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2075 | 13.4124 | 16.6968 | 20.825 | 23.9466 | 27.0585
| Halton Hills (Georgetown)Ice Accretion2080RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2080 | 13.0123 | 16.2473 | 20.325 | 23.391 | 26.46
| Halton Hills (Georgetown)Ice Accretion2085RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2085 | 12.1338 | 15.1994 | 19.0625 | 21.9785 | 24.885
| Halton Hills (Georgetown)Ice Accretion2090RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2090 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| Halton Hills (Georgetown)Ice Accretion2095RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2095 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| Halton Hills (Georgetown)Ice Accretion2100RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2100 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| Halton Hills (Georgetown)Wind2023RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2023 | 79.8296 | 86.0306 | 92.5704 | 99.0995 | 105.6246
| Halton Hills (Georgetown)Wind2025RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2025 | 79.8588 | 86.0734 | 92.6317 | 99.1767 | 105.7173
| Halton Hills (Georgetown)Wind2030RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2030 | 79.8879 | 86.1161 | 92.6931 | 99.2538 | 105.8099
| Halton Hills (Georgetown)Wind2035RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2035 | 79.917 | 86.1589 | 92.7544 | 99.3309 | 105.9026
| Halton Hills (Georgetown)Wind2040RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2040 | 79.9462 | 86.2017 | 92.8157 | 99.408 | 105.9952
| Halton Hills (Georgetown)Wind2045RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2045 | 79.9753 | 86.2445 | 92.8771 | 99.4851 | 106.0879
| Halton Hills (Georgetown)Wind2050RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2050 | 80.068 | 86.3643 | 93.0322 | 99.6705 | 106.3043
| Halton Hills (Georgetown)Wind2055RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2055 | 80.1315 | 86.4413 | 93.1261 | 99.7788 | 106.428
| Halton Hills (Georgetown)Wind2060RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2060 | 80.1951 | 86.5183 | 93.2199 | 99.8871 | 106.5518
| Halton Hills (Georgetown)Wind2065RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2065 | 80.2586 | 86.5953 | 93.3138 | 99.9954 | 106.6755
| Halton Hills (Georgetown)Wind2070RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2070 | 80.3222 | 86.6723 | 93.4076 | 100.1036 | 106.7993
| Halton Hills (Georgetown)Wind2075RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2075 | 80.4096 | 86.7949 | 93.5747 | 100.3071 | 107.0405
| Halton Hills (Georgetown)Wind2080RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2080 | 80.4969 | 86.9176 | 93.7419 | 100.5105 | 107.2818
| Halton Hills (Georgetown)Wind2085RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2085 | 80.5843 | 87.0402 | 93.909 | 100.714 | 107.523
| Halton Hills (Georgetown)Wind2090RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2090 | 80.6717 | 87.1628 | 94.0761 | 100.9174 | 107.7642
| Halton Hills (Georgetown)Wind2095RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2095 | 80.7591 | 87.2855 | 94.2433 | 101.1208 | 108.0054
| Halton Hills (Georgetown)Wind2100RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2100 | 80.8465 | 87.4081 | 94.4104 | 101.3243 | 108.2466
| Halton Hills (Georgetown)Wind2023RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2023 | 79.8296 | 86.0306 | 92.5704 | 99.0995 | 105.6246
| Halton Hills (Georgetown)Wind2025RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2025 | 79.8588 | 86.0734 | 92.6317 | 99.1767 | 105.7173
| Halton Hills (Georgetown)Wind2030RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2030 | 79.8879 | 86.1161 | 92.6931 | 99.2538 | 105.8099
| Halton Hills (Georgetown)Wind2035RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2035 | 79.917 | 86.1589 | 92.7544 | 99.3309 | 105.9026
| Halton Hills (Georgetown)Wind2040RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2040 | 79.9462 | 86.2017 | 92.8157 | 99.408 | 105.9952
| Halton Hills (Georgetown)Wind2045RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2045 | 79.9753 | 86.2445 | 92.8771 | 99.4851 | 106.0879
| Halton Hills (Georgetown)Wind2050RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2050 | 80.068 | 86.3643 | 93.0322 | 99.6705 | 106.3043
| Halton Hills (Georgetown)Wind2055RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2055 | 80.1315 | 86.4413 | 93.1261 | 99.7788 | 106.428
| Halton Hills (Georgetown)Wind2060RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2060 | 80.1951 | 86.5183 | 93.2199 | 99.8871 | 106.5518
| Halton Hills (Georgetown)Wind2065RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2065 | 80.2586 | 86.5953 | 93.3138 | 99.9954 | 106.6755
| Halton Hills (Georgetown)Wind2070RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2070 | 80.3222 | 86.6723 | 93.4076 | 100.1036 | 106.7993
| Halton Hills (Georgetown)Wind2075RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2075 | 80.4532 | 86.8562 | 93.6583 | 100.4088 | 107.1611
| Halton Hills (Georgetown)Wind2080RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2080 | 80.5843 | 87.0402 | 93.909 | 100.714 | 107.523
| Halton Hills (Georgetown)Wind2085RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2085 | 80.7154 | 87.2241 | 94.1597 | 101.0191 | 107.8848
| Halton Hills (Georgetown)Wind2090RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2090 | 81.1219 | 87.7617 | 94.8612 | 101.8591 | 108.8689
| Halton Hills (Georgetown)Wind2095RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2095 | 81.3973 | 88.1154 | 95.312 | 102.394 | 109.4912
| Halton Hills (Georgetown)Wind2100RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2100 | 81.6727 | 88.469 | 95.7628 | 102.9289 | 110.1135
| Halton Hills (Georgetown)Wind2023RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2023 | 79.8296 | 86.0306 | 92.5704 | 99.0995 | 105.6246
| Halton Hills (Georgetown)Wind2025RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2025 | 79.8879 | 86.1161 | 92.6931 | 99.2538 | 105.8099
| Halton Hills (Georgetown)Wind2030RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2030 | 79.9462 | 86.2017 | 92.8157 | 99.408 | 105.9952
| Halton Hills (Georgetown)Wind2035RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2035 | 80.0044 | 86.2873 | 92.9384 | 99.5622 | 106.1805
| Halton Hills (Georgetown)Wind2040RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2040 | 80.1103 | 86.4156 | 93.0948 | 99.7427 | 106.3868
| Halton Hills (Georgetown)Wind2045RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2045 | 80.2163 | 86.5439 | 93.2512 | 99.9232 | 106.593
| Halton Hills (Georgetown)Wind2050RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2050 | 80.4969 | 86.9176 | 93.7419 | 100.5105 | 107.2818
| Halton Hills (Georgetown)Wind2055RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2055 | 80.6717 | 87.1628 | 94.0761 | 100.9174 | 107.7642
| Halton Hills (Georgetown)Wind2060RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2060 | 81.1219 | 87.7617 | 94.8612 | 101.8591 | 108.8689
| Halton Hills (Georgetown)Wind2065RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2065 | 81.3973 | 88.1154 | 95.312 | 102.394 | 109.4912
| Halton Hills (Georgetown)Wind2070RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2070 | 81.8289 | 88.6943 | 96.0756 | 103.3128 | 110.5715
| Halton Hills (Georgetown)Wind2075RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2075 | 81.9851 | 88.9197 | 96.3884 | 103.6967 | 111.0295
| Halton Hills (Georgetown)Wind2080RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2080 | 82.1414 | 89.145 | 96.7012 | 104.0806 | 111.4874
| Halton Hills (Georgetown)Wind2085RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2085 | 82.3916 | 89.4701 | 97.1198 | 104.5827 | 112.0748
| Halton Hills (Georgetown)Wind2090RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2090 | 82.6418 | 89.7952 | 97.5384 | 105.0847 | 112.6621
| Halton Hills (Georgetown)Wind2095RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2095 | 82.6418 | 89.7952 | 97.5384 | 105.0847 | 112.6621
| Halton Hills (Georgetown)Wind2100RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2100 | 82.6418 | 89.7952 | 97.5384 | 105.0847 | 112.6621
| HamiltonIce Accretion2023RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2023 | 21.9108 | 26.2678 | 31.808 | 36.0154 | 40.2394
| HamiltonIce Accretion2025RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2025 | 21.7995 | 26.1483 | 31.6747 | 35.8767 | 40.0915
| HamiltonIce Accretion2030RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2030 | 21.6881 | 26.0288 | 31.5413 | 35.7381 | 39.9437
| HamiltonIce Accretion2035RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2035 | 21.5768 | 25.9093 | 31.408 | 35.5995 | 39.7958
| HamiltonIce Accretion2040RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2040 | 21.4655 | 25.7898 | 31.2747 | 35.4609 | 39.648
| HamiltonIce Accretion2045RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2045 | 21.3541 | 25.6702 | 31.1413 | 35.3223 | 39.5002
| HamiltonIce Accretion2050RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2050 | 20.9444 | 25.2267 | 30.656 | 34.8004 | 38.9411
| HamiltonIce Accretion2055RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2055 | 20.646 | 24.9027 | 30.304 | 34.4171 | 38.5298
| HamiltonIce Accretion2060RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2060 | 20.3477 | 24.5786 | 29.952 | 34.0338 | 38.1185
| HamiltonIce Accretion2065RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2065 | 20.0493 | 24.2546 | 29.6 | 33.6505 | 37.7073
| HamiltonIce Accretion2070RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2070 | 19.7509 | 23.9306 | 29.248 | 33.2672 | 37.296
| HamiltonIce Accretion2075RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2075 | 19.6544 | 23.8465 | 29.1733 | 33.2009 | 37.2288
| HamiltonIce Accretion2080RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2080 | 19.5579 | 23.7623 | 29.0987 | 33.1346 | 37.1616
| HamiltonIce Accretion2085RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2085 | 19.4614 | 23.6782 | 29.024 | 33.0683 | 37.0944
| HamiltonIce Accretion2090RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2090 | 19.3649 | 23.5941 | 28.9493 | 33.002 | 37.0272
| HamiltonIce Accretion2095RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2095 | 19.2684 | 23.51 | 28.8747 | 32.9357 | 36.96
| HamiltonIce Accretion2100RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2100 | 19.172 | 23.4259 | 28.8 | 32.8694 | 36.8928
| HamiltonIce Accretion2023RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2023 | 21.9108 | 26.2678 | 31.808 | 36.0154 | 40.2394
| HamiltonIce Accretion2025RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2025 | 21.7995 | 26.1483 | 31.6747 | 35.8767 | 40.0915
| HamiltonIce Accretion2030RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2030 | 21.6881 | 26.0288 | 31.5413 | 35.7381 | 39.9437
| HamiltonIce Accretion2035RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2035 | 21.5768 | 25.9093 | 31.408 | 35.5995 | 39.7958
| HamiltonIce Accretion2040RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2040 | 21.4655 | 25.7898 | 31.2747 | 35.4609 | 39.648
| HamiltonIce Accretion2045RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2045 | 21.3541 | 25.6702 | 31.1413 | 35.3223 | 39.5002
| HamiltonIce Accretion2050RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2050 | 20.9444 | 25.2267 | 30.656 | 34.8004 | 38.9411
| HamiltonIce Accretion2055RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2055 | 20.646 | 24.9027 | 30.304 | 34.4171 | 38.5298
| HamiltonIce Accretion2060RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2060 | 20.3477 | 24.5786 | 29.952 | 34.0338 | 38.1185
| HamiltonIce Accretion2065RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2065 | 20.0493 | 24.2546 | 29.6 | 33.6505 | 37.7073
| HamiltonIce Accretion2070RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2070 | 19.7509 | 23.9306 | 29.248 | 33.2672 | 37.296
| HamiltonIce Accretion2075RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2075 | 19.6062 | 23.8044 | 29.136 | 33.1678 | 37.1952
| HamiltonIce Accretion2080RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2080 | 19.4614 | 23.6782 | 29.024 | 33.0683 | 37.0944
| HamiltonIce Accretion2085RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2085 | 19.3167 | 23.5521 | 28.912 | 32.9689 | 36.9936
| HamiltonIce Accretion2090RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2090 | 18.5411 | 22.7088 | 27.968 | 31.9534 | 35.8982
| HamiltonIce Accretion2095RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2095 | 17.9102 | 21.9917 | 27.136 | 31.0373 | 34.9037
| HamiltonIce Accretion2100RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2100 | 17.2793 | 21.2746 | 26.304 | 30.1213 | 33.9091
| HamiltonIce Accretion2023RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2023 | 21.9108 | 26.2678 | 31.808 | 36.0154 | 40.2394
| HamiltonIce Accretion2025RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2025 | 21.6881 | 26.0288 | 31.5413 | 35.7381 | 39.9437
| HamiltonIce Accretion2030RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2030 | 21.4655 | 25.7898 | 31.2747 | 35.4609 | 39.648
| HamiltonIce Accretion2035RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2035 | 21.2428 | 25.5507 | 31.008 | 35.1837 | 39.3523
| HamiltonIce Accretion2040RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2040 | 20.7455 | 25.0107 | 30.4213 | 34.5449 | 38.6669
| HamiltonIce Accretion2045RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2045 | 20.2482 | 24.4706 | 29.8347 | 33.906 | 37.9814
| HamiltonIce Accretion2050RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2050 | 19.5579 | 23.7623 | 29.0987 | 33.1346 | 37.1616
| HamiltonIce Accretion2055RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2055 | 19.3649 | 23.5941 | 28.9493 | 33.002 | 37.0272
| HamiltonIce Accretion2060RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2060 | 18.5411 | 22.7088 | 27.968 | 31.9534 | 35.8982
| HamiltonIce Accretion2065RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2065 | 17.9102 | 21.9917 | 27.136 | 31.0373 | 34.9037
| HamiltonIce Accretion2070RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2070 | 16.871 | 20.823 | 25.8027 | 29.5668 | 33.3178
| HamiltonIce Accretion2075RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2075 | 16.4628 | 20.3715 | 25.3013 | 29.0124 | 32.7264
| HamiltonIce Accretion2080RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2080 | 16.0546 | 19.92 | 24.8 | 28.4579 | 32.135
| HamiltonIce Accretion2085RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2085 | 14.9635 | 18.6451 | 23.248 | 26.7222 | 30.1997
| HamiltonIce Accretion2090RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2090 | 13.8724 | 17.3702 | 21.696 | 24.9866 | 28.2643
| HamiltonIce Accretion2095RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2095 | 13.8724 | 17.3702 | 21.696 | 24.9866 | 28.2643
| HamiltonIce Accretion2100RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2100 | 13.8724 | 17.3702 | 21.696 | 24.9866 | 28.2643
| HamiltonWind2023RCP4.5 | Hamilton | Wind | RCP4.5 | 2023 | 83.2839 | 89.7889 | 96.6624 | 103.5109 | 110.3593
| HamiltonWind2025RCP4.5 | Hamilton | Wind | RCP4.5 | 2025 | 83.3019 | 89.8201 | 96.7104 | 103.5726 | 110.4359
| HamiltonWind2030RCP4.5 | Hamilton | Wind | RCP4.5 | 2030 | 83.3198 | 89.8514 | 96.7584 | 103.6342 | 110.5125
| HamiltonWind2035RCP4.5 | Hamilton | Wind | RCP4.5 | 2035 | 83.3378 | 89.8826 | 96.8064 | 103.6958 | 110.5891
| HamiltonWind2040RCP4.5 | Hamilton | Wind | RCP4.5 | 2040 | 83.3558 | 89.9139 | 96.8544 | 103.7575 | 110.6657
| HamiltonWind2045RCP4.5 | Hamilton | Wind | RCP4.5 | 2045 | 83.3737 | 89.9451 | 96.9024 | 103.8191 | 110.7423
| HamiltonWind2050RCP4.5 | Hamilton | Wind | RCP4.5 | 2050 | 83.4613 | 90.0674 | 97.0675 | 104.0225 | 110.9853
| HamiltonWind2055RCP4.5 | Hamilton | Wind | RCP4.5 | 2055 | 83.5309 | 90.1585 | 97.1846 | 104.1642 | 111.1516
| HamiltonWind2060RCP4.5 | Hamilton | Wind | RCP4.5 | 2060 | 83.6006 | 90.2496 | 97.3018 | 104.306 | 111.318
| HamiltonWind2065RCP4.5 | Hamilton | Wind | RCP4.5 | 2065 | 83.6702 | 90.3406 | 97.4189 | 104.4478 | 111.4843
| HamiltonWind2070RCP4.5 | Hamilton | Wind | RCP4.5 | 2070 | 83.7398 | 90.4317 | 97.536 | 104.5895 | 111.6507
| HamiltonWind2075RCP4.5 | Hamilton | Wind | RCP4.5 | 2075 | 83.8435 | 90.5701 | 97.7168 | 104.8052 | 111.9042
| HamiltonWind2080RCP4.5 | Hamilton | Wind | RCP4.5 | 2080 | 83.9471 | 90.7085 | 97.8976 | 105.0209 | 112.1578
| HamiltonWind2085RCP4.5 | Hamilton | Wind | RCP4.5 | 2085 | 84.0507 | 90.8469 | 98.0784 | 105.2366 | 112.4113
| HamiltonWind2090RCP4.5 | Hamilton | Wind | RCP4.5 | 2090 | 84.1543 | 90.9852 | 98.2592 | 105.4524 | 112.6648
| HamiltonWind2095RCP4.5 | Hamilton | Wind | RCP4.5 | 2095 | 84.2579 | 91.1236 | 98.44 | 105.6681 | 112.9184
| HamiltonWind2100RCP4.5 | Hamilton | Wind | RCP4.5 | 2100 | 84.3615 | 91.262 | 98.6208 | 105.8838 | 113.1719
| HamiltonWind2023RCP6.0 | Hamilton | Wind | RCP6.0 | 2023 | 83.2839 | 89.7889 | 96.6624 | 103.5109 | 110.3593
| HamiltonWind2025RCP6.0 | Hamilton | Wind | RCP6.0 | 2025 | 83.3019 | 89.8201 | 96.7104 | 103.5726 | 110.4359
| HamiltonWind2030RCP6.0 | Hamilton | Wind | RCP6.0 | 2030 | 83.3198 | 89.8514 | 96.7584 | 103.6342 | 110.5125
| HamiltonWind2035RCP6.0 | Hamilton | Wind | RCP6.0 | 2035 | 83.3378 | 89.8826 | 96.8064 | 103.6958 | 110.5891
| HamiltonWind2040RCP6.0 | Hamilton | Wind | RCP6.0 | 2040 | 83.3558 | 89.9139 | 96.8544 | 103.7575 | 110.6657
| HamiltonWind2045RCP6.0 | Hamilton | Wind | RCP6.0 | 2045 | 83.3737 | 89.9451 | 96.9024 | 103.8191 | 110.7423
| HamiltonWind2050RCP6.0 | Hamilton | Wind | RCP6.0 | 2050 | 83.4613 | 90.0674 | 97.0675 | 104.0225 | 110.9853
| HamiltonWind2055RCP6.0 | Hamilton | Wind | RCP6.0 | 2055 | 83.5309 | 90.1585 | 97.1846 | 104.1642 | 111.1516
| HamiltonWind2060RCP6.0 | Hamilton | Wind | RCP6.0 | 2060 | 83.6006 | 90.2496 | 97.3018 | 104.306 | 111.318
| HamiltonWind2065RCP6.0 | Hamilton | Wind | RCP6.0 | 2065 | 83.6702 | 90.3406 | 97.4189 | 104.4478 | 111.4843
| HamiltonWind2070RCP6.0 | Hamilton | Wind | RCP6.0 | 2070 | 83.7398 | 90.4317 | 97.536 | 104.5895 | 111.6507
| HamiltonWind2075RCP6.0 | Hamilton | Wind | RCP6.0 | 2075 | 83.8953 | 90.6393 | 97.8072 | 104.9131 | 112.031
| HamiltonWind2080RCP6.0 | Hamilton | Wind | RCP6.0 | 2080 | 84.0507 | 90.8469 | 98.0784 | 105.2366 | 112.4113
| HamiltonWind2085RCP6.0 | Hamilton | Wind | RCP6.0 | 2085 | 84.2061 | 91.0544 | 98.3496 | 105.5602 | 112.7916
| HamiltonWind2090RCP6.0 | Hamilton | Wind | RCP6.0 | 2090 | 84.6683 | 91.6519 | 99.12 | 106.4761 | 113.8577
| HamiltonWind2095RCP6.0 | Hamilton | Wind | RCP6.0 | 2095 | 84.975 | 92.0417 | 99.6192 | 107.0685 | 114.5436
| HamiltonWind2100RCP6.0 | Hamilton | Wind | RCP6.0 | 2100 | 85.2817 | 92.4316 | 100.1184 | 107.6608 | 115.2294
| HamiltonWind2023RCP8.5 | Hamilton | Wind | RCP8.5 | 2023 | 83.2839 | 89.7889 | 96.6624 | 103.5109 | 110.3593
| HamiltonWind2025RCP8.5 | Hamilton | Wind | RCP8.5 | 2025 | 83.3198 | 89.8514 | 96.7584 | 103.6342 | 110.5125
| HamiltonWind2030RCP8.5 | Hamilton | Wind | RCP8.5 | 2030 | 83.3558 | 89.9139 | 96.8544 | 103.7575 | 110.6657
| HamiltonWind2035RCP8.5 | Hamilton | Wind | RCP8.5 | 2035 | 83.3917 | 89.9764 | 96.9504 | 103.8807 | 110.8189
| HamiltonWind2040RCP8.5 | Hamilton | Wind | RCP8.5 | 2040 | 83.5077 | 90.1282 | 97.1456 | 104.117 | 111.0962
| HamiltonWind2045RCP8.5 | Hamilton | Wind | RCP8.5 | 2045 | 83.6238 | 90.2799 | 97.3408 | 104.3532 | 111.3734
| HamiltonWind2050RCP8.5 | Hamilton | Wind | RCP8.5 | 2050 | 83.9471 | 90.7085 | 97.8976 | 105.0209 | 112.1578
| HamiltonWind2055RCP8.5 | Hamilton | Wind | RCP8.5 | 2055 | 84.1543 | 90.9852 | 98.2592 | 105.4524 | 112.6648
| HamiltonWind2060RCP8.5 | Hamilton | Wind | RCP8.5 | 2060 | 84.6683 | 91.6519 | 99.12 | 106.4761 | 113.8577
| HamiltonWind2065RCP8.5 | Hamilton | Wind | RCP8.5 | 2065 | 84.975 | 92.0417 | 99.6192 | 107.0685 | 114.5436
| HamiltonWind2070RCP8.5 | Hamilton | Wind | RCP8.5 | 2070 | 85.453 | 92.6697 | 100.4448 | 108.058 | 115.7
| HamiltonWind2075RCP8.5 | Hamilton | Wind | RCP8.5 | 2075 | 85.6243 | 92.9077 | 100.7712 | 108.4552 | 116.1706
| HamiltonWind2080RCP8.5 | Hamilton | Wind | RCP8.5 | 2080 | 85.7956 | 93.1458 | 101.0976 | 108.8524 | 116.6412
| HamiltonWind2085RCP8.5 | Hamilton | Wind | RCP8.5 | 2085 | 86.0567 | 93.4985 | 101.5584 | 109.4122 | 117.2978
| HamiltonWind2090RCP8.5 | Hamilton | Wind | RCP8.5 | 2090 | 86.3178 | 93.8511 | 102.0192 | 109.972 | 117.9544
| HamiltonWind2095RCP8.5 | Hamilton | Wind | RCP8.5 | 2095 | 86.3178 | 93.8511 | 102.0192 | 109.972 | 117.9544
| HamiltonWind2100RCP8.5 | Hamilton | Wind | RCP8.5 | 2100 | 86.3178 | 93.8511 | 102.0192 | 109.972 | 117.9544
| HanoverIce Accretion2023RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2023 | 15.2933 | 18.333 | 22.198 | 25.1335 | 28.0804
| HanoverIce Accretion2025RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2025 | 15.2984 | 18.3543 | 22.231 | 25.179 | 28.1404
| HanoverIce Accretion2030RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2030 | 15.3035 | 18.3756 | 22.264 | 25.2246 | 28.2005
| HanoverIce Accretion2035RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2035 | 15.3086 | 18.3969 | 22.297 | 25.2702 | 28.2605
| HanoverIce Accretion2040RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2040 | 15.3137 | 18.4183 | 22.33 | 25.3158 | 28.3206
| HanoverIce Accretion2045RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2045 | 15.3188 | 18.4396 | 22.363 | 25.3613 | 28.3807
| HanoverIce Accretion2050RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2050 | 15.3178 | 18.4718 | 22.4356 | 25.4666 | 28.5183
| HanoverIce Accretion2055RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2055 | 15.3117 | 18.4828 | 22.4752 | 25.5262 | 28.596
| HanoverIce Accretion2060RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2060 | 15.3056 | 18.4937 | 22.5148 | 25.5859 | 28.6736
| HanoverIce Accretion2065RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2065 | 15.2994 | 18.5047 | 22.5544 | 25.6456 | 28.7512
| HanoverIce Accretion2070RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2070 | 15.2933 | 18.5156 | 22.594 | 25.7052 | 28.8288
| HanoverIce Accretion2075RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2075 | 15.227 | 18.4609 | 22.5573 | 25.6762 | 28.8103
| HanoverIce Accretion2080RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2080 | 15.1606 | 18.4061 | 22.5207 | 25.6472 | 28.7918
| HanoverIce Accretion2085RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2085 | 15.0943 | 18.3513 | 22.484 | 25.6182 | 28.7734
| HanoverIce Accretion2090RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2090 | 15.028 | 18.2965 | 22.4473 | 25.5892 | 28.7549
| HanoverIce Accretion2095RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2095 | 14.9616 | 18.2417 | 22.4107 | 25.5602 | 28.7364
| HanoverIce Accretion2100RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2100 | 14.8953 | 18.187 | 22.374 | 25.5312 | 28.7179
| HanoverIce Accretion2023RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2023 | 15.2933 | 18.333 | 22.198 | 25.1335 | 28.0804
| HanoverIce Accretion2025RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2025 | 15.2984 | 18.3543 | 22.231 | 25.179 | 28.1404
| HanoverIce Accretion2030RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2030 | 15.3035 | 18.3756 | 22.264 | 25.2246 | 28.2005
| HanoverIce Accretion2035RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2035 | 15.3086 | 18.3969 | 22.297 | 25.2702 | 28.2605
| HanoverIce Accretion2040RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2040 | 15.3137 | 18.4183 | 22.33 | 25.3158 | 28.3206
| HanoverIce Accretion2045RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2045 | 15.3188 | 18.4396 | 22.363 | 25.3613 | 28.3807
| HanoverIce Accretion2050RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2050 | 15.3178 | 18.4718 | 22.4356 | 25.4666 | 28.5183
| HanoverIce Accretion2055RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2055 | 15.3117 | 18.4828 | 22.4752 | 25.5262 | 28.596
| HanoverIce Accretion2060RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2060 | 15.3056 | 18.4937 | 22.5148 | 25.5859 | 28.6736
| HanoverIce Accretion2065RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2065 | 15.2994 | 18.5047 | 22.5544 | 25.6456 | 28.7512
| HanoverIce Accretion2070RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2070 | 15.2933 | 18.5156 | 22.594 | 25.7052 | 28.8288
| HanoverIce Accretion2075RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2075 | 15.1938 | 18.4335 | 22.539 | 25.6617 | 28.8011
| HanoverIce Accretion2080RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2080 | 15.0943 | 18.3513 | 22.484 | 25.6182 | 28.7734
| HanoverIce Accretion2085RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2085 | 14.9948 | 18.2691 | 22.429 | 25.5747 | 28.7456
| HanoverIce Accretion2090RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2090 | 14.6401 | 17.9191 | 22.0733 | 25.2163 | 28.376
| HanoverIce Accretion2095RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2095 | 14.385 | 17.6513 | 21.7727 | 24.9014 | 28.0342
| HanoverIce Accretion2100RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2100 | 14.1299 | 17.3835 | 21.472 | 24.5865 | 27.6923
| HanoverIce Accretion2023RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2023 | 15.2933 | 18.333 | 22.198 | 25.1335 | 28.0804
| HanoverIce Accretion2025RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2025 | 15.3035 | 18.3756 | 22.264 | 25.2246 | 28.2005
| HanoverIce Accretion2030RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2030 | 15.3137 | 18.4183 | 22.33 | 25.3158 | 28.3206
| HanoverIce Accretion2035RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2035 | 15.3239 | 18.4609 | 22.396 | 25.4069 | 28.4407
| HanoverIce Accretion2040RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2040 | 15.3137 | 18.4791 | 22.462 | 25.5064 | 28.5701
| HanoverIce Accretion2045RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2045 | 15.3035 | 18.4974 | 22.528 | 25.6058 | 28.6994
| HanoverIce Accretion2050RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2050 | 15.1606 | 18.4061 | 22.5207 | 25.6472 | 28.7918
| HanoverIce Accretion2055RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2055 | 15.028 | 18.2965 | 22.4473 | 25.5892 | 28.7549
| HanoverIce Accretion2060RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2060 | 14.6401 | 17.9191 | 22.0733 | 25.2163 | 28.376
| HanoverIce Accretion2065RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2065 | 14.385 | 17.6513 | 21.7727 | 24.9014 | 28.0342
| HanoverIce Accretion2070RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2070 | 13.7114 | 16.9088 | 20.9367 | 23.9982 | 27.0547
| HanoverIce Accretion2075RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2075 | 13.293 | 16.434 | 20.4013 | 23.4098 | 26.4172
| HanoverIce Accretion2080RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2080 | 12.8745 | 15.9592 | 19.866 | 22.8215 | 25.7796
| HanoverIce Accretion2085RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2085 | 12.4536 | 15.4936 | 19.338 | 22.2497 | 25.1698
| HanoverIce Accretion2090RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2090 | 12.0326 | 15.028 | 18.81 | 21.6779 | 24.5599
| HanoverIce Accretion2095RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2095 | 12.0326 | 15.028 | 18.81 | 21.6779 | 24.5599
| HanoverIce Accretion2100RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2100 | 12.0326 | 15.028 | 18.81 | 21.6779 | 24.5599
| HanoverWind2023RCP4.5 | Hanover | Wind | RCP4.5 | 2023 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2506
| HanoverWind2025RCP4.5 | Hanover | Wind | RCP4.5 | 2025 | 85.4139 | 92.1425 | 99.2626 | 106.3385 | 113.42
| HanoverWind2030RCP4.5 | Hanover | Wind | RCP4.5 | 2030 | 85.4957 | 92.2428 | 99.3883 | 106.4853 | 113.5894
| HanoverWind2035RCP4.5 | Hanover | Wind | RCP4.5 | 2035 | 85.5775 | 92.343 | 99.5141 | 106.6321 | 113.7589
| HanoverWind2040RCP4.5 | Hanover | Wind | RCP4.5 | 2040 | 85.6593 | 92.4433 | 99.6399 | 106.7789 | 113.9283
| HanoverWind2045RCP4.5 | Hanover | Wind | RCP4.5 | 2045 | 85.7411 | 92.5436 | 99.7656 | 106.9257 | 114.0978
| HanoverWind2050RCP4.5 | Hanover | Wind | RCP4.5 | 2050 | 85.8364 | 92.6566 | 99.9012 | 107.0809 | 114.2739
| HanoverWind2055RCP4.5 | Hanover | Wind | RCP4.5 | 2055 | 85.85 | 92.6693 | 99.911 | 107.0893 | 114.2806
| HanoverWind2060RCP4.5 | Hanover | Wind | RCP4.5 | 2060 | 85.8635 | 92.6821 | 99.9208 | 107.0977 | 114.2873
| HanoverWind2065RCP4.5 | Hanover | Wind | RCP4.5 | 2065 | 85.8771 | 92.6948 | 99.9306 | 107.1061 | 114.294
| HanoverWind2070RCP4.5 | Hanover | Wind | RCP4.5 | 2070 | 85.8906 | 92.7076 | 99.9404 | 107.1145 | 114.3007
| HanoverWind2075RCP4.5 | Hanover | Wind | RCP4.5 | 2075 | 85.9738 | 92.8155 | 100.0792 | 107.2805 | 114.4925
| HanoverWind2080RCP4.5 | Hanover | Wind | RCP4.5 | 2080 | 86.057 | 92.9233 | 100.2181 | 107.4465 | 114.6843
| HanoverWind2085RCP4.5 | Hanover | Wind | RCP4.5 | 2085 | 86.1402 | 93.0312 | 100.3569 | 107.6126 | 114.8761
| HanoverWind2090RCP4.5 | Hanover | Wind | RCP4.5 | 2090 | 86.2234 | 93.139 | 100.4957 | 107.7786 | 115.0679
| HanoverWind2095RCP4.5 | Hanover | Wind | RCP4.5 | 2095 | 86.3067 | 93.2469 | 100.6346 | 107.9446 | 115.2597
| HanoverWind2100RCP4.5 | Hanover | Wind | RCP4.5 | 2100 | 86.3899 | 93.3547 | 100.7734 | 108.1107 | 115.4514
| HanoverWind2023RCP6.0 | Hanover | Wind | RCP6.0 | 2023 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2506
| HanoverWind2025RCP6.0 | Hanover | Wind | RCP6.0 | 2025 | 85.4139 | 92.1425 | 99.2626 | 106.3385 | 113.42
| HanoverWind2030RCP6.0 | Hanover | Wind | RCP6.0 | 2030 | 85.4957 | 92.2428 | 99.3883 | 106.4853 | 113.5894
| HanoverWind2035RCP6.0 | Hanover | Wind | RCP6.0 | 2035 | 85.5775 | 92.343 | 99.5141 | 106.6321 | 113.7589
| HanoverWind2040RCP6.0 | Hanover | Wind | RCP6.0 | 2040 | 85.6593 | 92.4433 | 99.6399 | 106.7789 | 113.9283
| HanoverWind2045RCP6.0 | Hanover | Wind | RCP6.0 | 2045 | 85.7411 | 92.5436 | 99.7656 | 106.9257 | 114.0978
| HanoverWind2050RCP6.0 | Hanover | Wind | RCP6.0 | 2050 | 85.8364 | 92.6566 | 99.9012 | 107.0809 | 114.2739
| HanoverWind2055RCP6.0 | Hanover | Wind | RCP6.0 | 2055 | 85.85 | 92.6693 | 99.911 | 107.0893 | 114.2806
| HanoverWind2060RCP6.0 | Hanover | Wind | RCP6.0 | 2060 | 85.8635 | 92.6821 | 99.9208 | 107.0977 | 114.2873
| HanoverWind2065RCP6.0 | Hanover | Wind | RCP6.0 | 2065 | 85.8771 | 92.6948 | 99.9306 | 107.1061 | 114.294
| HanoverWind2070RCP6.0 | Hanover | Wind | RCP6.0 | 2070 | 85.8906 | 92.7076 | 99.9404 | 107.1145 | 114.3007
| HanoverWind2075RCP6.0 | Hanover | Wind | RCP6.0 | 2075 | 86.0154 | 92.8694 | 100.1487 | 107.3635 | 114.5884
| HanoverWind2080RCP6.0 | Hanover | Wind | RCP6.0 | 2080 | 86.1402 | 93.0312 | 100.3569 | 107.6126 | 114.8761
| HanoverWind2085RCP6.0 | Hanover | Wind | RCP6.0 | 2085 | 86.265 | 93.1929 | 100.5652 | 107.8616 | 115.1638
| HanoverWind2090RCP6.0 | Hanover | Wind | RCP6.0 | 2090 | 86.8017 | 93.8712 | 101.4169 | 108.8657 | 116.3229
| HanoverWind2095RCP6.0 | Hanover | Wind | RCP6.0 | 2095 | 87.2135 | 94.3876 | 102.0605 | 109.6206 | 117.1943
| HanoverWind2100RCP6.0 | Hanover | Wind | RCP6.0 | 2100 | 87.6253 | 94.9041 | 102.704 | 110.3756 | 118.0657
| HanoverWind2023RCP8.5 | Hanover | Wind | RCP8.5 | 2023 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2506
| HanoverWind2025RCP8.5 | Hanover | Wind | RCP8.5 | 2025 | 85.4957 | 92.2428 | 99.3883 | 106.4853 | 113.5894
| HanoverWind2030RCP8.5 | Hanover | Wind | RCP8.5 | 2030 | 85.6593 | 92.4433 | 99.6399 | 106.7789 | 113.9283
| HanoverWind2035RCP8.5 | Hanover | Wind | RCP8.5 | 2035 | 85.8229 | 92.6438 | 99.8914 | 107.0725 | 114.2672
| HanoverWind2040RCP8.5 | Hanover | Wind | RCP8.5 | 2040 | 85.8455 | 92.6651 | 99.9077 | 107.0865 | 114.2784
| HanoverWind2045RCP8.5 | Hanover | Wind | RCP8.5 | 2045 | 85.868 | 92.6863 | 99.9241 | 107.1005 | 114.2896
| HanoverWind2050RCP8.5 | Hanover | Wind | RCP8.5 | 2050 | 86.057 | 92.9233 | 100.2181 | 107.4465 | 114.6843
| HanoverWind2055RCP8.5 | Hanover | Wind | RCP8.5 | 2055 | 86.2234 | 93.139 | 100.4957 | 107.7786 | 115.0679
| HanoverWind2060RCP8.5 | Hanover | Wind | RCP8.5 | 2060 | 86.8017 | 93.8712 | 101.4169 | 108.8657 | 116.3229
| HanoverWind2065RCP8.5 | Hanover | Wind | RCP8.5 | 2065 | 87.2135 | 94.3876 | 102.0605 | 109.6206 | 117.1943
| HanoverWind2070RCP8.5 | Hanover | Wind | RCP8.5 | 2070 | 87.8397 | 95.1653 | 103.0241 | 110.7461 | 118.4865
| HanoverWind2075RCP8.5 | Hanover | Wind | RCP8.5 | 2075 | 88.0541 | 95.4266 | 103.3443 | 111.1166 | 118.9073
| HanoverWind2080RCP8.5 | Hanover | Wind | RCP8.5 | 2080 | 88.2685 | 95.6879 | 103.6644 | 111.4872 | 119.3281
| HanoverWind2085RCP8.5 | Hanover | Wind | RCP8.5 | 2085 | 88.2896 | 95.697 | 103.6644 | 111.4714 | 119.3058
| HanoverWind2090RCP8.5 | Hanover | Wind | RCP8.5 | 2090 | 88.3108 | 95.7061 | 103.6644 | 111.4557 | 119.2834
| HanoverWind2095RCP8.5 | Hanover | Wind | RCP8.5 | 2095 | 88.3108 | 95.7061 | 103.6644 | 111.4557 | 119.2834
| HanoverWind2100RCP8.5 | Hanover | Wind | RCP8.5 | 2100 | 88.3108 | 95.7061 | 103.6644 | 111.4557 | 119.2834
| HastingsIce Accretion2023RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| HastingsIce Accretion2025RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
| HastingsIce Accretion2030RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| HastingsIce Accretion2035RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
| HastingsIce Accretion2040RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| HastingsIce Accretion2045RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
| HastingsIce Accretion2050RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
| HastingsIce Accretion2055RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
| HastingsIce Accretion2060RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
| HastingsIce Accretion2065RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
| HastingsIce Accretion2070RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
| HastingsIce Accretion2075RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2075 | 16.8859 | 20.3972 | 24.8292 | 28.2123 | 31.5682
| HastingsIce Accretion2080RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2080 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
| HastingsIce Accretion2085RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2085 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
| HastingsIce Accretion2090RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2090 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
| HastingsIce Accretion2095RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2095 | 16.7235 | 20.3142 | 24.8458 | 28.2877 | 31.7152
| HastingsIce Accretion2100RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.2935 | 24.85 | 28.3065 | 31.752
| HastingsIce Accretion2023RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| HastingsIce Accretion2025RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
| HastingsIce Accretion2030RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| HastingsIce Accretion2035RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
| HastingsIce Accretion2040RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| HastingsIce Accretion2045RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
| HastingsIce Accretion2050RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
| HastingsIce Accretion2055RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
| HastingsIce Accretion2060RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
| HastingsIce Accretion2065RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
| HastingsIce Accretion2070RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
| HastingsIce Accretion2075RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2075 | 16.8656 | 20.3869 | 24.8313 | 28.2217 | 31.5866
| HastingsIce Accretion2080RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2080 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
| HastingsIce Accretion2085RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2085 | 16.7438 | 20.3246 | 24.8438 | 28.2782 | 31.6969
| HastingsIce Accretion2090RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2090 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
| HastingsIce Accretion2095RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2095 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
| HastingsIce Accretion2100RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2100 | 15.6565 | 19.173 | 23.6 | 26.9505 | 30.2715
| HastingsIce Accretion2023RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| HastingsIce Accretion2025RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2025 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| HastingsIce Accretion2030RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2030 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| HastingsIce Accretion2035RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2035 | 17.6745 | 21.2272 | 25.725 | 29.154 | 32.571
| HastingsIce Accretion2040RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2040 | 17.4251 | 20.9575 | 25.425 | 28.8338 | 32.2245
| HastingsIce Accretion2045RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2045 | 17.1758 | 20.6877 | 25.125 | 28.5137 | 31.878
| HastingsIce Accretion2050RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2050 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
| HastingsIce Accretion2055RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2055 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
| HastingsIce Accretion2060RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2060 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
| HastingsIce Accretion2065RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2065 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
| HastingsIce Accretion2070RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2070 | 15.2216 | 18.6888 | 23.05 | 26.3478 | 29.631
| HastingsIce Accretion2075RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2075 | 14.7867 | 18.2047 | 22.5 | 25.7452 | 28.9905
| HastingsIce Accretion2080RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2080 | 14.3518 | 17.7205 | 21.95 | 25.1425 | 28.35
| HastingsIce Accretion2085RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2085 | 13.6908 | 16.9424 | 21.025 | 24.0972 | 27.1845
| HastingsIce Accretion2090RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2090 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| HastingsIce Accretion2095RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2095 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| HastingsIce Accretion2100RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2100 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| HastingsWind2023RCP4.5 | Hastings | Wind | RCP4.5 | 2023 | 74.705 | 80.4759 | 86.5418 | 92.6089 | 98.6773
| HastingsWind2025RCP4.5 | Hastings | Wind | RCP4.5 | 2025 | 74.6766 | 80.4452 | 86.5117 | 92.5767 | 98.6446
| HastingsWind2030RCP4.5 | Hastings | Wind | RCP4.5 | 2030 | 74.6481 | 80.4146 | 86.4816 | 92.5445 | 98.6119
| HastingsWind2035RCP4.5 | Hastings | Wind | RCP4.5 | 2035 | 74.6196 | 80.3839 | 86.4515 | 92.5123 | 98.5792
| HastingsWind2040RCP4.5 | Hastings | Wind | RCP4.5 | 2040 | 74.5912 | 80.3532 | 86.4214 | 92.4801 | 98.5465
| HastingsWind2045RCP4.5 | Hastings | Wind | RCP4.5 | 2045 | 74.5627 | 80.3226 | 86.3913 | 92.4479 | 98.5139
| HastingsWind2050RCP4.5 | Hastings | Wind | RCP4.5 | 2050 | 74.6397 | 80.4327 | 86.5452 | 92.6365 | 98.74
| HastingsWind2055RCP4.5 | Hastings | Wind | RCP4.5 | 2055 | 74.7451 | 80.5735 | 86.7293 | 92.8574 | 98.9988
| HastingsWind2060RCP4.5 | Hastings | Wind | RCP4.5 | 2060 | 74.8506 | 80.7142 | 86.9133 | 93.0782 | 99.2577
| HastingsWind2065RCP4.5 | Hastings | Wind | RCP4.5 | 2065 | 74.956 | 80.855 | 87.0974 | 93.2991 | 99.5165
| HastingsWind2070RCP4.5 | Hastings | Wind | RCP4.5 | 2070 | 75.0615 | 80.9957 | 87.2814 | 93.5199 | 99.7753
| HastingsWind2075RCP4.5 | Hastings | Wind | RCP4.5 | 2075 | 75.1147 | 81.0691 | 87.3789 | 93.638 | 99.9142
| HastingsWind2080RCP4.5 | Hastings | Wind | RCP4.5 | 2080 | 75.1679 | 81.1424 | 87.4763 | 93.7561 | 100.0531
| HastingsWind2085RCP4.5 | Hastings | Wind | RCP4.5 | 2085 | 75.2211 | 81.2157 | 87.5738 | 93.8742 | 100.192
| HastingsWind2090RCP4.5 | Hastings | Wind | RCP4.5 | 2090 | 75.2744 | 81.289 | 87.6713 | 93.9923 | 100.3309
| HastingsWind2095RCP4.5 | Hastings | Wind | RCP4.5 | 2095 | 75.3276 | 81.3623 | 87.7687 | 94.1104 | 100.4698
| HastingsWind2100RCP4.5 | Hastings | Wind | RCP4.5 | 2100 | 75.3808 | 81.4356 | 87.8662 | 94.2285 | 100.6086
| HastingsWind2023RCP6.0 | Hastings | Wind | RCP6.0 | 2023 | 74.705 | 80.4759 | 86.5418 | 92.6089 | 98.6773
| HastingsWind2025RCP6.0 | Hastings | Wind | RCP6.0 | 2025 | 74.6766 | 80.4452 | 86.5117 | 92.5767 | 98.6446
| HastingsWind2030RCP6.0 | Hastings | Wind | RCP6.0 | 2030 | 74.6481 | 80.4146 | 86.4816 | 92.5445 | 98.6119
| HastingsWind2035RCP6.0 | Hastings | Wind | RCP6.0 | 2035 | 74.6196 | 80.3839 | 86.4515 | 92.5123 | 98.5792
| HastingsWind2040RCP6.0 | Hastings | Wind | RCP6.0 | 2040 | 74.5912 | 80.3532 | 86.4214 | 92.4801 | 98.5465
| HastingsWind2045RCP6.0 | Hastings | Wind | RCP6.0 | 2045 | 74.5627 | 80.3226 | 86.3913 | 92.4479 | 98.5139
| HastingsWind2050RCP6.0 | Hastings | Wind | RCP6.0 | 2050 | 74.6397 | 80.4327 | 86.5452 | 92.6365 | 98.74
| HastingsWind2055RCP6.0 | Hastings | Wind | RCP6.0 | 2055 | 74.7451 | 80.5735 | 86.7293 | 92.8574 | 98.9988
| HastingsWind2060RCP6.0 | Hastings | Wind | RCP6.0 | 2060 | 74.8506 | 80.7142 | 86.9133 | 93.0782 | 99.2577
| HastingsWind2065RCP6.0 | Hastings | Wind | RCP6.0 | 2065 | 74.956 | 80.855 | 87.0974 | 93.2991 | 99.5165
| HastingsWind2070RCP6.0 | Hastings | Wind | RCP6.0 | 2070 | 75.0615 | 80.9957 | 87.2814 | 93.5199 | 99.7753
| HastingsWind2075RCP6.0 | Hastings | Wind | RCP6.0 | 2075 | 75.1413 | 81.1057 | 87.4276 | 93.6971 | 99.9836
| HastingsWind2080RCP6.0 | Hastings | Wind | RCP6.0 | 2080 | 75.2211 | 81.2157 | 87.5738 | 93.8742 | 100.192
| HastingsWind2085RCP6.0 | Hastings | Wind | RCP6.0 | 2085 | 75.301 | 81.3257 | 87.72 | 94.0513 | 100.4003
| HastingsWind2090RCP6.0 | Hastings | Wind | RCP6.0 | 2090 | 75.6358 | 81.7449 | 88.2446 | 94.6702 | 101.1087
| HastingsWind2095RCP6.0 | Hastings | Wind | RCP6.0 | 2095 | 75.8907 | 82.0541 | 88.623 | 95.1119 | 101.6087
| HastingsWind2100RCP6.0 | Hastings | Wind | RCP6.0 | 2100 | 76.1457 | 82.3634 | 89.0014 | 95.5536 | 102.1087
| HastingsWind2023RCP8.5 | Hastings | Wind | RCP8.5 | 2023 | 74.705 | 80.4759 | 86.5418 | 92.6089 | 98.6773
| HastingsWind2025RCP8.5 | Hastings | Wind | RCP8.5 | 2025 | 74.6481 | 80.4146 | 86.4816 | 92.5445 | 98.6119
| HastingsWind2030RCP8.5 | Hastings | Wind | RCP8.5 | 2030 | 74.5912 | 80.3532 | 86.4214 | 92.4801 | 98.5465
| HastingsWind2035RCP8.5 | Hastings | Wind | RCP8.5 | 2035 | 74.5342 | 80.2919 | 86.3612 | 92.4157 | 98.4812
| HastingsWind2040RCP8.5 | Hastings | Wind | RCP8.5 | 2040 | 74.71 | 80.5265 | 86.6679 | 92.7838 | 98.9126
| HastingsWind2045RCP8.5 | Hastings | Wind | RCP8.5 | 2045 | 74.8857 | 80.7611 | 86.9747 | 93.1518 | 99.3439
| HastingsWind2050RCP8.5 | Hastings | Wind | RCP8.5 | 2050 | 75.1679 | 81.1424 | 87.4763 | 93.7561 | 100.0531
| HastingsWind2055RCP8.5 | Hastings | Wind | RCP8.5 | 2055 | 75.2744 | 81.289 | 87.6713 | 93.9923 | 100.3309
| HastingsWind2060RCP8.5 | Hastings | Wind | RCP8.5 | 2060 | 75.6358 | 81.7449 | 88.2446 | 94.6702 | 101.1087
| HastingsWind2065RCP8.5 | Hastings | Wind | RCP8.5 | 2065 | 75.8907 | 82.0541 | 88.623 | 95.1119 | 101.6087
| HastingsWind2070RCP8.5 | Hastings | Wind | RCP8.5 | 2070 | 76.0764 | 82.2861 | 88.9125 | 95.4554 | 102.0041
| HastingsWind2075RCP8.5 | Hastings | Wind | RCP8.5 | 2075 | 76.0071 | 82.2088 | 88.8237 | 95.3573 | 101.8995
| HastingsWind2080RCP8.5 | Hastings | Wind | RCP8.5 | 2080 | 75.9378 | 82.1315 | 88.7348 | 95.2591 | 101.7949
| HastingsWind2085RCP8.5 | Hastings | Wind | RCP8.5 | 2085 | 76.1197 | 82.4074 | 89.1304 | 95.7514 | 102.3881
| HastingsWind2090RCP8.5 | Hastings | Wind | RCP8.5 | 2090 | 76.3016 | 82.6833 | 89.526 | 96.2437 | 102.9812
| HastingsWind2095RCP8.5 | Hastings | Wind | RCP8.5 | 2095 | 76.3016 | 82.6833 | 89.526 | 96.2437 | 102.9812
| HastingsWind2100RCP8.5 | Hastings | Wind | RCP8.5 | 2100 | 76.3016 | 82.6833 | 89.526 | 96.2437 | 102.9812
| HawkesburyIce Accretion2023RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2023 | 20.6666 | 24.6012 | 29.61 | 33.4254 | 37.233
| HawkesburyIce Accretion2025RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2025 | 20.6736 | 24.6178 | 29.635 | 33.4593 | 37.2771
| HawkesburyIce Accretion2030RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2030 | 20.6805 | 24.6344 | 29.66 | 33.4932 | 37.3212
| HawkesburyIce Accretion2035RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2035 | 20.6875 | 24.651 | 29.685 | 33.5271 | 37.3653
| HawkesburyIce Accretion2040RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2040 | 20.6945 | 24.6676 | 29.71 | 33.561 | 37.4094
| HawkesburyIce Accretion2045RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2045 | 20.7014 | 24.6842 | 29.735 | 33.5949 | 37.4535
| HawkesburyIce Accretion2050RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2050 | 20.6625 | 24.661 | 29.724 | 33.5949 | 37.4674
| HawkesburyIce Accretion2055RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2055 | 20.6165 | 24.6211 | 29.688 | 33.561 | 37.4371
| HawkesburyIce Accretion2060RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2060 | 20.5706 | 24.5813 | 29.652 | 33.5271 | 37.4069
| HawkesburyIce Accretion2065RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2065 | 20.5247 | 24.5414 | 29.616 | 33.4932 | 37.3766
| HawkesburyIce Accretion2070RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2070 | 20.4788 | 24.5016 | 29.58 | 33.4593 | 37.3464
| HawkesburyIce Accretion2075RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2075 | 20.5588 | 24.6178 | 29.745 | 33.657 | 37.5795
| HawkesburyIce Accretion2080RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2080 | 20.6388 | 24.734 | 29.91 | 33.8548 | 37.8126
| HawkesburyIce Accretion2085RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2085 | 20.7188 | 24.8502 | 30.075 | 34.0525 | 38.0457
| HawkesburyIce Accretion2090RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2090 | 20.7988 | 24.9664 | 30.24 | 34.2503 | 38.2788
| HawkesburyIce Accretion2095RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2095 | 20.8789 | 25.0826 | 30.405 | 34.4481 | 38.5119
| HawkesburyIce Accretion2100RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2100 | 20.9589 | 25.1988 | 30.57 | 34.6458 | 38.745
| HawkesburyIce Accretion2023RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2023 | 20.6666 | 24.6012 | 29.61 | 33.4254 | 37.233
| HawkesburyIce Accretion2025RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2025 | 20.6736 | 24.6178 | 29.635 | 33.4593 | 37.2771
| HawkesburyIce Accretion2030RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2030 | 20.6805 | 24.6344 | 29.66 | 33.4932 | 37.3212
| HawkesburyIce Accretion2035RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2035 | 20.6875 | 24.651 | 29.685 | 33.5271 | 37.3653
| HawkesburyIce Accretion2040RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2040 | 20.6945 | 24.6676 | 29.71 | 33.561 | 37.4094
| HawkesburyIce Accretion2045RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2045 | 20.7014 | 24.6842 | 29.735 | 33.5949 | 37.4535
| HawkesburyIce Accretion2050RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2050 | 20.6625 | 24.661 | 29.724 | 33.5949 | 37.4674
| HawkesburyIce Accretion2055RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2055 | 20.6165 | 24.6211 | 29.688 | 33.561 | 37.4371
| HawkesburyIce Accretion2060RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2060 | 20.5706 | 24.5813 | 29.652 | 33.5271 | 37.4069
| HawkesburyIce Accretion2065RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2065 | 20.5247 | 24.5414 | 29.616 | 33.4932 | 37.3766
| HawkesburyIce Accretion2070RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2070 | 20.4788 | 24.5016 | 29.58 | 33.4593 | 37.3464
| HawkesburyIce Accretion2075RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2075 | 20.5988 | 24.6759 | 29.8275 | 33.7559 | 37.696
| HawkesburyIce Accretion2080RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2080 | 20.7188 | 24.8502 | 30.075 | 34.0525 | 38.0457
| HawkesburyIce Accretion2085RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2085 | 20.8389 | 25.0245 | 30.3225 | 34.3492 | 38.3953
| HawkesburyIce Accretion2090RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2090 | 20.9728 | 25.2403 | 30.65 | 34.7588 | 38.8836
| HawkesburyIce Accretion2095RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2095 | 20.9867 | 25.2818 | 30.73 | 34.8718 | 39.0222
| HawkesburyIce Accretion2100RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2100 | 21.0006 | 25.3233 | 30.81 | 34.9848 | 39.1608
| HawkesburyIce Accretion2023RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2023 | 20.6666 | 24.6012 | 29.61 | 33.4254 | 37.233
| HawkesburyIce Accretion2025RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2025 | 20.6805 | 24.6344 | 29.66 | 33.4932 | 37.3212
| HawkesburyIce Accretion2030RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2030 | 20.6945 | 24.6676 | 29.71 | 33.561 | 37.4094
| HawkesburyIce Accretion2035RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2035 | 20.7084 | 24.7008 | 29.76 | 33.6288 | 37.4976
| HawkesburyIce Accretion2040RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2040 | 20.6318 | 24.6344 | 29.7 | 33.5723 | 37.4472
| HawkesburyIce Accretion2045RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2045 | 20.5553 | 24.568 | 29.64 | 33.5158 | 37.3968
| HawkesburyIce Accretion2050RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2050 | 20.6388 | 24.734 | 29.91 | 33.8548 | 37.8126
| HawkesburyIce Accretion2055RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2055 | 20.7988 | 24.9664 | 30.24 | 34.2503 | 38.2788
| HawkesburyIce Accretion2060RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2060 | 20.9728 | 25.2403 | 30.65 | 34.7588 | 38.8836
| HawkesburyIce Accretion2065RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2065 | 20.9867 | 25.2818 | 30.73 | 34.8718 | 39.0222
| HawkesburyIce Accretion2070RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2070 | 21.0006 | 25.3648 | 30.9 | 35.1204 | 39.3372
| HawkesburyIce Accretion2075RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2075 | 21.0006 | 25.4063 | 30.99 | 35.256 | 39.5136
| HawkesburyIce Accretion2080RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2080 | 21.0006 | 25.4478 | 31.08 | 35.3916 | 39.69
| HawkesburyIce Accretion2085RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2085 | 20.5101 | 24.9124 | 30.495 | 34.7644 | 39.0096
| HawkesburyIce Accretion2090RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2090 | 20.0195 | 24.3771 | 29.91 | 34.1373 | 38.3292
| HawkesburyIce Accretion2095RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2095 | 20.0195 | 24.3771 | 29.91 | 34.1373 | 38.3292
| HawkesburyIce Accretion2100RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2100 | 20.0195 | 24.3771 | 29.91 | 34.1373 | 38.3292
| HawkesburyWind2023RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2023 | 83.2922 | 89.7532 | 96.5664 | 103.3671 | 110.1623
| HawkesburyWind2025RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2025 | 83.4055 | 89.8916 | 96.736 | 103.5623 | 110.3867
| HawkesburyWind2030RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2030 | 83.5188 | 90.03 | 96.9056 | 103.7575 | 110.611
| HawkesburyWind2035RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2035 | 83.6321 | 90.1683 | 97.0752 | 103.9526 | 110.8354
| HawkesburyWind2040RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2040 | 83.7454 | 90.3067 | 97.2448 | 104.1478 | 111.0597
| HawkesburyWind2045RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2045 | 83.8587 | 90.4451 | 97.4144 | 104.343 | 111.2841
| HawkesburyWind2050RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2050 | 83.8658 | 90.4406 | 97.3939 | 104.3101 | 111.2392
| HawkesburyWind2055RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2055 | 83.7597 | 90.2978 | 97.2038 | 104.0821 | 110.97
| HawkesburyWind2060RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2060 | 83.6536 | 90.1549 | 97.0138 | 103.854 | 110.7007
| HawkesburyWind2065RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2065 | 83.5475 | 90.0121 | 96.8237 | 103.626 | 110.4315
| HawkesburyWind2070RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2070 | 83.4414 | 89.8692 | 96.6336 | 103.398 | 110.1623
| HawkesburyWind2075RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2075 | 83.4538 | 89.8886 | 96.664 | 103.4356 | 110.2079
| HawkesburyWind2080RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2080 | 83.4663 | 89.9079 | 96.6944 | 103.4733 | 110.2535
| HawkesburyWind2085RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2085 | 83.4787 | 89.9273 | 96.7248 | 103.5109 | 110.2991
| HawkesburyWind2090RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2090 | 83.4912 | 89.9466 | 96.7552 | 103.5486 | 110.3447
| HawkesburyWind2095RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2095 | 83.5036 | 89.966 | 96.7856 | 103.5863 | 110.3903
| HawkesburyWind2100RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2100 | 83.516 | 89.9853 | 96.816 | 103.6239 | 110.4359
| HawkesburyWind2023RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2023 | 83.2922 | 89.7532 | 96.5664 | 103.3671 | 110.1623
| HawkesburyWind2025RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2025 | 83.4055 | 89.8916 | 96.736 | 103.5623 | 110.3867
| HawkesburyWind2030RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2030 | 83.5188 | 90.03 | 96.9056 | 103.7575 | 110.611
| HawkesburyWind2035RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2035 | 83.6321 | 90.1683 | 97.0752 | 103.9526 | 110.8354
| HawkesburyWind2040RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2040 | 83.7454 | 90.3067 | 97.2448 | 104.1478 | 111.0597
| HawkesburyWind2045RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2045 | 83.8587 | 90.4451 | 97.4144 | 104.343 | 111.2841
| HawkesburyWind2050RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2050 | 83.8658 | 90.4406 | 97.3939 | 104.3101 | 111.2392
| HawkesburyWind2055RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2055 | 83.7597 | 90.2978 | 97.2038 | 104.0821 | 110.97
| HawkesburyWind2060RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2060 | 83.6536 | 90.1549 | 97.0138 | 103.854 | 110.7007
| HawkesburyWind2065RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2065 | 83.5475 | 90.0121 | 96.8237 | 103.626 | 110.4315
| HawkesburyWind2070RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2070 | 83.4414 | 89.8692 | 96.6336 | 103.398 | 110.1623
| HawkesburyWind2075RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2075 | 83.4601 | 89.8983 | 96.6792 | 103.4544 | 110.2307
| HawkesburyWind2080RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2080 | 83.4787 | 89.9273 | 96.7248 | 103.5109 | 110.2991
| HawkesburyWind2085RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2085 | 83.4974 | 89.9563 | 96.7704 | 103.5674 | 110.3675
| HawkesburyWind2090RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2090 | 83.4 | 89.8306 | 96.608 | 103.374 | 110.1441
| HawkesburyWind2095RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2095 | 83.2839 | 89.6758 | 96.4 | 103.124 | 109.8522
| HawkesburyWind2100RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2100 | 83.1679 | 89.5211 | 96.192 | 102.8741 | 109.5604
| HawkesburyWind2023RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2023 | 83.2922 | 89.7532 | 96.5664 | 103.3671 | 110.1623
| HawkesburyWind2025RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2025 | 83.5188 | 90.03 | 96.9056 | 103.7575 | 110.611
| HawkesburyWind2030RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2030 | 83.7454 | 90.3067 | 97.2448 | 104.1478 | 111.0597
| HawkesburyWind2035RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2035 | 83.9719 | 90.5835 | 97.584 | 104.5381 | 111.5084
| HawkesburyWind2040RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2040 | 83.7951 | 90.3454 | 97.2672 | 104.1581 | 111.0597
| HawkesburyWind2045RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2045 | 83.6183 | 90.1073 | 96.9504 | 103.778 | 110.611
| HawkesburyWind2050RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2050 | 83.4663 | 89.9079 | 96.6944 | 103.4733 | 110.2535
| HawkesburyWind2055RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2055 | 83.4912 | 89.9466 | 96.7552 | 103.5486 | 110.3447
| HawkesburyWind2060RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2060 | 83.4 | 89.8306 | 96.608 | 103.374 | 110.1441
| HawkesburyWind2065RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2065 | 83.2839 | 89.6758 | 96.4 | 103.124 | 109.8522
| HawkesburyWind2070RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2070 | 83.3337 | 89.7294 | 96.4576 | 103.1857 | 109.9215
| HawkesburyWind2075RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2075 | 83.4994 | 89.9377 | 96.7232 | 103.4972 | 110.2827
| HawkesburyWind2080RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2080 | 83.6652 | 90.146 | 96.9888 | 103.8088 | 110.6438
| HawkesburyWind2085RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2085 | 83.574 | 90.021 | 96.8112 | 103.5931 | 110.3812
| HawkesburyWind2090RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2090 | 83.4829 | 89.896 | 96.6336 | 103.3774 | 110.1185
| HawkesburyWind2095RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2095 | 83.4829 | 89.896 | 96.6336 | 103.3774 | 110.1185
| HawkesburyWind2100RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2100 | 83.4829 | 89.896 | 96.6336 | 103.3774 | 110.1185
| HearstIce Accretion2023RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2023 | 10.4377 | 12.4375 | 14.97 | 16.9161 | 18.8433
| HearstIce Accretion2025RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2025 | 10.5247 | 12.5454 | 15.1025 | 17.0658 | 19.0134
| HearstIce Accretion2030RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2030 | 10.6117 | 12.6533 | 15.235 | 17.2156 | 19.1835
| HearstIce Accretion2035RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2035 | 10.6986 | 12.7613 | 15.3675 | 17.3653 | 19.3536
| HearstIce Accretion2040RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2040 | 10.7856 | 12.8691 | 15.5 | 17.515 | 19.5237
| HearstIce Accretion2045RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2045 | 10.8726 | 12.977 | 15.6325 | 17.6647 | 19.6938
| HearstIce Accretion2050RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2050 | 10.9992 | 13.1298 | 15.819 | 17.8755 | 19.9319
| HearstIce Accretion2055RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2055 | 11.0389 | 13.1746 | 15.873 | 17.9365 | 20
| HearstIce Accretion2060RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2060 | 11.0786 | 13.2194 | 15.927 | 17.9975 | 20.068
| HearstIce Accretion2065RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2065 | 11.1182 | 13.2642 | 15.981 | 18.0585 | 20.1361
| HearstIce Accretion2070RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2070 | 11.1579 | 13.309 | 16.035 | 18.1195 | 20.2041
| HearstIce Accretion2075RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2075 | 11.177 | 13.336 | 16.07 | 18.1619 | 20.2513
| HearstIce Accretion2080RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2080 | 11.1962 | 13.363 | 16.105 | 18.2043 | 20.2986
| HearstIce Accretion2085RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2085 | 11.2153 | 13.39 | 16.14 | 18.2467 | 20.3458
| HearstIce Accretion2090RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2090 | 11.2344 | 13.4169 | 16.175 | 18.289 | 20.3931
| HearstIce Accretion2095RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2095 | 11.2536 | 13.4439 | 16.21 | 18.3314 | 20.4403
| HearstIce Accretion2100RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2100 | 11.2727 | 13.4709 | 16.245 | 18.3738 | 20.4876
| HearstIce Accretion2023RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2023 | 10.4377 | 12.4375 | 14.97 | 16.9161 | 18.8433
| HearstIce Accretion2025RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2025 | 10.5247 | 12.5454 | 15.1025 | 17.0658 | 19.0134
| HearstIce Accretion2030RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2030 | 10.6117 | 12.6533 | 15.235 | 17.2156 | 19.1835
| HearstIce Accretion2035RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2035 | 10.6986 | 12.7613 | 15.3675 | 17.3653 | 19.3536
| HearstIce Accretion2040RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2040 | 10.7856 | 12.8691 | 15.5 | 17.515 | 19.5237
| HearstIce Accretion2045RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2045 | 10.8726 | 12.977 | 15.6325 | 17.6647 | 19.6938
| HearstIce Accretion2050RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2050 | 10.9992 | 13.1298 | 15.819 | 17.8755 | 19.9319
| HearstIce Accretion2055RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2055 | 11.0389 | 13.1746 | 15.873 | 17.9365 | 20
| HearstIce Accretion2060RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2060 | 11.0786 | 13.2194 | 15.927 | 17.9975 | 20.068
| HearstIce Accretion2065RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2065 | 11.1182 | 13.2642 | 15.981 | 18.0585 | 20.1361
| HearstIce Accretion2070RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2070 | 11.1579 | 13.309 | 16.035 | 18.1195 | 20.2041
| HearstIce Accretion2075RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2075 | 11.1866 | 13.3495 | 16.0875 | 18.1831 | 20.275
| HearstIce Accretion2080RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2080 | 11.2153 | 13.39 | 16.14 | 18.2467 | 20.3458
| HearstIce Accretion2085RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2085 | 11.244 | 13.4304 | 16.1925 | 18.3102 | 20.4167
| HearstIce Accretion2090RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2090 | 11.1788 | 13.3672 | 16.13 | 18.2438 | 20.349
| HearstIce Accretion2095RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2095 | 11.0848 | 13.2634 | 16.015 | 18.1139 | 20.2104
| HearstIce Accretion2100RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2100 | 10.9909 | 13.1596 | 15.9 | 17.9839 | 20.0718
| HearstIce Accretion2023RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2023 | 10.4377 | 12.4375 | 14.97 | 16.9161 | 18.8433
| HearstIce Accretion2025RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2025 | 10.6117 | 12.6533 | 15.235 | 17.2156 | 19.1835
| HearstIce Accretion2030RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2030 | 10.7856 | 12.8691 | 15.5 | 17.515 | 19.5237
| HearstIce Accretion2035RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2035 | 10.9596 | 13.0849 | 15.765 | 17.8144 | 19.8639
| HearstIce Accretion2040RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2040 | 11.0257 | 13.1596 | 15.855 | 17.9161 | 19.9773
| HearstIce Accretion2045RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2045 | 11.0918 | 13.2343 | 15.945 | 18.0178 | 20.0907
| HearstIce Accretion2050RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2050 | 11.1962 | 13.363 | 16.105 | 18.2043 | 20.2986
| HearstIce Accretion2055RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2055 | 11.2344 | 13.4169 | 16.175 | 18.289 | 20.3931
| HearstIce Accretion2060RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2060 | 11.1788 | 13.3672 | 16.13 | 18.2438 | 20.349
| HearstIce Accretion2065RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2065 | 11.0848 | 13.2634 | 16.015 | 18.1139 | 20.2104
| HearstIce Accretion2070RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2070 | 10.9387 | 13.114 | 15.865 | 17.9613 | 20.0529
| HearstIce Accretion2075RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2075 | 10.8865 | 13.0684 | 15.83 | 17.9387 | 20.034
| HearstIce Accretion2080RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2080 | 10.8343 | 13.0227 | 15.795 | 17.9161 | 20.0151
| HearstIce Accretion2085RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2085 | 10.6204 | 12.7986 | 15.5475 | 17.6534 | 19.741
| HearstIce Accretion2090RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2090 | 10.4064 | 12.5745 | 15.3 | 17.3907 | 19.467
| HearstIce Accretion2095RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2095 | 10.4064 | 12.5745 | 15.3 | 17.3907 | 19.467
| HearstIce Accretion2100RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2100 | 10.4064 | 12.5745 | 15.3 | 17.3907 | 19.467
| HearstWind2023RCP4.5 | Hearst | Wind | RCP4.5 | 2023 | 69.9352 | 75.3598 | 81.072 | 86.7813 | 92.4859
| HearstWind2025RCP4.5 | Hearst | Wind | RCP4.5 | 2025 | 70.0146 | 75.4528 | 81.1813 | 86.904 | 92.6227
| HearstWind2030RCP4.5 | Hearst | Wind | RCP4.5 | 2030 | 70.094 | 75.5458 | 81.2907 | 87.0267 | 92.7595
| HearstWind2035RCP4.5 | Hearst | Wind | RCP4.5 | 2035 | 70.1735 | 75.6388 | 81.4 | 87.1494 | 92.8963
| HearstWind2040RCP4.5 | Hearst | Wind | RCP4.5 | 2040 | 70.2529 | 75.7318 | 81.5093 | 87.2721 | 93.0331
| HearstWind2045RCP4.5 | Hearst | Wind | RCP4.5 | 2045 | 70.3324 | 75.8248 | 81.6187 | 87.3947 | 93.1699
| HearstWind2050RCP4.5 | Hearst | Wind | RCP4.5 | 2050 | 70.445 | 75.9431 | 81.744 | 87.526 | 93.3085
| HearstWind2055RCP4.5 | Hearst | Wind | RCP4.5 | 2055 | 70.4781 | 75.9684 | 81.76 | 87.5346 | 93.3104
| HearstWind2060RCP4.5 | Hearst | Wind | RCP4.5 | 2060 | 70.5113 | 75.9936 | 81.776 | 87.5431 | 93.3122
| HearstWind2065RCP4.5 | Hearst | Wind | RCP4.5 | 2065 | 70.5444 | 76.0189 | 81.792 | 87.5517 | 93.314
| HearstWind2070RCP4.5 | Hearst | Wind | RCP4.5 | 2070 | 70.5776 | 76.0442 | 81.808 | 87.5602 | 93.3158
| HearstWind2075RCP4.5 | Hearst | Wind | RCP4.5 | 2075 | 70.5811 | 76.0393 | 81.7907 | 87.5346 | 93.2809
| HearstWind2080RCP4.5 | Hearst | Wind | RCP4.5 | 2080 | 70.5845 | 76.0343 | 81.7733 | 87.5089 | 93.2459
| HearstWind2085RCP4.5 | Hearst | Wind | RCP4.5 | 2085 | 70.588 | 76.0294 | 81.756 | 87.4832 | 93.211
| HearstWind2090RCP4.5 | Hearst | Wind | RCP4.5 | 2090 | 70.5914 | 76.0244 | 81.7387 | 87.4575 | 93.176
| HearstWind2095RCP4.5 | Hearst | Wind | RCP4.5 | 2095 | 70.5949 | 76.0194 | 81.7213 | 87.4318 | 93.141
| HearstWind2100RCP4.5 | Hearst | Wind | RCP4.5 | 2100 | 70.5983 | 76.0145 | 81.704 | 87.4062 | 93.1061
| HearstWind2023RCP6.0 | Hearst | Wind | RCP6.0 | 2023 | 69.9352 | 75.3598 | 81.072 | 86.7813 | 92.4859
| HearstWind2025RCP6.0 | Hearst | Wind | RCP6.0 | 2025 | 70.0146 | 75.4528 | 81.1813 | 86.904 | 92.6227
| HearstWind2030RCP6.0 | Hearst | Wind | RCP6.0 | 2030 | 70.094 | 75.5458 | 81.2907 | 87.0267 | 92.7595
| HearstWind2035RCP6.0 | Hearst | Wind | RCP6.0 | 2035 | 70.1735 | 75.6388 | 81.4 | 87.1494 | 92.8963
| HearstWind2040RCP6.0 | Hearst | Wind | RCP6.0 | 2040 | 70.2529 | 75.7318 | 81.5093 | 87.2721 | 93.0331
| HearstWind2045RCP6.0 | Hearst | Wind | RCP6.0 | 2045 | 70.3324 | 75.8248 | 81.6187 | 87.3947 | 93.1699
| HearstWind2050RCP6.0 | Hearst | Wind | RCP6.0 | 2050 | 70.445 | 75.9431 | 81.744 | 87.526 | 93.3085
| HearstWind2055RCP6.0 | Hearst | Wind | RCP6.0 | 2055 | 70.4781 | 75.9684 | 81.76 | 87.5346 | 93.3104
| HearstWind2060RCP6.0 | Hearst | Wind | RCP6.0 | 2060 | 70.5113 | 75.9936 | 81.776 | 87.5431 | 93.3122
| HearstWind2065RCP6.0 | Hearst | Wind | RCP6.0 | 2065 | 70.5444 | 76.0189 | 81.792 | 87.5517 | 93.314
| HearstWind2070RCP6.0 | Hearst | Wind | RCP6.0 | 2070 | 70.5776 | 76.0442 | 81.808 | 87.5602 | 93.3158
| HearstWind2075RCP6.0 | Hearst | Wind | RCP6.0 | 2075 | 70.5828 | 76.0368 | 81.782 | 87.5217 | 93.2634
| HearstWind2080RCP6.0 | Hearst | Wind | RCP6.0 | 2080 | 70.588 | 76.0294 | 81.756 | 87.4832 | 93.211
| HearstWind2085RCP6.0 | Hearst | Wind | RCP6.0 | 2085 | 70.5931 | 76.0219 | 81.73 | 87.4447 | 93.1585
| HearstWind2090RCP6.0 | Hearst | Wind | RCP6.0 | 2090 | 70.6167 | 76.0219 | 81.7013 | 87.3919 | 93.0787
| HearstWind2095RCP6.0 | Hearst | Wind | RCP6.0 | 2095 | 70.6352 | 76.0294 | 81.6987 | 87.3776 | 93.0514
| HearstWind2100RCP6.0 | Hearst | Wind | RCP6.0 | 2100 | 70.6536 | 76.0368 | 81.696 | 87.3634 | 93.024
| HearstWind2023RCP8.5 | Hearst | Wind | RCP8.5 | 2023 | 69.9352 | 75.3598 | 81.072 | 86.7813 | 92.4859
| HearstWind2025RCP8.5 | Hearst | Wind | RCP8.5 | 2025 | 70.094 | 75.5458 | 81.2907 | 87.0267 | 92.7595
| HearstWind2030RCP8.5 | Hearst | Wind | RCP8.5 | 2030 | 70.2529 | 75.7318 | 81.5093 | 87.2721 | 93.0331
| HearstWind2035RCP8.5 | Hearst | Wind | RCP8.5 | 2035 | 70.4118 | 75.9178 | 81.728 | 87.5174 | 93.3067
| HearstWind2040RCP8.5 | Hearst | Wind | RCP8.5 | 2040 | 70.4671 | 75.9599 | 81.7547 | 87.5317 | 93.3098
| HearstWind2045RCP8.5 | Hearst | Wind | RCP8.5 | 2045 | 70.5223 | 76.0021 | 81.7813 | 87.546 | 93.3128
| HearstWind2050RCP8.5 | Hearst | Wind | RCP8.5 | 2050 | 70.5845 | 76.0343 | 81.7733 | 87.5089 | 93.2459
| HearstWind2055RCP8.5 | Hearst | Wind | RCP8.5 | 2055 | 70.5914 | 76.0244 | 81.7387 | 87.4575 | 93.176
| HearstWind2060RCP8.5 | Hearst | Wind | RCP8.5 | 2060 | 70.6167 | 76.0219 | 81.7013 | 87.3919 | 93.0787
| HearstWind2065RCP8.5 | Hearst | Wind | RCP8.5 | 2065 | 70.6352 | 76.0294 | 81.6987 | 87.3776 | 93.0514
| HearstWind2070RCP8.5 | Hearst | Wind | RCP8.5 | 2070 | 70.7987 | 76.2104 | 81.8987 | 87.5916 | 93.2824
| HearstWind2075RCP8.5 | Hearst | Wind | RCP8.5 | 2075 | 70.9437 | 76.384 | 82.1013 | 87.8199 | 93.5408
| HearstWind2080RCP8.5 | Hearst | Wind | RCP8.5 | 2080 | 71.0888 | 76.5576 | 82.304 | 88.0482 | 93.7992
| HearstWind2085RCP8.5 | Hearst | Wind | RCP8.5 | 2085 | 71.2649 | 76.7845 | 82.592 | 88.3906 | 94.1959
| HearstWind2090RCP8.5 | Hearst | Wind | RCP8.5 | 2090 | 71.4411 | 77.0114 | 82.88 | 88.733 | 94.5926
| HearstWind2095RCP8.5 | Hearst | Wind | RCP8.5 | 2095 | 71.4411 | 77.0114 | 82.88 | 88.733 | 94.5926
| HearstWind2100RCP8.5 | Hearst | Wind | RCP8.5 | 2100 | 71.4411 | 77.0114 | 82.88 | 88.733 | 94.5926
| Honey HarbourIce Accretion2023RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2023 | 13.6525 | 16.2846 | 19.62 | 22.1706 | 24.7464
| Honey HarbourIce Accretion2025RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2025 | 13.6363 | 16.2735 | 19.6133 | 22.1706 | 24.7464
| Honey HarbourIce Accretion2030RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2030 | 13.62 | 16.2625 | 19.6067 | 22.1706 | 24.7464
| Honey HarbourIce Accretion2035RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2035 | 13.6038 | 16.2514 | 19.6 | 22.1706 | 24.7464
| Honey HarbourIce Accretion2040RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2040 | 13.5876 | 16.2403 | 19.5933 | 22.1706 | 24.7464
| Honey HarbourIce Accretion2045RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2045 | 13.5713 | 16.2293 | 19.5867 | 22.1706 | 24.7464
| Honey HarbourIce Accretion2050RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2050 | 13.5523 | 16.2282 | 19.612 | 22.2113 | 24.8018
| Honey HarbourIce Accretion2055RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2055 | 13.5495 | 16.2381 | 19.644 | 22.252 | 24.8573
| Honey HarbourIce Accretion2060RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2060 | 13.5467 | 16.2481 | 19.676 | 22.2926 | 24.9127
| Honey HarbourIce Accretion2065RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2065 | 13.5439 | 16.258 | 19.708 | 22.3333 | 24.9682
| Honey HarbourIce Accretion2070RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2070 | 13.5412 | 16.268 | 19.74 | 22.374 | 25.0236
| Honey HarbourIce Accretion2075RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2075 | 13.5806 | 16.3316 | 19.83 | 22.4832 | 25.1538
| Honey HarbourIce Accretion2080RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2080 | 13.62 | 16.3953 | 19.92 | 22.5925 | 25.284
| Honey HarbourIce Accretion2085RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2085 | 13.6595 | 16.4589 | 20.01 | 22.7017 | 25.4142
| Honey HarbourIce Accretion2090RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2090 | 13.6989 | 16.5225 | 20.1 | 22.8109 | 25.5444
| Honey HarbourIce Accretion2095RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2095 | 13.7383 | 16.5862 | 20.19 | 22.9202 | 25.6746
| Honey HarbourIce Accretion2100RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2100 | 13.7778 | 16.6498 | 20.28 | 23.0294 | 25.8048
| Honey HarbourIce Accretion2023RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2023 | 13.6525 | 16.2846 | 19.62 | 22.1706 | 24.7464
| Honey HarbourIce Accretion2025RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2025 | 13.6363 | 16.2735 | 19.6133 | 22.1706 | 24.7464
| Honey HarbourIce Accretion2030RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2030 | 13.62 | 16.2625 | 19.6067 | 22.1706 | 24.7464
| Honey HarbourIce Accretion2035RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2035 | 13.6038 | 16.2514 | 19.6 | 22.1706 | 24.7464
| Honey HarbourIce Accretion2040RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2040 | 13.5876 | 16.2403 | 19.5933 | 22.1706 | 24.7464
| Honey HarbourIce Accretion2045RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2045 | 13.5713 | 16.2293 | 19.5867 | 22.1706 | 24.7464
| Honey HarbourIce Accretion2050RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2050 | 13.5523 | 16.2282 | 19.612 | 22.2113 | 24.8018
| Honey HarbourIce Accretion2055RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2055 | 13.5495 | 16.2381 | 19.644 | 22.252 | 24.8573
| Honey HarbourIce Accretion2060RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2060 | 13.5467 | 16.2481 | 19.676 | 22.2926 | 24.9127
| Honey HarbourIce Accretion2065RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2065 | 13.5439 | 16.258 | 19.708 | 22.3333 | 24.9682
| Honey HarbourIce Accretion2070RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2070 | 13.5412 | 16.268 | 19.74 | 22.374 | 25.0236
| Honey HarbourIce Accretion2075RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2075 | 13.6003 | 16.3634 | 19.875 | 22.5378 | 25.2189
| Honey HarbourIce Accretion2080RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2080 | 13.6595 | 16.4589 | 20.01 | 22.7017 | 25.4142
| Honey HarbourIce Accretion2085RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2085 | 13.7186 | 16.5543 | 20.145 | 22.8655 | 25.6095
| Honey HarbourIce Accretion2090RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2090 | 13.7546 | 16.6609 | 20.3333 | 23.1198 | 25.9224
| Honey HarbourIce Accretion2095RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2095 | 13.7314 | 16.6719 | 20.3867 | 23.2102 | 26.04
| Honey HarbourIce Accretion2100RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2100 | 13.7082 | 16.683 | 20.44 | 23.3006 | 26.1576
| Honey HarbourIce Accretion2023RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2023 | 13.6525 | 16.2846 | 19.62 | 22.1706 | 24.7464
| Honey HarbourIce Accretion2025RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2025 | 13.62 | 16.2625 | 19.6067 | 22.1706 | 24.7464
| Honey HarbourIce Accretion2030RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2030 | 13.5876 | 16.2403 | 19.5933 | 22.1706 | 24.7464
| Honey HarbourIce Accretion2035RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2035 | 13.5551 | 16.2182 | 19.58 | 22.1706 | 24.7464
| Honey HarbourIce Accretion2040RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2040 | 13.5504 | 16.2348 | 19.6333 | 22.2384 | 24.8388
| Honey HarbourIce Accretion2045RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2045 | 13.5458 | 16.2514 | 19.6867 | 22.3062 | 24.9312
| Honey HarbourIce Accretion2050RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2050 | 13.62 | 16.3953 | 19.92 | 22.5925 | 25.284
| Honey HarbourIce Accretion2055RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2055 | 13.6989 | 16.5225 | 20.1 | 22.8109 | 25.5444
| Honey HarbourIce Accretion2060RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2060 | 13.7546 | 16.6609 | 20.3333 | 23.1198 | 25.9224
| Honey HarbourIce Accretion2065RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2065 | 13.7314 | 16.6719 | 20.3867 | 23.2102 | 26.04
| Honey HarbourIce Accretion2070RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2070 | 13.4577 | 16.4174 | 20.1533 | 22.9917 | 25.83
| Honey HarbourIce Accretion2075RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2075 | 13.2072 | 16.1518 | 19.8667 | 22.6829 | 25.5024
| Honey HarbourIce Accretion2080RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2080 | 12.9567 | 15.8862 | 19.58 | 22.374 | 25.1748
| Honey HarbourIce Accretion2085RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2085 | 12.4348 | 15.2969 | 18.9 | 21.6282 | 24.3558
| Honey HarbourIce Accretion2090RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2090 | 11.9129 | 14.7076 | 18.22 | 20.8824 | 23.5368
| Honey HarbourIce Accretion2095RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2095 | 11.9129 | 14.7076 | 18.22 | 20.8824 | 23.5368
| Honey HarbourIce Accretion2100RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2100 | 11.9129 | 14.7076 | 18.22 | 20.8824 | 23.5368
| Honey HarbourWind2023RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2023 | 76.4728 | 82.3965 | 88.6424 | 94.8756 | 101.1125
| Honey HarbourWind2025RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2025 | 76.5513 | 82.4906 | 88.7539 | 95.0027 | 101.2546
| Honey HarbourWind2030RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2030 | 76.6298 | 82.5847 | 88.8653 | 95.1298 | 101.3968
| Honey HarbourWind2035RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2035 | 76.7083 | 82.6789 | 88.9768 | 95.257 | 101.5389
| Honey HarbourWind2040RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2040 | 76.7868 | 82.773 | 89.0883 | 95.3841 | 101.681
| Honey HarbourWind2045RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2045 | 76.8654 | 82.8671 | 89.1997 | 95.5112 | 101.8231
| Honey HarbourWind2050RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2050 | 77.0533 | 83.0922 | 89.4696 | 95.821 | 102.1739
| Honey HarbourWind2055RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2055 | 77.1627 | 83.2231 | 89.628 | 96.0037 | 102.3826
| Honey HarbourWind2060RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2060 | 77.2721 | 83.354 | 89.7864 | 96.1863 | 102.5912
| Honey HarbourWind2065RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2065 | 77.3816 | 83.485 | 89.9448 | 96.369 | 102.7999
| Honey HarbourWind2070RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2070 | 77.491 | 83.6159 | 90.1032 | 96.5517 | 103.0086
| Honey HarbourWind2075RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2075 | 77.5252 | 83.665 | 90.1721 | 96.6364 | 103.1089
| Honey HarbourWind2080RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2080 | 77.5594 | 83.7141 | 90.2411 | 96.7212 | 103.2092
| Honey HarbourWind2085RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2085 | 77.5936 | 83.7632 | 90.31 | 96.8059 | 103.3095
| Honey HarbourWind2090RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2090 | 77.6278 | 83.8123 | 90.3789 | 96.8906 | 103.4099
| Honey HarbourWind2095RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2095 | 77.662 | 83.8614 | 90.4479 | 96.9754 | 103.5102
| Honey HarbourWind2100RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2100 | 77.6961 | 83.9106 | 90.5168 | 97.0601 | 103.6105
| Honey HarbourWind2023RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2023 | 76.4728 | 82.3965 | 88.6424 | 94.8756 | 101.1125
| Honey HarbourWind2025RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2025 | 76.5513 | 82.4906 | 88.7539 | 95.0027 | 101.2546
| Honey HarbourWind2030RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2030 | 76.6298 | 82.5847 | 88.8653 | 95.1298 | 101.3968
| Honey HarbourWind2035RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2035 | 76.7083 | 82.6789 | 88.9768 | 95.257 | 101.5389
| Honey HarbourWind2040RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2040 | 76.7868 | 82.773 | 89.0883 | 95.3841 | 101.681
| Honey HarbourWind2045RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2045 | 76.8654 | 82.8671 | 89.1997 | 95.5112 | 101.8231
| Honey HarbourWind2050RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2050 | 77.0533 | 83.0922 | 89.4696 | 95.821 | 102.1739
| Honey HarbourWind2055RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2055 | 77.1627 | 83.2231 | 89.628 | 96.0037 | 102.3826
| Honey HarbourWind2060RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2060 | 77.2721 | 83.354 | 89.7864 | 96.1863 | 102.5912
| Honey HarbourWind2065RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2065 | 77.3816 | 83.485 | 89.9448 | 96.369 | 102.7999
| Honey HarbourWind2070RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2070 | 77.491 | 83.6159 | 90.1032 | 96.5517 | 103.0086
| Honey HarbourWind2075RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2075 | 77.5423 | 83.6896 | 90.2066 | 96.6788 | 103.1591
| Honey HarbourWind2080RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2080 | 77.5936 | 83.7632 | 90.31 | 96.8059 | 103.3095
| Honey HarbourWind2085RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2085 | 77.6449 | 83.8369 | 90.4134 | 96.933 | 103.46
| Honey HarbourWind2090RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2090 | 77.8101 | 84.0633 | 90.7133 | 97.2955 | 103.8847
| Honey HarbourWind2095RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2095 | 77.9241 | 84.2161 | 90.9099 | 97.5309 | 104.1589
| Honey HarbourWind2100RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2100 | 78.0381 | 84.3689 | 91.1064 | 97.7663 | 104.4331
| Honey HarbourWind2023RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2023 | 76.4728 | 82.3965 | 88.6424 | 94.8756 | 101.1125
| Honey HarbourWind2025RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2025 | 76.6298 | 82.5847 | 88.8653 | 95.1298 | 101.3968
| Honey HarbourWind2030RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2030 | 76.7868 | 82.773 | 89.0883 | 95.3841 | 101.681
| Honey HarbourWind2035RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2035 | 76.9439 | 82.9612 | 89.3112 | 95.6383 | 101.9652
| Honey HarbourWind2040RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2040 | 77.1263 | 83.1794 | 89.5752 | 95.9428 | 102.313
| Honey HarbourWind2045RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2045 | 77.3086 | 83.3977 | 89.8392 | 96.2472 | 102.6608
| Honey HarbourWind2050RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2050 | 77.5594 | 83.7141 | 90.2411 | 96.7212 | 103.2092
| Honey HarbourWind2055RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2055 | 77.6278 | 83.8123 | 90.3789 | 96.8906 | 103.4099
| Honey HarbourWind2060RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2060 | 77.8101 | 84.0633 | 90.7133 | 97.2955 | 103.8847
| Honey HarbourWind2065RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2065 | 77.9241 | 84.2161 | 90.9099 | 97.5309 | 104.1589
| Honey HarbourWind2070RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2070 | 78.0254 | 84.3634 | 91.1123 | 97.7789 | 104.4565
| Honey HarbourWind2075RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2075 | 78.0128 | 84.3579 | 91.1181 | 97.7914 | 104.4799
| Honey HarbourWind2080RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2080 | 78.0001 | 84.3525 | 91.124 | 97.804 | 104.5033
| Honey HarbourWind2085RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2085 | 78.0989 | 84.4793 | 91.2912 | 98.0017 | 104.7341
| Honey HarbourWind2090RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2090 | 78.1977 | 84.6062 | 91.4584 | 98.1995 | 104.9648
| Honey HarbourWind2095RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2095 | 78.1977 | 84.6062 | 91.4584 | 98.1995 | 104.9648
| Honey HarbourWind2100RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2100 | 78.1977 | 84.6062 | 91.4584 | 98.1995 | 104.9648
| HornepayneIce Accretion2023RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2023 | 10.5316 | 12.5496 | 15.105 | 17.0686 | 19.0323
| HornepayneIce Accretion2025RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2025 | 10.603 | 12.6388 | 15.22 | 17.1986 | 19.1803
| HornepayneIce Accretion2030RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2030 | 10.6743 | 12.728 | 15.335 | 17.3285 | 19.3284
| HornepayneIce Accretion2035RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2035 | 10.7456 | 12.8173 | 15.45 | 17.4585 | 19.4764
| HornepayneIce Accretion2040RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2040 | 10.8169 | 12.9065 | 15.565 | 17.5884 | 19.6245
| HornepayneIce Accretion2045RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2045 | 10.8883 | 12.9957 | 15.68 | 17.7184 | 19.7725
| HornepayneIce Accretion2050RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2050 | 10.9742 | 13.0974 | 15.804 | 17.8585 | 19.9282
| HornepayneIce Accretion2055RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2055 | 10.9888 | 13.1098 | 15.813 | 17.8687 | 19.9357
| HornepayneIce Accretion2060RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2060 | 11.0034 | 13.1223 | 15.822 | 17.8789 | 19.9433
| HornepayneIce Accretion2065RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2065 | 11.018 | 13.1348 | 15.831 | 17.889 | 19.9508
| HornepayneIce Accretion2070RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2070 | 11.0326 | 13.1472 | 15.84 | 17.8992 | 19.9584
| HornepayneIce Accretion2075RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2075 | 11.057 | 13.1825 | 15.8875 | 17.9557 | 20.0214
| HornepayneIce Accretion2080RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2080 | 11.0813 | 13.2177 | 15.935 | 18.0122 | 20.0844
| HornepayneIce Accretion2085RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2085 | 11.1057 | 13.253 | 15.9825 | 18.0687 | 20.1474
| HornepayneIce Accretion2090RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2090 | 11.1301 | 13.2883 | 16.03 | 18.1252 | 20.2104
| HornepayneIce Accretion2095RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2095 | 11.1544 | 13.3236 | 16.0775 | 18.1817 | 20.2734
| HornepayneIce Accretion2100RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2100 | 11.1788 | 13.3588 | 16.125 | 18.2382 | 20.3364
| HornepayneIce Accretion2023RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2023 | 10.5316 | 12.5496 | 15.105 | 17.0686 | 19.0323
| HornepayneIce Accretion2025RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2025 | 10.603 | 12.6388 | 15.22 | 17.1986 | 19.1803
| HornepayneIce Accretion2030RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2030 | 10.6743 | 12.728 | 15.335 | 17.3285 | 19.3284
| HornepayneIce Accretion2035RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2035 | 10.7456 | 12.8173 | 15.45 | 17.4585 | 19.4764
| HornepayneIce Accretion2040RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2040 | 10.8169 | 12.9065 | 15.565 | 17.5884 | 19.6245
| HornepayneIce Accretion2045RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2045 | 10.8883 | 12.9957 | 15.68 | 17.7184 | 19.7725
| HornepayneIce Accretion2050RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2050 | 10.9742 | 13.0974 | 15.804 | 17.8585 | 19.9282
| HornepayneIce Accretion2055RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2055 | 10.9888 | 13.1098 | 15.813 | 17.8687 | 19.9357
| HornepayneIce Accretion2060RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2060 | 11.0034 | 13.1223 | 15.822 | 17.8789 | 19.9433
| HornepayneIce Accretion2065RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2065 | 11.018 | 13.1348 | 15.831 | 17.889 | 19.9508
| HornepayneIce Accretion2070RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2070 | 11.0326 | 13.1472 | 15.84 | 17.8992 | 19.9584
| HornepayneIce Accretion2075RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2075 | 11.0692 | 13.2001 | 15.9112 | 17.984 | 20.0529
| HornepayneIce Accretion2080RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2080 | 11.1057 | 13.253 | 15.9825 | 18.0687 | 20.1474
| HornepayneIce Accretion2085RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2085 | 11.1422 | 13.3059 | 16.0538 | 18.1534 | 20.2419
| HornepayneIce Accretion2090RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2090 | 11.0744 | 13.2426 | 15.985 | 18.0856 | 20.1726
| HornepayneIce Accretion2095RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2095 | 10.97 | 13.1264 | 15.845 | 17.9331 | 20.0088
| HornepayneIce Accretion2100RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2100 | 10.8656 | 13.0102 | 15.705 | 17.7805 | 19.845
| HornepayneIce Accretion2023RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2023 | 10.5316 | 12.5496 | 15.105 | 17.0686 | 19.0323
| HornepayneIce Accretion2025RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2025 | 10.6743 | 12.728 | 15.335 | 17.3285 | 19.3284
| HornepayneIce Accretion2030RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2030 | 10.8169 | 12.9065 | 15.565 | 17.5884 | 19.6245
| HornepayneIce Accretion2035RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2035 | 10.9596 | 13.0849 | 15.795 | 17.8483 | 19.9206
| HornepayneIce Accretion2040RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2040 | 10.9839 | 13.1057 | 15.81 | 17.8653 | 19.9332
| HornepayneIce Accretion2045RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2045 | 11.0083 | 13.1265 | 15.825 | 17.8822 | 19.9458
| HornepayneIce Accretion2050RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2050 | 11.0813 | 13.2177 | 15.935 | 18.0122 | 20.0844
| HornepayneIce Accretion2055RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2055 | 11.1301 | 13.2883 | 16.03 | 18.1252 | 20.2104
| HornepayneIce Accretion2060RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2060 | 11.0744 | 13.2426 | 15.985 | 18.0856 | 20.1726
| HornepayneIce Accretion2065RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2065 | 10.97 | 13.1264 | 15.845 | 17.9331 | 20.0088
| HornepayneIce Accretion2070RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2070 | 10.7856 | 12.9231 | 15.615 | 17.6845 | 19.7442
| HornepayneIce Accretion2075RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2075 | 10.7056 | 12.8359 | 15.525 | 17.5884 | 19.6434
| HornepayneIce Accretion2080RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2080 | 10.6256 | 12.7488 | 15.435 | 17.4924 | 19.5426
| HornepayneIce Accretion2085RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2085 | 10.4533 | 12.5558 | 15.21 | 17.2466 | 19.2685
| HornepayneIce Accretion2090RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2090 | 10.2811 | 12.3628 | 14.985 | 17.0008 | 18.9945
| HornepayneIce Accretion2095RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2095 | 10.2811 | 12.3628 | 14.985 | 17.0008 | 18.9945
| HornepayneIce Accretion2100RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2100 | 10.2811 | 12.3628 | 14.985 | 17.0008 | 18.9945
| HornepayneWind2023RCP4.5 | Hornepayne | Wind | RCP4.5 | 2023 | 69.9697 | 75.4342 | 81.208 | 86.9525 | 92.7048
| HornepayneWind2025RCP4.5 | Hornepayne | Wind | RCP4.5 | 2025 | 70.0699 | 75.5582 | 81.3613 | 87.1322 | 92.91
| HornepayneWind2030RCP4.5 | Hornepayne | Wind | RCP4.5 | 2030 | 70.17 | 75.6822 | 81.5147 | 87.312 | 93.1152
| HornepayneWind2035RCP4.5 | Hornepayne | Wind | RCP4.5 | 2035 | 70.2702 | 75.8062 | 81.668 | 87.4918 | 93.3204
| HornepayneWind2040RCP4.5 | Hornepayne | Wind | RCP4.5 | 2040 | 70.3704 | 75.9302 | 81.8213 | 87.6715 | 93.5256
| HornepayneWind2045RCP4.5 | Hornepayne | Wind | RCP4.5 | 2045 | 70.4705 | 76.0542 | 81.9747 | 87.8513 | 93.7308
| HornepayneWind2050RCP4.5 | Hornepayne | Wind | RCP4.5 | 2050 | 70.6633 | 76.2927 | 82.2672 | 88.192 | 94.1202
| HornepayneWind2055RCP4.5 | Hornepayne | Wind | RCP4.5 | 2055 | 70.7558 | 76.4073 | 82.4064 | 88.3529 | 94.3044
| HornepayneWind2060RCP4.5 | Hornepayne | Wind | RCP4.5 | 2060 | 70.8484 | 76.5219 | 82.5456 | 88.5138 | 94.4887
| HornepayneWind2065RCP4.5 | Hornepayne | Wind | RCP4.5 | 2065 | 70.941 | 76.6365 | 82.6848 | 88.6748 | 94.6729
| HornepayneWind2070RCP4.5 | Hornepayne | Wind | RCP4.5 | 2070 | 71.0335 | 76.751 | 82.824 | 88.8357 | 94.8571
| HornepayneWind2075RCP4.5 | Hornepayne | Wind | RCP4.5 | 2075 | 71.0232 | 76.7262 | 82.7813 | 88.7786 | 94.7842
| HornepayneWind2080RCP4.5 | Hornepayne | Wind | RCP4.5 | 2080 | 71.0128 | 76.7014 | 82.7387 | 88.7215 | 94.7112
| HornepayneWind2085RCP4.5 | Hornepayne | Wind | RCP4.5 | 2085 | 71.0024 | 76.6766 | 82.696 | 88.6645 | 94.6382
| HornepayneWind2090RCP4.5 | Hornepayne | Wind | RCP4.5 | 2090 | 70.9921 | 76.6518 | 82.6533 | 88.6074 | 94.5653
| HornepayneWind2095RCP4.5 | Hornepayne | Wind | RCP4.5 | 2095 | 70.9817 | 76.627 | 82.6107 | 88.5503 | 94.4923
| HornepayneWind2100RCP4.5 | Hornepayne | Wind | RCP4.5 | 2100 | 70.9713 | 76.6022 | 82.568 | 88.4933 | 94.4194
| HornepayneWind2023RCP6.0 | Hornepayne | Wind | RCP6.0 | 2023 | 69.9697 | 75.4342 | 81.208 | 86.9525 | 92.7048
| HornepayneWind2025RCP6.0 | Hornepayne | Wind | RCP6.0 | 2025 | 70.0699 | 75.5582 | 81.3613 | 87.1322 | 92.91
| HornepayneWind2030RCP6.0 | Hornepayne | Wind | RCP6.0 | 2030 | 70.17 | 75.6822 | 81.5147 | 87.312 | 93.1152
| HornepayneWind2035RCP6.0 | Hornepayne | Wind | RCP6.0 | 2035 | 70.2702 | 75.8062 | 81.668 | 87.4918 | 93.3204
| HornepayneWind2040RCP6.0 | Hornepayne | Wind | RCP6.0 | 2040 | 70.3704 | 75.9302 | 81.8213 | 87.6715 | 93.5256
| HornepayneWind2045RCP6.0 | Hornepayne | Wind | RCP6.0 | 2045 | 70.4705 | 76.0542 | 81.9747 | 87.8513 | 93.7308
| HornepayneWind2050RCP6.0 | Hornepayne | Wind | RCP6.0 | 2050 | 70.6633 | 76.2927 | 82.2672 | 88.192 | 94.1202
| HornepayneWind2055RCP6.0 | Hornepayne | Wind | RCP6.0 | 2055 | 70.7558 | 76.4073 | 82.4064 | 88.3529 | 94.3044
| HornepayneWind2060RCP6.0 | Hornepayne | Wind | RCP6.0 | 2060 | 70.8484 | 76.5219 | 82.5456 | 88.5138 | 94.4887
| HornepayneWind2065RCP6.0 | Hornepayne | Wind | RCP6.0 | 2065 | 70.941 | 76.6365 | 82.6848 | 88.6748 | 94.6729
| HornepayneWind2070RCP6.0 | Hornepayne | Wind | RCP6.0 | 2070 | 71.0335 | 76.751 | 82.824 | 88.8357 | 94.8571
| HornepayneWind2075RCP6.0 | Hornepayne | Wind | RCP6.0 | 2075 | 71.018 | 76.7138 | 82.76 | 88.7501 | 94.7477
| HornepayneWind2080RCP6.0 | Hornepayne | Wind | RCP6.0 | 2080 | 71.0024 | 76.6766 | 82.696 | 88.6645 | 94.6382
| HornepayneWind2085RCP6.0 | Hornepayne | Wind | RCP6.0 | 2085 | 70.9869 | 76.6394 | 82.632 | 88.5789 | 94.5288
| HornepayneWind2090RCP6.0 | Hornepayne | Wind | RCP6.0 | 2090 | 71.121 | 76.7659 | 82.7467 | 88.6873 | 94.6291
| HornepayneWind2095RCP6.0 | Hornepayne | Wind | RCP6.0 | 2095 | 71.2707 | 76.9296 | 82.9253 | 88.8813 | 94.8389
| HornepayneWind2100RCP6.0 | Hornepayne | Wind | RCP6.0 | 2100 | 71.4204 | 77.0933 | 83.104 | 89.0754 | 95.0486
| HornepayneWind2023RCP8.5 | Hornepayne | Wind | RCP8.5 | 2023 | 69.9697 | 75.4342 | 81.208 | 86.9525 | 92.7048
| HornepayneWind2025RCP8.5 | Hornepayne | Wind | RCP8.5 | 2025 | 70.17 | 75.6822 | 81.5147 | 87.312 | 93.1152
| HornepayneWind2030RCP8.5 | Hornepayne | Wind | RCP8.5 | 2030 | 70.3704 | 75.9302 | 81.8213 | 87.6715 | 93.5256
| HornepayneWind2035RCP8.5 | Hornepayne | Wind | RCP8.5 | 2035 | 70.5707 | 76.1782 | 82.128 | 88.031 | 93.936
| HornepayneWind2040RCP8.5 | Hornepayne | Wind | RCP8.5 | 2040 | 70.725 | 76.3691 | 82.36 | 88.2993 | 94.243
| HornepayneWind2045RCP8.5 | Hornepayne | Wind | RCP8.5 | 2045 | 70.8792 | 76.5601 | 82.592 | 88.5675 | 94.5501
| HornepayneWind2050RCP8.5 | Hornepayne | Wind | RCP8.5 | 2050 | 71.0128 | 76.7014 | 82.7387 | 88.7215 | 94.7112
| HornepayneWind2055RCP8.5 | Hornepayne | Wind | RCP8.5 | 2055 | 70.9921 | 76.6518 | 82.6533 | 88.6074 | 94.5653
| HornepayneWind2060RCP8.5 | Hornepayne | Wind | RCP8.5 | 2060 | 71.121 | 76.7659 | 82.7467 | 88.6873 | 94.6291
| HornepayneWind2065RCP8.5 | Hornepayne | Wind | RCP8.5 | 2065 | 71.2707 | 76.9296 | 82.9253 | 88.8813 | 94.8389
| HornepayneWind2070RCP8.5 | Hornepayne | Wind | RCP8.5 | 2070 | 71.4687 | 77.133 | 83.1307 | 89.0896 | 95.0517
| HornepayneWind2075RCP8.5 | Hornepayne | Wind | RCP8.5 | 2075 | 71.5171 | 77.1726 | 83.1573 | 89.1039 | 95.0547
| HornepayneWind2080RCP8.5 | Hornepayne | Wind | RCP8.5 | 2080 | 71.5654 | 77.2123 | 83.184 | 89.1182 | 95.0578
| HornepayneWind2085RCP8.5 | Hornepayne | Wind | RCP8.5 | 2085 | 71.7692 | 77.4578 | 83.48 | 89.4606 | 95.4454
| HornepayneWind2090RCP8.5 | Hornepayne | Wind | RCP8.5 | 2090 | 71.973 | 77.7034 | 83.776 | 89.803 | 95.833
| HornepayneWind2095RCP8.5 | Hornepayne | Wind | RCP8.5 | 2095 | 71.973 | 77.7034 | 83.776 | 89.803 | 95.833
| HornepayneWind2100RCP8.5 | Hornepayne | Wind | RCP8.5 | 2100 | 71.973 | 77.7034 | 83.776 | 89.803 | 95.833
| HuntsvilleIce Accretion2023RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2023 | 15.2627 | 18.2235 | 21.978 | 24.8351 | 27.6923
| HuntsvilleIce Accretion2025RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2025 | 15.2601 | 18.2265 | 21.989 | 24.8517 | 27.7154
| HuntsvilleIce Accretion2030RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2030 | 15.2576 | 18.2296 | 22 | 24.8683 | 27.7385
| HuntsvilleIce Accretion2035RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2035 | 15.255 | 18.2326 | 22.011 | 24.8849 | 27.7616
| HuntsvilleIce Accretion2040RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2040 | 15.2525 | 18.2357 | 22.022 | 24.9014 | 27.7847
| HuntsvilleIce Accretion2045RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2045 | 15.2499 | 18.2387 | 22.033 | 24.918 | 27.8078
| HuntsvilleIce Accretion2050RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2050 | 15.2382 | 18.249 | 22.066 | 24.9744 | 27.8863
| HuntsvilleIce Accretion2055RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2055 | 15.229 | 18.2563 | 22.088 | 25.0141 | 27.9418
| HuntsvilleIce Accretion2060RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2060 | 15.2198 | 18.2637 | 22.11 | 25.0539 | 27.9972
| HuntsvilleIce Accretion2065RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2065 | 15.2106 | 18.271 | 22.132 | 25.0937 | 28.0526
| HuntsvilleIce Accretion2070RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2070 | 15.2015 | 18.2783 | 22.154 | 25.1335 | 28.1081
| HuntsvilleIce Accretion2075RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2075 | 15.2346 | 18.33 | 22.2347 | 25.2288 | 28.2236
| HuntsvilleIce Accretion2080RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2080 | 15.2678 | 18.3817 | 22.3153 | 25.3241 | 28.3391
| HuntsvilleIce Accretion2085RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2085 | 15.301 | 18.4335 | 22.396 | 25.4193 | 28.4546
| HuntsvilleIce Accretion2090RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2090 | 15.3341 | 18.4852 | 22.4767 | 25.5146 | 28.5701
| HuntsvilleIce Accretion2095RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2095 | 15.3673 | 18.5369 | 22.5573 | 25.6099 | 28.6856
| HuntsvilleIce Accretion2100RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2100 | 15.4005 | 18.5887 | 22.638 | 25.7052 | 28.8011
| HuntsvilleIce Accretion2023RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2023 | 15.2627 | 18.2235 | 21.978 | 24.8351 | 27.6923
| HuntsvilleIce Accretion2025RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2025 | 15.2601 | 18.2265 | 21.989 | 24.8517 | 27.7154
| HuntsvilleIce Accretion2030RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2030 | 15.2576 | 18.2296 | 22 | 24.8683 | 27.7385
| HuntsvilleIce Accretion2035RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2035 | 15.255 | 18.2326 | 22.011 | 24.8849 | 27.7616
| HuntsvilleIce Accretion2040RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2040 | 15.2525 | 18.2357 | 22.022 | 24.9014 | 27.7847
| HuntsvilleIce Accretion2045RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2045 | 15.2499 | 18.2387 | 22.033 | 24.918 | 27.8078
| HuntsvilleIce Accretion2050RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2050 | 15.2382 | 18.249 | 22.066 | 24.9744 | 27.8863
| HuntsvilleIce Accretion2055RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2055 | 15.229 | 18.2563 | 22.088 | 25.0141 | 27.9418
| HuntsvilleIce Accretion2060RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2060 | 15.2198 | 18.2637 | 22.11 | 25.0539 | 27.9972
| HuntsvilleIce Accretion2065RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2065 | 15.2106 | 18.271 | 22.132 | 25.0937 | 28.0526
| HuntsvilleIce Accretion2070RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2070 | 15.2015 | 18.2783 | 22.154 | 25.1335 | 28.1081
| HuntsvilleIce Accretion2075RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2075 | 15.2512 | 18.3559 | 22.275 | 25.2764 | 28.2813
| HuntsvilleIce Accretion2080RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2080 | 15.301 | 18.4335 | 22.396 | 25.4193 | 28.4546
| HuntsvilleIce Accretion2085RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2085 | 15.3507 | 18.5111 | 22.517 | 25.5623 | 28.6278
| HuntsvilleIce Accretion2090RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2090 | 15.4362 | 18.6739 | 22.7847 | 25.8958 | 29.0321
| HuntsvilleIce Accretion2095RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2095 | 15.4719 | 18.7591 | 22.9313 | 26.0864 | 29.2631
| HuntsvilleIce Accretion2100RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2100 | 15.5076 | 18.8443 | 23.078 | 26.277 | 29.4941
| HuntsvilleIce Accretion2023RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2023 | 15.2627 | 18.2235 | 21.978 | 24.8351 | 27.6923
| HuntsvilleIce Accretion2025RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2025 | 15.2576 | 18.2296 | 22 | 24.8683 | 27.7385
| HuntsvilleIce Accretion2030RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2030 | 15.2525 | 18.2357 | 22.022 | 24.9014 | 27.7847
| HuntsvilleIce Accretion2035RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2035 | 15.2474 | 18.2417 | 22.044 | 24.9346 | 27.8309
| HuntsvilleIce Accretion2040RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2040 | 15.2321 | 18.2539 | 22.0807 | 25.0009 | 27.9233
| HuntsvilleIce Accretion2045RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2045 | 15.2168 | 18.2661 | 22.1173 | 25.0672 | 28.0157
| HuntsvilleIce Accretion2050RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2050 | 15.2678 | 18.3817 | 22.3153 | 25.3241 | 28.3391
| HuntsvilleIce Accretion2055RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2055 | 15.3341 | 18.4852 | 22.4767 | 25.5146 | 28.5701
| HuntsvilleIce Accretion2060RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2060 | 15.4362 | 18.6739 | 22.7847 | 25.8958 | 29.0321
| HuntsvilleIce Accretion2065RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2065 | 15.4719 | 18.7591 | 22.9313 | 26.0864 | 29.2631
| HuntsvilleIce Accretion2070RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2070 | 15.2984 | 18.613 | 22.814 | 26.0036 | 29.1984
| HuntsvilleIce Accretion2075RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2075 | 15.0892 | 18.3817 | 22.55 | 25.7301 | 28.9027
| HuntsvilleIce Accretion2080RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2080 | 14.88 | 18.1504 | 22.286 | 25.4566 | 28.607
| HuntsvilleIce Accretion2085RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2085 | 14.3518 | 17.557 | 21.604 | 24.6984 | 27.7754
| HuntsvilleIce Accretion2090RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2090 | 13.8237 | 16.9635 | 20.922 | 23.9402 | 26.9438
| HuntsvilleIce Accretion2095RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2095 | 13.8237 | 16.9635 | 20.922 | 23.9402 | 26.9438
| HuntsvilleIce Accretion2100RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2100 | 13.8237 | 16.9635 | 20.922 | 23.9402 | 26.9438
| HuntsvilleWind2023RCP4.5 | Huntsville | Wind | RCP4.5 | 2023 | 69.1684 | 74.4595 | 80.024 | 85.5914 | 91.1635
| HuntsvilleWind2025RCP4.5 | Huntsville | Wind | RCP4.5 | 2025 | 69.2778 | 74.5996 | 80.2 | 85.7983 | 91.4006
| HuntsvilleWind2030RCP4.5 | Huntsville | Wind | RCP4.5 | 2030 | 69.3871 | 74.7398 | 80.376 | 86.0052 | 91.6378
| HuntsvilleWind2035RCP4.5 | Huntsville | Wind | RCP4.5 | 2035 | 69.4965 | 74.8799 | 80.552 | 86.212 | 91.8749
| HuntsvilleWind2040RCP4.5 | Huntsville | Wind | RCP4.5 | 2040 | 69.6059 | 75.02 | 80.728 | 86.4189 | 92.112
| HuntsvilleWind2045RCP4.5 | Huntsville | Wind | RCP4.5 | 2045 | 69.7153 | 75.1601 | 80.904 | 86.6258 | 92.3491
| HuntsvilleWind2050RCP4.5 | Huntsville | Wind | RCP4.5 | 2050 | 69.8274 | 75.2839 | 81.04 | 86.7727 | 92.5078
| HuntsvilleWind2055RCP4.5 | Huntsville | Wind | RCP4.5 | 2055 | 69.8302 | 75.2675 | 81 | 86.7128 | 92.4294
| HuntsvilleWind2060RCP4.5 | Huntsville | Wind | RCP4.5 | 2060 | 69.8329 | 75.2511 | 80.96 | 86.6529 | 92.3509
| HuntsvilleWind2065RCP4.5 | Huntsville | Wind | RCP4.5 | 2065 | 69.8357 | 75.2348 | 80.92 | 86.593 | 92.2725
| HuntsvilleWind2070RCP4.5 | Huntsville | Wind | RCP4.5 | 2070 | 69.8385 | 75.2184 | 80.88 | 86.533 | 92.1941
| HuntsvilleWind2075RCP4.5 | Huntsville | Wind | RCP4.5 | 2075 | 69.8626 | 75.2444 | 80.908 | 86.5644 | 92.2275
| HuntsvilleWind2080RCP4.5 | Huntsville | Wind | RCP4.5 | 2080 | 69.8868 | 75.2705 | 80.936 | 86.5958 | 92.261
| HuntsvilleWind2085RCP4.5 | Huntsville | Wind | RCP4.5 | 2085 | 69.911 | 75.2965 | 80.964 | 86.6272 | 92.2944
| HuntsvilleWind2090RCP4.5 | Huntsville | Wind | RCP4.5 | 2090 | 69.9352 | 75.3226 | 80.992 | 86.6586 | 92.3278
| HuntsvilleWind2095RCP4.5 | Huntsville | Wind | RCP4.5 | 2095 | 69.9593 | 75.3486 | 81.02 | 86.69 | 92.3613
| HuntsvilleWind2100RCP4.5 | Huntsville | Wind | RCP4.5 | 2100 | 69.9835 | 75.3746 | 81.048 | 86.7214 | 92.3947
| HuntsvilleWind2023RCP6.0 | Huntsville | Wind | RCP6.0 | 2023 | 69.1684 | 74.4595 | 80.024 | 85.5914 | 91.1635
| HuntsvilleWind2025RCP6.0 | Huntsville | Wind | RCP6.0 | 2025 | 69.2778 | 74.5996 | 80.2 | 85.7983 | 91.4006
| HuntsvilleWind2030RCP6.0 | Huntsville | Wind | RCP6.0 | 2030 | 69.3871 | 74.7398 | 80.376 | 86.0052 | 91.6378
| HuntsvilleWind2035RCP6.0 | Huntsville | Wind | RCP6.0 | 2035 | 69.4965 | 74.8799 | 80.552 | 86.212 | 91.8749
| HuntsvilleWind2040RCP6.0 | Huntsville | Wind | RCP6.0 | 2040 | 69.6059 | 75.02 | 80.728 | 86.4189 | 92.112
| HuntsvilleWind2045RCP6.0 | Huntsville | Wind | RCP6.0 | 2045 | 69.7153 | 75.1601 | 80.904 | 86.6258 | 92.3491
| HuntsvilleWind2050RCP6.0 | Huntsville | Wind | RCP6.0 | 2050 | 69.8274 | 75.2839 | 81.04 | 86.7727 | 92.5078
| HuntsvilleWind2055RCP6.0 | Huntsville | Wind | RCP6.0 | 2055 | 69.8302 | 75.2675 | 81 | 86.7128 | 92.4294
| HuntsvilleWind2060RCP6.0 | Huntsville | Wind | RCP6.0 | 2060 | 69.8329 | 75.2511 | 80.96 | 86.6529 | 92.3509
| HuntsvilleWind2065RCP6.0 | Huntsville | Wind | RCP6.0 | 2065 | 69.8357 | 75.2348 | 80.92 | 86.593 | 92.2725
| HuntsvilleWind2070RCP6.0 | Huntsville | Wind | RCP6.0 | 2070 | 69.8385 | 75.2184 | 80.88 | 86.533 | 92.1941
| HuntsvilleWind2075RCP6.0 | Huntsville | Wind | RCP6.0 | 2075 | 69.8747 | 75.2575 | 80.922 | 86.5801 | 92.2442
| HuntsvilleWind2080RCP6.0 | Huntsville | Wind | RCP6.0 | 2080 | 69.911 | 75.2965 | 80.964 | 86.6272 | 92.2944
| HuntsvilleWind2085RCP6.0 | Huntsville | Wind | RCP6.0 | 2085 | 69.9473 | 75.3356 | 81.006 | 86.6743 | 92.3446
| HuntsvilleWind2090RCP6.0 | Huntsville | Wind | RCP6.0 | 2090 | 69.9121 | 75.273 | 80.9093 | 86.553 | 92.1971
| HuntsvilleWind2095RCP6.0 | Huntsville | Wind | RCP6.0 | 2095 | 69.8408 | 75.1713 | 80.7707 | 86.3847 | 91.9995
| HuntsvilleWind2100RCP6.0 | Huntsville | Wind | RCP6.0 | 2100 | 69.7694 | 75.0696 | 80.632 | 86.2163 | 91.8019
| HuntsvilleWind2023RCP8.5 | Huntsville | Wind | RCP8.5 | 2023 | 69.1684 | 74.4595 | 80.024 | 85.5914 | 91.1635
| HuntsvilleWind2025RCP8.5 | Huntsville | Wind | RCP8.5 | 2025 | 69.3871 | 74.7398 | 80.376 | 86.0052 | 91.6378
| HuntsvilleWind2030RCP8.5 | Huntsville | Wind | RCP8.5 | 2030 | 69.6059 | 75.02 | 80.728 | 86.4189 | 92.112
| HuntsvilleWind2035RCP8.5 | Huntsville | Wind | RCP8.5 | 2035 | 69.8246 | 75.3002 | 81.08 | 86.8326 | 92.5862
| HuntsvilleWind2040RCP8.5 | Huntsville | Wind | RCP8.5 | 2040 | 69.8292 | 75.273 | 81.0133 | 86.7328 | 92.4555
| HuntsvilleWind2045RCP8.5 | Huntsville | Wind | RCP8.5 | 2045 | 69.8339 | 75.2457 | 80.9467 | 86.6329 | 92.3248
| HuntsvilleWind2050RCP8.5 | Huntsville | Wind | RCP8.5 | 2050 | 69.8868 | 75.2705 | 80.936 | 86.5958 | 92.261
| HuntsvilleWind2055RCP8.5 | Huntsville | Wind | RCP8.5 | 2055 | 69.9352 | 75.3226 | 80.992 | 86.6586 | 92.3278
| HuntsvilleWind2060RCP8.5 | Huntsville | Wind | RCP8.5 | 2060 | 69.9121 | 75.273 | 80.9093 | 86.553 | 92.1971
| HuntsvilleWind2065RCP8.5 | Huntsville | Wind | RCP8.5 | 2065 | 69.8408 | 75.1713 | 80.7707 | 86.3847 | 91.9995
| HuntsvilleWind2070RCP8.5 | Huntsville | Wind | RCP8.5 | 2070 | 69.8615 | 75.1787 | 80.7627 | 86.3618 | 91.9661
| HuntsvilleWind2075RCP8.5 | Huntsville | Wind | RCP8.5 | 2075 | 69.9536 | 75.2878 | 80.8933 | 86.5074 | 92.1302
| HuntsvilleWind2080RCP8.5 | Huntsville | Wind | RCP8.5 | 2080 | 70.0457 | 75.397 | 81.024 | 86.6529 | 92.2944
| HuntsvilleWind2085RCP8.5 | Huntsville | Wind | RCP8.5 | 2085 | 70.3393 | 75.7615 | 81.468 | 87.1708 | 92.8826
| HuntsvilleWind2090RCP8.5 | Huntsville | Wind | RCP8.5 | 2090 | 70.6329 | 76.1261 | 81.912 | 87.6886 | 93.4709
| HuntsvilleWind2095RCP8.5 | Huntsville | Wind | RCP8.5 | 2095 | 70.6329 | 76.1261 | 81.912 | 87.6886 | 93.4709
| HuntsvilleWind2100RCP8.5 | Huntsville | Wind | RCP8.5 | 2100 | 70.6329 | 76.1261 | 81.912 | 87.6886 | 93.4709
| IngersollIce Accretion2023RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2023 | 21.1182 | 25.3183 | 30.628 | 34.6797 | 38.7475
| IngersollIce Accretion2025RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2025 | 21.0751 | 25.2797 | 30.5918 | 34.6505 | 38.715
| IngersollIce Accretion2030RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2030 | 21.0319 | 25.2411 | 30.5557 | 34.6213 | 38.6824
| IngersollIce Accretion2035RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2035 | 20.9888 | 25.2025 | 30.5195 | 34.5921 | 38.6499
| IngersollIce Accretion2040RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2040 | 20.9457 | 25.1639 | 30.4833 | 34.5629 | 38.6173
| IngersollIce Accretion2045RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2045 | 20.9025 | 25.1253 | 30.4472 | 34.5337 | 38.5848
| IngersollIce Accretion2050RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2050 | 20.7256 | 24.9581 | 30.2932 | 34.3854 | 38.4429
| IngersollIce Accretion2055RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2055 | 20.5919 | 24.8294 | 30.1754 | 34.2663 | 38.3335
| IngersollIce Accretion2060RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2060 | 20.4582 | 24.7008 | 30.0576 | 34.1472 | 38.2241
| IngersollIce Accretion2065RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2065 | 20.3244 | 24.5722 | 29.9398 | 34.0281 | 38.1147
| IngersollIce Accretion2070RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2070 | 20.1907 | 24.4435 | 29.822 | 33.909 | 38.0054
| IngersollIce Accretion2075RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2075 | 20.1331 | 24.4006 | 29.8013 | 33.9032 | 38.0119
| IngersollIce Accretion2080RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2080 | 20.0756 | 24.3577 | 29.7807 | 33.8974 | 38.0184
| IngersollIce Accretion2085RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2085 | 20.0181 | 24.3148 | 29.76 | 33.8915 | 38.0249
| IngersollIce Accretion2090RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2090 | 19.9606 | 24.272 | 29.7393 | 33.8857 | 38.0314
| IngersollIce Accretion2095RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2095 | 19.9031 | 24.2291 | 29.7187 | 33.8798 | 38.0379
| IngersollIce Accretion2100RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2100 | 19.8455 | 24.1862 | 29.698 | 33.874 | 38.0444
| IngersollIce Accretion2023RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2023 | 21.1182 | 25.3183 | 30.628 | 34.6797 | 38.7475
| IngersollIce Accretion2025RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2025 | 21.0751 | 25.2797 | 30.5918 | 34.6505 | 38.715
| IngersollIce Accretion2030RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2030 | 21.0319 | 25.2411 | 30.5557 | 34.6213 | 38.6824
| IngersollIce Accretion2035RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2035 | 20.9888 | 25.2025 | 30.5195 | 34.5921 | 38.6499
| IngersollIce Accretion2040RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2040 | 20.9457 | 25.1639 | 30.4833 | 34.5629 | 38.6173
| IngersollIce Accretion2045RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2045 | 20.9025 | 25.1253 | 30.4472 | 34.5337 | 38.5848
| IngersollIce Accretion2050RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2050 | 20.7256 | 24.9581 | 30.2932 | 34.3854 | 38.4429
| IngersollIce Accretion2055RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2055 | 20.5919 | 24.8294 | 30.1754 | 34.2663 | 38.3335
| IngersollIce Accretion2060RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2060 | 20.4582 | 24.7008 | 30.0576 | 34.1472 | 38.2241
| IngersollIce Accretion2065RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2065 | 20.3244 | 24.5722 | 29.9398 | 34.0281 | 38.1147
| IngersollIce Accretion2070RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2070 | 20.1907 | 24.4435 | 29.822 | 33.909 | 38.0054
| IngersollIce Accretion2075RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2075 | 20.1044 | 24.3792 | 29.791 | 33.9003 | 38.0151
| IngersollIce Accretion2080RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2080 | 20.0181 | 24.3148 | 29.76 | 33.8915 | 38.0249
| IngersollIce Accretion2085RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2085 | 19.9318 | 24.2505 | 29.729 | 33.8828 | 38.0347
| IngersollIce Accretion2090RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2090 | 19.3997 | 23.7059 | 29.1503 | 33.2902 | 37.4065
| IngersollIce Accretion2095RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2095 | 18.9539 | 23.2256 | 28.6027 | 32.7063 | 36.7685
| IngersollIce Accretion2100RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2100 | 18.5081 | 22.7453 | 28.055 | 32.1225 | 36.1305
| IngersollIce Accretion2023RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2023 | 21.1182 | 25.3183 | 30.628 | 34.6797 | 38.7475
| IngersollIce Accretion2025RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2025 | 21.0319 | 25.2411 | 30.5557 | 34.6213 | 38.6824
| IngersollIce Accretion2030RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2030 | 20.9457 | 25.1639 | 30.4833 | 34.5629 | 38.6173
| IngersollIce Accretion2035RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2035 | 20.8594 | 25.0867 | 30.411 | 34.5045 | 38.5522
| IngersollIce Accretion2040RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2040 | 20.6365 | 24.8723 | 30.2147 | 34.306 | 38.3699
| IngersollIce Accretion2045RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2045 | 20.4136 | 24.6579 | 30.0183 | 34.1075 | 38.1877
| IngersollIce Accretion2050RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2050 | 20.0756 | 24.3577 | 29.7807 | 33.8974 | 38.0184
| IngersollIce Accretion2055RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2055 | 19.9606 | 24.272 | 29.7393 | 33.8857 | 38.0314
| IngersollIce Accretion2060RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2060 | 19.3997 | 23.7059 | 29.1503 | 33.2902 | 37.4065
| IngersollIce Accretion2065RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2065 | 18.9539 | 23.2256 | 28.6027 | 32.7063 | 36.7685
| IngersollIce Accretion2070RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2070 | 18.1198 | 22.3251 | 27.6003 | 31.6321 | 35.6097
| IngersollIce Accretion2075RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2075 | 17.7316 | 21.9048 | 27.1457 | 31.1417 | 35.0889
| IngersollIce Accretion2080RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2080 | 17.3433 | 21.4845 | 26.691 | 30.6512 | 34.5681
| IngersollIce Accretion2085RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2085 | 16.3833 | 20.3782 | 25.389 | 29.18 | 32.9666
| IngersollIce Accretion2090RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2090 | 15.4234 | 19.2718 | 24.087 | 27.7087 | 31.3652
| IngersollIce Accretion2095RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2095 | 15.4234 | 19.2718 | 24.087 | 27.7087 | 31.3652
| IngersollIce Accretion2100RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2100 | 15.4234 | 19.2718 | 24.087 | 27.7087 | 31.3652
| IngersollWind2023RCP4.5 | Ingersoll | Wind | RCP4.5 | 2023 | 88.8679 | 95.875 | 103.2954 | 110.6789 | 118.0707
| IngersollWind2025RCP4.5 | Ingersoll | Wind | RCP4.5 | 2025 | 88.9501 | 95.9841 | 103.4365 | 110.848 | 118.2684
| IngersollWind2030RCP4.5 | Ingersoll | Wind | RCP4.5 | 2030 | 89.0323 | 96.0932 | 103.5776 | 111.0172 | 118.4661
| IngersollWind2035RCP4.5 | Ingersoll | Wind | RCP4.5 | 2035 | 89.1145 | 96.2023 | 103.7187 | 111.1864 | 118.6637
| IngersollWind2040RCP4.5 | Ingersoll | Wind | RCP4.5 | 2040 | 89.1967 | 96.3114 | 103.8598 | 111.3555 | 118.8614
| IngersollWind2045RCP4.5 | Ingersoll | Wind | RCP4.5 | 2045 | 89.2789 | 96.4204 | 104.0009 | 111.5247 | 119.0591
| IngersollWind2050RCP4.5 | Ingersoll | Wind | RCP4.5 | 2050 | 89.4316 | 96.6149 | 104.2501 | 111.8183 | 119.3986
| IngersollWind2055RCP4.5 | Ingersoll | Wind | RCP4.5 | 2055 | 89.502 | 96.7003 | 104.3582 | 111.9427 | 119.5405
| IngersollWind2060RCP4.5 | Ingersoll | Wind | RCP4.5 | 2060 | 89.5725 | 96.7857 | 104.4664 | 112.0671 | 119.6824
| IngersollWind2065RCP4.5 | Ingersoll | Wind | RCP4.5 | 2065 | 89.6429 | 96.871 | 104.5745 | 112.1916 | 119.8242
| IngersollWind2070RCP4.5 | Ingersoll | Wind | RCP4.5 | 2070 | 89.7134 | 96.9564 | 104.6826 | 112.316 | 119.9661
| IngersollWind2075RCP4.5 | Ingersoll | Wind | RCP4.5 | 2075 | 89.8015 | 97.0781 | 104.8475 | 112.5179 | 120.2064
| IngersollWind2080RCP4.5 | Ingersoll | Wind | RCP4.5 | 2080 | 89.8896 | 97.1999 | 105.0124 | 112.7198 | 120.4467
| IngersollWind2085RCP4.5 | Ingersoll | Wind | RCP4.5 | 2085 | 89.9776 | 97.3216 | 105.1773 | 112.9217 | 120.687
| IngersollWind2090RCP4.5 | Ingersoll | Wind | RCP4.5 | 2090 | 90.0657 | 97.4434 | 105.3422 | 113.1236 | 120.9273
| IngersollWind2095RCP4.5 | Ingersoll | Wind | RCP4.5 | 2095 | 90.1538 | 97.5651 | 105.5071 | 113.3255 | 121.1676
| IngersollWind2100RCP4.5 | Ingersoll | Wind | RCP4.5 | 2100 | 90.2419 | 97.6868 | 105.672 | 113.5274 | 121.4079
| IngersollWind2023RCP6.0 | Ingersoll | Wind | RCP6.0 | 2023 | 88.8679 | 95.875 | 103.2954 | 110.6789 | 118.0707
| IngersollWind2025RCP6.0 | Ingersoll | Wind | RCP6.0 | 2025 | 88.9501 | 95.9841 | 103.4365 | 110.848 | 118.2684
| IngersollWind2030RCP6.0 | Ingersoll | Wind | RCP6.0 | 2030 | 89.0323 | 96.0932 | 103.5776 | 111.0172 | 118.4661
| IngersollWind2035RCP6.0 | Ingersoll | Wind | RCP6.0 | 2035 | 89.1145 | 96.2023 | 103.7187 | 111.1864 | 118.6637
| IngersollWind2040RCP6.0 | Ingersoll | Wind | RCP6.0 | 2040 | 89.1967 | 96.3114 | 103.8598 | 111.3555 | 118.8614
| IngersollWind2045RCP6.0 | Ingersoll | Wind | RCP6.0 | 2045 | 89.2789 | 96.4204 | 104.0009 | 111.5247 | 119.0591
| IngersollWind2050RCP6.0 | Ingersoll | Wind | RCP6.0 | 2050 | 89.4316 | 96.6149 | 104.2501 | 111.8183 | 119.3986
| IngersollWind2055RCP6.0 | Ingersoll | Wind | RCP6.0 | 2055 | 89.502 | 96.7003 | 104.3582 | 111.9427 | 119.5405
| IngersollWind2060RCP6.0 | Ingersoll | Wind | RCP6.0 | 2060 | 89.5725 | 96.7857 | 104.4664 | 112.0671 | 119.6824
| IngersollWind2065RCP6.0 | Ingersoll | Wind | RCP6.0 | 2065 | 89.6429 | 96.871 | 104.5745 | 112.1916 | 119.8242
| IngersollWind2070RCP6.0 | Ingersoll | Wind | RCP6.0 | 2070 | 89.7134 | 96.9564 | 104.6826 | 112.316 | 119.9661
| IngersollWind2075RCP6.0 | Ingersoll | Wind | RCP6.0 | 2075 | 89.8455 | 97.139 | 104.9299 | 112.6188 | 120.3265
| IngersollWind2080RCP6.0 | Ingersoll | Wind | RCP6.0 | 2080 | 89.9776 | 97.3216 | 105.1773 | 112.9217 | 120.687
| IngersollWind2085RCP6.0 | Ingersoll | Wind | RCP6.0 | 2085 | 90.1097 | 97.5042 | 105.4246 | 113.2246 | 121.0475
| IngersollWind2090RCP6.0 | Ingersoll | Wind | RCP6.0 | 2090 | 90.603 | 98.1516 | 106.2636 | 114.2259 | 122.218
| IngersollWind2095RCP6.0 | Ingersoll | Wind | RCP6.0 | 2095 | 90.9641 | 98.6165 | 106.8552 | 114.9244 | 123.0281
| IngersollWind2100RCP6.0 | Ingersoll | Wind | RCP6.0 | 2100 | 91.3252 | 99.0813 | 107.4468 | 115.6229 | 123.8382
| IngersollWind2023RCP8.5 | Ingersoll | Wind | RCP8.5 | 2023 | 88.8679 | 95.875 | 103.2954 | 110.6789 | 118.0707
| IngersollWind2025RCP8.5 | Ingersoll | Wind | RCP8.5 | 2025 | 89.0323 | 96.0932 | 103.5776 | 111.0172 | 118.4661
| IngersollWind2030RCP8.5 | Ingersoll | Wind | RCP8.5 | 2030 | 89.1967 | 96.3114 | 103.8598 | 111.3555 | 118.8614
| IngersollWind2035RCP8.5 | Ingersoll | Wind | RCP8.5 | 2035 | 89.3611 | 96.5295 | 104.142 | 111.6939 | 119.2568
| IngersollWind2040RCP8.5 | Ingersoll | Wind | RCP8.5 | 2040 | 89.4785 | 96.6718 | 104.3222 | 111.9012 | 119.4932
| IngersollWind2045RCP8.5 | Ingersoll | Wind | RCP8.5 | 2045 | 89.596 | 96.8141 | 104.5024 | 112.1086 | 119.7296
| IngersollWind2050RCP8.5 | Ingersoll | Wind | RCP8.5 | 2050 | 89.8896 | 97.1999 | 105.0124 | 112.7198 | 120.4467
| IngersollWind2055RCP8.5 | Ingersoll | Wind | RCP8.5 | 2055 | 90.0657 | 97.4434 | 105.3422 | 113.1236 | 120.9273
| IngersollWind2060RCP8.5 | Ingersoll | Wind | RCP8.5 | 2060 | 90.603 | 98.1516 | 106.2636 | 114.2259 | 122.218
| IngersollWind2065RCP8.5 | Ingersoll | Wind | RCP8.5 | 2065 | 90.9641 | 98.6165 | 106.8552 | 114.9244 | 123.0281
| IngersollWind2070RCP8.5 | Ingersoll | Wind | RCP8.5 | 2070 | 91.5542 | 99.388 | 107.8514 | 116.1104 | 124.4118
| IngersollWind2075RCP8.5 | Ingersoll | Wind | RCP8.5 | 2075 | 91.7832 | 99.6947 | 108.256 | 116.5979 | 124.9855
| IngersollWind2080RCP8.5 | Ingersoll | Wind | RCP8.5 | 2080 | 92.0122 | 100.0014 | 108.6606 | 117.0854 | 125.5591
| IngersollWind2085RCP8.5 | Ingersoll | Wind | RCP8.5 | 2085 | 92.4614 | 100.5895 | 109.4307 | 118.0076 | 126.6347
| IngersollWind2090RCP8.5 | Ingersoll | Wind | RCP8.5 | 2090 | 92.9105 | 101.1777 | 110.2008 | 118.9299 | 127.7103
| IngersollWind2095RCP8.5 | Ingersoll | Wind | RCP8.5 | 2095 | 92.9105 | 101.1777 | 110.2008 | 118.9299 | 127.7103
| IngersollWind2100RCP8.5 | Ingersoll | Wind | RCP8.5 | 2100 | 92.9105 | 101.1777 | 110.2008 | 118.9299 | 127.7103
| Iroquois FallsIce Accretion2023RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2023 | 12.4751 | 14.8354 | 17.838 | 20.1366 | 22.4305
| Iroquois FallsIce Accretion2025RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2025 | 12.5231 | 14.8952 | 17.913 | 20.2213 | 22.525
| Iroquois FallsIce Accretion2030RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2030 | 12.5712 | 14.9549 | 17.988 | 20.3061 | 22.6195
| Iroquois FallsIce Accretion2035RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2035 | 12.6192 | 15.0147 | 18.063 | 20.3908 | 22.714
| Iroquois FallsIce Accretion2040RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2040 | 12.6672 | 15.0745 | 18.138 | 20.4756 | 22.8085
| Iroquois FallsIce Accretion2045RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2045 | 12.7152 | 15.1342 | 18.213 | 20.5603 | 22.903
| Iroquois FallsIce Accretion2050RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2050 | 12.8384 | 15.2926 | 18.414 | 20.7956 | 23.1699
| Iroquois FallsIce Accretion2055RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2055 | 12.9135 | 15.3912 | 18.54 | 20.9461 | 23.3423
| Iroquois FallsIce Accretion2060RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2060 | 12.9887 | 15.4898 | 18.666 | 21.0966 | 23.5146
| Iroquois FallsIce Accretion2065RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2065 | 13.0638 | 15.5884 | 18.792 | 21.2472 | 23.687
| Iroquois FallsIce Accretion2070RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2070 | 13.139 | 15.687 | 18.918 | 21.3977 | 23.8594
| Iroquois FallsIce Accretion2075RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2075 | 13.1223 | 15.6721 | 18.903 | 21.3841 | 23.8442
| Iroquois FallsIce Accretion2080RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2080 | 13.1056 | 15.6571 | 18.888 | 21.3706 | 23.8291
| Iroquois FallsIce Accretion2085RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2085 | 13.0889 | 15.6422 | 18.873 | 21.357 | 23.814
| Iroquois FallsIce Accretion2090RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2090 | 13.0722 | 15.6272 | 18.858 | 21.3434 | 23.7989
| Iroquois FallsIce Accretion2095RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2095 | 13.0555 | 15.6123 | 18.843 | 21.3299 | 23.7838
| Iroquois FallsIce Accretion2100RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2100 | 13.0388 | 15.5974 | 18.828 | 21.3163 | 23.7686
| Iroquois FallsIce Accretion2023RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2023 | 12.4751 | 14.8354 | 17.838 | 20.1366 | 22.4305
| Iroquois FallsIce Accretion2025RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2025 | 12.5231 | 14.8952 | 17.913 | 20.2213 | 22.525
| Iroquois FallsIce Accretion2030RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2030 | 12.5712 | 14.9549 | 17.988 | 20.3061 | 22.6195
| Iroquois FallsIce Accretion2035RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2035 | 12.6192 | 15.0147 | 18.063 | 20.3908 | 22.714
| Iroquois FallsIce Accretion2040RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2040 | 12.6672 | 15.0745 | 18.138 | 20.4756 | 22.8085
| Iroquois FallsIce Accretion2045RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2045 | 12.7152 | 15.1342 | 18.213 | 20.5603 | 22.903
| Iroquois FallsIce Accretion2050RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2050 | 12.8384 | 15.2926 | 18.414 | 20.7956 | 23.1699
| Iroquois FallsIce Accretion2055RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2055 | 12.9135 | 15.3912 | 18.54 | 20.9461 | 23.3423
| Iroquois FallsIce Accretion2060RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2060 | 12.9887 | 15.4898 | 18.666 | 21.0966 | 23.5146
| Iroquois FallsIce Accretion2065RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2065 | 13.0638 | 15.5884 | 18.792 | 21.2472 | 23.687
| Iroquois FallsIce Accretion2070RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2070 | 13.139 | 15.687 | 18.918 | 21.3977 | 23.8594
| Iroquois FallsIce Accretion2075RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2075 | 13.1139 | 15.6646 | 18.8955 | 21.3773 | 23.8367
| Iroquois FallsIce Accretion2080RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2080 | 13.0889 | 15.6422 | 18.873 | 21.357 | 23.814
| Iroquois FallsIce Accretion2085RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2085 | 13.0638 | 15.6198 | 18.8505 | 21.3367 | 23.7913
| Iroquois FallsIce Accretion2090RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2090 | 12.926 | 15.4729 | 18.696 | 21.1672 | 23.6174
| Iroquois FallsIce Accretion2095RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2095 | 12.8133 | 15.3484 | 18.564 | 21.018 | 23.4662
| Iroquois FallsIce Accretion2100RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2100 | 12.7006 | 15.2239 | 18.432 | 20.8688 | 23.315
| Iroquois FallsIce Accretion2023RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2023 | 12.4751 | 14.8354 | 17.838 | 20.1366 | 22.4305
| Iroquois FallsIce Accretion2025RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2025 | 12.5712 | 14.9549 | 17.988 | 20.3061 | 22.6195
| Iroquois FallsIce Accretion2030RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2030 | 12.6672 | 15.0745 | 18.138 | 20.4756 | 22.8085
| Iroquois FallsIce Accretion2035RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2035 | 12.7632 | 15.194 | 18.288 | 20.6451 | 22.9975
| Iroquois FallsIce Accretion2040RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2040 | 12.8885 | 15.3583 | 18.498 | 20.896 | 23.2848
| Iroquois FallsIce Accretion2045RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2045 | 13.0137 | 15.5227 | 18.708 | 21.1468 | 23.5721
| Iroquois FallsIce Accretion2050RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2050 | 13.1056 | 15.6571 | 18.888 | 21.3706 | 23.8291
| Iroquois FallsIce Accretion2055RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2055 | 13.0722 | 15.6272 | 18.858 | 21.3434 | 23.7989
| Iroquois FallsIce Accretion2060RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2060 | 12.926 | 15.4729 | 18.696 | 21.1672 | 23.6174
| Iroquois FallsIce Accretion2065RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2065 | 12.8133 | 15.3484 | 18.564 | 21.018 | 23.4662
| Iroquois FallsIce Accretion2070RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2070 | 12.6254 | 15.1492 | 18.354 | 20.7943 | 23.2319
| Iroquois FallsIce Accretion2075RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2075 | 12.5503 | 15.0745 | 18.276 | 20.7197 | 23.1487
| Iroquois FallsIce Accretion2080RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2080 | 12.4751 | 14.9998 | 18.198 | 20.6451 | 23.0656
| Iroquois FallsIce Accretion2085RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2085 | 12.3374 | 14.8728 | 18.072 | 20.5231 | 22.9522
| Iroquois FallsIce Accretion2090RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2090 | 12.1996 | 14.7458 | 17.946 | 20.401 | 22.8388
| Iroquois FallsIce Accretion2095RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2095 | 12.1996 | 14.7458 | 17.946 | 20.401 | 22.8388
| Iroquois FallsIce Accretion2100RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2100 | 12.1996 | 14.7458 | 17.946 | 20.401 | 22.8388
| Iroquois FallsWind2023RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2023 | 75.0392 | 80.8598 | 86.9976 | 93.1242 | 99.2557
| Iroquois FallsWind2025RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2025 | 75.0305 | 80.8331 | 86.946 | 93.0537 | 99.1642
| Iroquois FallsWind2030RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2030 | 75.0219 | 80.8065 | 86.8944 | 92.9831 | 99.0727
| Iroquois FallsWind2035RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2035 | 75.0132 | 80.7798 | 86.8428 | 92.9126 | 98.9812
| Iroquois FallsWind2040RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2040 | 75.0046 | 80.7531 | 86.7912 | 92.842 | 98.8897
| Iroquois FallsWind2045RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2045 | 74.9959 | 80.7265 | 86.7396 | 92.7715 | 98.7982
| Iroquois FallsWind2050RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2050 | 75.0199 | 80.7478 | 86.7534 | 92.7819 | 98.8028
| Iroquois FallsWind2055RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2055 | 75.0526 | 80.7958 | 86.8187 | 92.8629 | 98.8988
| Iroquois FallsWind2060RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2060 | 75.0853 | 80.8438 | 86.8841 | 92.9439 | 98.9949
| Iroquois FallsWind2065RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2065 | 75.1179 | 80.8918 | 86.9494 | 93.0249 | 99.091
| Iroquois FallsWind2070RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2070 | 75.1506 | 80.9398 | 87.0148 | 93.1058 | 99.1871
| Iroquois FallsWind2075RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2075 | 75.1803 | 80.9584 | 87.0234 | 93.1043 | 99.1773
| Iroquois FallsWind2080RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2080 | 75.21 | 80.9771 | 87.032 | 93.1028 | 99.1675
| Iroquois FallsWind2085RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2085 | 75.2397 | 80.9957 | 87.0406 | 93.1012 | 99.1577
| Iroquois FallsWind2090RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2090 | 75.2694 | 81.0144 | 87.0492 | 93.0997 | 99.1479
| Iroquois FallsWind2095RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2095 | 75.2991 | 81.0331 | 87.0578 | 93.0982 | 99.138
| Iroquois FallsWind2100RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2100 | 75.3288 | 81.0517 | 87.0664 | 93.0966 | 99.1282
| Iroquois FallsWind2023RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2023 | 75.0392 | 80.8598 | 86.9976 | 93.1242 | 99.2557
| Iroquois FallsWind2025RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2025 | 75.0305 | 80.8331 | 86.946 | 93.0537 | 99.1642
| Iroquois FallsWind2030RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2030 | 75.0219 | 80.8065 | 86.8944 | 92.9831 | 99.0727
| Iroquois FallsWind2035RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2035 | 75.0132 | 80.7798 | 86.8428 | 92.9126 | 98.9812
| Iroquois FallsWind2040RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2040 | 75.0046 | 80.7531 | 86.7912 | 92.842 | 98.8897
| Iroquois FallsWind2045RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2045 | 74.9959 | 80.7265 | 86.7396 | 92.7715 | 98.7982
| Iroquois FallsWind2050RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2050 | 75.0199 | 80.7478 | 86.7534 | 92.7819 | 98.8028
| Iroquois FallsWind2055RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2055 | 75.0526 | 80.7958 | 86.8187 | 92.8629 | 98.8988
| Iroquois FallsWind2060RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2060 | 75.0853 | 80.8438 | 86.8841 | 92.9439 | 98.9949
| Iroquois FallsWind2065RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2065 | 75.1179 | 80.8918 | 86.9494 | 93.0249 | 99.091
| Iroquois FallsWind2070RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2070 | 75.1506 | 80.9398 | 87.0148 | 93.1058 | 99.1871
| Iroquois FallsWind2075RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2075 | 75.1952 | 80.9678 | 87.0277 | 93.1035 | 99.1724
| Iroquois FallsWind2080RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2080 | 75.2397 | 80.9957 | 87.0406 | 93.1012 | 99.1577
| Iroquois FallsWind2085RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2085 | 75.2843 | 81.0237 | 87.0535 | 93.0989 | 99.143
| Iroquois FallsWind2090RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2090 | 75.5863 | 81.3743 | 87.4649 | 93.5598 | 99.6577
| Iroquois FallsWind2095RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2095 | 75.8437 | 81.6969 | 87.8633 | 94.023 | 100.1871
| Iroquois FallsWind2100RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2100 | 76.1011 | 82.0195 | 88.2618 | 94.4861 | 100.7165
| Iroquois FallsWind2023RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2023 | 75.0392 | 80.8598 | 86.9976 | 93.1242 | 99.2557
| Iroquois FallsWind2025RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2025 | 75.0219 | 80.8065 | 86.8944 | 92.9831 | 99.0727
| Iroquois FallsWind2030RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2030 | 75.0046 | 80.7531 | 86.7912 | 92.842 | 98.8897
| Iroquois FallsWind2035RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2035 | 74.9872 | 80.6998 | 86.688 | 92.7009 | 98.7067
| Iroquois FallsWind2040RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2040 | 75.0417 | 80.7798 | 86.7969 | 92.8359 | 98.8668
| Iroquois FallsWind2045RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2045 | 75.0961 | 80.8598 | 86.9059 | 92.9709 | 99.0269
| Iroquois FallsWind2050RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2050 | 75.21 | 80.9771 | 87.032 | 93.1028 | 99.1675
| Iroquois FallsWind2055RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2055 | 75.2694 | 81.0144 | 87.0492 | 93.0997 | 99.1479
| Iroquois FallsWind2060RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2060 | 75.5863 | 81.3743 | 87.4649 | 93.5598 | 99.6577
| Iroquois FallsWind2065RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2065 | 75.8437 | 81.6969 | 87.8633 | 94.023 | 100.1871
| Iroquois FallsWind2070RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2070 | 76.2868 | 82.2114 | 88.4625 | 94.6947 | 100.9354
| Iroquois FallsWind2075RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2075 | 76.4724 | 82.4034 | 88.6631 | 94.9033 | 101.1544
| Iroquois FallsWind2080RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2080 | 76.6581 | 82.5953 | 88.8638 | 95.1119 | 101.3734
| Iroquois FallsWind2085RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2085 | 76.7917 | 82.7873 | 89.1175 | 95.4247 | 101.741
| Iroquois FallsWind2090RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2090 | 76.9254 | 82.9793 | 89.3712 | 95.7376 | 102.1087
| Iroquois FallsWind2095RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2095 | 76.9254 | 82.9793 | 89.3712 | 95.7376 | 102.1087
| Iroquois FallsWind2100RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2100 | 76.9254 | 82.9793 | 89.3712 | 95.7376 | 102.1087
| JellicoeIce Accretion2023RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2023 | 9.9269 | 11.8175 | 14.224 | 16.0573 | 17.887
| JellicoeIce Accretion2025RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2025 | 10.0049 | 11.9105 | 14.3337 | 16.1839 | 18.0281
| JellicoeIce Accretion2030RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2030 | 10.0828 | 12.0035 | 14.4433 | 16.3104 | 18.1692
| JellicoeIce Accretion2035RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2035 | 10.1607 | 12.0964 | 14.553 | 16.437 | 18.3103
| JellicoeIce Accretion2040RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2040 | 10.2387 | 12.1894 | 14.6627 | 16.5635 | 18.4514
| JellicoeIce Accretion2045RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2045 | 10.3166 | 12.2823 | 14.7723 | 16.6901 | 18.5926
| JellicoeIce Accretion2050RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2050 | 10.4355 | 12.4195 | 14.9352 | 16.8736 | 18.7972
| JellicoeIce Accretion2055RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2055 | 10.4764 | 12.4636 | 14.9884 | 16.9306 | 18.8607
| JellicoeIce Accretion2060RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2060 | 10.5173 | 12.5078 | 15.0416 | 16.9875 | 18.9242
| JellicoeIce Accretion2065RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2065 | 10.5582 | 12.5519 | 15.0948 | 17.0445 | 18.9877
| JellicoeIce Accretion2070RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2070 | 10.5991 | 12.5961 | 15.148 | 17.1014 | 19.0512
| JellicoeIce Accretion2075RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2075 | 10.6219 | 12.6251 | 15.1807 | 17.1383 | 19.0924
| JellicoeIce Accretion2080RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2080 | 10.6446 | 12.6542 | 15.2133 | 17.1752 | 19.1335
| JellicoeIce Accretion2085RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2085 | 10.6673 | 12.6832 | 15.246 | 17.2122 | 19.1747
| JellicoeIce Accretion2090RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2090 | 10.6901 | 12.7123 | 15.2787 | 17.2491 | 19.2158
| JellicoeIce Accretion2095RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2095 | 10.7128 | 12.7413 | 15.3113 | 17.286 | 19.257
| JellicoeIce Accretion2100RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2100 | 10.7355 | 12.7704 | 15.344 | 17.3229 | 19.2982
| JellicoeIce Accretion2023RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2023 | 9.9269 | 11.8175 | 14.224 | 16.0573 | 17.887
| JellicoeIce Accretion2025RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2025 | 10.0049 | 11.9105 | 14.3337 | 16.1839 | 18.0281
| JellicoeIce Accretion2030RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2030 | 10.0828 | 12.0035 | 14.4433 | 16.3104 | 18.1692
| JellicoeIce Accretion2035RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2035 | 10.1607 | 12.0964 | 14.553 | 16.437 | 18.3103
| JellicoeIce Accretion2040RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2040 | 10.2387 | 12.1894 | 14.6627 | 16.5635 | 18.4514
| JellicoeIce Accretion2045RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2045 | 10.3166 | 12.2823 | 14.7723 | 16.6901 | 18.5926
| JellicoeIce Accretion2050RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2050 | 10.4355 | 12.4195 | 14.9352 | 16.8736 | 18.7972
| JellicoeIce Accretion2055RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2055 | 10.4764 | 12.4636 | 14.9884 | 16.9306 | 18.8607
| JellicoeIce Accretion2060RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2060 | 10.5173 | 12.5078 | 15.0416 | 16.9875 | 18.9242
| JellicoeIce Accretion2065RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2065 | 10.5582 | 12.5519 | 15.0948 | 17.0445 | 18.9877
| JellicoeIce Accretion2070RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2070 | 10.5991 | 12.5961 | 15.148 | 17.1014 | 19.0512
| JellicoeIce Accretion2075RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2075 | 10.6332 | 12.6397 | 15.197 | 17.1568 | 19.1129
| JellicoeIce Accretion2080RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2080 | 10.6673 | 12.6832 | 15.246 | 17.2122 | 19.1747
| JellicoeIce Accretion2085RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2085 | 10.7014 | 12.7268 | 15.295 | 17.2675 | 19.2364
| JellicoeIce Accretion2090RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2090 | 10.6868 | 12.7045 | 15.26 | 17.228 | 19.1864
| JellicoeIce Accretion2095RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2095 | 10.6381 | 12.6387 | 15.176 | 17.1331 | 19.0747
| JellicoeIce Accretion2100RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2100 | 10.5894 | 12.5728 | 15.092 | 17.0381 | 18.963
| JellicoeIce Accretion2023RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2023 | 9.9269 | 11.8175 | 14.224 | 16.0573 | 17.887
| JellicoeIce Accretion2025RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2025 | 10.0828 | 12.0035 | 14.4433 | 16.3104 | 18.1692
| JellicoeIce Accretion2030RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2030 | 10.2387 | 12.1894 | 14.6627 | 16.5635 | 18.4514
| JellicoeIce Accretion2035RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2035 | 10.3945 | 12.3753 | 14.882 | 16.8167 | 18.7337
| JellicoeIce Accretion2040RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2040 | 10.4627 | 12.4489 | 14.9707 | 16.9116 | 18.8395
| JellicoeIce Accretion2045RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2045 | 10.5309 | 12.5225 | 15.0593 | 17.0065 | 18.9454
| JellicoeIce Accretion2050RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2050 | 10.6446 | 12.6542 | 15.2133 | 17.1752 | 19.1335
| JellicoeIce Accretion2055RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2055 | 10.6901 | 12.7123 | 15.2787 | 17.2491 | 19.2158
| JellicoeIce Accretion2060RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2060 | 10.6868 | 12.7045 | 15.26 | 17.228 | 19.1864
| JellicoeIce Accretion2065RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2065 | 10.6381 | 12.6387 | 15.176 | 17.1331 | 19.0747
| JellicoeIce Accretion2070RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2070 | 10.6056 | 12.6077 | 15.1527 | 17.1067 | 19.0512
| JellicoeIce Accretion2075RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2075 | 10.6219 | 12.6426 | 15.2133 | 17.1752 | 19.1394
| JellicoeIce Accretion2080RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2080 | 10.6381 | 12.6774 | 15.274 | 17.2438 | 19.2276
| JellicoeIce Accretion2085RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2085 | 10.5017 | 12.5322 | 15.113 | 17.0777 | 19.0512
| JellicoeIce Accretion2090RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2090 | 10.3653 | 12.3869 | 14.952 | 16.9116 | 18.8748
| JellicoeIce Accretion2095RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2095 | 10.3653 | 12.3869 | 14.952 | 16.9116 | 18.8748
| JellicoeIce Accretion2100RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2100 | 10.3653 | 12.3869 | 14.952 | 16.9116 | 18.8748
| JellicoeWind2023RCP4.5 | Jellicoe | Wind | RCP4.5 | 2023 | 73.6382 | 79.2951 | 85.2465 | 91.2047 | 97.1616
| JellicoeWind2025RCP4.5 | Jellicoe | Wind | RCP4.5 | 2025 | 73.7397 | 79.4163 | 85.391 | 91.3699 | 97.3474
| JellicoeWind2030RCP4.5 | Jellicoe | Wind | RCP4.5 | 2030 | 73.8413 | 79.5375 | 85.5355 | 91.5351 | 97.5331
| JellicoeWind2035RCP4.5 | Jellicoe | Wind | RCP4.5 | 2035 | 73.9428 | 79.6587 | 85.68 | 91.7003 | 97.7188
| JellicoeWind2040RCP4.5 | Jellicoe | Wind | RCP4.5 | 2040 | 74.0443 | 79.7799 | 85.8245 | 91.8656 | 97.9045
| JellicoeWind2045RCP4.5 | Jellicoe | Wind | RCP4.5 | 2045 | 74.1459 | 79.9011 | 85.969 | 92.0308 | 98.0903
| JellicoeWind2050RCP4.5 | Jellicoe | Wind | RCP4.5 | 2050 | 74.3795 | 80.1757 | 86.2937 | 92.3979 | 98.5008
| JellicoeWind2055RCP4.5 | Jellicoe | Wind | RCP4.5 | 2055 | 74.5116 | 80.329 | 86.4739 | 92.5998 | 98.7256
| JellicoeWind2060RCP4.5 | Jellicoe | Wind | RCP4.5 | 2060 | 74.6437 | 80.4824 | 86.6541 | 92.8017 | 98.9504
| JellicoeWind2065RCP4.5 | Jellicoe | Wind | RCP4.5 | 2065 | 74.7759 | 80.6357 | 86.8343 | 93.0037 | 99.1752
| JellicoeWind2070RCP4.5 | Jellicoe | Wind | RCP4.5 | 2070 | 74.908 | 80.7891 | 87.0145 | 93.2056 | 99.4
| JellicoeWind2075RCP4.5 | Jellicoe | Wind | RCP4.5 | 2075 | 74.9471 | 80.8339 | 87.0641 | 93.2601 | 99.4614
| JellicoeWind2080RCP4.5 | Jellicoe | Wind | RCP4.5 | 2080 | 74.9863 | 80.8787 | 87.1137 | 93.3147 | 99.5228
| JellicoeWind2085RCP4.5 | Jellicoe | Wind | RCP4.5 | 2085 | 75.0254 | 80.9235 | 87.1633 | 93.3693 | 99.5841
| JellicoeWind2090RCP4.5 | Jellicoe | Wind | RCP4.5 | 2090 | 75.0645 | 80.9683 | 87.2128 | 93.4238 | 99.6455
| JellicoeWind2095RCP4.5 | Jellicoe | Wind | RCP4.5 | 2095 | 75.1037 | 81.0131 | 87.2624 | 93.4784 | 99.7069
| JellicoeWind2100RCP4.5 | Jellicoe | Wind | RCP4.5 | 2100 | 75.1428 | 81.0579 | 87.312 | 93.533 | 99.7682
| JellicoeWind2023RCP6.0 | Jellicoe | Wind | RCP6.0 | 2023 | 73.6382 | 79.2951 | 85.2465 | 91.2047 | 97.1616
| JellicoeWind2025RCP6.0 | Jellicoe | Wind | RCP6.0 | 2025 | 73.7397 | 79.4163 | 85.391 | 91.3699 | 97.3474
| JellicoeWind2030RCP6.0 | Jellicoe | Wind | RCP6.0 | 2030 | 73.8413 | 79.5375 | 85.5355 | 91.5351 | 97.5331
| JellicoeWind2035RCP6.0 | Jellicoe | Wind | RCP6.0 | 2035 | 73.9428 | 79.6587 | 85.68 | 91.7003 | 97.7188
| JellicoeWind2040RCP6.0 | Jellicoe | Wind | RCP6.0 | 2040 | 74.0443 | 79.7799 | 85.8245 | 91.8656 | 97.9045
| JellicoeWind2045RCP6.0 | Jellicoe | Wind | RCP6.0 | 2045 | 74.1459 | 79.9011 | 85.969 | 92.0308 | 98.0903
| JellicoeWind2050RCP6.0 | Jellicoe | Wind | RCP6.0 | 2050 | 74.3795 | 80.1757 | 86.2937 | 92.3979 | 98.5008
| JellicoeWind2055RCP6.0 | Jellicoe | Wind | RCP6.0 | 2055 | 74.5116 | 80.329 | 86.4739 | 92.5998 | 98.7256
| JellicoeWind2060RCP6.0 | Jellicoe | Wind | RCP6.0 | 2060 | 74.6437 | 80.4824 | 86.6541 | 92.8017 | 98.9504
| JellicoeWind2065RCP6.0 | Jellicoe | Wind | RCP6.0 | 2065 | 74.7759 | 80.6357 | 86.8343 | 93.0037 | 99.1752
| JellicoeWind2070RCP6.0 | Jellicoe | Wind | RCP6.0 | 2070 | 74.908 | 80.7891 | 87.0145 | 93.2056 | 99.4
| JellicoeWind2075RCP6.0 | Jellicoe | Wind | RCP6.0 | 2075 | 74.9667 | 80.8563 | 87.0889 | 93.2874 | 99.4921
| JellicoeWind2080RCP6.0 | Jellicoe | Wind | RCP6.0 | 2080 | 75.0254 | 80.9235 | 87.1633 | 93.3693 | 99.5841
| JellicoeWind2085RCP6.0 | Jellicoe | Wind | RCP6.0 | 2085 | 75.0841 | 80.9907 | 87.2376 | 93.4511 | 99.6762
| JellicoeWind2090RCP6.0 | Jellicoe | Wind | RCP6.0 | 2090 | 75.1918 | 81.1237 | 87.397 | 93.6361 | 99.8877
| JellicoeWind2095RCP6.0 | Jellicoe | Wind | RCP6.0 | 2095 | 75.2407 | 81.1896 | 87.482 | 93.7391 | 100.0073
| JellicoeWind2100RCP6.0 | Jellicoe | Wind | RCP6.0 | 2100 | 75.2896 | 81.2555 | 87.567 | 93.8422 | 100.1268
| JellicoeWind2023RCP8.5 | Jellicoe | Wind | RCP8.5 | 2023 | 73.6382 | 79.2951 | 85.2465 | 91.2047 | 97.1616
| JellicoeWind2025RCP8.5 | Jellicoe | Wind | RCP8.5 | 2025 | 73.8413 | 79.5375 | 85.5355 | 91.5351 | 97.5331
| JellicoeWind2030RCP8.5 | Jellicoe | Wind | RCP8.5 | 2030 | 74.0443 | 79.7799 | 85.8245 | 91.8656 | 97.9045
| JellicoeWind2035RCP8.5 | Jellicoe | Wind | RCP8.5 | 2035 | 74.2474 | 80.0223 | 86.1135 | 92.196 | 98.276
| JellicoeWind2040RCP8.5 | Jellicoe | Wind | RCP8.5 | 2040 | 74.4676 | 80.2779 | 86.4138 | 92.5325 | 98.6507
| JellicoeWind2045RCP8.5 | Jellicoe | Wind | RCP8.5 | 2045 | 74.6878 | 80.5335 | 86.7142 | 92.869 | 99.0253
| JellicoeWind2050RCP8.5 | Jellicoe | Wind | RCP8.5 | 2050 | 74.9863 | 80.8787 | 87.1137 | 93.3147 | 99.5228
| JellicoeWind2055RCP8.5 | Jellicoe | Wind | RCP8.5 | 2055 | 75.0645 | 80.9683 | 87.2128 | 93.4238 | 99.6455
| JellicoeWind2060RCP8.5 | Jellicoe | Wind | RCP8.5 | 2060 | 75.1918 | 81.1237 | 87.397 | 93.6361 | 99.8877
| JellicoeWind2065RCP8.5 | Jellicoe | Wind | RCP8.5 | 2065 | 75.2407 | 81.1896 | 87.482 | 93.7391 | 100.0073
| JellicoeWind2070RCP8.5 | Jellicoe | Wind | RCP8.5 | 2070 | 75.3288 | 81.3029 | 87.6265 | 93.9119 | 100.2043
| JellicoeWind2075RCP8.5 | Jellicoe | Wind | RCP8.5 | 2075 | 75.3679 | 81.3504 | 87.686 | 93.9817 | 100.2818
| JellicoeWind2080RCP8.5 | Jellicoe | Wind | RCP8.5 | 2080 | 75.4071 | 81.3978 | 87.7455 | 94.0514 | 100.3593
| JellicoeWind2085RCP8.5 | Jellicoe | Wind | RCP8.5 | 2085 | 75.5979 | 81.6389 | 88.0472 | 94.4061 | 100.7663
| JellicoeWind2090RCP8.5 | Jellicoe | Wind | RCP8.5 | 2090 | 75.7887 | 81.88 | 88.349 | 94.7608 | 101.1733
| JellicoeWind2095RCP8.5 | Jellicoe | Wind | RCP8.5 | 2095 | 75.7887 | 81.88 | 88.349 | 94.7608 | 101.1733
| JellicoeWind2100RCP8.5 | Jellicoe | Wind | RCP8.5 | 2100 | 75.7887 | 81.88 | 88.349 | 94.7608 | 101.1733
| KapuskasingIce Accretion2023RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2023 | 10.7195 | 12.7737 | 15.375 | 17.3568 | 19.3536
| KapuskasingIce Accretion2025RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2025 | 10.77 | 12.8401 | 15.465 | 17.4642 | 19.4764
| KapuskasingIce Accretion2030RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2030 | 10.8204 | 12.9065 | 15.555 | 17.5715 | 19.5993
| KapuskasingIce Accretion2035RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2035 | 10.8709 | 12.9729 | 15.645 | 17.6789 | 19.7221
| KapuskasingIce Accretion2040RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2040 | 10.9213 | 13.0393 | 15.735 | 17.7862 | 19.845
| KapuskasingIce Accretion2045RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2045 | 10.9718 | 13.1057 | 15.825 | 17.8936 | 19.9678
| KapuskasingIce Accretion2050RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2050 | 11.0723 | 13.2244 | 15.966 | 18.0551 | 20.1474
| KapuskasingIce Accretion2055RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2055 | 11.1224 | 13.2767 | 16.017 | 18.1094 | 20.2041
| KapuskasingIce Accretion2060RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2060 | 11.1725 | 13.329 | 16.068 | 18.1636 | 20.2608
| KapuskasingIce Accretion2065RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2065 | 11.2226 | 13.3813 | 16.119 | 18.2179 | 20.3175
| KapuskasingIce Accretion2070RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2070 | 11.2727 | 13.4335 | 16.17 | 18.2721 | 20.3742
| KapuskasingIce Accretion2075RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2075 | 11.3058 | 13.4792 | 16.23 | 18.3427 | 20.4561
| KapuskasingIce Accretion2080RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2080 | 11.3388 | 13.5248 | 16.29 | 18.4134 | 20.538
| KapuskasingIce Accretion2085RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2085 | 11.3719 | 13.5705 | 16.35 | 18.484 | 20.6199
| KapuskasingIce Accretion2090RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2090 | 11.4049 | 13.6161 | 16.41 | 18.5546 | 20.7018
| KapuskasingIce Accretion2095RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2095 | 11.438 | 13.6618 | 16.47 | 18.6252 | 20.7837
| KapuskasingIce Accretion2100RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2100 | 11.471 | 13.7074 | 16.53 | 18.6959 | 20.8656
| KapuskasingIce Accretion2023RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2023 | 10.7195 | 12.7737 | 15.375 | 17.3568 | 19.3536
| KapuskasingIce Accretion2025RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2025 | 10.77 | 12.8401 | 15.465 | 17.4642 | 19.4764
| KapuskasingIce Accretion2030RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2030 | 10.8204 | 12.9065 | 15.555 | 17.5715 | 19.5993
| KapuskasingIce Accretion2035RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2035 | 10.8709 | 12.9729 | 15.645 | 17.6789 | 19.7221
| KapuskasingIce Accretion2040RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2040 | 10.9213 | 13.0393 | 15.735 | 17.7862 | 19.845
| KapuskasingIce Accretion2045RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2045 | 10.9718 | 13.1057 | 15.825 | 17.8936 | 19.9678
| KapuskasingIce Accretion2050RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2050 | 11.0723 | 13.2244 | 15.966 | 18.0551 | 20.1474
| KapuskasingIce Accretion2055RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2055 | 11.1224 | 13.2767 | 16.017 | 18.1094 | 20.2041
| KapuskasingIce Accretion2060RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2060 | 11.1725 | 13.329 | 16.068 | 18.1636 | 20.2608
| KapuskasingIce Accretion2065RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2065 | 11.2226 | 13.3813 | 16.119 | 18.2179 | 20.3175
| KapuskasingIce Accretion2070RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2070 | 11.2727 | 13.4335 | 16.17 | 18.2721 | 20.3742
| KapuskasingIce Accretion2075RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2075 | 11.3223 | 13.502 | 16.26 | 18.378 | 20.497
| KapuskasingIce Accretion2080RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2080 | 11.3719 | 13.5705 | 16.35 | 18.484 | 20.6199
| KapuskasingIce Accretion2085RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2085 | 11.4214 | 13.639 | 16.44 | 18.5899 | 20.7428
| KapuskasingIce Accretion2090RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2090 | 11.4536 | 13.7033 | 16.55 | 18.7297 | 20.9097
| KapuskasingIce Accretion2095RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2095 | 11.4362 | 13.6991 | 16.57 | 18.7636 | 20.9538
| KapuskasingIce Accretion2100RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2100 | 11.4188 | 13.695 | 16.59 | 18.7975 | 20.9979
| KapuskasingIce Accretion2023RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2023 | 10.7195 | 12.7737 | 15.375 | 17.3568 | 19.3536
| KapuskasingIce Accretion2025RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2025 | 10.8204 | 12.9065 | 15.555 | 17.5715 | 19.5993
| KapuskasingIce Accretion2030RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2030 | 10.9213 | 13.0393 | 15.735 | 17.7862 | 19.845
| KapuskasingIce Accretion2035RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2035 | 11.0222 | 13.1721 | 15.915 | 18.0009 | 20.0907
| KapuskasingIce Accretion2040RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2040 | 11.1057 | 13.2592 | 16 | 18.0913 | 20.1852
| KapuskasingIce Accretion2045RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2045 | 11.1892 | 13.3464 | 16.085 | 18.1817 | 20.2797
| KapuskasingIce Accretion2050RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2050 | 11.3388 | 13.5248 | 16.29 | 18.4134 | 20.538
| KapuskasingIce Accretion2055RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2055 | 11.4049 | 13.6161 | 16.41 | 18.5546 | 20.7018
| KapuskasingIce Accretion2060RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2060 | 11.4536 | 13.7033 | 16.55 | 18.7297 | 20.9097
| KapuskasingIce Accretion2065RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2065 | 11.4362 | 13.6991 | 16.57 | 18.7636 | 20.9538
| KapuskasingIce Accretion2070RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2070 | 11.4188 | 13.7157 | 16.63 | 18.8484 | 21.0672
| KapuskasingIce Accretion2075RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2075 | 11.4188 | 13.7365 | 16.67 | 18.8993 | 21.1365
| KapuskasingIce Accretion2080RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2080 | 11.4188 | 13.7572 | 16.71 | 18.9501 | 21.2058
| KapuskasingIce Accretion2085RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2085 | 11.2623 | 13.5954 | 16.545 | 18.7806 | 21.0357
| KapuskasingIce Accretion2090RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2090 | 11.1057 | 13.4335 | 16.38 | 18.6111 | 20.8656
| KapuskasingIce Accretion2095RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2095 | 11.1057 | 13.4335 | 16.38 | 18.6111 | 20.8656
| KapuskasingIce Accretion2100RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2100 | 11.1057 | 13.4335 | 16.38 | 18.6111 | 20.8656
| KapuskasingWind2023RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2023 | 74.4382 | 80.2357 | 86.3515 | 92.4507 | 98.5473
| KapuskasingWind2025RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2025 | 74.5948 | 80.4215 | 86.5739 | 92.7038 | 98.8315
| KapuskasingWind2030RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2030 | 74.7514 | 80.6073 | 86.7963 | 92.957 | 99.1158
| KapuskasingWind2035RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2035 | 74.908 | 80.7931 | 87.0188 | 93.2101 | 99.4
| KapuskasingWind2040RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2040 | 75.0645 | 80.9788 | 87.2412 | 93.4633 | 99.6843
| KapuskasingWind2045RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2045 | 75.2211 | 81.1646 | 87.4636 | 93.7164 | 99.9685
| KapuskasingWind2050RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2050 | 75.385 | 81.3519 | 87.6775 | 93.955 | 100.2314
| KapuskasingWind2055RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2055 | 75.3924 | 81.3535 | 87.669 | 93.9404 | 100.2101
| KapuskasingWind2060RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2060 | 75.3997 | 81.3551 | 87.6605 | 93.9259 | 100.1888
| KapuskasingWind2065RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2065 | 75.4071 | 81.3567 | 87.652 | 93.9113 | 100.1675
| KapuskasingWind2070RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2070 | 75.4144 | 81.3583 | 87.6435 | 93.8968 | 100.1462
| KapuskasingWind2075RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2075 | 75.4217 | 81.3543 | 87.6265 | 93.8695 | 100.109
| KapuskasingWind2080RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2080 | 75.4291 | 81.3504 | 87.6095 | 93.8422 | 100.0719
| KapuskasingWind2085RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2085 | 75.4364 | 81.3464 | 87.5925 | 93.8149 | 100.0347
| KapuskasingWind2090RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2090 | 75.4438 | 81.3424 | 87.5755 | 93.7876 | 99.9976
| KapuskasingWind2095RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2095 | 75.4511 | 81.3385 | 87.5585 | 93.7604 | 99.9604
| KapuskasingWind2100RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2100 | 75.4584 | 81.3345 | 87.5415 | 93.7331 | 99.9233
| KapuskasingWind2023RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2023 | 74.4382 | 80.2357 | 86.3515 | 92.4507 | 98.5473
| KapuskasingWind2025RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2025 | 74.5948 | 80.4215 | 86.5739 | 92.7038 | 98.8315
| KapuskasingWind2030RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2030 | 74.7514 | 80.6073 | 86.7963 | 92.957 | 99.1158
| KapuskasingWind2035RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2035 | 74.908 | 80.7931 | 87.0188 | 93.2101 | 99.4
| KapuskasingWind2040RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2040 | 75.0645 | 80.9788 | 87.2412 | 93.4633 | 99.6843
| KapuskasingWind2045RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2045 | 75.2211 | 81.1646 | 87.4636 | 93.7164 | 99.9685
| KapuskasingWind2050RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2050 | 75.385 | 81.3519 | 87.6775 | 93.955 | 100.2314
| KapuskasingWind2055RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2055 | 75.3924 | 81.3535 | 87.669 | 93.9404 | 100.2101
| KapuskasingWind2060RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2060 | 75.3997 | 81.3551 | 87.6605 | 93.9259 | 100.1888
| KapuskasingWind2065RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2065 | 75.4071 | 81.3567 | 87.652 | 93.9113 | 100.1675
| KapuskasingWind2070RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2070 | 75.4144 | 81.3583 | 87.6435 | 93.8968 | 100.1462
| KapuskasingWind2075RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2075 | 75.4254 | 81.3523 | 87.618 | 93.8559 | 100.0904
| KapuskasingWind2080RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2080 | 75.4364 | 81.3464 | 87.5925 | 93.8149 | 100.0347
| KapuskasingWind2085RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2085 | 75.4474 | 81.3405 | 87.567 | 93.774 | 99.979
| KapuskasingWind2090RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2090 | 75.4878 | 81.3556 | 87.5472 | 93.727 | 99.9071
| KapuskasingWind2095RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2095 | 75.5172 | 81.3767 | 87.5528 | 93.7209 | 99.891
| KapuskasingWind2100RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2100 | 75.5465 | 81.3978 | 87.5585 | 93.7149 | 99.8748
| KapuskasingWind2023RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2023 | 74.4382 | 80.2357 | 86.3515 | 92.4507 | 98.5473
| KapuskasingWind2025RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2025 | 74.7514 | 80.6073 | 86.7963 | 92.957 | 99.1158
| KapuskasingWind2030RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2030 | 75.0645 | 80.9788 | 87.2412 | 93.4633 | 99.6843
| KapuskasingWind2035RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2035 | 75.3777 | 81.3504 | 87.686 | 93.9695 | 100.2527
| KapuskasingWind2040RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2040 | 75.3899 | 81.353 | 87.6718 | 93.9453 | 100.2172
| KapuskasingWind2045RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2045 | 75.4022 | 81.3556 | 87.6577 | 93.921 | 100.1817
| KapuskasingWind2050RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2050 | 75.4291 | 81.3504 | 87.6095 | 93.8422 | 100.0719
| KapuskasingWind2055RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2055 | 75.4438 | 81.3424 | 87.5755 | 93.7876 | 99.9976
| KapuskasingWind2060RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2060 | 75.4878 | 81.3556 | 87.5472 | 93.727 | 99.9071
| KapuskasingWind2065RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2065 | 75.5172 | 81.3767 | 87.5528 | 93.7209 | 99.891
| KapuskasingWind2070RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2070 | 75.7227 | 81.5849 | 87.7597 | 93.9271 | 100.1009
| KapuskasingWind2075RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2075 | 75.8988 | 81.772 | 87.9608 | 94.1393 | 100.327
| KapuskasingWind2080RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2080 | 76.075 | 81.959 | 88.162 | 94.3515 | 100.5531
| KapuskasingWind2085RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2085 | 76.1851 | 82.0974 | 88.3277 | 94.5471 | 100.7712
| KapuskasingWind2090RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2090 | 76.2951 | 82.2357 | 88.4935 | 94.7426 | 100.9892
| KapuskasingWind2095RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2095 | 76.2951 | 82.2357 | 88.4935 | 94.7426 | 100.9892
| KapuskasingWind2100RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2100 | 76.2951 | 82.2357 | 88.4935 | 94.7426 | 100.9892
| KemptvilleIce Accretion2023RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2023 | 20.5623 | 24.4518 | 29.4 | 33.1542 | 36.9306
| KemptvilleIce Accretion2025RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2025 | 20.5588 | 24.4601 | 29.42 | 33.1881 | 36.9747
| KemptvilleIce Accretion2030RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2030 | 20.5553 | 24.4684 | 29.44 | 33.222 | 37.0188
| KemptvilleIce Accretion2035RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2035 | 20.5518 | 24.4767 | 29.46 | 33.2559 | 37.0629
| KemptvilleIce Accretion2040RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2040 | 20.5483 | 24.485 | 29.48 | 33.2898 | 37.107
| KemptvilleIce Accretion2045RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2045 | 20.5449 | 24.4933 | 29.5 | 33.3237 | 37.1511
| KemptvilleIce Accretion2050RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2050 | 20.5623 | 24.5414 | 29.586 | 33.439 | 37.2935
| KemptvilleIce Accretion2055RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2055 | 20.5831 | 24.5813 | 29.652 | 33.5203 | 37.3918
| KemptvilleIce Accretion2060RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2060 | 20.604 | 24.6211 | 29.718 | 33.6017 | 37.49
| KemptvilleIce Accretion2065RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2065 | 20.6249 | 24.661 | 29.784 | 33.683 | 37.5883
| KemptvilleIce Accretion2070RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2070 | 20.6458 | 24.7008 | 29.85 | 33.7644 | 37.6866
| KemptvilleIce Accretion2075RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2075 | 20.7188 | 24.817 | 30.015 | 33.9678 | 37.9323
| KemptvilleIce Accretion2080RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2080 | 20.7919 | 24.9332 | 30.18 | 34.1712 | 38.178
| KemptvilleIce Accretion2085RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2085 | 20.8649 | 25.0494 | 30.345 | 34.3746 | 38.4237
| KemptvilleIce Accretion2090RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2090 | 20.938 | 25.1656 | 30.51 | 34.578 | 38.6694
| KemptvilleIce Accretion2095RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2095 | 21.0111 | 25.2818 | 30.675 | 34.7814 | 38.9151
| KemptvilleIce Accretion2100RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2100 | 21.0841 | 25.398 | 30.84 | 34.9848 | 39.1608
| KemptvilleIce Accretion2023RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2023 | 20.5623 | 24.4518 | 29.4 | 33.1542 | 36.9306
| KemptvilleIce Accretion2025RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2025 | 20.5588 | 24.4601 | 29.42 | 33.1881 | 36.9747
| KemptvilleIce Accretion2030RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2030 | 20.5553 | 24.4684 | 29.44 | 33.222 | 37.0188
| KemptvilleIce Accretion2035RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2035 | 20.5518 | 24.4767 | 29.46 | 33.2559 | 37.0629
| KemptvilleIce Accretion2040RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2040 | 20.5483 | 24.485 | 29.48 | 33.2898 | 37.107
| KemptvilleIce Accretion2045RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2045 | 20.5449 | 24.4933 | 29.5 | 33.3237 | 37.1511
| KemptvilleIce Accretion2050RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2050 | 20.5623 | 24.5414 | 29.586 | 33.439 | 37.2935
| KemptvilleIce Accretion2055RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2055 | 20.5831 | 24.5813 | 29.652 | 33.5203 | 37.3918
| KemptvilleIce Accretion2060RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2060 | 20.604 | 24.6211 | 29.718 | 33.6017 | 37.49
| KemptvilleIce Accretion2065RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2065 | 20.6249 | 24.661 | 29.784 | 33.683 | 37.5883
| KemptvilleIce Accretion2070RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2070 | 20.6458 | 24.7008 | 29.85 | 33.7644 | 37.6866
| KemptvilleIce Accretion2075RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2075 | 20.7554 | 24.8751 | 30.0975 | 34.0695 | 38.0551
| KemptvilleIce Accretion2080RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2080 | 20.8649 | 25.0494 | 30.345 | 34.3746 | 38.4237
| KemptvilleIce Accretion2085RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2085 | 20.9745 | 25.2237 | 30.5925 | 34.6797 | 38.7922
| KemptvilleIce Accretion2090RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2090 | 21.0911 | 25.4561 | 30.97 | 35.1656 | 39.3876
| KemptvilleIce Accretion2095RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2095 | 21.0981 | 25.5142 | 31.1 | 35.3464 | 39.6144
| KemptvilleIce Accretion2100RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2100 | 21.105 | 25.5723 | 31.23 | 35.5272 | 39.8412
| KemptvilleIce Accretion2023RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2023 | 20.5623 | 24.4518 | 29.4 | 33.1542 | 36.9306
| KemptvilleIce Accretion2025RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2025 | 20.5553 | 24.4684 | 29.44 | 33.222 | 37.0188
| KemptvilleIce Accretion2030RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2030 | 20.5483 | 24.485 | 29.48 | 33.2898 | 37.107
| KemptvilleIce Accretion2035RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2035 | 20.5414 | 24.5016 | 29.52 | 33.3576 | 37.1952
| KemptvilleIce Accretion2040RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2040 | 20.5762 | 24.568 | 29.63 | 33.4932 | 37.359
| KemptvilleIce Accretion2045RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2045 | 20.611 | 24.6344 | 29.74 | 33.6288 | 37.5228
| KemptvilleIce Accretion2050RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2050 | 20.7919 | 24.9332 | 30.18 | 34.1712 | 38.178
| KemptvilleIce Accretion2055RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2055 | 20.938 | 25.1656 | 30.51 | 34.578 | 38.6694
| KemptvilleIce Accretion2060RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2060 | 21.0911 | 25.4561 | 30.97 | 35.1656 | 39.3876
| KemptvilleIce Accretion2065RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2065 | 21.0981 | 25.5142 | 31.1 | 35.3464 | 39.6144
| KemptvilleIce Accretion2070RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2070 | 20.764 | 25.1905 | 30.8 | 35.0639 | 39.3246
| KemptvilleIce Accretion2075RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2075 | 20.4231 | 24.8087 | 30.37 | 34.6006 | 38.808
| KemptvilleIce Accretion2080RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2080 | 20.0821 | 24.4269 | 29.94 | 34.1373 | 38.2914
| KemptvilleIce Accretion2085RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2085 | 19.2158 | 23.4433 | 28.8 | 32.866 | 36.9117
| KemptvilleIce Accretion2090RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2090 | 18.3495 | 22.4598 | 27.66 | 31.5948 | 35.532
| KemptvilleIce Accretion2095RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2095 | 18.3495 | 22.4598 | 27.66 | 31.5948 | 35.532
| KemptvilleIce Accretion2100RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2100 | 18.3495 | 22.4598 | 27.66 | 31.5948 | 35.532
| KemptvilleWind2023RCP4.5 | Kemptville | Wind | RCP4.5 | 2023 | 75.9789 | 81.8236 | 87.9736 | 94.1223 | 100.2698
| KemptvilleWind2025RCP4.5 | Kemptville | Wind | RCP4.5 | 2025 | 75.9852 | 81.825 | 87.9707 | 94.1145 | 100.2581
| KemptvilleWind2030RCP4.5 | Kemptville | Wind | RCP4.5 | 2030 | 75.9915 | 81.8264 | 87.9677 | 94.1066 | 100.2464
| KemptvilleWind2035RCP4.5 | Kemptville | Wind | RCP4.5 | 2035 | 75.9979 | 81.8277 | 87.9648 | 94.0988 | 100.2347
| KemptvilleWind2040RCP4.5 | Kemptville | Wind | RCP4.5 | 2040 | 76.0042 | 81.8291 | 87.9619 | 94.0909 | 100.223
| KemptvilleWind2045RCP4.5 | Kemptville | Wind | RCP4.5 | 2045 | 76.0105 | 81.8305 | 87.9589 | 94.0831 | 100.2113
| KemptvilleWind2050RCP4.5 | Kemptville | Wind | RCP4.5 | 2050 | 76.0032 | 81.8204 | 87.9454 | 94.0677 | 100.1936
| KemptvilleWind2055RCP4.5 | Kemptville | Wind | RCP4.5 | 2055 | 75.9895 | 81.8089 | 87.9349 | 94.0602 | 100.1876
| KemptvilleWind2060RCP4.5 | Kemptville | Wind | RCP4.5 | 2060 | 75.9758 | 81.7974 | 87.9243 | 94.0527 | 100.1816
| KemptvilleWind2065RCP4.5 | Kemptville | Wind | RCP4.5 | 2065 | 75.9621 | 81.786 | 87.9138 | 94.0451 | 100.1755
| KemptvilleWind2070RCP4.5 | Kemptville | Wind | RCP4.5 | 2070 | 75.9485 | 81.7745 | 87.9032 | 94.0376 | 100.1695
| KemptvilleWind2075RCP4.5 | Kemptville | Wind | RCP4.5 | 2075 | 75.9181 | 81.7445 | 87.8739 | 94.0093 | 100.1411
| KemptvilleWind2080RCP4.5 | Kemptville | Wind | RCP4.5 | 2080 | 75.8877 | 81.7145 | 87.8445 | 93.9811 | 100.1127
| KemptvilleWind2085RCP4.5 | Kemptville | Wind | RCP4.5 | 2085 | 75.8573 | 81.6845 | 87.8152 | 93.9528 | 100.0842
| KemptvilleWind2090RCP4.5 | Kemptville | Wind | RCP4.5 | 2090 | 75.8269 | 81.6545 | 87.7859 | 93.9246 | 100.0558
| KemptvilleWind2095RCP4.5 | Kemptville | Wind | RCP4.5 | 2095 | 75.7965 | 81.6245 | 87.7565 | 93.8964 | 100.0274
| KemptvilleWind2100RCP4.5 | Kemptville | Wind | RCP4.5 | 2100 | 75.7661 | 81.5945 | 87.7272 | 93.8681 | 99.999
| KemptvilleWind2023RCP6.0 | Kemptville | Wind | RCP6.0 | 2023 | 75.9789 | 81.8236 | 87.9736 | 94.1223 | 100.2698
| KemptvilleWind2025RCP6.0 | Kemptville | Wind | RCP6.0 | 2025 | 75.9852 | 81.825 | 87.9707 | 94.1145 | 100.2581
| KemptvilleWind2030RCP6.0 | Kemptville | Wind | RCP6.0 | 2030 | 75.9915 | 81.8264 | 87.9677 | 94.1066 | 100.2464
| KemptvilleWind2035RCP6.0 | Kemptville | Wind | RCP6.0 | 2035 | 75.9979 | 81.8277 | 87.9648 | 94.0988 | 100.2347
| KemptvilleWind2040RCP6.0 | Kemptville | Wind | RCP6.0 | 2040 | 76.0042 | 81.8291 | 87.9619 | 94.0909 | 100.223
| KemptvilleWind2045RCP6.0 | Kemptville | Wind | RCP6.0 | 2045 | 76.0105 | 81.8305 | 87.9589 | 94.0831 | 100.2113
| KemptvilleWind2050RCP6.0 | Kemptville | Wind | RCP6.0 | 2050 | 76.0032 | 81.8204 | 87.9454 | 94.0677 | 100.1936
| KemptvilleWind2055RCP6.0 | Kemptville | Wind | RCP6.0 | 2055 | 75.9895 | 81.8089 | 87.9349 | 94.0602 | 100.1876
| KemptvilleWind2060RCP6.0 | Kemptville | Wind | RCP6.0 | 2060 | 75.9758 | 81.7974 | 87.9243 | 94.0527 | 100.1816
| KemptvilleWind2065RCP6.0 | Kemptville | Wind | RCP6.0 | 2065 | 75.9621 | 81.786 | 87.9138 | 94.0451 | 100.1755
| KemptvilleWind2070RCP6.0 | Kemptville | Wind | RCP6.0 | 2070 | 75.9485 | 81.7745 | 87.9032 | 94.0376 | 100.1695
| KemptvilleWind2075RCP6.0 | Kemptville | Wind | RCP6.0 | 2075 | 75.9029 | 81.7295 | 87.8592 | 93.9952 | 100.1269
| KemptvilleWind2080RCP6.0 | Kemptville | Wind | RCP6.0 | 2080 | 75.8573 | 81.6845 | 87.8152 | 93.9528 | 100.0842
| KemptvilleWind2085RCP6.0 | Kemptville | Wind | RCP6.0 | 2085 | 75.8117 | 81.6395 | 87.7712 | 93.9105 | 100.0416
| KemptvilleWind2090RCP6.0 | Kemptville | Wind | RCP6.0 | 2090 | 75.7332 | 81.5508 | 87.6744 | 93.8053 | 99.9254
| KemptvilleWind2095RCP6.0 | Kemptville | Wind | RCP6.0 | 2095 | 75.7002 | 81.5072 | 87.6216 | 93.7426 | 99.8518
| KemptvilleWind2100RCP6.0 | Kemptville | Wind | RCP6.0 | 2100 | 75.6673 | 81.4635 | 87.5688 | 93.6798 | 99.7783
| KemptvilleWind2023RCP8.5 | Kemptville | Wind | RCP8.5 | 2023 | 75.9789 | 81.8236 | 87.9736 | 94.1223 | 100.2698
| KemptvilleWind2025RCP8.5 | Kemptville | Wind | RCP8.5 | 2025 | 75.9915 | 81.8264 | 87.9677 | 94.1066 | 100.2464
| KemptvilleWind2030RCP8.5 | Kemptville | Wind | RCP8.5 | 2030 | 76.0042 | 81.8291 | 87.9619 | 94.0909 | 100.223
| KemptvilleWind2035RCP8.5 | Kemptville | Wind | RCP8.5 | 2035 | 76.0168 | 81.8318 | 87.956 | 94.0753 | 100.1996
| KemptvilleWind2040RCP8.5 | Kemptville | Wind | RCP8.5 | 2040 | 75.9941 | 81.8127 | 87.9384 | 94.0627 | 100.1896
| KemptvilleWind2045RCP8.5 | Kemptville | Wind | RCP8.5 | 2045 | 75.9713 | 81.7936 | 87.9208 | 94.0501 | 100.1796
| KemptvilleWind2050RCP8.5 | Kemptville | Wind | RCP8.5 | 2050 | 75.8877 | 81.7145 | 87.8445 | 93.9811 | 100.1127
| KemptvilleWind2055RCP8.5 | Kemptville | Wind | RCP8.5 | 2055 | 75.8269 | 81.6545 | 87.7859 | 93.9246 | 100.0558
| KemptvilleWind2060RCP8.5 | Kemptville | Wind | RCP8.5 | 2060 | 75.7332 | 81.5508 | 87.6744 | 93.8053 | 99.9254
| KemptvilleWind2065RCP8.5 | Kemptville | Wind | RCP8.5 | 2065 | 75.7002 | 81.5072 | 87.6216 | 93.7426 | 99.8518
| KemptvilleWind2070RCP8.5 | Kemptville | Wind | RCP8.5 | 2070 | 75.7104 | 81.5154 | 87.6275 | 93.7457 | 99.8552
| KemptvilleWind2075RCP8.5 | Kemptville | Wind | RCP8.5 | 2075 | 75.7534 | 81.5672 | 87.6861 | 93.8116 | 99.9321
| KemptvilleWind2080RCP8.5 | Kemptville | Wind | RCP8.5 | 2080 | 75.7965 | 81.619 | 87.7448 | 93.8775 | 100.009
| KemptvilleWind2085RCP8.5 | Kemptville | Wind | RCP8.5 | 2085 | 75.7357 | 81.5617 | 87.692 | 93.8304 | 99.9639
| KemptvilleWind2090RCP8.5 | Kemptville | Wind | RCP8.5 | 2090 | 75.6749 | 81.5045 | 87.6392 | 93.7834 | 99.9187
| KemptvilleWind2095RCP8.5 | Kemptville | Wind | RCP8.5 | 2095 | 75.6749 | 81.5045 | 87.6392 | 93.7834 | 99.9187
| KemptvilleWind2100RCP8.5 | Kemptville | Wind | RCP8.5 | 2100 | 75.6749 | 81.5045 | 87.6392 | 93.7834 | 99.9187
| KenoraIce Accretion2023RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2023 | 9.4531 | 11.2432 | 13.52 | 15.2776 | 17.0188
| KenoraIce Accretion2025RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2025 | 9.4923 | 11.2863 | 13.5677 | 15.3266 | 17.0734
| KenoraIce Accretion2030RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2030 | 9.5315 | 11.3295 | 13.6153 | 15.3755 | 17.128
| KenoraIce Accretion2035RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2035 | 9.5707 | 11.3727 | 13.663 | 15.4245 | 17.1826
| KenoraIce Accretion2040RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2040 | 9.6099 | 11.4158 | 13.7107 | 15.4735 | 17.2372
| KenoraIce Accretion2045RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2045 | 9.6491 | 11.459 | 13.7583 | 15.5224 | 17.2918
| KenoraIce Accretion2050RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2050 | 9.6684 | 11.4762 | 13.7748 | 15.5361 | 17.3038
| KenoraIce Accretion2055RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2055 | 9.6485 | 11.4503 | 13.7436 | 15.5009 | 17.2612
| KenoraIce Accretion2060RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2060 | 9.6286 | 11.4245 | 13.7124 | 15.4656 | 17.2187
| KenoraIce Accretion2065RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2065 | 9.6087 | 11.3986 | 13.6812 | 15.4304 | 17.1761
| KenoraIce Accretion2070RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2070 | 9.5888 | 11.3727 | 13.65 | 15.3951 | 17.1335
| KenoraIce Accretion2075RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2075 | 9.6445 | 11.4428 | 13.7367 | 15.4955 | 17.2454
| KenoraIce Accretion2080RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2080 | 9.7003 | 11.5129 | 13.8233 | 15.5959 | 17.3573
| KenoraIce Accretion2085RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2085 | 9.7561 | 11.5831 | 13.91 | 15.6963 | 17.4693
| KenoraIce Accretion2090RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2090 | 9.8119 | 11.6532 | 13.9967 | 15.7966 | 17.5812
| KenoraIce Accretion2095RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2095 | 9.8677 | 11.7233 | 14.0833 | 15.897 | 17.6931
| KenoraIce Accretion2100RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2100 | 9.9235 | 11.7935 | 14.17 | 15.9974 | 17.8051
| KenoraIce Accretion2023RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2023 | 9.4531 | 11.2432 | 13.52 | 15.2776 | 17.0188
| KenoraIce Accretion2025RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2025 | 9.4923 | 11.2863 | 13.5677 | 15.3266 | 17.0734
| KenoraIce Accretion2030RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2030 | 9.5315 | 11.3295 | 13.6153 | 15.3755 | 17.128
| KenoraIce Accretion2035RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2035 | 9.5707 | 11.3727 | 13.663 | 15.4245 | 17.1826
| KenoraIce Accretion2040RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2040 | 9.6099 | 11.4158 | 13.7107 | 15.4735 | 17.2372
| KenoraIce Accretion2045RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2045 | 9.6491 | 11.459 | 13.7583 | 15.5224 | 17.2918
| KenoraIce Accretion2050RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2050 | 9.6684 | 11.4762 | 13.7748 | 15.5361 | 17.3038
| KenoraIce Accretion2055RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2055 | 9.6485 | 11.4503 | 13.7436 | 15.5009 | 17.2612
| KenoraIce Accretion2060RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2060 | 9.6286 | 11.4245 | 13.7124 | 15.4656 | 17.2187
| KenoraIce Accretion2065RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2065 | 9.6087 | 11.3986 | 13.6812 | 15.4304 | 17.1761
| KenoraIce Accretion2070RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2070 | 9.5888 | 11.3727 | 13.65 | 15.3951 | 17.1335
| KenoraIce Accretion2075RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2075 | 9.6724 | 11.4779 | 13.78 | 15.5457 | 17.3014
| KenoraIce Accretion2080RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2080 | 9.7561 | 11.5831 | 13.91 | 15.6963 | 17.4693
| KenoraIce Accretion2085RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2085 | 9.8398 | 11.6883 | 14.04 | 15.8468 | 17.6372
| KenoraIce Accretion2090RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2090 | 9.9235 | 11.7935 | 14.17 | 15.9925 | 17.8051
| KenoraIce Accretion2095RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2095 | 9.9235 | 11.7935 | 14.17 | 15.9876 | 17.8051
| KenoraIce Accretion2100RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2100 | 9.9235 | 11.7935 | 14.17 | 15.9827 | 17.8051
| KenoraIce Accretion2023RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2023 | 9.4531 | 11.2432 | 13.52 | 15.2776 | 17.0188
| KenoraIce Accretion2025RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2025 | 9.5315 | 11.3295 | 13.6153 | 15.3755 | 17.128
| KenoraIce Accretion2030RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2030 | 9.6099 | 11.4158 | 13.7107 | 15.4735 | 17.2372
| KenoraIce Accretion2035RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2035 | 9.6883 | 11.5021 | 13.806 | 15.5714 | 17.3464
| KenoraIce Accretion2040RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2040 | 9.6551 | 11.459 | 13.754 | 15.5126 | 17.2754
| KenoraIce Accretion2045RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2045 | 9.6219 | 11.4158 | 13.702 | 15.4539 | 17.2045
| KenoraIce Accretion2050RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2050 | 9.7003 | 11.5129 | 13.8233 | 15.5959 | 17.3573
| KenoraIce Accretion2055RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2055 | 9.8119 | 11.6532 | 13.9967 | 15.7966 | 17.5812
| KenoraIce Accretion2060RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2060 | 9.9235 | 11.7935 | 14.17 | 15.9925 | 17.8051
| KenoraIce Accretion2065RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2065 | 9.9235 | 11.7935 | 14.17 | 15.9876 | 17.8051
| KenoraIce Accretion2070RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2070 | 9.9657 | 11.851 | 14.248 | 16.0758 | 17.9088
| KenoraIce Accretion2075RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2075 | 10.0079 | 11.9086 | 14.326 | 16.1688 | 18.0125
| KenoraIce Accretion2080RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2080 | 10.0501 | 11.9661 | 14.404 | 16.2618 | 18.1163
| KenoraIce Accretion2085RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2085 | 9.7878 | 11.6532 | 14.0205 | 15.8285 | 17.6331
| KenoraIce Accretion2090RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2090 | 9.5254 | 11.3403 | 13.637 | 15.3951 | 17.1499
| KenoraIce Accretion2095RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2095 | 9.5254 | 11.3403 | 13.637 | 15.3951 | 17.1499
| KenoraIce Accretion2100RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2100 | 9.5254 | 11.3403 | 13.637 | 15.3951 | 17.1499
| KenoraWind2023RCP4.5 | Kenora | Wind | RCP4.5 | 2023 | 75.0838 | 81.0837 | 87.462 | 93.7776 | 100.0988
| KenoraWind2025RCP4.5 | Kenora | Wind | RCP4.5 | 2025 | 75.09 | 81.0757 | 87.4333 | 93.7331 | 100.0384
| KenoraWind2030RCP4.5 | Kenora | Wind | RCP4.5 | 2030 | 75.0961 | 81.0677 | 87.4047 | 93.6886 | 99.9779
| KenoraWind2035RCP4.5 | Kenora | Wind | RCP4.5 | 2035 | 75.1023 | 81.0597 | 87.376 | 93.6442 | 99.9175
| KenoraWind2040RCP4.5 | Kenora | Wind | RCP4.5 | 2040 | 75.1085 | 81.0517 | 87.3473 | 93.5997 | 99.857
| KenoraWind2045RCP4.5 | Kenora | Wind | RCP4.5 | 2045 | 75.1147 | 81.0437 | 87.3187 | 93.5552 | 99.7965
| KenoraWind2050RCP4.5 | Kenora | Wind | RCP4.5 | 2050 | 75.2174 | 81.1573 | 87.4431 | 93.6911 | 99.9459
| KenoraWind2055RCP4.5 | Kenora | Wind | RCP4.5 | 2055 | 75.314 | 81.2789 | 87.5962 | 93.8714 | 100.1557
| KenoraWind2060RCP4.5 | Kenora | Wind | RCP4.5 | 2060 | 75.4105 | 81.4004 | 87.7492 | 94.0518 | 100.3655
| KenoraWind2065RCP4.5 | Kenora | Wind | RCP4.5 | 2065 | 75.507 | 81.522 | 87.9023 | 94.2322 | 100.5753
| KenoraWind2070RCP4.5 | Kenora | Wind | RCP4.5 | 2070 | 75.6036 | 81.6436 | 88.0554 | 94.4125 | 100.7851
| KenoraWind2075RCP4.5 | Kenora | Wind | RCP4.5 | 2075 | 75.6679 | 81.7209 | 88.15 | 94.5214 | 100.9077
| KenoraWind2080RCP4.5 | Kenora | Wind | RCP4.5 | 2080 | 75.7323 | 81.7982 | 88.2446 | 94.6303 | 101.0302
| KenoraWind2085RCP4.5 | Kenora | Wind | RCP4.5 | 2085 | 75.7967 | 81.8755 | 88.3392 | 94.7392 | 101.1528
| KenoraWind2090RCP4.5 | Kenora | Wind | RCP4.5 | 2090 | 75.861 | 81.9528 | 88.4338 | 94.8481 | 101.2753
| KenoraWind2095RCP4.5 | Kenora | Wind | RCP4.5 | 2095 | 75.9254 | 82.0302 | 88.5284 | 94.957 | 101.3979
| KenoraWind2100RCP4.5 | Kenora | Wind | RCP4.5 | 2100 | 75.9897 | 82.1075 | 88.623 | 95.0659 | 101.5204
| KenoraWind2023RCP6.0 | Kenora | Wind | RCP6.0 | 2023 | 75.0838 | 81.0837 | 87.462 | 93.7776 | 100.0988
| KenoraWind2025RCP6.0 | Kenora | Wind | RCP6.0 | 2025 | 75.09 | 81.0757 | 87.4333 | 93.7331 | 100.0384
| KenoraWind2030RCP6.0 | Kenora | Wind | RCP6.0 | 2030 | 75.0961 | 81.0677 | 87.4047 | 93.6886 | 99.9779
| KenoraWind2035RCP6.0 | Kenora | Wind | RCP6.0 | 2035 | 75.1023 | 81.0597 | 87.376 | 93.6442 | 99.9175
| KenoraWind2040RCP6.0 | Kenora | Wind | RCP6.0 | 2040 | 75.1085 | 81.0517 | 87.3473 | 93.5997 | 99.857
| KenoraWind2045RCP6.0 | Kenora | Wind | RCP6.0 | 2045 | 75.1147 | 81.0437 | 87.3187 | 93.5552 | 99.7965
| KenoraWind2050RCP6.0 | Kenora | Wind | RCP6.0 | 2050 | 75.2174 | 81.1573 | 87.4431 | 93.6911 | 99.9459
| KenoraWind2055RCP6.0 | Kenora | Wind | RCP6.0 | 2055 | 75.314 | 81.2789 | 87.5962 | 93.8714 | 100.1557
| KenoraWind2060RCP6.0 | Kenora | Wind | RCP6.0 | 2060 | 75.4105 | 81.4004 | 87.7492 | 94.0518 | 100.3655
| KenoraWind2065RCP6.0 | Kenora | Wind | RCP6.0 | 2065 | 75.507 | 81.522 | 87.9023 | 94.2322 | 100.5753
| KenoraWind2070RCP6.0 | Kenora | Wind | RCP6.0 | 2070 | 75.6036 | 81.6436 | 88.0554 | 94.4125 | 100.7851
| KenoraWind2075RCP6.0 | Kenora | Wind | RCP6.0 | 2075 | 75.7001 | 81.7596 | 88.1973 | 94.5759 | 100.9689
| KenoraWind2080RCP6.0 | Kenora | Wind | RCP6.0 | 2080 | 75.7967 | 81.8755 | 88.3392 | 94.7392 | 101.1528
| KenoraWind2085RCP6.0 | Kenora | Wind | RCP6.0 | 2085 | 75.8932 | 81.9915 | 88.4811 | 94.9025 | 101.3366
| KenoraWind2090RCP6.0 | Kenora | Wind | RCP6.0 | 2090 | 76.2472 | 82.4514 | 89.0731 | 95.6057 | 102.1544
| KenoraWind2095RCP6.0 | Kenora | Wind | RCP6.0 | 2095 | 76.5046 | 82.7953 | 89.5231 | 96.1456 | 102.7884
| KenoraWind2100RCP6.0 | Kenora | Wind | RCP6.0 | 2100 | 76.762 | 83.1392 | 89.9732 | 96.6854 | 103.4224
| KenoraWind2023RCP8.5 | Kenora | Wind | RCP8.5 | 2023 | 75.0838 | 81.0837 | 87.462 | 93.7776 | 100.0988
| KenoraWind2025RCP8.5 | Kenora | Wind | RCP8.5 | 2025 | 75.0961 | 81.0677 | 87.4047 | 93.6886 | 99.9779
| KenoraWind2030RCP8.5 | Kenora | Wind | RCP8.5 | 2030 | 75.1085 | 81.0517 | 87.3473 | 93.5997 | 99.857
| KenoraWind2035RCP8.5 | Kenora | Wind | RCP8.5 | 2035 | 75.1209 | 81.0357 | 87.29 | 93.5107 | 99.7361
| KenoraWind2040RCP8.5 | Kenora | Wind | RCP8.5 | 2040 | 75.2818 | 81.2384 | 87.5451 | 93.8113 | 100.0858
| KenoraWind2045RCP8.5 | Kenora | Wind | RCP8.5 | 2045 | 75.4427 | 81.441 | 87.8003 | 94.1119 | 100.4354
| KenoraWind2050RCP8.5 | Kenora | Wind | RCP8.5 | 2050 | 75.7323 | 81.7982 | 88.2446 | 94.6303 | 101.0302
| KenoraWind2055RCP8.5 | Kenora | Wind | RCP8.5 | 2055 | 75.861 | 81.9528 | 88.4338 | 94.8481 | 101.2753
| KenoraWind2060RCP8.5 | Kenora | Wind | RCP8.5 | 2060 | 76.2472 | 82.4514 | 89.0731 | 95.6057 | 102.1544
| KenoraWind2065RCP8.5 | Kenora | Wind | RCP8.5 | 2065 | 76.5046 | 82.7953 | 89.5231 | 96.1456 | 102.7884
| KenoraWind2070RCP8.5 | Kenora | Wind | RCP8.5 | 2070 | 76.9724 | 83.3925 | 90.2799 | 97.0382 | 103.8178
| KenoraWind2075RCP8.5 | Kenora | Wind | RCP8.5 | 2075 | 77.1828 | 83.6457 | 90.5867 | 97.3909 | 104.2133
| KenoraWind2080RCP8.5 | Kenora | Wind | RCP8.5 | 2080 | 77.3932 | 83.899 | 90.8934 | 97.7436 | 104.6087
| KenoraWind2085RCP8.5 | Kenora | Wind | RCP8.5 | 2085 | 77.4341 | 83.959 | 90.9751 | 97.8449 | 104.7312
| KenoraWind2090RCP8.5 | Kenora | Wind | RCP8.5 | 2090 | 77.4749 | 84.019 | 91.0568 | 97.9461 | 104.8538
| KenoraWind2095RCP8.5 | Kenora | Wind | RCP8.5 | 2095 | 77.4749 | 84.019 | 91.0568 | 97.9461 | 104.8538
| KenoraWind2100RCP8.5 | Kenora | Wind | RCP8.5 | 2100 | 77.4749 | 84.019 | 91.0568 | 97.9461 | 104.8538
| KillaloeIce Accretion2023RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2023 | 13.8613 | 16.4838 | 19.8 | 22.3288 | 24.8724
| KillaloeIce Accretion2025RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2025 | 13.9517 | 16.5972 | 19.94 | 22.4908 | 25.0572
| KillaloeIce Accretion2030RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2030 | 14.0422 | 16.7107 | 20.08 | 22.6527 | 25.242
| KillaloeIce Accretion2035RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2035 | 14.1326 | 16.8241 | 20.22 | 22.8147 | 25.4268
| KillaloeIce Accretion2040RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2040 | 14.2231 | 16.9375 | 20.36 | 22.9767 | 25.6116
| KillaloeIce Accretion2045RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2045 | 14.3136 | 17.051 | 20.5 | 23.1386 | 25.7964
| KillaloeIce Accretion2050RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2050 | 14.4068 | 17.181 | 20.676 | 23.3503 | 26.0417
| KillaloeIce Accretion2055RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2055 | 14.4096 | 17.1976 | 20.712 | 23.4 | 26.1022
| KillaloeIce Accretion2060RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2060 | 14.4124 | 17.2142 | 20.748 | 23.4498 | 26.1626
| KillaloeIce Accretion2065RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2065 | 14.4151 | 17.2308 | 20.784 | 23.4995 | 26.2231
| KillaloeIce Accretion2070RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2070 | 14.4179 | 17.2474 | 20.82 | 23.5492 | 26.2836
| KillaloeIce Accretion2075RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2075 | 14.4574 | 17.3027 | 20.9 | 23.6471 | 26.397
| KillaloeIce Accretion2080RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2080 | 14.4968 | 17.3581 | 20.98 | 23.7451 | 26.5104
| KillaloeIce Accretion2085RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2085 | 14.5362 | 17.4134 | 21.06 | 23.843 | 26.6238
| KillaloeIce Accretion2090RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2090 | 14.5757 | 17.4687 | 21.14 | 23.9409 | 26.7372
| KillaloeIce Accretion2095RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2095 | 14.6151 | 17.5241 | 21.22 | 24.0389 | 26.8506
| KillaloeIce Accretion2100RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2100 | 14.6545 | 17.5794 | 21.3 | 24.1368 | 26.964
| KillaloeIce Accretion2023RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2023 | 13.8613 | 16.4838 | 19.8 | 22.3288 | 24.8724
| KillaloeIce Accretion2025RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2025 | 13.9517 | 16.5972 | 19.94 | 22.4908 | 25.0572
| KillaloeIce Accretion2030RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2030 | 14.0422 | 16.7107 | 20.08 | 22.6527 | 25.242
| KillaloeIce Accretion2035RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2035 | 14.1326 | 16.8241 | 20.22 | 22.8147 | 25.4268
| KillaloeIce Accretion2040RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2040 | 14.2231 | 16.9375 | 20.36 | 22.9767 | 25.6116
| KillaloeIce Accretion2045RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2045 | 14.3136 | 17.051 | 20.5 | 23.1386 | 25.7964
| KillaloeIce Accretion2050RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2050 | 14.4068 | 17.181 | 20.676 | 23.3503 | 26.0417
| KillaloeIce Accretion2055RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2055 | 14.4096 | 17.1976 | 20.712 | 23.4 | 26.1022
| KillaloeIce Accretion2060RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2060 | 14.4124 | 17.2142 | 20.748 | 23.4498 | 26.1626
| KillaloeIce Accretion2065RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2065 | 14.4151 | 17.2308 | 20.784 | 23.4995 | 26.2231
| KillaloeIce Accretion2070RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2070 | 14.4179 | 17.2474 | 20.82 | 23.5492 | 26.2836
| KillaloeIce Accretion2075RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2075 | 14.4771 | 17.3304 | 20.94 | 23.6961 | 26.4537
| KillaloeIce Accretion2080RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2080 | 14.5362 | 17.4134 | 21.06 | 23.843 | 26.6238
| KillaloeIce Accretion2085RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2085 | 14.5954 | 17.4964 | 21.18 | 23.9899 | 26.7939
| KillaloeIce Accretion2090RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2090 | 14.5525 | 17.4687 | 21.18 | 24.0087 | 26.8296
| KillaloeIce Accretion2095RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2095 | 14.4504 | 17.3581 | 21.06 | 23.8807 | 26.6952
| KillaloeIce Accretion2100RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2100 | 14.3483 | 17.2474 | 20.94 | 23.7526 | 26.5608
| KillaloeIce Accretion2023RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2023 | 13.8613 | 16.4838 | 19.8 | 22.3288 | 24.8724
| KillaloeIce Accretion2025RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2025 | 14.0422 | 16.7107 | 20.08 | 22.6527 | 25.242
| KillaloeIce Accretion2030RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2030 | 14.2231 | 16.9375 | 20.36 | 22.9767 | 25.6116
| KillaloeIce Accretion2035RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2035 | 14.404 | 17.1644 | 20.64 | 23.3006 | 25.9812
| KillaloeIce Accretion2040RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2040 | 14.4087 | 17.1921 | 20.7 | 23.3835 | 26.082
| KillaloeIce Accretion2045RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2045 | 14.4133 | 17.2197 | 20.76 | 23.4663 | 26.1828
| KillaloeIce Accretion2050RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2050 | 14.4968 | 17.3581 | 20.98 | 23.7451 | 26.5104
| KillaloeIce Accretion2055RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2055 | 14.5757 | 17.4687 | 21.14 | 23.9409 | 26.7372
| KillaloeIce Accretion2060RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2060 | 14.5525 | 17.4687 | 21.18 | 24.0087 | 26.8296
| KillaloeIce Accretion2065RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2065 | 14.4504 | 17.3581 | 21.06 | 23.8807 | 26.6952
| KillaloeIce Accretion2070RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2070 | 14.302 | 17.2253 | 20.9333 | 23.7601 | 26.586
| KillaloeIce Accretion2075RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2075 | 14.2556 | 17.2031 | 20.9267 | 23.7677 | 26.6112
| KillaloeIce Accretion2080RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2080 | 14.2092 | 17.181 | 20.92 | 23.7752 | 26.6364
| KillaloeIce Accretion2085RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2085 | 13.9448 | 16.9071 | 20.64 | 23.4927 | 26.334
| KillaloeIce Accretion2090RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2090 | 13.6803 | 16.6332 | 20.36 | 23.2102 | 26.0316
| KillaloeIce Accretion2095RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2095 | 13.6803 | 16.6332 | 20.36 | 23.2102 | 26.0316
| KillaloeIce Accretion2100RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2100 | 13.6803 | 16.6332 | 20.36 | 23.2102 | 26.0316
| KillaloeWind2023RCP4.5 | Killaloe | Wind | RCP4.5 | 2023 | 69.4033 | 74.7869 | 80.464 | 86.1307 | 91.7928
| KillaloeWind2025RCP4.5 | Killaloe | Wind | RCP4.5 | 2025 | 69.4965 | 74.9047 | 80.612 | 86.3048 | 91.995
| KillaloeWind2030RCP4.5 | Killaloe | Wind | RCP4.5 | 2030 | 69.5898 | 75.0225 | 80.76 | 86.4788 | 92.1971
| KillaloeWind2035RCP4.5 | Killaloe | Wind | RCP4.5 | 2035 | 69.683 | 75.1403 | 80.908 | 86.6529 | 92.3993
| KillaloeWind2040RCP4.5 | Killaloe | Wind | RCP4.5 | 2040 | 69.7763 | 75.2581 | 81.056 | 86.8269 | 92.6014
| KillaloeWind2045RCP4.5 | Killaloe | Wind | RCP4.5 | 2045 | 69.8695 | 75.3759 | 81.204 | 87.001 | 92.8036
| KillaloeWind2050RCP4.5 | Killaloe | Wind | RCP4.5 | 2050 | 69.9835 | 75.519 | 81.384 | 87.211 | 93.0441
| KillaloeWind2055RCP4.5 | Killaloe | Wind | RCP4.5 | 2055 | 70.0042 | 75.5443 | 81.416 | 87.2469 | 93.0824
| KillaloeWind2060RCP4.5 | Killaloe | Wind | RCP4.5 | 2060 | 70.025 | 75.5696 | 81.448 | 87.2829 | 93.1207
| KillaloeWind2065RCP4.5 | Killaloe | Wind | RCP4.5 | 2065 | 70.0457 | 75.5949 | 81.48 | 87.3188 | 93.159
| KillaloeWind2070RCP4.5 | Killaloe | Wind | RCP4.5 | 2070 | 70.0664 | 75.6202 | 81.512 | 87.3548 | 93.1973
| KillaloeWind2075RCP4.5 | Killaloe | Wind | RCP4.5 | 2075 | 70.0894 | 75.6549 | 81.5587 | 87.4133 | 93.2687
| KillaloeWind2080RCP4.5 | Killaloe | Wind | RCP4.5 | 2080 | 70.1125 | 75.6896 | 81.6053 | 87.4718 | 93.3402
| KillaloeWind2085RCP4.5 | Killaloe | Wind | RCP4.5 | 2085 | 70.1355 | 75.7243 | 81.652 | 87.5303 | 93.4116
| KillaloeWind2090RCP4.5 | Killaloe | Wind | RCP4.5 | 2090 | 70.1585 | 75.759 | 81.6987 | 87.5888 | 93.483
| KillaloeWind2095RCP4.5 | Killaloe | Wind | RCP4.5 | 2095 | 70.1815 | 75.7938 | 81.7453 | 87.6473 | 93.5545
| KillaloeWind2100RCP4.5 | Killaloe | Wind | RCP4.5 | 2100 | 70.2046 | 75.8285 | 81.792 | 87.7058 | 93.6259
| KillaloeWind2023RCP6.0 | Killaloe | Wind | RCP6.0 | 2023 | 69.4033 | 74.7869 | 80.464 | 86.1307 | 91.7928
| KillaloeWind2025RCP6.0 | Killaloe | Wind | RCP6.0 | 2025 | 69.4965 | 74.9047 | 80.612 | 86.3048 | 91.995
| KillaloeWind2030RCP6.0 | Killaloe | Wind | RCP6.0 | 2030 | 69.5898 | 75.0225 | 80.76 | 86.4788 | 92.1971
| KillaloeWind2035RCP6.0 | Killaloe | Wind | RCP6.0 | 2035 | 69.683 | 75.1403 | 80.908 | 86.6529 | 92.3993
| KillaloeWind2040RCP6.0 | Killaloe | Wind | RCP6.0 | 2040 | 69.7763 | 75.2581 | 81.056 | 86.8269 | 92.6014
| KillaloeWind2045RCP6.0 | Killaloe | Wind | RCP6.0 | 2045 | 69.8695 | 75.3759 | 81.204 | 87.001 | 92.8036
| KillaloeWind2050RCP6.0 | Killaloe | Wind | RCP6.0 | 2050 | 69.9835 | 75.519 | 81.384 | 87.211 | 93.0441
| KillaloeWind2055RCP6.0 | Killaloe | Wind | RCP6.0 | 2055 | 70.0042 | 75.5443 | 81.416 | 87.2469 | 93.0824
| KillaloeWind2060RCP6.0 | Killaloe | Wind | RCP6.0 | 2060 | 70.025 | 75.5696 | 81.448 | 87.2829 | 93.1207
| KillaloeWind2065RCP6.0 | Killaloe | Wind | RCP6.0 | 2065 | 70.0457 | 75.5949 | 81.48 | 87.3188 | 93.159
| KillaloeWind2070RCP6.0 | Killaloe | Wind | RCP6.0 | 2070 | 70.0664 | 75.6202 | 81.512 | 87.3548 | 93.1973
| KillaloeWind2075RCP6.0 | Killaloe | Wind | RCP6.0 | 2075 | 70.101 | 75.6722 | 81.582 | 87.4425 | 93.3044
| KillaloeWind2080RCP6.0 | Killaloe | Wind | RCP6.0 | 2080 | 70.1355 | 75.7243 | 81.652 | 87.5303 | 93.4116
| KillaloeWind2085RCP6.0 | Killaloe | Wind | RCP6.0 | 2085 | 70.17 | 75.7764 | 81.722 | 87.618 | 93.5188
| KillaloeWind2090RCP6.0 | Killaloe | Wind | RCP6.0 | 2090 | 70.2161 | 75.826 | 81.776 | 87.6744 | 93.5834
| KillaloeWind2095RCP6.0 | Killaloe | Wind | RCP6.0 | 2095 | 70.2276 | 75.8235 | 81.76 | 87.643 | 93.5408
| KillaloeWind2100RCP6.0 | Killaloe | Wind | RCP6.0 | 2100 | 70.2391 | 75.821 | 81.744 | 87.6116 | 93.4982
| KillaloeWind2023RCP8.5 | Killaloe | Wind | RCP8.5 | 2023 | 69.4033 | 74.7869 | 80.464 | 86.1307 | 91.7928
| KillaloeWind2025RCP8.5 | Killaloe | Wind | RCP8.5 | 2025 | 69.5898 | 75.0225 | 80.76 | 86.4788 | 92.1971
| KillaloeWind2030RCP8.5 | Killaloe | Wind | RCP8.5 | 2030 | 69.7763 | 75.2581 | 81.056 | 86.8269 | 92.6014
| KillaloeWind2035RCP8.5 | Killaloe | Wind | RCP8.5 | 2035 | 69.9628 | 75.4937 | 81.352 | 87.175 | 93.0058
| KillaloeWind2040RCP8.5 | Killaloe | Wind | RCP8.5 | 2040 | 69.9973 | 75.5358 | 81.4053 | 87.235 | 93.0696
| KillaloeWind2045RCP8.5 | Killaloe | Wind | RCP8.5 | 2045 | 70.0319 | 75.578 | 81.4587 | 87.2949 | 93.1334
| KillaloeWind2050RCP8.5 | Killaloe | Wind | RCP8.5 | 2050 | 70.1125 | 75.6896 | 81.6053 | 87.4718 | 93.3402
| KillaloeWind2055RCP8.5 | Killaloe | Wind | RCP8.5 | 2055 | 70.1585 | 75.759 | 81.6987 | 87.5888 | 93.483
| KillaloeWind2060RCP8.5 | Killaloe | Wind | RCP8.5 | 2060 | 70.2161 | 75.826 | 81.776 | 87.6744 | 93.5834
| KillaloeWind2065RCP8.5 | Killaloe | Wind | RCP8.5 | 2065 | 70.2276 | 75.8235 | 81.76 | 87.643 | 93.5408
| KillaloeWind2070RCP8.5 | Killaloe | Wind | RCP8.5 | 2070 | 70.2345 | 75.7789 | 81.6533 | 87.4861 | 93.331
| KillaloeWind2075RCP8.5 | Killaloe | Wind | RCP8.5 | 2075 | 70.2299 | 75.7367 | 81.5627 | 87.3605 | 93.1638
| KillaloeWind2080RCP8.5 | Killaloe | Wind | RCP8.5 | 2080 | 70.2253 | 75.6946 | 81.472 | 87.235 | 92.9966
| KillaloeWind2085RCP8.5 | Killaloe | Wind | RCP8.5 | 2085 | 70.2564 | 75.7206 | 81.492 | 87.2478 | 93.0012
| KillaloeWind2090RCP8.5 | Killaloe | Wind | RCP8.5 | 2090 | 70.2875 | 75.7466 | 81.512 | 87.2606 | 93.0058
| KillaloeWind2095RCP8.5 | Killaloe | Wind | RCP8.5 | 2095 | 70.2875 | 75.7466 | 81.512 | 87.2606 | 93.0058
| KillaloeWind2100RCP8.5 | Killaloe | Wind | RCP8.5 | 2100 | 70.2875 | 75.7466 | 81.512 | 87.2606 | 93.0058
| KincardineIce Accretion2023RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2023 | 14.0283 | 16.8324 | 20.36 | 23.0746 | 25.7544
| KincardineIce Accretion2025RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2025 | 14.0561 | 16.8767 | 20.4267 | 23.1537 | 25.851
| KincardineIce Accretion2030RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2030 | 14.0839 | 16.9209 | 20.4933 | 23.2328 | 25.9476
| KincardineIce Accretion2035RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2035 | 14.1118 | 16.9652 | 20.56 | 23.3119 | 26.0442
| KincardineIce Accretion2040RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2040 | 14.1396 | 17.0095 | 20.6267 | 23.391 | 26.1408
| KincardineIce Accretion2045RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2045 | 14.1674 | 17.0537 | 20.6933 | 23.4701 | 26.2374
| KincardineIce Accretion2050RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2050 | 14.1006 | 17.005 | 20.672 | 23.4633 | 26.2534
| KincardineIce Accretion2055RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2055 | 14.006 | 16.9121 | 20.584 | 23.3774 | 26.1727
| KincardineIce Accretion2060RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2060 | 13.9114 | 16.8191 | 20.496 | 23.2916 | 26.0921
| KincardineIce Accretion2065RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2065 | 13.8167 | 16.7262 | 20.408 | 23.2057 | 26.0114
| KincardineIce Accretion2070RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2070 | 13.7221 | 16.6332 | 20.32 | 23.1198 | 25.9308
| KincardineIce Accretion2075RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2075 | 13.6131 | 16.5198 | 20.2 | 22.9955 | 25.8006
| KincardineIce Accretion2080RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2080 | 13.5041 | 16.4063 | 20.08 | 22.8712 | 25.6704
| KincardineIce Accretion2085RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2085 | 13.395 | 16.2929 | 19.96 | 22.7469 | 25.5402
| KincardineIce Accretion2090RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2090 | 13.286 | 16.1795 | 19.84 | 22.6226 | 25.41
| KincardineIce Accretion2095RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2095 | 13.177 | 16.066 | 19.72 | 22.4983 | 25.2798
| KincardineIce Accretion2100RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2100 | 13.068 | 15.9526 | 19.6 | 22.374 | 25.1496
| KincardineIce Accretion2023RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2023 | 14.0283 | 16.8324 | 20.36 | 23.0746 | 25.7544
| KincardineIce Accretion2025RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2025 | 14.0561 | 16.8767 | 20.4267 | 23.1537 | 25.851
| KincardineIce Accretion2030RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2030 | 14.0839 | 16.9209 | 20.4933 | 23.2328 | 25.9476
| KincardineIce Accretion2035RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2035 | 14.1118 | 16.9652 | 20.56 | 23.3119 | 26.0442
| KincardineIce Accretion2040RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2040 | 14.1396 | 17.0095 | 20.6267 | 23.391 | 26.1408
| KincardineIce Accretion2045RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2045 | 14.1674 | 17.0537 | 20.6933 | 23.4701 | 26.2374
| KincardineIce Accretion2050RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2050 | 14.1006 | 17.005 | 20.672 | 23.4633 | 26.2534
| KincardineIce Accretion2055RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2055 | 14.006 | 16.9121 | 20.584 | 23.3774 | 26.1727
| KincardineIce Accretion2060RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2060 | 13.9114 | 16.8191 | 20.496 | 23.2916 | 26.0921
| KincardineIce Accretion2065RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2065 | 13.8167 | 16.7262 | 20.408 | 23.2057 | 26.0114
| KincardineIce Accretion2070RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2070 | 13.7221 | 16.6332 | 20.32 | 23.1198 | 25.9308
| KincardineIce Accretion2075RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2075 | 13.5586 | 16.463 | 20.14 | 22.9333 | 25.7355
| KincardineIce Accretion2080RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2080 | 13.395 | 16.2929 | 19.96 | 22.7469 | 25.5402
| KincardineIce Accretion2085RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2085 | 13.2315 | 16.1227 | 19.78 | 22.5604 | 25.3449
| KincardineIce Accretion2090RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2090 | 12.6412 | 15.4657 | 19.0267 | 21.7412 | 24.444
| KincardineIce Accretion2095RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2095 | 12.2144 | 14.9787 | 18.4533 | 21.1084 | 23.7384
| KincardineIce Accretion2100RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2100 | 11.7876 | 14.4918 | 17.88 | 20.4756 | 23.0328
| KincardineIce Accretion2023RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2023 | 14.0283 | 16.8324 | 20.36 | 23.0746 | 25.7544
| KincardineIce Accretion2025RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2025 | 14.0839 | 16.9209 | 20.4933 | 23.2328 | 25.9476
| KincardineIce Accretion2030RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2030 | 14.1396 | 17.0095 | 20.6267 | 23.391 | 26.1408
| KincardineIce Accretion2035RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2035 | 14.1953 | 17.098 | 20.76 | 23.5492 | 26.334
| KincardineIce Accretion2040RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2040 | 14.0375 | 16.9431 | 20.6133 | 23.4061 | 26.1996
| KincardineIce Accretion2045RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2045 | 13.8798 | 16.7881 | 20.4667 | 23.2629 | 26.0652
| KincardineIce Accretion2050RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2050 | 13.5041 | 16.4063 | 20.08 | 22.8712 | 25.6704
| KincardineIce Accretion2055RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2055 | 13.286 | 16.1795 | 19.84 | 22.6226 | 25.41
| KincardineIce Accretion2060RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2060 | 12.6412 | 15.4657 | 19.0267 | 21.7412 | 24.444
| KincardineIce Accretion2065RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2065 | 12.2144 | 14.9787 | 18.4533 | 21.1084 | 23.7384
| KincardineIce Accretion2070RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2070 | 11.333 | 13.9717 | 17.28 | 19.8051 | 22.302
| KincardineIce Accretion2075RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2075 | 10.8784 | 13.4515 | 16.68 | 19.1347 | 21.5712
| KincardineIce Accretion2080RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2080 | 10.4238 | 12.9314 | 16.08 | 18.4642 | 20.8404
| KincardineIce Accretion2085RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2085 | 9.9019 | 12.3255 | 15.36 | 17.6619 | 19.9584
| KincardineIce Accretion2090RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2090 | 9.38 | 11.7196 | 14.64 | 16.8596 | 19.0764
| KincardineIce Accretion2095RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2095 | 9.38 | 11.7196 | 14.64 | 16.8596 | 19.0764
| KincardineIce Accretion2100RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2100 | 9.38 | 11.7196 | 14.64 | 16.8596 | 19.0764
| KincardineWind2023RCP4.5 | Kincardine | Wind | RCP4.5 | 2023 | 86.3225 | 93.1196 | 100.3167 | 107.4766 | 114.6432
| KincardineWind2025RCP4.5 | Kincardine | Wind | RCP4.5 | 2025 | 86.4422 | 93.2608 | 100.485 | 107.669 | 114.8595
| KincardineWind2030RCP4.5 | Kincardine | Wind | RCP4.5 | 2030 | 86.5619 | 93.4019 | 100.6533 | 107.8615 | 115.0758
| KincardineWind2035RCP4.5 | Kincardine | Wind | RCP4.5 | 2035 | 86.6815 | 93.5431 | 100.8216 | 108.0539 | 115.2921
| KincardineWind2040RCP4.5 | Kincardine | Wind | RCP4.5 | 2040 | 86.8012 | 93.6843 | 100.9899 | 108.2463 | 115.5084
| KincardineWind2045RCP4.5 | Kincardine | Wind | RCP4.5 | 2045 | 86.9209 | 93.8255 | 101.1582 | 108.4388 | 115.7248
| KincardineWind2050RCP4.5 | Kincardine | Wind | RCP4.5 | 2050 | 87.0611 | 93.9832 | 101.3344 | 108.6312 | 115.9366
| KincardineWind2055RCP4.5 | Kincardine | Wind | RCP4.5 | 2055 | 87.0816 | 93.9998 | 101.3423 | 108.6312 | 115.932
| KincardineWind2060RCP4.5 | Kincardine | Wind | RCP4.5 | 2060 | 87.1021 | 94.0164 | 101.3503 | 108.6312 | 115.9275
| KincardineWind2065RCP4.5 | Kincardine | Wind | RCP4.5 | 2065 | 87.1226 | 94.0329 | 101.3582 | 108.6312 | 115.923
| KincardineWind2070RCP4.5 | Kincardine | Wind | RCP4.5 | 2070 | 87.1432 | 94.0495 | 101.3661 | 108.6312 | 115.9185
| KincardineWind2075RCP4.5 | Kincardine | Wind | RCP4.5 | 2075 | 87.2557 | 94.1968 | 101.5559 | 108.859 | 116.1818
| KincardineWind2080RCP4.5 | Kincardine | Wind | RCP4.5 | 2080 | 87.3683 | 94.3441 | 101.7456 | 109.0867 | 116.4452
| KincardineWind2085RCP4.5 | Kincardine | Wind | RCP4.5 | 2085 | 87.4808 | 94.4914 | 101.9353 | 109.3145 | 116.7085
| KincardineWind2090RCP4.5 | Kincardine | Wind | RCP4.5 | 2090 | 87.5934 | 94.6388 | 102.1251 | 109.5422 | 116.9719
| KincardineWind2095RCP4.5 | Kincardine | Wind | RCP4.5 | 2095 | 87.7059 | 94.7861 | 102.3149 | 109.77 | 117.2352
| KincardineWind2100RCP4.5 | Kincardine | Wind | RCP4.5 | 2100 | 87.8185 | 94.9334 | 102.5046 | 109.9977 | 117.4985
| KincardineWind2023RCP6.0 | Kincardine | Wind | RCP6.0 | 2023 | 86.3225 | 93.1196 | 100.3167 | 107.4766 | 114.6432
| KincardineWind2025RCP6.0 | Kincardine | Wind | RCP6.0 | 2025 | 86.4422 | 93.2608 | 100.485 | 107.669 | 114.8595
| KincardineWind2030RCP6.0 | Kincardine | Wind | RCP6.0 | 2030 | 86.5619 | 93.4019 | 100.6533 | 107.8615 | 115.0758
| KincardineWind2035RCP6.0 | Kincardine | Wind | RCP6.0 | 2035 | 86.6815 | 93.5431 | 100.8216 | 108.0539 | 115.2921
| KincardineWind2040RCP6.0 | Kincardine | Wind | RCP6.0 | 2040 | 86.8012 | 93.6843 | 100.9899 | 108.2463 | 115.5084
| KincardineWind2045RCP6.0 | Kincardine | Wind | RCP6.0 | 2045 | 86.9209 | 93.8255 | 101.1582 | 108.4388 | 115.7248
| KincardineWind2050RCP6.0 | Kincardine | Wind | RCP6.0 | 2050 | 87.0611 | 93.9832 | 101.3344 | 108.6312 | 115.9366
| KincardineWind2055RCP6.0 | Kincardine | Wind | RCP6.0 | 2055 | 87.0816 | 93.9998 | 101.3423 | 108.6312 | 115.932
| KincardineWind2060RCP6.0 | Kincardine | Wind | RCP6.0 | 2060 | 87.1021 | 94.0164 | 101.3503 | 108.6312 | 115.9275
| KincardineWind2065RCP6.0 | Kincardine | Wind | RCP6.0 | 2065 | 87.1226 | 94.0329 | 101.3582 | 108.6312 | 115.923
| KincardineWind2070RCP6.0 | Kincardine | Wind | RCP6.0 | 2070 | 87.1432 | 94.0495 | 101.3661 | 108.6312 | 115.9185
| KincardineWind2075RCP6.0 | Kincardine | Wind | RCP6.0 | 2075 | 87.312 | 94.2705 | 101.6507 | 108.9728 | 116.3135
| KincardineWind2080RCP6.0 | Kincardine | Wind | RCP6.0 | 2080 | 87.4808 | 94.4914 | 101.9353 | 109.3145 | 116.7085
| KincardineWind2085RCP6.0 | Kincardine | Wind | RCP6.0 | 2085 | 87.6497 | 94.7124 | 102.22 | 109.6561 | 117.1035
| KincardineWind2090RCP6.0 | Kincardine | Wind | RCP6.0 | 2090 | 88.1376 | 95.3231 | 102.9864 | 110.5591 | 118.1381
| KincardineWind2095RCP6.0 | Kincardine | Wind | RCP6.0 | 2095 | 88.4568 | 95.7129 | 103.4682 | 111.1206 | 118.7776
| KincardineWind2100RCP6.0 | Kincardine | Wind | RCP6.0 | 2100 | 88.7759 | 96.1027 | 103.95 | 111.682 | 119.4172
| KincardineWind2023RCP8.5 | Kincardine | Wind | RCP8.5 | 2023 | 86.3225 | 93.1196 | 100.3167 | 107.4766 | 114.6432
| KincardineWind2025RCP8.5 | Kincardine | Wind | RCP8.5 | 2025 | 86.5619 | 93.4019 | 100.6533 | 107.8615 | 115.0758
| KincardineWind2030RCP8.5 | Kincardine | Wind | RCP8.5 | 2030 | 86.8012 | 93.6843 | 100.9899 | 108.2463 | 115.5084
| KincardineWind2035RCP8.5 | Kincardine | Wind | RCP8.5 | 2035 | 87.0406 | 93.9666 | 101.3265 | 108.6312 | 115.9411
| KincardineWind2040RCP8.5 | Kincardine | Wind | RCP8.5 | 2040 | 87.0748 | 93.9943 | 101.3397 | 108.6312 | 115.9336
| KincardineWind2045RCP8.5 | Kincardine | Wind | RCP8.5 | 2045 | 87.109 | 94.0219 | 101.3529 | 108.6312 | 115.926
| KincardineWind2050RCP8.5 | Kincardine | Wind | RCP8.5 | 2050 | 87.3683 | 94.3441 | 101.7456 | 109.0867 | 116.4452
| KincardineWind2055RCP8.5 | Kincardine | Wind | RCP8.5 | 2055 | 87.5934 | 94.6388 | 102.1251 | 109.5422 | 116.9719
| KincardineWind2060RCP8.5 | Kincardine | Wind | RCP8.5 | 2060 | 88.1376 | 95.3231 | 102.9864 | 110.5591 | 118.1381
| KincardineWind2065RCP8.5 | Kincardine | Wind | RCP8.5 | 2065 | 88.4568 | 95.7129 | 103.4682 | 111.1206 | 118.7776
| KincardineWind2070RCP8.5 | Kincardine | Wind | RCP8.5 | 2070 | 88.9326 | 96.2868 | 104.1645 | 111.9186 | 119.6843
| KincardineWind2075RCP8.5 | Kincardine | Wind | RCP8.5 | 2075 | 89.0894 | 96.4709 | 104.379 | 112.1552 | 119.9514
| KincardineWind2080RCP8.5 | Kincardine | Wind | RCP8.5 | 2080 | 89.2461 | 96.6551 | 104.5935 | 112.3917 | 120.2185
| KincardineWind2085RCP8.5 | Kincardine | Wind | RCP8.5 | 2085 | 89.4513 | 96.8991 | 104.8855 | 112.7307 | 120.5966
| KincardineWind2090RCP8.5 | Kincardine | Wind | RCP8.5 | 2090 | 89.6564 | 97.1431 | 105.1776 | 113.0697 | 120.9746
| KincardineWind2095RCP8.5 | Kincardine | Wind | RCP8.5 | 2095 | 89.6564 | 97.1431 | 105.1776 | 113.0697 | 120.9746
| KincardineWind2100RCP8.5 | Kincardine | Wind | RCP8.5 | 2100 | 89.6564 | 97.1431 | 105.1776 | 113.0697 | 120.9746
| KingstonIce Accretion2023RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2023 | 19.4837 | 23.2168 | 27.972 | 31.6084 | 35.2094
| KingstonIce Accretion2025RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2025 | 19.5649 | 23.3291 | 28.1213 | 31.7824 | 35.4152
| KingstonIce Accretion2030RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2030 | 19.6461 | 23.4414 | 28.2707 | 31.9564 | 35.621
| KingstonIce Accretion2035RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2035 | 19.7272 | 23.5537 | 28.42 | 32.1304 | 35.8268
| KingstonIce Accretion2040RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2040 | 19.8084 | 23.6661 | 28.5693 | 32.3044 | 36.0326
| KingstonIce Accretion2045RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2045 | 19.8896 | 23.7784 | 28.7187 | 32.4785 | 36.2384
| KingstonIce Accretion2050RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2050 | 19.8617 | 23.7792 | 28.7504 | 32.5322 | 36.3243
| KingstonIce Accretion2055RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2055 | 19.7526 | 23.6676 | 28.6328 | 32.412 | 36.2043
| KingstonIce Accretion2060RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2060 | 19.6435 | 23.5561 | 28.5152 | 32.2918 | 36.0844
| KingstonIce Accretion2065RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2065 | 19.5343 | 23.4445 | 28.3976 | 32.1716 | 35.9644
| KingstonIce Accretion2070RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2070 | 19.4252 | 23.333 | 28.28 | 32.0513 | 35.8445
| KingstonIce Accretion2075RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2075 | 19.4382 | 23.3756 | 28.3547 | 32.1515 | 35.968
| KingstonIce Accretion2080RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2080 | 19.4512 | 23.4182 | 28.4293 | 32.2517 | 36.0914
| KingstonIce Accretion2085RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2085 | 19.4642 | 23.4608 | 28.504 | 32.3519 | 36.2149
| KingstonIce Accretion2090RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2090 | 19.4772 | 23.5034 | 28.5787 | 32.4521 | 36.3384
| KingstonIce Accretion2095RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2095 | 19.4902 | 23.546 | 28.6533 | 32.5523 | 36.4619
| KingstonIce Accretion2100RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2100 | 19.5032 | 23.5886 | 28.728 | 32.6525 | 36.5854
| KingstonIce Accretion2023RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2023 | 19.4837 | 23.2168 | 27.972 | 31.6084 | 35.2094
| KingstonIce Accretion2025RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2025 | 19.5649 | 23.3291 | 28.1213 | 31.7824 | 35.4152
| KingstonIce Accretion2030RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2030 | 19.6461 | 23.4414 | 28.2707 | 31.9564 | 35.621
| KingstonIce Accretion2035RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2035 | 19.7272 | 23.5537 | 28.42 | 32.1304 | 35.8268
| KingstonIce Accretion2040RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2040 | 19.8084 | 23.6661 | 28.5693 | 32.3044 | 36.0326
| KingstonIce Accretion2045RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2045 | 19.8896 | 23.7784 | 28.7187 | 32.4785 | 36.2384
| KingstonIce Accretion2050RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2050 | 19.8617 | 23.7792 | 28.7504 | 32.5322 | 36.3243
| KingstonIce Accretion2055RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2055 | 19.7526 | 23.6676 | 28.6328 | 32.412 | 36.2043
| KingstonIce Accretion2060RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2060 | 19.6435 | 23.5561 | 28.5152 | 32.2918 | 36.0844
| KingstonIce Accretion2065RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2065 | 19.5343 | 23.4445 | 28.3976 | 32.1716 | 35.9644
| KingstonIce Accretion2070RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2070 | 19.4252 | 23.333 | 28.28 | 32.0513 | 35.8445
| KingstonIce Accretion2075RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2075 | 19.4447 | 23.3969 | 28.392 | 32.2016 | 36.0297
| KingstonIce Accretion2080RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2080 | 19.4642 | 23.4608 | 28.504 | 32.3519 | 36.2149
| KingstonIce Accretion2085RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2085 | 19.4837 | 23.5247 | 28.616 | 32.5022 | 36.4001
| KingstonIce Accretion2090RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2090 | 19.172 | 23.2168 | 28.3173 | 32.199 | 36.0914
| KingstonIce Accretion2095RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2095 | 18.8407 | 22.8449 | 27.9067 | 31.7455 | 35.5975
| KingstonIce Accretion2100RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2100 | 18.5095 | 22.4731 | 27.496 | 31.292 | 35.1036
| KingstonIce Accretion2023RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2023 | 19.4837 | 23.2168 | 27.972 | 31.6084 | 35.2094
| KingstonIce Accretion2025RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2025 | 19.6461 | 23.4414 | 28.2707 | 31.9564 | 35.621
| KingstonIce Accretion2030RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2030 | 19.8084 | 23.6661 | 28.5693 | 32.3044 | 36.0326
| KingstonIce Accretion2035RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2035 | 19.9708 | 23.8907 | 28.868 | 32.6525 | 36.4442
| KingstonIce Accretion2040RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2040 | 19.7889 | 23.7048 | 28.672 | 32.4521 | 36.2443
| KingstonIce Accretion2045RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2045 | 19.6071 | 23.5189 | 28.476 | 32.2517 | 36.0444
| KingstonIce Accretion2050RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2050 | 19.4512 | 23.4182 | 28.4293 | 32.2517 | 36.0914
| KingstonIce Accretion2055RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2055 | 19.4772 | 23.5034 | 28.5787 | 32.4521 | 36.3384
| KingstonIce Accretion2060RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2060 | 19.172 | 23.2168 | 28.3173 | 32.199 | 36.0914
| KingstonIce Accretion2065RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2065 | 18.8407 | 22.8449 | 27.9067 | 31.7455 | 35.5975
| KingstonIce Accretion2070RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2070 | 18.2432 | 22.1942 | 27.188 | 30.9756 | 34.7626
| KingstonIce Accretion2075RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2075 | 17.977 | 21.9153 | 26.88 | 30.6592 | 34.4215
| KingstonIce Accretion2080RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2080 | 17.7107 | 21.6364 | 26.572 | 30.3428 | 34.0805
| KingstonIce Accretion2085RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2085 | 17.0482 | 20.8579 | 25.648 | 29.2986 | 32.9162
| KingstonIce Accretion2090RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2090 | 16.3858 | 20.0794 | 24.724 | 28.2545 | 31.752
| KingstonIce Accretion2095RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2095 | 16.3858 | 20.0794 | 24.724 | 28.2545 | 31.752
| KingstonIce Accretion2100RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2100 | 16.3858 | 20.0794 | 24.724 | 28.2545 | 31.752
| KingstonWind2023RCP4.5 | Kingston | Wind | RCP4.5 | 2023 | 87.8991 | 94.5754 | 101.592 | 108.627 | 115.6637
| KingstonWind2025RCP4.5 | Kingston | Wind | RCP4.5 | 2025 | 87.8829 | 94.547 | 101.5444 | 108.5652 | 115.5862
| KingstonWind2030RCP4.5 | Kingston | Wind | RCP4.5 | 2030 | 87.8668 | 94.5185 | 101.4968 | 108.5033 | 115.5087
| KingstonWind2035RCP4.5 | Kingston | Wind | RCP4.5 | 2035 | 87.8506 | 94.49 | 101.4492 | 108.4415 | 115.4312
| KingstonWind2040RCP4.5 | Kingston | Wind | RCP4.5 | 2040 | 87.8345 | 94.4616 | 101.4016 | 108.3797 | 115.3536
| KingstonWind2045RCP4.5 | Kingston | Wind | RCP4.5 | 2045 | 87.8183 | 94.4331 | 101.354 | 108.3178 | 115.2761
| KingstonWind2050RCP4.5 | Kingston | Wind | RCP4.5 | 2050 | 87.9131 | 94.5394 | 101.4716 | 108.4459 | 115.4149
| KingstonWind2055RCP4.5 | Kingston | Wind | RCP4.5 | 2055 | 88.0241 | 94.6741 | 101.6369 | 108.6358 | 115.6312
| KingstonWind2060RCP4.5 | Kingston | Wind | RCP4.5 | 2060 | 88.1351 | 94.8088 | 101.8021 | 108.8257 | 115.8474
| KingstonWind2065RCP4.5 | Kingston | Wind | RCP4.5 | 2065 | 88.2461 | 94.9435 | 101.9674 | 109.0156 | 116.0637
| KingstonWind2070RCP4.5 | Kingston | Wind | RCP4.5 | 2070 | 88.357 | 95.0782 | 102.1326 | 109.2055 | 116.28
| KingstonWind2075RCP4.5 | Kingston | Wind | RCP4.5 | 2075 | 88.4774 | 95.2426 | 102.3502 | 109.4674 | 116.5862
| KingstonWind2080RCP4.5 | Kingston | Wind | RCP4.5 | 2080 | 88.5978 | 95.407 | 102.5678 | 109.7294 | 116.8924
| KingstonWind2085RCP4.5 | Kingston | Wind | RCP4.5 | 2085 | 88.7182 | 95.5714 | 102.7854 | 109.9913 | 117.1986
| KingstonWind2090RCP4.5 | Kingston | Wind | RCP4.5 | 2090 | 88.8385 | 95.7359 | 103.003 | 110.2532 | 117.5048
| KingstonWind2095RCP4.5 | Kingston | Wind | RCP4.5 | 2095 | 88.9589 | 95.9003 | 103.2206 | 110.5152 | 117.811
| KingstonWind2100RCP4.5 | Kingston | Wind | RCP4.5 | 2100 | 89.0793 | 96.0647 | 103.4382 | 110.7771 | 118.1172
| KingstonWind2023RCP6.0 | Kingston | Wind | RCP6.0 | 2023 | 87.8991 | 94.5754 | 101.592 | 108.627 | 115.6637
| KingstonWind2025RCP6.0 | Kingston | Wind | RCP6.0 | 2025 | 87.8829 | 94.547 | 101.5444 | 108.5652 | 115.5862
| KingstonWind2030RCP6.0 | Kingston | Wind | RCP6.0 | 2030 | 87.8668 | 94.5185 | 101.4968 | 108.5033 | 115.5087
| KingstonWind2035RCP6.0 | Kingston | Wind | RCP6.0 | 2035 | 87.8506 | 94.49 | 101.4492 | 108.4415 | 115.4312
| KingstonWind2040RCP6.0 | Kingston | Wind | RCP6.0 | 2040 | 87.8345 | 94.4616 | 101.4016 | 108.3797 | 115.3536
| KingstonWind2045RCP6.0 | Kingston | Wind | RCP6.0 | 2045 | 87.8183 | 94.4331 | 101.354 | 108.3178 | 115.2761
| KingstonWind2050RCP6.0 | Kingston | Wind | RCP6.0 | 2050 | 87.9131 | 94.5394 | 101.4716 | 108.4459 | 115.4149
| KingstonWind2055RCP6.0 | Kingston | Wind | RCP6.0 | 2055 | 88.0241 | 94.6741 | 101.6369 | 108.6358 | 115.6312
| KingstonWind2060RCP6.0 | Kingston | Wind | RCP6.0 | 2060 | 88.1351 | 94.8088 | 101.8021 | 108.8257 | 115.8474
| KingstonWind2065RCP6.0 | Kingston | Wind | RCP6.0 | 2065 | 88.2461 | 94.9435 | 101.9674 | 109.0156 | 116.0637
| KingstonWind2070RCP6.0 | Kingston | Wind | RCP6.0 | 2070 | 88.357 | 95.0782 | 102.1326 | 109.2055 | 116.28
| KingstonWind2075RCP6.0 | Kingston | Wind | RCP6.0 | 2075 | 88.5376 | 95.3248 | 102.459 | 109.5984 | 116.7393
| KingstonWind2080RCP6.0 | Kingston | Wind | RCP6.0 | 2080 | 88.7182 | 95.5714 | 102.7854 | 109.9913 | 117.1986
| KingstonWind2085RCP6.0 | Kingston | Wind | RCP6.0 | 2085 | 88.8987 | 95.8181 | 103.1118 | 110.3842 | 117.6579
| KingstonWind2090RCP6.0 | Kingston | Wind | RCP6.0 | 2090 | 89.2818 | 96.3272 | 103.7782 | 111.1846 | 118.5901
| KingstonWind2095RCP6.0 | Kingston | Wind | RCP6.0 | 2095 | 89.4844 | 96.5896 | 104.1182 | 111.592 | 119.063
| KingstonWind2100RCP6.0 | Kingston | Wind | RCP6.0 | 2100 | 89.687 | 96.8521 | 104.4582 | 111.9995 | 119.5358
| KingstonWind2023RCP8.5 | Kingston | Wind | RCP8.5 | 2023 | 87.8991 | 94.5754 | 101.592 | 108.627 | 115.6637
| KingstonWind2025RCP8.5 | Kingston | Wind | RCP8.5 | 2025 | 87.8668 | 94.5185 | 101.4968 | 108.5033 | 115.5087
| KingstonWind2030RCP8.5 | Kingston | Wind | RCP8.5 | 2030 | 87.8345 | 94.4616 | 101.4016 | 108.3797 | 115.3536
| KingstonWind2035RCP8.5 | Kingston | Wind | RCP8.5 | 2035 | 87.8022 | 94.4047 | 101.3064 | 108.256 | 115.1986
| KingstonWind2040RCP8.5 | Kingston | Wind | RCP8.5 | 2040 | 87.9871 | 94.6292 | 101.5818 | 108.5725 | 115.5591
| KingstonWind2045RCP8.5 | Kingston | Wind | RCP8.5 | 2045 | 88.1721 | 94.8537 | 101.8572 | 108.889 | 115.9195
| KingstonWind2050RCP8.5 | Kingston | Wind | RCP8.5 | 2050 | 88.5978 | 95.407 | 102.5678 | 109.7294 | 116.8924
| KingstonWind2055RCP8.5 | Kingston | Wind | RCP8.5 | 2055 | 88.8385 | 95.7359 | 103.003 | 110.2532 | 117.5048
| KingstonWind2060RCP8.5 | Kingston | Wind | RCP8.5 | 2060 | 89.2818 | 96.3272 | 103.7782 | 111.1846 | 118.5901
| KingstonWind2065RCP8.5 | Kingston | Wind | RCP8.5 | 2065 | 89.4844 | 96.5896 | 104.1182 | 111.592 | 119.063
| KingstonWind2070RCP8.5 | Kingston | Wind | RCP8.5 | 2070 | 89.7604 | 96.9596 | 104.6078 | 112.185 | 119.7568
| KingstonWind2075RCP8.5 | Kingston | Wind | RCP8.5 | 2075 | 89.8338 | 97.0671 | 104.7574 | 112.3705 | 119.9777
| KingstonWind2080RCP8.5 | Kingston | Wind | RCP8.5 | 2080 | 89.9072 | 97.1746 | 104.907 | 112.5561 | 120.1986
| KingstonWind2085RCP8.5 | Kingston | Wind | RCP8.5 | 2085 | 90.0789 | 97.4117 | 105.2283 | 112.9435 | 120.6638
| KingstonWind2090RCP8.5 | Kingston | Wind | RCP8.5 | 2090 | 90.2507 | 97.6489 | 105.5496 | 113.331 | 121.1289
| KingstonWind2095RCP8.5 | Kingston | Wind | RCP8.5 | 2095 | 90.2507 | 97.6489 | 105.5496 | 113.331 | 121.1289
| KingstonWind2100RCP8.5 | Kingston | Wind | RCP8.5 | 2100 | 90.2507 | 97.6489 | 105.5496 | 113.331 | 121.1289
| KinmountIce Accretion2023RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2023 | 17.2396 | 20.584 | 24.825 | 28.0522 | 31.311
| KinmountIce Accretion2025RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2025 | 17.2251 | 20.5771 | 24.825 | 28.057 | 31.3215
| KinmountIce Accretion2030RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2030 | 17.2106 | 20.5702 | 24.825 | 28.0617 | 31.332
| KinmountIce Accretion2035RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2035 | 17.1961 | 20.5633 | 24.825 | 28.0664 | 31.3425
| KinmountIce Accretion2040RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2040 | 17.1816 | 20.5563 | 24.825 | 28.0711 | 31.353
| KinmountIce Accretion2045RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2045 | 17.1671 | 20.5494 | 24.825 | 28.0758 | 31.3635
| KinmountIce Accretion2050RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2050 | 17.1109 | 20.5134 | 24.81 | 28.0748 | 31.374
| KinmountIce Accretion2055RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2055 | 17.0691 | 20.4844 | 24.795 | 28.0692 | 31.374
| KinmountIce Accretion2060RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2060 | 17.0274 | 20.4553 | 24.78 | 28.0635 | 31.374
| KinmountIce Accretion2065RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2065 | 16.9856 | 20.4263 | 24.765 | 28.0579 | 31.374
| KinmountIce Accretion2070RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2070 | 16.9439 | 20.3972 | 24.75 | 28.0522 | 31.374
| KinmountIce Accretion2075RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2075 | 17.0134 | 20.4975 | 24.8875 | 28.2217 | 31.5735
| KinmountIce Accretion2080RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2080 | 17.083 | 20.5978 | 25.025 | 28.3912 | 31.773
| KinmountIce Accretion2085RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2085 | 17.1526 | 20.6981 | 25.1625 | 28.5607 | 31.9725
| KinmountIce Accretion2090RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2090 | 17.2222 | 20.7984 | 25.3 | 28.7302 | 32.172
| KinmountIce Accretion2095RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2095 | 17.2918 | 20.8987 | 25.4375 | 28.8997 | 32.3715
| KinmountIce Accretion2100RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2100 | 17.3614 | 20.999 | 25.575 | 29.0692 | 32.571
| KinmountIce Accretion2023RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2023 | 17.2396 | 20.584 | 24.825 | 28.0522 | 31.311
| KinmountIce Accretion2025RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2025 | 17.2251 | 20.5771 | 24.825 | 28.057 | 31.3215
| KinmountIce Accretion2030RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2030 | 17.2106 | 20.5702 | 24.825 | 28.0617 | 31.332
| KinmountIce Accretion2035RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2035 | 17.1961 | 20.5633 | 24.825 | 28.0664 | 31.3425
| KinmountIce Accretion2040RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2040 | 17.1816 | 20.5563 | 24.825 | 28.0711 | 31.353
| KinmountIce Accretion2045RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2045 | 17.1671 | 20.5494 | 24.825 | 28.0758 | 31.3635
| KinmountIce Accretion2050RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2050 | 17.1109 | 20.5134 | 24.81 | 28.0748 | 31.374
| KinmountIce Accretion2055RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2055 | 17.0691 | 20.4844 | 24.795 | 28.0692 | 31.374
| KinmountIce Accretion2060RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2060 | 17.0274 | 20.4553 | 24.78 | 28.0635 | 31.374
| KinmountIce Accretion2065RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2065 | 16.9856 | 20.4263 | 24.765 | 28.0579 | 31.374
| KinmountIce Accretion2070RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2070 | 16.9439 | 20.3972 | 24.75 | 28.0522 | 31.374
| KinmountIce Accretion2075RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2075 | 17.0482 | 20.5477 | 24.9563 | 28.3065 | 31.6732
| KinmountIce Accretion2080RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2080 | 17.1526 | 20.6981 | 25.1625 | 28.5607 | 31.9725
| KinmountIce Accretion2085RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2085 | 17.257 | 20.8486 | 25.3687 | 28.815 | 32.2717
| KinmountIce Accretion2090RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2090 | 17.2512 | 20.916 | 25.5333 | 29.0504 | 32.5815
| KinmountIce Accretion2095RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2095 | 17.141 | 20.833 | 25.4917 | 29.0316 | 32.592
| KinmountIce Accretion2100RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2100 | 17.0308 | 20.75 | 25.45 | 29.0127 | 32.6025
| KinmountIce Accretion2023RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2023 | 17.2396 | 20.584 | 24.825 | 28.0522 | 31.311
| KinmountIce Accretion2025RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2025 | 17.2106 | 20.5702 | 24.825 | 28.0617 | 31.332
| KinmountIce Accretion2030RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2030 | 17.1816 | 20.5563 | 24.825 | 28.0711 | 31.353
| KinmountIce Accretion2035RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2035 | 17.1526 | 20.5425 | 24.825 | 28.0805 | 31.374
| KinmountIce Accretion2040RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2040 | 17.083 | 20.4941 | 24.8 | 28.0711 | 31.374
| KinmountIce Accretion2045RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2045 | 17.0134 | 20.4457 | 24.775 | 28.0617 | 31.374
| KinmountIce Accretion2050RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2050 | 17.083 | 20.5978 | 25.025 | 28.3912 | 31.773
| KinmountIce Accretion2055RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2055 | 17.2222 | 20.7984 | 25.3 | 28.7302 | 32.172
| KinmountIce Accretion2060RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2060 | 17.2512 | 20.916 | 25.5333 | 29.0504 | 32.5815
| KinmountIce Accretion2065RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2065 | 17.141 | 20.833 | 25.4917 | 29.0316 | 32.592
| KinmountIce Accretion2070RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2070 | 16.8105 | 20.5218 | 25.2167 | 28.7773 | 32.3505
| KinmountIce Accretion2075RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2075 | 16.5901 | 20.2935 | 24.9833 | 28.5419 | 32.0985
| KinmountIce Accretion2080RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2080 | 16.3698 | 20.0652 | 24.75 | 28.3065 | 31.8465
| KinmountIce Accretion2085RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2085 | 15.6826 | 19.2871 | 23.85 | 27.3177 | 30.7597
| KinmountIce Accretion2090RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2090 | 14.9955 | 18.509 | 22.95 | 26.329 | 29.673
| KinmountIce Accretion2095RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2095 | 14.9955 | 18.509 | 22.95 | 26.329 | 29.673
| KinmountIce Accretion2100RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2100 | 14.9955 | 18.509 | 22.95 | 26.329 | 29.673
| KinmountWind2023RCP4.5 | Kinmount | Wind | RCP4.5 | 2023 | 69.3273 | 74.6381 | 80.224 | 85.814 | 91.4006
| KinmountWind2025RCP4.5 | Kinmount | Wind | RCP4.5 | 2025 | 69.3802 | 74.7001 | 80.2973 | 85.8967 | 91.4934
| KinmountWind2030RCP4.5 | Kinmount | Wind | RCP4.5 | 2030 | 69.4332 | 74.7621 | 80.3707 | 85.9795 | 91.5861
| KinmountWind2035RCP4.5 | Kinmount | Wind | RCP4.5 | 2035 | 69.4862 | 74.8241 | 80.444 | 86.0622 | 91.6788
| KinmountWind2040RCP4.5 | Kinmount | Wind | RCP4.5 | 2040 | 69.5391 | 74.8861 | 80.5173 | 86.145 | 91.7715
| KinmountWind2045RCP4.5 | Kinmount | Wind | RCP4.5 | 2045 | 69.5921 | 74.9481 | 80.5907 | 86.2277 | 91.8642
| KinmountWind2050RCP4.5 | Kinmount | Wind | RCP4.5 | 2050 | 69.7155 | 75.0889 | 80.7504 | 86.4046 | 92.0591
| KinmountWind2055RCP4.5 | Kinmount | Wind | RCP4.5 | 2055 | 69.786 | 75.1678 | 80.8368 | 86.4988 | 92.1612
| KinmountWind2060RCP4.5 | Kinmount | Wind | RCP4.5 | 2060 | 69.8564 | 75.2467 | 80.9232 | 86.593 | 92.2634
| KinmountWind2065RCP4.5 | Kinmount | Wind | RCP4.5 | 2065 | 69.9269 | 75.3255 | 81.0096 | 86.6871 | 92.3655
| KinmountWind2070RCP4.5 | Kinmount | Wind | RCP4.5 | 2070 | 69.9973 | 75.4044 | 81.096 | 86.7813 | 92.4677
| KinmountWind2075RCP4.5 | Kinmount | Wind | RCP4.5 | 2075 | 69.9755 | 75.3821 | 81.072 | 86.757 | 92.4434
| KinmountWind2080RCP4.5 | Kinmount | Wind | RCP4.5 | 2080 | 69.9536 | 75.3598 | 81.048 | 86.7328 | 92.419
| KinmountWind2085RCP4.5 | Kinmount | Wind | RCP4.5 | 2085 | 69.9317 | 75.3374 | 81.024 | 86.7085 | 92.3947
| KinmountWind2090RCP4.5 | Kinmount | Wind | RCP4.5 | 2090 | 69.9098 | 75.3151 | 81 | 86.6843 | 92.3704
| KinmountWind2095RCP4.5 | Kinmount | Wind | RCP4.5 | 2095 | 69.888 | 75.2928 | 80.976 | 86.66 | 92.3461
| KinmountWind2100RCP4.5 | Kinmount | Wind | RCP4.5 | 2100 | 69.8661 | 75.2705 | 80.952 | 86.6358 | 92.3218
| KinmountWind2023RCP6.0 | Kinmount | Wind | RCP6.0 | 2023 | 69.3273 | 74.6381 | 80.224 | 85.814 | 91.4006
| KinmountWind2025RCP6.0 | Kinmount | Wind | RCP6.0 | 2025 | 69.3802 | 74.7001 | 80.2973 | 85.8967 | 91.4934
| KinmountWind2030RCP6.0 | Kinmount | Wind | RCP6.0 | 2030 | 69.4332 | 74.7621 | 80.3707 | 85.9795 | 91.5861
| KinmountWind2035RCP6.0 | Kinmount | Wind | RCP6.0 | 2035 | 69.4862 | 74.8241 | 80.444 | 86.0622 | 91.6788
| KinmountWind2040RCP6.0 | Kinmount | Wind | RCP6.0 | 2040 | 69.5391 | 74.8861 | 80.5173 | 86.145 | 91.7715
| KinmountWind2045RCP6.0 | Kinmount | Wind | RCP6.0 | 2045 | 69.5921 | 74.9481 | 80.5907 | 86.2277 | 91.8642
| KinmountWind2050RCP6.0 | Kinmount | Wind | RCP6.0 | 2050 | 69.7155 | 75.0889 | 80.7504 | 86.4046 | 92.0591
| KinmountWind2055RCP6.0 | Kinmount | Wind | RCP6.0 | 2055 | 69.786 | 75.1678 | 80.8368 | 86.4988 | 92.1612
| KinmountWind2060RCP6.0 | Kinmount | Wind | RCP6.0 | 2060 | 69.8564 | 75.2467 | 80.9232 | 86.593 | 92.2634
| KinmountWind2065RCP6.0 | Kinmount | Wind | RCP6.0 | 2065 | 69.9269 | 75.3255 | 81.0096 | 86.6871 | 92.3655
| KinmountWind2070RCP6.0 | Kinmount | Wind | RCP6.0 | 2070 | 69.9973 | 75.4044 | 81.096 | 86.7813 | 92.4677
| KinmountWind2075RCP6.0 | Kinmount | Wind | RCP6.0 | 2075 | 69.9645 | 75.3709 | 81.06 | 86.7449 | 92.4312
| KinmountWind2080RCP6.0 | Kinmount | Wind | RCP6.0 | 2080 | 69.9317 | 75.3374 | 81.024 | 86.7085 | 92.3947
| KinmountWind2085RCP6.0 | Kinmount | Wind | RCP6.0 | 2085 | 69.8989 | 75.304 | 80.988 | 86.6721 | 92.3582
| KinmountWind2090RCP6.0 | Kinmount | Wind | RCP6.0 | 2090 | 69.9167 | 75.3275 | 81.0187 | 86.7099 | 92.4038
| KinmountWind2095RCP6.0 | Kinmount | Wind | RCP6.0 | 2095 | 69.9674 | 75.3846 | 81.0853 | 86.7841 | 92.4859
| KinmountWind2100RCP6.0 | Kinmount | Wind | RCP6.0 | 2100 | 70.0181 | 75.4416 | 81.152 | 86.8583 | 92.568
| KinmountWind2023RCP8.5 | Kinmount | Wind | RCP8.5 | 2023 | 69.3273 | 74.6381 | 80.224 | 85.814 | 91.4006
| KinmountWind2025RCP8.5 | Kinmount | Wind | RCP8.5 | 2025 | 69.4332 | 74.7621 | 80.3707 | 85.9795 | 91.5861
| KinmountWind2030RCP8.5 | Kinmount | Wind | RCP8.5 | 2030 | 69.5391 | 74.8861 | 80.5173 | 86.145 | 91.7715
| KinmountWind2035RCP8.5 | Kinmount | Wind | RCP8.5 | 2035 | 69.645 | 75.0101 | 80.664 | 86.3105 | 91.957
| KinmountWind2040RCP8.5 | Kinmount | Wind | RCP8.5 | 2040 | 69.7625 | 75.1415 | 80.808 | 86.4674 | 92.1272
| KinmountWind2045RCP8.5 | Kinmount | Wind | RCP8.5 | 2045 | 69.8799 | 75.273 | 80.952 | 86.6243 | 92.2974
| KinmountWind2050RCP8.5 | Kinmount | Wind | RCP8.5 | 2050 | 69.9536 | 75.3598 | 81.048 | 86.7328 | 92.419
| KinmountWind2055RCP8.5 | Kinmount | Wind | RCP8.5 | 2055 | 69.9098 | 75.3151 | 81 | 86.6843 | 92.3704
| KinmountWind2060RCP8.5 | Kinmount | Wind | RCP8.5 | 2060 | 69.9167 | 75.3275 | 81.0187 | 86.7099 | 92.4038
| KinmountWind2065RCP8.5 | Kinmount | Wind | RCP8.5 | 2065 | 69.9674 | 75.3846 | 81.0853 | 86.7841 | 92.4859
| KinmountWind2070RCP8.5 | Kinmount | Wind | RCP8.5 | 2070 | 70.0342 | 75.454 | 81.1627 | 86.8669 | 92.5741
| KinmountWind2075RCP8.5 | Kinmount | Wind | RCP8.5 | 2075 | 70.0503 | 75.4664 | 81.1733 | 86.8754 | 92.5802
| KinmountWind2080RCP8.5 | Kinmount | Wind | RCP8.5 | 2080 | 70.0664 | 75.4788 | 81.184 | 86.884 | 92.5862
| KinmountWind2085RCP8.5 | Kinmount | Wind | RCP8.5 | 2085 | 70.1666 | 75.5904 | 81.304 | 87.0124 | 92.723
| KinmountWind2090RCP8.5 | Kinmount | Wind | RCP8.5 | 2090 | 70.2667 | 75.702 | 81.424 | 87.1408 | 92.8598
| KinmountWind2095RCP8.5 | Kinmount | Wind | RCP8.5 | 2095 | 70.2667 | 75.702 | 81.424 | 87.1408 | 92.8598
| KinmountWind2100RCP8.5 | Kinmount | Wind | RCP8.5 | 2100 | 70.2667 | 75.702 | 81.424 | 87.1408 | 92.8598
| Kirkland LakeIce Accretion2023RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2023 | 14.6545 | 17.5296 | 21.16 | 23.9334 | 26.712
| Kirkland LakeIce Accretion2025RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2025 | 14.6638 | 17.5407 | 21.1733 | 23.9522 | 26.733
| Kirkland LakeIce Accretion2030RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2030 | 14.6731 | 17.5517 | 21.1867 | 23.9711 | 26.754
| Kirkland LakeIce Accretion2035RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2035 | 14.6824 | 17.5628 | 21.2 | 23.9899 | 26.775
| Kirkland LakeIce Accretion2040RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2040 | 14.6916 | 17.5739 | 21.2133 | 24.0087 | 26.796
| Kirkland LakeIce Accretion2045RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2045 | 14.7009 | 17.5849 | 21.2267 | 24.0276 | 26.817
| Kirkland LakeIce Accretion2050RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2050 | 14.816 | 17.7321 | 21.416 | 24.2498 | 27.0698
| Kirkland LakeIce Accretion2055RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2055 | 14.9217 | 17.8682 | 21.592 | 24.4532 | 27.3017
| Kirkland LakeIce Accretion2060RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2060 | 15.0275 | 18.0044 | 21.768 | 24.6566 | 27.5335
| Kirkland LakeIce Accretion2065RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2065 | 15.1333 | 18.1405 | 21.944 | 24.86 | 27.7654
| Kirkland LakeIce Accretion2070RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2070 | 15.239 | 18.2766 | 22.12 | 25.0634 | 27.9972
| Kirkland LakeIce Accretion2075RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2075 | 15.3249 | 18.39 | 22.2667 | 25.2367 | 28.1988
| Kirkland LakeIce Accretion2080RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2080 | 15.4107 | 18.5035 | 22.4133 | 25.4099 | 28.4004
| Kirkland LakeIce Accretion2085RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2085 | 15.4965 | 18.6169 | 22.56 | 25.5832 | 28.602
| Kirkland LakeIce Accretion2090RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2090 | 15.5823 | 18.7303 | 22.7067 | 25.7565 | 28.8036
| Kirkland LakeIce Accretion2095RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2095 | 15.6681 | 18.8438 | 22.8533 | 25.9297 | 29.0052
| Kirkland LakeIce Accretion2100RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2100 | 15.754 | 18.9572 | 23 | 26.103 | 29.2068
| Kirkland LakeIce Accretion2023RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2023 | 14.6545 | 17.5296 | 21.16 | 23.9334 | 26.712
| Kirkland LakeIce Accretion2025RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2025 | 14.6638 | 17.5407 | 21.1733 | 23.9522 | 26.733
| Kirkland LakeIce Accretion2030RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2030 | 14.6731 | 17.5517 | 21.1867 | 23.9711 | 26.754
| Kirkland LakeIce Accretion2035RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2035 | 14.6824 | 17.5628 | 21.2 | 23.9899 | 26.775
| Kirkland LakeIce Accretion2040RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2040 | 14.6916 | 17.5739 | 21.2133 | 24.0087 | 26.796
| Kirkland LakeIce Accretion2045RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2045 | 14.7009 | 17.5849 | 21.2267 | 24.0276 | 26.817
| Kirkland LakeIce Accretion2050RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2050 | 14.816 | 17.7321 | 21.416 | 24.2498 | 27.0698
| Kirkland LakeIce Accretion2055RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2055 | 14.9217 | 17.8682 | 21.592 | 24.4532 | 27.3017
| Kirkland LakeIce Accretion2060RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2060 | 15.0275 | 18.0044 | 21.768 | 24.6566 | 27.5335
| Kirkland LakeIce Accretion2065RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2065 | 15.1333 | 18.1405 | 21.944 | 24.86 | 27.7654
| Kirkland LakeIce Accretion2070RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2070 | 15.239 | 18.2766 | 22.12 | 25.0634 | 27.9972
| Kirkland LakeIce Accretion2075RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2075 | 15.3678 | 18.4467 | 22.34 | 25.3233 | 28.2996
| Kirkland LakeIce Accretion2080RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2080 | 15.4965 | 18.6169 | 22.56 | 25.5832 | 28.602
| Kirkland LakeIce Accretion2085RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2085 | 15.6252 | 18.787 | 22.78 | 25.8431 | 28.9044
| Kirkland LakeIce Accretion2090RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2090 | 15.7586 | 18.9793 | 23.0467 | 26.1633 | 29.274
| Kirkland LakeIce Accretion2095RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2095 | 15.7632 | 19.0015 | 23.0933 | 26.2235 | 29.3412
| Kirkland LakeIce Accretion2100RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2100 | 15.7679 | 19.0236 | 23.14 | 26.2838 | 29.4084
| Kirkland LakeIce Accretion2023RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2023 | 14.6545 | 17.5296 | 21.16 | 23.9334 | 26.712
| Kirkland LakeIce Accretion2025RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2025 | 14.6731 | 17.5517 | 21.1867 | 23.9711 | 26.754
| Kirkland LakeIce Accretion2030RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2030 | 14.6916 | 17.5739 | 21.2133 | 24.0087 | 26.796
| Kirkland LakeIce Accretion2035RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2035 | 14.7102 | 17.596 | 21.24 | 24.0464 | 26.838
| Kirkland LakeIce Accretion2040RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2040 | 14.8865 | 17.8229 | 21.5333 | 24.3854 | 27.2244
| Kirkland LakeIce Accretion2045RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2045 | 15.0627 | 18.0497 | 21.8267 | 24.7244 | 27.6108
| Kirkland LakeIce Accretion2050RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2050 | 15.4107 | 18.5035 | 22.4133 | 25.4099 | 28.4004
| Kirkland LakeIce Accretion2055RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2055 | 15.5823 | 18.7303 | 22.7067 | 25.7565 | 28.8036
| Kirkland LakeIce Accretion2060RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2060 | 15.7586 | 18.9793 | 23.0467 | 26.1633 | 29.274
| Kirkland LakeIce Accretion2065RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2065 | 15.7632 | 19.0015 | 23.0933 | 26.2235 | 29.3412
| Kirkland LakeIce Accretion2070RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2070 | 15.5359 | 18.7469 | 22.8067 | 25.9071 | 28.9968
| Kirkland LakeIce Accretion2075RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2075 | 15.304 | 18.4703 | 22.4733 | 25.5305 | 28.5852
| Kirkland LakeIce Accretion2080RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2080 | 15.072 | 18.1936 | 22.14 | 25.1538 | 28.1736
| Kirkland LakeIce Accretion2085RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2085 | 14.8841 | 18.0027 | 21.94 | 24.9391 | 27.9468
| Kirkland LakeIce Accretion2090RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2090 | 14.6963 | 17.8118 | 21.74 | 24.7244 | 27.72
| Kirkland LakeIce Accretion2095RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2095 | 14.6963 | 17.8118 | 21.74 | 24.7244 | 27.72
| Kirkland LakeIce Accretion2100RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2100 | 14.6963 | 17.8118 | 21.74 | 24.7244 | 27.72
| Kirkland LakeWind2023RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2023 | 74.7422 | 80.4759 | 86.4902 | 92.5169 | 98.5498
| Kirkland LakeWind2025RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2025 | 74.8065 | 80.5439 | 86.5662 | 92.5982 | 98.6364
| Kirkland LakeWind2030RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2030 | 74.8709 | 80.6118 | 86.6421 | 92.6795 | 98.723
| Kirkland LakeWind2035RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2035 | 74.9353 | 80.6798 | 86.7181 | 92.7608 | 98.8096
| Kirkland LakeWind2040RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2040 | 74.9996 | 80.7478 | 86.7941 | 92.842 | 98.8962
| Kirkland LakeWind2045RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2045 | 75.064 | 80.8158 | 86.87 | 92.9233 | 98.9828
| Kirkland LakeWind2050RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2050 | 75.1476 | 80.8982 | 86.9512 | 93.0046 | 99.0616
| Kirkland LakeWind2055RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2055 | 75.1669 | 80.9126 | 86.9563 | 93.0046 | 99.0537
| Kirkland LakeWind2060RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2060 | 75.1862 | 80.927 | 86.9615 | 93.0046 | 99.0459
| Kirkland LakeWind2065RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2065 | 75.2056 | 80.9414 | 86.9666 | 93.0046 | 99.038
| Kirkland LakeWind2070RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2070 | 75.2249 | 80.9558 | 86.9718 | 93.0046 | 99.0302
| Kirkland LakeWind2075RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2075 | 75.2669 | 81.0064 | 87.032 | 93.0736 | 99.1086
| Kirkland LakeWind2080RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2080 | 75.309 | 81.0571 | 87.0922 | 93.1426 | 99.1871
| Kirkland LakeWind2085RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2085 | 75.3511 | 81.1077 | 87.1524 | 93.2117 | 99.2655
| Kirkland LakeWind2090RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2090 | 75.3932 | 81.1584 | 87.2126 | 93.2807 | 99.3439
| Kirkland LakeWind2095RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2095 | 75.4353 | 81.209 | 87.2728 | 93.3497 | 99.4224
| Kirkland LakeWind2100RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2100 | 75.4773 | 81.2597 | 87.333 | 93.4187 | 99.5008
| Kirkland LakeWind2023RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2023 | 74.7422 | 80.4759 | 86.4902 | 92.5169 | 98.5498
| Kirkland LakeWind2025RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2025 | 74.8065 | 80.5439 | 86.5662 | 92.5982 | 98.6364
| Kirkland LakeWind2030RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2030 | 74.8709 | 80.6118 | 86.6421 | 92.6795 | 98.723
| Kirkland LakeWind2035RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2035 | 74.9353 | 80.6798 | 86.7181 | 92.7608 | 98.8096
| Kirkland LakeWind2040RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2040 | 74.9996 | 80.7478 | 86.7941 | 92.842 | 98.8962
| Kirkland LakeWind2045RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2045 | 75.064 | 80.8158 | 86.87 | 92.9233 | 98.9828
| Kirkland LakeWind2050RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2050 | 75.1476 | 80.8982 | 86.9512 | 93.0046 | 99.0616
| Kirkland LakeWind2055RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2055 | 75.1669 | 80.9126 | 86.9563 | 93.0046 | 99.0537
| Kirkland LakeWind2060RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2060 | 75.1862 | 80.927 | 86.9615 | 93.0046 | 99.0459
| Kirkland LakeWind2065RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2065 | 75.2056 | 80.9414 | 86.9666 | 93.0046 | 99.038
| Kirkland LakeWind2070RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2070 | 75.2249 | 80.9558 | 86.9718 | 93.0046 | 99.0302
| Kirkland LakeWind2075RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2075 | 75.288 | 81.0317 | 87.0621 | 93.1081 | 99.1479
| Kirkland LakeWind2080RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2080 | 75.3511 | 81.1077 | 87.1524 | 93.2117 | 99.2655
| Kirkland LakeWind2085RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2085 | 75.4142 | 81.1837 | 87.2427 | 93.3152 | 99.3831
| Kirkland LakeWind2090RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2090 | 75.5194 | 81.2997 | 87.3731 | 93.4586 | 99.5433
| Kirkland LakeWind2095RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2095 | 75.5615 | 81.3397 | 87.4133 | 93.4985 | 99.5858
| Kirkland LakeWind2100RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2100 | 75.6036 | 81.3797 | 87.4534 | 93.5383 | 99.6282
| Kirkland LakeWind2023RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2023 | 74.7422 | 80.4759 | 86.4902 | 92.5169 | 98.5498
| Kirkland LakeWind2025RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2025 | 74.8709 | 80.6118 | 86.6421 | 92.6795 | 98.723
| Kirkland LakeWind2030RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2030 | 74.9996 | 80.7478 | 86.7941 | 92.842 | 98.8962
| Kirkland LakeWind2035RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2035 | 75.1283 | 80.8838 | 86.946 | 93.0046 | 99.0694
| Kirkland LakeWind2040RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2040 | 75.1605 | 80.9078 | 86.9546 | 93.0046 | 99.0563
| Kirkland LakeWind2045RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2045 | 75.1927 | 80.9318 | 86.9632 | 93.0046 | 99.0433
| Kirkland LakeWind2050RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2050 | 75.309 | 81.0571 | 87.0922 | 93.1426 | 99.1871
| Kirkland LakeWind2055RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2055 | 75.3932 | 81.1584 | 87.2126 | 93.2807 | 99.3439
| Kirkland LakeWind2060RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2060 | 75.5194 | 81.2997 | 87.3731 | 93.4586 | 99.5433
| Kirkland LakeWind2065RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2065 | 75.5615 | 81.3397 | 87.4133 | 93.4985 | 99.5858
| Kirkland LakeWind2070RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2070 | 75.7199 | 81.497 | 87.5709 | 93.658 | 99.7459
| Kirkland LakeWind2075RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2075 | 75.8363 | 81.6143 | 87.6885 | 93.7776 | 99.8635
| Kirkland LakeWind2080RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2080 | 75.9526 | 81.7316 | 87.806 | 93.8972 | 99.9812
| Kirkland LakeWind2085RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2085 | 75.9526 | 81.7436 | 87.8318 | 93.934 | 100.0302
| Kirkland LakeWind2090RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2090 | 75.9526 | 81.7556 | 87.8576 | 93.9708 | 100.0792
| Kirkland LakeWind2095RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2095 | 75.9526 | 81.7556 | 87.8576 | 93.9708 | 100.0792
| Kirkland LakeWind2100RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2100 | 75.9526 | 81.7556 | 87.8576 | 93.9708 | 100.0792
| KitchenerIce Accretion2023RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
| KitchenerIce Accretion2025RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2025 | 17.3208 | 20.7984 | 25.1958 | 28.5655 | 31.92
| KitchenerIce Accretion2030RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2030 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
| KitchenerIce Accretion2035RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2035 | 17.3788 | 20.8953 | 25.3375 | 28.7444 | 32.13
| KitchenerIce Accretion2040RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2040 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
| KitchenerIce Accretion2045RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2045 | 17.4367 | 20.9921 | 25.4792 | 28.9233 | 32.34
| KitchenerIce Accretion2050RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2050 | 17.4101 | 20.9907 | 25.51 | 28.9788 | 32.4198
| KitchenerIce Accretion2055RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2055 | 17.3544 | 20.9409 | 25.47 | 28.9449 | 32.3946
| KitchenerIce Accretion2060RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2060 | 17.2987 | 20.8911 | 25.43 | 28.911 | 32.3694
| KitchenerIce Accretion2065RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2065 | 17.2431 | 20.8413 | 25.39 | 28.8771 | 32.3442
| KitchenerIce Accretion2070RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2070 | 17.1874 | 20.7915 | 25.35 | 28.8432 | 32.319
| KitchenerIce Accretion2075RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2075 | 17.1555 | 20.7846 | 25.3708 | 28.8809 | 32.3768
| KitchenerIce Accretion2080RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2080 | 17.1236 | 20.7777 | 25.3917 | 28.9186 | 32.4345
| KitchenerIce Accretion2085RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2085 | 17.0917 | 20.7707 | 25.4125 | 28.9562 | 32.4922
| KitchenerIce Accretion2090RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2090 | 17.0598 | 20.7638 | 25.4333 | 28.9939 | 32.55
| KitchenerIce Accretion2095RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2095 | 17.0279 | 20.7569 | 25.4542 | 29.0316 | 32.6077
| KitchenerIce Accretion2100RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2100 | 16.996 | 20.75 | 25.475 | 29.0692 | 32.6655
| KitchenerIce Accretion2023RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
| KitchenerIce Accretion2025RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2025 | 17.3208 | 20.7984 | 25.1958 | 28.5655 | 31.92
| KitchenerIce Accretion2030RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2030 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
| KitchenerIce Accretion2035RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2035 | 17.3788 | 20.8953 | 25.3375 | 28.7444 | 32.13
| KitchenerIce Accretion2040RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2040 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
| KitchenerIce Accretion2045RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2045 | 17.4367 | 20.9921 | 25.4792 | 28.9233 | 32.34
| KitchenerIce Accretion2050RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2050 | 17.4101 | 20.9907 | 25.51 | 28.9788 | 32.4198
| KitchenerIce Accretion2055RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2055 | 17.3544 | 20.9409 | 25.47 | 28.9449 | 32.3946
| KitchenerIce Accretion2060RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2060 | 17.2987 | 20.8911 | 25.43 | 28.911 | 32.3694
| KitchenerIce Accretion2065RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2065 | 17.2431 | 20.8413 | 25.39 | 28.8771 | 32.3442
| KitchenerIce Accretion2070RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2070 | 17.1874 | 20.7915 | 25.35 | 28.8432 | 32.319
| KitchenerIce Accretion2075RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2075 | 17.1396 | 20.7811 | 25.3813 | 28.8997 | 32.4056
| KitchenerIce Accretion2080RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2080 | 17.0917 | 20.7707 | 25.4125 | 28.9562 | 32.4922
| KitchenerIce Accretion2085RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2085 | 17.0439 | 20.7604 | 25.4437 | 29.0127 | 32.5789
| KitchenerIce Accretion2090RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2090 | 16.6887 | 20.4249 | 25.1333 | 28.7114 | 32.298
| KitchenerIce Accretion2095RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2095 | 16.3814 | 20.0998 | 24.7917 | 28.3536 | 31.9305
| KitchenerIce Accretion2100RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2100 | 16.074 | 19.7747 | 24.45 | 27.9957 | 31.563
| KitchenerIce Accretion2023RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
| KitchenerIce Accretion2025RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2025 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
| KitchenerIce Accretion2030RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2030 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
| KitchenerIce Accretion2035RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2035 | 17.4657 | 21.0405 | 25.55 | 29.0127 | 32.445
| KitchenerIce Accretion2040RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2040 | 17.373 | 20.9575 | 25.4833 | 28.9562 | 32.403
| KitchenerIce Accretion2045RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2045 | 17.2802 | 20.8745 | 25.4167 | 28.8997 | 32.361
| KitchenerIce Accretion2050RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2050 | 17.1236 | 20.7777 | 25.3917 | 28.9186 | 32.4345
| KitchenerIce Accretion2055RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2055 | 17.0598 | 20.7638 | 25.4333 | 28.9939 | 32.55
| KitchenerIce Accretion2060RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2060 | 16.6887 | 20.4249 | 25.1333 | 28.7114 | 32.298
| KitchenerIce Accretion2065RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2065 | 16.3814 | 20.0998 | 24.7917 | 28.3536 | 31.9305
| KitchenerIce Accretion2070RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2070 | 15.6507 | 19.3182 | 23.95 | 27.4684 | 30.9855
| KitchenerIce Accretion2075RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2075 | 15.2274 | 18.8617 | 23.45 | 26.9411 | 30.408
| KitchenerIce Accretion2080RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2080 | 14.8041 | 18.4052 | 22.95 | 26.4137 | 29.8305
| KitchenerIce Accretion2085RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2085 | 13.9778 | 17.43 | 21.7875 | 25.086 | 28.3657
| KitchenerIce Accretion2090RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2090 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
| KitchenerIce Accretion2095RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2095 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
| KitchenerIce Accretion2100RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2100 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
| KitchenerWind2023RCP4.5 | Kitchener | Wind | RCP4.5 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
| KitchenerWind2025RCP4.5 | Kitchener | Wind | RCP4.5 | 2025 | 81.5488 | 87.8469 | 94.481 | 101.1097 | 107.7494
| KitchenerWind2030RCP4.5 | Kitchener | Wind | RCP4.5 | 2030 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
| KitchenerWind2035RCP4.5 | Kitchener | Wind | RCP4.5 | 2035 | 81.6625 | 88.0013 | 94.6909 | 101.3645 | 108.0494
| KitchenerWind2040RCP4.5 | Kitchener | Wind | RCP4.5 | 2040 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
| KitchenerWind2045RCP4.5 | Kitchener | Wind | RCP4.5 | 2045 | 81.7761 | 88.1558 | 94.9008 | 101.6193 | 108.3495
| KitchenerWind2050RCP4.5 | Kitchener | Wind | RCP4.5 | 2050 | 81.8962 | 88.3099 | 95.096 | 101.8513 | 108.6174
| KitchenerWind2055RCP4.5 | Kitchener | Wind | RCP4.5 | 2055 | 81.9595 | 88.3869 | 95.1863 | 101.9559 | 108.7353
| KitchenerWind2060RCP4.5 | Kitchener | Wind | RCP4.5 | 2060 | 82.0229 | 88.4638 | 95.2765 | 102.0605 | 108.8531
| KitchenerWind2065RCP4.5 | Kitchener | Wind | RCP4.5 | 2065 | 82.0862 | 88.5407 | 95.3668 | 102.1651 | 108.971
| KitchenerWind2070RCP4.5 | Kitchener | Wind | RCP4.5 | 2070 | 82.1495 | 88.6177 | 95.457 | 102.2697 | 109.0889
| KitchenerWind2075RCP4.5 | Kitchener | Wind | RCP4.5 | 2075 | 82.2185 | 88.7167 | 95.598 | 102.4424 | 109.2961
| KitchenerWind2080RCP4.5 | Kitchener | Wind | RCP4.5 | 2080 | 82.2875 | 88.8158 | 95.739 | 102.6151 | 109.5032
| KitchenerWind2085RCP4.5 | Kitchener | Wind | RCP4.5 | 2085 | 82.3564 | 88.9149 | 95.88 | 102.7877 | 109.7104
| KitchenerWind2090RCP4.5 | Kitchener | Wind | RCP4.5 | 2090 | 82.4254 | 89.014 | 96.021 | 102.9604 | 109.9176
| KitchenerWind2095RCP4.5 | Kitchener | Wind | RCP4.5 | 2095 | 82.4944 | 89.113 | 96.162 | 103.1331 | 110.1248
| KitchenerWind2100RCP4.5 | Kitchener | Wind | RCP4.5 | 2100 | 82.5634 | 89.2121 | 96.303 | 103.3057 | 110.3319
| KitchenerWind2023RCP6.0 | Kitchener | Wind | RCP6.0 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
| KitchenerWind2025RCP6.0 | Kitchener | Wind | RCP6.0 | 2025 | 81.5488 | 87.8469 | 94.481 | 101.1097 | 107.7494
| KitchenerWind2030RCP6.0 | Kitchener | Wind | RCP6.0 | 2030 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
| KitchenerWind2035RCP6.0 | Kitchener | Wind | RCP6.0 | 2035 | 81.6625 | 88.0013 | 94.6909 | 101.3645 | 108.0494
| KitchenerWind2040RCP6.0 | Kitchener | Wind | RCP6.0 | 2040 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
| KitchenerWind2045RCP6.0 | Kitchener | Wind | RCP6.0 | 2045 | 81.7761 | 88.1558 | 94.9008 | 101.6193 | 108.3495
| KitchenerWind2050RCP6.0 | Kitchener | Wind | RCP6.0 | 2050 | 81.8962 | 88.3099 | 95.096 | 101.8513 | 108.6174
| KitchenerWind2055RCP6.0 | Kitchener | Wind | RCP6.0 | 2055 | 81.9595 | 88.3869 | 95.1863 | 101.9559 | 108.7353
| KitchenerWind2060RCP6.0 | Kitchener | Wind | RCP6.0 | 2060 | 82.0229 | 88.4638 | 95.2765 | 102.0605 | 108.8531
| KitchenerWind2065RCP6.0 | Kitchener | Wind | RCP6.0 | 2065 | 82.0862 | 88.5407 | 95.3668 | 102.1651 | 108.971
| KitchenerWind2070RCP6.0 | Kitchener | Wind | RCP6.0 | 2070 | 82.1495 | 88.6177 | 95.457 | 102.2697 | 109.0889
| KitchenerWind2075RCP6.0 | Kitchener | Wind | RCP6.0 | 2075 | 82.253 | 88.7663 | 95.6685 | 102.5287 | 109.3996
| KitchenerWind2080RCP6.0 | Kitchener | Wind | RCP6.0 | 2080 | 82.3564 | 88.9149 | 95.88 | 102.7877 | 109.7104
| KitchenerWind2085RCP6.0 | Kitchener | Wind | RCP6.0 | 2085 | 82.4599 | 89.0635 | 96.0915 | 103.0467 | 110.0212
| KitchenerWind2090RCP6.0 | Kitchener | Wind | RCP6.0 | 2090 | 82.8421 | 89.5618 | 96.7385 | 103.8187 | 110.9213
| KitchenerWind2095RCP6.0 | Kitchener | Wind | RCP6.0 | 2095 | 83.1208 | 89.9115 | 97.1741 | 104.3316 | 111.5107
| KitchenerWind2100RCP6.0 | Kitchener | Wind | RCP6.0 | 2100 | 83.3995 | 90.2612 | 97.6096 | 104.8446 | 112.1001
| KitchenerWind2023RCP8.5 | Kitchener | Wind | RCP8.5 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
| KitchenerWind2025RCP8.5 | Kitchener | Wind | RCP8.5 | 2025 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
| KitchenerWind2030RCP8.5 | Kitchener | Wind | RCP8.5 | 2030 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
| KitchenerWind2035RCP8.5 | Kitchener | Wind | RCP8.5 | 2035 | 81.8329 | 88.233 | 95.0058 | 101.7467 | 108.4995
| KitchenerWind2040RCP8.5 | Kitchener | Wind | RCP8.5 | 2040 | 81.9384 | 88.3612 | 95.1562 | 101.9211 | 108.696
| KitchenerWind2045RCP8.5 | Kitchener | Wind | RCP8.5 | 2045 | 82.044 | 88.4894 | 95.3066 | 102.0954 | 108.8924
| KitchenerWind2050RCP8.5 | Kitchener | Wind | RCP8.5 | 2050 | 82.2875 | 88.8158 | 95.739 | 102.6151 | 109.5032
| KitchenerWind2055RCP8.5 | Kitchener | Wind | RCP8.5 | 2055 | 82.4254 | 89.014 | 96.021 | 102.9604 | 109.9176
| KitchenerWind2060RCP8.5 | Kitchener | Wind | RCP8.5 | 2060 | 82.8421 | 89.5618 | 96.7385 | 103.8187 | 110.9213
| KitchenerWind2065RCP8.5 | Kitchener | Wind | RCP8.5 | 2065 | 83.1208 | 89.9115 | 97.1741 | 104.3316 | 111.5107
| KitchenerWind2070RCP8.5 | Kitchener | Wind | RCP8.5 | 2070 | 83.6457 | 90.5933 | 98.0451 | 105.371 | 112.718
| KitchenerWind2075RCP8.5 | Kitchener | Wind | RCP8.5 | 2075 | 83.8919 | 90.9255 | 98.4807 | 105.8973 | 113.336
| KitchenerWind2080RCP8.5 | Kitchener | Wind | RCP8.5 | 2080 | 84.1381 | 91.2577 | 98.9162 | 106.4237 | 113.9539
| KitchenerWind2085RCP8.5 | Kitchener | Wind | RCP8.5 | 2085 | 84.3775 | 91.5768 | 99.3392 | 106.9266 | 114.5433
| KitchenerWind2090RCP8.5 | Kitchener | Wind | RCP8.5 | 2090 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
| KitchenerWind2095RCP8.5 | Kitchener | Wind | RCP8.5 | 2095 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
| KitchenerWind2100RCP8.5 | Kitchener | Wind | RCP8.5 | 2100 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
| KitchenuhmaykoosibIce Accretion2023RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2023 | 12.8634 | 15.3583 | 18.504 | 20.9299 | 23.3377
| KitchenuhmaykoosibIce Accretion2025RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2025 | 13.0116 | 15.5326 | 18.714 | 21.1672 | 23.6023
| KitchenuhmaykoosibIce Accretion2030RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2030 | 13.1598 | 15.7069 | 18.924 | 21.4045 | 23.8669
| KitchenuhmaykoosibIce Accretion2035RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2035 | 13.3081 | 15.8812 | 19.134 | 21.6418 | 24.1315
| KitchenuhmaykoosibIce Accretion2040RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2040 | 13.4563 | 16.0555 | 19.344 | 21.8791 | 24.3961
| KitchenuhmaykoosibIce Accretion2045RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2045 | 13.6045 | 16.2298 | 19.554 | 22.1164 | 24.6607
| KitchenuhmaykoosibIce Accretion2050RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2050 | 13.7402 | 16.3772 | 19.7208 | 22.2967 | 24.8573
| KitchenuhmaykoosibIce Accretion2055RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2055 | 13.7277 | 16.3503 | 19.6776 | 22.2398 | 24.7892
| KitchenuhmaykoosibIce Accretion2060RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2060 | 13.7151 | 16.3234 | 19.6344 | 22.1828 | 24.7212
| KitchenuhmaykoosibIce Accretion2065RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2065 | 13.7026 | 16.2966 | 19.5912 | 22.1259 | 24.6532
| KitchenuhmaykoosibIce Accretion2070RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2070 | 13.6901 | 16.2697 | 19.548 | 22.0689 | 24.5851
| KitchenuhmaykoosibIce Accretion2075RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2075 | 13.7318 | 16.3294 | 19.626 | 22.1604 | 24.691
| KitchenuhmaykoosibIce Accretion2080RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2080 | 13.7736 | 16.3892 | 19.704 | 22.252 | 24.7968
| KitchenuhmaykoosibIce Accretion2085RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2085 | 13.8153 | 16.4489 | 19.782 | 22.3435 | 24.9026
| KitchenuhmaykoosibIce Accretion2090RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2090 | 13.8571 | 16.5087 | 19.86 | 22.435 | 25.0085
| KitchenuhmaykoosibIce Accretion2095RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2095 | 13.8988 | 16.5685 | 19.938 | 22.5266 | 25.1143
| KitchenuhmaykoosibIce Accretion2100RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2100 | 13.9406 | 16.6282 | 20.016 | 22.6181 | 25.2202
| KitchenuhmaykoosibIce Accretion2023RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2023 | 12.8634 | 15.3583 | 18.504 | 20.9299 | 23.3377
| KitchenuhmaykoosibIce Accretion2025RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2025 | 13.0116 | 15.5326 | 18.714 | 21.1672 | 23.6023
| KitchenuhmaykoosibIce Accretion2030RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2030 | 13.1598 | 15.7069 | 18.924 | 21.4045 | 23.8669
| KitchenuhmaykoosibIce Accretion2035RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2035 | 13.3081 | 15.8812 | 19.134 | 21.6418 | 24.1315
| KitchenuhmaykoosibIce Accretion2040RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2040 | 13.4563 | 16.0555 | 19.344 | 21.8791 | 24.3961
| KitchenuhmaykoosibIce Accretion2045RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2045 | 13.6045 | 16.2298 | 19.554 | 22.1164 | 24.6607
| KitchenuhmaykoosibIce Accretion2050RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2050 | 13.7402 | 16.3772 | 19.7208 | 22.2967 | 24.8573
| KitchenuhmaykoosibIce Accretion2055RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2055 | 13.7277 | 16.3503 | 19.6776 | 22.2398 | 24.7892
| KitchenuhmaykoosibIce Accretion2060RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2060 | 13.7151 | 16.3234 | 19.6344 | 22.1828 | 24.7212
| KitchenuhmaykoosibIce Accretion2065RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2065 | 13.7026 | 16.2966 | 19.5912 | 22.1259 | 24.6532
| KitchenuhmaykoosibIce Accretion2070RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2070 | 13.6901 | 16.2697 | 19.548 | 22.0689 | 24.5851
| KitchenuhmaykoosibIce Accretion2075RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2075 | 13.7527 | 16.3593 | 19.665 | 22.2062 | 24.7439
| KitchenuhmaykoosibIce Accretion2080RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2080 | 13.8153 | 16.4489 | 19.782 | 22.3435 | 24.9026
| KitchenuhmaykoosibIce Accretion2085RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2085 | 13.878 | 16.5386 | 19.899 | 22.4808 | 25.0614
| KitchenuhmaykoosibIce Accretion2090RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2090 | 13.8153 | 16.4539 | 19.782 | 22.3401 | 24.8951
| KitchenuhmaykoosibIce Accretion2095RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2095 | 13.6901 | 16.2796 | 19.548 | 22.0621 | 24.57
| KitchenuhmaykoosibIce Accretion2100RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2100 | 13.5648 | 16.1053 | 19.314 | 21.7841 | 24.2449
| KitchenuhmaykoosibIce Accretion2023RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2023 | 12.8634 | 15.3583 | 18.504 | 20.9299 | 23.3377
| KitchenuhmaykoosibIce Accretion2025RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2025 | 13.1598 | 15.7069 | 18.924 | 21.4045 | 23.8669
| KitchenuhmaykoosibIce Accretion2030RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2030 | 13.4563 | 16.0555 | 19.344 | 21.8791 | 24.3961
| KitchenuhmaykoosibIce Accretion2035RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2035 | 13.7527 | 16.4041 | 19.764 | 22.3537 | 24.9253
| KitchenuhmaykoosibIce Accretion2040RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2040 | 13.7318 | 16.3593 | 19.692 | 22.2587 | 24.8119
| KitchenuhmaykoosibIce Accretion2045RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2045 | 13.711 | 16.3145 | 19.62 | 22.1638 | 24.6985
| KitchenuhmaykoosibIce Accretion2050RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2050 | 13.7736 | 16.3892 | 19.704 | 22.252 | 24.7968
| KitchenuhmaykoosibIce Accretion2055RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2055 | 13.8571 | 16.5087 | 19.86 | 22.435 | 25.0085
| KitchenuhmaykoosibIce Accretion2060RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2060 | 13.8153 | 16.4539 | 19.782 | 22.3401 | 24.8951
| KitchenuhmaykoosibIce Accretion2065RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2065 | 13.6901 | 16.2796 | 19.548 | 22.0621 | 24.57
| KitchenuhmaykoosibIce Accretion2070RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2070 | 13.5272 | 16.0705 | 19.29 | 21.7638 | 24.2298
| KitchenuhmaykoosibIce Accretion2075RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2075 | 13.4897 | 16.0356 | 19.266 | 21.7435 | 24.2147
| KitchenuhmaykoosibIce Accretion2080RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2080 | 13.4521 | 16.0007 | 19.242 | 21.7231 | 24.1996
| KitchenuhmaykoosibIce Accretion2085RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2085 | 13.5147 | 16.068 | 19.314 | 21.8045 | 24.2903
| KitchenuhmaykoosibIce Accretion2090RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2090 | 13.5773 | 16.1352 | 19.386 | 21.8858 | 24.381
| KitchenuhmaykoosibIce Accretion2095RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2095 | 13.5773 | 16.1352 | 19.386 | 21.8858 | 24.381
| KitchenuhmaykoosibIce Accretion2100RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2100 | 13.5773 | 16.1352 | 19.386 | 21.8858 | 24.381
| KitchenuhmaykoosibWind2023RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2023 | 80.0839 | 86.2787 | 92.8096 | 99.3358 | 105.8554
| KitchenuhmaykoosibWind2025RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2025 | 80.1673 | 86.3814 | 92.9353 | 99.4818 | 106.0232
| KitchenuhmaykoosibWind2030RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2030 | 80.2507 | 86.484 | 93.0611 | 99.6278 | 106.191
| KitchenuhmaykoosibWind2035RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2035 | 80.3341 | 86.5867 | 93.1868 | 99.7739 | 106.3588
| KitchenuhmaykoosibWind2040RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2040 | 80.4175 | 86.6894 | 93.3125 | 99.9199 | 106.5266
| KitchenuhmaykoosibWind2045RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2045 | 80.5009 | 86.7921 | 93.4383 | 100.0659 | 106.6944
| KitchenuhmaykoosibWind2050RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2050 | 80.7527 | 87.0932 | 93.7977 | 100.4757 | 107.1559
| KitchenuhmaykoosibWind2055RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2055 | 80.9212 | 87.2917 | 94.0314 | 100.7396 | 107.4496
| KitchenuhmaykoosibWind2060RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2060 | 81.0896 | 87.4902 | 94.265 | 101.0034 | 107.7432
| KitchenuhmaykoosibWind2065RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2065 | 81.258 | 87.6887 | 94.4987 | 101.2672 | 108.0369
| KitchenuhmaykoosibWind2070RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2070 | 81.4264 | 87.8872 | 94.7324 | 101.531 | 108.3306
| KitchenuhmaykoosibWind2075RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2075 | 81.4198 | 87.8587 | 94.6757 | 101.4506 | 108.2274
| KitchenuhmaykoosibWind2080RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2080 | 81.4132 | 87.8302 | 94.6189 | 101.3702 | 108.1243
| KitchenuhmaykoosibWind2085RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2085 | 81.4065 | 87.8017 | 94.5622 | 101.2898 | 108.0212
| KitchenuhmaykoosibWind2090RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2090 | 81.3999 | 87.7732 | 94.5055 | 101.2094 | 107.918
| KitchenuhmaykoosibWind2095RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2095 | 81.3933 | 87.7446 | 94.4487 | 101.1291 | 107.8149
| KitchenuhmaykoosibWind2100RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2100 | 81.3867 | 87.7161 | 94.392 | 101.0487 | 107.7118
| KitchenuhmaykoosibWind2023RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2023 | 80.0839 | 86.2787 | 92.8096 | 99.3358 | 105.8554
| KitchenuhmaykoosibWind2025RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2025 | 80.1673 | 86.3814 | 92.9353 | 99.4818 | 106.0232
| KitchenuhmaykoosibWind2030RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2030 | 80.2507 | 86.484 | 93.0611 | 99.6278 | 106.191
| KitchenuhmaykoosibWind2035RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2035 | 80.3341 | 86.5867 | 93.1868 | 99.7739 | 106.3588
| KitchenuhmaykoosibWind2040RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2040 | 80.4175 | 86.6894 | 93.3125 | 99.9199 | 106.5266
| KitchenuhmaykoosibWind2045RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2045 | 80.5009 | 86.7921 | 93.4383 | 100.0659 | 106.6944
| KitchenuhmaykoosibWind2050RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2050 | 80.7527 | 87.0932 | 93.7977 | 100.4757 | 107.1559
| KitchenuhmaykoosibWind2055RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2055 | 80.9212 | 87.2917 | 94.0314 | 100.7396 | 107.4496
| KitchenuhmaykoosibWind2060RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2060 | 81.0896 | 87.4902 | 94.265 | 101.0034 | 107.7432
| KitchenuhmaykoosibWind2065RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2065 | 81.258 | 87.6887 | 94.4987 | 101.2672 | 108.0369
| KitchenuhmaykoosibWind2070RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2070 | 81.4264 | 87.8872 | 94.7324 | 101.531 | 108.3306
| KitchenuhmaykoosibWind2075RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2075 | 81.4165 | 87.8445 | 94.6473 | 101.4104 | 108.1759
| KitchenuhmaykoosibWind2080RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2080 | 81.4065 | 87.8017 | 94.5622 | 101.2898 | 108.0212
| KitchenuhmaykoosibWind2085RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2085 | 81.3966 | 87.7589 | 94.4771 | 101.1692 | 107.8665
| KitchenuhmaykoosibWind2090RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2090 | 81.4317 | 87.7503 | 94.4073 | 101.0487 | 107.6978
| KitchenuhmaykoosibWind2095RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2095 | 81.4767 | 87.7846 | 94.4227 | 101.0487 | 107.6838
| KitchenuhmaykoosibWind2100RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2100 | 81.5217 | 87.8188 | 94.438 | 101.0487 | 107.6698
| KitchenuhmaykoosibWind2023RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2023 | 80.0839 | 86.2787 | 92.8096 | 99.3358 | 105.8554
| KitchenuhmaykoosibWind2025RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2025 | 80.2507 | 86.484 | 93.0611 | 99.6278 | 106.191
| KitchenuhmaykoosibWind2030RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2030 | 80.4175 | 86.6894 | 93.3125 | 99.9199 | 106.5266
| KitchenuhmaykoosibWind2035RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2035 | 80.5843 | 86.8947 | 93.564 | 100.2119 | 106.8622
| KitchenuhmaykoosibWind2040RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2040 | 80.865 | 87.2256 | 93.9535 | 100.6516 | 107.3517
| KitchenuhmaykoosibWind2045RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2045 | 81.1457 | 87.5564 | 94.3429 | 101.0913 | 107.8411
| KitchenuhmaykoosibWind2050RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2050 | 81.4132 | 87.8302 | 94.6189 | 101.3702 | 108.1243
| KitchenuhmaykoosibWind2055RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2055 | 81.3999 | 87.7732 | 94.5055 | 101.2094 | 107.918
| KitchenuhmaykoosibWind2060RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2060 | 81.4317 | 87.7503 | 94.4073 | 101.0487 | 107.6978
| KitchenuhmaykoosibWind2065RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2065 | 81.4767 | 87.7846 | 94.4227 | 101.0487 | 107.6838
| KitchenuhmaykoosibWind2070RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2070 | 81.5191 | 87.7903 | 94.3797 | 100.9666 | 107.5614
| KitchenuhmaykoosibWind2075RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2075 | 81.5164 | 87.7617 | 94.3215 | 100.8846 | 107.4531
| KitchenuhmaykoosibWind2080RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2080 | 81.5138 | 87.7332 | 94.2632 | 100.8026 | 107.3447
| KitchenuhmaykoosibWind2085RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2085 | 81.6568 | 87.8958 | 94.4518 | 101.0142 | 107.5807
| KitchenuhmaykoosibWind2090RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2090 | 81.7998 | 88.0584 | 94.6404 | 101.2259 | 107.8166
| KitchenuhmaykoosibWind2095RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2095 | 81.7998 | 88.0584 | 94.6404 | 101.2259 | 107.8166
| KitchenuhmaykoosibWind2100RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2100 | 81.7998 | 88.0584 | 94.6404 | 101.2259 | 107.8166
| LakefieldIce Accretion2023RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2023 | 17.1526 | 20.4387 | 24.625 | 27.8262 | 30.996
| LakefieldIce Accretion2025RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2025 | 17.1468 | 20.4422 | 24.6333 | 27.8404 | 31.017
| LakefieldIce Accretion2030RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2030 | 17.141 | 20.4457 | 24.6417 | 27.8545 | 31.038
| LakefieldIce Accretion2035RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2035 | 17.1352 | 20.4491 | 24.65 | 27.8686 | 31.059
| LakefieldIce Accretion2040RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2040 | 17.1294 | 20.4526 | 24.6583 | 27.8827 | 31.08
| LakefieldIce Accretion2045RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2045 | 17.1236 | 20.456 | 24.6667 | 27.8969 | 31.101
| LakefieldIce Accretion2050RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2050 | 17.0795 | 20.4305 | 24.66 | 27.9053 | 31.1283
| LakefieldIce Accretion2055RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2055 | 17.0413 | 20.4014 | 24.645 | 27.8997 | 31.1346
| LakefieldIce Accretion2060RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2060 | 17.003 | 20.3724 | 24.63 | 27.894 | 31.1409
| LakefieldIce Accretion2065RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2065 | 16.9647 | 20.3433 | 24.615 | 27.8884 | 31.1472
| LakefieldIce Accretion2070RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2070 | 16.9265 | 20.3143 | 24.6 | 27.8827 | 31.1535
| LakefieldIce Accretion2075RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2075 | 16.996 | 20.418 | 24.7417 | 28.0522 | 31.353
| LakefieldIce Accretion2080RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2080 | 17.0656 | 20.5218 | 24.8833 | 28.2217 | 31.5525
| LakefieldIce Accretion2085RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2085 | 17.1352 | 20.6255 | 25.025 | 28.3912 | 31.752
| LakefieldIce Accretion2090RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2090 | 17.2048 | 20.7292 | 25.1667 | 28.5607 | 31.9515
| LakefieldIce Accretion2095RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2095 | 17.2744 | 20.833 | 25.3083 | 28.7302 | 32.151
| LakefieldIce Accretion2100RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2100 | 17.344 | 20.9367 | 25.45 | 28.8997 | 32.3505
| LakefieldIce Accretion2023RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2023 | 17.1526 | 20.4387 | 24.625 | 27.8262 | 30.996
| LakefieldIce Accretion2025RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2025 | 17.1468 | 20.4422 | 24.6333 | 27.8404 | 31.017
| LakefieldIce Accretion2030RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2030 | 17.141 | 20.4457 | 24.6417 | 27.8545 | 31.038
| LakefieldIce Accretion2035RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2035 | 17.1352 | 20.4491 | 24.65 | 27.8686 | 31.059
| LakefieldIce Accretion2040RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2040 | 17.1294 | 20.4526 | 24.6583 | 27.8827 | 31.08
| LakefieldIce Accretion2045RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2045 | 17.1236 | 20.456 | 24.6667 | 27.8969 | 31.101
| LakefieldIce Accretion2050RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2050 | 17.0795 | 20.4305 | 24.66 | 27.9053 | 31.1283
| LakefieldIce Accretion2055RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2055 | 17.0413 | 20.4014 | 24.645 | 27.8997 | 31.1346
| LakefieldIce Accretion2060RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2060 | 17.003 | 20.3724 | 24.63 | 27.894 | 31.1409
| LakefieldIce Accretion2065RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2065 | 16.9647 | 20.3433 | 24.615 | 27.8884 | 31.1472
| LakefieldIce Accretion2070RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2070 | 16.9265 | 20.3143 | 24.6 | 27.8827 | 31.1535
| LakefieldIce Accretion2075RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2075 | 17.0308 | 20.4699 | 24.8125 | 28.137 | 31.4528
| LakefieldIce Accretion2080RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2080 | 17.1352 | 20.6255 | 25.025 | 28.3912 | 31.752
| LakefieldIce Accretion2085RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2085 | 17.2396 | 20.7811 | 25.2375 | 28.6455 | 32.0512
| LakefieldIce Accretion2090RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2090 | 17.2048 | 20.8122 | 25.35 | 28.815 | 32.277
| LakefieldIce Accretion2095RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2095 | 17.0656 | 20.6877 | 25.25 | 28.7302 | 32.2035
| LakefieldIce Accretion2100RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2100 | 16.9265 | 20.5633 | 25.15 | 28.6455 | 32.13
| LakefieldIce Accretion2023RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2023 | 17.1526 | 20.4387 | 24.625 | 27.8262 | 30.996
| LakefieldIce Accretion2025RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2025 | 17.141 | 20.4457 | 24.6417 | 27.8545 | 31.038
| LakefieldIce Accretion2030RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2030 | 17.1294 | 20.4526 | 24.6583 | 27.8827 | 31.08
| LakefieldIce Accretion2035RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2035 | 17.1178 | 20.4595 | 24.675 | 27.911 | 31.122
| LakefieldIce Accretion2040RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2040 | 17.054 | 20.4111 | 24.65 | 27.9016 | 31.1325
| LakefieldIce Accretion2045RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2045 | 16.9902 | 20.3627 | 24.625 | 27.8922 | 31.143
| LakefieldIce Accretion2050RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2050 | 17.0656 | 20.5218 | 24.8833 | 28.2217 | 31.5525
| LakefieldIce Accretion2055RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2055 | 17.2048 | 20.7292 | 25.1667 | 28.5607 | 31.9515
| LakefieldIce Accretion2060RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2060 | 17.2048 | 20.8122 | 25.35 | 28.815 | 32.277
| LakefieldIce Accretion2065RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2065 | 17.0656 | 20.6877 | 25.25 | 28.7302 | 32.2035
| LakefieldIce Accretion2070RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2070 | 16.6887 | 20.3143 | 24.8917 | 28.3724 | 31.8465
| LakefieldIce Accretion2075RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2075 | 16.451 | 20.0652 | 24.6333 | 28.0993 | 31.563
| LakefieldIce Accretion2080RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2080 | 16.2132 | 19.8163 | 24.375 | 27.8262 | 31.2795
| LakefieldIce Accretion2085RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2085 | 15.8131 | 19.3909 | 23.9125 | 27.346 | 30.7755
| LakefieldIce Accretion2090RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2090 | 15.413 | 18.9655 | 23.45 | 26.8657 | 30.2715
| LakefieldIce Accretion2095RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2095 | 15.413 | 18.9655 | 23.45 | 26.8657 | 30.2715
| LakefieldIce Accretion2100RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2100 | 15.413 | 18.9655 | 23.45 | 26.8657 | 30.2715
| LakefieldWind2023RCP4.5 | Lakefield | Wind | RCP4.5 | 2023 | 74.705 | 80.5079 | 86.6364 | 92.7562 | 98.8635
| LakefieldWind2025RCP4.5 | Lakefield | Wind | RCP4.5 | 2025 | 74.788 | 80.6132 | 86.7683 | 92.9111 | 99.0416
| LakefieldWind2030RCP4.5 | Lakefield | Wind | RCP4.5 | 2030 | 74.8709 | 80.7185 | 86.9001 | 93.066 | 99.2197
| LakefieldWind2035RCP4.5 | Lakefield | Wind | RCP4.5 | 2035 | 74.9538 | 80.8238 | 87.032 | 93.2209 | 99.3979
| LakefieldWind2040RCP4.5 | Lakefield | Wind | RCP4.5 | 2040 | 75.0367 | 80.9291 | 87.1639 | 93.3758 | 99.576
| LakefieldWind2045RCP4.5 | Lakefield | Wind | RCP4.5 | 2045 | 75.1197 | 81.0344 | 87.2957 | 93.5307 | 99.7541
| LakefieldWind2050RCP4.5 | Lakefield | Wind | RCP4.5 | 2050 | 75.2056 | 81.1285 | 87.3966 | 93.6377 | 99.8694
| LakefieldWind2055RCP4.5 | Lakefield | Wind | RCP4.5 | 2055 | 75.2085 | 81.1173 | 87.3657 | 93.5899 | 99.8067
| LakefieldWind2060RCP4.5 | Lakefield | Wind | RCP4.5 | 2060 | 75.2115 | 81.1061 | 87.3347 | 93.542 | 99.7439
| LakefieldWind2065RCP4.5 | Lakefield | Wind | RCP4.5 | 2065 | 75.2145 | 81.0949 | 87.3038 | 93.4942 | 99.6812
| LakefieldWind2070RCP4.5 | Lakefield | Wind | RCP4.5 | 2070 | 75.2174 | 81.0837 | 87.2728 | 93.4463 | 99.6184
| LakefieldWind2075RCP4.5 | Lakefield | Wind | RCP4.5 | 2075 | 75.2224 | 81.0944 | 87.2914 | 93.4708 | 99.6495
| LakefieldWind2080RCP4.5 | Lakefield | Wind | RCP4.5 | 2080 | 75.2273 | 81.1051 | 87.3101 | 93.4954 | 99.6805
| LakefieldWind2085RCP4.5 | Lakefield | Wind | RCP4.5 | 2085 | 75.2323 | 81.1157 | 87.3287 | 93.5199 | 99.7116
| LakefieldWind2090RCP4.5 | Lakefield | Wind | RCP4.5 | 2090 | 75.2372 | 81.1264 | 87.3473 | 93.5445 | 99.7426
| LakefieldWind2095RCP4.5 | Lakefield | Wind | RCP4.5 | 2095 | 75.2422 | 81.137 | 87.366 | 93.569 | 99.7737
| LakefieldWind2100RCP4.5 | Lakefield | Wind | RCP4.5 | 2100 | 75.2471 | 81.1477 | 87.3846 | 93.5935 | 99.8047
| LakefieldWind2023RCP6.0 | Lakefield | Wind | RCP6.0 | 2023 | 74.705 | 80.5079 | 86.6364 | 92.7562 | 98.8635
| LakefieldWind2025RCP6.0 | Lakefield | Wind | RCP6.0 | 2025 | 74.788 | 80.6132 | 86.7683 | 92.9111 | 99.0416
| LakefieldWind2030RCP6.0 | Lakefield | Wind | RCP6.0 | 2030 | 74.8709 | 80.7185 | 86.9001 | 93.066 | 99.2197
| LakefieldWind2035RCP6.0 | Lakefield | Wind | RCP6.0 | 2035 | 74.9538 | 80.8238 | 87.032 | 93.2209 | 99.3979
| LakefieldWind2040RCP6.0 | Lakefield | Wind | RCP6.0 | 2040 | 75.0367 | 80.9291 | 87.1639 | 93.3758 | 99.576
| LakefieldWind2045RCP6.0 | Lakefield | Wind | RCP6.0 | 2045 | 75.1197 | 81.0344 | 87.2957 | 93.5307 | 99.7541
| LakefieldWind2050RCP6.0 | Lakefield | Wind | RCP6.0 | 2050 | 75.2056 | 81.1285 | 87.3966 | 93.6377 | 99.8694
| LakefieldWind2055RCP6.0 | Lakefield | Wind | RCP6.0 | 2055 | 75.2085 | 81.1173 | 87.3657 | 93.5899 | 99.8067
| LakefieldWind2060RCP6.0 | Lakefield | Wind | RCP6.0 | 2060 | 75.2115 | 81.1061 | 87.3347 | 93.542 | 99.7439
| LakefieldWind2065RCP6.0 | Lakefield | Wind | RCP6.0 | 2065 | 75.2145 | 81.0949 | 87.3038 | 93.4942 | 99.6812
| LakefieldWind2070RCP6.0 | Lakefield | Wind | RCP6.0 | 2070 | 75.2174 | 81.0837 | 87.2728 | 93.4463 | 99.6184
| LakefieldWind2075RCP6.0 | Lakefield | Wind | RCP6.0 | 2075 | 75.2249 | 81.0997 | 87.3007 | 93.4831 | 99.665
| LakefieldWind2080RCP6.0 | Lakefield | Wind | RCP6.0 | 2080 | 75.2323 | 81.1157 | 87.3287 | 93.5199 | 99.7116
| LakefieldWind2085RCP6.0 | Lakefield | Wind | RCP6.0 | 2085 | 75.2397 | 81.1317 | 87.3567 | 93.5567 | 99.7582
| LakefieldWind2090RCP6.0 | Lakefield | Wind | RCP6.0 | 2090 | 75.3412 | 81.2543 | 87.505 | 93.7254 | 99.9485
| LakefieldWind2095RCP6.0 | Lakefield | Wind | RCP6.0 | 2095 | 75.4353 | 81.361 | 87.6254 | 93.8573 | 100.0923
| LakefieldWind2100RCP6.0 | Lakefield | Wind | RCP6.0 | 2100 | 75.5293 | 81.4676 | 87.7458 | 93.9892 | 100.2361
| LakefieldWind2023RCP8.5 | Lakefield | Wind | RCP8.5 | 2023 | 74.705 | 80.5079 | 86.6364 | 92.7562 | 98.8635
| LakefieldWind2025RCP8.5 | Lakefield | Wind | RCP8.5 | 2025 | 74.8709 | 80.7185 | 86.9001 | 93.066 | 99.2197
| LakefieldWind2030RCP8.5 | Lakefield | Wind | RCP8.5 | 2030 | 75.0367 | 80.9291 | 87.1639 | 93.3758 | 99.576
| LakefieldWind2035RCP8.5 | Lakefield | Wind | RCP8.5 | 2035 | 75.2026 | 81.1397 | 87.4276 | 93.6856 | 99.9322
| LakefieldWind2040RCP8.5 | Lakefield | Wind | RCP8.5 | 2040 | 75.2075 | 81.121 | 87.376 | 93.6058 | 99.8276
| LakefieldWind2045RCP8.5 | Lakefield | Wind | RCP8.5 | 2045 | 75.2125 | 81.1024 | 87.3244 | 93.5261 | 99.723
| LakefieldWind2050RCP8.5 | Lakefield | Wind | RCP8.5 | 2050 | 75.2273 | 81.1051 | 87.3101 | 93.4954 | 99.6805
| LakefieldWind2055RCP8.5 | Lakefield | Wind | RCP8.5 | 2055 | 75.2372 | 81.1264 | 87.3473 | 93.5445 | 99.7426
| LakefieldWind2060RCP8.5 | Lakefield | Wind | RCP8.5 | 2060 | 75.3412 | 81.2543 | 87.505 | 93.7254 | 99.9485
| LakefieldWind2065RCP8.5 | Lakefield | Wind | RCP8.5 | 2065 | 75.4353 | 81.361 | 87.6254 | 93.8573 | 100.0923
| LakefieldWind2070RCP8.5 | Lakefield | Wind | RCP8.5 | 2070 | 75.6135 | 81.5769 | 87.8863 | 94.161 | 100.4354
| LakefieldWind2075RCP8.5 | Lakefield | Wind | RCP8.5 | 2075 | 75.6976 | 81.6862 | 88.0267 | 94.3328 | 100.6348
| LakefieldWind2080RCP8.5 | Lakefield | Wind | RCP8.5 | 2080 | 75.7818 | 81.7955 | 88.1672 | 94.5045 | 100.8341
| LakefieldWind2085RCP8.5 | Lakefield | Wind | RCP8.5 | 2085 | 75.8858 | 81.9275 | 88.3349 | 94.7024 | 101.0645
| LakefieldWind2090RCP8.5 | Lakefield | Wind | RCP8.5 | 2090 | 75.9897 | 82.0595 | 88.5026 | 94.9002 | 101.2949
| LakefieldWind2095RCP8.5 | Lakefield | Wind | RCP8.5 | 2095 | 75.9897 | 82.0595 | 88.5026 | 94.9002 | 101.2949
| LakefieldWind2100RCP8.5 | Lakefield | Wind | RCP8.5 | 2100 | 75.9897 | 82.0595 | 88.5026 | 94.9002 | 101.2949
| Lansdowne HouseIce Accretion2023RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2023 | 10.3438 | 12.3255 | 14.835 | 16.7466 | 18.6732
| Lansdowne HouseIce Accretion2025RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2025 | 10.4655 | 12.4666 | 15.0025 | 16.9359 | 18.8811
| Lansdowne HouseIce Accretion2030RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2030 | 10.5873 | 12.6077 | 15.17 | 17.1252 | 19.089
| Lansdowne HouseIce Accretion2035RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2035 | 10.7091 | 12.7488 | 15.3375 | 17.3144 | 19.2969
| Lansdowne HouseIce Accretion2040RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2040 | 10.8308 | 12.8899 | 15.505 | 17.5037 | 19.5048
| Lansdowne HouseIce Accretion2045RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2045 | 10.9526 | 13.031 | 15.6725 | 17.693 | 19.7127
| Lansdowne HouseIce Accretion2050RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2050 | 11.0786 | 13.1696 | 15.831 | 17.8653 | 19.8979
| Lansdowne HouseIce Accretion2055RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2055 | 11.0827 | 13.1671 | 15.822 | 17.8483 | 19.8752
| Lansdowne HouseIce Accretion2060RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2060 | 11.0869 | 13.1646 | 15.813 | 17.8314 | 19.8526
| Lansdowne HouseIce Accretion2065RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2065 | 11.0911 | 13.1621 | 15.804 | 17.8145 | 19.8299
| Lansdowne HouseIce Accretion2070RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2070 | 11.0953 | 13.1596 | 15.795 | 17.7975 | 19.8072
| Lansdowne HouseIce Accretion2075RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2075 | 11.1109 | 13.1804 | 15.8175 | 17.8257 | 19.8387
| Lansdowne HouseIce Accretion2080RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2080 | 11.1266 | 13.2011 | 15.84 | 17.854 | 19.8702
| Lansdowne HouseIce Accretion2085RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2085 | 11.1422 | 13.2219 | 15.8625 | 17.8822 | 19.9017
| Lansdowne HouseIce Accretion2090RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2090 | 11.1579 | 13.2426 | 15.885 | 17.9105 | 19.9332
| Lansdowne HouseIce Accretion2095RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2095 | 11.1735 | 13.2634 | 15.9075 | 17.9387 | 19.9647
| Lansdowne HouseIce Accretion2100RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2100 | 11.1892 | 13.2841 | 15.93 | 17.967 | 19.9962
| Lansdowne HouseIce Accretion2023RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2023 | 10.3438 | 12.3255 | 14.835 | 16.7466 | 18.6732
| Lansdowne HouseIce Accretion2025RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2025 | 10.4655 | 12.4666 | 15.0025 | 16.9359 | 18.8811
| Lansdowne HouseIce Accretion2030RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2030 | 10.5873 | 12.6077 | 15.17 | 17.1252 | 19.089
| Lansdowne HouseIce Accretion2035RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2035 | 10.7091 | 12.7488 | 15.3375 | 17.3144 | 19.2969
| Lansdowne HouseIce Accretion2040RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2040 | 10.8308 | 12.8899 | 15.505 | 17.5037 | 19.5048
| Lansdowne HouseIce Accretion2045RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2045 | 10.9526 | 13.031 | 15.6725 | 17.693 | 19.7127
| Lansdowne HouseIce Accretion2050RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2050 | 11.0786 | 13.1696 | 15.831 | 17.8653 | 19.8979
| Lansdowne HouseIce Accretion2055RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2055 | 11.0827 | 13.1671 | 15.822 | 17.8483 | 19.8752
| Lansdowne HouseIce Accretion2060RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2060 | 11.0869 | 13.1646 | 15.813 | 17.8314 | 19.8526
| Lansdowne HouseIce Accretion2065RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2065 | 11.0911 | 13.1621 | 15.804 | 17.8145 | 19.8299
| Lansdowne HouseIce Accretion2070RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2070 | 11.0953 | 13.1596 | 15.795 | 17.7975 | 19.8072
| Lansdowne HouseIce Accretion2075RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2075 | 11.1188 | 13.1908 | 15.8287 | 17.8399 | 19.8544
| Lansdowne HouseIce Accretion2080RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2080 | 11.1422 | 13.2219 | 15.8625 | 17.8822 | 19.9017
| Lansdowne HouseIce Accretion2085RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2085 | 11.1657 | 13.253 | 15.8963 | 17.9246 | 19.9489
| Lansdowne HouseIce Accretion2090RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2090 | 11.0257 | 13.0891 | 15.695 | 17.7014 | 19.7001
| Lansdowne HouseIce Accretion2095RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2095 | 10.8622 | 12.8941 | 15.46 | 17.4359 | 19.404
| Lansdowne HouseIce Accretion2100RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2100 | 10.6986 | 12.699 | 15.225 | 17.1703 | 19.1079
| Lansdowne HouseIce Accretion2023RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2023 | 10.3438 | 12.3255 | 14.835 | 16.7466 | 18.6732
| Lansdowne HouseIce Accretion2025RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2025 | 10.5873 | 12.6077 | 15.17 | 17.1252 | 19.089
| Lansdowne HouseIce Accretion2030RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2030 | 10.8308 | 12.8899 | 15.505 | 17.5037 | 19.5048
| Lansdowne HouseIce Accretion2035RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2035 | 11.0744 | 13.1721 | 15.84 | 17.8822 | 19.9206
| Lansdowne HouseIce Accretion2040RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2040 | 11.0813 | 13.1679 | 15.825 | 17.854 | 19.8828
| Lansdowne HouseIce Accretion2045RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2045 | 11.0883 | 13.1638 | 15.81 | 17.8257 | 19.845
| Lansdowne HouseIce Accretion2050RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2050 | 11.1266 | 13.2011 | 15.84 | 17.854 | 19.8702
| Lansdowne HouseIce Accretion2055RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2055 | 11.1579 | 13.2426 | 15.885 | 17.9105 | 19.9332
| Lansdowne HouseIce Accretion2060RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2060 | 11.0257 | 13.0891 | 15.695 | 17.7014 | 19.7001
| Lansdowne HouseIce Accretion2065RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2065 | 10.8622 | 12.8941 | 15.46 | 17.4359 | 19.404
| Lansdowne HouseIce Accretion2070RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2070 | 10.7299 | 12.7405 | 15.28 | 17.2325 | 19.1835
| Lansdowne HouseIce Accretion2075RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2075 | 10.7613 | 12.782 | 15.335 | 17.2947 | 19.2591
| Lansdowne HouseIce Accretion2080RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2080 | 10.7926 | 12.8235 | 15.39 | 17.3568 | 19.3347
| Lansdowne HouseIce Accretion2085RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2085 | 10.6308 | 12.6367 | 15.1725 | 17.1195 | 19.0701
| Lansdowne HouseIce Accretion2090RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2090 | 10.469 | 12.45 | 14.955 | 16.8822 | 18.8055
| Lansdowne HouseIce Accretion2095RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2095 | 10.469 | 12.45 | 14.955 | 16.8822 | 18.8055
| Lansdowne HouseIce Accretion2100RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2100 | 10.469 | 12.45 | 14.955 | 16.8822 | 18.8055
| Lansdowne HouseWind2023RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2023 | 73.6089 | 79.3188 | 85.34 | 91.3593 | 97.3651
| Lansdowne HouseWind2025RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2025 | 73.7018 | 79.4268 | 85.4647 | 91.4972 | 97.5202
| Lansdowne HouseWind2030RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2030 | 73.7948 | 79.5348 | 85.5893 | 91.6352 | 97.6752
| Lansdowne HouseWind2035RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2035 | 73.8878 | 79.6429 | 85.714 | 91.7731 | 97.8302
| Lansdowne HouseWind2040RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2040 | 73.9807 | 79.7509 | 85.8387 | 91.911 | 97.9853
| Lansdowne HouseWind2045RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2045 | 74.0737 | 79.8589 | 85.9633 | 92.049 | 98.1403
| Lansdowne HouseWind2050RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2050 | 74.2401 | 80.046 | 86.1747 | 92.2815 | 98.3961
| Lansdowne HouseWind2055RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2055 | 74.3135 | 80.1251 | 86.2614 | 92.3761 | 98.4969
| Lansdowne HouseWind2060RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2060 | 74.3869 | 80.2041 | 86.3481 | 92.4707 | 98.5977
| Lansdowne HouseWind2065RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2065 | 74.4602 | 80.2832 | 86.4348 | 92.5653 | 98.6985
| Lansdowne HouseWind2070RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2070 | 74.5336 | 80.3622 | 86.5215 | 92.6599 | 98.7992
| Lansdowne HouseWind2075RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2075 | 74.6168 | 80.4558 | 86.6263 | 92.7751 | 98.9236
| Lansdowne HouseWind2080RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2080 | 74.7 | 80.5493 | 86.7312 | 92.8903 | 99.048
| Lansdowne HouseWind2085RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2085 | 74.7832 | 80.6429 | 86.836 | 93.0055 | 99.1723
| Lansdowne HouseWind2090RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2090 | 74.8664 | 80.7364 | 86.9408 | 93.1207 | 99.2967
| Lansdowne HouseWind2095RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2095 | 74.9496 | 80.8299 | 87.0457 | 93.2359 | 99.421
| Lansdowne HouseWind2100RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2100 | 75.0327 | 80.9235 | 87.1505 | 93.3511 | 99.5454
| Lansdowne HouseWind2023RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2023 | 73.6089 | 79.3188 | 85.34 | 91.3593 | 97.3651
| Lansdowne HouseWind2025RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2025 | 73.7018 | 79.4268 | 85.4647 | 91.4972 | 97.5202
| Lansdowne HouseWind2030RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2030 | 73.7948 | 79.5348 | 85.5893 | 91.6352 | 97.6752
| Lansdowne HouseWind2035RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2035 | 73.8878 | 79.6429 | 85.714 | 91.7731 | 97.8302
| Lansdowne HouseWind2040RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2040 | 73.9807 | 79.7509 | 85.8387 | 91.911 | 97.9853
| Lansdowne HouseWind2045RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2045 | 74.0737 | 79.8589 | 85.9633 | 92.049 | 98.1403
| Lansdowne HouseWind2050RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2050 | 74.2401 | 80.046 | 86.1747 | 92.2815 | 98.3961
| Lansdowne HouseWind2055RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2055 | 74.3135 | 80.1251 | 86.2614 | 92.3761 | 98.4969
| Lansdowne HouseWind2060RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2060 | 74.3869 | 80.2041 | 86.3481 | 92.4707 | 98.5977
| Lansdowne HouseWind2065RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2065 | 74.4602 | 80.2832 | 86.4348 | 92.5653 | 98.6985
| Lansdowne HouseWind2070RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2070 | 74.5336 | 80.3622 | 86.5215 | 92.6599 | 98.7992
| Lansdowne HouseWind2075RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2075 | 74.6584 | 80.5025 | 86.6788 | 92.8327 | 98.9858
| Lansdowne HouseWind2080RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2080 | 74.7832 | 80.6429 | 86.836 | 93.0055 | 99.1723
| Lansdowne HouseWind2085RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2085 | 74.908 | 80.7832 | 86.9933 | 93.1783 | 99.3588
| Lansdowne HouseWind2090RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2090 | 74.9716 | 80.8102 | 86.9692 | 93.1146 | 99.2547
| Lansdowne HouseWind2095RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2095 | 74.9104 | 80.6969 | 86.7878 | 92.8781 | 98.964
| Lansdowne HouseWind2100RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2100 | 74.8492 | 80.5836 | 86.6065 | 92.6417 | 98.6733
| Lansdowne HouseWind2023RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2023 | 73.6089 | 79.3188 | 85.34 | 91.3593 | 97.3651
| Lansdowne HouseWind2025RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2025 | 73.7948 | 79.5348 | 85.5893 | 91.6352 | 97.6752
| Lansdowne HouseWind2030RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2030 | 73.9807 | 79.7509 | 85.8387 | 91.911 | 97.9853
| Lansdowne HouseWind2035RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2035 | 74.1667 | 79.967 | 86.088 | 92.1869 | 98.2954
| Lansdowne HouseWind2040RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2040 | 74.289 | 80.0987 | 86.2325 | 92.3446 | 98.4633
| Lansdowne HouseWind2045RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2045 | 74.4113 | 80.2305 | 86.377 | 92.5022 | 98.6313
| Lansdowne HouseWind2050RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2050 | 74.7 | 80.5493 | 86.7312 | 92.8903 | 99.048
| Lansdowne HouseWind2055RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2055 | 74.8664 | 80.7364 | 86.9408 | 93.1207 | 99.2967
| Lansdowne HouseWind2060RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2060 | 74.9716 | 80.8102 | 86.9692 | 93.1146 | 99.2547
| Lansdowne HouseWind2065RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2065 | 74.9104 | 80.6969 | 86.7878 | 92.8781 | 98.964
| Lansdowne HouseWind2070RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2070 | 75.0548 | 80.8234 | 86.8898 | 92.963 | 99.0318
| Lansdowne HouseWind2075RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2075 | 75.2603 | 81.0631 | 87.1732 | 93.2844 | 99.3903
| Lansdowne HouseWind2080RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2080 | 75.4658 | 81.3029 | 87.4565 | 93.6057 | 99.7489
| Lansdowne HouseWind2085RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2085 | 75.5942 | 81.4729 | 87.6732 | 93.8649 | 100.0493
| Lansdowne HouseWind2090RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2090 | 75.7227 | 81.6428 | 87.89 | 94.1242 | 100.3496
| Lansdowne HouseWind2095RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2095 | 75.7227 | 81.6428 | 87.89 | 94.1242 | 100.3496
| Lansdowne HouseWind2100RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2100 | 75.7227 | 81.6428 | 87.89 | 94.1242 | 100.3496
| LeamingtonIce Accretion2023RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2023 | 18.3536 | 22.0083 | 26.628 | 30.1529 | 33.6924
| LeamingtonIce Accretion2025RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2025 | 18.253 | 21.9153 | 26.5393 | 30.0685 | 33.6042
| LeamingtonIce Accretion2030RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2030 | 18.1523 | 21.8224 | 26.4507 | 29.9842 | 33.516
| LeamingtonIce Accretion2035RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2035 | 18.0516 | 21.7294 | 26.362 | 29.8998 | 33.4278
| LeamingtonIce Accretion2040RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2040 | 17.951 | 21.6364 | 26.2733 | 29.8154 | 33.3396
| LeamingtonIce Accretion2045RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2045 | 17.8503 | 21.5435 | 26.1847 | 29.7311 | 33.2514
| LeamingtonIce Accretion2050RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2050 | 17.2275 | 20.8602 | 25.4184 | 28.8936 | 32.3376
| LeamingtonIce Accretion2055RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2055 | 16.7053 | 20.2699 | 24.7408 | 28.1406 | 31.5121
| LeamingtonIce Accretion2060RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2060 | 16.1832 | 19.6796 | 24.0632 | 27.3876 | 30.6865
| LeamingtonIce Accretion2065RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2065 | 15.661 | 19.0893 | 23.3856 | 26.6346 | 29.861
| LeamingtonIce Accretion2070RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2070 | 15.1388 | 18.499 | 22.708 | 25.8815 | 29.0354
| LeamingtonIce Accretion2075RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2075 | 14.7849 | 18.0846 | 22.2133 | 25.3278 | 28.4239
| LeamingtonIce Accretion2080RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2080 | 14.4309 | 17.6701 | 21.7187 | 24.7741 | 27.8124
| LeamingtonIce Accretion2085RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2085 | 14.077 | 17.2557 | 21.224 | 24.2204 | 27.2009
| LeamingtonIce Accretion2090RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2090 | 13.723 | 16.8413 | 20.7293 | 23.6667 | 26.5894
| LeamingtonIce Accretion2095RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2095 | 13.3691 | 16.4268 | 20.2347 | 23.113 | 25.9778
| LeamingtonIce Accretion2100RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2100 | 13.0151 | 16.0124 | 19.74 | 22.5593 | 25.3663
| LeamingtonIce Accretion2023RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2023 | 18.3536 | 22.0083 | 26.628 | 30.1529 | 33.6924
| LeamingtonIce Accretion2025RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2025 | 18.253 | 21.9153 | 26.5393 | 30.0685 | 33.6042
| LeamingtonIce Accretion2030RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2030 | 18.1523 | 21.8224 | 26.4507 | 29.9842 | 33.516
| LeamingtonIce Accretion2035RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2035 | 18.0516 | 21.7294 | 26.362 | 29.8998 | 33.4278
| LeamingtonIce Accretion2040RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2040 | 17.951 | 21.6364 | 26.2733 | 29.8154 | 33.3396
| LeamingtonIce Accretion2045RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2045 | 17.8503 | 21.5435 | 26.1847 | 29.7311 | 33.2514
| LeamingtonIce Accretion2050RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2050 | 17.2275 | 20.8602 | 25.4184 | 28.8936 | 32.3376
| LeamingtonIce Accretion2055RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2055 | 16.7053 | 20.2699 | 24.7408 | 28.1406 | 31.5121
| LeamingtonIce Accretion2060RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2060 | 16.1832 | 19.6796 | 24.0632 | 27.3876 | 30.6865
| LeamingtonIce Accretion2065RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2065 | 15.661 | 19.0893 | 23.3856 | 26.6346 | 29.861
| LeamingtonIce Accretion2070RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2070 | 15.1388 | 18.499 | 22.708 | 25.8815 | 29.0354
| LeamingtonIce Accretion2075RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2075 | 14.6079 | 17.8774 | 21.966 | 25.051 | 28.1182
| LeamingtonIce Accretion2080RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2080 | 14.077 | 17.2557 | 21.224 | 24.2204 | 27.2009
| LeamingtonIce Accretion2085RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2085 | 13.546 | 16.634 | 20.482 | 23.3899 | 26.2836
| LeamingtonIce Accretion2090RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2090 | 11.8656 | 14.618 | 18.0413 | 20.6293 | 23.2142
| LeamingtonIce Accretion2095RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2095 | 10.716 | 13.2236 | 16.3427 | 18.6992 | 21.0622
| LeamingtonIce Accretion2100RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2100 | 9.5665 | 11.8292 | 14.644 | 16.7692 | 18.9101
| LeamingtonIce Accretion2023RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2023 | 18.3536 | 22.0083 | 26.628 | 30.1529 | 33.6924
| LeamingtonIce Accretion2025RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2025 | 18.1523 | 21.8224 | 26.4507 | 29.9842 | 33.516
| LeamingtonIce Accretion2030RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2030 | 17.951 | 21.6364 | 26.2733 | 29.8154 | 33.3396
| LeamingtonIce Accretion2035RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2035 | 17.7496 | 21.4505 | 26.096 | 29.6467 | 33.1632
| LeamingtonIce Accretion2040RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2040 | 16.8794 | 20.4667 | 24.9667 | 28.3916 | 31.7873
| LeamingtonIce Accretion2045RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2045 | 16.0091 | 19.4829 | 23.8373 | 27.1366 | 30.4114
| LeamingtonIce Accretion2050RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2050 | 14.4309 | 17.6701 | 21.7187 | 24.7741 | 27.8124
| LeamingtonIce Accretion2055RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2055 | 13.723 | 16.8413 | 20.7293 | 23.6667 | 26.5894
| LeamingtonIce Accretion2060RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2060 | 11.8656 | 14.618 | 18.0413 | 20.6293 | 23.2142
| LeamingtonIce Accretion2065RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2065 | 10.716 | 13.2236 | 16.3427 | 18.6992 | 21.0622
| LeamingtonIce Accretion2070RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2070 | 9.0469 | 11.2094 | 13.888 | 15.9149 | 17.9458
| LeamingtonIce Accretion2075RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2075 | 8.5274 | 10.5897 | 13.132 | 15.0606 | 16.9814
| LeamingtonIce Accretion2080RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2080 | 8.0078 | 9.97 | 12.376 | 14.2064 | 16.0171
| LeamingtonIce Accretion2085RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2085 | 7.2577 | 9.0636 | 11.284 | 12.9724 | 14.6412
| LeamingtonIce Accretion2090RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2090 | 6.5076 | 8.1572 | 10.192 | 11.7384 | 13.2653
| LeamingtonIce Accretion2095RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2095 | 6.5076 | 8.1572 | 10.192 | 11.7384 | 13.2653
| LeamingtonIce Accretion2100RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2100 | 6.5076 | 8.1572 | 10.192 | 11.7384 | 13.2653
| LeamingtonWind2023RCP4.5 | Leamington | Wind | RCP4.5 | 2023 | 85.0782 | 91.6686 | 98.6174 | 105.5521 | 112.4909
| LeamingtonWind2025RCP4.5 | Leamington | Wind | RCP4.5 | 2025 | 85.1784 | 91.7977 | 98.7824 | 105.7461 | 112.7162
| LeamingtonWind2030RCP4.5 | Leamington | Wind | RCP4.5 | 2030 | 85.2785 | 91.9268 | 98.9473 | 105.9401 | 112.9415
| LeamingtonWind2035RCP4.5 | Leamington | Wind | RCP4.5 | 2035 | 85.3786 | 92.056 | 99.1123 | 106.134 | 113.1668
| LeamingtonWind2040RCP4.5 | Leamington | Wind | RCP4.5 | 2040 | 85.4788 | 92.1851 | 99.2773 | 106.328 | 113.3921
| LeamingtonWind2045RCP4.5 | Leamington | Wind | RCP4.5 | 2045 | 85.5789 | 92.3142 | 99.4422 | 106.522 | 113.6174
| LeamingtonWind2050RCP4.5 | Leamington | Wind | RCP4.5 | 2050 | 85.7298 | 92.5071 | 99.6876 | 106.8104 | 113.9522
| LeamingtonWind2055RCP4.5 | Leamington | Wind | RCP4.5 | 2055 | 85.7806 | 92.5709 | 99.7679 | 106.9048 | 114.0617
| LeamingtonWind2060RCP4.5 | Leamington | Wind | RCP4.5 | 2060 | 85.8314 | 92.6347 | 99.8483 | 106.9991 | 114.1711
| LeamingtonWind2065RCP4.5 | Leamington | Wind | RCP4.5 | 2065 | 85.8821 | 92.6985 | 99.9286 | 107.0935 | 114.2806
| LeamingtonWind2070RCP4.5 | Leamington | Wind | RCP4.5 | 2070 | 85.9329 | 92.7623 | 100.009 | 107.1879 | 114.3901
| LeamingtonWind2075RCP4.5 | Leamington | Wind | RCP4.5 | 2075 | 86.136 | 93.0296 | 100.3569 | 107.6073 | 114.878
| LeamingtonWind2080RCP4.5 | Leamington | Wind | RCP4.5 | 2080 | 86.3391 | 93.297 | 100.7048 | 108.0268 | 115.3658
| LeamingtonWind2085RCP4.5 | Leamington | Wind | RCP4.5 | 2085 | 86.5422 | 93.5643 | 101.0527 | 108.4462 | 115.8536
| LeamingtonWind2090RCP4.5 | Leamington | Wind | RCP4.5 | 2090 | 86.7453 | 93.8317 | 101.4006 | 108.8657 | 116.3415
| LeamingtonWind2095RCP4.5 | Leamington | Wind | RCP4.5 | 2095 | 86.9484 | 94.099 | 101.7485 | 109.2851 | 116.8293
| LeamingtonWind2100RCP4.5 | Leamington | Wind | RCP4.5 | 2100 | 87.1515 | 94.3664 | 102.0964 | 109.7045 | 117.3172
| LeamingtonWind2023RCP6.0 | Leamington | Wind | RCP6.0 | 2023 | 85.0782 | 91.6686 | 98.6174 | 105.5521 | 112.4909
| LeamingtonWind2025RCP6.0 | Leamington | Wind | RCP6.0 | 2025 | 85.1784 | 91.7977 | 98.7824 | 105.7461 | 112.7162
| LeamingtonWind2030RCP6.0 | Leamington | Wind | RCP6.0 | 2030 | 85.2785 | 91.9268 | 98.9473 | 105.9401 | 112.9415
| LeamingtonWind2035RCP6.0 | Leamington | Wind | RCP6.0 | 2035 | 85.3786 | 92.056 | 99.1123 | 106.134 | 113.1668
| LeamingtonWind2040RCP6.0 | Leamington | Wind | RCP6.0 | 2040 | 85.4788 | 92.1851 | 99.2773 | 106.328 | 113.3921
| LeamingtonWind2045RCP6.0 | Leamington | Wind | RCP6.0 | 2045 | 85.5789 | 92.3142 | 99.4422 | 106.522 | 113.6174
| LeamingtonWind2050RCP6.0 | Leamington | Wind | RCP6.0 | 2050 | 85.7298 | 92.5071 | 99.6876 | 106.8104 | 113.9522
| LeamingtonWind2055RCP6.0 | Leamington | Wind | RCP6.0 | 2055 | 85.7806 | 92.5709 | 99.7679 | 106.9048 | 114.0617
| LeamingtonWind2060RCP6.0 | Leamington | Wind | RCP6.0 | 2060 | 85.8314 | 92.6347 | 99.8483 | 106.9991 | 114.1711
| LeamingtonWind2065RCP6.0 | Leamington | Wind | RCP6.0 | 2065 | 85.8821 | 92.6985 | 99.9286 | 107.0935 | 114.2806
| LeamingtonWind2070RCP6.0 | Leamington | Wind | RCP6.0 | 2070 | 85.9329 | 92.7623 | 100.009 | 107.1879 | 114.3901
| LeamingtonWind2075RCP6.0 | Leamington | Wind | RCP6.0 | 2075 | 86.2375 | 93.1633 | 100.5309 | 107.8171 | 115.1219
| LeamingtonWind2080RCP6.0 | Leamington | Wind | RCP6.0 | 2080 | 86.5422 | 93.5643 | 101.0527 | 108.4462 | 115.8536
| LeamingtonWind2085RCP6.0 | Leamington | Wind | RCP6.0 | 2085 | 86.8468 | 93.9653 | 101.5746 | 109.0754 | 116.5854
| LeamingtonWind2090RCP6.0 | Leamington | Wind | RCP6.0 | 2090 | 87.5379 | 94.8433 | 102.6844 | 110.3861 | 118.0992
| LeamingtonWind2095RCP6.0 | Leamington | Wind | RCP6.0 | 2095 | 87.9243 | 95.3203 | 103.2724 | 111.0677 | 118.8813
| LeamingtonWind2100RCP6.0 | Leamington | Wind | RCP6.0 | 2100 | 88.3108 | 95.7973 | 103.8604 | 111.7493 | 119.6633
| LeamingtonWind2023RCP8.5 | Leamington | Wind | RCP8.5 | 2023 | 85.0782 | 91.6686 | 98.6174 | 105.5521 | 112.4909
| LeamingtonWind2025RCP8.5 | Leamington | Wind | RCP8.5 | 2025 | 85.2785 | 91.9268 | 98.9473 | 105.9401 | 112.9415
| LeamingtonWind2030RCP8.5 | Leamington | Wind | RCP8.5 | 2030 | 85.4788 | 92.1851 | 99.2773 | 106.328 | 113.3921
| LeamingtonWind2035RCP8.5 | Leamington | Wind | RCP8.5 | 2035 | 85.679 | 92.4433 | 99.6072 | 106.716 | 113.8427
| LeamingtonWind2040RCP8.5 | Leamington | Wind | RCP8.5 | 2040 | 85.7637 | 92.5496 | 99.7411 | 106.8733 | 114.0252
| LeamingtonWind2045RCP8.5 | Leamington | Wind | RCP8.5 | 2045 | 85.8483 | 92.656 | 99.8751 | 107.0306 | 114.2076
| LeamingtonWind2050RCP8.5 | Leamington | Wind | RCP8.5 | 2050 | 86.3391 | 93.297 | 100.7048 | 108.0268 | 115.3658
| LeamingtonWind2055RCP8.5 | Leamington | Wind | RCP8.5 | 2055 | 86.7453 | 93.8317 | 101.4006 | 108.8657 | 116.3415
| LeamingtonWind2060RCP8.5 | Leamington | Wind | RCP8.5 | 2060 | 87.5379 | 94.8433 | 102.6844 | 110.3861 | 118.0992
| LeamingtonWind2065RCP8.5 | Leamington | Wind | RCP8.5 | 2065 | 87.9243 | 95.3203 | 103.2724 | 111.0677 | 118.8813
| LeamingtonWind2070RCP8.5 | Leamington | Wind | RCP8.5 | 2070 | 88.4292 | 95.937 | 104.0205 | 111.9311 | 119.8644
| LeamingtonWind2075RCP8.5 | Leamington | Wind | RCP8.5 | 2075 | 88.5477 | 96.0768 | 104.1805 | 112.1128 | 120.0655
| LeamingtonWind2080RCP8.5 | Leamington | Wind | RCP8.5 | 2080 | 88.6662 | 96.2165 | 104.3406 | 112.2946 | 120.2666
| LeamingtonWind2085RCP8.5 | Leamington | Wind | RCP8.5 | 2085 | 89.1527 | 96.8044 | 105.0658 | 113.1335 | 121.2218
| LeamingtonWind2090RCP8.5 | Leamington | Wind | RCP8.5 | 2090 | 89.6393 | 97.3922 | 105.791 | 113.9723 | 122.177
| LeamingtonWind2095RCP8.5 | Leamington | Wind | RCP8.5 | 2095 | 89.6393 | 97.3922 | 105.791 | 113.9723 | 122.177
| LeamingtonWind2100RCP8.5 | Leamington | Wind | RCP8.5 | 2100 | 89.6393 | 97.3922 | 105.791 | 113.9723 | 122.177
| LindsayIce Accretion2023RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
| LindsayIce Accretion2025RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
| LindsayIce Accretion2030RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
| LindsayIce Accretion2035RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
| LindsayIce Accretion2040RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
| LindsayIce Accretion2045RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
| LindsayIce Accretion2050RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
| LindsayIce Accretion2055RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
| LindsayIce Accretion2060RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
| LindsayIce Accretion2065RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
| LindsayIce Accretion2070RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
| LindsayIce Accretion2075RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2075 | 17.2744 | 20.8814 | 25.4167 | 28.8762 | 32.34
| LindsayIce Accretion2080RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2080 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
| LindsayIce Accretion2085RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2085 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
| LindsayIce Accretion2090RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2090 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
| LindsayIce Accretion2095RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2095 | 17.2048 | 20.9091 | 25.5833 | 29.121 | 32.676
| LindsayIce Accretion2100RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2100 | 17.1874 | 20.916 | 25.625 | 29.1822 | 32.76
| LindsayIce Accretion2023RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
| LindsayIce Accretion2025RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
| LindsayIce Accretion2030RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
| LindsayIce Accretion2035RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
| LindsayIce Accretion2040RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
| LindsayIce Accretion2045RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
| LindsayIce Accretion2050RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
| LindsayIce Accretion2055RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
| LindsayIce Accretion2060RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
| LindsayIce Accretion2065RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
| LindsayIce Accretion2070RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
| LindsayIce Accretion2075RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2075 | 17.2657 | 20.8849 | 25.4375 | 28.9068 | 32.382
| LindsayIce Accretion2080RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2080 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
| LindsayIce Accretion2085RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2085 | 17.2135 | 20.9056 | 25.5625 | 29.0904 | 32.634
| LindsayIce Accretion2090RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2090 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
| LindsayIce Accretion2095RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2095 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
| LindsayIce Accretion2100RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2100 | 16.2654 | 19.8992 | 24.5 | 27.9957 | 31.4685
| LindsayIce Accretion2023RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
| LindsayIce Accretion2025RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2025 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
| LindsayIce Accretion2030RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2030 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
| LindsayIce Accretion2035RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2035 | 17.6919 | 21.2272 | 25.725 | 29.154 | 32.6025
| LindsayIce Accretion2040RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2040 | 17.5585 | 21.1097 | 25.6083 | 29.041 | 32.487
| LindsayIce Accretion2045RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2045 | 17.4251 | 20.9921 | 25.4917 | 28.928 | 32.3715
| LindsayIce Accretion2050RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2050 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
| LindsayIce Accretion2055RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2055 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
| LindsayIce Accretion2060RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2060 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
| LindsayIce Accretion2065RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2065 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
| LindsayIce Accretion2070RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2070 | 15.9987 | 19.6226 | 24.2083 | 27.685 | 31.143
| LindsayIce Accretion2075RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2075 | 15.7319 | 19.3459 | 23.9167 | 27.3742 | 30.8175
| LindsayIce Accretion2080RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2080 | 15.4652 | 19.0693 | 23.625 | 27.0635 | 30.492
| LindsayIce Accretion2085RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2085 | 14.8911 | 18.426 | 22.8875 | 26.2584 | 29.6258
| LindsayIce Accretion2090RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2090 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
| LindsayIce Accretion2095RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2095 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
| LindsayIce Accretion2100RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2100 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
| LindsayWind2023RCP4.5 | Lindsay | Wind | RCP4.5 | 2023 | 74.7496 | 80.5159 | 86.5762 | 92.6365 | 98.7067
| LindsayWind2025RCP4.5 | Lindsay | Wind | RCP4.5 | 2025 | 74.783 | 80.5599 | 86.635 | 92.7086 | 98.79
| LindsayWind2030RCP4.5 | Lindsay | Wind | RCP4.5 | 2030 | 74.8164 | 80.6038 | 86.6937 | 92.7807 | 98.8733
| LindsayWind2035RCP4.5 | Lindsay | Wind | RCP4.5 | 2035 | 74.8499 | 80.6478 | 86.7525 | 92.8528 | 98.9567
| LindsayWind2040RCP4.5 | Lindsay | Wind | RCP4.5 | 2040 | 74.8833 | 80.6918 | 86.8113 | 92.9249 | 99.04
| LindsayWind2045RCP4.5 | Lindsay | Wind | RCP4.5 | 2045 | 74.9167 | 80.7358 | 86.87 | 92.9969 | 99.1233
| LindsayWind2050RCP4.5 | Lindsay | Wind | RCP4.5 | 2050 | 75.0169 | 80.8582 | 87.02 | 93.1703 | 99.3204
| LindsayWind2055RCP4.5 | Lindsay | Wind | RCP4.5 | 2055 | 75.0838 | 80.9366 | 87.1111 | 93.2715 | 99.4341
| LindsayWind2060RCP4.5 | Lindsay | Wind | RCP4.5 | 2060 | 75.1506 | 81.0149 | 87.2023 | 93.3727 | 99.5479
| LindsayWind2065RCP4.5 | Lindsay | Wind | RCP4.5 | 2065 | 75.2174 | 81.0933 | 87.2934 | 93.4739 | 99.6616
| LindsayWind2070RCP4.5 | Lindsay | Wind | RCP4.5 | 2070 | 75.2843 | 81.1717 | 87.3846 | 93.5751 | 99.7753
| LindsayWind2075RCP4.5 | Lindsay | Wind | RCP4.5 | 2075 | 75.3573 | 81.2623 | 87.4964 | 93.707 | 99.9256
| LindsayWind2080RCP4.5 | Lindsay | Wind | RCP4.5 | 2080 | 75.4303 | 81.353 | 87.6082 | 93.8389 | 100.076
| LindsayWind2085RCP4.5 | Lindsay | Wind | RCP4.5 | 2085 | 75.5033 | 81.4436 | 87.72 | 93.9708 | 100.2263
| LindsayWind2090RCP4.5 | Lindsay | Wind | RCP4.5 | 2090 | 75.5764 | 81.5343 | 87.8318 | 94.1027 | 100.3766
| LindsayWind2095RCP4.5 | Lindsay | Wind | RCP4.5 | 2095 | 75.6494 | 81.6249 | 87.9436 | 94.2346 | 100.5269
| LindsayWind2100RCP4.5 | Lindsay | Wind | RCP4.5 | 2100 | 75.7224 | 81.7156 | 88.0554 | 94.3665 | 100.6773
| LindsayWind2023RCP6.0 | Lindsay | Wind | RCP6.0 | 2023 | 74.7496 | 80.5159 | 86.5762 | 92.6365 | 98.7067
| LindsayWind2025RCP6.0 | Lindsay | Wind | RCP6.0 | 2025 | 74.783 | 80.5599 | 86.635 | 92.7086 | 98.79
| LindsayWind2030RCP6.0 | Lindsay | Wind | RCP6.0 | 2030 | 74.8164 | 80.6038 | 86.6937 | 92.7807 | 98.8733
| LindsayWind2035RCP6.0 | Lindsay | Wind | RCP6.0 | 2035 | 74.8499 | 80.6478 | 86.7525 | 92.8528 | 98.9567
| LindsayWind2040RCP6.0 | Lindsay | Wind | RCP6.0 | 2040 | 74.8833 | 80.6918 | 86.8113 | 92.9249 | 99.04
| LindsayWind2045RCP6.0 | Lindsay | Wind | RCP6.0 | 2045 | 74.9167 | 80.7358 | 86.87 | 92.9969 | 99.1233
| LindsayWind2050RCP6.0 | Lindsay | Wind | RCP6.0 | 2050 | 75.0169 | 80.8582 | 87.02 | 93.1703 | 99.3204
| LindsayWind2055RCP6.0 | Lindsay | Wind | RCP6.0 | 2055 | 75.0838 | 80.9366 | 87.1111 | 93.2715 | 99.4341
| LindsayWind2060RCP6.0 | Lindsay | Wind | RCP6.0 | 2060 | 75.1506 | 81.0149 | 87.2023 | 93.3727 | 99.5479
| LindsayWind2065RCP6.0 | Lindsay | Wind | RCP6.0 | 2065 | 75.2174 | 81.0933 | 87.2934 | 93.4739 | 99.6616
| LindsayWind2070RCP6.0 | Lindsay | Wind | RCP6.0 | 2070 | 75.2843 | 81.1717 | 87.3846 | 93.5751 | 99.7753
| LindsayWind2075RCP6.0 | Lindsay | Wind | RCP6.0 | 2075 | 75.3938 | 81.3077 | 87.5523 | 93.773 | 100.0008
| LindsayWind2080RCP6.0 | Lindsay | Wind | RCP6.0 | 2080 | 75.5033 | 81.4436 | 87.72 | 93.9708 | 100.2263
| LindsayWind2085RCP6.0 | Lindsay | Wind | RCP6.0 | 2085 | 75.6129 | 81.5796 | 87.8877 | 94.1687 | 100.4518
| LindsayWind2090RCP6.0 | Lindsay | Wind | RCP6.0 | 2090 | 75.9625 | 81.9902 | 88.3765 | 94.7223 | 101.0727
| LindsayWind2095RCP6.0 | Lindsay | Wind | RCP6.0 | 2095 | 76.2026 | 82.2648 | 88.6975 | 95.0781 | 101.4681
| LindsayWind2100RCP6.0 | Lindsay | Wind | RCP6.0 | 2100 | 76.4427 | 82.5394 | 89.0186 | 95.4339 | 101.8636
| LindsayWind2023RCP8.5 | Lindsay | Wind | RCP8.5 | 2023 | 74.7496 | 80.5159 | 86.5762 | 92.6365 | 98.7067
| LindsayWind2025RCP8.5 | Lindsay | Wind | RCP8.5 | 2025 | 74.8164 | 80.6038 | 86.6937 | 92.7807 | 98.8733
| LindsayWind2030RCP8.5 | Lindsay | Wind | RCP8.5 | 2030 | 74.8833 | 80.6918 | 86.8113 | 92.9249 | 99.04
| LindsayWind2035RCP8.5 | Lindsay | Wind | RCP8.5 | 2035 | 74.9501 | 80.7798 | 86.9288 | 93.069 | 99.2067
| LindsayWind2040RCP8.5 | Lindsay | Wind | RCP8.5 | 2040 | 75.0615 | 80.9104 | 87.0807 | 93.2377 | 99.3962
| LindsayWind2045RCP8.5 | Lindsay | Wind | RCP8.5 | 2045 | 75.1729 | 81.0411 | 87.2327 | 93.4064 | 99.5858
| LindsayWind2050RCP8.5 | Lindsay | Wind | RCP8.5 | 2050 | 75.4303 | 81.353 | 87.6082 | 93.8389 | 100.076
| LindsayWind2055RCP8.5 | Lindsay | Wind | RCP8.5 | 2055 | 75.5764 | 81.5343 | 87.8318 | 94.1027 | 100.3766
| LindsayWind2060RCP8.5 | Lindsay | Wind | RCP8.5 | 2060 | 75.9625 | 81.9902 | 88.3765 | 94.7223 | 101.0727
| LindsayWind2065RCP8.5 | Lindsay | Wind | RCP8.5 | 2065 | 76.2026 | 82.2648 | 88.6975 | 95.0781 | 101.4681
| LindsayWind2070RCP8.5 | Lindsay | Wind | RCP8.5 | 2070 | 76.5269 | 82.6487 | 89.1533 | 95.5934 | 102.0498
| LindsayWind2075RCP8.5 | Lindsay | Wind | RCP8.5 | 2075 | 76.611 | 82.758 | 89.2881 | 95.7529 | 102.2361
| LindsayWind2080RCP8.5 | Lindsay | Wind | RCP8.5 | 2080 | 76.6952 | 82.8673 | 89.4228 | 95.9124 | 102.4224
| LindsayWind2085RCP8.5 | Lindsay | Wind | RCP8.5 | 2085 | 76.892 | 83.1432 | 89.8098 | 96.3863 | 102.9861
| LindsayWind2090RCP8.5 | Lindsay | Wind | RCP8.5 | 2090 | 77.0888 | 83.4191 | 90.1968 | 96.8603 | 103.5498
| LindsayWind2095RCP8.5 | Lindsay | Wind | RCP8.5 | 2095 | 77.0888 | 83.4191 | 90.1968 | 96.8603 | 103.5498
| LindsayWind2100RCP8.5 | Lindsay | Wind | RCP8.5 | 2100 | 77.0888 | 83.4191 | 90.1968 | 96.8603 | 103.5498
| Lion's HeadIce Accretion2023RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2023 | 14.0283 | 16.8324 | 20.36 | 23.0746 | 25.7544
| Lion's HeadIce Accretion2025RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2025 | 14.0561 | 16.8767 | 20.4267 | 23.1537 | 25.851
| Lion's HeadIce Accretion2030RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2030 | 14.0839 | 16.9209 | 20.4933 | 23.2328 | 25.9476
| Lion's HeadIce Accretion2035RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2035 | 14.1118 | 16.9652 | 20.56 | 23.3119 | 26.0442
| Lion's HeadIce Accretion2040RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2040 | 14.1396 | 17.0095 | 20.6267 | 23.391 | 26.1408
| Lion's HeadIce Accretion2045RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2045 | 14.1674 | 17.0537 | 20.6933 | 23.4701 | 26.2374
| Lion's HeadIce Accretion2050RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2050 | 14.1006 | 17.005 | 20.672 | 23.4633 | 26.2534
| Lion's HeadIce Accretion2055RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2055 | 14.006 | 16.9121 | 20.584 | 23.3774 | 26.1727
| Lion's HeadIce Accretion2060RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2060 | 13.9114 | 16.8191 | 20.496 | 23.2916 | 26.0921
| Lion's HeadIce Accretion2065RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2065 | 13.8167 | 16.7262 | 20.408 | 23.2057 | 26.0114
| Lion's HeadIce Accretion2070RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2070 | 13.7221 | 16.6332 | 20.32 | 23.1198 | 25.9308
| Lion's HeadIce Accretion2075RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2075 | 13.6131 | 16.5198 | 20.2 | 22.9955 | 25.8006
| Lion's HeadIce Accretion2080RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2080 | 13.5041 | 16.4063 | 20.08 | 22.8712 | 25.6704
| Lion's HeadIce Accretion2085RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2085 | 13.395 | 16.2929 | 19.96 | 22.7469 | 25.5402
| Lion's HeadIce Accretion2090RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2090 | 13.286 | 16.1795 | 19.84 | 22.6226 | 25.41
| Lion's HeadIce Accretion2095RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2095 | 13.177 | 16.066 | 19.72 | 22.4983 | 25.2798
| Lion's HeadIce Accretion2100RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2100 | 13.068 | 15.9526 | 19.6 | 22.374 | 25.1496
| Lion's HeadIce Accretion2023RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2023 | 14.0283 | 16.8324 | 20.36 | 23.0746 | 25.7544
| Lion's HeadIce Accretion2025RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2025 | 14.0561 | 16.8767 | 20.4267 | 23.1537 | 25.851
| Lion's HeadIce Accretion2030RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2030 | 14.0839 | 16.9209 | 20.4933 | 23.2328 | 25.9476
| Lion's HeadIce Accretion2035RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2035 | 14.1118 | 16.9652 | 20.56 | 23.3119 | 26.0442
| Lion's HeadIce Accretion2040RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2040 | 14.1396 | 17.0095 | 20.6267 | 23.391 | 26.1408
| Lion's HeadIce Accretion2045RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2045 | 14.1674 | 17.0537 | 20.6933 | 23.4701 | 26.2374
| Lion's HeadIce Accretion2050RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2050 | 14.1006 | 17.005 | 20.672 | 23.4633 | 26.2534
| Lion's HeadIce Accretion2055RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2055 | 14.006 | 16.9121 | 20.584 | 23.3774 | 26.1727
| Lion's HeadIce Accretion2060RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2060 | 13.9114 | 16.8191 | 20.496 | 23.2916 | 26.0921
| Lion's HeadIce Accretion2065RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2065 | 13.8167 | 16.7262 | 20.408 | 23.2057 | 26.0114
| Lion's HeadIce Accretion2070RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2070 | 13.7221 | 16.6332 | 20.32 | 23.1198 | 25.9308
| Lion's HeadIce Accretion2075RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2075 | 13.5586 | 16.463 | 20.14 | 22.9333 | 25.7355
| Lion's HeadIce Accretion2080RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2080 | 13.395 | 16.2929 | 19.96 | 22.7469 | 25.5402
| Lion's HeadIce Accretion2085RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2085 | 13.2315 | 16.1227 | 19.78 | 22.5604 | 25.3449
| Lion's HeadIce Accretion2090RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2090 | 12.6412 | 15.4657 | 19.0267 | 21.7412 | 24.444
| Lion's HeadIce Accretion2095RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2095 | 12.2144 | 14.9787 | 18.4533 | 21.1084 | 23.7384
| Lion's HeadIce Accretion2100RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2100 | 11.7876 | 14.4918 | 17.88 | 20.4756 | 23.0328
| Lion's HeadIce Accretion2023RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2023 | 14.0283 | 16.8324 | 20.36 | 23.0746 | 25.7544
| Lion's HeadIce Accretion2025RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2025 | 14.0839 | 16.9209 | 20.4933 | 23.2328 | 25.9476
| Lion's HeadIce Accretion2030RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2030 | 14.1396 | 17.0095 | 20.6267 | 23.391 | 26.1408
| Lion's HeadIce Accretion2035RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2035 | 14.1953 | 17.098 | 20.76 | 23.5492 | 26.334
| Lion's HeadIce Accretion2040RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2040 | 14.0375 | 16.9431 | 20.6133 | 23.4061 | 26.1996
| Lion's HeadIce Accretion2045RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2045 | 13.8798 | 16.7881 | 20.4667 | 23.2629 | 26.0652
| Lion's HeadIce Accretion2050RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2050 | 13.5041 | 16.4063 | 20.08 | 22.8712 | 25.6704
| Lion's HeadIce Accretion2055RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2055 | 13.286 | 16.1795 | 19.84 | 22.6226 | 25.41
| Lion's HeadIce Accretion2060RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2060 | 12.6412 | 15.4657 | 19.0267 | 21.7412 | 24.444
| Lion's HeadIce Accretion2065RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2065 | 12.2144 | 14.9787 | 18.4533 | 21.1084 | 23.7384
| Lion's HeadIce Accretion2070RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2070 | 11.333 | 13.9717 | 17.28 | 19.8051 | 22.302
| Lion's HeadIce Accretion2075RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2075 | 10.8784 | 13.4515 | 16.68 | 19.1347 | 21.5712
| Lion's HeadIce Accretion2080RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2080 | 10.4238 | 12.9314 | 16.08 | 18.4642 | 20.8404
| Lion's HeadIce Accretion2085RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2085 | 9.9019 | 12.3255 | 15.36 | 17.6619 | 19.9584
| Lion's HeadIce Accretion2090RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2090 | 9.38 | 11.7196 | 14.64 | 16.8596 | 19.0764
| Lion's HeadIce Accretion2095RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2095 | 9.38 | 11.7196 | 14.64 | 16.8596 | 19.0764
| Lion's HeadIce Accretion2100RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2100 | 9.38 | 11.7196 | 14.64 | 16.8596 | 19.0764
| Lion's HeadWind2023RCP4.5 | Lion's Head | Wind | RCP4.5 | 2023 | 83.7067 | 90.2978 | 97.2768 | 104.2197 | 111.1692
| Lion's HeadWind2025RCP4.5 | Lion's Head | Wind | RCP4.5 | 2025 | 83.8227 | 90.4347 | 97.44 | 104.4063 | 111.3789
| Lion's HeadWind2030RCP4.5 | Lion's Head | Wind | RCP4.5 | 2030 | 83.9388 | 90.5716 | 97.6032 | 104.5929 | 111.5887
| Lion's HeadWind2035RCP4.5 | Lion's Head | Wind | RCP4.5 | 2035 | 84.0548 | 90.7085 | 97.7664 | 104.7795 | 111.7984
| Lion's HeadWind2040RCP4.5 | Lion's Head | Wind | RCP4.5 | 2040 | 84.1709 | 90.8454 | 97.9296 | 104.9661 | 112.0082
| Lion's HeadWind2045RCP4.5 | Lion's Head | Wind | RCP4.5 | 2045 | 84.2869 | 90.9823 | 98.0928 | 105.1528 | 112.218
| Lion's HeadWind2050RCP4.5 | Lion's Head | Wind | RCP4.5 | 2050 | 84.4229 | 91.1352 | 98.2637 | 105.3394 | 112.4233
| Lion's HeadWind2055RCP4.5 | Lion's Head | Wind | RCP4.5 | 2055 | 84.4428 | 91.1513 | 98.2714 | 105.3394 | 112.419
| Lion's HeadWind2060RCP4.5 | Lion's Head | Wind | RCP4.5 | 2060 | 84.4627 | 91.1674 | 98.279 | 105.3394 | 112.4146
| Lion's HeadWind2065RCP4.5 | Lion's Head | Wind | RCP4.5 | 2065 | 84.4826 | 91.1834 | 98.2867 | 105.3394 | 112.4102
| Lion's HeadWind2070RCP4.5 | Lion's Head | Wind | RCP4.5 | 2070 | 84.5025 | 91.1995 | 98.2944 | 105.3394 | 112.4058
| Lion's HeadWind2075RCP4.5 | Lion's Head | Wind | RCP4.5 | 2075 | 84.6116 | 91.3424 | 98.4784 | 105.5602 | 112.6612
| Lion's HeadWind2080RCP4.5 | Lion's Head | Wind | RCP4.5 | 2080 | 84.7208 | 91.4852 | 98.6624 | 105.7811 | 112.9165
| Lion's HeadWind2085RCP4.5 | Lion's Head | Wind | RCP4.5 | 2085 | 84.8299 | 91.6281 | 98.8464 | 106.0019 | 113.1719
| Lion's HeadWind2090RCP4.5 | Lion's Head | Wind | RCP4.5 | 2090 | 84.939 | 91.7709 | 99.0304 | 106.2228 | 113.4273
| Lion's HeadWind2095RCP4.5 | Lion's Head | Wind | RCP4.5 | 2095 | 85.0482 | 91.9138 | 99.2144 | 106.4436 | 113.6826
| Lion's HeadWind2100RCP4.5 | Lion's Head | Wind | RCP4.5 | 2100 | 85.1573 | 92.0566 | 99.3984 | 106.6644 | 113.938
| Lion's HeadWind2023RCP6.0 | Lion's Head | Wind | RCP6.0 | 2023 | 83.7067 | 90.2978 | 97.2768 | 104.2197 | 111.1692
| Lion's HeadWind2025RCP6.0 | Lion's Head | Wind | RCP6.0 | 2025 | 83.8227 | 90.4347 | 97.44 | 104.4063 | 111.3789
| Lion's HeadWind2030RCP6.0 | Lion's Head | Wind | RCP6.0 | 2030 | 83.9388 | 90.5716 | 97.6032 | 104.5929 | 111.5887
| Lion's HeadWind2035RCP6.0 | Lion's Head | Wind | RCP6.0 | 2035 | 84.0548 | 90.7085 | 97.7664 | 104.7795 | 111.7984
| Lion's HeadWind2040RCP6.0 | Lion's Head | Wind | RCP6.0 | 2040 | 84.1709 | 90.8454 | 97.9296 | 104.9661 | 112.0082
| Lion's HeadWind2045RCP6.0 | Lion's Head | Wind | RCP6.0 | 2045 | 84.2869 | 90.9823 | 98.0928 | 105.1528 | 112.218
| Lion's HeadWind2050RCP6.0 | Lion's Head | Wind | RCP6.0 | 2050 | 84.4229 | 91.1352 | 98.2637 | 105.3394 | 112.4233
| Lion's HeadWind2055RCP6.0 | Lion's Head | Wind | RCP6.0 | 2055 | 84.4428 | 91.1513 | 98.2714 | 105.3394 | 112.419
| Lion's HeadWind2060RCP6.0 | Lion's Head | Wind | RCP6.0 | 2060 | 84.4627 | 91.1674 | 98.279 | 105.3394 | 112.4146
| Lion's HeadWind2065RCP6.0 | Lion's Head | Wind | RCP6.0 | 2065 | 84.4826 | 91.1834 | 98.2867 | 105.3394 | 112.4102
| Lion's HeadWind2070RCP6.0 | Lion's Head | Wind | RCP6.0 | 2070 | 84.5025 | 91.1995 | 98.2944 | 105.3394 | 112.4058
| Lion's HeadWind2075RCP6.0 | Lion's Head | Wind | RCP6.0 | 2075 | 84.6662 | 91.4138 | 98.5704 | 105.6706 | 112.7889
| Lion's HeadWind2080RCP6.0 | Lion's Head | Wind | RCP6.0 | 2080 | 84.8299 | 91.6281 | 98.8464 | 106.0019 | 113.1719
| Lion's HeadWind2085RCP6.0 | Lion's Head | Wind | RCP6.0 | 2085 | 84.9936 | 91.8423 | 99.1224 | 106.3332 | 113.5549
| Lion's HeadWind2090RCP6.0 | Lion's Head | Wind | RCP6.0 | 2090 | 85.4668 | 92.4346 | 99.8656 | 107.2089 | 114.5581
| Lion's HeadWind2095RCP6.0 | Lion's Head | Wind | RCP6.0 | 2095 | 85.7763 | 92.8125 | 100.3328 | 107.7533 | 115.1783
| Lion's HeadWind2100RCP6.0 | Lion's Head | Wind | RCP6.0 | 2100 | 86.0857 | 93.1905 | 100.8 | 108.2977 | 115.7985
| Lion's HeadWind2023RCP8.5 | Lion's Head | Wind | RCP8.5 | 2023 | 83.7067 | 90.2978 | 97.2768 | 104.2197 | 111.1692
| Lion's HeadWind2025RCP8.5 | Lion's Head | Wind | RCP8.5 | 2025 | 83.9388 | 90.5716 | 97.6032 | 104.5929 | 111.5887
| Lion's HeadWind2030RCP8.5 | Lion's Head | Wind | RCP8.5 | 2030 | 84.1709 | 90.8454 | 97.9296 | 104.9661 | 112.0082
| Lion's HeadWind2035RCP8.5 | Lion's Head | Wind | RCP8.5 | 2035 | 84.403 | 91.1192 | 98.256 | 105.3394 | 112.4277
| Lion's HeadWind2040RCP8.5 | Lion's Head | Wind | RCP8.5 | 2040 | 84.4361 | 91.146 | 98.2688 | 105.3394 | 112.4204
| Lion's HeadWind2045RCP8.5 | Lion's Head | Wind | RCP8.5 | 2045 | 84.4693 | 91.1727 | 98.2816 | 105.3394 | 112.4131
| Lion's HeadWind2050RCP8.5 | Lion's Head | Wind | RCP8.5 | 2050 | 84.7208 | 91.4852 | 98.6624 | 105.7811 | 112.9165
| Lion's HeadWind2055RCP8.5 | Lion's Head | Wind | RCP8.5 | 2055 | 84.939 | 91.7709 | 99.0304 | 106.2228 | 113.4273
| Lion's HeadWind2060RCP8.5 | Lion's Head | Wind | RCP8.5 | 2060 | 85.4668 | 92.4346 | 99.8656 | 107.2089 | 114.5581
| Lion's HeadWind2065RCP8.5 | Lion's Head | Wind | RCP8.5 | 2065 | 85.7763 | 92.8125 | 100.3328 | 107.7533 | 115.1783
| Lion's HeadWind2070RCP8.5 | Lion's Head | Wind | RCP8.5 | 2070 | 86.2377 | 93.369 | 101.008 | 108.5271 | 116.0575
| Lion's HeadWind2075RCP8.5 | Lion's Head | Wind | RCP8.5 | 2075 | 86.3897 | 93.5476 | 101.216 | 108.7565 | 116.3165
| Lion's HeadWind2080RCP8.5 | Lion's Head | Wind | RCP8.5 | 2080 | 86.5417 | 93.7261 | 101.424 | 108.9859 | 116.5755
| Lion's HeadWind2085RCP8.5 | Lion's Head | Wind | RCP8.5 | 2085 | 86.7406 | 93.9627 | 101.7072 | 109.3146 | 116.9421
| Lion's HeadWind2090RCP8.5 | Lion's Head | Wind | RCP8.5 | 2090 | 86.9396 | 94.1993 | 101.9904 | 109.6433 | 117.3087
| Lion's HeadWind2095RCP8.5 | Lion's Head | Wind | RCP8.5 | 2095 | 86.9396 | 94.1993 | 101.9904 | 109.6433 | 117.3087
| Lion's HeadWind2100RCP8.5 | Lion's Head | Wind | RCP8.5 | 2100 | 86.9396 | 94.1993 | 101.9904 | 109.6433 | 117.3087
| ListowelIce Accretion2023RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2023 | 15.9725 | 19.1854 | 23.253 | 26.3539 | 29.4437
| ListowelIce Accretion2025RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2025 | 16.0498 | 19.2841 | 23.3795 | 26.5055 | 29.6176
| ListowelIce Accretion2030RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2030 | 16.1272 | 19.3827 | 23.506 | 26.6571 | 29.7914
| ListowelIce Accretion2035RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2035 | 16.2045 | 19.4813 | 23.6325 | 26.8087 | 29.9653
| ListowelIce Accretion2040RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2040 | 16.2819 | 19.58 | 23.759 | 26.9603 | 30.1392
| ListowelIce Accretion2045RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2045 | 16.3592 | 19.6786 | 23.8855 | 27.1119 | 30.3131
| ListowelIce Accretion2050RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2050 | 16.443 | 19.8078 | 24.0764 | 27.3415 | 30.5913
| ListowelIce Accretion2055RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2055 | 16.4494 | 19.8383 | 24.1408 | 27.4194 | 30.6956
| ListowelIce Accretion2060RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2060 | 16.4558 | 19.8689 | 24.2052 | 27.4974 | 30.7999
| ListowelIce Accretion2065RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2065 | 16.4622 | 19.8994 | 24.2696 | 27.5754 | 30.9043
| ListowelIce Accretion2070RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2070 | 16.4686 | 19.93 | 24.334 | 27.6534 | 31.0086
| ListowelIce Accretion2075RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2075 | 16.4179 | 19.8981 | 24.3187 | 27.6577 | 31.0231
| ListowelIce Accretion2080RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2080 | 16.3672 | 19.8663 | 24.3033 | 27.662 | 31.0376
| ListowelIce Accretion2085RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2085 | 16.3165 | 19.8345 | 24.288 | 27.6664 | 31.0521
| ListowelIce Accretion2090RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2090 | 16.2659 | 19.8027 | 24.2727 | 27.6707 | 31.0666
| ListowelIce Accretion2095RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2095 | 16.2152 | 19.7709 | 24.2573 | 27.675 | 31.0811
| ListowelIce Accretion2100RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2100 | 16.1645 | 19.7391 | 24.242 | 27.6793 | 31.0955
| ListowelIce Accretion2023RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2023 | 15.9725 | 19.1854 | 23.253 | 26.3539 | 29.4437
| ListowelIce Accretion2025RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2025 | 16.0498 | 19.2841 | 23.3795 | 26.5055 | 29.6176
| ListowelIce Accretion2030RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2030 | 16.1272 | 19.3827 | 23.506 | 26.6571 | 29.7914
| ListowelIce Accretion2035RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2035 | 16.2045 | 19.4813 | 23.6325 | 26.8087 | 29.9653
| ListowelIce Accretion2040RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2040 | 16.2819 | 19.58 | 23.759 | 26.9603 | 30.1392
| ListowelIce Accretion2045RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2045 | 16.3592 | 19.6786 | 23.8855 | 27.1119 | 30.3131
| ListowelIce Accretion2050RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2050 | 16.443 | 19.8078 | 24.0764 | 27.3415 | 30.5913
| ListowelIce Accretion2055RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2055 | 16.4494 | 19.8383 | 24.1408 | 27.4194 | 30.6956
| ListowelIce Accretion2060RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2060 | 16.4558 | 19.8689 | 24.2052 | 27.4974 | 30.7999
| ListowelIce Accretion2065RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2065 | 16.4622 | 19.8994 | 24.2696 | 27.5754 | 30.9043
| ListowelIce Accretion2070RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2070 | 16.4686 | 19.93 | 24.334 | 27.6534 | 31.0086
| ListowelIce Accretion2075RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2075 | 16.3926 | 19.8822 | 24.311 | 27.6599 | 31.0303
| ListowelIce Accretion2080RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2080 | 16.3165 | 19.8345 | 24.288 | 27.6664 | 31.0521
| ListowelIce Accretion2085RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2085 | 16.2405 | 19.7868 | 24.265 | 27.6729 | 31.0738
| ListowelIce Accretion2090RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2090 | 15.8978 | 19.4654 | 23.9583 | 27.3761 | 30.7864
| ListowelIce Accretion2095RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2095 | 15.631 | 19.1918 | 23.6747 | 27.0729 | 30.4773
| ListowelIce Accretion2100RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2100 | 15.3643 | 18.9182 | 23.391 | 26.7697 | 30.1682
| ListowelIce Accretion2023RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2023 | 15.9725 | 19.1854 | 23.253 | 26.3539 | 29.4437
| ListowelIce Accretion2025RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2025 | 16.1272 | 19.3827 | 23.506 | 26.6571 | 29.7914
| ListowelIce Accretion2030RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2030 | 16.2819 | 19.58 | 23.759 | 26.9603 | 30.1392
| ListowelIce Accretion2035RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2035 | 16.4366 | 19.7772 | 24.012 | 27.2635 | 30.487
| ListowelIce Accretion2040RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2040 | 16.4473 | 19.8281 | 24.1193 | 27.3935 | 30.6608
| ListowelIce Accretion2045RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2045 | 16.4579 | 19.8791 | 24.2267 | 27.5234 | 30.8347
| ListowelIce Accretion2050RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2050 | 16.3672 | 19.8663 | 24.3033 | 27.662 | 31.0376
| ListowelIce Accretion2055RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2055 | 16.2659 | 19.8027 | 24.2727 | 27.6707 | 31.0666
| ListowelIce Accretion2060RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2060 | 15.8978 | 19.4654 | 23.9583 | 27.3761 | 30.7864
| ListowelIce Accretion2065RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2065 | 15.631 | 19.1918 | 23.6747 | 27.0729 | 30.4773
| ListowelIce Accretion2070RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2070 | 14.8735 | 18.3646 | 22.7623 | 26.0853 | 29.4147
| ListowelIce Accretion2075RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2075 | 14.3827 | 17.811 | 22.1337 | 25.4009 | 28.6612
| ListowelIce Accretion2080RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2080 | 13.8919 | 17.2574 | 21.505 | 24.7165 | 27.9077
| ListowelIce Accretion2085RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2085 | 13.1717 | 16.4079 | 20.493 | 23.5729 | 26.6471
| ListowelIce Accretion2090RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2090 | 12.4515 | 15.5583 | 19.481 | 22.4294 | 25.3865
| ListowelIce Accretion2095RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2095 | 12.4515 | 15.5583 | 19.481 | 22.4294 | 25.3865
| ListowelIce Accretion2100RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2100 | 12.4515 | 15.5583 | 19.481 | 22.4294 | 25.3865
| ListowelWind2023RCP4.5 | Listowel | Wind | RCP4.5 | 2023 | 84.3441 | 90.9317 | 97.8827 | 104.8175 | 111.7521
| ListowelWind2025RCP4.5 | Listowel | Wind | RCP4.5 | 2025 | 84.3888 | 90.9843 | 97.9458 | 104.8884 | 111.8332
| ListowelWind2030RCP4.5 | Listowel | Wind | RCP4.5 | 2030 | 84.4334 | 91.0369 | 98.0088 | 104.9594 | 111.9143
| ListowelWind2035RCP4.5 | Listowel | Wind | RCP4.5 | 2035 | 84.4781 | 91.0895 | 98.0719 | 105.0303 | 111.9954
| ListowelWind2040RCP4.5 | Listowel | Wind | RCP4.5 | 2040 | 84.5228 | 91.1422 | 98.1349 | 105.1012 | 112.0765
| ListowelWind2045RCP4.5 | Listowel | Wind | RCP4.5 | 2045 | 84.5675 | 91.1948 | 98.1979 | 105.1721 | 112.1576
| ListowelWind2050RCP4.5 | Listowel | Wind | RCP4.5 | 2050 | 84.6205 | 91.2528 | 98.261 | 105.241 | 112.2299
| ListowelWind2055RCP4.5 | Listowel | Wind | RCP4.5 | 2055 | 84.6289 | 91.2582 | 98.261 | 105.2389 | 112.221
| ListowelWind2060RCP4.5 | Listowel | Wind | RCP4.5 | 2060 | 84.6373 | 91.2637 | 98.261 | 105.2368 | 112.2122
| ListowelWind2065RCP4.5 | Listowel | Wind | RCP4.5 | 2065 | 84.6456 | 91.2691 | 98.261 | 105.2348 | 112.2033
| ListowelWind2070RCP4.5 | Listowel | Wind | RCP4.5 | 2070 | 84.654 | 91.2745 | 98.261 | 105.2327 | 112.1945
| ListowelWind2075RCP4.5 | Listowel | Wind | RCP4.5 | 2075 | 84.7475 | 91.4023 | 98.434 | 105.4437 | 112.4451
| ListowelWind2080RCP4.5 | Listowel | Wind | RCP4.5 | 2080 | 84.8411 | 91.5301 | 98.607 | 105.6548 | 112.6958
| ListowelWind2085RCP4.5 | Listowel | Wind | RCP4.5 | 2085 | 84.9346 | 91.6579 | 98.7799 | 105.8658 | 112.9464
| ListowelWind2090RCP4.5 | Listowel | Wind | RCP4.5 | 2090 | 85.0281 | 91.7857 | 98.9529 | 106.0768 | 113.1971
| ListowelWind2095RCP4.5 | Listowel | Wind | RCP4.5 | 2095 | 85.1217 | 91.9135 | 99.1259 | 106.2879 | 113.4477
| ListowelWind2100RCP4.5 | Listowel | Wind | RCP4.5 | 2100 | 85.2152 | 92.0413 | 99.2989 | 106.4989 | 113.6984
| ListowelWind2023RCP6.0 | Listowel | Wind | RCP6.0 | 2023 | 84.3441 | 90.9317 | 97.8827 | 104.8175 | 111.7521
| ListowelWind2025RCP6.0 | Listowel | Wind | RCP6.0 | 2025 | 84.3888 | 90.9843 | 97.9458 | 104.8884 | 111.8332
| ListowelWind2030RCP6.0 | Listowel | Wind | RCP6.0 | 2030 | 84.4334 | 91.0369 | 98.0088 | 104.9594 | 111.9143
| ListowelWind2035RCP6.0 | Listowel | Wind | RCP6.0 | 2035 | 84.4781 | 91.0895 | 98.0719 | 105.0303 | 111.9954
| ListowelWind2040RCP6.0 | Listowel | Wind | RCP6.0 | 2040 | 84.5228 | 91.1422 | 98.1349 | 105.1012 | 112.0765
| ListowelWind2045RCP6.0 | Listowel | Wind | RCP6.0 | 2045 | 84.5675 | 91.1948 | 98.1979 | 105.1721 | 112.1576
| ListowelWind2050RCP6.0 | Listowel | Wind | RCP6.0 | 2050 | 84.6205 | 91.2528 | 98.261 | 105.241 | 112.2299
| ListowelWind2055RCP6.0 | Listowel | Wind | RCP6.0 | 2055 | 84.6289 | 91.2582 | 98.261 | 105.2389 | 112.221
| ListowelWind2060RCP6.0 | Listowel | Wind | RCP6.0 | 2060 | 84.6373 | 91.2637 | 98.261 | 105.2368 | 112.2122
| ListowelWind2065RCP6.0 | Listowel | Wind | RCP6.0 | 2065 | 84.6456 | 91.2691 | 98.261 | 105.2348 | 112.2033
| ListowelWind2070RCP6.0 | Listowel | Wind | RCP6.0 | 2070 | 84.654 | 91.2745 | 98.261 | 105.2327 | 112.1945
| ListowelWind2075RCP6.0 | Listowel | Wind | RCP6.0 | 2075 | 84.7943 | 91.4662 | 98.5205 | 105.5492 | 112.5704
| ListowelWind2080RCP6.0 | Listowel | Wind | RCP6.0 | 2080 | 84.9346 | 91.6579 | 98.7799 | 105.8658 | 112.9464
| ListowelWind2085RCP6.0 | Listowel | Wind | RCP6.0 | 2085 | 85.0749 | 91.8496 | 99.0394 | 106.1824 | 113.3224
| ListowelWind2090RCP6.0 | Listowel | Wind | RCP6.0 | 2090 | 85.5865 | 92.4983 | 99.8583 | 107.1459 | 114.4392
| ListowelWind2095RCP6.0 | Listowel | Wind | RCP6.0 | 2095 | 85.9578 | 92.9554 | 100.4176 | 107.7928 | 115.1801
| ListowelWind2100RCP6.0 | Listowel | Wind | RCP6.0 | 2100 | 86.3292 | 93.4125 | 100.977 | 108.4398 | 115.921
| ListowelWind2023RCP8.5 | Listowel | Wind | RCP8.5 | 2023 | 84.3441 | 90.9317 | 97.8827 | 104.8175 | 111.7521
| ListowelWind2025RCP8.5 | Listowel | Wind | RCP8.5 | 2025 | 84.4334 | 91.0369 | 98.0088 | 104.9594 | 111.9143
| ListowelWind2030RCP8.5 | Listowel | Wind | RCP8.5 | 2030 | 84.5228 | 91.1422 | 98.1349 | 105.1012 | 112.0765
| ListowelWind2035RCP8.5 | Listowel | Wind | RCP8.5 | 2035 | 84.6121 | 91.2474 | 98.261 | 105.2431 | 112.2387
| ListowelWind2040RCP8.5 | Listowel | Wind | RCP8.5 | 2040 | 84.6261 | 91.2564 | 98.261 | 105.2396 | 112.224
| ListowelWind2045RCP8.5 | Listowel | Wind | RCP8.5 | 2045 | 84.64 | 91.2655 | 98.261 | 105.2361 | 112.2092
| ListowelWind2050RCP8.5 | Listowel | Wind | RCP8.5 | 2050 | 84.8411 | 91.5301 | 98.607 | 105.6548 | 112.6958
| ListowelWind2055RCP8.5 | Listowel | Wind | RCP8.5 | 2055 | 85.0281 | 91.7857 | 98.9529 | 106.0768 | 113.1971
| ListowelWind2060RCP8.5 | Listowel | Wind | RCP8.5 | 2060 | 85.5865 | 92.4983 | 99.8583 | 107.1459 | 114.4392
| ListowelWind2065RCP8.5 | Listowel | Wind | RCP8.5 | 2065 | 85.9578 | 92.9554 | 100.4176 | 107.7928 | 115.1801
| ListowelWind2070RCP8.5 | Listowel | Wind | RCP8.5 | 2070 | 86.6028 | 93.7703 | 101.4458 | 109.0003 | 116.5771
| ListowelWind2075RCP8.5 | Listowel | Wind | RCP8.5 | 2075 | 86.8764 | 94.1281 | 101.9147 | 109.5607 | 117.2332
| ListowelWind2080RCP8.5 | Listowel | Wind | RCP8.5 | 2080 | 87.15 | 94.486 | 102.3835 | 110.1212 | 117.8893
| ListowelWind2085RCP8.5 | Listowel | Wind | RCP8.5 | 2085 | 87.3636 | 94.7701 | 102.757 | 110.5675 | 118.4091
| ListowelWind2090RCP8.5 | Listowel | Wind | RCP8.5 | 2090 | 87.5772 | 95.0543 | 103.1304 | 111.0138 | 118.9288
| ListowelWind2095RCP8.5 | Listowel | Wind | RCP8.5 | 2095 | 87.5772 | 95.0543 | 103.1304 | 111.0138 | 118.9288
| ListowelWind2100RCP8.5 | Listowel | Wind | RCP8.5 | 2100 | 87.5772 | 95.0543 | 103.1304 | 111.0138 | 118.9288
| LondonIce Accretion2023RCP4.5 | London | Ice Accretion | RCP4.5 | 2023 | 21.9553 | 26.3475 | 31.904 | 36.1238 | 40.3603
| LondonIce Accretion2025RCP4.5 | London | Ice Accretion | RCP4.5 | 2025 | 21.8254 | 26.2059 | 31.7493 | 35.9611 | 40.1856
| LondonIce Accretion2030RCP4.5 | London | Ice Accretion | RCP4.5 | 2030 | 21.6956 | 26.0642 | 31.5947 | 35.7984 | 40.0109
| LondonIce Accretion2035RCP4.5 | London | Ice Accretion | RCP4.5 | 2035 | 21.5657 | 25.9226 | 31.44 | 35.6357 | 39.8362
| LondonIce Accretion2040RCP4.5 | London | Ice Accretion | RCP4.5 | 2040 | 21.4358 | 25.7809 | 31.2853 | 35.473 | 39.6614
| LondonIce Accretion2045RCP4.5 | London | Ice Accretion | RCP4.5 | 2045 | 21.3059 | 25.6393 | 31.1307 | 35.3102 | 39.4867
| LondonIce Accretion2050RCP4.5 | London | Ice Accretion | RCP4.5 | 2050 | 20.7618 | 25.0408 | 30.4576 | 34.5834 | 38.6991
| LondonIce Accretion2055RCP4.5 | London | Ice Accretion | RCP4.5 | 2055 | 20.3477 | 24.5839 | 29.9392 | 34.0193 | 38.0863
| LondonIce Accretion2060RCP4.5 | London | Ice Accretion | RCP4.5 | 2060 | 19.9335 | 24.1271 | 29.4208 | 33.4552 | 37.4734
| LondonIce Accretion2065RCP4.5 | London | Ice Accretion | RCP4.5 | 2065 | 19.5193 | 23.6703 | 28.9024 | 32.8911 | 36.8605
| LondonIce Accretion2070RCP4.5 | London | Ice Accretion | RCP4.5 | 2070 | 19.1052 | 23.2134 | 28.384 | 32.327 | 36.2477
| LondonIce Accretion2075RCP4.5 | London | Ice Accretion | RCP4.5 | 2075 | 18.9604 | 23.0674 | 28.2347 | 32.1703 | 36.0864
| LondonIce Accretion2080RCP4.5 | London | Ice Accretion | RCP4.5 | 2080 | 18.8157 | 22.9213 | 28.0853 | 32.0137 | 35.9251
| LondonIce Accretion2085RCP4.5 | London | Ice Accretion | RCP4.5 | 2085 | 18.6709 | 22.7752 | 27.936 | 31.857 | 35.7638
| LondonIce Accretion2090RCP4.5 | London | Ice Accretion | RCP4.5 | 2090 | 18.5262 | 22.6291 | 27.7867 | 31.7003 | 35.6026
| LondonIce Accretion2095RCP4.5 | London | Ice Accretion | RCP4.5 | 2095 | 18.3815 | 22.483 | 27.6373 | 31.5436 | 35.4413
| LondonIce Accretion2100RCP4.5 | London | Ice Accretion | RCP4.5 | 2100 | 18.2367 | 22.337 | 27.488 | 31.3869 | 35.28
| LondonIce Accretion2023RCP6.0 | London | Ice Accretion | RCP6.0 | 2023 | 21.9553 | 26.3475 | 31.904 | 36.1238 | 40.3603
| LondonIce Accretion2025RCP6.0 | London | Ice Accretion | RCP6.0 | 2025 | 21.8254 | 26.2059 | 31.7493 | 35.9611 | 40.1856
| LondonIce Accretion2030RCP6.0 | London | Ice Accretion | RCP6.0 | 2030 | 21.6956 | 26.0642 | 31.5947 | 35.7984 | 40.0109
| LondonIce Accretion2035RCP6.0 | London | Ice Accretion | RCP6.0 | 2035 | 21.5657 | 25.9226 | 31.44 | 35.6357 | 39.8362
| LondonIce Accretion2040RCP6.0 | London | Ice Accretion | RCP6.0 | 2040 | 21.4358 | 25.7809 | 31.2853 | 35.473 | 39.6614
| LondonIce Accretion2045RCP6.0 | London | Ice Accretion | RCP6.0 | 2045 | 21.3059 | 25.6393 | 31.1307 | 35.3102 | 39.4867
| LondonIce Accretion2050RCP6.0 | London | Ice Accretion | RCP6.0 | 2050 | 20.7618 | 25.0408 | 30.4576 | 34.5834 | 38.6991
| LondonIce Accretion2055RCP6.0 | London | Ice Accretion | RCP6.0 | 2055 | 20.3477 | 24.5839 | 29.9392 | 34.0193 | 38.0863
| LondonIce Accretion2060RCP6.0 | London | Ice Accretion | RCP6.0 | 2060 | 19.9335 | 24.1271 | 29.4208 | 33.4552 | 37.4734
| LondonIce Accretion2065RCP6.0 | London | Ice Accretion | RCP6.0 | 2065 | 19.5193 | 23.6703 | 28.9024 | 32.8911 | 36.8605
| LondonIce Accretion2070RCP6.0 | London | Ice Accretion | RCP6.0 | 2070 | 19.1052 | 23.2134 | 28.384 | 32.327 | 36.2477
| LondonIce Accretion2075RCP6.0 | London | Ice Accretion | RCP6.0 | 2075 | 18.888 | 22.9943 | 28.16 | 32.092 | 36.0058
| LondonIce Accretion2080RCP6.0 | London | Ice Accretion | RCP6.0 | 2080 | 18.6709 | 22.7752 | 27.936 | 31.857 | 35.7638
| LondonIce Accretion2085RCP6.0 | London | Ice Accretion | RCP6.0 | 2085 | 18.4538 | 22.5561 | 27.712 | 31.6219 | 35.5219
| LondonIce Accretion2090RCP6.0 | London | Ice Accretion | RCP6.0 | 2090 | 17.7172 | 21.7526 | 26.8267 | 30.6637 | 34.487
| LondonIce Accretion2095RCP6.0 | London | Ice Accretion | RCP6.0 | 2095 | 17.1976 | 21.1683 | 26.1653 | 29.9405 | 33.6941
| LondonIce Accretion2100RCP6.0 | London | Ice Accretion | RCP6.0 | 2100 | 16.678 | 20.584 | 25.504 | 29.2173 | 32.9011
| LondonIce Accretion2023RCP8.5 | London | Ice Accretion | RCP8.5 | 2023 | 21.9553 | 26.3475 | 31.904 | 36.1238 | 40.3603
| LondonIce Accretion2025RCP8.5 | London | Ice Accretion | RCP8.5 | 2025 | 21.6956 | 26.0642 | 31.5947 | 35.7984 | 40.0109
| LondonIce Accretion2030RCP8.5 | London | Ice Accretion | RCP8.5 | 2030 | 21.4358 | 25.7809 | 31.2853 | 35.473 | 39.6614
| LondonIce Accretion2035RCP8.5 | London | Ice Accretion | RCP8.5 | 2035 | 21.176 | 25.4976 | 30.976 | 35.1475 | 39.312
| LondonIce Accretion2040RCP8.5 | London | Ice Accretion | RCP8.5 | 2040 | 20.4857 | 24.7362 | 30.112 | 34.2074 | 38.2906
| LondonIce Accretion2045RCP8.5 | London | Ice Accretion | RCP8.5 | 2045 | 19.7954 | 23.9748 | 29.248 | 33.2672 | 37.2691
| LondonIce Accretion2050RCP8.5 | London | Ice Accretion | RCP8.5 | 2050 | 18.8157 | 22.9213 | 28.0853 | 32.0137 | 35.9251
| LondonIce Accretion2055RCP8.5 | London | Ice Accretion | RCP8.5 | 2055 | 18.5262 | 22.6291 | 27.7867 | 31.7003 | 35.6026
| LondonIce Accretion2060RCP8.5 | London | Ice Accretion | RCP8.5 | 2060 | 17.7172 | 21.7526 | 26.8267 | 30.6637 | 34.487
| LondonIce Accretion2065RCP8.5 | London | Ice Accretion | RCP8.5 | 2065 | 17.1976 | 21.1683 | 26.1653 | 29.9405 | 33.6941
| LondonIce Accretion2070RCP8.5 | London | Ice Accretion | RCP8.5 | 2070 | 16.344 | 20.2299 | 25.12 | 28.7954 | 32.4576
| LondonIce Accretion2075RCP8.5 | London | Ice Accretion | RCP8.5 | 2075 | 16.01 | 19.8757 | 24.736 | 28.3735 | 32.0141
| LondonIce Accretion2080RCP8.5 | London | Ice Accretion | RCP8.5 | 2080 | 15.676 | 19.5216 | 24.352 | 27.9517 | 31.5706
| LondonIce Accretion2085RCP8.5 | London | Ice Accretion | RCP8.5 | 2085 | 14.6851 | 18.353 | 22.944 | 26.3787 | 29.8166
| LondonIce Accretion2090RCP8.5 | London | Ice Accretion | RCP8.5 | 2090 | 13.6943 | 17.1843 | 21.536 | 24.8058 | 28.0627
| LondonIce Accretion2095RCP8.5 | London | Ice Accretion | RCP8.5 | 2095 | 13.6943 | 17.1843 | 21.536 | 24.8058 | 28.0627
| LondonIce Accretion2100RCP8.5 | London | Ice Accretion | RCP8.5 | 2100 | 13.6943 | 17.1843 | 21.536 | 24.8058 | 28.0627
| LondonWind2023RCP4.5 | London | Wind | RCP4.5 | 2023 | 87.0563 | 93.9114 | 101.17 | 108.391 | 115.6188
| LondonWind2025RCP4.5 | London | Wind | RCP4.5 | 2025 | 87.1657 | 94.0571 | 101.3617 | 108.621 | 115.8886
| LondonWind2030RCP4.5 | London | Wind | RCP4.5 | 2030 | 87.275 | 94.2028 | 101.5533 | 108.8511 | 116.1584
| LondonWind2035RCP4.5 | London | Wind | RCP4.5 | 2035 | 87.3844 | 94.3485 | 101.745 | 109.0811 | 116.4282
| LondonWind2040RCP4.5 | London | Wind | RCP4.5 | 2040 | 87.4938 | 94.4942 | 101.9367 | 109.3112 | 116.698
| LondonWind2045RCP4.5 | London | Wind | RCP4.5 | 2045 | 87.6032 | 94.6399 | 102.1283 | 109.5412 | 116.9678
| LondonWind2050RCP4.5 | London | Wind | RCP4.5 | 2050 | 87.7644 | 94.8581 | 102.42 | 109.8954 | 117.3858
| LondonWind2055RCP4.5 | London | Wind | RCP4.5 | 2055 | 87.8162 | 94.9307 | 102.52 | 110.0195 | 117.534
| LondonWind2060RCP4.5 | London | Wind | RCP4.5 | 2060 | 87.868 | 95.0032 | 102.62 | 110.1437 | 117.6822
| LondonWind2065RCP4.5 | London | Wind | RCP4.5 | 2065 | 87.9198 | 95.0758 | 102.72 | 110.2678 | 117.8304
| LondonWind2070RCP4.5 | London | Wind | RCP4.5 | 2070 | 87.9716 | 95.1483 | 102.82 | 110.3919 | 117.9786
| LondonWind2075RCP4.5 | London | Wind | RCP4.5 | 2075 | 88.1241 | 95.3467 | 103.0767 | 110.6969 | 118.3339
| LondonWind2080RCP4.5 | London | Wind | RCP4.5 | 2080 | 88.2767 | 95.5451 | 103.3333 | 111.0018 | 118.6892
| LondonWind2085RCP4.5 | London | Wind | RCP4.5 | 2085 | 88.4292 | 95.7435 | 103.59 | 111.3067 | 119.0445
| LondonWind2090RCP4.5 | London | Wind | RCP4.5 | 2090 | 88.5818 | 95.9419 | 103.8467 | 111.6117 | 119.3998
| LondonWind2095RCP4.5 | London | Wind | RCP4.5 | 2095 | 88.7343 | 96.1403 | 104.1033 | 111.9167 | 119.7551
| LondonWind2100RCP4.5 | London | Wind | RCP4.5 | 2100 | 88.8869 | 96.3387 | 104.36 | 112.2216 | 120.1104
| LondonWind2023RCP6.0 | London | Wind | RCP6.0 | 2023 | 87.0563 | 93.9114 | 101.17 | 108.391 | 115.6188
| LondonWind2025RCP6.0 | London | Wind | RCP6.0 | 2025 | 87.1657 | 94.0571 | 101.3617 | 108.621 | 115.8886
| LondonWind2030RCP6.0 | London | Wind | RCP6.0 | 2030 | 87.275 | 94.2028 | 101.5533 | 108.8511 | 116.1584
| LondonWind2035RCP6.0 | London | Wind | RCP6.0 | 2035 | 87.3844 | 94.3485 | 101.745 | 109.0811 | 116.4282
| LondonWind2040RCP6.0 | London | Wind | RCP6.0 | 2040 | 87.4938 | 94.4942 | 101.9367 | 109.3112 | 116.698
| LondonWind2045RCP6.0 | London | Wind | RCP6.0 | 2045 | 87.6032 | 94.6399 | 102.1283 | 109.5412 | 116.9678
| LondonWind2050RCP6.0 | London | Wind | RCP6.0 | 2050 | 87.7644 | 94.8581 | 102.42 | 109.8954 | 117.3858
| LondonWind2055RCP6.0 | London | Wind | RCP6.0 | 2055 | 87.8162 | 94.9307 | 102.52 | 110.0195 | 117.534
| LondonWind2060RCP6.0 | London | Wind | RCP6.0 | 2060 | 87.868 | 95.0032 | 102.62 | 110.1437 | 117.6822
| LondonWind2065RCP6.0 | London | Wind | RCP6.0 | 2065 | 87.9198 | 95.0758 | 102.72 | 110.2678 | 117.8304
| LondonWind2070RCP6.0 | London | Wind | RCP6.0 | 2070 | 87.9716 | 95.1483 | 102.82 | 110.3919 | 117.9786
| LondonWind2075RCP6.0 | London | Wind | RCP6.0 | 2075 | 88.2004 | 95.4459 | 103.205 | 110.8493 | 118.5115
| LondonWind2080RCP6.0 | London | Wind | RCP6.0 | 2080 | 88.4292 | 95.7435 | 103.59 | 111.3067 | 119.0445
| LondonWind2085RCP6.0 | London | Wind | RCP6.0 | 2085 | 88.6581 | 96.0411 | 103.975 | 111.7642 | 119.5774
| LondonWind2090RCP6.0 | London | Wind | RCP6.0 | 2090 | 89.2639 | 96.8192 | 104.9633 | 112.9314 | 120.9312
| LondonWind2095RCP6.0 | London | Wind | RCP6.0 | 2095 | 89.641 | 97.2997 | 105.5667 | 113.6411 | 121.752
| LondonWind2100RCP6.0 | London | Wind | RCP6.0 | 2100 | 90.018 | 97.7802 | 106.17 | 114.3509 | 122.5728
| LondonWind2023RCP8.5 | London | Wind | RCP8.5 | 2023 | 87.0563 | 93.9114 | 101.17 | 108.391 | 115.6188
| LondonWind2025RCP8.5 | London | Wind | RCP8.5 | 2025 | 87.275 | 94.2028 | 101.5533 | 108.8511 | 116.1584
| LondonWind2030RCP8.5 | London | Wind | RCP8.5 | 2030 | 87.4938 | 94.4942 | 101.9367 | 109.3112 | 116.698
| LondonWind2035RCP8.5 | London | Wind | RCP8.5 | 2035 | 87.7125 | 94.7856 | 102.32 | 109.7713 | 117.2376
| LondonWind2040RCP8.5 | London | Wind | RCP8.5 | 2040 | 87.7989 | 94.9065 | 102.4867 | 109.9782 | 117.4846
| LondonWind2045RCP8.5 | London | Wind | RCP8.5 | 2045 | 87.8852 | 95.0274 | 102.6533 | 110.185 | 117.7316
| LondonWind2050RCP8.5 | London | Wind | RCP8.5 | 2050 | 88.2767 | 95.5451 | 103.3333 | 111.0018 | 118.6892
| LondonWind2055RCP8.5 | London | Wind | RCP8.5 | 2055 | 88.5818 | 95.9419 | 103.8467 | 111.6117 | 119.3998
| LondonWind2060RCP8.5 | London | Wind | RCP8.5 | 2060 | 89.2639 | 96.8192 | 104.9633 | 112.9314 | 120.9312
| LondonWind2065RCP8.5 | London | Wind | RCP8.5 | 2065 | 89.641 | 97.2997 | 105.5667 | 113.6411 | 121.752
| LondonWind2070RCP8.5 | London | Wind | RCP8.5 | 2070 | 90.2512 | 98.0716 | 106.54 | 114.7896 | 123.0782
| LondonWind2075RCP8.5 | London | Wind | RCP8.5 | 2075 | 90.4843 | 98.363 | 106.91 | 115.2283 | 123.5836
| LondonWind2080RCP8.5 | London | Wind | RCP8.5 | 2080 | 90.7175 | 98.6544 | 107.28 | 115.667 | 124.089
| LondonWind2085RCP8.5 | London | Wind | RCP8.5 | 2085 | 91.1147 | 99.1799 | 107.97 | 116.4909 | 125.058
| LondonWind2090RCP8.5 | London | Wind | RCP8.5 | 2090 | 91.5119 | 99.7053 | 108.66 | 117.3148 | 126.027
| LondonWind2095RCP8.5 | London | Wind | RCP8.5 | 2095 | 91.5119 | 99.7053 | 108.66 | 117.3148 | 126.027
| LondonWind2100RCP8.5 | London | Wind | RCP8.5 | 2100 | 91.5119 | 99.7053 | 108.66 | 117.3148 | 126.027
| LucanIce Accretion2023RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425
| LucanIce Accretion2025RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2025 | 17.1352 | 20.5563 | 24.8625 | 28.1605 | 31.4423
| LucanIce Accretion2030RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2030 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542
| LucanIce Accretion2035RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2035 | 17.17 | 20.6255 | 24.9875 | 28.3206 | 31.6418
| LucanIce Accretion2040RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2040 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415
| LucanIce Accretion2045RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2045 | 17.2048 | 20.6947 | 25.1125 | 28.4807 | 31.8412
| LucanIce Accretion2050RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2050 | 17.1526 | 20.6794 | 25.145 | 28.5438 | 31.941
| LucanIce Accretion2055RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2055 | 17.083 | 20.6296 | 25.115 | 28.5268 | 31.941
| LucanIce Accretion2060RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2060 | 17.0134 | 20.5799 | 25.085 | 28.5099 | 31.941
| LucanIce Accretion2065RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2065 | 16.9439 | 20.53 | 25.055 | 28.4929 | 31.941
| LucanIce Accretion2070RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2070 | 16.8743 | 20.4802 | 25.025 | 28.476 | 31.941
| LucanIce Accretion2075RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2075 | 16.8424 | 20.4664 | 25.0375 | 28.5042 | 31.9883
| LucanIce Accretion2080RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2080 | 16.8105 | 20.4526 | 25.05 | 28.5325 | 32.0355
| LucanIce Accretion2085RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2085 | 16.7786 | 20.4387 | 25.0625 | 28.5607 | 32.0827
| LucanIce Accretion2090RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2090 | 16.7467 | 20.4249 | 25.075 | 28.589 | 32.13
| LucanIce Accretion2095RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2095 | 16.7148 | 20.4111 | 25.0875 | 28.6172 | 32.1773
| LucanIce Accretion2100RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.3972 | 25.1 | 28.6455 | 32.2245
| LucanIce Accretion2023RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425
| LucanIce Accretion2025RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2025 | 17.1352 | 20.5563 | 24.8625 | 28.1605 | 31.4423
| LucanIce Accretion2030RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2030 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542
| LucanIce Accretion2035RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2035 | 17.17 | 20.6255 | 24.9875 | 28.3206 | 31.6418
| LucanIce Accretion2040RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2040 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415
| LucanIce Accretion2045RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2045 | 17.2048 | 20.6947 | 25.1125 | 28.4807 | 31.8412
| LucanIce Accretion2050RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2050 | 17.1526 | 20.6794 | 25.145 | 28.5438 | 31.941
| LucanIce Accretion2055RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2055 | 17.083 | 20.6296 | 25.115 | 28.5268 | 31.941
| LucanIce Accretion2060RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2060 | 17.0134 | 20.5799 | 25.085 | 28.5099 | 31.941
| LucanIce Accretion2065RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2065 | 16.9439 | 20.53 | 25.055 | 28.4929 | 31.941
| LucanIce Accretion2070RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2070 | 16.8743 | 20.4802 | 25.025 | 28.476 | 31.941
| LucanIce Accretion2075RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2075 | 16.8264 | 20.4595 | 25.0437 | 28.5184 | 32.0119
| LucanIce Accretion2080RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2080 | 16.7786 | 20.4387 | 25.0625 | 28.5607 | 32.0827
| LucanIce Accretion2085RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2085 | 16.7308 | 20.418 | 25.0813 | 28.6031 | 32.1536
| LucanIce Accretion2090RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2090 | 16.4742 | 20.1898 | 24.8833 | 28.4289 | 31.9935
| LucanIce Accretion2095RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2095 | 16.2654 | 19.9822 | 24.6667 | 28.2123 | 31.7625
| LucanIce Accretion2100RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2100 | 16.0566 | 19.7747 | 24.45 | 27.9957 | 31.5315
| LucanIce Accretion2023RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425
| LucanIce Accretion2025RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2025 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542
| LucanIce Accretion2030RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2030 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415
| LucanIce Accretion2035RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2035 | 17.2222 | 20.7293 | 25.175 | 28.5607 | 31.941
| LucanIce Accretion2040RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2040 | 17.1062 | 20.6462 | 25.125 | 28.5325 | 31.941
| LucanIce Accretion2045RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2045 | 16.9902 | 20.5633 | 25.075 | 28.5042 | 31.941
| LucanIce Accretion2050RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2050 | 16.8105 | 20.4526 | 25.05 | 28.5325 | 32.0355
| LucanIce Accretion2055RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2055 | 16.7467 | 20.4249 | 25.075 | 28.589 | 32.13
| LucanIce Accretion2060RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2060 | 16.4742 | 20.1898 | 24.8833 | 28.4289 | 31.9935
| LucanIce Accretion2065RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2065 | 16.2654 | 19.9822 | 24.6667 | 28.2123 | 31.7625
| LucanIce Accretion2070RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2070 | 15.6797 | 19.3528 | 23.975 | 27.4778 | 30.9645
| LucanIce Accretion2075RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2075 | 15.3028 | 18.9309 | 23.5 | 26.9599 | 30.3975
| LucanIce Accretion2080RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2080 | 14.9259 | 18.509 | 23.025 | 26.442 | 29.8305
| LucanIce Accretion2085RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2085 | 14.1431 | 17.5856 | 21.925 | 25.2131 | 28.476
| LucanIce Accretion2090RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2090 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215
| LucanIce Accretion2095RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2095 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215
| LucanIce Accretion2100RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2100 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215
| LucanWind2023RCP4.5 | Lucan | Wind | RCP4.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| LucanWind2025RCP4.5 | Lucan | Wind | RCP4.5 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
| LucanWind2030RCP4.5 | Lucan | Wind | RCP4.5 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| LucanWind2035RCP4.5 | Lucan | Wind | RCP4.5 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
| LucanWind2040RCP4.5 | Lucan | Wind | RCP4.5 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| LucanWind2045RCP4.5 | Lucan | Wind | RCP4.5 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
| LucanWind2050RCP4.5 | Lucan | Wind | RCP4.5 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
| LucanWind2055RCP4.5 | Lucan | Wind | RCP4.5 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
| LucanWind2060RCP4.5 | Lucan | Wind | RCP4.5 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
| LucanWind2065RCP4.5 | Lucan | Wind | RCP4.5 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
| LucanWind2070RCP4.5 | Lucan | Wind | RCP4.5 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
| LucanWind2075RCP4.5 | Lucan | Wind | RCP4.5 | 2075 | 86.3504 | 93.3577 | 100.8387 | 108.226 | 115.6228
| LucanWind2080RCP4.5 | Lucan | Wind | RCP4.5 | 2080 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
| LucanWind2085RCP4.5 | Lucan | Wind | RCP4.5 | 2085 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
| LucanWind2090RCP4.5 | Lucan | Wind | RCP4.5 | 2090 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
| LucanWind2095RCP4.5 | Lucan | Wind | RCP4.5 | 2095 | 86.7678 | 93.9167 | 101.5705 | 109.1068 | 116.6655
| LucanWind2100RCP4.5 | Lucan | Wind | RCP4.5 | 2100 | 86.8722 | 94.0565 | 101.7534 | 109.327 | 116.9262
| LucanWind2023RCP6.0 | Lucan | Wind | RCP6.0 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| LucanWind2025RCP6.0 | Lucan | Wind | RCP6.0 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
| LucanWind2030RCP6.0 | Lucan | Wind | RCP6.0 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| LucanWind2035RCP6.0 | Lucan | Wind | RCP6.0 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
| LucanWind2040RCP6.0 | Lucan | Wind | RCP6.0 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| LucanWind2045RCP6.0 | Lucan | Wind | RCP6.0 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
| LucanWind2050RCP6.0 | Lucan | Wind | RCP6.0 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
| LucanWind2055RCP6.0 | Lucan | Wind | RCP6.0 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
| LucanWind2060RCP6.0 | Lucan | Wind | RCP6.0 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
| LucanWind2065RCP6.0 | Lucan | Wind | RCP6.0 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
| LucanWind2070RCP6.0 | Lucan | Wind | RCP6.0 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
| LucanWind2075RCP6.0 | Lucan | Wind | RCP6.0 | 2075 | 86.4026 | 93.4276 | 100.9302 | 108.3361 | 115.7531
| LucanWind2080RCP6.0 | Lucan | Wind | RCP6.0 | 2080 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
| LucanWind2085RCP6.0 | Lucan | Wind | RCP6.0 | 2085 | 86.7157 | 93.8469 | 101.479 | 108.9967 | 116.5351
| LucanWind2090RCP6.0 | Lucan | Wind | RCP6.0 | 2090 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
| LucanWind2095RCP6.0 | Lucan | Wind | RCP6.0 | 2095 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
| LucanWind2100RCP6.0 | Lucan | Wind | RCP6.0 | 2100 | 87.7861 | 95.1502 | 103.0568 | 110.8265 | 118.6131
| LucanWind2023RCP8.5 | Lucan | Wind | RCP8.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| LucanWind2025RCP8.5 | Lucan | Wind | RCP8.5 | 2025 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| LucanWind2030RCP8.5 | Lucan | Wind | RCP8.5 | 2030 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| LucanWind2035RCP8.5 | Lucan | Wind | RCP8.5 | 2035 | 86.0768 | 93.0084 | 100.3912 | 107.7017 | 115.0269
| LucanWind2040RCP8.5 | Lucan | Wind | RCP8.5 | 2040 | 86.1332 | 93.0782 | 100.4794 | 107.8031 | 115.1386
| LucanWind2045RCP8.5 | Lucan | Wind | RCP8.5 | 2045 | 86.1896 | 93.1481 | 100.5676 | 107.9044 | 115.2504
| LucanWind2050RCP8.5 | Lucan | Wind | RCP8.5 | 2050 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
| LucanWind2055RCP8.5 | Lucan | Wind | RCP8.5 | 2055 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
| LucanWind2060RCP8.5 | Lucan | Wind | RCP8.5 | 2060 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
| LucanWind2065RCP8.5 | Lucan | Wind | RCP8.5 | 2065 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
| LucanWind2070RCP8.5 | Lucan | Wind | RCP8.5 | 2070 | 88.0541 | 95.5026 | 103.5207 | 111.3788 | 119.2611
| LucanWind2075RCP8.5 | Lucan | Wind | RCP8.5 | 2075 | 88.322 | 95.855 | 103.9845 | 111.9311 | 119.9091
| LucanWind2080RCP8.5 | Lucan | Wind | RCP8.5 | 2080 | 88.59 | 96.2074 | 104.4484 | 112.4833 | 120.5571
| LucanWind2085RCP8.5 | Lucan | Wind | RCP8.5 | 2085 | 88.9454 | 96.6585 | 105.0217 | 113.1649 | 121.3447
| LucanWind2090RCP8.5 | Lucan | Wind | RCP8.5 | 2090 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| LucanWind2095RCP8.5 | Lucan | Wind | RCP8.5 | 2095 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| LucanWind2100RCP8.5 | Lucan | Wind | RCP8.5 | 2100 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| MaitlandIce Accretion2023RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2023 | 20.6249 | 24.5763 | 29.61 | 33.4593 | 37.3086
| MaitlandIce Accretion2025RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2025 | 20.6945 | 24.6801 | 29.755 | 33.6345 | 37.5102
| MaitlandIce Accretion2030RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2030 | 20.764 | 24.7838 | 29.9 | 33.8096 | 37.7118
| MaitlandIce Accretion2035RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2035 | 20.8336 | 24.8875 | 30.045 | 33.9847 | 37.9134
| MaitlandIce Accretion2040RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2040 | 20.9032 | 24.9913 | 30.19 | 34.1599 | 38.115
| MaitlandIce Accretion2045RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2045 | 20.9728 | 25.0951 | 30.335 | 34.335 | 38.3166
| MaitlandIce Accretion2050RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2050 | 20.9046 | 25.0544 | 30.318 | 34.3339 | 38.3368
| MaitlandIce Accretion2055RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2055 | 20.7668 | 24.91 | 30.156 | 34.1576 | 38.1553
| MaitlandIce Accretion2060RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2060 | 20.6291 | 24.7655 | 29.994 | 33.9814 | 37.9739
| MaitlandIce Accretion2065RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2065 | 20.4913 | 24.6211 | 29.832 | 33.8051 | 37.7924
| MaitlandIce Accretion2070RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2070 | 20.3535 | 24.4767 | 29.67 | 33.6288 | 37.611
| MaitlandIce Accretion2075RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2075 | 20.4231 | 24.5846 | 29.825 | 33.8209 | 37.8378
| MaitlandIce Accretion2080RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2080 | 20.4927 | 24.6925 | 29.98 | 34.013 | 38.0646
| MaitlandIce Accretion2085RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2085 | 20.5623 | 24.8004 | 30.135 | 34.2051 | 38.2914
| MaitlandIce Accretion2090RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2090 | 20.6318 | 24.9083 | 30.29 | 34.3972 | 38.5182
| MaitlandIce Accretion2095RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2095 | 20.7014 | 25.0162 | 30.445 | 34.5893 | 38.745
| MaitlandIce Accretion2100RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2100 | 20.771 | 25.1241 | 30.6 | 34.7814 | 38.9718
| MaitlandIce Accretion2023RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2023 | 20.6249 | 24.5763 | 29.61 | 33.4593 | 37.3086
| MaitlandIce Accretion2025RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2025 | 20.6945 | 24.6801 | 29.755 | 33.6345 | 37.5102
| MaitlandIce Accretion2030RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2030 | 20.764 | 24.7838 | 29.9 | 33.8096 | 37.7118
| MaitlandIce Accretion2035RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2035 | 20.8336 | 24.8875 | 30.045 | 33.9847 | 37.9134
| MaitlandIce Accretion2040RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2040 | 20.9032 | 24.9913 | 30.19 | 34.1599 | 38.115
| MaitlandIce Accretion2045RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2045 | 20.9728 | 25.0951 | 30.335 | 34.335 | 38.3166
| MaitlandIce Accretion2050RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2050 | 20.9046 | 25.0544 | 30.318 | 34.3339 | 38.3368
| MaitlandIce Accretion2055RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2055 | 20.7668 | 24.91 | 30.156 | 34.1576 | 38.1553
| MaitlandIce Accretion2060RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2060 | 20.6291 | 24.7655 | 29.994 | 33.9814 | 37.9739
| MaitlandIce Accretion2065RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2065 | 20.4913 | 24.6211 | 29.832 | 33.8051 | 37.7924
| MaitlandIce Accretion2070RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2070 | 20.3535 | 24.4767 | 29.67 | 33.6288 | 37.611
| MaitlandIce Accretion2075RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2075 | 20.4579 | 24.6385 | 29.9025 | 33.9169 | 37.9512
| MaitlandIce Accretion2080RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2080 | 20.5623 | 24.8004 | 30.135 | 34.2051 | 38.2914
| MaitlandIce Accretion2085RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2085 | 20.6666 | 24.9622 | 30.3675 | 34.4932 | 38.6316
| MaitlandIce Accretion2090RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2090 | 20.6249 | 24.9913 | 30.49 | 34.6797 | 38.8836
| MaitlandIce Accretion2095RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2095 | 20.4788 | 24.8585 | 30.38 | 34.578 | 38.7954
| MaitlandIce Accretion2100RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2100 | 20.3326 | 24.7257 | 30.27 | 34.4763 | 38.7072
| MaitlandIce Accretion2023RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2023 | 20.6249 | 24.5763 | 29.61 | 33.4593 | 37.3086
| MaitlandIce Accretion2025RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2025 | 20.764 | 24.7838 | 29.9 | 33.8096 | 37.7118
| MaitlandIce Accretion2030RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2030 | 20.9032 | 24.9913 | 30.19 | 34.1599 | 38.115
| MaitlandIce Accretion2035RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2035 | 21.0424 | 25.1988 | 30.48 | 34.5102 | 38.5182
| MaitlandIce Accretion2040RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2040 | 20.8128 | 24.9581 | 30.21 | 34.2164 | 38.2158
| MaitlandIce Accretion2045RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2045 | 20.5831 | 24.7174 | 29.94 | 33.9226 | 37.9134
| MaitlandIce Accretion2050RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2050 | 20.4927 | 24.6925 | 29.98 | 34.013 | 38.0646
| MaitlandIce Accretion2055RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2055 | 20.6318 | 24.9083 | 30.29 | 34.3972 | 38.5182
| MaitlandIce Accretion2060RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2060 | 20.6249 | 24.9913 | 30.49 | 34.6797 | 38.8836
| MaitlandIce Accretion2065RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2065 | 20.4788 | 24.8585 | 30.38 | 34.578 | 38.7954
| MaitlandIce Accretion2070RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2070 | 20.0473 | 24.4103 | 29.91 | 34.0808 | 38.2662
| MaitlandIce Accretion2075RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2075 | 19.762 | 24.0949 | 29.55 | 33.6853 | 37.8252
| MaitlandIce Accretion2080RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2080 | 19.4767 | 23.7795 | 29.19 | 33.2898 | 37.3842
| MaitlandIce Accretion2085RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2085 | 18.7148 | 22.8831 | 28.14 | 32.1202 | 36.0801
| MaitlandIce Accretion2090RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2090 | 17.9528 | 21.9867 | 27.09 | 30.9507 | 34.776
| MaitlandIce Accretion2095RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2095 | 17.9528 | 21.9867 | 27.09 | 30.9507 | 34.776
| MaitlandIce Accretion2100RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2100 | 17.9528 | 21.9867 | 27.09 | 30.9507 | 34.776
| MaitlandWind2023RCP4.5 | Maitland | Wind | RCP4.5 | 2023 | 81.0025 | 87.3376 | 94.0323 | 100.7041 | 107.3771
| MaitlandWind2025RCP4.5 | Maitland | Wind | RCP4.5 | 2025 | 81.0065 | 87.3333 | 94.0153 | 100.6759 | 107.3399
| MaitlandWind2030RCP4.5 | Maitland | Wind | RCP4.5 | 2030 | 81.0105 | 87.329 | 93.9982 | 100.6477 | 107.3028
| MaitlandWind2035RCP4.5 | Maitland | Wind | RCP4.5 | 2035 | 81.0146 | 87.3246 | 93.9812 | 100.6195 | 107.2657
| MaitlandWind2040RCP4.5 | Maitland | Wind | RCP4.5 | 2040 | 81.0186 | 87.3203 | 93.9641 | 100.5913 | 107.2286
| MaitlandWind2045RCP4.5 | Maitland | Wind | RCP4.5 | 2045 | 81.0226 | 87.316 | 93.9471 | 100.5631 | 107.1915
| MaitlandWind2050RCP4.5 | Maitland | Wind | RCP4.5 | 2050 | 80.9447 | 87.1871 | 93.7514 | 100.314 | 106.8851
| MaitlandWind2055RCP4.5 | Maitland | Wind | RCP4.5 | 2055 | 80.8628 | 87.0626 | 93.5729 | 100.0931 | 106.6158
| MaitlandWind2060RCP4.5 | Maitland | Wind | RCP4.5 | 2060 | 80.7809 | 86.938 | 93.3943 | 99.8722 | 106.3465
| MaitlandWind2065RCP4.5 | Maitland | Wind | RCP4.5 | 2065 | 80.699 | 86.8135 | 93.2158 | 99.6513 | 106.0773
| MaitlandWind2070RCP4.5 | Maitland | Wind | RCP4.5 | 2070 | 80.6171 | 86.6889 | 93.0372 | 99.4304 | 105.808
| MaitlandWind2075RCP4.5 | Maitland | Wind | RCP4.5 | 2075 | 80.5836 | 86.6457 | 92.9845 | 99.369 | 105.739
| MaitlandWind2080RCP4.5 | Maitland | Wind | RCP4.5 | 2080 | 80.5501 | 86.6024 | 92.9318 | 99.3077 | 105.6701
| MaitlandWind2085RCP4.5 | Maitland | Wind | RCP4.5 | 2085 | 80.5167 | 86.5592 | 92.8791 | 99.2463 | 105.6012
| MaitlandWind2090RCP4.5 | Maitland | Wind | RCP4.5 | 2090 | 80.4832 | 86.5159 | 92.8264 | 99.1849 | 105.5323
| MaitlandWind2095RCP4.5 | Maitland | Wind | RCP4.5 | 2095 | 80.4498 | 86.4727 | 92.7737 | 99.1236 | 105.4634
| MaitlandWind2100RCP4.5 | Maitland | Wind | RCP4.5 | 2100 | 80.4163 | 86.4295 | 92.721 | 99.0622 | 105.3945
| MaitlandWind2023RCP6.0 | Maitland | Wind | RCP6.0 | 2023 | 81.0025 | 87.3376 | 94.0323 | 100.7041 | 107.3771
| MaitlandWind2025RCP6.0 | Maitland | Wind | RCP6.0 | 2025 | 81.0065 | 87.3333 | 94.0153 | 100.6759 | 107.3399
| MaitlandWind2030RCP6.0 | Maitland | Wind | RCP6.0 | 2030 | 81.0105 | 87.329 | 93.9982 | 100.6477 | 107.3028
| MaitlandWind2035RCP6.0 | Maitland | Wind | RCP6.0 | 2035 | 81.0146 | 87.3246 | 93.9812 | 100.6195 | 107.2657
| MaitlandWind2040RCP6.0 | Maitland | Wind | RCP6.0 | 2040 | 81.0186 | 87.3203 | 93.9641 | 100.5913 | 107.2286
| MaitlandWind2045RCP6.0 | Maitland | Wind | RCP6.0 | 2045 | 81.0226 | 87.316 | 93.9471 | 100.5631 | 107.1915
| MaitlandWind2050RCP6.0 | Maitland | Wind | RCP6.0 | 2050 | 80.9447 | 87.1871 | 93.7514 | 100.314 | 106.8851
| MaitlandWind2055RCP6.0 | Maitland | Wind | RCP6.0 | 2055 | 80.8628 | 87.0626 | 93.5729 | 100.0931 | 106.6158
| MaitlandWind2060RCP6.0 | Maitland | Wind | RCP6.0 | 2060 | 80.7809 | 86.938 | 93.3943 | 99.8722 | 106.3465
| MaitlandWind2065RCP6.0 | Maitland | Wind | RCP6.0 | 2065 | 80.699 | 86.8135 | 93.2158 | 99.6513 | 106.0773
| MaitlandWind2070RCP6.0 | Maitland | Wind | RCP6.0 | 2070 | 80.6171 | 86.6889 | 93.0372 | 99.4304 | 105.808
| MaitlandWind2075RCP6.0 | Maitland | Wind | RCP6.0 | 2075 | 80.5669 | 86.6241 | 92.9582 | 99.3383 | 105.7046
| MaitlandWind2080RCP6.0 | Maitland | Wind | RCP6.0 | 2080 | 80.5167 | 86.5592 | 92.8791 | 99.2463 | 105.6012
| MaitlandWind2085RCP6.0 | Maitland | Wind | RCP6.0 | 2085 | 80.4665 | 86.4943 | 92.8 | 99.1543 | 105.4979
| MaitlandWind2090RCP6.0 | Maitland | Wind | RCP6.0 | 2090 | 80.3467 | 86.3343 | 92.5877 | 98.8964 | 105.193
| MaitlandWind2095RCP6.0 | Maitland | Wind | RCP6.0 | 2095 | 80.2771 | 86.2392 | 92.4544 | 98.7305 | 104.9916
| MaitlandWind2100RCP6.0 | Maitland | Wind | RCP6.0 | 2100 | 80.2075 | 86.144 | 92.3211 | 98.5647 | 104.7902
| MaitlandWind2023RCP8.5 | Maitland | Wind | RCP8.5 | 2023 | 81.0025 | 87.3376 | 94.0323 | 100.7041 | 107.3771
| MaitlandWind2025RCP8.5 | Maitland | Wind | RCP8.5 | 2025 | 81.0105 | 87.329 | 93.9982 | 100.6477 | 107.3028
| MaitlandWind2030RCP8.5 | Maitland | Wind | RCP8.5 | 2030 | 81.0186 | 87.3203 | 93.9641 | 100.5913 | 107.2286
| MaitlandWind2035RCP8.5 | Maitland | Wind | RCP8.5 | 2035 | 81.0266 | 87.3117 | 93.93 | 100.535 | 107.1544
| MaitlandWind2040RCP8.5 | Maitland | Wind | RCP8.5 | 2040 | 80.8901 | 87.1041 | 93.6324 | 100.1668 | 106.7056
| MaitlandWind2045RCP8.5 | Maitland | Wind | RCP8.5 | 2045 | 80.7536 | 86.8965 | 93.3348 | 99.7986 | 106.2568
| MaitlandWind2050RCP8.5 | Maitland | Wind | RCP8.5 | 2050 | 80.5501 | 86.6024 | 92.9318 | 99.3077 | 105.6701
| MaitlandWind2055RCP8.5 | Maitland | Wind | RCP8.5 | 2055 | 80.4832 | 86.5159 | 92.8264 | 99.1849 | 105.5323
| MaitlandWind2060RCP8.5 | Maitland | Wind | RCP8.5 | 2060 | 80.3467 | 86.3343 | 92.5877 | 98.8964 | 105.193
| MaitlandWind2065RCP8.5 | Maitland | Wind | RCP8.5 | 2065 | 80.2771 | 86.2392 | 92.4544 | 98.7305 | 104.9916
| MaitlandWind2070RCP8.5 | Maitland | Wind | RCP8.5 | 2070 | 80.336 | 86.3141 | 92.5443 | 98.8333 | 105.1118
| MaitlandWind2075RCP8.5 | Maitland | Wind | RCP8.5 | 2075 | 80.4645 | 86.4842 | 92.7675 | 99.102 | 105.4334
| MaitlandWind2080RCP8.5 | Maitland | Wind | RCP8.5 | 2080 | 80.593 | 86.6543 | 92.9907 | 99.3707 | 105.755
| MaitlandWind2085RCP8.5 | Maitland | Wind | RCP8.5 | 2085 | 80.5769 | 86.6543 | 93.0093 | 99.4055 | 105.8027
| MaitlandWind2090RCP8.5 | Maitland | Wind | RCP8.5 | 2090 | 80.5608 | 86.6543 | 93.0279 | 99.4403 | 105.8504
| MaitlandWind2095RCP8.5 | Maitland | Wind | RCP8.5 | 2095 | 80.5608 | 86.6543 | 93.0279 | 99.4403 | 105.8504
| MaitlandWind2100RCP8.5 | Maitland | Wind | RCP8.5 | 2100 | 80.5608 | 86.6543 | 93.0279 | 99.4403 | 105.8504
| MarkdaleIce Accretion2023RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2023 | 15.3852 | 18.3878 | 22.198 | 25.1335 | 28.0249
| MarkdaleIce Accretion2025RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2025 | 15.3954 | 18.4122 | 22.2383 | 25.1832 | 28.0896
| MarkdaleIce Accretion2030RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2030 | 15.4056 | 18.4365 | 22.2787 | 25.2329 | 28.1543
| MarkdaleIce Accretion2035RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2035 | 15.4158 | 18.4609 | 22.319 | 25.2826 | 28.219
| MarkdaleIce Accretion2040RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2040 | 15.426 | 18.4852 | 22.3593 | 25.3323 | 28.2836
| MarkdaleIce Accretion2045RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2045 | 15.4362 | 18.5096 | 22.3997 | 25.3821 | 28.3483
| MarkdaleIce Accretion2050RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2050 | 15.3913 | 18.4828 | 22.396 | 25.392 | 28.3742
| MarkdaleIce Accretion2055RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2055 | 15.3362 | 18.4316 | 22.352 | 25.3522 | 28.3354
| MarkdaleIce Accretion2060RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2060 | 15.2811 | 18.3805 | 22.308 | 25.3125 | 28.2966
| MarkdaleIce Accretion2065RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2065 | 15.2259 | 18.3294 | 22.264 | 25.2727 | 28.2578
| MarkdaleIce Accretion2070RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2070 | 15.1708 | 18.2783 | 22.22 | 25.2329 | 28.219
| MarkdaleIce Accretion2075RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2075 | 15.1147 | 18.2387 | 22.198 | 25.2205 | 28.219
| MarkdaleIce Accretion2080RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2080 | 15.0586 | 18.1991 | 22.176 | 25.208 | 28.219
| MarkdaleIce Accretion2085RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2085 | 15.0024 | 18.1596 | 22.154 | 25.1956 | 28.219
| MarkdaleIce Accretion2090RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2090 | 14.9463 | 18.12 | 22.132 | 25.1832 | 28.219
| MarkdaleIce Accretion2095RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2095 | 14.8902 | 18.0804 | 22.11 | 25.1707 | 28.219
| MarkdaleIce Accretion2100RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2100 | 14.834 | 18.0409 | 22.088 | 25.1583 | 28.219
| MarkdaleIce Accretion2023RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2023 | 15.3852 | 18.3878 | 22.198 | 25.1335 | 28.0249
| MarkdaleIce Accretion2025RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2025 | 15.3954 | 18.4122 | 22.2383 | 25.1832 | 28.0896
| MarkdaleIce Accretion2030RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2030 | 15.4056 | 18.4365 | 22.2787 | 25.2329 | 28.1543
| MarkdaleIce Accretion2035RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2035 | 15.4158 | 18.4609 | 22.319 | 25.2826 | 28.219
| MarkdaleIce Accretion2040RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2040 | 15.426 | 18.4852 | 22.3593 | 25.3323 | 28.2836
| MarkdaleIce Accretion2045RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2045 | 15.4362 | 18.5096 | 22.3997 | 25.3821 | 28.3483
| MarkdaleIce Accretion2050RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2050 | 15.3913 | 18.4828 | 22.396 | 25.392 | 28.3742
| MarkdaleIce Accretion2055RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2055 | 15.3362 | 18.4316 | 22.352 | 25.3522 | 28.3354
| MarkdaleIce Accretion2060RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2060 | 15.2811 | 18.3805 | 22.308 | 25.3125 | 28.2966
| MarkdaleIce Accretion2065RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2065 | 15.2259 | 18.3294 | 22.264 | 25.2727 | 28.2578
| MarkdaleIce Accretion2070RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2070 | 15.1708 | 18.2783 | 22.22 | 25.2329 | 28.219
| MarkdaleIce Accretion2075RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2075 | 15.0866 | 18.2189 | 22.187 | 25.2143 | 28.219
| MarkdaleIce Accretion2080RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2080 | 15.0024 | 18.1596 | 22.154 | 25.1956 | 28.219
| MarkdaleIce Accretion2085RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2085 | 14.9182 | 18.1002 | 22.121 | 25.177 | 28.219
| MarkdaleIce Accretion2090RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2090 | 14.5738 | 17.767 | 21.7873 | 24.8434 | 27.8863
| MarkdaleIce Accretion2095RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2095 | 14.3136 | 17.4931 | 21.4867 | 24.5285 | 27.5537
| MarkdaleIce Accretion2100RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2100 | 14.0533 | 17.2192 | 21.186 | 24.2136 | 27.221
| MarkdaleIce Accretion2023RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2023 | 15.3852 | 18.3878 | 22.198 | 25.1335 | 28.0249
| MarkdaleIce Accretion2025RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2025 | 15.4056 | 18.4365 | 22.2787 | 25.2329 | 28.1543
| MarkdaleIce Accretion2030RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2030 | 15.426 | 18.4852 | 22.3593 | 25.3323 | 28.2836
| MarkdaleIce Accretion2035RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2035 | 15.4464 | 18.5339 | 22.44 | 25.4318 | 28.413
| MarkdaleIce Accretion2040RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2040 | 15.3545 | 18.4487 | 22.3667 | 25.3655 | 28.3483
| MarkdaleIce Accretion2045RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2045 | 15.2627 | 18.3635 | 22.2933 | 25.2992 | 28.2836
| MarkdaleIce Accretion2050RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2050 | 15.0586 | 18.1991 | 22.176 | 25.208 | 28.219
| MarkdaleIce Accretion2055RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2055 | 14.9463 | 18.12 | 22.132 | 25.1832 | 28.219
| MarkdaleIce Accretion2060RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2060 | 14.5738 | 17.767 | 21.7873 | 24.8434 | 27.8863
| MarkdaleIce Accretion2065RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2065 | 14.3136 | 17.4931 | 21.4867 | 24.5285 | 27.5537
| MarkdaleIce Accretion2070RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2070 | 13.6655 | 16.787 | 20.702 | 23.6916 | 26.6574
| MarkdaleIce Accretion2075RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2075 | 13.2777 | 16.3549 | 20.218 | 23.1695 | 26.0938
| MarkdaleIce Accretion2080RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2080 | 12.8899 | 15.9227 | 19.734 | 22.6475 | 25.5301
| MarkdaleIce Accretion2085RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2085 | 12.2316 | 15.1649 | 18.843 | 21.6406 | 24.4213
| MarkdaleIce Accretion2090RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2090 | 11.5733 | 14.4071 | 17.952 | 20.6338 | 23.3125
| MarkdaleIce Accretion2095RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2095 | 11.5733 | 14.4071 | 17.952 | 20.6338 | 23.3125
| MarkdaleIce Accretion2100RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2100 | 11.5733 | 14.4071 | 17.952 | 20.6338 | 23.3125
| MarkdaleWind2023RCP4.5 | Markdale | Wind | RCP4.5 | 2023 | 82.8943 | 89.1818 | 95.7696 | 102.3913 | 109.0022
| MarkdaleWind2025RCP4.5 | Markdale | Wind | RCP4.5 | 2025 | 82.9703 | 89.2755 | 95.888 | 102.5283 | 109.1609
| MarkdaleWind2030RCP4.5 | Markdale | Wind | RCP4.5 | 2030 | 83.0463 | 89.3693 | 96.0064 | 102.6652 | 109.3196
| MarkdaleWind2035RCP4.5 | Markdale | Wind | RCP4.5 | 2035 | 83.1223 | 89.463 | 96.1248 | 102.8022 | 109.4783
| MarkdaleWind2040RCP4.5 | Markdale | Wind | RCP4.5 | 2040 | 83.1983 | 89.5568 | 96.2432 | 102.9391 | 109.637
| MarkdaleWind2045RCP4.5 | Markdale | Wind | RCP4.5 | 2045 | 83.2742 | 89.6505 | 96.3616 | 103.0761 | 109.7957
| MarkdaleWind2050RCP4.5 | Markdale | Wind | RCP4.5 | 2050 | 83.3469 | 89.7353 | 96.4608 | 103.1884 | 109.9215
| MarkdaleWind2055RCP4.5 | Markdale | Wind | RCP4.5 | 2055 | 83.3436 | 89.7264 | 96.4416 | 103.1638 | 109.8887
| MarkdaleWind2060RCP4.5 | Markdale | Wind | RCP4.5 | 2060 | 83.3403 | 89.7175 | 96.4224 | 103.1391 | 109.8559
| MarkdaleWind2065RCP4.5 | Markdale | Wind | RCP4.5 | 2065 | 83.337 | 89.7085 | 96.4032 | 103.1144 | 109.823
| MarkdaleWind2070RCP4.5 | Markdale | Wind | RCP4.5 | 2070 | 83.3337 | 89.6996 | 96.384 | 103.0898 | 109.7902
| MarkdaleWind2075RCP4.5 | Markdale | Wind | RCP4.5 | 2075 | 83.3516 | 89.719 | 96.4048 | 103.112 | 109.8139
| MarkdaleWind2080RCP4.5 | Markdale | Wind | RCP4.5 | 2080 | 83.3696 | 89.7383 | 96.4256 | 103.1343 | 109.8376
| MarkdaleWind2085RCP4.5 | Markdale | Wind | RCP4.5 | 2085 | 83.3875 | 89.7576 | 96.4464 | 103.1566 | 109.8613
| MarkdaleWind2090RCP4.5 | Markdale | Wind | RCP4.5 | 2090 | 83.4055 | 89.777 | 96.4672 | 103.1788 | 109.8851
| MarkdaleWind2095RCP4.5 | Markdale | Wind | RCP4.5 | 2095 | 83.4235 | 89.7963 | 96.488 | 103.2011 | 109.9088
| MarkdaleWind2100RCP4.5 | Markdale | Wind | RCP4.5 | 2100 | 83.4414 | 89.8157 | 96.5088 | 103.2233 | 109.9325
| MarkdaleWind2023RCP6.0 | Markdale | Wind | RCP6.0 | 2023 | 82.8943 | 89.1818 | 95.7696 | 102.3913 | 109.0022
| MarkdaleWind2025RCP6.0 | Markdale | Wind | RCP6.0 | 2025 | 82.9703 | 89.2755 | 95.888 | 102.5283 | 109.1609
| MarkdaleWind2030RCP6.0 | Markdale | Wind | RCP6.0 | 2030 | 83.0463 | 89.3693 | 96.0064 | 102.6652 | 109.3196
| MarkdaleWind2035RCP6.0 | Markdale | Wind | RCP6.0 | 2035 | 83.1223 | 89.463 | 96.1248 | 102.8022 | 109.4783
| MarkdaleWind2040RCP6.0 | Markdale | Wind | RCP6.0 | 2040 | 83.1983 | 89.5568 | 96.2432 | 102.9391 | 109.637
| MarkdaleWind2045RCP6.0 | Markdale | Wind | RCP6.0 | 2045 | 83.2742 | 89.6505 | 96.3616 | 103.0761 | 109.7957
| MarkdaleWind2050RCP6.0 | Markdale | Wind | RCP6.0 | 2050 | 83.3469 | 89.7353 | 96.4608 | 103.1884 | 109.9215
| MarkdaleWind2055RCP6.0 | Markdale | Wind | RCP6.0 | 2055 | 83.3436 | 89.7264 | 96.4416 | 103.1638 | 109.8887
| MarkdaleWind2060RCP6.0 | Markdale | Wind | RCP6.0 | 2060 | 83.3403 | 89.7175 | 96.4224 | 103.1391 | 109.8559
| MarkdaleWind2065RCP6.0 | Markdale | Wind | RCP6.0 | 2065 | 83.337 | 89.7085 | 96.4032 | 103.1144 | 109.823
| MarkdaleWind2070RCP6.0 | Markdale | Wind | RCP6.0 | 2070 | 83.3337 | 89.6996 | 96.384 | 103.0898 | 109.7902
| MarkdaleWind2075RCP6.0 | Markdale | Wind | RCP6.0 | 2075 | 83.3606 | 89.7286 | 96.4152 | 103.1232 | 109.8258
| MarkdaleWind2080RCP6.0 | Markdale | Wind | RCP6.0 | 2080 | 83.3875 | 89.7576 | 96.4464 | 103.1566 | 109.8613
| MarkdaleWind2085RCP6.0 | Markdale | Wind | RCP6.0 | 2085 | 83.4145 | 89.7867 | 96.4776 | 103.1899 | 109.8969
| MarkdaleWind2090RCP6.0 | Markdale | Wind | RCP6.0 | 2090 | 83.574 | 89.9764 | 96.704 | 103.4459 | 110.1805
| MarkdaleWind2095RCP6.0 | Markdale | Wind | RCP6.0 | 2095 | 83.7067 | 90.1371 | 96.8992 | 103.6684 | 110.4286
| MarkdaleWind2100RCP6.0 | Markdale | Wind | RCP6.0 | 2100 | 83.8393 | 90.2978 | 97.0944 | 103.891 | 110.6767
| MarkdaleWind2023RCP8.5 | Markdale | Wind | RCP8.5 | 2023 | 82.8943 | 89.1818 | 95.7696 | 102.3913 | 109.0022
| MarkdaleWind2025RCP8.5 | Markdale | Wind | RCP8.5 | 2025 | 83.0463 | 89.3693 | 96.0064 | 102.6652 | 109.3196
| MarkdaleWind2030RCP8.5 | Markdale | Wind | RCP8.5 | 2030 | 83.1983 | 89.5568 | 96.2432 | 102.9391 | 109.637
| MarkdaleWind2035RCP8.5 | Markdale | Wind | RCP8.5 | 2035 | 83.3502 | 89.7443 | 96.48 | 103.2131 | 109.9544
| MarkdaleWind2040RCP8.5 | Markdale | Wind | RCP8.5 | 2040 | 83.3447 | 89.7294 | 96.448 | 103.172 | 109.8996
| MarkdaleWind2045RCP8.5 | Markdale | Wind | RCP8.5 | 2045 | 83.3392 | 89.7145 | 96.416 | 103.1309 | 109.8449
| MarkdaleWind2050RCP8.5 | Markdale | Wind | RCP8.5 | 2050 | 83.3696 | 89.7383 | 96.4256 | 103.1343 | 109.8376
| MarkdaleWind2055RCP8.5 | Markdale | Wind | RCP8.5 | 2055 | 83.4055 | 89.777 | 96.4672 | 103.1788 | 109.8851
| MarkdaleWind2060RCP8.5 | Markdale | Wind | RCP8.5 | 2060 | 83.574 | 89.9764 | 96.704 | 103.4459 | 110.1805
| MarkdaleWind2065RCP8.5 | Markdale | Wind | RCP8.5 | 2065 | 83.7067 | 90.1371 | 96.8992 | 103.6684 | 110.4286
| MarkdaleWind2070RCP8.5 | Markdale | Wind | RCP8.5 | 2070 | 83.9084 | 90.3811 | 97.1904 | 104.0006 | 110.8044
| MarkdaleWind2075RCP8.5 | Markdale | Wind | RCP8.5 | 2075 | 83.9775 | 90.4644 | 97.2864 | 104.1101 | 110.932
| MarkdaleWind2080RCP8.5 | Markdale | Wind | RCP8.5 | 2080 | 84.0465 | 90.5478 | 97.3824 | 104.2197 | 111.0597
| MarkdaleWind2085RCP8.5 | Markdale | Wind | RCP8.5 | 2085 | 84.3657 | 90.9763 | 97.9536 | 104.9079 | 111.8641
| MarkdaleWind2090RCP8.5 | Markdale | Wind | RCP8.5 | 2090 | 84.6848 | 91.4049 | 98.5248 | 105.5962 | 112.6685
| MarkdaleWind2095RCP8.5 | Markdale | Wind | RCP8.5 | 2095 | 84.6848 | 91.4049 | 98.5248 | 105.5962 | 112.6685
| MarkdaleWind2100RCP8.5 | Markdale | Wind | RCP8.5 | 2100 | 84.6848 | 91.4049 | 98.5248 | 105.5962 | 112.6685
| MarkhamIce Accretion2023RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| MarkhamIce Accretion2025RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| MarkhamIce Accretion2030RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| MarkhamIce Accretion2035RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| MarkhamIce Accretion2040RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| MarkhamIce Accretion2045RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| MarkhamIce Accretion2050RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| MarkhamIce Accretion2055RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| MarkhamIce Accretion2060RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| MarkhamIce Accretion2065RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| MarkhamIce Accretion2070RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| MarkhamIce Accretion2075RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
| MarkhamIce Accretion2080RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| MarkhamIce Accretion2085RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| MarkhamIce Accretion2090RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| MarkhamIce Accretion2095RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
| MarkhamIce Accretion2100RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
| MarkhamIce Accretion2023RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| MarkhamIce Accretion2025RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| MarkhamIce Accretion2030RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| MarkhamIce Accretion2035RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| MarkhamIce Accretion2040RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| MarkhamIce Accretion2045RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| MarkhamIce Accretion2050RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| MarkhamIce Accretion2055RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| MarkhamIce Accretion2060RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| MarkhamIce Accretion2065RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| MarkhamIce Accretion2070RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| MarkhamIce Accretion2075RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
| MarkhamIce Accretion2080RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| MarkhamIce Accretion2085RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
| MarkhamIce Accretion2090RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| MarkhamIce Accretion2095RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| MarkhamIce Accretion2100RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
| MarkhamIce Accretion2023RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| MarkhamIce Accretion2025RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| MarkhamIce Accretion2030RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| MarkhamIce Accretion2035RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
| MarkhamIce Accretion2040RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
| MarkhamIce Accretion2045RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
| MarkhamIce Accretion2050RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| MarkhamIce Accretion2055RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| MarkhamIce Accretion2060RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| MarkhamIce Accretion2065RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| MarkhamIce Accretion2070RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
| MarkhamIce Accretion2075RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
| MarkhamIce Accretion2080RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
| MarkhamIce Accretion2085RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
| MarkhamIce Accretion2090RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| MarkhamIce Accretion2095RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| MarkhamIce Accretion2100RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| MarkhamWind2023RCP4.5 | Markham | Wind | RCP4.5 | 2023 | 82.2277 | 88.5267 | 95.152 | 101.7821 | 108.4083
| MarkhamWind2025RCP4.5 | Markham | Wind | RCP4.5 | 2025 | 82.2427 | 88.5591 | 95.2043 | 101.8516 | 108.4949
| MarkhamWind2030RCP4.5 | Markham | Wind | RCP4.5 | 2030 | 82.2578 | 88.5915 | 95.2565 | 101.9211 | 108.5816
| MarkhamWind2035RCP4.5 | Markham | Wind | RCP4.5 | 2035 | 82.2728 | 88.6239 | 95.3088 | 101.9905 | 108.6682
| MarkhamWind2040RCP4.5 | Markham | Wind | RCP4.5 | 2040 | 82.2879 | 88.6563 | 95.361 | 102.06 | 108.7549
| MarkhamWind2045RCP4.5 | Markham | Wind | RCP4.5 | 2045 | 82.3029 | 88.6887 | 95.4132 | 102.1294 | 108.8415
| MarkhamWind2050RCP4.5 | Markham | Wind | RCP4.5 | 2050 | 82.3983 | 88.8218 | 95.5928 | 102.3473 | 109.1014
| MarkhamWind2055RCP4.5 | Markham | Wind | RCP4.5 | 2055 | 82.4787 | 88.9225 | 95.7201 | 102.4957 | 109.2747
| MarkhamWind2060RCP4.5 | Markham | Wind | RCP4.5 | 2060 | 82.5591 | 89.0232 | 95.8474 | 102.6441 | 109.448
| MarkhamWind2065RCP4.5 | Markham | Wind | RCP4.5 | 2065 | 82.6395 | 89.1239 | 95.9747 | 102.7925 | 109.6213
| MarkhamWind2070RCP4.5 | Markham | Wind | RCP4.5 | 2070 | 82.7199 | 89.2247 | 96.102 | 102.941 | 109.7945
| MarkhamWind2075RCP4.5 | Markham | Wind | RCP4.5 | 2075 | 82.8593 | 89.4043 | 96.3316 | 103.2137 | 110.1104
| MarkhamWind2080RCP4.5 | Markham | Wind | RCP4.5 | 2080 | 82.9988 | 89.584 | 96.5612 | 103.4865 | 110.4263
| MarkhamWind2085RCP4.5 | Markham | Wind | RCP4.5 | 2085 | 83.1382 | 89.7636 | 96.7908 | 103.7592 | 110.7422
| MarkhamWind2090RCP4.5 | Markham | Wind | RCP4.5 | 2090 | 83.2777 | 89.9432 | 97.0203 | 104.032 | 111.058
| MarkhamWind2095RCP4.5 | Markham | Wind | RCP4.5 | 2095 | 83.4172 | 90.1229 | 97.2499 | 104.3048 | 111.3739
| MarkhamWind2100RCP4.5 | Markham | Wind | RCP4.5 | 2100 | 83.5566 | 90.3025 | 97.4795 | 104.5775 | 111.6898
| MarkhamWind2023RCP6.0 | Markham | Wind | RCP6.0 | 2023 | 82.2277 | 88.5267 | 95.152 | 101.7821 | 108.4083
| MarkhamWind2025RCP6.0 | Markham | Wind | RCP6.0 | 2025 | 82.2427 | 88.5591 | 95.2043 | 101.8516 | 108.4949
| MarkhamWind2030RCP6.0 | Markham | Wind | RCP6.0 | 2030 | 82.2578 | 88.5915 | 95.2565 | 101.9211 | 108.5816
| MarkhamWind2035RCP6.0 | Markham | Wind | RCP6.0 | 2035 | 82.2728 | 88.6239 | 95.3088 | 101.9905 | 108.6682
| MarkhamWind2040RCP6.0 | Markham | Wind | RCP6.0 | 2040 | 82.2879 | 88.6563 | 95.361 | 102.06 | 108.7549
| MarkhamWind2045RCP6.0 | Markham | Wind | RCP6.0 | 2045 | 82.3029 | 88.6887 | 95.4132 | 102.1294 | 108.8415
| MarkhamWind2050RCP6.0 | Markham | Wind | RCP6.0 | 2050 | 82.3983 | 88.8218 | 95.5928 | 102.3473 | 109.1014
| MarkhamWind2055RCP6.0 | Markham | Wind | RCP6.0 | 2055 | 82.4787 | 88.9225 | 95.7201 | 102.4957 | 109.2747
| MarkhamWind2060RCP6.0 | Markham | Wind | RCP6.0 | 2060 | 82.5591 | 89.0232 | 95.8474 | 102.6441 | 109.448
| MarkhamWind2065RCP6.0 | Markham | Wind | RCP6.0 | 2065 | 82.6395 | 89.1239 | 95.9747 | 102.7925 | 109.6213
| MarkhamWind2070RCP6.0 | Markham | Wind | RCP6.0 | 2070 | 82.7199 | 89.2247 | 96.102 | 102.941 | 109.7945
| MarkhamWind2075RCP6.0 | Markham | Wind | RCP6.0 | 2075 | 82.9291 | 89.4941 | 96.4464 | 103.3501 | 110.2684
| MarkhamWind2080RCP6.0 | Markham | Wind | RCP6.0 | 2080 | 83.1382 | 89.7636 | 96.7908 | 103.7592 | 110.7422
| MarkhamWind2085RCP6.0 | Markham | Wind | RCP6.0 | 2085 | 83.3474 | 90.0331 | 97.1351 | 104.1684 | 111.216
| MarkhamWind2090RCP6.0 | Markham | Wind | RCP6.0 | 2090 | 83.9886 | 90.8326 | 98.135 | 105.3399 | 112.5634
| MarkhamWind2095RCP6.0 | Markham | Wind | RCP6.0 | 2095 | 84.4207 | 91.3627 | 98.7905 | 106.1023 | 113.437
| MarkhamWind2100RCP6.0 | Markham | Wind | RCP6.0 | 2100 | 84.8527 | 91.8928 | 99.446 | 106.8646 | 114.3107
| MarkhamWind2023RCP8.5 | Markham | Wind | RCP8.5 | 2023 | 82.2277 | 88.5267 | 95.152 | 101.7821 | 108.4083
| MarkhamWind2025RCP8.5 | Markham | Wind | RCP8.5 | 2025 | 82.2578 | 88.5915 | 95.2565 | 101.9211 | 108.5816
| MarkhamWind2030RCP8.5 | Markham | Wind | RCP8.5 | 2030 | 82.2879 | 88.6563 | 95.361 | 102.06 | 108.7549
| MarkhamWind2035RCP8.5 | Markham | Wind | RCP8.5 | 2035 | 82.3179 | 88.7211 | 95.4655 | 102.1989 | 108.9281
| MarkhamWind2040RCP8.5 | Markham | Wind | RCP8.5 | 2040 | 82.4519 | 88.8889 | 95.6777 | 102.4463 | 109.2169
| MarkhamWind2045RCP8.5 | Markham | Wind | RCP8.5 | 2045 | 82.5859 | 89.0568 | 95.8898 | 102.6936 | 109.5057
| MarkhamWind2050RCP8.5 | Markham | Wind | RCP8.5 | 2050 | 82.9988 | 89.584 | 96.5612 | 103.4865 | 110.4263
| MarkhamWind2055RCP8.5 | Markham | Wind | RCP8.5 | 2055 | 83.2777 | 89.9432 | 97.0203 | 104.032 | 111.058
| MarkhamWind2060RCP8.5 | Markham | Wind | RCP8.5 | 2060 | 83.9886 | 90.8326 | 98.135 | 105.3399 | 112.5634
| MarkhamWind2065RCP8.5 | Markham | Wind | RCP8.5 | 2065 | 84.4207 | 91.3627 | 98.7905 | 106.1023 | 113.437
| MarkhamWind2070RCP8.5 | Markham | Wind | RCP8.5 | 2070 | 84.9812 | 92.0666 | 99.6772 | 107.1493 | 114.6428
| MarkhamWind2075RCP8.5 | Markham | Wind | RCP8.5 | 2075 | 85.1097 | 92.2403 | 99.9083 | 107.4339 | 114.9749
| MarkhamWind2080RCP8.5 | Markham | Wind | RCP8.5 | 2080 | 85.2382 | 92.4141 | 100.1395 | 107.7185 | 115.307
| MarkhamWind2085RCP8.5 | Markham | Wind | RCP8.5 | 2085 | 85.513 | 92.8028 | 100.6715 | 108.3691 | 116.0814
| MarkhamWind2090RCP8.5 | Markham | Wind | RCP8.5 | 2090 | 85.7878 | 93.1916 | 101.2035 | 109.0196 | 116.8557
| MarkhamWind2095RCP8.5 | Markham | Wind | RCP8.5 | 2095 | 85.7878 | 93.1916 | 101.2035 | 109.0196 | 116.8557
| MarkhamWind2100RCP8.5 | Markham | Wind | RCP8.5 | 2100 | 85.7878 | 93.1916 | 101.2035 | 109.0196 | 116.8557
| MartinIce Accretion2023RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2023 | 10.5421 | 12.5745 | 15.15 | 17.1195 | 19.089
| MartinIce Accretion2025RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2025 | 10.6482 | 12.7052 | 15.3125 | 17.3059 | 19.3
| MartinIce Accretion2030RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2030 | 10.7543 | 12.8359 | 15.475 | 17.4924 | 19.5111
| MartinIce Accretion2035RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2035 | 10.8604 | 12.9667 | 15.6375 | 17.6788 | 19.7221
| MartinIce Accretion2040RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2040 | 10.9665 | 13.0974 | 15.8 | 17.8653 | 19.9332
| MartinIce Accretion2045RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2045 | 11.0727 | 13.2281 | 15.9625 | 18.0517 | 20.1442
| MartinIce Accretion2050RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2050 | 11.1475 | 13.319 | 16.071 | 18.1738 | 20.2797
| MartinIce Accretion2055RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2055 | 11.1161 | 13.2792 | 16.017 | 18.1094 | 20.2041
| MartinIce Accretion2060RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2060 | 11.0848 | 13.2393 | 15.963 | 18.045 | 20.1285
| MartinIce Accretion2065RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2065 | 11.0535 | 13.1995 | 15.909 | 17.9806 | 20.0529
| MartinIce Accretion2070RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2070 | 11.0222 | 13.1596 | 15.855 | 17.9161 | 19.9773
| MartinIce Accretion2075RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2075 | 11.0553 | 13.197 | 15.9 | 17.967 | 20.034
| MartinIce Accretion2080RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2080 | 11.0883 | 13.2343 | 15.945 | 18.0178 | 20.0907
| MartinIce Accretion2085RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2085 | 11.1214 | 13.2717 | 15.99 | 18.0687 | 20.1474
| MartinIce Accretion2090RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2090 | 11.1544 | 13.309 | 16.035 | 18.1195 | 20.2041
| MartinIce Accretion2095RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2095 | 11.1875 | 13.3464 | 16.08 | 18.1704 | 20.2608
| MartinIce Accretion2100RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2100 | 11.2205 | 13.3837 | 16.125 | 18.2212 | 20.3175
| MartinIce Accretion2023RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2023 | 10.5421 | 12.5745 | 15.15 | 17.1195 | 19.089
| MartinIce Accretion2025RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2025 | 10.6482 | 12.7052 | 15.3125 | 17.3059 | 19.3
| MartinIce Accretion2030RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2030 | 10.7543 | 12.8359 | 15.475 | 17.4924 | 19.5111
| MartinIce Accretion2035RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2035 | 10.8604 | 12.9667 | 15.6375 | 17.6788 | 19.7221
| MartinIce Accretion2040RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2040 | 10.9665 | 13.0974 | 15.8 | 17.8653 | 19.9332
| MartinIce Accretion2045RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2045 | 11.0727 | 13.2281 | 15.9625 | 18.0517 | 20.1442
| MartinIce Accretion2050RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2050 | 11.1475 | 13.319 | 16.071 | 18.1738 | 20.2797
| MartinIce Accretion2055RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2055 | 11.1161 | 13.2792 | 16.017 | 18.1094 | 20.2041
| MartinIce Accretion2060RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2060 | 11.0848 | 13.2393 | 15.963 | 18.045 | 20.1285
| MartinIce Accretion2065RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2065 | 11.0535 | 13.1995 | 15.909 | 17.9806 | 20.0529
| MartinIce Accretion2070RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2070 | 11.0222 | 13.1596 | 15.855 | 17.9161 | 19.9773
| MartinIce Accretion2075RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2075 | 11.0718 | 13.2157 | 15.9225 | 17.9924 | 20.0623
| MartinIce Accretion2080RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2080 | 11.1214 | 13.2717 | 15.99 | 18.0687 | 20.1474
| MartinIce Accretion2085RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2085 | 11.1709 | 13.3277 | 16.0575 | 18.145 | 20.2325
| MartinIce Accretion2090RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2090 | 11.1475 | 13.2924 | 16.015 | 18.0969 | 20.1789
| MartinIce Accretion2095RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2095 | 11.0744 | 13.2011 | 15.905 | 17.9726 | 20.0403
| MartinIce Accretion2100RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2100 | 11.0013 | 13.1098 | 15.795 | 17.8483 | 19.9017
| MartinIce Accretion2023RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2023 | 10.5421 | 12.5745 | 15.15 | 17.1195 | 19.089
| MartinIce Accretion2025RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2025 | 10.7543 | 12.8359 | 15.475 | 17.4924 | 19.5111
| MartinIce Accretion2030RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2030 | 10.9665 | 13.0974 | 15.8 | 17.8653 | 19.9332
| MartinIce Accretion2035RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2035 | 11.1788 | 13.3588 | 16.125 | 18.2382 | 20.3553
| MartinIce Accretion2040RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2040 | 11.1266 | 13.2924 | 16.035 | 18.1308 | 20.2293
| MartinIce Accretion2045RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2045 | 11.0744 | 13.226 | 15.945 | 18.0235 | 20.1033
| MartinIce Accretion2050RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2050 | 11.0883 | 13.2343 | 15.945 | 18.0178 | 20.0907
| MartinIce Accretion2055RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2055 | 11.1544 | 13.309 | 16.035 | 18.1195 | 20.2041
| MartinIce Accretion2060RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2060 | 11.1475 | 13.2924 | 16.015 | 18.0969 | 20.1789
| MartinIce Accretion2065RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2065 | 11.0744 | 13.2011 | 15.905 | 17.9726 | 20.0403
| MartinIce Accretion2070RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2070 | 11.0083 | 13.1306 | 15.835 | 17.8992 | 19.9647
| MartinIce Accretion2075RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2075 | 11.0152 | 13.1513 | 15.875 | 17.9501 | 20.0277
| MartinIce Accretion2080RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2080 | 11.0222 | 13.1721 | 15.915 | 18.0009 | 20.0907
| MartinIce Accretion2085RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2085 | 10.7613 | 12.8795 | 15.5625 | 17.611 | 19.6654
| MartinIce Accretion2090RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2090 | 10.5003 | 12.5869 | 15.21 | 17.2212 | 19.2402
| MartinIce Accretion2095RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2095 | 10.5003 | 12.5869 | 15.21 | 17.2212 | 19.2402
| MartinIce Accretion2100RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2100 | 10.5003 | 12.5869 | 15.21 | 17.2212 | 19.2402
| MartinWind2023RCP4.5 | Martin | Wind | RCP4.5 | 2023 | 72.4382 | 77.9794 | 83.7984 | 89.6373 | 95.4631
| MartinWind2025RCP4.5 | Martin | Wind | RCP4.5 | 2025 | 72.5313 | 78.0927 | 83.9356 | 89.7946 | 95.6419
| MartinWind2030RCP4.5 | Martin | Wind | RCP4.5 | 2030 | 72.6244 | 78.2059 | 84.0728 | 89.9519 | 95.8206
| MartinWind2035RCP4.5 | Martin | Wind | RCP4.5 | 2035 | 72.7175 | 78.3192 | 84.21 | 90.1092 | 95.9994
| MartinWind2040RCP4.5 | Martin | Wind | RCP4.5 | 2040 | 72.8106 | 78.4325 | 84.3472 | 90.2665 | 96.1782
| MartinWind2045RCP4.5 | Martin | Wind | RCP4.5 | 2045 | 72.9036 | 78.5458 | 84.4844 | 90.4238 | 96.3569
| MartinWind2050RCP4.5 | Martin | Wind | RCP4.5 | 2050 | 73.0591 | 78.7434 | 84.7325 | 90.7141 | 96.6927
| MartinWind2055RCP4.5 | Martin | Wind | RCP4.5 | 2055 | 73.1215 | 78.8278 | 84.8434 | 90.8471 | 96.8497
| MartinWind2060RCP4.5 | Martin | Wind | RCP4.5 | 2060 | 73.1839 | 78.9121 | 84.9542 | 90.9801 | 97.0068
| MartinWind2065RCP4.5 | Martin | Wind | RCP4.5 | 2065 | 73.2462 | 78.9965 | 85.0651 | 91.1132 | 97.1638
| MartinWind2070RCP4.5 | Martin | Wind | RCP4.5 | 2070 | 73.3086 | 79.0809 | 85.176 | 91.2462 | 97.3209
| MartinWind2075RCP4.5 | Martin | Wind | RCP4.5 | 2075 | 73.467 | 79.2788 | 85.4238 | 91.5368 | 97.6545
| MartinWind2080RCP4.5 | Martin | Wind | RCP4.5 | 2080 | 73.6253 | 79.4767 | 85.6716 | 91.8274 | 97.988
| MartinWind2085RCP4.5 | Martin | Wind | RCP4.5 | 2085 | 73.7837 | 79.6746 | 85.9194 | 92.118 | 98.3216
| MartinWind2090RCP4.5 | Martin | Wind | RCP4.5 | 2090 | 73.9421 | 79.8725 | 86.1672 | 92.4086 | 98.6551
| MartinWind2095RCP4.5 | Martin | Wind | RCP4.5 | 2095 | 74.1004 | 80.0704 | 86.415 | 92.6992 | 98.9887
| MartinWind2100RCP4.5 | Martin | Wind | RCP4.5 | 2100 | 74.2588 | 80.2683 | 86.6628 | 92.9898 | 99.3223
| MartinWind2023RCP6.0 | Martin | Wind | RCP6.0 | 2023 | 72.4382 | 77.9794 | 83.7984 | 89.6373 | 95.4631
| MartinWind2025RCP6.0 | Martin | Wind | RCP6.0 | 2025 | 72.5313 | 78.0927 | 83.9356 | 89.7946 | 95.6419
| MartinWind2030RCP6.0 | Martin | Wind | RCP6.0 | 2030 | 72.6244 | 78.2059 | 84.0728 | 89.9519 | 95.8206
| MartinWind2035RCP6.0 | Martin | Wind | RCP6.0 | 2035 | 72.7175 | 78.3192 | 84.21 | 90.1092 | 95.9994
| MartinWind2040RCP6.0 | Martin | Wind | RCP6.0 | 2040 | 72.8106 | 78.4325 | 84.3472 | 90.2665 | 96.1782
| MartinWind2045RCP6.0 | Martin | Wind | RCP6.0 | 2045 | 72.9036 | 78.5458 | 84.4844 | 90.4238 | 96.3569
| MartinWind2050RCP6.0 | Martin | Wind | RCP6.0 | 2050 | 73.0591 | 78.7434 | 84.7325 | 90.7141 | 96.6927
| MartinWind2055RCP6.0 | Martin | Wind | RCP6.0 | 2055 | 73.1215 | 78.8278 | 84.8434 | 90.8471 | 96.8497
| MartinWind2060RCP6.0 | Martin | Wind | RCP6.0 | 2060 | 73.1839 | 78.9121 | 84.9542 | 90.9801 | 97.0068
| MartinWind2065RCP6.0 | Martin | Wind | RCP6.0 | 2065 | 73.2462 | 78.9965 | 85.0651 | 91.1132 | 97.1638
| MartinWind2070RCP6.0 | Martin | Wind | RCP6.0 | 2070 | 73.3086 | 79.0809 | 85.176 | 91.2462 | 97.3209
| MartinWind2075RCP6.0 | Martin | Wind | RCP6.0 | 2075 | 73.5462 | 79.3777 | 85.5477 | 91.6821 | 97.8212
| MartinWind2080RCP6.0 | Martin | Wind | RCP6.0 | 2080 | 73.7837 | 79.6746 | 85.9194 | 92.118 | 98.3216
| MartinWind2085RCP6.0 | Martin | Wind | RCP6.0 | 2085 | 74.0213 | 79.9714 | 86.2911 | 92.5539 | 98.8219
| MartinWind2090RCP6.0 | Martin | Wind | RCP6.0 | 2090 | 74.4836 | 80.5599 | 87.038 | 93.4333 | 99.8394
| MartinWind2095RCP6.0 | Martin | Wind | RCP6.0 | 2095 | 74.7085 | 80.8516 | 87.4132 | 93.8767 | 100.3565
| MartinWind2100RCP6.0 | Martin | Wind | RCP6.0 | 2100 | 74.9334 | 81.1432 | 87.7884 | 94.3201 | 100.8736
| MartinWind2023RCP8.5 | Martin | Wind | RCP8.5 | 2023 | 72.4382 | 77.9794 | 83.7984 | 89.6373 | 95.4631
| MartinWind2025RCP8.5 | Martin | Wind | RCP8.5 | 2025 | 72.6244 | 78.2059 | 84.0728 | 89.9519 | 95.8206
| MartinWind2030RCP8.5 | Martin | Wind | RCP8.5 | 2030 | 72.8106 | 78.4325 | 84.3472 | 90.2665 | 96.1782
| MartinWind2035RCP8.5 | Martin | Wind | RCP8.5 | 2035 | 72.9967 | 78.659 | 84.6216 | 90.5811 | 96.5357
| MartinWind2040RCP8.5 | Martin | Wind | RCP8.5 | 2040 | 73.1007 | 78.7996 | 84.8064 | 90.8028 | 96.7974
| MartinWind2045RCP8.5 | Martin | Wind | RCP8.5 | 2045 | 73.2047 | 78.9403 | 84.9912 | 91.0245 | 97.0591
| MartinWind2050RCP8.5 | Martin | Wind | RCP8.5 | 2050 | 73.6253 | 79.4767 | 85.6716 | 91.8274 | 97.988
| MartinWind2055RCP8.5 | Martin | Wind | RCP8.5 | 2055 | 73.9421 | 79.8725 | 86.1672 | 92.4086 | 98.6551
| MartinWind2060RCP8.5 | Martin | Wind | RCP8.5 | 2060 | 74.4836 | 80.5599 | 87.038 | 93.4333 | 99.8394
| MartinWind2065RCP8.5 | Martin | Wind | RCP8.5 | 2065 | 74.7085 | 80.8516 | 87.4132 | 93.8767 | 100.3565
| MartinWind2070RCP8.5 | Martin | Wind | RCP8.5 | 2070 | 75.1195 | 81.3464 | 88.0152 | 94.5657 | 101.1385
| MartinWind2075RCP8.5 | Martin | Wind | RCP8.5 | 2075 | 75.3057 | 81.5495 | 88.242 | 94.8114 | 101.4035
| MartinWind2080RCP8.5 | Martin | Wind | RCP8.5 | 2080 | 75.4919 | 81.7526 | 88.4688 | 95.0571 | 101.6684
| MartinWind2085RCP8.5 | Martin | Wind | RCP8.5 | 2085 | 75.4556 | 81.6901 | 88.3722 | 94.9358 | 101.5152
| MartinWind2090RCP8.5 | Martin | Wind | RCP8.5 | 2090 | 75.4193 | 81.6276 | 88.2756 | 94.8144 | 101.362
| MartinWind2095RCP8.5 | Martin | Wind | RCP8.5 | 2095 | 75.4193 | 81.6276 | 88.2756 | 94.8144 | 101.362
| MartinWind2100RCP8.5 | Martin | Wind | RCP8.5 | 2100 | 75.4193 | 81.6276 | 88.2756 | 94.8144 | 101.362
| MathesonIce Accretion2023RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2023 | 13.2475 | 15.77 | 18.962 | 21.4056 | 23.8682
| MathesonIce Accretion2025RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2025 | 13.2563 | 15.7805 | 18.9747 | 21.4199 | 23.8841
| MathesonIce Accretion2030RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2030 | 13.2651 | 15.791 | 18.9873 | 21.4342 | 23.9001
| MathesonIce Accretion2035RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2035 | 13.274 | 15.8015 | 19 | 21.4485 | 23.9161
| MathesonIce Accretion2040RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2040 | 13.2828 | 15.8121 | 19.0127 | 21.4628 | 23.932
| MathesonIce Accretion2045RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2045 | 13.2916 | 15.8226 | 19.0253 | 21.4772 | 23.948
| MathesonIce Accretion2050RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2050 | 13.4405 | 16.0065 | 19.2584 | 21.7448 | 24.2512
| MathesonIce Accretion2055RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2055 | 13.5807 | 16.18 | 19.4788 | 21.9982 | 24.5385
| MathesonIce Accretion2060RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2060 | 13.7208 | 16.3535 | 19.6992 | 22.2515 | 24.8258
| MathesonIce Accretion2065RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2065 | 13.861 | 16.527 | 19.9196 | 22.5049 | 25.1131
| MathesonIce Accretion2070RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2070 | 14.0011 | 16.7004 | 20.14 | 22.7582 | 25.4003
| MathesonIce Accretion2075RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2075 | 14.0232 | 16.7346 | 20.1875 | 22.8155 | 25.4642
| MathesonIce Accretion2080RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2080 | 14.0452 | 16.7688 | 20.235 | 22.8727 | 25.528
| MathesonIce Accretion2085RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2085 | 14.0672 | 16.8029 | 20.2825 | 22.93 | 25.5919
| MathesonIce Accretion2090RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2090 | 14.0893 | 16.8371 | 20.33 | 22.9872 | 25.6557
| MathesonIce Accretion2095RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2095 | 14.1113 | 16.8713 | 20.3775 | 23.0445 | 25.7195
| MathesonIce Accretion2100RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2100 | 14.1333 | 16.9054 | 20.425 | 23.1017 | 25.7834
| MathesonIce Accretion2023RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2023 | 13.2475 | 15.77 | 18.962 | 21.4056 | 23.8682
| MathesonIce Accretion2025RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2025 | 13.2563 | 15.7805 | 18.9747 | 21.4199 | 23.8841
| MathesonIce Accretion2030RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2030 | 13.2651 | 15.791 | 18.9873 | 21.4342 | 23.9001
| MathesonIce Accretion2035RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2035 | 13.274 | 15.8015 | 19 | 21.4485 | 23.9161
| MathesonIce Accretion2040RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2040 | 13.2828 | 15.8121 | 19.0127 | 21.4628 | 23.932
| MathesonIce Accretion2045RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2045 | 13.2916 | 15.8226 | 19.0253 | 21.4772 | 23.948
| MathesonIce Accretion2050RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2050 | 13.4405 | 16.0065 | 19.2584 | 21.7448 | 24.2512
| MathesonIce Accretion2055RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2055 | 13.5807 | 16.18 | 19.4788 | 21.9982 | 24.5385
| MathesonIce Accretion2060RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2060 | 13.7208 | 16.3535 | 19.6992 | 22.2515 | 24.8258
| MathesonIce Accretion2065RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2065 | 13.861 | 16.527 | 19.9196 | 22.5049 | 25.1131
| MathesonIce Accretion2070RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2070 | 14.0011 | 16.7004 | 20.14 | 22.7582 | 25.4003
| MathesonIce Accretion2075RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2075 | 14.0342 | 16.7517 | 20.2112 | 22.8441 | 25.4961
| MathesonIce Accretion2080RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2080 | 14.0672 | 16.8029 | 20.2825 | 22.93 | 25.5919
| MathesonIce Accretion2085RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2085 | 14.1003 | 16.8542 | 20.3538 | 23.0158 | 25.6876
| MathesonIce Accretion2090RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2090 | 14.0452 | 16.8213 | 20.3427 | 23.023 | 25.7036
| MathesonIce Accretion2095RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2095 | 13.957 | 16.7372 | 20.2603 | 22.9443 | 25.6238
| MathesonIce Accretion2100RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2100 | 13.8689 | 16.6531 | 20.178 | 22.8655 | 25.544
| MathesonIce Accretion2023RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2023 | 13.2475 | 15.77 | 18.962 | 21.4056 | 23.8682
| MathesonIce Accretion2025RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2025 | 13.2651 | 15.791 | 18.9873 | 21.4342 | 23.9001
| MathesonIce Accretion2030RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2030 | 13.2828 | 15.8121 | 19.0127 | 21.4628 | 23.932
| MathesonIce Accretion2035RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2035 | 13.3004 | 15.8331 | 19.038 | 21.4915 | 23.9639
| MathesonIce Accretion2040RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2040 | 13.534 | 16.1222 | 19.4053 | 21.9137 | 24.4427
| MathesonIce Accretion2045RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2045 | 13.7675 | 16.4113 | 19.7727 | 22.336 | 24.9215
| MathesonIce Accretion2050RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2050 | 14.0452 | 16.7688 | 20.235 | 22.8727 | 25.528
| MathesonIce Accretion2055RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2055 | 14.0893 | 16.8371 | 20.33 | 22.9872 | 25.6557
| MathesonIce Accretion2060RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2060 | 14.0452 | 16.8213 | 20.3427 | 23.023 | 25.7036
| MathesonIce Accretion2065RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2065 | 13.957 | 16.7372 | 20.2603 | 22.9443 | 25.6238
| MathesonIce Accretion2070RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2070 | 13.7147 | 16.4849 | 19.988 | 22.6652 | 25.3285
| MathesonIce Accretion2075RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2075 | 13.5604 | 16.3167 | 19.798 | 22.4648 | 25.1131
| MathesonIce Accretion2080RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2080 | 13.4062 | 16.1485 | 19.608 | 22.2644 | 24.8976
| MathesonIce Accretion2085RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2085 | 13.1153 | 15.8252 | 19.247 | 21.8672 | 24.4667
| MathesonIce Accretion2090RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2090 | 12.8244 | 15.5019 | 18.886 | 21.47 | 24.0358
| MathesonIce Accretion2095RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2095 | 12.8244 | 15.5019 | 18.886 | 21.47 | 24.0358
| MathesonIce Accretion2100RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2100 | 12.8244 | 15.5019 | 18.886 | 21.47 | 24.0358
| MathesonWind2023RCP4.5 | Matheson | Wind | RCP4.5 | 2023 | 74.8016 | 80.5479 | 86.5848 | 92.6273 | 98.6773
| MathesonWind2025RCP4.5 | Matheson | Wind | RCP4.5 | 2025 | 74.8288 | 80.5652 | 86.5891 | 92.6212 | 98.6609
| MathesonWind2030RCP4.5 | Matheson | Wind | RCP4.5 | 2030 | 74.856 | 80.5825 | 86.5934 | 92.6151 | 98.6446
| MathesonWind2035RCP4.5 | Matheson | Wind | RCP4.5 | 2035 | 74.8833 | 80.5998 | 86.5977 | 92.6089 | 98.6282
| MathesonWind2040RCP4.5 | Matheson | Wind | RCP4.5 | 2040 | 74.9105 | 80.6172 | 86.602 | 92.6028 | 98.6119
| MathesonWind2045RCP4.5 | Matheson | Wind | RCP4.5 | 2045 | 74.9377 | 80.6345 | 86.6063 | 92.5967 | 98.5956
| MathesonWind2050RCP4.5 | Matheson | Wind | RCP4.5 | 2050 | 75.0258 | 80.727 | 86.7035 | 92.6991 | 98.7008
| MathesonWind2055RCP4.5 | Matheson | Wind | RCP4.5 | 2055 | 75.0867 | 80.8022 | 86.7964 | 92.8077 | 98.8224
| MathesonWind2060RCP4.5 | Matheson | Wind | RCP4.5 | 2060 | 75.1476 | 80.8774 | 86.8892 | 92.9163 | 98.9439
| MathesonWind2065RCP4.5 | Matheson | Wind | RCP4.5 | 2065 | 75.2085 | 80.9526 | 86.9821 | 93.0249 | 99.0655
| MathesonWind2070RCP4.5 | Matheson | Wind | RCP4.5 | 2070 | 75.2694 | 81.0277 | 87.075 | 93.1334 | 99.1871
| MathesonWind2075RCP4.5 | Matheson | Wind | RCP4.5 | 2075 | 75.3152 | 81.0757 | 87.1252 | 93.1856 | 99.2426
| MathesonWind2080RCP4.5 | Matheson | Wind | RCP4.5 | 2080 | 75.361 | 81.1237 | 87.1753 | 93.2377 | 99.2982
| MathesonWind2085RCP4.5 | Matheson | Wind | RCP4.5 | 2085 | 75.4068 | 81.1717 | 87.2255 | 93.2899 | 99.3537
| MathesonWind2090RCP4.5 | Matheson | Wind | RCP4.5 | 2090 | 75.4526 | 81.2197 | 87.2757 | 93.342 | 99.4093
| MathesonWind2095RCP4.5 | Matheson | Wind | RCP4.5 | 2095 | 75.4984 | 81.2677 | 87.3258 | 93.3942 | 99.4648
| MathesonWind2100RCP4.5 | Matheson | Wind | RCP4.5 | 2100 | 75.5442 | 81.3157 | 87.376 | 93.4463 | 99.5204
| MathesonWind2023RCP6.0 | Matheson | Wind | RCP6.0 | 2023 | 74.8016 | 80.5479 | 86.5848 | 92.6273 | 98.6773
| MathesonWind2025RCP6.0 | Matheson | Wind | RCP6.0 | 2025 | 74.8288 | 80.5652 | 86.5891 | 92.6212 | 98.6609
| MathesonWind2030RCP6.0 | Matheson | Wind | RCP6.0 | 2030 | 74.856 | 80.5825 | 86.5934 | 92.6151 | 98.6446
| MathesonWind2035RCP6.0 | Matheson | Wind | RCP6.0 | 2035 | 74.8833 | 80.5998 | 86.5977 | 92.6089 | 98.6282
| MathesonWind2040RCP6.0 | Matheson | Wind | RCP6.0 | 2040 | 74.9105 | 80.6172 | 86.602 | 92.6028 | 98.6119
| MathesonWind2045RCP6.0 | Matheson | Wind | RCP6.0 | 2045 | 74.9377 | 80.6345 | 86.6063 | 92.5967 | 98.5956
| MathesonWind2050RCP6.0 | Matheson | Wind | RCP6.0 | 2050 | 75.0258 | 80.727 | 86.7035 | 92.6991 | 98.7008
| MathesonWind2055RCP6.0 | Matheson | Wind | RCP6.0 | 2055 | 75.0867 | 80.8022 | 86.7964 | 92.8077 | 98.8224
| MathesonWind2060RCP6.0 | Matheson | Wind | RCP6.0 | 2060 | 75.1476 | 80.8774 | 86.8892 | 92.9163 | 98.9439
| MathesonWind2065RCP6.0 | Matheson | Wind | RCP6.0 | 2065 | 75.2085 | 80.9526 | 86.9821 | 93.0249 | 99.0655
| MathesonWind2070RCP6.0 | Matheson | Wind | RCP6.0 | 2070 | 75.2694 | 81.0277 | 87.075 | 93.1334 | 99.1871
| MathesonWind2075RCP6.0 | Matheson | Wind | RCP6.0 | 2075 | 75.3381 | 81.0997 | 87.1502 | 93.2117 | 99.2704
| MathesonWind2080RCP6.0 | Matheson | Wind | RCP6.0 | 2080 | 75.4068 | 81.1717 | 87.2255 | 93.2899 | 99.3537
| MathesonWind2085RCP6.0 | Matheson | Wind | RCP6.0 | 2085 | 75.4755 | 81.2437 | 87.3008 | 93.3681 | 99.4371
| MathesonWind2090RCP6.0 | Matheson | Wind | RCP6.0 | 2090 | 75.7447 | 81.5449 | 87.6397 | 93.7438 | 99.8472
| MathesonWind2095RCP6.0 | Matheson | Wind | RCP6.0 | 2095 | 75.9452 | 81.7742 | 87.9035 | 94.0414 | 100.174
| MathesonWind2100RCP6.0 | Matheson | Wind | RCP6.0 | 2100 | 76.1457 | 82.0035 | 88.1672 | 94.3389 | 100.5008
| MathesonWind2023RCP8.5 | Matheson | Wind | RCP8.5 | 2023 | 74.8016 | 80.5479 | 86.5848 | 92.6273 | 98.6773
| MathesonWind2025RCP8.5 | Matheson | Wind | RCP8.5 | 2025 | 74.856 | 80.5825 | 86.5934 | 92.6151 | 98.6446
| MathesonWind2030RCP8.5 | Matheson | Wind | RCP8.5 | 2030 | 74.9105 | 80.6172 | 86.602 | 92.6028 | 98.6119
| MathesonWind2035RCP8.5 | Matheson | Wind | RCP8.5 | 2035 | 74.965 | 80.6518 | 86.6106 | 92.5905 | 98.5792
| MathesonWind2040RCP8.5 | Matheson | Wind | RCP8.5 | 2040 | 75.0664 | 80.7771 | 86.7654 | 92.7715 | 98.7818
| MathesonWind2045RCP8.5 | Matheson | Wind | RCP8.5 | 2045 | 75.1679 | 80.9024 | 86.9202 | 92.9525 | 98.9845
| MathesonWind2050RCP8.5 | Matheson | Wind | RCP8.5 | 2050 | 75.361 | 81.1237 | 87.1753 | 93.2377 | 99.2982
| MathesonWind2055RCP8.5 | Matheson | Wind | RCP8.5 | 2055 | 75.4526 | 81.2197 | 87.2757 | 93.342 | 99.4093
| MathesonWind2060RCP8.5 | Matheson | Wind | RCP8.5 | 2060 | 75.7447 | 81.5449 | 87.6397 | 93.7438 | 99.8472
| MathesonWind2065RCP8.5 | Matheson | Wind | RCP8.5 | 2065 | 75.9452 | 81.7742 | 87.9035 | 94.0414 | 100.174
| MathesonWind2070RCP8.5 | Matheson | Wind | RCP8.5 | 2070 | 76.2521 | 82.1101 | 88.2704 | 94.4371 | 100.5988
| MathesonWind2075RCP8.5 | Matheson | Wind | RCP8.5 | 2075 | 76.3586 | 82.2168 | 88.3736 | 94.5352 | 100.6969
| MathesonWind2080RCP8.5 | Matheson | Wind | RCP8.5 | 2080 | 76.465 | 82.3234 | 88.4768 | 94.6334 | 100.7949
| MathesonWind2085RCP8.5 | Matheson | Wind | RCP8.5 | 2085 | 76.5504 | 82.4274 | 88.6015 | 94.776 | 100.9567
| MathesonWind2090RCP8.5 | Matheson | Wind | RCP8.5 | 2090 | 76.6358 | 82.5314 | 88.7262 | 94.9186 | 101.1185
| MathesonWind2095RCP8.5 | Matheson | Wind | RCP8.5 | 2095 | 76.6358 | 82.5314 | 88.7262 | 94.9186 | 101.1185
| MathesonWind2100RCP8.5 | Matheson | Wind | RCP8.5 | 2100 | 76.6358 | 82.5314 | 88.7262 | 94.9186 | 101.1185
| MattawaIce Accretion2023RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2023 | 15.4165 | 18.4409 | 22.26 | 25.2013 | 28.127
| MattawaIce Accretion2025RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2025 | 15.509 | 18.56 | 22.414 | 25.3792 | 28.3298
| MattawaIce Accretion2030RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2030 | 15.6016 | 18.6791 | 22.568 | 25.5572 | 28.5327
| MattawaIce Accretion2035RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2035 | 15.6941 | 18.7983 | 22.722 | 25.7352 | 28.7356
| MattawaIce Accretion2040RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2040 | 15.7867 | 18.9174 | 22.876 | 25.9132 | 28.9384
| MattawaIce Accretion2045RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2045 | 15.8792 | 19.0365 | 23.03 | 26.0911 | 29.1413
| MattawaIce Accretion2050RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2050 | 16.0565 | 19.2741 | 23.3436 | 26.4589 | 29.5611
| MattawaIce Accretion2055RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2055 | 16.1413 | 19.3926 | 23.5032 | 26.6488 | 29.7781
| MattawaIce Accretion2060RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2060 | 16.226 | 19.5111 | 23.6628 | 26.8386 | 29.9951
| MattawaIce Accretion2065RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2065 | 16.3108 | 19.6297 | 23.8224 | 27.0285 | 30.212
| MattawaIce Accretion2070RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2070 | 16.3955 | 19.7482 | 23.982 | 27.2183 | 30.429
| MattawaIce Accretion2075RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2075 | 16.3712 | 19.7249 | 23.9645 | 27.2025 | 30.4202
| MattawaIce Accretion2080RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2080 | 16.3468 | 19.7017 | 23.947 | 27.1867 | 30.4114
| MattawaIce Accretion2085RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2085 | 16.3225 | 19.6785 | 23.9295 | 27.1708 | 30.4025
| MattawaIce Accretion2090RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2090 | 16.2981 | 19.6552 | 23.912 | 27.155 | 30.3937
| MattawaIce Accretion2095RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2095 | 16.2738 | 19.632 | 23.8945 | 27.1392 | 30.3849
| MattawaIce Accretion2100RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2100 | 16.2494 | 19.6088 | 23.877 | 27.1234 | 30.3761
| MattawaIce Accretion2023RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2023 | 15.4165 | 18.4409 | 22.26 | 25.2013 | 28.127
| MattawaIce Accretion2025RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2025 | 15.509 | 18.56 | 22.414 | 25.3792 | 28.3298
| MattawaIce Accretion2030RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2030 | 15.6016 | 18.6791 | 22.568 | 25.5572 | 28.5327
| MattawaIce Accretion2035RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2035 | 15.6941 | 18.7983 | 22.722 | 25.7352 | 28.7356
| MattawaIce Accretion2040RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2040 | 15.7867 | 18.9174 | 22.876 | 25.9132 | 28.9384
| MattawaIce Accretion2045RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2045 | 15.8792 | 19.0365 | 23.03 | 26.0911 | 29.1413
| MattawaIce Accretion2050RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2050 | 16.0565 | 19.2741 | 23.3436 | 26.4589 | 29.5611
| MattawaIce Accretion2055RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2055 | 16.1413 | 19.3926 | 23.5032 | 26.6488 | 29.7781
| MattawaIce Accretion2060RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2060 | 16.226 | 19.5111 | 23.6628 | 26.8386 | 29.9951
| MattawaIce Accretion2065RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2065 | 16.3108 | 19.6297 | 23.8224 | 27.0285 | 30.212
| MattawaIce Accretion2070RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2070 | 16.3955 | 19.7482 | 23.982 | 27.2183 | 30.429
| MattawaIce Accretion2075RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2075 | 16.359 | 19.7133 | 23.9557 | 27.1946 | 30.4158
| MattawaIce Accretion2080RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2080 | 16.3225 | 19.6785 | 23.9295 | 27.1708 | 30.4025
| MattawaIce Accretion2085RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2085 | 16.2859 | 19.6436 | 23.9032 | 27.1471 | 30.3893
| MattawaIce Accretion2090RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2090 | 16.2348 | 19.6146 | 23.898 | 27.1629 | 30.429
| MattawaIce Accretion2095RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2095 | 16.2202 | 19.6204 | 23.919 | 27.2025 | 30.4819
| MattawaIce Accretion2100RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2100 | 16.2056 | 19.6262 | 23.94 | 27.242 | 30.5348
| MattawaIce Accretion2023RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2023 | 15.4165 | 18.4409 | 22.26 | 25.2013 | 28.127
| MattawaIce Accretion2025RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2025 | 15.6016 | 18.6791 | 22.568 | 25.5572 | 28.5327
| MattawaIce Accretion2030RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2030 | 15.7867 | 18.9174 | 22.876 | 25.9132 | 28.9384
| MattawaIce Accretion2035RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2035 | 15.9718 | 19.1556 | 23.184 | 26.2691 | 29.3441
| MattawaIce Accretion2040RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2040 | 16.113 | 19.3531 | 23.45 | 26.5855 | 29.7058
| MattawaIce Accretion2045RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2045 | 16.2543 | 19.5507 | 23.716 | 26.9019 | 30.0674
| MattawaIce Accretion2050RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2050 | 16.3468 | 19.7017 | 23.947 | 27.1867 | 30.4114
| MattawaIce Accretion2055RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2055 | 16.2981 | 19.6552 | 23.912 | 27.155 | 30.3937
| MattawaIce Accretion2060RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2060 | 16.2348 | 19.6146 | 23.898 | 27.1629 | 30.429
| MattawaIce Accretion2065RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2065 | 16.2202 | 19.6204 | 23.919 | 27.2025 | 30.4819
| MattawaIce Accretion2070RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2070 | 15.9328 | 19.3008 | 23.555 | 26.8149 | 30.0586
| MattawaIce Accretion2075RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2075 | 15.66 | 18.9755 | 23.17 | 26.3878 | 29.5823
| MattawaIce Accretion2080RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2080 | 15.3872 | 18.6501 | 22.785 | 25.9606 | 29.106
| MattawaIce Accretion2085RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2085 | 15.2192 | 18.4932 | 22.638 | 25.8064 | 28.9605
| MattawaIce Accretion2090RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2090 | 15.0512 | 18.3364 | 22.491 | 25.6521 | 28.8149
| MattawaIce Accretion2095RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2095 | 15.0512 | 18.3364 | 22.491 | 25.6521 | 28.8149
| MattawaIce Accretion2100RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2100 | 15.0512 | 18.3364 | 22.491 | 25.6521 | 28.8149
| MattawaWind2023RCP4.5 | Mattawa | Wind | RCP4.5 | 2023 | 75.1729 | 81.0037 | 87.161 | 93.2991 | 99.442
| MattawaWind2025RCP4.5 | Mattawa | Wind | RCP4.5 | 2025 | 75.2088 | 81.0437 | 87.2011 | 93.342 | 99.4877
| MattawaWind2030RCP4.5 | Mattawa | Wind | RCP4.5 | 2030 | 75.2447 | 81.0837 | 87.2413 | 93.385 | 99.5335
| MattawaWind2035RCP4.5 | Mattawa | Wind | RCP4.5 | 2035 | 75.2806 | 81.1237 | 87.2814 | 93.4279 | 99.5792
| MattawaWind2040RCP4.5 | Mattawa | Wind | RCP4.5 | 2040 | 75.3164 | 81.1637 | 87.3215 | 93.4708 | 99.625
| MattawaWind2045RCP4.5 | Mattawa | Wind | RCP4.5 | 2045 | 75.3523 | 81.2037 | 87.3617 | 93.5138 | 99.6707
| MattawaWind2050RCP4.5 | Mattawa | Wind | RCP4.5 | 2050 | 75.3422 | 81.1813 | 87.321 | 93.461 | 99.6028
| MattawaWind2055RCP4.5 | Mattawa | Wind | RCP4.5 | 2055 | 75.2962 | 81.1189 | 87.2401 | 93.3653 | 99.489
| MattawaWind2060RCP4.5 | Mattawa | Wind | RCP4.5 | 2060 | 75.2501 | 81.0565 | 87.1593 | 93.2696 | 99.3753
| MattawaWind2065RCP4.5 | Mattawa | Wind | RCP4.5 | 2065 | 75.2041 | 80.9941 | 87.0784 | 93.1739 | 99.2616
| MattawaWind2070RCP4.5 | Mattawa | Wind | RCP4.5 | 2070 | 75.158 | 80.9318 | 86.9976 | 93.0782 | 99.1479
| MattawaWind2075RCP4.5 | Mattawa | Wind | RCP4.5 | 2075 | 75.2385 | 81.0304 | 87.118 | 93.2163 | 99.3047
| MattawaWind2080RCP4.5 | Mattawa | Wind | RCP4.5 | 2080 | 75.3189 | 81.129 | 87.2384 | 93.3543 | 99.4616
| MattawaWind2085RCP4.5 | Mattawa | Wind | RCP4.5 | 2085 | 75.3994 | 81.2277 | 87.3588 | 93.4923 | 99.6184
| MattawaWind2090RCP4.5 | Mattawa | Wind | RCP4.5 | 2090 | 75.4798 | 81.3263 | 87.4792 | 93.6304 | 99.7753
| MattawaWind2095RCP4.5 | Mattawa | Wind | RCP4.5 | 2095 | 75.5603 | 81.425 | 87.5996 | 93.7684 | 99.9322
| MattawaWind2100RCP4.5 | Mattawa | Wind | RCP4.5 | 2100 | 75.6407 | 81.5236 | 87.72 | 93.9064 | 100.089
| MattawaWind2023RCP6.0 | Mattawa | Wind | RCP6.0 | 2023 | 75.1729 | 81.0037 | 87.161 | 93.2991 | 99.442
| MattawaWind2025RCP6.0 | Mattawa | Wind | RCP6.0 | 2025 | 75.2088 | 81.0437 | 87.2011 | 93.342 | 99.4877
| MattawaWind2030RCP6.0 | Mattawa | Wind | RCP6.0 | 2030 | 75.2447 | 81.0837 | 87.2413 | 93.385 | 99.5335
| MattawaWind2035RCP6.0 | Mattawa | Wind | RCP6.0 | 2035 | 75.2806 | 81.1237 | 87.2814 | 93.4279 | 99.5792
| MattawaWind2040RCP6.0 | Mattawa | Wind | RCP6.0 | 2040 | 75.3164 | 81.1637 | 87.3215 | 93.4708 | 99.625
| MattawaWind2045RCP6.0 | Mattawa | Wind | RCP6.0 | 2045 | 75.3523 | 81.2037 | 87.3617 | 93.5138 | 99.6707
| MattawaWind2050RCP6.0 | Mattawa | Wind | RCP6.0 | 2050 | 75.3422 | 81.1813 | 87.321 | 93.461 | 99.6028
| MattawaWind2055RCP6.0 | Mattawa | Wind | RCP6.0 | 2055 | 75.2962 | 81.1189 | 87.2401 | 93.3653 | 99.489
| MattawaWind2060RCP6.0 | Mattawa | Wind | RCP6.0 | 2060 | 75.2501 | 81.0565 | 87.1593 | 93.2696 | 99.3753
| MattawaWind2065RCP6.0 | Mattawa | Wind | RCP6.0 | 2065 | 75.2041 | 80.9941 | 87.0784 | 93.1739 | 99.2616
| MattawaWind2070RCP6.0 | Mattawa | Wind | RCP6.0 | 2070 | 75.158 | 80.9318 | 86.9976 | 93.0782 | 99.1479
| MattawaWind2075RCP6.0 | Mattawa | Wind | RCP6.0 | 2075 | 75.2787 | 81.0797 | 87.1782 | 93.2853 | 99.3831
| MattawaWind2080RCP6.0 | Mattawa | Wind | RCP6.0 | 2080 | 75.3994 | 81.2277 | 87.3588 | 93.4923 | 99.6184
| MattawaWind2085RCP6.0 | Mattawa | Wind | RCP6.0 | 2085 | 75.52 | 81.3757 | 87.5394 | 93.6994 | 99.8537
| MattawaWind2090RCP6.0 | Mattawa | Wind | RCP6.0 | 2090 | 75.6135 | 81.4943 | 87.6913 | 93.8788 | 100.0629
| MattawaWind2095RCP6.0 | Mattawa | Wind | RCP6.0 | 2095 | 75.5863 | 81.465 | 87.6627 | 93.8512 | 100.0367
| MattawaWind2100RCP6.0 | Mattawa | Wind | RCP6.0 | 2100 | 75.559 | 81.4356 | 87.634 | 93.8236 | 100.0106
| MattawaWind2023RCP8.5 | Mattawa | Wind | RCP8.5 | 2023 | 75.1729 | 81.0037 | 87.161 | 93.2991 | 99.442
| MattawaWind2025RCP8.5 | Mattawa | Wind | RCP8.5 | 2025 | 75.2447 | 81.0837 | 87.2413 | 93.385 | 99.5335
| MattawaWind2030RCP8.5 | Mattawa | Wind | RCP8.5 | 2030 | 75.3164 | 81.1637 | 87.3215 | 93.4708 | 99.625
| MattawaWind2035RCP8.5 | Mattawa | Wind | RCP8.5 | 2035 | 75.3882 | 81.2437 | 87.4018 | 93.5567 | 99.7165
| MattawaWind2040RCP8.5 | Mattawa | Wind | RCP8.5 | 2040 | 75.3115 | 81.1397 | 87.2671 | 93.3972 | 99.5269
| MattawaWind2045RCP8.5 | Mattawa | Wind | RCP8.5 | 2045 | 75.2348 | 81.0357 | 87.1323 | 93.2377 | 99.3374
| MattawaWind2050RCP8.5 | Mattawa | Wind | RCP8.5 | 2050 | 75.3189 | 81.129 | 87.2384 | 93.3543 | 99.4616
| MattawaWind2055RCP8.5 | Mattawa | Wind | RCP8.5 | 2055 | 75.4798 | 81.3263 | 87.4792 | 93.6304 | 99.7753
| MattawaWind2060RCP8.5 | Mattawa | Wind | RCP8.5 | 2060 | 75.6135 | 81.4943 | 87.6913 | 93.8788 | 100.0629
| MattawaWind2065RCP8.5 | Mattawa | Wind | RCP8.5 | 2065 | 75.5863 | 81.465 | 87.6627 | 93.8512 | 100.0367
| MattawaWind2070RCP8.5 | Mattawa | Wind | RCP8.5 | 2070 | 75.7595 | 81.6676 | 87.8977 | 94.115 | 100.3341
| MattawaWind2075RCP8.5 | Mattawa | Wind | RCP8.5 | 2075 | 75.96 | 81.8995 | 88.1615 | 94.4064 | 100.6577
| MattawaWind2080RCP8.5 | Mattawa | Wind | RCP8.5 | 2080 | 76.1605 | 82.1315 | 88.4252 | 94.6978 | 100.9812
| MattawaWind2085RCP8.5 | Mattawa | Wind | RCP8.5 | 2085 | 76.1828 | 82.1395 | 88.4166 | 94.6748 | 100.942
| MattawaWind2090RCP8.5 | Mattawa | Wind | RCP8.5 | 2090 | 76.2051 | 82.1475 | 88.408 | 94.6518 | 100.9028
| MattawaWind2095RCP8.5 | Mattawa | Wind | RCP8.5 | 2095 | 76.2051 | 82.1475 | 88.408 | 94.6518 | 100.9028
| MattawaWind2100RCP8.5 | Mattawa | Wind | RCP8.5 | 2100 | 76.2051 | 82.1475 | 88.408 | 94.6518 | 100.9028
| MidlandIce Accretion2023RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2023 | 13.6525 | 16.2846 | 19.62 | 22.1706 | 24.7464
| MidlandIce Accretion2025RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2025 | 13.6363 | 16.2735 | 19.6133 | 22.1706 | 24.7464
| MidlandIce Accretion2030RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2030 | 13.62 | 16.2625 | 19.6067 | 22.1706 | 24.7464
| MidlandIce Accretion2035RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2035 | 13.6038 | 16.2514 | 19.6 | 22.1706 | 24.7464
| MidlandIce Accretion2040RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2040 | 13.5876 | 16.2403 | 19.5933 | 22.1706 | 24.7464
| MidlandIce Accretion2045RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2045 | 13.5713 | 16.2293 | 19.5867 | 22.1706 | 24.7464
| MidlandIce Accretion2050RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2050 | 13.5523 | 16.2282 | 19.612 | 22.2113 | 24.8018
| MidlandIce Accretion2055RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2055 | 13.5495 | 16.2381 | 19.644 | 22.252 | 24.8573
| MidlandIce Accretion2060RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2060 | 13.5467 | 16.2481 | 19.676 | 22.2926 | 24.9127
| MidlandIce Accretion2065RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2065 | 13.5439 | 16.258 | 19.708 | 22.3333 | 24.9682
| MidlandIce Accretion2070RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2070 | 13.5412 | 16.268 | 19.74 | 22.374 | 25.0236
| MidlandIce Accretion2075RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2075 | 13.5806 | 16.3316 | 19.83 | 22.4832 | 25.1538
| MidlandIce Accretion2080RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2080 | 13.62 | 16.3953 | 19.92 | 22.5925 | 25.284
| MidlandIce Accretion2085RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2085 | 13.6595 | 16.4589 | 20.01 | 22.7017 | 25.4142
| MidlandIce Accretion2090RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2090 | 13.6989 | 16.5225 | 20.1 | 22.8109 | 25.5444
| MidlandIce Accretion2095RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2095 | 13.7383 | 16.5862 | 20.19 | 22.9202 | 25.6746
| MidlandIce Accretion2100RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2100 | 13.7778 | 16.6498 | 20.28 | 23.0294 | 25.8048
| MidlandIce Accretion2023RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2023 | 13.6525 | 16.2846 | 19.62 | 22.1706 | 24.7464
| MidlandIce Accretion2025RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2025 | 13.6363 | 16.2735 | 19.6133 | 22.1706 | 24.7464
| MidlandIce Accretion2030RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2030 | 13.62 | 16.2625 | 19.6067 | 22.1706 | 24.7464
| MidlandIce Accretion2035RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2035 | 13.6038 | 16.2514 | 19.6 | 22.1706 | 24.7464
| MidlandIce Accretion2040RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2040 | 13.5876 | 16.2403 | 19.5933 | 22.1706 | 24.7464
| MidlandIce Accretion2045RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2045 | 13.5713 | 16.2293 | 19.5867 | 22.1706 | 24.7464
| MidlandIce Accretion2050RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2050 | 13.5523 | 16.2282 | 19.612 | 22.2113 | 24.8018
| MidlandIce Accretion2055RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2055 | 13.5495 | 16.2381 | 19.644 | 22.252 | 24.8573
| MidlandIce Accretion2060RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2060 | 13.5467 | 16.2481 | 19.676 | 22.2926 | 24.9127
| MidlandIce Accretion2065RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2065 | 13.5439 | 16.258 | 19.708 | 22.3333 | 24.9682
| MidlandIce Accretion2070RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2070 | 13.5412 | 16.268 | 19.74 | 22.374 | 25.0236
| MidlandIce Accretion2075RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2075 | 13.6003 | 16.3634 | 19.875 | 22.5378 | 25.2189
| MidlandIce Accretion2080RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2080 | 13.6595 | 16.4589 | 20.01 | 22.7017 | 25.4142
| MidlandIce Accretion2085RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2085 | 13.7186 | 16.5543 | 20.145 | 22.8655 | 25.6095
| MidlandIce Accretion2090RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2090 | 13.7546 | 16.6609 | 20.3333 | 23.1198 | 25.9224
| MidlandIce Accretion2095RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2095 | 13.7314 | 16.6719 | 20.3867 | 23.2102 | 26.04
| MidlandIce Accretion2100RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2100 | 13.7082 | 16.683 | 20.44 | 23.3006 | 26.1576
| MidlandIce Accretion2023RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2023 | 13.6525 | 16.2846 | 19.62 | 22.1706 | 24.7464
| MidlandIce Accretion2025RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2025 | 13.62 | 16.2625 | 19.6067 | 22.1706 | 24.7464
| MidlandIce Accretion2030RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2030 | 13.5876 | 16.2403 | 19.5933 | 22.1706 | 24.7464
| MidlandIce Accretion2035RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2035 | 13.5551 | 16.2182 | 19.58 | 22.1706 | 24.7464
| MidlandIce Accretion2040RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2040 | 13.5504 | 16.2348 | 19.6333 | 22.2384 | 24.8388
| MidlandIce Accretion2045RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2045 | 13.5458 | 16.2514 | 19.6867 | 22.3062 | 24.9312
| MidlandIce Accretion2050RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2050 | 13.62 | 16.3953 | 19.92 | 22.5925 | 25.284
| MidlandIce Accretion2055RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2055 | 13.6989 | 16.5225 | 20.1 | 22.8109 | 25.5444
| MidlandIce Accretion2060RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2060 | 13.7546 | 16.6609 | 20.3333 | 23.1198 | 25.9224
| MidlandIce Accretion2065RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2065 | 13.7314 | 16.6719 | 20.3867 | 23.2102 | 26.04
| MidlandIce Accretion2070RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2070 | 13.4577 | 16.4174 | 20.1533 | 22.9917 | 25.83
| MidlandIce Accretion2075RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2075 | 13.2072 | 16.1518 | 19.8667 | 22.6829 | 25.5024
| MidlandIce Accretion2080RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2080 | 12.9567 | 15.8862 | 19.58 | 22.374 | 25.1748
| MidlandIce Accretion2085RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2085 | 12.4348 | 15.2969 | 18.9 | 21.6282 | 24.3558
| MidlandIce Accretion2090RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2090 | 11.9129 | 14.7076 | 18.22 | 20.8824 | 23.5368
| MidlandIce Accretion2095RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2095 | 11.9129 | 14.7076 | 18.22 | 20.8824 | 23.5368
| MidlandIce Accretion2100RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2100 | 11.9129 | 14.7076 | 18.22 | 20.8824 | 23.5368
| MidlandWind2023RCP4.5 | Midland | Wind | RCP4.5 | 2023 | 78.2108 | 84.2692 | 90.657 | 97.0319 | 103.4105
| MidlandWind2025RCP4.5 | Midland | Wind | RCP4.5 | 2025 | 78.2911 | 84.3654 | 90.771 | 97.1619 | 103.5559
| MidlandWind2030RCP4.5 | Midland | Wind | RCP4.5 | 2030 | 78.3714 | 84.4617 | 90.885 | 97.2919 | 103.7012
| MidlandWind2035RCP4.5 | Midland | Wind | RCP4.5 | 2035 | 78.4517 | 84.5579 | 90.999 | 97.4219 | 103.8466
| MidlandWind2040RCP4.5 | Midland | Wind | RCP4.5 | 2040 | 78.532 | 84.6542 | 91.113 | 97.5519 | 103.9919
| MidlandWind2045RCP4.5 | Midland | Wind | RCP4.5 | 2045 | 78.6123 | 84.7504 | 91.227 | 97.6819 | 104.1373
| MidlandWind2050RCP4.5 | Midland | Wind | RCP4.5 | 2050 | 78.8045 | 84.9806 | 91.503 | 97.9987 | 104.496
| MidlandWind2055RCP4.5 | Midland | Wind | RCP4.5 | 2055 | 78.9164 | 85.1145 | 91.665 | 98.1856 | 104.7095
| MidlandWind2060RCP4.5 | Midland | Wind | RCP4.5 | 2060 | 79.0283 | 85.2485 | 91.827 | 98.3724 | 104.9229
| MidlandWind2065RCP4.5 | Midland | Wind | RCP4.5 | 2065 | 79.1402 | 85.3824 | 91.989 | 98.5592 | 105.1363
| MidlandWind2070RCP4.5 | Midland | Wind | RCP4.5 | 2070 | 79.2521 | 85.5163 | 92.151 | 98.746 | 105.3497
| MidlandWind2075RCP4.5 | Midland | Wind | RCP4.5 | 2075 | 79.2871 | 85.5665 | 92.2215 | 98.8327 | 105.4523
| MidlandWind2080RCP4.5 | Midland | Wind | RCP4.5 | 2080 | 79.3221 | 85.6167 | 92.292 | 98.9194 | 105.5549
| MidlandWind2085RCP4.5 | Midland | Wind | RCP4.5 | 2085 | 79.3571 | 85.667 | 92.3625 | 99.006 | 105.6575
| MidlandWind2090RCP4.5 | Midland | Wind | RCP4.5 | 2090 | 79.392 | 85.7172 | 92.433 | 99.0927 | 105.7601
| MidlandWind2095RCP4.5 | Midland | Wind | RCP4.5 | 2095 | 79.427 | 85.7674 | 92.5035 | 99.1794 | 105.8627
| MidlandWind2100RCP4.5 | Midland | Wind | RCP4.5 | 2100 | 79.462 | 85.8176 | 92.574 | 99.266 | 105.9653
| MidlandWind2023RCP6.0 | Midland | Wind | RCP6.0 | 2023 | 78.2108 | 84.2692 | 90.657 | 97.0319 | 103.4105
| MidlandWind2025RCP6.0 | Midland | Wind | RCP6.0 | 2025 | 78.2911 | 84.3654 | 90.771 | 97.1619 | 103.5559
| MidlandWind2030RCP6.0 | Midland | Wind | RCP6.0 | 2030 | 78.3714 | 84.4617 | 90.885 | 97.2919 | 103.7012
| MidlandWind2035RCP6.0 | Midland | Wind | RCP6.0 | 2035 | 78.4517 | 84.5579 | 90.999 | 97.4219 | 103.8466
| MidlandWind2040RCP6.0 | Midland | Wind | RCP6.0 | 2040 | 78.532 | 84.6542 | 91.113 | 97.5519 | 103.9919
| MidlandWind2045RCP6.0 | Midland | Wind | RCP6.0 | 2045 | 78.6123 | 84.7504 | 91.227 | 97.6819 | 104.1373
| MidlandWind2050RCP6.0 | Midland | Wind | RCP6.0 | 2050 | 78.8045 | 84.9806 | 91.503 | 97.9987 | 104.496
| MidlandWind2055RCP6.0 | Midland | Wind | RCP6.0 | 2055 | 78.9164 | 85.1145 | 91.665 | 98.1856 | 104.7095
| MidlandWind2060RCP6.0 | Midland | Wind | RCP6.0 | 2060 | 79.0283 | 85.2485 | 91.827 | 98.3724 | 104.9229
| MidlandWind2065RCP6.0 | Midland | Wind | RCP6.0 | 2065 | 79.1402 | 85.3824 | 91.989 | 98.5592 | 105.1363
| MidlandWind2070RCP6.0 | Midland | Wind | RCP6.0 | 2070 | 79.2521 | 85.5163 | 92.151 | 98.746 | 105.3497
| MidlandWind2075RCP6.0 | Midland | Wind | RCP6.0 | 2075 | 79.3046 | 85.5916 | 92.2567 | 98.876 | 105.5036
| MidlandWind2080RCP6.0 | Midland | Wind | RCP6.0 | 2080 | 79.3571 | 85.667 | 92.3625 | 99.006 | 105.6575
| MidlandWind2085RCP6.0 | Midland | Wind | RCP6.0 | 2085 | 79.4095 | 85.7423 | 92.4682 | 99.136 | 105.8114
| MidlandWind2090RCP6.0 | Midland | Wind | RCP6.0 | 2090 | 79.5785 | 85.9739 | 92.775 | 99.5068 | 106.2457
| MidlandWind2095RCP6.0 | Midland | Wind | RCP6.0 | 2095 | 79.6951 | 86.1301 | 92.976 | 99.7475 | 106.5262
| MidlandWind2100RCP6.0 | Midland | Wind | RCP6.0 | 2100 | 79.8117 | 86.2863 | 93.177 | 99.9883 | 106.8066
| MidlandWind2023RCP8.5 | Midland | Wind | RCP8.5 | 2023 | 78.2108 | 84.2692 | 90.657 | 97.0319 | 103.4105
| MidlandWind2025RCP8.5 | Midland | Wind | RCP8.5 | 2025 | 78.3714 | 84.4617 | 90.885 | 97.2919 | 103.7012
| MidlandWind2030RCP8.5 | Midland | Wind | RCP8.5 | 2030 | 78.532 | 84.6542 | 91.113 | 97.5519 | 103.9919
| MidlandWind2035RCP8.5 | Midland | Wind | RCP8.5 | 2035 | 78.6926 | 84.8467 | 91.341 | 97.8119 | 104.2826
| MidlandWind2040RCP8.5 | Midland | Wind | RCP8.5 | 2040 | 78.8791 | 85.0699 | 91.611 | 98.1233 | 104.6383
| MidlandWind2045RCP8.5 | Midland | Wind | RCP8.5 | 2045 | 79.0656 | 85.2931 | 91.881 | 98.4347 | 104.994
| MidlandWind2050RCP8.5 | Midland | Wind | RCP8.5 | 2050 | 79.3221 | 85.6167 | 92.292 | 98.9194 | 105.5549
| MidlandWind2055RCP8.5 | Midland | Wind | RCP8.5 | 2055 | 79.392 | 85.7172 | 92.433 | 99.0927 | 105.7601
| MidlandWind2060RCP8.5 | Midland | Wind | RCP8.5 | 2060 | 79.5785 | 85.9739 | 92.775 | 99.5068 | 106.2457
| MidlandWind2065RCP8.5 | Midland | Wind | RCP8.5 | 2065 | 79.6951 | 86.1301 | 92.976 | 99.7475 | 106.5262
| MidlandWind2070RCP8.5 | Midland | Wind | RCP8.5 | 2070 | 79.7987 | 86.2807 | 93.183 | 100.0011 | 106.8305
| MidlandWind2075RCP8.5 | Midland | Wind | RCP8.5 | 2075 | 79.7858 | 86.2752 | 93.189 | 100.014 | 106.8545
| MidlandWind2080RCP8.5 | Midland | Wind | RCP8.5 | 2080 | 79.7728 | 86.2696 | 93.195 | 100.0268 | 106.8784
| MidlandWind2085RCP8.5 | Midland | Wind | RCP8.5 | 2085 | 79.8739 | 86.3993 | 93.366 | 100.229 | 107.1144
| MidlandWind2090RCP8.5 | Midland | Wind | RCP8.5 | 2090 | 79.9749 | 86.5291 | 93.537 | 100.4313 | 107.3504
| MidlandWind2095RCP8.5 | Midland | Wind | RCP8.5 | 2095 | 79.9749 | 86.5291 | 93.537 | 100.4313 | 107.3504
| MidlandWind2100RCP8.5 | Midland | Wind | RCP8.5 | 2100 | 79.9749 | 86.5291 | 93.537 | 100.4313 | 107.3504
| MiltonIce Accretion2023RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| MiltonIce Accretion2025RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
| MiltonIce Accretion2030RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| MiltonIce Accretion2035RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
| MiltonIce Accretion2040RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| MiltonIce Accretion2045RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
| MiltonIce Accretion2050RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
| MiltonIce Accretion2055RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
| MiltonIce Accretion2060RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
| MiltonIce Accretion2065RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
| MiltonIce Accretion2070RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
| MiltonIce Accretion2075RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2075 | 15.5377 | 18.8894 | 23.1125 | 26.329 | 29.5313
| MiltonIce Accretion2080RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2080 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
| MiltonIce Accretion2085RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2085 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
| MiltonIce Accretion2090RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2090 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
| MiltonIce Accretion2095RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2095 | 15.3405 | 18.7511 | 23.0625 | 26.329 | 29.5942
| MiltonIce Accretion2100RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2100 | 15.2912 | 18.7165 | 23.05 | 26.329 | 29.61
| MiltonIce Accretion2023RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| MiltonIce Accretion2025RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
| MiltonIce Accretion2030RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| MiltonIce Accretion2035RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
| MiltonIce Accretion2040RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| MiltonIce Accretion2045RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
| MiltonIce Accretion2050RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
| MiltonIce Accretion2055RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
| MiltonIce Accretion2060RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
| MiltonIce Accretion2065RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
| MiltonIce Accretion2070RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
| MiltonIce Accretion2075RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2075 | 15.513 | 18.8721 | 23.1062 | 26.329 | 29.5391
| MiltonIce Accretion2080RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2080 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
| MiltonIce Accretion2085RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2085 | 15.3652 | 18.7684 | 23.0688 | 26.329 | 29.5864
| MiltonIce Accretion2090RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2090 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
| MiltonIce Accretion2095RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2095 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
| MiltonIce Accretion2100RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2100 | 14.2127 | 17.596 | 21.825 | 25.0577 | 28.2555
| MiltonIce Accretion2023RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| MiltonIce Accretion2025RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2025 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| MiltonIce Accretion2030RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2030 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| MiltonIce Accretion2035RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2035 | 16.6133 | 20.0652 | 24.425 | 27.7415 | 31.059
| MiltonIce Accretion2040RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2040 | 16.2712 | 19.6848 | 23.9917 | 27.2707 | 30.5445
| MiltonIce Accretion2045RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2045 | 15.9291 | 19.3044 | 23.5583 | 26.7998 | 30.03
| MiltonIce Accretion2050RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2050 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
| MiltonIce Accretion2055RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2055 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
| MiltonIce Accretion2060RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2060 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
| MiltonIce Accretion2065RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2065 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
| MiltonIce Accretion2070RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2070 | 13.8125 | 17.1464 | 21.325 | 24.5022 | 27.657
| MiltonIce Accretion2075RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2075 | 13.4124 | 16.6968 | 20.825 | 23.9466 | 27.0585
| MiltonIce Accretion2080RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2080 | 13.0123 | 16.2473 | 20.325 | 23.391 | 26.46
| MiltonIce Accretion2085RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2085 | 12.1338 | 15.1994 | 19.0625 | 21.9785 | 24.885
| MiltonIce Accretion2090RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2090 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| MiltonIce Accretion2095RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2095 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| MiltonIce Accretion2100RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2100 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| MiltonWind2023RCP4.5 | Milton | Wind | RCP4.5 | 2023 | 82.4328 | 88.8359 | 95.589 | 102.3311 | 109.0689
| MiltonWind2025RCP4.5 | Milton | Wind | RCP4.5 | 2025 | 82.4629 | 88.8801 | 95.6523 | 102.4107 | 109.1646
| MiltonWind2030RCP4.5 | Milton | Wind | RCP4.5 | 2030 | 82.4929 | 88.9243 | 95.7157 | 102.4903 | 109.2603
| MiltonWind2035RCP4.5 | Milton | Wind | RCP4.5 | 2035 | 82.523 | 88.9685 | 95.779 | 102.5699 | 109.3559
| MiltonWind2040RCP4.5 | Milton | Wind | RCP4.5 | 2040 | 82.5531 | 89.0126 | 95.8423 | 102.6496 | 109.4516
| MiltonWind2045RCP4.5 | Milton | Wind | RCP4.5 | 2045 | 82.5832 | 89.0568 | 95.9057 | 102.7292 | 109.5473
| MiltonWind2050RCP4.5 | Milton | Wind | RCP4.5 | 2050 | 82.6789 | 89.1805 | 96.0659 | 102.9206 | 109.7707
| MiltonWind2055RCP4.5 | Milton | Wind | RCP4.5 | 2055 | 82.7445 | 89.26 | 96.1628 | 103.0324 | 109.8985
| MiltonWind2060RCP4.5 | Milton | Wind | RCP4.5 | 2060 | 82.8101 | 89.3395 | 96.2597 | 103.1443 | 110.0263
| MiltonWind2065RCP4.5 | Milton | Wind | RCP4.5 | 2065 | 82.8757 | 89.419 | 96.3566 | 103.2561 | 110.1541
| MiltonWind2070RCP4.5 | Milton | Wind | RCP4.5 | 2070 | 82.9414 | 89.4985 | 96.4535 | 103.3679 | 110.2819
| MiltonWind2075RCP4.5 | Milton | Wind | RCP4.5 | 2075 | 83.0316 | 89.6252 | 96.6261 | 103.578 | 110.531
| MiltonWind2080RCP4.5 | Milton | Wind | RCP4.5 | 2080 | 83.1218 | 89.7518 | 96.7987 | 103.788 | 110.7801
| MiltonWind2085RCP4.5 | Milton | Wind | RCP4.5 | 2085 | 83.2121 | 89.8785 | 96.9712 | 103.9981 | 111.0292
| MiltonWind2090RCP4.5 | Milton | Wind | RCP4.5 | 2090 | 83.3023 | 90.0051 | 97.1438 | 104.2082 | 111.2782
| MiltonWind2095RCP4.5 | Milton | Wind | RCP4.5 | 2095 | 83.3925 | 90.1317 | 97.3164 | 104.4183 | 111.5273
| MiltonWind2100RCP4.5 | Milton | Wind | RCP4.5 | 2100 | 83.4828 | 90.2584 | 97.489 | 104.6283 | 111.7764
| MiltonWind2023RCP6.0 | Milton | Wind | RCP6.0 | 2023 | 82.4328 | 88.8359 | 95.589 | 102.3311 | 109.0689
| MiltonWind2025RCP6.0 | Milton | Wind | RCP6.0 | 2025 | 82.4629 | 88.8801 | 95.6523 | 102.4107 | 109.1646
| MiltonWind2030RCP6.0 | Milton | Wind | RCP6.0 | 2030 | 82.4929 | 88.9243 | 95.7157 | 102.4903 | 109.2603
| MiltonWind2035RCP6.0 | Milton | Wind | RCP6.0 | 2035 | 82.523 | 88.9685 | 95.779 | 102.5699 | 109.3559
| MiltonWind2040RCP6.0 | Milton | Wind | RCP6.0 | 2040 | 82.5531 | 89.0126 | 95.8423 | 102.6496 | 109.4516
| MiltonWind2045RCP6.0 | Milton | Wind | RCP6.0 | 2045 | 82.5832 | 89.0568 | 95.9057 | 102.7292 | 109.5473
| MiltonWind2050RCP6.0 | Milton | Wind | RCP6.0 | 2050 | 82.6789 | 89.1805 | 96.0659 | 102.9206 | 109.7707
| MiltonWind2055RCP6.0 | Milton | Wind | RCP6.0 | 2055 | 82.7445 | 89.26 | 96.1628 | 103.0324 | 109.8985
| MiltonWind2060RCP6.0 | Milton | Wind | RCP6.0 | 2060 | 82.8101 | 89.3395 | 96.2597 | 103.1443 | 110.0263
| MiltonWind2065RCP6.0 | Milton | Wind | RCP6.0 | 2065 | 82.8757 | 89.419 | 96.3566 | 103.2561 | 110.1541
| MiltonWind2070RCP6.0 | Milton | Wind | RCP6.0 | 2070 | 82.9414 | 89.4985 | 96.4535 | 103.3679 | 110.2819
| MiltonWind2075RCP6.0 | Milton | Wind | RCP6.0 | 2075 | 83.0767 | 89.6885 | 96.7124 | 103.683 | 110.6555
| MiltonWind2080RCP6.0 | Milton | Wind | RCP6.0 | 2080 | 83.2121 | 89.8785 | 96.9712 | 103.9981 | 111.0292
| MiltonWind2085RCP6.0 | Milton | Wind | RCP6.0 | 2085 | 83.3474 | 90.0684 | 97.2301 | 104.3132 | 111.4028
| MiltonWind2090RCP6.0 | Milton | Wind | RCP6.0 | 2090 | 83.7671 | 90.6235 | 97.9545 | 105.1806 | 112.419
| MiltonWind2095RCP6.0 | Milton | Wind | RCP6.0 | 2095 | 84.0515 | 90.9887 | 98.42 | 105.7329 | 113.0616
| MiltonWind2100RCP6.0 | Milton | Wind | RCP6.0 | 2100 | 84.3359 | 91.3539 | 98.8855 | 106.2852 | 113.7042
| MiltonWind2023RCP8.5 | Milton | Wind | RCP8.5 | 2023 | 82.4328 | 88.8359 | 95.589 | 102.3311 | 109.0689
| MiltonWind2025RCP8.5 | Milton | Wind | RCP8.5 | 2025 | 82.4929 | 88.9243 | 95.7157 | 102.4903 | 109.2603
| MiltonWind2030RCP8.5 | Milton | Wind | RCP8.5 | 2030 | 82.5531 | 89.0126 | 95.8423 | 102.6496 | 109.4516
| MiltonWind2035RCP8.5 | Milton | Wind | RCP8.5 | 2035 | 82.6132 | 89.101 | 95.969 | 102.8088 | 109.6429
| MiltonWind2040RCP8.5 | Milton | Wind | RCP8.5 | 2040 | 82.7226 | 89.2335 | 96.1305 | 102.9952 | 109.8559
| MiltonWind2045RCP8.5 | Milton | Wind | RCP8.5 | 2045 | 82.832 | 89.366 | 96.292 | 103.1815 | 110.0689
| MiltonWind2050RCP8.5 | Milton | Wind | RCP8.5 | 2050 | 83.1218 | 89.7518 | 96.7987 | 103.788 | 110.7801
| MiltonWind2055RCP8.5 | Milton | Wind | RCP8.5 | 2055 | 83.3023 | 90.0051 | 97.1438 | 104.2082 | 111.2782
| MiltonWind2060RCP8.5 | Milton | Wind | RCP8.5 | 2060 | 83.7671 | 90.6235 | 97.9545 | 105.1806 | 112.419
| MiltonWind2065RCP8.5 | Milton | Wind | RCP8.5 | 2065 | 84.0515 | 90.9887 | 98.42 | 105.7329 | 113.0616
| MiltonWind2070RCP8.5 | Milton | Wind | RCP8.5 | 2070 | 84.4972 | 91.5866 | 99.2085 | 106.6817 | 114.1771
| MiltonWind2075RCP8.5 | Milton | Wind | RCP8.5 | 2075 | 84.6586 | 91.8192 | 99.5315 | 107.0781 | 114.65
| MiltonWind2080RCP8.5 | Milton | Wind | RCP8.5 | 2080 | 84.8199 | 92.0519 | 99.8545 | 107.4745 | 115.1229
| MiltonWind2085RCP8.5 | Milton | Wind | RCP8.5 | 2085 | 85.0783 | 92.3876 | 100.2867 | 107.993 | 115.7294
| MiltonWind2090RCP8.5 | Milton | Wind | RCP8.5 | 2090 | 85.3367 | 92.7233 | 100.719 | 108.5114 | 116.3359
| MiltonWind2095RCP8.5 | Milton | Wind | RCP8.5 | 2095 | 85.3367 | 92.7233 | 100.719 | 108.5114 | 116.3359
| MiltonWind2100RCP8.5 | Milton | Wind | RCP8.5 | 2100 | 85.3367 | 92.7233 | 100.719 | 108.5114 | 116.3359
| MilvertonIce Accretion2023RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2023 | 15.9725 | 19.1854 | 23.253 | 26.3539 | 29.4437
| MilvertonIce Accretion2025RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2025 | 16.0498 | 19.2841 | 23.3795 | 26.5055 | 29.6176
| MilvertonIce Accretion2030RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2030 | 16.1272 | 19.3827 | 23.506 | 26.6571 | 29.7914
| MilvertonIce Accretion2035RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2035 | 16.2045 | 19.4813 | 23.6325 | 26.8087 | 29.9653
| MilvertonIce Accretion2040RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2040 | 16.2819 | 19.58 | 23.759 | 26.9603 | 30.1392
| MilvertonIce Accretion2045RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2045 | 16.3592 | 19.6786 | 23.8855 | 27.1119 | 30.3131
| MilvertonIce Accretion2050RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2050 | 16.443 | 19.8078 | 24.0764 | 27.3415 | 30.5913
| MilvertonIce Accretion2055RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2055 | 16.4494 | 19.8383 | 24.1408 | 27.4194 | 30.6956
| MilvertonIce Accretion2060RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2060 | 16.4558 | 19.8689 | 24.2052 | 27.4974 | 30.7999
| MilvertonIce Accretion2065RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2065 | 16.4622 | 19.8994 | 24.2696 | 27.5754 | 30.9043
| MilvertonIce Accretion2070RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2070 | 16.4686 | 19.93 | 24.334 | 27.6534 | 31.0086
| MilvertonIce Accretion2075RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2075 | 16.4179 | 19.8981 | 24.3187 | 27.6577 | 31.0231
| MilvertonIce Accretion2080RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2080 | 16.3672 | 19.8663 | 24.3033 | 27.662 | 31.0376
| MilvertonIce Accretion2085RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2085 | 16.3165 | 19.8345 | 24.288 | 27.6664 | 31.0521
| MilvertonIce Accretion2090RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2090 | 16.2659 | 19.8027 | 24.2727 | 27.6707 | 31.0666
| MilvertonIce Accretion2095RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2095 | 16.2152 | 19.7709 | 24.2573 | 27.675 | 31.0811
| MilvertonIce Accretion2100RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2100 | 16.1645 | 19.7391 | 24.242 | 27.6793 | 31.0955
| MilvertonIce Accretion2023RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2023 | 15.9725 | 19.1854 | 23.253 | 26.3539 | 29.4437
| MilvertonIce Accretion2025RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2025 | 16.0498 | 19.2841 | 23.3795 | 26.5055 | 29.6176
| MilvertonIce Accretion2030RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2030 | 16.1272 | 19.3827 | 23.506 | 26.6571 | 29.7914
| MilvertonIce Accretion2035RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2035 | 16.2045 | 19.4813 | 23.6325 | 26.8087 | 29.9653
| MilvertonIce Accretion2040RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2040 | 16.2819 | 19.58 | 23.759 | 26.9603 | 30.1392
| MilvertonIce Accretion2045RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2045 | 16.3592 | 19.6786 | 23.8855 | 27.1119 | 30.3131
| MilvertonIce Accretion2050RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2050 | 16.443 | 19.8078 | 24.0764 | 27.3415 | 30.5913
| MilvertonIce Accretion2055RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2055 | 16.4494 | 19.8383 | 24.1408 | 27.4194 | 30.6956
| MilvertonIce Accretion2060RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2060 | 16.4558 | 19.8689 | 24.2052 | 27.4974 | 30.7999
| MilvertonIce Accretion2065RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2065 | 16.4622 | 19.8994 | 24.2696 | 27.5754 | 30.9043
| MilvertonIce Accretion2070RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2070 | 16.4686 | 19.93 | 24.334 | 27.6534 | 31.0086
| MilvertonIce Accretion2075RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2075 | 16.3926 | 19.8822 | 24.311 | 27.6599 | 31.0303
| MilvertonIce Accretion2080RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2080 | 16.3165 | 19.8345 | 24.288 | 27.6664 | 31.0521
| MilvertonIce Accretion2085RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2085 | 16.2405 | 19.7868 | 24.265 | 27.6729 | 31.0738
| MilvertonIce Accretion2090RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2090 | 15.8978 | 19.4654 | 23.9583 | 27.3761 | 30.7864
| MilvertonIce Accretion2095RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2095 | 15.631 | 19.1918 | 23.6747 | 27.0729 | 30.4773
| MilvertonIce Accretion2100RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2100 | 15.3643 | 18.9182 | 23.391 | 26.7697 | 30.1682
| MilvertonIce Accretion2023RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2023 | 15.9725 | 19.1854 | 23.253 | 26.3539 | 29.4437
| MilvertonIce Accretion2025RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2025 | 16.1272 | 19.3827 | 23.506 | 26.6571 | 29.7914
| MilvertonIce Accretion2030RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2030 | 16.2819 | 19.58 | 23.759 | 26.9603 | 30.1392
| MilvertonIce Accretion2035RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2035 | 16.4366 | 19.7772 | 24.012 | 27.2635 | 30.487
| MilvertonIce Accretion2040RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2040 | 16.4473 | 19.8281 | 24.1193 | 27.3935 | 30.6608
| MilvertonIce Accretion2045RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2045 | 16.4579 | 19.8791 | 24.2267 | 27.5234 | 30.8347
| MilvertonIce Accretion2050RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2050 | 16.3672 | 19.8663 | 24.3033 | 27.662 | 31.0376
| MilvertonIce Accretion2055RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2055 | 16.2659 | 19.8027 | 24.2727 | 27.6707 | 31.0666
| MilvertonIce Accretion2060RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2060 | 15.8978 | 19.4654 | 23.9583 | 27.3761 | 30.7864
| MilvertonIce Accretion2065RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2065 | 15.631 | 19.1918 | 23.6747 | 27.0729 | 30.4773
| MilvertonIce Accretion2070RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2070 | 14.8735 | 18.3646 | 22.7623 | 26.0853 | 29.4147
| MilvertonIce Accretion2075RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2075 | 14.3827 | 17.811 | 22.1337 | 25.4009 | 28.6612
| MilvertonIce Accretion2080RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2080 | 13.8919 | 17.2574 | 21.505 | 24.7165 | 27.9077
| MilvertonIce Accretion2085RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2085 | 13.1717 | 16.4079 | 20.493 | 23.5729 | 26.6471
| MilvertonIce Accretion2090RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2090 | 12.4515 | 15.5583 | 19.481 | 22.4294 | 25.3865
| MilvertonIce Accretion2095RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2095 | 12.4515 | 15.5583 | 19.481 | 22.4294 | 25.3865
| MilvertonIce Accretion2100RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2100 | 12.4515 | 15.5583 | 19.481 | 22.4294 | 25.3865
| MilvertonWind2023RCP4.5 | Milverton | Wind | RCP4.5 | 2023 | 85.2136 | 91.8691 | 98.8918 | 105.8981 | 112.9042
| MilvertonWind2025RCP4.5 | Milverton | Wind | RCP4.5 | 2025 | 85.2588 | 91.9223 | 98.9555 | 105.9698 | 112.9862
| MilvertonWind2030RCP4.5 | Milverton | Wind | RCP4.5 | 2030 | 85.3039 | 91.9754 | 99.0192 | 106.0414 | 113.0681
| MilvertonWind2035RCP4.5 | Milverton | Wind | RCP4.5 | 2035 | 85.349 | 92.0286 | 99.0829 | 106.1131 | 113.15
| MilvertonWind2040RCP4.5 | Milverton | Wind | RCP4.5 | 2040 | 85.3942 | 92.0818 | 99.1466 | 106.1847 | 113.2319
| MilvertonWind2045RCP4.5 | Milverton | Wind | RCP4.5 | 2045 | 85.4393 | 92.1349 | 99.2103 | 106.2564 | 113.3139
| MilvertonWind2050RCP4.5 | Milverton | Wind | RCP4.5 | 2050 | 85.4929 | 92.1936 | 99.274 | 106.3259 | 113.3869
| MilvertonWind2055RCP4.5 | Milverton | Wind | RCP4.5 | 2055 | 85.5013 | 92.199 | 99.274 | 106.3238 | 113.3779
| MilvertonWind2060RCP4.5 | Milverton | Wind | RCP4.5 | 2060 | 85.5098 | 92.2045 | 99.274 | 106.3217 | 113.369
| MilvertonWind2065RCP4.5 | Milverton | Wind | RCP4.5 | 2065 | 85.5183 | 92.21 | 99.274 | 106.3197 | 113.36
| MilvertonWind2070RCP4.5 | Milverton | Wind | RCP4.5 | 2070 | 85.5267 | 92.2155 | 99.274 | 106.3176 | 113.3511
| MilvertonWind2075RCP4.5 | Milverton | Wind | RCP4.5 | 2075 | 85.6212 | 92.3446 | 99.4488 | 106.5308 | 113.6043
| MilvertonWind2080RCP4.5 | Milverton | Wind | RCP4.5 | 2080 | 85.7157 | 92.4737 | 99.6235 | 106.744 | 113.8576
| MilvertonWind2085RCP4.5 | Milverton | Wind | RCP4.5 | 2085 | 85.8102 | 92.6028 | 99.7983 | 106.9572 | 114.1108
| MilvertonWind2090RCP4.5 | Milverton | Wind | RCP4.5 | 2090 | 85.9047 | 92.7319 | 99.9731 | 107.1704 | 114.364
| MilvertonWind2095RCP4.5 | Milverton | Wind | RCP4.5 | 2095 | 85.9992 | 92.861 | 100.1478 | 107.3836 | 114.6173
| MilvertonWind2100RCP4.5 | Milverton | Wind | RCP4.5 | 2100 | 86.0937 | 92.9901 | 100.3226 | 107.5968 | 114.8705
| MilvertonWind2023RCP6.0 | Milverton | Wind | RCP6.0 | 2023 | 85.2136 | 91.8691 | 98.8918 | 105.8981 | 112.9042
| MilvertonWind2025RCP6.0 | Milverton | Wind | RCP6.0 | 2025 | 85.2588 | 91.9223 | 98.9555 | 105.9698 | 112.9862
| MilvertonWind2030RCP6.0 | Milverton | Wind | RCP6.0 | 2030 | 85.3039 | 91.9754 | 99.0192 | 106.0414 | 113.0681
| MilvertonWind2035RCP6.0 | Milverton | Wind | RCP6.0 | 2035 | 85.349 | 92.0286 | 99.0829 | 106.1131 | 113.15
| MilvertonWind2040RCP6.0 | Milverton | Wind | RCP6.0 | 2040 | 85.3942 | 92.0818 | 99.1466 | 106.1847 | 113.2319
| MilvertonWind2045RCP6.0 | Milverton | Wind | RCP6.0 | 2045 | 85.4393 | 92.1349 | 99.2103 | 106.2564 | 113.3139
| MilvertonWind2050RCP6.0 | Milverton | Wind | RCP6.0 | 2050 | 85.4929 | 92.1936 | 99.274 | 106.3259 | 113.3869
| MilvertonWind2055RCP6.0 | Milverton | Wind | RCP6.0 | 2055 | 85.5013 | 92.199 | 99.274 | 106.3238 | 113.3779
| MilvertonWind2060RCP6.0 | Milverton | Wind | RCP6.0 | 2060 | 85.5098 | 92.2045 | 99.274 | 106.3217 | 113.369
| MilvertonWind2065RCP6.0 | Milverton | Wind | RCP6.0 | 2065 | 85.5183 | 92.21 | 99.274 | 106.3197 | 113.36
| MilvertonWind2070RCP6.0 | Milverton | Wind | RCP6.0 | 2070 | 85.5267 | 92.2155 | 99.274 | 106.3176 | 113.3511
| MilvertonWind2075RCP6.0 | Milverton | Wind | RCP6.0 | 2075 | 85.6685 | 92.4091 | 99.5361 | 106.6374 | 113.731
| MilvertonWind2080RCP6.0 | Milverton | Wind | RCP6.0 | 2080 | 85.8102 | 92.6028 | 99.7983 | 106.9572 | 114.1108
| MilvertonWind2085RCP6.0 | Milverton | Wind | RCP6.0 | 2085 | 85.9519 | 92.7965 | 100.0605 | 107.277 | 114.4907
| MilvertonWind2090RCP6.0 | Milverton | Wind | RCP6.0 | 2090 | 86.4688 | 93.4519 | 100.8877 | 108.2505 | 115.619
| MilvertonWind2095RCP6.0 | Milverton | Wind | RCP6.0 | 2095 | 86.844 | 93.9137 | 101.4529 | 108.9041 | 116.3676
| MilvertonWind2100RCP6.0 | Milverton | Wind | RCP6.0 | 2100 | 87.2192 | 94.3755 | 102.018 | 109.5577 | 117.1161
| MilvertonWind2023RCP8.5 | Milverton | Wind | RCP8.5 | 2023 | 85.2136 | 91.8691 | 98.8918 | 105.8981 | 112.9042
| MilvertonWind2025RCP8.5 | Milverton | Wind | RCP8.5 | 2025 | 85.3039 | 91.9754 | 99.0192 | 106.0414 | 113.0681
| MilvertonWind2030RCP8.5 | Milverton | Wind | RCP8.5 | 2030 | 85.3942 | 92.0818 | 99.1466 | 106.1847 | 113.2319
| MilvertonWind2035RCP8.5 | Milverton | Wind | RCP8.5 | 2035 | 85.4844 | 92.1881 | 99.274 | 106.328 | 113.3958
| MilvertonWind2040RCP8.5 | Milverton | Wind | RCP8.5 | 2040 | 85.4985 | 92.1972 | 99.274 | 106.3245 | 113.3809
| MilvertonWind2045RCP8.5 | Milverton | Wind | RCP8.5 | 2045 | 85.5126 | 92.2063 | 99.274 | 106.321 | 113.366
| MilvertonWind2050RCP8.5 | Milverton | Wind | RCP8.5 | 2050 | 85.7157 | 92.4737 | 99.6235 | 106.744 | 113.8576
| MilvertonWind2055RCP8.5 | Milverton | Wind | RCP8.5 | 2055 | 85.9047 | 92.7319 | 99.9731 | 107.1704 | 114.364
| MilvertonWind2060RCP8.5 | Milverton | Wind | RCP8.5 | 2060 | 86.4688 | 93.4519 | 100.8877 | 108.2505 | 115.619
| MilvertonWind2065RCP8.5 | Milverton | Wind | RCP8.5 | 2065 | 86.844 | 93.9137 | 101.4529 | 108.9041 | 116.3676
| MilvertonWind2070RCP8.5 | Milverton | Wind | RCP8.5 | 2070 | 87.4956 | 94.737 | 102.4917 | 110.124 | 117.7789
| MilvertonWind2075RCP8.5 | Milverton | Wind | RCP8.5 | 2075 | 87.772 | 95.0985 | 102.9653 | 110.6902 | 118.4418
| MilvertonWind2080RCP8.5 | Milverton | Wind | RCP8.5 | 2080 | 88.0484 | 95.46 | 103.439 | 111.2565 | 119.1047
| MilvertonWind2085RCP8.5 | Milverton | Wind | RCP8.5 | 2085 | 88.2642 | 95.7471 | 103.8163 | 111.7074 | 119.6298
| MilvertonWind2090RCP8.5 | Milverton | Wind | RCP8.5 | 2090 | 88.48 | 96.0342 | 104.1936 | 112.1583 | 120.1549
| MilvertonWind2095RCP8.5 | Milverton | Wind | RCP8.5 | 2095 | 88.48 | 96.0342 | 104.1936 | 112.1583 | 120.1549
| MilvertonWind2100RCP8.5 | Milverton | Wind | RCP8.5 | 2100 | 88.48 | 96.0342 | 104.1936 | 112.1583 | 120.1549
| MindenIce Accretion2023RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2023 | 16.8569 | 20.0652 | 24.125 | 27.233 | 30.366
| MindenIce Accretion2025RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2025 | 16.8395 | 20.041 | 24.0917 | 27.1953 | 30.3188
| MindenIce Accretion2030RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2030 | 16.8221 | 20.0168 | 24.0583 | 27.1577 | 30.2715
| MindenIce Accretion2035RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2035 | 16.8047 | 19.9926 | 24.025 | 27.12 | 30.2242
| MindenIce Accretion2040RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2040 | 16.7873 | 19.9684 | 23.9917 | 27.0823 | 30.177
| MindenIce Accretion2045RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2045 | 16.7699 | 19.9442 | 23.9583 | 27.0447 | 30.1298
| MindenIce Accretion2050RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2050 | 16.749 | 19.9324 | 23.965 | 27.0635 | 30.1581
| MindenIce Accretion2055RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2055 | 16.7455 | 19.9449 | 24.005 | 27.12 | 30.2337
| MindenIce Accretion2060RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2060 | 16.7421 | 19.9573 | 24.045 | 27.1765 | 30.3093
| MindenIce Accretion2065RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2065 | 16.7386 | 19.9698 | 24.085 | 27.233 | 30.3849
| MindenIce Accretion2070RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2070 | 16.7351 | 19.9823 | 24.125 | 27.2895 | 30.4605
| MindenIce Accretion2075RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2075 | 16.8134 | 20.0929 | 24.2708 | 27.4637 | 30.66
| MindenIce Accretion2080RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2080 | 16.8917 | 20.2036 | 24.4167 | 27.6379 | 30.8595
| MindenIce Accretion2085RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2085 | 16.9699 | 20.3143 | 24.5625 | 27.8121 | 31.059
| MindenIce Accretion2090RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2090 | 17.0482 | 20.4249 | 24.7083 | 27.9863 | 31.2585
| MindenIce Accretion2095RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2095 | 17.1265 | 20.5356 | 24.8542 | 28.1605 | 31.458
| MindenIce Accretion2100RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2100 | 17.2048 | 20.6462 | 25 | 28.3347 | 31.6575
| MindenIce Accretion2023RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2023 | 16.8569 | 20.0652 | 24.125 | 27.233 | 30.366
| MindenIce Accretion2025RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2025 | 16.8395 | 20.041 | 24.0917 | 27.1953 | 30.3188
| MindenIce Accretion2030RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2030 | 16.8221 | 20.0168 | 24.0583 | 27.1577 | 30.2715
| MindenIce Accretion2035RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2035 | 16.8047 | 19.9926 | 24.025 | 27.12 | 30.2242
| MindenIce Accretion2040RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2040 | 16.7873 | 19.9684 | 23.9917 | 27.0823 | 30.177
| MindenIce Accretion2045RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2045 | 16.7699 | 19.9442 | 23.9583 | 27.0447 | 30.1298
| MindenIce Accretion2050RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2050 | 16.749 | 19.9324 | 23.965 | 27.0635 | 30.1581
| MindenIce Accretion2055RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2055 | 16.7455 | 19.9449 | 24.005 | 27.12 | 30.2337
| MindenIce Accretion2060RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2060 | 16.7421 | 19.9573 | 24.045 | 27.1765 | 30.3093
| MindenIce Accretion2065RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2065 | 16.7386 | 19.9698 | 24.085 | 27.233 | 30.3849
| MindenIce Accretion2070RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2070 | 16.7351 | 19.9823 | 24.125 | 27.2895 | 30.4605
| MindenIce Accretion2075RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2075 | 16.8525 | 20.1483 | 24.3438 | 27.5508 | 30.7597
| MindenIce Accretion2080RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2080 | 16.9699 | 20.3143 | 24.5625 | 27.8121 | 31.059
| MindenIce Accretion2085RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2085 | 17.0874 | 20.4802 | 24.7812 | 28.0734 | 31.3582
| MindenIce Accretion2090RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2090 | 17.3034 | 20.8053 | 25.2417 | 28.6361 | 32.0145
| MindenIce Accretion2095RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2095 | 17.402 | 20.9644 | 25.4833 | 28.9374 | 32.3715
| MindenIce Accretion2100RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2100 | 17.5005 | 21.1235 | 25.725 | 29.2387 | 32.7285
| MindenIce Accretion2023RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2023 | 16.8569 | 20.0652 | 24.125 | 27.233 | 30.366
| MindenIce Accretion2025RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2025 | 16.8221 | 20.0168 | 24.0583 | 27.1577 | 30.2715
| MindenIce Accretion2030RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2030 | 16.7873 | 19.9684 | 23.9917 | 27.0823 | 30.177
| MindenIce Accretion2035RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2035 | 16.7525 | 19.92 | 23.925 | 27.007 | 30.0825
| MindenIce Accretion2040RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2040 | 16.7467 | 19.9407 | 23.9917 | 27.1012 | 30.2085
| MindenIce Accretion2045RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2045 | 16.7409 | 19.9615 | 24.0583 | 27.1953 | 30.3345
| MindenIce Accretion2050RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2050 | 16.8917 | 20.2036 | 24.4167 | 27.6379 | 30.8595
| MindenIce Accretion2055RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2055 | 17.0482 | 20.4249 | 24.7083 | 27.9863 | 31.2585
| MindenIce Accretion2060RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2060 | 17.3034 | 20.8053 | 25.2417 | 28.6361 | 32.0145
| MindenIce Accretion2065RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2065 | 17.402 | 20.9644 | 25.4833 | 28.9374 | 32.3715
| MindenIce Accretion2070RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2070 | 17.373 | 20.999 | 25.6 | 29.1163 | 32.613
| MindenIce Accretion2075RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2075 | 17.2454 | 20.8745 | 25.475 | 28.9939 | 32.4975
| MindenIce Accretion2080RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2080 | 17.1178 | 20.75 | 25.35 | 28.8715 | 32.382
| MindenIce Accretion2085RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2085 | 16.6916 | 20.2831 | 24.8375 | 28.3065 | 31.7677
| MindenIce Accretion2090RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2090 | 16.2654 | 19.8163 | 24.325 | 27.7415 | 31.1535
| MindenIce Accretion2095RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2095 | 16.2654 | 19.8163 | 24.325 | 27.7415 | 31.1535
| MindenIce Accretion2100RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2100 | 16.2654 | 19.8163 | 24.325 | 27.7415 | 31.1535
| MindenWind2023RCP4.5 | Minden | Wind | RCP4.5 | 2023 | 69.5414 | 74.9134 | 80.576 | 86.2334 | 91.884
| MindenWind2025RCP4.5 | Minden | Wind | RCP4.5 | 2025 | 69.6266 | 75.0287 | 80.728 | 86.4161 | 92.0998
| MindenWind2030RCP4.5 | Minden | Wind | RCP4.5 | 2030 | 69.7118 | 75.144 | 80.88 | 86.5987 | 92.3157
| MindenWind2035RCP4.5 | Minden | Wind | RCP4.5 | 2035 | 69.797 | 75.2593 | 81.032 | 86.7813 | 92.5315
| MindenWind2040RCP4.5 | Minden | Wind | RCP4.5 | 2040 | 69.8822 | 75.3746 | 81.184 | 86.9639 | 92.7474
| MindenWind2045RCP4.5 | Minden | Wind | RCP4.5 | 2045 | 69.9674 | 75.49 | 81.336 | 87.1465 | 92.9632
| MindenWind2050RCP4.5 | Minden | Wind | RCP4.5 | 2050 | 70.0498 | 75.5949 | 81.4672 | 87.3 | 93.1407
| MindenWind2055RCP4.5 | Minden | Wind | RCP4.5 | 2055 | 70.0471 | 75.5844 | 81.4464 | 87.2709 | 93.1024
| MindenWind2060RCP4.5 | Minden | Wind | RCP4.5 | 2060 | 70.0443 | 75.574 | 81.4256 | 87.2418 | 93.0641
| MindenWind2065RCP4.5 | Minden | Wind | RCP4.5 | 2065 | 70.0415 | 75.5636 | 81.4048 | 87.2127 | 93.0258
| MindenWind2070RCP4.5 | Minden | Wind | RCP4.5 | 2070 | 70.0388 | 75.5532 | 81.384 | 87.1836 | 92.9875
| MindenWind2075RCP4.5 | Minden | Wind | RCP4.5 | 2075 | 69.9996 | 75.5024 | 81.32 | 87.1094 | 92.9009
| MindenWind2080RCP4.5 | Minden | Wind | RCP4.5 | 2080 | 69.9605 | 75.4515 | 81.256 | 87.0352 | 92.8142
| MindenWind2085RCP4.5 | Minden | Wind | RCP4.5 | 2085 | 69.9214 | 75.4007 | 81.192 | 86.961 | 92.7276
| MindenWind2090RCP4.5 | Minden | Wind | RCP4.5 | 2090 | 69.8822 | 75.3498 | 81.128 | 86.8869 | 92.641
| MindenWind2095RCP4.5 | Minden | Wind | RCP4.5 | 2095 | 69.8431 | 75.299 | 81.064 | 86.8127 | 92.5543
| MindenWind2100RCP4.5 | Minden | Wind | RCP4.5 | 2100 | 69.8039 | 75.2482 | 81 | 86.7385 | 92.4677
| MindenWind2023RCP6.0 | Minden | Wind | RCP6.0 | 2023 | 69.5414 | 74.9134 | 80.576 | 86.2334 | 91.884
| MindenWind2025RCP6.0 | Minden | Wind | RCP6.0 | 2025 | 69.6266 | 75.0287 | 80.728 | 86.4161 | 92.0998
| MindenWind2030RCP6.0 | Minden | Wind | RCP6.0 | 2030 | 69.7118 | 75.144 | 80.88 | 86.5987 | 92.3157
| MindenWind2035RCP6.0 | Minden | Wind | RCP6.0 | 2035 | 69.797 | 75.2593 | 81.032 | 86.7813 | 92.5315
| MindenWind2040RCP6.0 | Minden | Wind | RCP6.0 | 2040 | 69.8822 | 75.3746 | 81.184 | 86.9639 | 92.7474
| MindenWind2045RCP6.0 | Minden | Wind | RCP6.0 | 2045 | 69.9674 | 75.49 | 81.336 | 87.1465 | 92.9632
| MindenWind2050RCP6.0 | Minden | Wind | RCP6.0 | 2050 | 70.0498 | 75.5949 | 81.4672 | 87.3 | 93.1407
| MindenWind2055RCP6.0 | Minden | Wind | RCP6.0 | 2055 | 70.0471 | 75.5844 | 81.4464 | 87.2709 | 93.1024
| MindenWind2060RCP6.0 | Minden | Wind | RCP6.0 | 2060 | 70.0443 | 75.574 | 81.4256 | 87.2418 | 93.0641
| MindenWind2065RCP6.0 | Minden | Wind | RCP6.0 | 2065 | 70.0415 | 75.5636 | 81.4048 | 87.2127 | 93.0258
| MindenWind2070RCP6.0 | Minden | Wind | RCP6.0 | 2070 | 70.0388 | 75.5532 | 81.384 | 87.1836 | 92.9875
| MindenWind2075RCP6.0 | Minden | Wind | RCP6.0 | 2075 | 69.9801 | 75.4769 | 81.288 | 87.0723 | 92.8576
| MindenWind2080RCP6.0 | Minden | Wind | RCP6.0 | 2080 | 69.9214 | 75.4007 | 81.192 | 86.961 | 92.7276
| MindenWind2085RCP6.0 | Minden | Wind | RCP6.0 | 2085 | 69.8626 | 75.3244 | 81.096 | 86.8498 | 92.5976
| MindenWind2090RCP6.0 | Minden | Wind | RCP6.0 | 2090 | 69.7302 | 75.1465 | 80.8613 | 86.5673 | 92.267
| MindenWind2095RCP6.0 | Minden | Wind | RCP6.0 | 2095 | 69.6566 | 75.0448 | 80.7227 | 86.3961 | 92.0664
| MindenWind2100RCP6.0 | Minden | Wind | RCP6.0 | 2100 | 69.5829 | 74.9431 | 80.584 | 86.2249 | 91.8658
| MindenWind2023RCP8.5 | Minden | Wind | RCP8.5 | 2023 | 69.5414 | 74.9134 | 80.576 | 86.2334 | 91.884
| MindenWind2025RCP8.5 | Minden | Wind | RCP8.5 | 2025 | 69.7118 | 75.144 | 80.88 | 86.5987 | 92.3157
| MindenWind2030RCP8.5 | Minden | Wind | RCP8.5 | 2030 | 69.8822 | 75.3746 | 81.184 | 86.9639 | 92.7474
| MindenWind2035RCP8.5 | Minden | Wind | RCP8.5 | 2035 | 70.0526 | 75.6053 | 81.488 | 87.3291 | 93.179
| MindenWind2040RCP8.5 | Minden | Wind | RCP8.5 | 2040 | 70.048 | 75.5879 | 81.4533 | 87.2806 | 93.1152
| MindenWind2045RCP8.5 | Minden | Wind | RCP8.5 | 2045 | 70.0434 | 75.5706 | 81.4187 | 87.2321 | 93.0514
| MindenWind2050RCP8.5 | Minden | Wind | RCP8.5 | 2050 | 69.9605 | 75.4515 | 81.256 | 87.0352 | 92.8142
| MindenWind2055RCP8.5 | Minden | Wind | RCP8.5 | 2055 | 69.8822 | 75.3498 | 81.128 | 86.8869 | 92.641
| MindenWind2060RCP8.5 | Minden | Wind | RCP8.5 | 2060 | 69.7302 | 75.1465 | 80.8613 | 86.5673 | 92.267
| MindenWind2065RCP8.5 | Minden | Wind | RCP8.5 | 2065 | 69.6566 | 75.0448 | 80.7227 | 86.3961 | 92.0664
| MindenWind2070RCP8.5 | Minden | Wind | RCP8.5 | 2070 | 69.5944 | 74.9382 | 80.5547 | 86.1764 | 91.7989
| MindenWind2075RCP8.5 | Minden | Wind | RCP8.5 | 2075 | 69.6059 | 74.9332 | 80.5253 | 86.1279 | 91.732
| MindenWind2080RCP8.5 | Minden | Wind | RCP8.5 | 2080 | 69.6174 | 74.9282 | 80.496 | 86.0794 | 91.6651
| MindenWind2085RCP8.5 | Minden | Wind | RCP8.5 | 2085 | 69.8316 | 75.1961 | 80.832 | 86.4731 | 92.1166
| MindenWind2090RCP8.5 | Minden | Wind | RCP8.5 | 2090 | 70.0457 | 75.4639 | 81.168 | 86.8669 | 92.568
| MindenWind2095RCP8.5 | Minden | Wind | RCP8.5 | 2095 | 70.0457 | 75.4639 | 81.168 | 86.8669 | 92.568
| MindenWind2100RCP8.5 | Minden | Wind | RCP8.5 | 2100 | 70.0457 | 75.4639 | 81.168 | 86.8669 | 92.568
| MississaugaIce Accretion2023RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| MississaugaIce Accretion2025RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
| MississaugaIce Accretion2030RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| MississaugaIce Accretion2035RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
| MississaugaIce Accretion2040RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| MississaugaIce Accretion2045RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
| MississaugaIce Accretion2050RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
| MississaugaIce Accretion2055RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
| MississaugaIce Accretion2060RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
| MississaugaIce Accretion2065RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
| MississaugaIce Accretion2070RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
| MississaugaIce Accretion2075RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2075 | 15.5377 | 18.8894 | 23.1125 | 26.329 | 29.5313
| MississaugaIce Accretion2080RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2080 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
| MississaugaIce Accretion2085RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2085 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
| MississaugaIce Accretion2090RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2090 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
| MississaugaIce Accretion2095RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2095 | 15.3405 | 18.7511 | 23.0625 | 26.329 | 29.5942
| MississaugaIce Accretion2100RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2100 | 15.2912 | 18.7165 | 23.05 | 26.329 | 29.61
| MississaugaIce Accretion2023RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| MississaugaIce Accretion2025RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
| MississaugaIce Accretion2030RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| MississaugaIce Accretion2035RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
| MississaugaIce Accretion2040RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| MississaugaIce Accretion2045RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
| MississaugaIce Accretion2050RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
| MississaugaIce Accretion2055RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
| MississaugaIce Accretion2060RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
| MississaugaIce Accretion2065RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
| MississaugaIce Accretion2070RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
| MississaugaIce Accretion2075RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2075 | 15.513 | 18.8721 | 23.1062 | 26.329 | 29.5391
| MississaugaIce Accretion2080RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2080 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
| MississaugaIce Accretion2085RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2085 | 15.3652 | 18.7684 | 23.0688 | 26.329 | 29.5864
| MississaugaIce Accretion2090RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2090 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
| MississaugaIce Accretion2095RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2095 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
| MississaugaIce Accretion2100RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2100 | 14.2127 | 17.596 | 21.825 | 25.0577 | 28.2555
| MississaugaIce Accretion2023RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| MississaugaIce Accretion2025RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2025 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| MississaugaIce Accretion2030RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2030 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| MississaugaIce Accretion2035RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2035 | 16.6133 | 20.0652 | 24.425 | 27.7415 | 31.059
| MississaugaIce Accretion2040RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2040 | 16.2712 | 19.6848 | 23.9917 | 27.2707 | 30.5445
| MississaugaIce Accretion2045RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2045 | 15.9291 | 19.3044 | 23.5583 | 26.7998 | 30.03
| MississaugaIce Accretion2050RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2050 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
| MississaugaIce Accretion2055RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2055 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
| MississaugaIce Accretion2060RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2060 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
| MississaugaIce Accretion2065RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2065 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
| MississaugaIce Accretion2070RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2070 | 13.8125 | 17.1464 | 21.325 | 24.5022 | 27.657
| MississaugaIce Accretion2075RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2075 | 13.4124 | 16.6968 | 20.825 | 23.9466 | 27.0585
| MississaugaIce Accretion2080RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2080 | 13.0123 | 16.2473 | 20.325 | 23.391 | 26.46
| MississaugaIce Accretion2085RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2085 | 12.1338 | 15.1994 | 19.0625 | 21.9785 | 24.885
| MississaugaIce Accretion2090RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2090 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| MississaugaIce Accretion2095RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2095 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| MississaugaIce Accretion2100RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2100 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| MississaugaWind2023RCP4.5 | Mississauga | Wind | RCP4.5 | 2023 | 85.0359 | 91.6413 | 98.6076 | 105.5626 | 112.5132
| MississaugaWind2025RCP4.5 | Mississauga | Wind | RCP4.5 | 2025 | 85.0669 | 91.6868 | 98.6729 | 105.6447 | 112.6119
| MississaugaWind2030RCP4.5 | Mississauga | Wind | RCP4.5 | 2030 | 85.098 | 91.7324 | 98.7383 | 105.7268 | 112.7106
| MississaugaWind2035RCP4.5 | Mississauga | Wind | RCP4.5 | 2035 | 85.129 | 91.778 | 98.8036 | 105.809 | 112.8093
| MississaugaWind2040RCP4.5 | Mississauga | Wind | RCP4.5 | 2040 | 85.16 | 91.8235 | 98.8689 | 105.8911 | 112.908
| MississaugaWind2045RCP4.5 | Mississauga | Wind | RCP4.5 | 2045 | 85.1911 | 91.8691 | 98.9343 | 105.9733 | 113.0066
| MississaugaWind2050RCP4.5 | Mississauga | Wind | RCP4.5 | 2050 | 85.2898 | 91.9967 | 99.0996 | 106.1708 | 113.2372
| MississaugaWind2055RCP4.5 | Mississauga | Wind | RCP4.5 | 2055 | 85.3575 | 92.0787 | 99.1995 | 106.2861 | 113.369
| MississaugaWind2060RCP4.5 | Mississauga | Wind | RCP4.5 | 2060 | 85.4252 | 92.1608 | 99.2995 | 106.4014 | 113.5008
| MississaugaWind2065RCP4.5 | Mississauga | Wind | RCP4.5 | 2065 | 85.4929 | 92.2428 | 99.3994 | 106.5168 | 113.6326
| MississaugaWind2070RCP4.5 | Mississauga | Wind | RCP4.5 | 2070 | 85.5606 | 92.3248 | 99.4994 | 106.6321 | 113.7645
| MississaugaWind2075RCP4.5 | Mississauga | Wind | RCP4.5 | 2075 | 85.6537 | 92.4555 | 99.6774 | 106.8488 | 114.0214
| MississaugaWind2080RCP4.5 | Mississauga | Wind | RCP4.5 | 2080 | 85.7467 | 92.5861 | 99.8555 | 107.0656 | 114.2784
| MississaugaWind2085RCP4.5 | Mississauga | Wind | RCP4.5 | 2085 | 85.8398 | 92.7167 | 100.0335 | 107.2823 | 114.5353
| MississaugaWind2090RCP4.5 | Mississauga | Wind | RCP4.5 | 2090 | 85.9329 | 92.8474 | 100.2115 | 107.499 | 114.7923
| MississaugaWind2095RCP4.5 | Mississauga | Wind | RCP4.5 | 2095 | 86.026 | 92.978 | 100.3896 | 107.7157 | 115.0493
| MississaugaWind2100RCP4.5 | Mississauga | Wind | RCP4.5 | 2100 | 86.1191 | 93.1086 | 100.5676 | 107.9324 | 115.3062
| MississaugaWind2023RCP6.0 | Mississauga | Wind | RCP6.0 | 2023 | 85.0359 | 91.6413 | 98.6076 | 105.5626 | 112.5132
| MississaugaWind2025RCP6.0 | Mississauga | Wind | RCP6.0 | 2025 | 85.0669 | 91.6868 | 98.6729 | 105.6447 | 112.6119
| MississaugaWind2030RCP6.0 | Mississauga | Wind | RCP6.0 | 2030 | 85.098 | 91.7324 | 98.7383 | 105.7268 | 112.7106
| MississaugaWind2035RCP6.0 | Mississauga | Wind | RCP6.0 | 2035 | 85.129 | 91.778 | 98.8036 | 105.809 | 112.8093
| MississaugaWind2040RCP6.0 | Mississauga | Wind | RCP6.0 | 2040 | 85.16 | 91.8235 | 98.8689 | 105.8911 | 112.908
| MississaugaWind2045RCP6.0 | Mississauga | Wind | RCP6.0 | 2045 | 85.1911 | 91.8691 | 98.9343 | 105.9733 | 113.0066
| MississaugaWind2050RCP6.0 | Mississauga | Wind | RCP6.0 | 2050 | 85.2898 | 91.9967 | 99.0996 | 106.1708 | 113.2372
| MississaugaWind2055RCP6.0 | Mississauga | Wind | RCP6.0 | 2055 | 85.3575 | 92.0787 | 99.1995 | 106.2861 | 113.369
| MississaugaWind2060RCP6.0 | Mississauga | Wind | RCP6.0 | 2060 | 85.4252 | 92.1608 | 99.2995 | 106.4014 | 113.5008
| MississaugaWind2065RCP6.0 | Mississauga | Wind | RCP6.0 | 2065 | 85.4929 | 92.2428 | 99.3994 | 106.5168 | 113.6326
| MississaugaWind2070RCP6.0 | Mississauga | Wind | RCP6.0 | 2070 | 85.5606 | 92.3248 | 99.4994 | 106.6321 | 113.7645
| MississaugaWind2075RCP6.0 | Mississauga | Wind | RCP6.0 | 2075 | 85.7002 | 92.5208 | 99.7665 | 106.9572 | 114.1499
| MississaugaWind2080RCP6.0 | Mississauga | Wind | RCP6.0 | 2080 | 85.8398 | 92.7167 | 100.0335 | 107.2823 | 114.5353
| MississaugaWind2085RCP6.0 | Mississauga | Wind | RCP6.0 | 2085 | 85.9794 | 92.9127 | 100.3006 | 107.6073 | 114.9208
| MississaugaWind2090RCP6.0 | Mississauga | Wind | RCP6.0 | 2090 | 86.4124 | 93.4853 | 101.0478 | 108.5021 | 115.9691
| MississaugaWind2095RCP6.0 | Mississauga | Wind | RCP6.0 | 2095 | 86.7058 | 93.862 | 101.528 | 109.0719 | 116.632
| MississaugaWind2100RCP6.0 | Mississauga | Wind | RCP6.0 | 2100 | 86.9991 | 94.2388 | 102.0082 | 109.6416 | 117.2948
| MississaugaWind2023RCP8.5 | Mississauga | Wind | RCP8.5 | 2023 | 85.0359 | 91.6413 | 98.6076 | 105.5626 | 112.5132
| MississaugaWind2025RCP8.5 | Mississauga | Wind | RCP8.5 | 2025 | 85.098 | 91.7324 | 98.7383 | 105.7268 | 112.7106
| MississaugaWind2030RCP8.5 | Mississauga | Wind | RCP8.5 | 2030 | 85.16 | 91.8235 | 98.8689 | 105.8911 | 112.908
| MississaugaWind2035RCP8.5 | Mississauga | Wind | RCP8.5 | 2035 | 85.2221 | 91.9147 | 98.9996 | 106.0554 | 113.1053
| MississaugaWind2040RCP8.5 | Mississauga | Wind | RCP8.5 | 2040 | 85.3349 | 92.0514 | 99.1662 | 106.2476 | 113.325
| MississaugaWind2045RCP8.5 | Mississauga | Wind | RCP8.5 | 2045 | 85.4477 | 92.1881 | 99.3328 | 106.4399 | 113.5448
| MississaugaWind2050RCP8.5 | Mississauga | Wind | RCP8.5 | 2050 | 85.7467 | 92.5861 | 99.8555 | 107.0656 | 114.2784
| MississaugaWind2055RCP8.5 | Mississauga | Wind | RCP8.5 | 2055 | 85.9329 | 92.8474 | 100.2115 | 107.499 | 114.7923
| MississaugaWind2060RCP8.5 | Mississauga | Wind | RCP8.5 | 2060 | 86.4124 | 93.4853 | 101.0478 | 108.5021 | 115.9691
| MississaugaWind2065RCP8.5 | Mississauga | Wind | RCP8.5 | 2065 | 86.7058 | 93.862 | 101.528 | 109.0719 | 116.632
| MississaugaWind2070RCP8.5 | Mississauga | Wind | RCP8.5 | 2070 | 87.1656 | 94.4788 | 102.3414 | 110.0506 | 117.7827
| MississaugaWind2075RCP8.5 | Mississauga | Wind | RCP8.5 | 2075 | 87.332 | 94.7188 | 102.6746 | 110.4595 | 118.2705
| MississaugaWind2080RCP8.5 | Mississauga | Wind | RCP8.5 | 2080 | 87.4984 | 94.9588 | 103.0078 | 110.8685 | 118.7584
| MississaugaWind2085RCP8.5 | Mississauga | Wind | RCP8.5 | 2085 | 87.765 | 95.3051 | 103.4537 | 111.4033 | 119.384
| MississaugaWind2090RCP8.5 | Mississauga | Wind | RCP8.5 | 2090 | 88.0315 | 95.6514 | 103.8996 | 111.938 | 120.0096
| MississaugaWind2095RCP8.5 | Mississauga | Wind | RCP8.5 | 2095 | 88.0315 | 95.6514 | 103.8996 | 111.938 | 120.0096
| MississaugaWind2100RCP8.5 | Mississauga | Wind | RCP8.5 | 2100 | 88.0315 | 95.6514 | 103.8996 | 111.938 | 120.0096
| Mississauga Port CreditIce Accretion2023RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2023 | 16.7003 | 20.003 | 24.175 | 27.3742 | 30.555
| Mississauga Port CreditIce Accretion2025RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2025 | 16.6191 | 19.9165 | 24.0833 | 27.2801 | 30.4552
| Mississauga Port CreditIce Accretion2030RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2030 | 16.5379 | 19.8301 | 23.9917 | 27.1859 | 30.3555
| Mississauga Port CreditIce Accretion2035RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2035 | 16.4568 | 19.7436 | 23.9 | 27.0917 | 30.2557
| Mississauga Port CreditIce Accretion2040RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2040 | 16.3756 | 19.6572 | 23.8083 | 26.9976 | 30.156
| Mississauga Port CreditIce Accretion2045RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2045 | 16.2944 | 19.5707 | 23.7167 | 26.9034 | 30.0562
| Mississauga Port CreditIce Accretion2050RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2050 | 15.8896 | 19.1232 | 23.215 | 26.3516 | 29.4588
| Mississauga Port CreditIce Accretion2055RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2055 | 15.5661 | 18.7622 | 22.805 | 25.8939 | 28.9611
| Mississauga Port CreditIce Accretion2060RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2060 | 15.2425 | 18.4011 | 22.395 | 25.4363 | 28.4634
| Mississauga Port CreditIce Accretion2065RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2065 | 14.9189 | 18.0401 | 21.985 | 24.9786 | 27.9657
| Mississauga Port CreditIce Accretion2070RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2070 | 14.5954 | 17.679 | 21.575 | 24.521 | 27.468
| Mississauga Port CreditIce Accretion2075RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2075 | 14.491 | 17.5752 | 21.4708 | 24.4174 | 27.363
| Mississauga Port CreditIce Accretion2080RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2080 | 14.3866 | 17.4715 | 21.3667 | 24.3138 | 27.258
| Mississauga Port CreditIce Accretion2085RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2085 | 14.2822 | 17.3678 | 21.2625 | 24.2102 | 27.153
| Mississauga Port CreditIce Accretion2090RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2090 | 14.1779 | 17.264 | 21.1583 | 24.1067 | 27.048
| Mississauga Port CreditIce Accretion2095RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2095 | 14.0735 | 17.1602 | 21.0542 | 24.0031 | 26.943
| Mississauga Port CreditIce Accretion2100RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2100 | 13.9691 | 17.0565 | 20.95 | 23.8995 | 26.838
| Mississauga Port CreditIce Accretion2023RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2023 | 16.7003 | 20.003 | 24.175 | 27.3742 | 30.555
| Mississauga Port CreditIce Accretion2025RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2025 | 16.6191 | 19.9165 | 24.0833 | 27.2801 | 30.4552
| Mississauga Port CreditIce Accretion2030RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2030 | 16.5379 | 19.8301 | 23.9917 | 27.1859 | 30.3555
| Mississauga Port CreditIce Accretion2035RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2035 | 16.4568 | 19.7436 | 23.9 | 27.0917 | 30.2557
| Mississauga Port CreditIce Accretion2040RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2040 | 16.3756 | 19.6572 | 23.8083 | 26.9976 | 30.156
| Mississauga Port CreditIce Accretion2045RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2045 | 16.2944 | 19.5707 | 23.7167 | 26.9034 | 30.0562
| Mississauga Port CreditIce Accretion2050RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2050 | 15.8896 | 19.1232 | 23.215 | 26.3516 | 29.4588
| Mississauga Port CreditIce Accretion2055RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2055 | 15.5661 | 18.7622 | 22.805 | 25.8939 | 28.9611
| Mississauga Port CreditIce Accretion2060RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2060 | 15.2425 | 18.4011 | 22.395 | 25.4363 | 28.4634
| Mississauga Port CreditIce Accretion2065RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2065 | 14.9189 | 18.0401 | 21.985 | 24.9786 | 27.9657
| Mississauga Port CreditIce Accretion2070RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2070 | 14.5954 | 17.679 | 21.575 | 24.521 | 27.468
| Mississauga Port CreditIce Accretion2075RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2075 | 14.4388 | 17.5234 | 21.4187 | 24.3656 | 27.3105
| Mississauga Port CreditIce Accretion2080RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2080 | 14.2822 | 17.3678 | 21.2625 | 24.2102 | 27.153
| Mississauga Port CreditIce Accretion2085RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2085 | 14.1257 | 17.2121 | 21.1062 | 24.0549 | 26.9955
| Mississauga Port CreditIce Accretion2090RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2090 | 13.4704 | 16.4962 | 20.3 | 23.1838 | 26.0505
| Mississauga Port CreditIce Accretion2095RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2095 | 12.9717 | 15.936 | 19.65 | 22.4682 | 25.263
| Mississauga Port CreditIce Accretion2100RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2100 | 12.473 | 15.3758 | 19 | 21.7525 | 24.4755
| Mississauga Port CreditIce Accretion2023RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2023 | 16.7003 | 20.003 | 24.175 | 27.3742 | 30.555
| Mississauga Port CreditIce Accretion2025RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2025 | 16.5379 | 19.8301 | 23.9917 | 27.1859 | 30.3555
| Mississauga Port CreditIce Accretion2030RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2030 | 16.3756 | 19.6572 | 23.8083 | 26.9976 | 30.156
| Mississauga Port CreditIce Accretion2035RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2035 | 16.2132 | 19.4843 | 23.625 | 26.8092 | 29.9565
| Mississauga Port CreditIce Accretion2040RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2040 | 15.6739 | 18.8825 | 22.9417 | 26.0465 | 29.127
| Mississauga Port CreditIce Accretion2045RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2045 | 15.1347 | 18.2808 | 22.2583 | 25.2837 | 28.2975
| Mississauga Port CreditIce Accretion2050RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2050 | 14.3866 | 17.4715 | 21.3667 | 24.3138 | 27.258
| Mississauga Port CreditIce Accretion2055RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2055 | 14.1779 | 17.264 | 21.1583 | 24.1067 | 27.048
| Mississauga Port CreditIce Accretion2060RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2060 | 13.4704 | 16.4962 | 20.3 | 23.1838 | 26.0505
| Mississauga Port CreditIce Accretion2065RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2065 | 12.9717 | 15.936 | 19.65 | 22.4682 | 25.263
| Mississauga Port CreditIce Accretion2070RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2070 | 12.1831 | 15.0576 | 18.6417 | 21.3664 | 24.0555
| Mississauga Port CreditIce Accretion2075RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2075 | 11.8932 | 14.7394 | 18.2833 | 20.9803 | 23.6355
| Mississauga Port CreditIce Accretion2080RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2080 | 11.6032 | 14.4213 | 17.925 | 20.5942 | 23.2155
| Mississauga Port CreditIce Accretion2085RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2085 | 10.9944 | 13.695 | 17.0625 | 19.6196 | 22.1445
| Mississauga Port CreditIce Accretion2090RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2090 | 10.3855 | 12.9688 | 16.2 | 18.645 | 21.0735
| Mississauga Port CreditIce Accretion2095RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2095 | 10.3855 | 12.9688 | 16.2 | 18.645 | 21.0735
| Mississauga Port CreditIce Accretion2100RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2100 | 10.3855 | 12.9688 | 16.2 | 18.645 | 21.0735
| Mississauga Port CreditWind2023RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2023 | 86.3482 | 93.1564 | 100.3662 | 107.5295 | 114.6996
| Mississauga Port CreditWind2025RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2025 | 86.3282 | 93.1349 | 100.3431 | 107.5048 | 114.6733
| Mississauga Port CreditWind2030RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2030 | 86.3083 | 93.1135 | 100.32 | 107.4801 | 114.6469
| Mississauga Port CreditWind2035RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2035 | 86.2883 | 93.092 | 100.2969 | 107.4554 | 114.6206
| Mississauga Port CreditWind2040RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2040 | 86.2684 | 93.0705 | 100.2738 | 107.4307 | 114.5943
| Mississauga Port CreditWind2045RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2045 | 86.2484 | 93.049 | 100.2507 | 107.406 | 114.5679
| Mississauga Port CreditWind2050RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2050 | 86.3345 | 93.1601 | 100.3939 | 107.5762 | 114.7673
| Mississauga Port CreditWind2055RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2055 | 86.4405 | 93.2927 | 100.5602 | 107.7711 | 114.9931
| Mississauga Port CreditWind2060RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2060 | 86.5465 | 93.4253 | 100.7266 | 107.966 | 115.2188
| Mississauga Port CreditWind2065RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2065 | 86.6525 | 93.5579 | 100.8929 | 108.1609 | 115.4445
| Mississauga Port CreditWind2070RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2070 | 86.7585 | 93.6904 | 101.0592 | 108.3558 | 115.6702
| Mississauga Port CreditWind2075RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2075 | 86.8112 | 93.7626 | 101.1549 | 108.4741 | 115.8075
| Mississauga Port CreditWind2080RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2080 | 86.8639 | 93.8347 | 101.2506 | 108.5924 | 115.9448
| Mississauga Port CreditWind2085RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2085 | 86.9166 | 93.9068 | 101.3463 | 108.7107 | 116.0822
| Mississauga Port CreditWind2090RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2090 | 86.9693 | 93.9789 | 101.442 | 108.829 | 116.2195
| Mississauga Port CreditWind2095RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2095 | 87.0221 | 94.051 | 101.5377 | 108.9472 | 116.3568
| Mississauga Port CreditWind2100RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2100 | 87.0748 | 94.1232 | 101.6334 | 109.0655 | 116.4941
| Mississauga Port CreditWind2023RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2023 | 86.3482 | 93.1564 | 100.3662 | 107.5295 | 114.6996
| Mississauga Port CreditWind2025RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2025 | 86.3282 | 93.1349 | 100.3431 | 107.5048 | 114.6733
| Mississauga Port CreditWind2030RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2030 | 86.3083 | 93.1135 | 100.32 | 107.4801 | 114.6469
| Mississauga Port CreditWind2035RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2035 | 86.2883 | 93.092 | 100.2969 | 107.4554 | 114.6206
| Mississauga Port CreditWind2040RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2040 | 86.2684 | 93.0705 | 100.2738 | 107.4307 | 114.5943
| Mississauga Port CreditWind2045RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2045 | 86.2484 | 93.049 | 100.2507 | 107.406 | 114.5679
| Mississauga Port CreditWind2050RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2050 | 86.3345 | 93.1601 | 100.3939 | 107.5762 | 114.7673
| Mississauga Port CreditWind2055RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2055 | 86.4405 | 93.2927 | 100.5602 | 107.7711 | 114.9931
| Mississauga Port CreditWind2060RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2060 | 86.5465 | 93.4253 | 100.7266 | 107.966 | 115.2188
| Mississauga Port CreditWind2065RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2065 | 86.6525 | 93.5579 | 100.8929 | 108.1609 | 115.4445
| Mississauga Port CreditWind2070RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2070 | 86.7585 | 93.6904 | 101.0592 | 108.3558 | 115.6702
| Mississauga Port CreditWind2075RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2075 | 86.8376 | 93.7986 | 101.2027 | 108.5332 | 115.8762
| Mississauga Port CreditWind2080RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2080 | 86.9166 | 93.9068 | 101.3463 | 108.7107 | 116.0822
| Mississauga Port CreditWind2085RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2085 | 86.9957 | 94.015 | 101.4898 | 108.8881 | 116.2881
| Mississauga Port CreditWind2090RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2090 | 87.24 | 94.3411 | 101.9172 | 109.401 | 116.8891
| Mississauga Port CreditWind2095RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2095 | 87.4053 | 94.559 | 102.201 | 109.7364 | 117.2841
| Mississauga Port CreditWind2100RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2100 | 87.5706 | 94.7769 | 102.4848 | 110.0719 | 117.6791
| Mississauga Port CreditWind2023RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2023 | 86.3482 | 93.1564 | 100.3662 | 107.5295 | 114.6996
| Mississauga Port CreditWind2025RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2025 | 86.3083 | 93.1135 | 100.32 | 107.4801 | 114.6469
| Mississauga Port CreditWind2030RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2030 | 86.2684 | 93.0705 | 100.2738 | 107.4307 | 114.5943
| Mississauga Port CreditWind2035RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2035 | 86.2285 | 93.0275 | 100.2276 | 107.3812 | 114.5416
| Mississauga Port CreditWind2040RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2040 | 86.4051 | 93.2485 | 100.5048 | 107.7061 | 114.9178
| Mississauga Port CreditWind2045RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2045 | 86.5818 | 93.4695 | 100.782 | 108.0309 | 115.294
| Mississauga Port CreditWind2050RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2050 | 86.8639 | 93.8347 | 101.2506 | 108.5924 | 115.9448
| Mississauga Port CreditWind2055RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2055 | 86.9693 | 93.9789 | 101.442 | 108.829 | 116.2195
| Mississauga Port CreditWind2060RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2060 | 87.24 | 94.3411 | 101.9172 | 109.401 | 116.8891
| Mississauga Port CreditWind2065RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2065 | 87.4053 | 94.559 | 102.201 | 109.7364 | 117.2841
| Mississauga Port CreditWind2070RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2070 | 87.488 | 94.6971 | 102.4122 | 110.0012 | 117.6152
| Mississauga Port CreditWind2075RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2075 | 87.4053 | 94.6173 | 102.3396 | 109.9306 | 117.5512
| Mississauga Port CreditWind2080RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2080 | 87.3227 | 94.5375 | 102.267 | 109.86 | 117.4873
| Mississauga Port CreditWind2085RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2085 | 87.5535 | 94.8827 | 102.757 | 110.4744 | 118.2208
| Mississauga Port CreditWind2090RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2090 | 87.7843 | 95.228 | 103.2471 | 111.0888 | 118.9544
| Mississauga Port CreditWind2095RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2095 | 87.7843 | 95.228 | 103.2471 | 111.0888 | 118.9544
| Mississauga Port CreditWind2100RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2100 | 87.7843 | 95.228 | 103.2471 | 111.0888 | 118.9544
| MitchellIce Accretion2023RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2023 | 16.4331 | 19.7009 | 23.808 | 26.9573 | 30.0888
| MitchellIce Accretion2025RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2025 | 16.4498 | 19.7341 | 23.868 | 27.0341 | 30.1846
| MitchellIce Accretion2030RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2030 | 16.4665 | 19.7673 | 23.928 | 27.111 | 30.2803
| MitchellIce Accretion2035RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2035 | 16.4832 | 19.8005 | 23.988 | 27.1878 | 30.3761
| MitchellIce Accretion2040RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2040 | 16.4999 | 19.8337 | 24.048 | 27.2646 | 30.4718
| MitchellIce Accretion2045RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2045 | 16.5166 | 19.8669 | 24.108 | 27.3415 | 30.5676
| MitchellIce Accretion2050RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2050 | 16.4665 | 19.8523 | 24.1392 | 27.402 | 30.6634
| MitchellIce Accretion2055RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2055 | 16.3997 | 19.8045 | 24.1104 | 27.3858 | 30.6634
| MitchellIce Accretion2060RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2060 | 16.3329 | 19.7567 | 24.0816 | 27.3695 | 30.6634
| MitchellIce Accretion2065RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2065 | 16.2661 | 19.7088 | 24.0528 | 27.3532 | 30.6634
| MitchellIce Accretion2070RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2070 | 16.1993 | 19.661 | 24.024 | 27.337 | 30.6634
| MitchellIce Accretion2075RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2075 | 16.1687 | 19.6478 | 24.036 | 27.3641 | 30.7087
| MitchellIce Accretion2080RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2080 | 16.1381 | 19.6345 | 24.048 | 27.3912 | 30.7541
| MitchellIce Accretion2085RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2085 | 16.1074 | 19.6212 | 24.06 | 27.4183 | 30.7994
| MitchellIce Accretion2090RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2090 | 16.0768 | 19.6079 | 24.072 | 27.4454 | 30.8448
| MitchellIce Accretion2095RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2095 | 16.0462 | 19.5946 | 24.084 | 27.4726 | 30.8902
| MitchellIce Accretion2100RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2100 | 16.0156 | 19.5814 | 24.096 | 27.4997 | 30.9355
| MitchellIce Accretion2023RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2023 | 16.4331 | 19.7009 | 23.808 | 26.9573 | 30.0888
| MitchellIce Accretion2025RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2025 | 16.4498 | 19.7341 | 23.868 | 27.0341 | 30.1846
| MitchellIce Accretion2030RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2030 | 16.4665 | 19.7673 | 23.928 | 27.111 | 30.2803
| MitchellIce Accretion2035RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2035 | 16.4832 | 19.8005 | 23.988 | 27.1878 | 30.3761
| MitchellIce Accretion2040RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2040 | 16.4999 | 19.8337 | 24.048 | 27.2646 | 30.4718
| MitchellIce Accretion2045RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2045 | 16.5166 | 19.8669 | 24.108 | 27.3415 | 30.5676
| MitchellIce Accretion2050RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2050 | 16.4665 | 19.8523 | 24.1392 | 27.402 | 30.6634
| MitchellIce Accretion2055RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2055 | 16.3997 | 19.8045 | 24.1104 | 27.3858 | 30.6634
| MitchellIce Accretion2060RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2060 | 16.3329 | 19.7567 | 24.0816 | 27.3695 | 30.6634
| MitchellIce Accretion2065RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2065 | 16.2661 | 19.7088 | 24.0528 | 27.3532 | 30.6634
| MitchellIce Accretion2070RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2070 | 16.1993 | 19.661 | 24.024 | 27.337 | 30.6634
| MitchellIce Accretion2075RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2075 | 16.1534 | 19.6411 | 24.042 | 27.3776 | 30.7314
| MitchellIce Accretion2080RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2080 | 16.1074 | 19.6212 | 24.06 | 27.4183 | 30.7994
| MitchellIce Accretion2085RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2085 | 16.0615 | 19.6013 | 24.078 | 27.459 | 30.8675
| MitchellIce Accretion2090RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2090 | 15.8152 | 19.3822 | 23.888 | 27.2918 | 30.7138
| MitchellIce Accretion2095RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2095 | 15.6148 | 19.183 | 23.68 | 27.0838 | 30.492
| MitchellIce Accretion2100RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2100 | 15.4144 | 18.9838 | 23.472 | 26.8759 | 30.2702
| MitchellIce Accretion2023RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2023 | 16.4331 | 19.7009 | 23.808 | 26.9573 | 30.0888
| MitchellIce Accretion2025RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2025 | 16.4665 | 19.7673 | 23.928 | 27.111 | 30.2803
| MitchellIce Accretion2030RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2030 | 16.4999 | 19.8337 | 24.048 | 27.2646 | 30.4718
| MitchellIce Accretion2035RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2035 | 16.5333 | 19.9001 | 24.168 | 27.4183 | 30.6634
| MitchellIce Accretion2040RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2040 | 16.422 | 19.8204 | 24.12 | 27.3912 | 30.6634
| MitchellIce Accretion2045RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2045 | 16.3106 | 19.7407 | 24.072 | 27.3641 | 30.6634
| MitchellIce Accretion2050RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2050 | 16.1381 | 19.6345 | 24.048 | 27.3912 | 30.7541
| MitchellIce Accretion2055RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2055 | 16.0768 | 19.6079 | 24.072 | 27.4454 | 30.8448
| MitchellIce Accretion2060RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2060 | 15.8152 | 19.3822 | 23.888 | 27.2918 | 30.7138
| MitchellIce Accretion2065RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2065 | 15.6148 | 19.183 | 23.68 | 27.0838 | 30.492
| MitchellIce Accretion2070RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2070 | 15.0525 | 18.5787 | 23.016 | 26.3787 | 29.7259
| MitchellIce Accretion2075RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2075 | 14.6907 | 18.1737 | 22.56 | 25.8815 | 29.1816
| MitchellIce Accretion2080RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2080 | 14.3289 | 17.7686 | 22.104 | 25.3843 | 28.6373
| MitchellIce Accretion2085RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2085 | 13.5773 | 16.8822 | 21.048 | 24.2046 | 27.337
| MitchellIce Accretion2090RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2090 | 12.8258 | 15.9958 | 19.992 | 23.0249 | 26.0366
| MitchellIce Accretion2095RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2095 | 12.8258 | 15.9958 | 19.992 | 23.0249 | 26.0366
| MitchellIce Accretion2100RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2100 | 12.8258 | 15.9958 | 19.992 | 23.0249 | 26.0366
| MitchellWind2023RCP4.5 | Mitchell | Wind | RCP4.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| MitchellWind2025RCP4.5 | Mitchell | Wind | RCP4.5 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
| MitchellWind2030RCP4.5 | Mitchell | Wind | RCP4.5 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| MitchellWind2035RCP4.5 | Mitchell | Wind | RCP4.5 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
| MitchellWind2040RCP4.5 | Mitchell | Wind | RCP4.5 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| MitchellWind2045RCP4.5 | Mitchell | Wind | RCP4.5 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
| MitchellWind2050RCP4.5 | Mitchell | Wind | RCP4.5 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
| MitchellWind2055RCP4.5 | Mitchell | Wind | RCP4.5 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
| MitchellWind2060RCP4.5 | Mitchell | Wind | RCP4.5 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
| MitchellWind2065RCP4.5 | Mitchell | Wind | RCP4.5 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
| MitchellWind2070RCP4.5 | Mitchell | Wind | RCP4.5 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
| MitchellWind2075RCP4.5 | Mitchell | Wind | RCP4.5 | 2075 | 86.3504 | 93.3577 | 100.8387 | 108.226 | 115.6228
| MitchellWind2080RCP4.5 | Mitchell | Wind | RCP4.5 | 2080 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
| MitchellWind2085RCP4.5 | Mitchell | Wind | RCP4.5 | 2085 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
| MitchellWind2090RCP4.5 | Mitchell | Wind | RCP4.5 | 2090 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
| MitchellWind2095RCP4.5 | Mitchell | Wind | RCP4.5 | 2095 | 86.7678 | 93.9167 | 101.5705 | 109.1068 | 116.6655
| MitchellWind2100RCP4.5 | Mitchell | Wind | RCP4.5 | 2100 | 86.8722 | 94.0565 | 101.7534 | 109.327 | 116.9262
| MitchellWind2023RCP6.0 | Mitchell | Wind | RCP6.0 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| MitchellWind2025RCP6.0 | Mitchell | Wind | RCP6.0 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
| MitchellWind2030RCP6.0 | Mitchell | Wind | RCP6.0 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| MitchellWind2035RCP6.0 | Mitchell | Wind | RCP6.0 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
| MitchellWind2040RCP6.0 | Mitchell | Wind | RCP6.0 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| MitchellWind2045RCP6.0 | Mitchell | Wind | RCP6.0 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
| MitchellWind2050RCP6.0 | Mitchell | Wind | RCP6.0 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
| MitchellWind2055RCP6.0 | Mitchell | Wind | RCP6.0 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
| MitchellWind2060RCP6.0 | Mitchell | Wind | RCP6.0 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
| MitchellWind2065RCP6.0 | Mitchell | Wind | RCP6.0 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
| MitchellWind2070RCP6.0 | Mitchell | Wind | RCP6.0 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
| MitchellWind2075RCP6.0 | Mitchell | Wind | RCP6.0 | 2075 | 86.4026 | 93.4276 | 100.9302 | 108.3361 | 115.7531
| MitchellWind2080RCP6.0 | Mitchell | Wind | RCP6.0 | 2080 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
| MitchellWind2085RCP6.0 | Mitchell | Wind | RCP6.0 | 2085 | 86.7157 | 93.8469 | 101.479 | 108.9967 | 116.5351
| MitchellWind2090RCP6.0 | Mitchell | Wind | RCP6.0 | 2090 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
| MitchellWind2095RCP6.0 | Mitchell | Wind | RCP6.0 | 2095 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
| MitchellWind2100RCP6.0 | Mitchell | Wind | RCP6.0 | 2100 | 87.7861 | 95.1502 | 103.0568 | 110.8265 | 118.6131
| MitchellWind2023RCP8.5 | Mitchell | Wind | RCP8.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| MitchellWind2025RCP8.5 | Mitchell | Wind | RCP8.5 | 2025 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| MitchellWind2030RCP8.5 | Mitchell | Wind | RCP8.5 | 2030 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| MitchellWind2035RCP8.5 | Mitchell | Wind | RCP8.5 | 2035 | 86.0768 | 93.0084 | 100.3912 | 107.7017 | 115.0269
| MitchellWind2040RCP8.5 | Mitchell | Wind | RCP8.5 | 2040 | 86.1332 | 93.0782 | 100.4794 | 107.8031 | 115.1386
| MitchellWind2045RCP8.5 | Mitchell | Wind | RCP8.5 | 2045 | 86.1896 | 93.1481 | 100.5676 | 107.9044 | 115.2504
| MitchellWind2050RCP8.5 | Mitchell | Wind | RCP8.5 | 2050 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
| MitchellWind2055RCP8.5 | Mitchell | Wind | RCP8.5 | 2055 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
| MitchellWind2060RCP8.5 | Mitchell | Wind | RCP8.5 | 2060 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
| MitchellWind2065RCP8.5 | Mitchell | Wind | RCP8.5 | 2065 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
| MitchellWind2070RCP8.5 | Mitchell | Wind | RCP8.5 | 2070 | 88.0541 | 95.5026 | 103.5207 | 111.3788 | 119.2611
| MitchellWind2075RCP8.5 | Mitchell | Wind | RCP8.5 | 2075 | 88.322 | 95.855 | 103.9845 | 111.9311 | 119.9091
| MitchellWind2080RCP8.5 | Mitchell | Wind | RCP8.5 | 2080 | 88.59 | 96.2074 | 104.4484 | 112.4833 | 120.5571
| MitchellWind2085RCP8.5 | Mitchell | Wind | RCP8.5 | 2085 | 88.9454 | 96.6585 | 105.0217 | 113.1649 | 121.3447
| MitchellWind2090RCP8.5 | Mitchell | Wind | RCP8.5 | 2090 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| MitchellWind2095RCP8.5 | Mitchell | Wind | RCP8.5 | 2095 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| MitchellWind2100RCP8.5 | Mitchell | Wind | RCP8.5 | 2100 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| MoosoneeIce Accretion2023RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2023 | 10.6256 | 12.6492 | 15.195 | 17.1534 | 19.1079
| MoosoneeIce Accretion2025RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2025 | 10.6969 | 12.7363 | 15.305 | 17.2805 | 19.2528
| MoosoneeIce Accretion2030RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2030 | 10.7682 | 12.8235 | 15.415 | 17.4076 | 19.3977
| MoosoneeIce Accretion2035RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2035 | 10.8395 | 12.9107 | 15.525 | 17.5348 | 19.5426
| MoosoneeIce Accretion2040RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2040 | 10.9109 | 12.9978 | 15.635 | 17.6619 | 19.6875
| MoosoneeIce Accretion2045RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2045 | 10.9822 | 13.0849 | 15.745 | 17.789 | 19.8324
| MoosoneeIce Accretion2050RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2050 | 11.0368 | 13.1646 | 15.858 | 17.9263 | 19.9962
| MoosoneeIce Accretion2055RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2055 | 11.0201 | 13.1572 | 15.861 | 17.9365 | 20.0151
| MoosoneeIce Accretion2060RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2060 | 11.0034 | 13.1497 | 15.864 | 17.9467 | 20.034
| MoosoneeIce Accretion2065RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2065 | 10.9867 | 13.1422 | 15.867 | 17.9568 | 20.0529
| MoosoneeIce Accretion2070RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2070 | 10.97 | 13.1347 | 15.87 | 17.967 | 20.0718
| MoosoneeIce Accretion2075RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2075 | 10.8865 | 13.0455 | 15.775 | 17.8681 | 19.9647
| MoosoneeIce Accretion2080RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2080 | 10.803 | 12.9563 | 15.68 | 17.7692 | 19.8576
| MoosoneeIce Accretion2085RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2085 | 10.7195 | 12.8671 | 15.585 | 17.6704 | 19.7505
| MoosoneeIce Accretion2090RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2090 | 10.636 | 12.7778 | 15.49 | 17.5715 | 19.6434
| MoosoneeIce Accretion2095RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2095 | 10.5525 | 12.6886 | 15.395 | 17.4726 | 19.5363
| MoosoneeIce Accretion2100RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2100 | 10.469 | 12.5994 | 15.3 | 17.3737 | 19.4292
| MoosoneeIce Accretion2023RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2023 | 10.6256 | 12.6492 | 15.195 | 17.1534 | 19.1079
| MoosoneeIce Accretion2025RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2025 | 10.6969 | 12.7363 | 15.305 | 17.2805 | 19.2528
| MoosoneeIce Accretion2030RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2030 | 10.7682 | 12.8235 | 15.415 | 17.4076 | 19.3977
| MoosoneeIce Accretion2035RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2035 | 10.8395 | 12.9107 | 15.525 | 17.5348 | 19.5426
| MoosoneeIce Accretion2040RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2040 | 10.9109 | 12.9978 | 15.635 | 17.6619 | 19.6875
| MoosoneeIce Accretion2045RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2045 | 10.9822 | 13.0849 | 15.745 | 17.789 | 19.8324
| MoosoneeIce Accretion2050RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2050 | 11.0368 | 13.1646 | 15.858 | 17.9263 | 19.9962
| MoosoneeIce Accretion2055RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2055 | 11.0201 | 13.1572 | 15.861 | 17.9365 | 20.0151
| MoosoneeIce Accretion2060RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2060 | 11.0034 | 13.1497 | 15.864 | 17.9467 | 20.034
| MoosoneeIce Accretion2065RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2065 | 10.9867 | 13.1422 | 15.867 | 17.9568 | 20.0529
| MoosoneeIce Accretion2070RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2070 | 10.97 | 13.1347 | 15.87 | 17.967 | 20.0718
| MoosoneeIce Accretion2075RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2075 | 10.8448 | 13.0009 | 15.7275 | 17.8187 | 19.9111
| MoosoneeIce Accretion2080RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2080 | 10.7195 | 12.8671 | 15.585 | 17.6704 | 19.7505
| MoosoneeIce Accretion2085RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2085 | 10.5943 | 12.7332 | 15.4425 | 17.5221 | 19.5898
| MoosoneeIce Accretion2090RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2090 | 10.1628 | 12.2549 | 14.905 | 16.9387 | 18.9504
| MoosoneeIce Accretion2095RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2095 | 9.8567 | 11.9105 | 14.51 | 16.5037 | 18.4716
| MoosoneeIce Accretion2100RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2100 | 9.5505 | 11.5661 | 14.115 | 16.0686 | 17.9928
| MoosoneeIce Accretion2023RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2023 | 10.6256 | 12.6492 | 15.195 | 17.1534 | 19.1079
| MoosoneeIce Accretion2025RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2025 | 10.7682 | 12.8235 | 15.415 | 17.4076 | 19.3977
| MoosoneeIce Accretion2030RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2030 | 10.9109 | 12.9978 | 15.635 | 17.6619 | 19.6875
| MoosoneeIce Accretion2035RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2035 | 11.0535 | 13.1721 | 15.855 | 17.9161 | 19.9773
| MoosoneeIce Accretion2040RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2040 | 11.0257 | 13.1596 | 15.86 | 17.9331 | 20.0088
| MoosoneeIce Accretion2045RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2045 | 10.9978 | 13.1472 | 15.865 | 17.95 | 20.0403
| MoosoneeIce Accretion2050RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2050 | 10.803 | 12.9563 | 15.68 | 17.7692 | 19.8576
| MoosoneeIce Accretion2055RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2055 | 10.636 | 12.7778 | 15.49 | 17.5715 | 19.6434
| MoosoneeIce Accretion2060RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2060 | 10.1628 | 12.2549 | 14.905 | 16.9387 | 18.9504
| MoosoneeIce Accretion2065RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2065 | 9.8567 | 11.9105 | 14.51 | 16.5037 | 18.4716
| MoosoneeIce Accretion2070RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2070 | 9.2756 | 11.2631 | 13.775 | 15.6957 | 17.5959
| MoosoneeIce Accretion2075RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2075 | 9.0008 | 10.9602 | 13.435 | 15.3228 | 17.199
| MoosoneeIce Accretion2080RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2080 | 8.7259 | 10.6572 | 13.095 | 14.9499 | 16.8021
| MoosoneeIce Accretion2085RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2085 | 8.2823 | 10.1592 | 12.525 | 14.3312 | 16.1217
| MoosoneeIce Accretion2090RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2090 | 7.8387 | 9.6612 | 11.955 | 13.7125 | 15.4413
| MoosoneeIce Accretion2095RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2095 | 7.8387 | 9.6612 | 11.955 | 13.7125 | 15.4413
| MoosoneeIce Accretion2100RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2100 | 7.8387 | 9.6612 | 11.955 | 13.7125 | 15.4413
| MoosoneeWind2023RCP4.5 | Moosonee | Wind | RCP4.5 | 2023 | 77.2022 | 83.2886 | 89.7248 | 96.1279 | 102.5371
| MoosoneeWind2025RCP4.5 | Moosonee | Wind | RCP4.5 | 2025 | 77.315 | 83.4195 | 89.8803 | 96.3037 | 102.7327
| MoosoneeWind2030RCP4.5 | Moosonee | Wind | RCP4.5 | 2030 | 77.4277 | 83.5505 | 90.0357 | 96.4795 | 102.9283
| MoosoneeWind2035RCP4.5 | Moosonee | Wind | RCP4.5 | 2035 | 77.5404 | 83.6814 | 90.1912 | 96.6552 | 103.1239
| MoosoneeWind2040RCP4.5 | Moosonee | Wind | RCP4.5 | 2040 | 77.6531 | 83.8123 | 90.3467 | 96.831 | 103.3196
| MoosoneeWind2045RCP4.5 | Moosonee | Wind | RCP4.5 | 2045 | 77.7658 | 83.9433 | 90.5021 | 97.0068 | 103.5152
| MoosoneeWind2050RCP4.5 | Moosonee | Wind | RCP4.5 | 2050 | 77.9287 | 84.1282 | 90.7122 | 97.239 | 103.771
| MoosoneeWind2055RCP4.5 | Moosonee | Wind | RCP4.5 | 2055 | 77.9788 | 84.1823 | 90.7667 | 97.2955 | 103.8312
| MoosoneeWind2060RCP4.5 | Moosonee | Wind | RCP4.5 | 2060 | 78.029 | 84.2363 | 90.8213 | 97.352 | 103.8914
| MoosoneeWind2065RCP4.5 | Moosonee | Wind | RCP4.5 | 2065 | 78.0791 | 84.2903 | 90.8758 | 97.4085 | 103.9516
| MoosoneeWind2070RCP4.5 | Moosonee | Wind | RCP4.5 | 2070 | 78.1293 | 84.3443 | 90.9304 | 97.465 | 104.0118
| MoosoneeWind2075RCP4.5 | Moosonee | Wind | RCP4.5 | 2075 | 78.1343 | 84.3348 | 90.9025 | 97.4226 | 103.9549
| MoosoneeWind2080RCP4.5 | Moosonee | Wind | RCP4.5 | 2080 | 78.1394 | 84.3252 | 90.8747 | 97.3803 | 103.8981
| MoosoneeWind2085RCP4.5 | Moosonee | Wind | RCP4.5 | 2085 | 78.1445 | 84.3157 | 90.8468 | 97.3379 | 103.8412
| MoosoneeWind2090RCP4.5 | Moosonee | Wind | RCP4.5 | 2090 | 78.1495 | 84.3061 | 90.8189 | 97.2955 | 103.7844
| MoosoneeWind2095RCP4.5 | Moosonee | Wind | RCP4.5 | 2095 | 78.1546 | 84.2966 | 90.7911 | 97.2532 | 103.7275
| MoosoneeWind2100RCP4.5 | Moosonee | Wind | RCP4.5 | 2100 | 78.1597 | 84.287 | 90.7632 | 97.2108 | 103.6707
| MoosoneeWind2023RCP6.0 | Moosonee | Wind | RCP6.0 | 2023 | 77.2022 | 83.2886 | 89.7248 | 96.1279 | 102.5371
| MoosoneeWind2025RCP6.0 | Moosonee | Wind | RCP6.0 | 2025 | 77.315 | 83.4195 | 89.8803 | 96.3037 | 102.7327
| MoosoneeWind2030RCP6.0 | Moosonee | Wind | RCP6.0 | 2030 | 77.4277 | 83.5505 | 90.0357 | 96.4795 | 102.9283
| MoosoneeWind2035RCP6.0 | Moosonee | Wind | RCP6.0 | 2035 | 77.5404 | 83.6814 | 90.1912 | 96.6552 | 103.1239
| MoosoneeWind2040RCP6.0 | Moosonee | Wind | RCP6.0 | 2040 | 77.6531 | 83.8123 | 90.3467 | 96.831 | 103.3196
| MoosoneeWind2045RCP6.0 | Moosonee | Wind | RCP6.0 | 2045 | 77.7658 | 83.9433 | 90.5021 | 97.0068 | 103.5152
| MoosoneeWind2050RCP6.0 | Moosonee | Wind | RCP6.0 | 2050 | 77.9287 | 84.1282 | 90.7122 | 97.239 | 103.771
| MoosoneeWind2055RCP6.0 | Moosonee | Wind | RCP6.0 | 2055 | 77.9788 | 84.1823 | 90.7667 | 97.2955 | 103.8312
| MoosoneeWind2060RCP6.0 | Moosonee | Wind | RCP6.0 | 2060 | 78.029 | 84.2363 | 90.8213 | 97.352 | 103.8914
| MoosoneeWind2065RCP6.0 | Moosonee | Wind | RCP6.0 | 2065 | 78.0791 | 84.2903 | 90.8758 | 97.4085 | 103.9516
| MoosoneeWind2070RCP6.0 | Moosonee | Wind | RCP6.0 | 2070 | 78.1293 | 84.3443 | 90.9304 | 97.465 | 104.0118
| MoosoneeWind2075RCP6.0 | Moosonee | Wind | RCP6.0 | 2075 | 78.1369 | 84.33 | 90.8886 | 97.4015 | 103.9265
| MoosoneeWind2080RCP6.0 | Moosonee | Wind | RCP6.0 | 2080 | 78.1445 | 84.3157 | 90.8468 | 97.3379 | 103.8412
| MoosoneeWind2085RCP6.0 | Moosonee | Wind | RCP6.0 | 2085 | 78.1521 | 84.3013 | 90.805 | 97.2743 | 103.756
| MoosoneeWind2090RCP6.0 | Moosonee | Wind | RCP6.0 | 2090 | 78.3674 | 84.5134 | 91.0096 | 97.4776 | 103.9549
| MoosoneeWind2095RCP6.0 | Moosonee | Wind | RCP6.0 | 2095 | 78.5751 | 84.7399 | 91.256 | 97.7444 | 104.2392
| MoosoneeWind2100RCP6.0 | Moosonee | Wind | RCP6.0 | 2100 | 78.7828 | 84.9663 | 91.5024 | 98.0111 | 104.5234
| MoosoneeWind2023RCP8.5 | Moosonee | Wind | RCP8.5 | 2023 | 77.2022 | 83.2886 | 89.7248 | 96.1279 | 102.5371
| MoosoneeWind2025RCP8.5 | Moosonee | Wind | RCP8.5 | 2025 | 77.4277 | 83.5505 | 90.0357 | 96.4795 | 102.9283
| MoosoneeWind2030RCP8.5 | Moosonee | Wind | RCP8.5 | 2030 | 77.6531 | 83.8123 | 90.3467 | 96.831 | 103.3196
| MoosoneeWind2035RCP8.5 | Moosonee | Wind | RCP8.5 | 2035 | 77.8785 | 84.0742 | 90.6576 | 97.1825 | 103.7108
| MoosoneeWind2040RCP8.5 | Moosonee | Wind | RCP8.5 | 2040 | 77.9621 | 84.1643 | 90.7485 | 97.2767 | 103.8111
| MoosoneeWind2045RCP8.5 | Moosonee | Wind | RCP8.5 | 2045 | 78.0457 | 84.2543 | 90.8395 | 97.3709 | 103.9115
| MoosoneeWind2050RCP8.5 | Moosonee | Wind | RCP8.5 | 2050 | 78.1394 | 84.3252 | 90.8747 | 97.3803 | 103.8981
| MoosoneeWind2055RCP8.5 | Moosonee | Wind | RCP8.5 | 2055 | 78.1495 | 84.3061 | 90.8189 | 97.2955 | 103.7844
| MoosoneeWind2060RCP8.5 | Moosonee | Wind | RCP8.5 | 2060 | 78.3674 | 84.5134 | 91.0096 | 97.4776 | 103.9549
| MoosoneeWind2065RCP8.5 | Moosonee | Wind | RCP8.5 | 2065 | 78.5751 | 84.7399 | 91.256 | 97.7444 | 104.2392
| MoosoneeWind2070RCP8.5 | Moosonee | Wind | RCP8.5 | 2070 | 78.8157 | 84.9772 | 91.4789 | 97.9641 | 104.4498
| MoosoneeWind2075RCP8.5 | Moosonee | Wind | RCP8.5 | 2075 | 78.8486 | 84.9881 | 91.4555 | 97.917 | 104.3763
| MoosoneeWind2080RCP8.5 | Moosonee | Wind | RCP8.5 | 2080 | 78.8815 | 84.999 | 91.432 | 97.8699 | 104.3027
| MoosoneeWind2085RCP8.5 | Moosonee | Wind | RCP8.5 | 2085 | 78.9385 | 85.0481 | 91.4716 | 97.8982 | 104.3228
| MoosoneeWind2090RCP8.5 | Moosonee | Wind | RCP8.5 | 2090 | 78.9955 | 85.0972 | 91.5112 | 97.9264 | 104.3428
| MoosoneeWind2095RCP8.5 | Moosonee | Wind | RCP8.5 | 2095 | 78.9955 | 85.0972 | 91.5112 | 97.9264 | 104.3428
| MoosoneeWind2100RCP8.5 | Moosonee | Wind | RCP8.5 | 2100 | 78.9955 | 85.0972 | 91.5112 | 97.9264 | 104.3428
| MorrisburgIce Accretion2023RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2023 | 21.0215 | 25.0743 | 30.21 | 34.1373 | 38.0646
| MorrisburgIce Accretion2025RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2025 | 21.0737 | 25.1531 | 30.325 | 34.2842 | 38.2347
| MorrisburgIce Accretion2030RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2030 | 21.1259 | 25.232 | 30.44 | 34.4311 | 38.4048
| MorrisburgIce Accretion2035RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2035 | 21.1781 | 25.3108 | 30.555 | 34.578 | 38.5749
| MorrisburgIce Accretion2040RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2040 | 21.2303 | 25.3897 | 30.67 | 34.7249 | 38.745
| MorrisburgIce Accretion2045RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2045 | 21.2825 | 25.4686 | 30.785 | 34.8718 | 38.9151
| MorrisburgIce Accretion2050RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2050 | 21.3054 | 25.5325 | 30.9 | 35.0187 | 39.1003
| MorrisburgIce Accretion2055RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2055 | 21.2762 | 25.5175 | 30.9 | 35.0187 | 39.1154
| MorrisburgIce Accretion2060RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2060 | 21.247 | 25.5026 | 30.9 | 35.0187 | 39.1306
| MorrisburgIce Accretion2065RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2065 | 21.2177 | 25.4876 | 30.9 | 35.0187 | 39.1457
| MorrisburgIce Accretion2070RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2070 | 21.1885 | 25.4727 | 30.9 | 35.0187 | 39.1608
| MorrisburgIce Accretion2075RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2075 | 21.2859 | 25.6138 | 31.1 | 35.2616 | 39.4443
| MorrisburgIce Accretion2080RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2080 | 21.3834 | 25.7549 | 31.3 | 35.5046 | 39.7278
| MorrisburgIce Accretion2085RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2085 | 21.4808 | 25.896 | 31.5 | 35.7475 | 40.0113
| MorrisburgIce Accretion2090RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2090 | 21.5782 | 26.0371 | 31.7 | 35.9905 | 40.2948
| MorrisburgIce Accretion2095RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2095 | 21.6756 | 26.1782 | 31.9 | 36.2334 | 40.5783
| MorrisburgIce Accretion2100RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2100 | 21.773 | 26.3193 | 32.1 | 36.4764 | 40.8618
| MorrisburgIce Accretion2023RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2023 | 21.0215 | 25.0743 | 30.21 | 34.1373 | 38.0646
| MorrisburgIce Accretion2025RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2025 | 21.0737 | 25.1531 | 30.325 | 34.2842 | 38.2347
| MorrisburgIce Accretion2030RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2030 | 21.1259 | 25.232 | 30.44 | 34.4311 | 38.4048
| MorrisburgIce Accretion2035RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2035 | 21.1781 | 25.3108 | 30.555 | 34.578 | 38.5749
| MorrisburgIce Accretion2040RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2040 | 21.2303 | 25.3897 | 30.67 | 34.7249 | 38.745
| MorrisburgIce Accretion2045RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2045 | 21.2825 | 25.4686 | 30.785 | 34.8718 | 38.9151
| MorrisburgIce Accretion2050RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2050 | 21.3054 | 25.5325 | 30.9 | 35.0187 | 39.1003
| MorrisburgIce Accretion2055RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2055 | 21.2762 | 25.5175 | 30.9 | 35.0187 | 39.1154
| MorrisburgIce Accretion2060RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2060 | 21.247 | 25.5026 | 30.9 | 35.0187 | 39.1306
| MorrisburgIce Accretion2065RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2065 | 21.2177 | 25.4876 | 30.9 | 35.0187 | 39.1457
| MorrisburgIce Accretion2070RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2070 | 21.1885 | 25.4727 | 30.9 | 35.0187 | 39.1608
| MorrisburgIce Accretion2075RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2075 | 21.3346 | 25.6843 | 31.2 | 35.3831 | 39.586
| MorrisburgIce Accretion2080RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2080 | 21.4808 | 25.896 | 31.5 | 35.7475 | 40.0113
| MorrisburgIce Accretion2085RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2085 | 21.6269 | 26.1076 | 31.8 | 36.112 | 40.4365
| MorrisburgIce Accretion2090RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2090 | 21.6269 | 26.1948 | 31.98 | 36.3634 | 40.761
| MorrisburgIce Accretion2095RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2095 | 21.4808 | 26.0703 | 31.86 | 36.2504 | 40.6602
| MorrisburgIce Accretion2100RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2100 | 21.3346 | 25.9458 | 31.74 | 36.1374 | 40.5594
| MorrisburgIce Accretion2023RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2023 | 21.0215 | 25.0743 | 30.21 | 34.1373 | 38.0646
| MorrisburgIce Accretion2025RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2025 | 21.1259 | 25.232 | 30.44 | 34.4311 | 38.4048
| MorrisburgIce Accretion2030RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2030 | 21.2303 | 25.3897 | 30.67 | 34.7249 | 38.745
| MorrisburgIce Accretion2035RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2035 | 21.3346 | 25.5474 | 30.9 | 35.0187 | 39.0852
| MorrisburgIce Accretion2040RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2040 | 21.2859 | 25.5225 | 30.9 | 35.0187 | 39.1104
| MorrisburgIce Accretion2045RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2045 | 21.2372 | 25.4976 | 30.9 | 35.0187 | 39.1356
| MorrisburgIce Accretion2050RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2050 | 21.3834 | 25.7549 | 31.3 | 35.5046 | 39.7278
| MorrisburgIce Accretion2055RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2055 | 21.5782 | 26.0371 | 31.7 | 35.9905 | 40.2948
| MorrisburgIce Accretion2060RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2060 | 21.6269 | 26.1948 | 31.98 | 36.3634 | 40.761
| MorrisburgIce Accretion2065RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2065 | 21.4808 | 26.0703 | 31.86 | 36.2504 | 40.6602
| MorrisburgIce Accretion2070RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2070 | 21.0563 | 25.6387 | 31.4 | 35.7758 | 40.1688
| MorrisburgIce Accretion2075RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2075 | 20.778 | 25.3316 | 31.06 | 35.4142 | 39.7782
| MorrisburgIce Accretion2080RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2080 | 20.4996 | 25.0245 | 30.72 | 35.0526 | 39.3876
| MorrisburgIce Accretion2085RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2085 | 19.6333 | 24.0036 | 29.52 | 33.6966 | 37.8756
| MorrisburgIce Accretion2090RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2090 | 18.767 | 22.9827 | 28.32 | 32.3406 | 36.3636
| MorrisburgIce Accretion2095RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2095 | 18.767 | 22.9827 | 28.32 | 32.3406 | 36.3636
| MorrisburgIce Accretion2100RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2100 | 18.767 | 22.9827 | 28.32 | 32.3406 | 36.3636
| MorrisburgWind2023RCP4.5 | Morrisburg | Wind | RCP4.5 | 2023 | 80.9302 | 87.2425 | 93.8928 | 100.535 | 107.165
| MorrisburgWind2025RCP4.5 | Morrisburg | Wind | RCP4.5 | 2025 | 80.9731 | 87.2828 | 93.9316 | 100.5731 | 107.2021
| MorrisburgWind2030RCP4.5 | Morrisburg | Wind | RCP4.5 | 2030 | 81.0159 | 87.3232 | 93.9703 | 100.6112 | 107.2392
| MorrisburgWind2035RCP4.5 | Morrisburg | Wind | RCP4.5 | 2035 | 81.0587 | 87.3635 | 94.0091 | 100.6494 | 107.2763
| MorrisburgWind2040RCP4.5 | Morrisburg | Wind | RCP4.5 | 2040 | 81.1016 | 87.4039 | 94.0478 | 100.6875 | 107.3134
| MorrisburgWind2045RCP4.5 | Morrisburg | Wind | RCP4.5 | 2045 | 81.1444 | 87.4443 | 94.0866 | 100.7257 | 107.3506
| MorrisburgWind2050RCP4.5 | Morrisburg | Wind | RCP4.5 | 2050 | 81.1631 | 87.4552 | 94.09 | 100.72 | 107.3389
| MorrisburgWind2055RCP4.5 | Morrisburg | Wind | RCP4.5 | 2055 | 81.139 | 87.4258 | 94.0546 | 100.6763 | 107.2901
| MorrisburgWind2060RCP4.5 | Morrisburg | Wind | RCP4.5 | 2060 | 81.1149 | 87.3964 | 94.0193 | 100.6325 | 107.2414
| MorrisburgWind2065RCP4.5 | Morrisburg | Wind | RCP4.5 | 2065 | 81.0908 | 87.367 | 93.9839 | 100.5887 | 107.1926
| MorrisburgWind2070RCP4.5 | Morrisburg | Wind | RCP4.5 | 2070 | 81.0668 | 87.3376 | 93.9486 | 100.5449 | 107.1438
| MorrisburgWind2075RCP4.5 | Morrisburg | Wind | RCP4.5 | 2075 | 81.0467 | 87.316 | 93.9253 | 100.5217 | 107.1191
| MorrisburgWind2080RCP4.5 | Morrisburg | Wind | RCP4.5 | 2080 | 81.0266 | 87.2944 | 93.9021 | 100.4985 | 107.0943
| MorrisburgWind2085RCP4.5 | Morrisburg | Wind | RCP4.5 | 2085 | 81.0065 | 87.2727 | 93.8788 | 100.4752 | 107.0696
| MorrisburgWind2090RCP4.5 | Morrisburg | Wind | RCP4.5 | 2090 | 80.9864 | 87.2511 | 93.8556 | 100.452 | 107.0449
| MorrisburgWind2095RCP4.5 | Morrisburg | Wind | RCP4.5 | 2095 | 80.9664 | 87.2295 | 93.8323 | 100.4288 | 107.0201
| MorrisburgWind2100RCP4.5 | Morrisburg | Wind | RCP4.5 | 2100 | 80.9463 | 87.2079 | 93.8091 | 100.4056 | 106.9954
| MorrisburgWind2023RCP6.0 | Morrisburg | Wind | RCP6.0 | 2023 | 80.9302 | 87.2425 | 93.8928 | 100.535 | 107.165
| MorrisburgWind2025RCP6.0 | Morrisburg | Wind | RCP6.0 | 2025 | 80.9731 | 87.2828 | 93.9316 | 100.5731 | 107.2021
| MorrisburgWind2030RCP6.0 | Morrisburg | Wind | RCP6.0 | 2030 | 81.0159 | 87.3232 | 93.9703 | 100.6112 | 107.2392
| MorrisburgWind2035RCP6.0 | Morrisburg | Wind | RCP6.0 | 2035 | 81.0587 | 87.3635 | 94.0091 | 100.6494 | 107.2763
| MorrisburgWind2040RCP6.0 | Morrisburg | Wind | RCP6.0 | 2040 | 81.1016 | 87.4039 | 94.0478 | 100.6875 | 107.3134
| MorrisburgWind2045RCP6.0 | Morrisburg | Wind | RCP6.0 | 2045 | 81.1444 | 87.4443 | 94.0866 | 100.7257 | 107.3506
| MorrisburgWind2050RCP6.0 | Morrisburg | Wind | RCP6.0 | 2050 | 81.1631 | 87.4552 | 94.09 | 100.72 | 107.3389
| MorrisburgWind2055RCP6.0 | Morrisburg | Wind | RCP6.0 | 2055 | 81.139 | 87.4258 | 94.0546 | 100.6763 | 107.2901
| MorrisburgWind2060RCP6.0 | Morrisburg | Wind | RCP6.0 | 2060 | 81.1149 | 87.3964 | 94.0193 | 100.6325 | 107.2414
| MorrisburgWind2065RCP6.0 | Morrisburg | Wind | RCP6.0 | 2065 | 81.0908 | 87.367 | 93.9839 | 100.5887 | 107.1926
| MorrisburgWind2070RCP6.0 | Morrisburg | Wind | RCP6.0 | 2070 | 81.0668 | 87.3376 | 93.9486 | 100.5449 | 107.1438
| MorrisburgWind2075RCP6.0 | Morrisburg | Wind | RCP6.0 | 2075 | 81.0366 | 87.3052 | 93.9137 | 100.5101 | 107.1067
| MorrisburgWind2080RCP6.0 | Morrisburg | Wind | RCP6.0 | 2080 | 81.0065 | 87.2727 | 93.8788 | 100.4752 | 107.0696
| MorrisburgWind2085RCP6.0 | Morrisburg | Wind | RCP6.0 | 2085 | 80.9764 | 87.2403 | 93.844 | 100.4404 | 107.0325
| MorrisburgWind2090RCP6.0 | Morrisburg | Wind | RCP6.0 | 2090 | 80.8954 | 87.1473 | 93.7347 | 100.3193 | 106.9
| MorrisburgWind2095RCP6.0 | Morrisburg | Wind | RCP6.0 | 2095 | 80.8446 | 87.0868 | 93.6603 | 100.2331 | 106.8045
| MorrisburgWind2100RCP6.0 | Morrisburg | Wind | RCP6.0 | 2100 | 80.7937 | 87.0262 | 93.5859 | 100.1469 | 106.7091
| MorrisburgWind2023RCP8.5 | Morrisburg | Wind | RCP8.5 | 2023 | 80.9302 | 87.2425 | 93.8928 | 100.535 | 107.165
| MorrisburgWind2025RCP8.5 | Morrisburg | Wind | RCP8.5 | 2025 | 81.0159 | 87.3232 | 93.9703 | 100.6112 | 107.2392
| MorrisburgWind2030RCP8.5 | Morrisburg | Wind | RCP8.5 | 2030 | 81.1016 | 87.4039 | 94.0478 | 100.6875 | 107.3134
| MorrisburgWind2035RCP8.5 | Morrisburg | Wind | RCP8.5 | 2035 | 81.1872 | 87.4846 | 94.1253 | 100.7638 | 107.3877
| MorrisburgWind2040RCP8.5 | Morrisburg | Wind | RCP8.5 | 2040 | 81.1471 | 87.4356 | 94.0664 | 100.6909 | 107.3064
| MorrisburgWind2045RCP8.5 | Morrisburg | Wind | RCP8.5 | 2045 | 81.1069 | 87.3866 | 94.0075 | 100.6179 | 107.2251
| MorrisburgWind2050RCP8.5 | Morrisburg | Wind | RCP8.5 | 2050 | 81.0266 | 87.2944 | 93.9021 | 100.4985 | 107.0943
| MorrisburgWind2055RCP8.5 | Morrisburg | Wind | RCP8.5 | 2055 | 80.9864 | 87.2511 | 93.8556 | 100.452 | 107.0449
| MorrisburgWind2060RCP8.5 | Morrisburg | Wind | RCP8.5 | 2060 | 80.8954 | 87.1473 | 93.7347 | 100.3193 | 106.9
| MorrisburgWind2065RCP8.5 | Morrisburg | Wind | RCP8.5 | 2065 | 80.8446 | 87.0868 | 93.6603 | 100.2331 | 106.8045
| MorrisburgWind2070RCP8.5 | Morrisburg | Wind | RCP8.5 | 2070 | 80.9517 | 87.2367 | 93.8618 | 100.4786 | 107.0943
| MorrisburgWind2075RCP8.5 | Morrisburg | Wind | RCP8.5 | 2075 | 81.1096 | 87.4472 | 94.1377 | 100.8103 | 107.4795
| MorrisburgWind2080RCP8.5 | Morrisburg | Wind | RCP8.5 | 2080 | 81.2675 | 87.6576 | 94.4136 | 101.142 | 107.8647
| MorrisburgWind2085RCP8.5 | Morrisburg | Wind | RCP8.5 | 2085 | 81.1471 | 87.4803 | 94.1671 | 100.8385 | 107.499
| MorrisburgWind2090RCP8.5 | Morrisburg | Wind | RCP8.5 | 2090 | 81.0266 | 87.303 | 93.9207 | 100.535 | 107.1332
| MorrisburgWind2095RCP8.5 | Morrisburg | Wind | RCP8.5 | 2095 | 81.0266 | 87.303 | 93.9207 | 100.535 | 107.1332
| MorrisburgWind2100RCP8.5 | Morrisburg | Wind | RCP8.5 | 2100 | 81.0266 | 87.303 | 93.9207 | 100.535 | 107.1332
| Mount ForestIce Accretion2023RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2023 | 15.2933 | 18.333 | 22.198 | 25.1335 | 28.0804
| Mount ForestIce Accretion2025RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2025 | 15.2984 | 18.3543 | 22.231 | 25.179 | 28.1404
| Mount ForestIce Accretion2030RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2030 | 15.3035 | 18.3756 | 22.264 | 25.2246 | 28.2005
| Mount ForestIce Accretion2035RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2035 | 15.3086 | 18.3969 | 22.297 | 25.2702 | 28.2605
| Mount ForestIce Accretion2040RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2040 | 15.3137 | 18.4183 | 22.33 | 25.3158 | 28.3206
| Mount ForestIce Accretion2045RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2045 | 15.3188 | 18.4396 | 22.363 | 25.3613 | 28.3807
| Mount ForestIce Accretion2050RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2050 | 15.3178 | 18.4718 | 22.4356 | 25.4666 | 28.5183
| Mount ForestIce Accretion2055RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2055 | 15.3117 | 18.4828 | 22.4752 | 25.5262 | 28.596
| Mount ForestIce Accretion2060RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2060 | 15.3056 | 18.4937 | 22.5148 | 25.5859 | 28.6736
| Mount ForestIce Accretion2065RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2065 | 15.2994 | 18.5047 | 22.5544 | 25.6456 | 28.7512
| Mount ForestIce Accretion2070RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2070 | 15.2933 | 18.5156 | 22.594 | 25.7052 | 28.8288
| Mount ForestIce Accretion2075RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2075 | 15.227 | 18.4609 | 22.5573 | 25.6762 | 28.8103
| Mount ForestIce Accretion2080RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2080 | 15.1606 | 18.4061 | 22.5207 | 25.6472 | 28.7918
| Mount ForestIce Accretion2085RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2085 | 15.0943 | 18.3513 | 22.484 | 25.6182 | 28.7734
| Mount ForestIce Accretion2090RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2090 | 15.028 | 18.2965 | 22.4473 | 25.5892 | 28.7549
| Mount ForestIce Accretion2095RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2095 | 14.9616 | 18.2417 | 22.4107 | 25.5602 | 28.7364
| Mount ForestIce Accretion2100RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2100 | 14.8953 | 18.187 | 22.374 | 25.5312 | 28.7179
| Mount ForestIce Accretion2023RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2023 | 15.2933 | 18.333 | 22.198 | 25.1335 | 28.0804
| Mount ForestIce Accretion2025RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2025 | 15.2984 | 18.3543 | 22.231 | 25.179 | 28.1404
| Mount ForestIce Accretion2030RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2030 | 15.3035 | 18.3756 | 22.264 | 25.2246 | 28.2005
| Mount ForestIce Accretion2035RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2035 | 15.3086 | 18.3969 | 22.297 | 25.2702 | 28.2605
| Mount ForestIce Accretion2040RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2040 | 15.3137 | 18.4183 | 22.33 | 25.3158 | 28.3206
| Mount ForestIce Accretion2045RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2045 | 15.3188 | 18.4396 | 22.363 | 25.3613 | 28.3807
| Mount ForestIce Accretion2050RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2050 | 15.3178 | 18.4718 | 22.4356 | 25.4666 | 28.5183
| Mount ForestIce Accretion2055RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2055 | 15.3117 | 18.4828 | 22.4752 | 25.5262 | 28.596
| Mount ForestIce Accretion2060RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2060 | 15.3056 | 18.4937 | 22.5148 | 25.5859 | 28.6736
| Mount ForestIce Accretion2065RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2065 | 15.2994 | 18.5047 | 22.5544 | 25.6456 | 28.7512
| Mount ForestIce Accretion2070RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2070 | 15.2933 | 18.5156 | 22.594 | 25.7052 | 28.8288
| Mount ForestIce Accretion2075RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2075 | 15.1938 | 18.4335 | 22.539 | 25.6617 | 28.8011
| Mount ForestIce Accretion2080RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2080 | 15.0943 | 18.3513 | 22.484 | 25.6182 | 28.7734
| Mount ForestIce Accretion2085RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2085 | 14.9948 | 18.2691 | 22.429 | 25.5747 | 28.7456
| Mount ForestIce Accretion2090RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2090 | 14.6401 | 17.9191 | 22.0733 | 25.2163 | 28.376
| Mount ForestIce Accretion2095RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2095 | 14.385 | 17.6513 | 21.7727 | 24.9014 | 28.0342
| Mount ForestIce Accretion2100RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2100 | 14.1299 | 17.3835 | 21.472 | 24.5865 | 27.6923
| Mount ForestIce Accretion2023RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2023 | 15.2933 | 18.333 | 22.198 | 25.1335 | 28.0804
| Mount ForestIce Accretion2025RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2025 | 15.3035 | 18.3756 | 22.264 | 25.2246 | 28.2005
| Mount ForestIce Accretion2030RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2030 | 15.3137 | 18.4183 | 22.33 | 25.3158 | 28.3206
| Mount ForestIce Accretion2035RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2035 | 15.3239 | 18.4609 | 22.396 | 25.4069 | 28.4407
| Mount ForestIce Accretion2040RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2040 | 15.3137 | 18.4791 | 22.462 | 25.5064 | 28.5701
| Mount ForestIce Accretion2045RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2045 | 15.3035 | 18.4974 | 22.528 | 25.6058 | 28.6994
| Mount ForestIce Accretion2050RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2050 | 15.1606 | 18.4061 | 22.5207 | 25.6472 | 28.7918
| Mount ForestIce Accretion2055RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2055 | 15.028 | 18.2965 | 22.4473 | 25.5892 | 28.7549
| Mount ForestIce Accretion2060RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2060 | 14.6401 | 17.9191 | 22.0733 | 25.2163 | 28.376
| Mount ForestIce Accretion2065RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2065 | 14.385 | 17.6513 | 21.7727 | 24.9014 | 28.0342
| Mount ForestIce Accretion2070RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2070 | 13.7114 | 16.9088 | 20.9367 | 23.9982 | 27.0547
| Mount ForestIce Accretion2075RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2075 | 13.293 | 16.434 | 20.4013 | 23.4098 | 26.4172
| Mount ForestIce Accretion2080RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2080 | 12.8745 | 15.9592 | 19.866 | 22.8215 | 25.7796
| Mount ForestIce Accretion2085RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2085 | 12.4536 | 15.4936 | 19.338 | 22.2497 | 25.1698
| Mount ForestIce Accretion2090RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2090 | 12.0326 | 15.028 | 18.81 | 21.6779 | 24.5599
| Mount ForestIce Accretion2095RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2095 | 12.0326 | 15.028 | 18.81 | 21.6779 | 24.5599
| Mount ForestIce Accretion2100RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2100 | 12.0326 | 15.028 | 18.81 | 21.6779 | 24.5599
| Mount ForestWind2023RCP4.5 | Mount Forest | Wind | RCP4.5 | 2023 | 83.5906 | 90.1639 | 97.1136 | 104.0245 | 110.9393
| Mount ForestWind2025RCP4.5 | Mount Forest | Wind | RCP4.5 | 2025 | 83.6708 | 90.2621 | 97.2368 | 104.1684 | 111.1053
| Mount ForestWind2030RCP4.5 | Mount Forest | Wind | RCP4.5 | 2030 | 83.7509 | 90.3603 | 97.36 | 104.3122 | 111.2713
| Mount ForestWind2035RCP4.5 | Mount Forest | Wind | RCP4.5 | 2035 | 83.831 | 90.4585 | 97.4832 | 104.456 | 111.4373
| Mount ForestWind2040RCP4.5 | Mount Forest | Wind | RCP4.5 | 2040 | 83.9111 | 90.5567 | 97.6064 | 104.5998 | 111.6033
| Mount ForestWind2045RCP4.5 | Mount Forest | Wind | RCP4.5 | 2045 | 83.9913 | 90.6549 | 97.7296 | 104.7436 | 111.7692
| Mount ForestWind2050RCP4.5 | Mount Forest | Wind | RCP4.5 | 2050 | 84.0847 | 90.7656 | 97.8624 | 104.8956 | 111.9418
| Mount ForestWind2055RCP4.5 | Mount Forest | Wind | RCP4.5 | 2055 | 84.0979 | 90.7781 | 97.872 | 104.9038 | 111.9484
| Mount ForestWind2060RCP4.5 | Mount Forest | Wind | RCP4.5 | 2060 | 84.1112 | 90.7906 | 97.8816 | 104.912 | 111.9549
| Mount ForestWind2065RCP4.5 | Mount Forest | Wind | RCP4.5 | 2065 | 84.1245 | 90.8031 | 97.8912 | 104.9203 | 111.9615
| Mount ForestWind2070RCP4.5 | Mount Forest | Wind | RCP4.5 | 2070 | 84.1377 | 90.8156 | 97.9008 | 104.9285 | 111.9681
| Mount ForestWind2075RCP4.5 | Mount Forest | Wind | RCP4.5 | 2075 | 84.2192 | 90.9213 | 98.0368 | 105.0911 | 112.1559
| Mount ForestWind2080RCP4.5 | Mount Forest | Wind | RCP4.5 | 2080 | 84.3008 | 91.0269 | 98.1728 | 105.2538 | 112.3438
| Mount ForestWind2085RCP4.5 | Mount Forest | Wind | RCP4.5 | 2085 | 84.3823 | 91.1326 | 98.3088 | 105.4164 | 112.5317
| Mount ForestWind2090RCP4.5 | Mount Forest | Wind | RCP4.5 | 2090 | 84.4638 | 91.2382 | 98.4448 | 105.579 | 112.7196
| Mount ForestWind2095RCP4.5 | Mount Forest | Wind | RCP4.5 | 2095 | 84.5453 | 91.3439 | 98.5808 | 105.7417 | 112.9074
| Mount ForestWind2100RCP4.5 | Mount Forest | Wind | RCP4.5 | 2100 | 84.6268 | 91.4495 | 98.7168 | 105.9043 | 113.0953
| Mount ForestWind2023RCP6.0 | Mount Forest | Wind | RCP6.0 | 2023 | 83.5906 | 90.1639 | 97.1136 | 104.0245 | 110.9393
| Mount ForestWind2025RCP6.0 | Mount Forest | Wind | RCP6.0 | 2025 | 83.6708 | 90.2621 | 97.2368 | 104.1684 | 111.1053
| Mount ForestWind2030RCP6.0 | Mount Forest | Wind | RCP6.0 | 2030 | 83.7509 | 90.3603 | 97.36 | 104.3122 | 111.2713
| Mount ForestWind2035RCP6.0 | Mount Forest | Wind | RCP6.0 | 2035 | 83.831 | 90.4585 | 97.4832 | 104.456 | 111.4373
| Mount ForestWind2040RCP6.0 | Mount Forest | Wind | RCP6.0 | 2040 | 83.9111 | 90.5567 | 97.6064 | 104.5998 | 111.6033
| Mount ForestWind2045RCP6.0 | Mount Forest | Wind | RCP6.0 | 2045 | 83.9913 | 90.6549 | 97.7296 | 104.7436 | 111.7692
| Mount ForestWind2050RCP6.0 | Mount Forest | Wind | RCP6.0 | 2050 | 84.0847 | 90.7656 | 97.8624 | 104.8956 | 111.9418
| Mount ForestWind2055RCP6.0 | Mount Forest | Wind | RCP6.0 | 2055 | 84.0979 | 90.7781 | 97.872 | 104.9038 | 111.9484
| Mount ForestWind2060RCP6.0 | Mount Forest | Wind | RCP6.0 | 2060 | 84.1112 | 90.7906 | 97.8816 | 104.912 | 111.9549
| Mount ForestWind2065RCP6.0 | Mount Forest | Wind | RCP6.0 | 2065 | 84.1245 | 90.8031 | 97.8912 | 104.9203 | 111.9615
| Mount ForestWind2070RCP6.0 | Mount Forest | Wind | RCP6.0 | 2070 | 84.1377 | 90.8156 | 97.9008 | 104.9285 | 111.9681
| Mount ForestWind2075RCP6.0 | Mount Forest | Wind | RCP6.0 | 2075 | 84.26 | 90.9741 | 98.1048 | 105.1724 | 112.2499
| Mount ForestWind2080RCP6.0 | Mount Forest | Wind | RCP6.0 | 2080 | 84.3823 | 91.1326 | 98.3088 | 105.4164 | 112.5317
| Mount ForestWind2085RCP6.0 | Mount Forest | Wind | RCP6.0 | 2085 | 84.5045 | 91.291 | 98.5128 | 105.6604 | 112.8135
| Mount ForestWind2090RCP6.0 | Mount Forest | Wind | RCP6.0 | 2090 | 85.0302 | 91.9554 | 99.3472 | 106.6439 | 113.9489
| Mount ForestWind2095RCP6.0 | Mount Forest | Wind | RCP6.0 | 2095 | 85.4336 | 92.4613 | 99.9776 | 107.3835 | 114.8026
| Mount ForestWind2100RCP6.0 | Mount Forest | Wind | RCP6.0 | 2100 | 85.8371 | 92.9673 | 100.608 | 108.1231 | 115.6562
| Mount ForestWind2023RCP8.5 | Mount Forest | Wind | RCP8.5 | 2023 | 83.5906 | 90.1639 | 97.1136 | 104.0245 | 110.9393
| Mount ForestWind2025RCP8.5 | Mount Forest | Wind | RCP8.5 | 2025 | 83.7509 | 90.3603 | 97.36 | 104.3122 | 111.2713
| Mount ForestWind2030RCP8.5 | Mount Forest | Wind | RCP8.5 | 2030 | 83.9111 | 90.5567 | 97.6064 | 104.5998 | 111.6033
| Mount ForestWind2035RCP8.5 | Mount Forest | Wind | RCP8.5 | 2035 | 84.0714 | 90.7531 | 97.8528 | 104.8874 | 111.9352
| Mount ForestWind2040RCP8.5 | Mount Forest | Wind | RCP8.5 | 2040 | 84.0935 | 90.774 | 97.8688 | 104.9011 | 111.9462
| Mount ForestWind2045RCP8.5 | Mount Forest | Wind | RCP8.5 | 2045 | 84.1156 | 90.7948 | 97.8848 | 104.9148 | 111.9571
| Mount ForestWind2050RCP8.5 | Mount Forest | Wind | RCP8.5 | 2050 | 84.3008 | 91.0269 | 98.1728 | 105.2538 | 112.3438
| Mount ForestWind2055RCP8.5 | Mount Forest | Wind | RCP8.5 | 2055 | 84.4638 | 91.2382 | 98.4448 | 105.579 | 112.7196
| Mount ForestWind2060RCP8.5 | Mount Forest | Wind | RCP8.5 | 2060 | 85.0302 | 91.9554 | 99.3472 | 106.6439 | 113.9489
| Mount ForestWind2065RCP8.5 | Mount Forest | Wind | RCP8.5 | 2065 | 85.4336 | 92.4613 | 99.9776 | 107.3835 | 114.8026
| Mount ForestWind2070RCP8.5 | Mount Forest | Wind | RCP8.5 | 2070 | 86.0471 | 93.2232 | 100.9216 | 108.486 | 116.0684
| Mount ForestWind2075RCP8.5 | Mount Forest | Wind | RCP8.5 | 2075 | 86.2571 | 93.4791 | 101.2352 | 108.849 | 116.4806
| Mount ForestWind2080RCP8.5 | Mount Forest | Wind | RCP8.5 | 2080 | 86.4671 | 93.7351 | 101.5488 | 109.2119 | 116.8929
| Mount ForestWind2085RCP8.5 | Mount Forest | Wind | RCP8.5 | 2085 | 86.4878 | 93.744 | 101.5488 | 109.1965 | 116.871
| Mount ForestWind2090RCP8.5 | Mount Forest | Wind | RCP8.5 | 2090 | 86.5085 | 93.7529 | 101.5488 | 109.1811 | 116.8491
| Mount ForestWind2095RCP8.5 | Mount Forest | Wind | RCP8.5 | 2095 | 86.5085 | 93.7529 | 101.5488 | 109.1811 | 116.8491
| Mount ForestWind2100RCP8.5 | Mount Forest | Wind | RCP8.5 | 2100 | 86.5085 | 93.7529 | 101.5488 | 109.1811 | 116.8491
| NakinaIce Accretion2023RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2023 | 8.442 | 10.0596 | 12.108 | 13.682 | 15.2561
| NakinaIce Accretion2025RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2025 | 8.5213 | 10.1542 | 12.222 | 13.8086 | 15.3972
| NakinaIce Accretion2030RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2030 | 8.6007 | 10.2488 | 12.336 | 13.9352 | 15.5383
| NakinaIce Accretion2035RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2035 | 8.68 | 10.3435 | 12.45 | 14.0617 | 15.6794
| NakinaIce Accretion2040RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2040 | 8.7593 | 10.4381 | 12.564 | 14.1883 | 15.8206
| NakinaIce Accretion2045RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2045 | 8.8386 | 10.5327 | 12.678 | 14.3148 | 15.9617
| NakinaIce Accretion2050RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2050 | 8.958 | 10.6711 | 12.84 | 14.4956 | 16.1603
| NakinaIce Accretion2055RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2055 | 8.9981 | 10.715 | 12.888 | 14.5499 | 16.2177
| NakinaIce Accretion2060RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2060 | 9.0382 | 10.7588 | 12.936 | 14.6041 | 16.2752
| NakinaIce Accretion2065RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2065 | 9.0783 | 10.8026 | 12.984 | 14.6584 | 16.3326
| NakinaIce Accretion2070RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2070 | 9.1184 | 10.8464 | 13.032 | 14.7126 | 16.3901
| NakinaIce Accretion2075RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2075 | 9.1198 | 10.8498 | 13.038 | 14.7194 | 16.3976
| NakinaIce Accretion2080RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2080 | 9.1212 | 10.8531 | 13.044 | 14.7262 | 16.4052
| NakinaIce Accretion2085RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2085 | 9.1225 | 10.8564 | 13.05 | 14.7329 | 16.4128
| NakinaIce Accretion2090RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2090 | 9.1239 | 10.8597 | 13.056 | 14.7397 | 16.4203
| NakinaIce Accretion2095RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2095 | 9.1253 | 10.863 | 13.062 | 14.7465 | 16.4279
| NakinaIce Accretion2100RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2100 | 9.1267 | 10.8664 | 13.068 | 14.7533 | 16.4354
| NakinaIce Accretion2023RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2023 | 8.442 | 10.0596 | 12.108 | 13.682 | 15.2561
| NakinaIce Accretion2025RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2025 | 8.5213 | 10.1542 | 12.222 | 13.8086 | 15.3972
| NakinaIce Accretion2030RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2030 | 8.6007 | 10.2488 | 12.336 | 13.9352 | 15.5383
| NakinaIce Accretion2035RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2035 | 8.68 | 10.3435 | 12.45 | 14.0617 | 15.6794
| NakinaIce Accretion2040RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2040 | 8.7593 | 10.4381 | 12.564 | 14.1883 | 15.8206
| NakinaIce Accretion2045RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2045 | 8.8386 | 10.5327 | 12.678 | 14.3148 | 15.9617
| NakinaIce Accretion2050RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2050 | 8.958 | 10.6711 | 12.84 | 14.4956 | 16.1603
| NakinaIce Accretion2055RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2055 | 8.9981 | 10.715 | 12.888 | 14.5499 | 16.2177
| NakinaIce Accretion2060RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2060 | 9.0382 | 10.7588 | 12.936 | 14.6041 | 16.2752
| NakinaIce Accretion2065RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2065 | 9.0783 | 10.8026 | 12.984 | 14.6584 | 16.3326
| NakinaIce Accretion2070RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2070 | 9.1184 | 10.8464 | 13.032 | 14.7126 | 16.3901
| NakinaIce Accretion2075RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2075 | 9.1205 | 10.8514 | 13.041 | 14.7228 | 16.4014
| NakinaIce Accretion2080RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2080 | 9.1225 | 10.8564 | 13.05 | 14.7329 | 16.4128
| NakinaIce Accretion2085RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2085 | 9.1246 | 10.8614 | 13.059 | 14.7431 | 16.4241
| NakinaIce Accretion2090RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2090 | 9.0404 | 10.7634 | 12.944 | 14.6132 | 16.2792
| NakinaIce Accretion2095RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2095 | 8.9541 | 10.6605 | 12.82 | 14.473 | 16.123
| NakinaIce Accretion2100RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2100 | 8.8679 | 10.5576 | 12.696 | 14.3329 | 15.9667
| NakinaIce Accretion2023RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2023 | 8.442 | 10.0596 | 12.108 | 13.682 | 15.2561
| NakinaIce Accretion2025RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2025 | 8.6007 | 10.2488 | 12.336 | 13.9352 | 15.5383
| NakinaIce Accretion2030RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2030 | 8.7593 | 10.4381 | 12.564 | 14.1883 | 15.8206
| NakinaIce Accretion2035RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2035 | 8.918 | 10.6273 | 12.792 | 14.4414 | 16.1028
| NakinaIce Accretion2040RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2040 | 8.9848 | 10.7004 | 12.872 | 14.5318 | 16.1986
| NakinaIce Accretion2045RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2045 | 9.0516 | 10.7734 | 12.952 | 14.6222 | 16.2943
| NakinaIce Accretion2050RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2050 | 9.1212 | 10.8531 | 13.044 | 14.7262 | 16.4052
| NakinaIce Accretion2055RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2055 | 9.1239 | 10.8597 | 13.056 | 14.7397 | 16.4203
| NakinaIce Accretion2060RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2060 | 9.0404 | 10.7634 | 12.944 | 14.6132 | 16.2792
| NakinaIce Accretion2065RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2065 | 8.9541 | 10.6605 | 12.82 | 14.473 | 16.123
| NakinaIce Accretion2070RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2070 | 8.8595 | 10.5576 | 12.708 | 14.3555 | 15.997
| NakinaIce Accretion2075RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2075 | 8.8512 | 10.5576 | 12.72 | 14.3781 | 16.0272
| NakinaIce Accretion2080RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2080 | 8.8428 | 10.5576 | 12.732 | 14.4007 | 16.0574
| NakinaIce Accretion2085RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2085 | 8.8595 | 10.5974 | 12.798 | 14.4821 | 16.1633
| NakinaIce Accretion2090RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2090 | 8.8762 | 10.6373 | 12.864 | 14.5634 | 16.2691
| NakinaIce Accretion2095RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2095 | 8.8762 | 10.6373 | 12.864 | 14.5634 | 16.2691
| NakinaIce Accretion2100RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2100 | 8.8762 | 10.6373 | 12.864 | 14.5634 | 16.2691
| NakinaWind2023RCP4.5 | Nakina | Wind | RCP4.5 | 2023 | 69.2858 | 74.5934 | 80.16 | 85.7455 | 91.3186
| NakinaWind2025RCP4.5 | Nakina | Wind | RCP4.5 | 2025 | 69.3998 | 74.7323 | 80.332 | 85.9438 | 91.5466
| NakinaWind2030RCP4.5 | Nakina | Wind | RCP4.5 | 2030 | 69.5138 | 74.8712 | 80.504 | 86.1421 | 91.7746
| NakinaWind2035RCP4.5 | Nakina | Wind | RCP4.5 | 2035 | 69.6278 | 75.0101 | 80.676 | 86.3404 | 92.0026
| NakinaWind2040RCP4.5 | Nakina | Wind | RCP4.5 | 2040 | 69.7417 | 75.149 | 80.848 | 86.5387 | 92.2306
| NakinaWind2045RCP4.5 | Nakina | Wind | RCP4.5 | 2045 | 69.8557 | 75.2878 | 81.02 | 86.7371 | 92.4586
| NakinaWind2050RCP4.5 | Nakina | Wind | RCP4.5 | 2050 | 70.0595 | 75.5339 | 81.3184 | 87.0775 | 92.8452
| NakinaWind2055RCP4.5 | Nakina | Wind | RCP4.5 | 2055 | 70.1493 | 75.641 | 81.4448 | 87.2196 | 93.0039
| NakinaWind2060RCP4.5 | Nakina | Wind | RCP4.5 | 2060 | 70.2391 | 75.7481 | 81.5712 | 87.3616 | 93.1626
| NakinaWind2065RCP4.5 | Nakina | Wind | RCP4.5 | 2065 | 70.3289 | 75.8553 | 81.6976 | 87.5037 | 93.3213
| NakinaWind2070RCP4.5 | Nakina | Wind | RCP4.5 | 2070 | 70.4187 | 75.9624 | 81.824 | 87.6458 | 93.48
| NakinaWind2075RCP4.5 | Nakina | Wind | RCP4.5 | 2075 | 70.5085 | 76.069 | 81.9507 | 87.7914 | 93.6426
| NakinaWind2080RCP4.5 | Nakina | Wind | RCP4.5 | 2080 | 70.5983 | 76.1757 | 82.0773 | 87.9369 | 93.8053
| NakinaWind2085RCP4.5 | Nakina | Wind | RCP4.5 | 2085 | 70.6881 | 76.2823 | 82.204 | 88.0824 | 93.9679
| NakinaWind2090RCP4.5 | Nakina | Wind | RCP4.5 | 2090 | 70.7779 | 76.389 | 82.3307 | 88.2279 | 94.1306
| NakinaWind2095RCP4.5 | Nakina | Wind | RCP4.5 | 2095 | 70.8677 | 76.4956 | 82.4573 | 88.3734 | 94.2932
| NakinaWind2100RCP4.5 | Nakina | Wind | RCP4.5 | 2100 | 70.9575 | 76.6022 | 82.584 | 88.519 | 94.4558
| NakinaWind2023RCP6.0 | Nakina | Wind | RCP6.0 | 2023 | 69.2858 | 74.5934 | 80.16 | 85.7455 | 91.3186
| NakinaWind2025RCP6.0 | Nakina | Wind | RCP6.0 | 2025 | 69.3998 | 74.7323 | 80.332 | 85.9438 | 91.5466
| NakinaWind2030RCP6.0 | Nakina | Wind | RCP6.0 | 2030 | 69.5138 | 74.8712 | 80.504 | 86.1421 | 91.7746
| NakinaWind2035RCP6.0 | Nakina | Wind | RCP6.0 | 2035 | 69.6278 | 75.0101 | 80.676 | 86.3404 | 92.0026
| NakinaWind2040RCP6.0 | Nakina | Wind | RCP6.0 | 2040 | 69.7417 | 75.149 | 80.848 | 86.5387 | 92.2306
| NakinaWind2045RCP6.0 | Nakina | Wind | RCP6.0 | 2045 | 69.8557 | 75.2878 | 81.02 | 86.7371 | 92.4586
| NakinaWind2050RCP6.0 | Nakina | Wind | RCP6.0 | 2050 | 70.0595 | 75.5339 | 81.3184 | 87.0775 | 92.8452
| NakinaWind2055RCP6.0 | Nakina | Wind | RCP6.0 | 2055 | 70.1493 | 75.641 | 81.4448 | 87.2196 | 93.0039
| NakinaWind2060RCP6.0 | Nakina | Wind | RCP6.0 | 2060 | 70.2391 | 75.7481 | 81.5712 | 87.3616 | 93.1626
| NakinaWind2065RCP6.0 | Nakina | Wind | RCP6.0 | 2065 | 70.3289 | 75.8553 | 81.6976 | 87.5037 | 93.3213
| NakinaWind2070RCP6.0 | Nakina | Wind | RCP6.0 | 2070 | 70.4187 | 75.9624 | 81.824 | 87.6458 | 93.48
| NakinaWind2075RCP6.0 | Nakina | Wind | RCP6.0 | 2075 | 70.5534 | 76.1224 | 82.014 | 87.8641 | 93.724
| NakinaWind2080RCP6.0 | Nakina | Wind | RCP6.0 | 2080 | 70.6881 | 76.2823 | 82.204 | 88.0824 | 93.9679
| NakinaWind2085RCP6.0 | Nakina | Wind | RCP6.0 | 2085 | 70.8228 | 76.4423 | 82.394 | 88.3007 | 94.2119
| NakinaWind2090RCP6.0 | Nakina | Wind | RCP6.0 | 2090 | 71.0151 | 76.6742 | 82.672 | 88.6217 | 94.5744
| NakinaWind2095RCP6.0 | Nakina | Wind | RCP6.0 | 2095 | 71.0727 | 76.7461 | 82.76 | 88.7244 | 94.693
| NakinaWind2100RCP6.0 | Nakina | Wind | RCP6.0 | 2100 | 71.1302 | 76.818 | 82.848 | 88.8271 | 94.8115
| NakinaWind2023RCP8.5 | Nakina | Wind | RCP8.5 | 2023 | 69.2858 | 74.5934 | 80.16 | 85.7455 | 91.3186
| NakinaWind2025RCP8.5 | Nakina | Wind | RCP8.5 | 2025 | 69.5138 | 74.8712 | 80.504 | 86.1421 | 91.7746
| NakinaWind2030RCP8.5 | Nakina | Wind | RCP8.5 | 2030 | 69.7417 | 75.149 | 80.848 | 86.5387 | 92.2306
| NakinaWind2035RCP8.5 | Nakina | Wind | RCP8.5 | 2035 | 69.9697 | 75.4267 | 81.192 | 86.9354 | 92.6866
| NakinaWind2040RCP8.5 | Nakina | Wind | RCP8.5 | 2040 | 70.1194 | 75.6053 | 81.4027 | 87.1722 | 92.951
| NakinaWind2045RCP8.5 | Nakina | Wind | RCP8.5 | 2045 | 70.269 | 75.7838 | 81.6133 | 87.409 | 93.2155
| NakinaWind2050RCP8.5 | Nakina | Wind | RCP8.5 | 2050 | 70.5983 | 76.1757 | 82.0773 | 87.9369 | 93.8053
| NakinaWind2055RCP8.5 | Nakina | Wind | RCP8.5 | 2055 | 70.7779 | 76.389 | 82.3307 | 88.2279 | 94.1306
| NakinaWind2060RCP8.5 | Nakina | Wind | RCP8.5 | 2060 | 71.0151 | 76.6742 | 82.672 | 88.6217 | 94.5744
| NakinaWind2065RCP8.5 | Nakina | Wind | RCP8.5 | 2065 | 71.0727 | 76.7461 | 82.76 | 88.7244 | 94.693
| NakinaWind2070RCP8.5 | Nakina | Wind | RCP8.5 | 2070 | 71.1279 | 76.8056 | 82.824 | 88.7929 | 94.769
| NakinaWind2075RCP8.5 | Nakina | Wind | RCP8.5 | 2075 | 71.1256 | 76.7932 | 82.8 | 88.7586 | 94.7264
| NakinaWind2080RCP8.5 | Nakina | Wind | RCP8.5 | 2080 | 71.1233 | 76.7808 | 82.776 | 88.7244 | 94.6838
| NakinaWind2085RCP8.5 | Nakina | Wind | RCP8.5 | 2085 | 71.1993 | 76.8701 | 82.884 | 88.8485 | 94.8252
| NakinaWind2090RCP8.5 | Nakina | Wind | RCP8.5 | 2090 | 71.2753 | 76.9594 | 82.992 | 88.9726 | 94.9666
| NakinaWind2095RCP8.5 | Nakina | Wind | RCP8.5 | 2095 | 71.2753 | 76.9594 | 82.992 | 88.9726 | 94.9666
| NakinaWind2100RCP8.5 | Nakina | Wind | RCP8.5 | 2100 | 71.2753 | 76.9594 | 82.992 | 88.9726 | 94.9666
| Nanticoke (Jarvis)Ice Accretion2023RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2023 | 23.2802 | 27.9096 | 33.796 | 38.2663 | 42.7543
| Nanticoke (Jarvis)Ice Accretion2025RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2025 | 23.1619 | 27.7826 | 33.6543 | 38.119 | 42.5972
| Nanticoke (Jarvis)Ice Accretion2030RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2030 | 23.0436 | 27.6556 | 33.5127 | 37.9718 | 42.4402
| Nanticoke (Jarvis)Ice Accretion2035RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2035 | 22.9253 | 27.5286 | 33.371 | 37.8245 | 42.2831
| Nanticoke (Jarvis)Ice Accretion2040RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2040 | 22.8071 | 27.4016 | 33.2293 | 37.6772 | 42.126
| Nanticoke (Jarvis)Ice Accretion2045RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2045 | 22.6888 | 27.2746 | 33.0877 | 37.5299 | 41.9689
| Nanticoke (Jarvis)Ice Accretion2050RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2050 | 22.2534 | 26.8034 | 32.572 | 36.9754 | 41.3749
| Nanticoke (Jarvis)Ice Accretion2055RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2055 | 21.9364 | 26.4591 | 32.198 | 36.5682 | 40.9379
| Nanticoke (Jarvis)Ice Accretion2060RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2060 | 21.6194 | 26.1148 | 31.824 | 36.1609 | 40.5009
| Nanticoke (Jarvis)Ice Accretion2065RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2065 | 21.3024 | 25.7705 | 31.45 | 35.7537 | 40.064
| Nanticoke (Jarvis)Ice Accretion2070RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2070 | 20.9853 | 25.4262 | 31.076 | 35.3464 | 39.627
| Nanticoke (Jarvis)Ice Accretion2075RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2075 | 20.8828 | 25.3369 | 30.9967 | 35.276 | 39.5556
| Nanticoke (Jarvis)Ice Accretion2080RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2080 | 20.7803 | 25.2475 | 30.9173 | 35.2055 | 39.4842
| Nanticoke (Jarvis)Ice Accretion2085RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2085 | 20.6778 | 25.1581 | 30.838 | 35.1351 | 39.4128
| Nanticoke (Jarvis)Ice Accretion2090RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2090 | 20.5752 | 25.0688 | 30.7587 | 35.0647 | 39.3414
| Nanticoke (Jarvis)Ice Accretion2095RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2095 | 20.4727 | 24.9794 | 30.6793 | 34.9942 | 39.27
| Nanticoke (Jarvis)Ice Accretion2100RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2100 | 20.3702 | 24.89 | 30.6 | 34.9238 | 39.1986
| Nanticoke (Jarvis)Ice Accretion2023RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2023 | 23.2802 | 27.9096 | 33.796 | 38.2663 | 42.7543
| Nanticoke (Jarvis)Ice Accretion2025RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2025 | 23.1619 | 27.7826 | 33.6543 | 38.119 | 42.5972
| Nanticoke (Jarvis)Ice Accretion2030RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2030 | 23.0436 | 27.6556 | 33.5127 | 37.9718 | 42.4402
| Nanticoke (Jarvis)Ice Accretion2035RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2035 | 22.9253 | 27.5286 | 33.371 | 37.8245 | 42.2831
| Nanticoke (Jarvis)Ice Accretion2040RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2040 | 22.8071 | 27.4016 | 33.2293 | 37.6772 | 42.126
| Nanticoke (Jarvis)Ice Accretion2045RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2045 | 22.6888 | 27.2746 | 33.0877 | 37.5299 | 41.9689
| Nanticoke (Jarvis)Ice Accretion2050RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2050 | 22.2534 | 26.8034 | 32.572 | 36.9754 | 41.3749
| Nanticoke (Jarvis)Ice Accretion2055RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2055 | 21.9364 | 26.4591 | 32.198 | 36.5682 | 40.9379
| Nanticoke (Jarvis)Ice Accretion2060RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2060 | 21.6194 | 26.1148 | 31.824 | 36.1609 | 40.5009
| Nanticoke (Jarvis)Ice Accretion2065RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2065 | 21.3024 | 25.7705 | 31.45 | 35.7537 | 40.064
| Nanticoke (Jarvis)Ice Accretion2070RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2070 | 20.9853 | 25.4262 | 31.076 | 35.3464 | 39.627
| Nanticoke (Jarvis)Ice Accretion2075RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2075 | 20.8315 | 25.2922 | 30.957 | 35.2407 | 39.5199
| Nanticoke (Jarvis)Ice Accretion2080RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2080 | 20.6778 | 25.1581 | 30.838 | 35.1351 | 39.4128
| Nanticoke (Jarvis)Ice Accretion2085RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2085 | 20.524 | 25.0241 | 30.719 | 35.0294 | 39.3057
| Nanticoke (Jarvis)Ice Accretion2090RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2090 | 19.6999 | 24.1281 | 29.716 | 33.9505 | 38.1419
| Nanticoke (Jarvis)Ice Accretion2095RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2095 | 19.0295 | 23.3662 | 28.832 | 32.9772 | 37.0852
| Nanticoke (Jarvis)Ice Accretion2100RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2100 | 18.3592 | 22.6042 | 27.948 | 32.0039 | 36.0284
| Nanticoke (Jarvis)Ice Accretion2023RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2023 | 23.2802 | 27.9096 | 33.796 | 38.2663 | 42.7543
| Nanticoke (Jarvis)Ice Accretion2025RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2025 | 23.0436 | 27.6556 | 33.5127 | 37.9718 | 42.4402
| Nanticoke (Jarvis)Ice Accretion2030RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2030 | 22.8071 | 27.4016 | 33.2293 | 37.6772 | 42.126
| Nanticoke (Jarvis)Ice Accretion2035RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2035 | 22.5705 | 27.1476 | 32.946 | 37.3827 | 41.8118
| Nanticoke (Jarvis)Ice Accretion2040RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2040 | 22.0421 | 26.5738 | 32.3227 | 36.7039 | 41.0836
| Nanticoke (Jarvis)Ice Accretion2045RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2045 | 21.5137 | 26 | 31.6993 | 36.0252 | 40.3553
| Nanticoke (Jarvis)Ice Accretion2050RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2050 | 20.7803 | 25.2475 | 30.9173 | 35.2055 | 39.4842
| Nanticoke (Jarvis)Ice Accretion2055RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2055 | 20.5752 | 25.0688 | 30.7587 | 35.0647 | 39.3414
| Nanticoke (Jarvis)Ice Accretion2060RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2060 | 19.6999 | 24.1281 | 29.716 | 33.9505 | 38.1419
| Nanticoke (Jarvis)Ice Accretion2065RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2065 | 19.0295 | 23.3662 | 28.832 | 32.9772 | 37.0852
| Nanticoke (Jarvis)Ice Accretion2070RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2070 | 17.9255 | 22.1245 | 27.4153 | 31.4148 | 35.4001
| Nanticoke (Jarvis)Ice Accretion2075RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2075 | 17.4917 | 21.6447 | 26.8827 | 30.8256 | 34.7718
| Nanticoke (Jarvis)Ice Accretion2080RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2080 | 17.058 | 21.165 | 26.35 | 30.2365 | 34.1435
| Nanticoke (Jarvis)Ice Accretion2085RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2085 | 15.8987 | 19.8104 | 24.701 | 28.3924 | 32.0872
| Nanticoke (Jarvis)Ice Accretion2090RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2090 | 14.7394 | 18.4559 | 23.052 | 26.5482 | 30.0308
| Nanticoke (Jarvis)Ice Accretion2095RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2095 | 14.7394 | 18.4559 | 23.052 | 26.5482 | 30.0308
| Nanticoke (Jarvis)Ice Accretion2100RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2100 | 14.7394 | 18.4559 | 23.052 | 26.5482 | 30.0308
| Nanticoke (Jarvis)Wind2023RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2023 | 87.6216 | 94.4654 | 101.6969 | 108.9021 | 116.1072
| Nanticoke (Jarvis)Wind2025RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2025 | 87.6405 | 94.4983 | 101.7474 | 108.967 | 116.1878
| Nanticoke (Jarvis)Wind2030RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2030 | 87.6594 | 94.5312 | 101.7979 | 109.0318 | 116.2684
| Nanticoke (Jarvis)Wind2035RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2035 | 87.6783 | 94.564 | 101.8484 | 109.0967 | 116.349
| Nanticoke (Jarvis)Wind2040RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2040 | 87.6972 | 94.5969 | 101.8989 | 109.1615 | 116.4296
| Nanticoke (Jarvis)Wind2045RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2045 | 87.7161 | 94.6298 | 101.9494 | 109.2263 | 116.5102
| Nanticoke (Jarvis)Wind2050RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2050 | 87.8083 | 94.7585 | 102.1231 | 109.4403 | 116.7658
| Nanticoke (Jarvis)Wind2055RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2055 | 87.8815 | 94.8543 | 102.2463 | 109.5895 | 116.9408
| Nanticoke (Jarvis)Wind2060RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2060 | 87.9548 | 94.9501 | 102.3696 | 109.7386 | 117.1158
| Nanticoke (Jarvis)Wind2065RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2065 | 88.028 | 95.0459 | 102.4928 | 109.8877 | 117.2908
| Nanticoke (Jarvis)Wind2070RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2070 | 88.1013 | 95.1417 | 102.616 | 110.0369 | 117.4658
| Nanticoke (Jarvis)Wind2075RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2075 | 88.2103 | 95.2873 | 102.8062 | 110.2638 | 117.7326
| Nanticoke (Jarvis)Wind2080RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2080 | 88.3193 | 95.4329 | 102.9964 | 110.4908 | 117.9993
| Nanticoke (Jarvis)Wind2085RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2085 | 88.4283 | 95.5785 | 103.1867 | 110.7177 | 118.2661
| Nanticoke (Jarvis)Wind2090RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2090 | 88.5373 | 95.7241 | 103.3769 | 110.9447 | 118.5328
| Nanticoke (Jarvis)Wind2095RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2095 | 88.6464 | 95.8697 | 103.5671 | 111.1716 | 118.7995
| Nanticoke (Jarvis)Wind2100RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2100 | 88.7554 | 96.0152 | 103.7573 | 111.3986 | 119.0663
| Nanticoke (Jarvis)Wind2023RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2023 | 87.6216 | 94.4654 | 101.6969 | 108.9021 | 116.1072
| Nanticoke (Jarvis)Wind2025RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2025 | 87.6405 | 94.4983 | 101.7474 | 108.967 | 116.1878
| Nanticoke (Jarvis)Wind2030RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2030 | 87.6594 | 94.5312 | 101.7979 | 109.0318 | 116.2684
| Nanticoke (Jarvis)Wind2035RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2035 | 87.6783 | 94.564 | 101.8484 | 109.0967 | 116.349
| Nanticoke (Jarvis)Wind2040RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2040 | 87.6972 | 94.5969 | 101.8989 | 109.1615 | 116.4296
| Nanticoke (Jarvis)Wind2045RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2045 | 87.7161 | 94.6298 | 101.9494 | 109.2263 | 116.5102
| Nanticoke (Jarvis)Wind2050RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2050 | 87.8083 | 94.7585 | 102.1231 | 109.4403 | 116.7658
| Nanticoke (Jarvis)Wind2055RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2055 | 87.8815 | 94.8543 | 102.2463 | 109.5895 | 116.9408
| Nanticoke (Jarvis)Wind2060RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2060 | 87.9548 | 94.9501 | 102.3696 | 109.7386 | 117.1158
| Nanticoke (Jarvis)Wind2065RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2065 | 88.028 | 95.0459 | 102.4928 | 109.8877 | 117.2908
| Nanticoke (Jarvis)Wind2070RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2070 | 88.1013 | 95.1417 | 102.616 | 110.0369 | 117.4658
| Nanticoke (Jarvis)Wind2075RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2075 | 88.2648 | 95.3601 | 102.9013 | 110.3773 | 117.8659
| Nanticoke (Jarvis)Wind2080RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2080 | 88.4283 | 95.5785 | 103.1867 | 110.7177 | 118.2661
| Nanticoke (Jarvis)Wind2085RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2085 | 88.5919 | 95.7969 | 103.472 | 111.0581 | 118.6662
| Nanticoke (Jarvis)Wind2090RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2090 | 89.0781 | 96.4254 | 104.2825 | 112.0218 | 119.7878
| Nanticoke (Jarvis)Wind2095RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2095 | 89.4007 | 96.8356 | 104.8077 | 112.645 | 120.5094
| Nanticoke (Jarvis)Wind2100RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2100 | 89.7234 | 97.2457 | 105.3329 | 113.2682 | 121.2309
| Nanticoke (Jarvis)Wind2023RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2023 | 87.6216 | 94.4654 | 101.6969 | 108.9021 | 116.1072
| Nanticoke (Jarvis)Wind2025RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2025 | 87.6594 | 94.5312 | 101.7979 | 109.0318 | 116.2684
| Nanticoke (Jarvis)Wind2030RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2030 | 87.6972 | 94.5969 | 101.8989 | 109.1615 | 116.4296
| Nanticoke (Jarvis)Wind2035RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2035 | 87.735 | 94.6627 | 101.9999 | 109.2912 | 116.5908
| Nanticoke (Jarvis)Wind2040RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2040 | 87.8571 | 94.8223 | 102.2053 | 109.5398 | 116.8825
| Nanticoke (Jarvis)Wind2045RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2045 | 87.9792 | 94.982 | 102.4106 | 109.7883 | 117.1741
| Nanticoke (Jarvis)Wind2050RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2050 | 88.3193 | 95.4329 | 102.9964 | 110.4908 | 117.9993
| Nanticoke (Jarvis)Wind2055RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2055 | 88.5373 | 95.7241 | 103.3769 | 110.9447 | 118.5328
| Nanticoke (Jarvis)Wind2060RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2060 | 89.0781 | 96.4254 | 104.2825 | 112.0218 | 119.7878
| Nanticoke (Jarvis)Wind2065RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2065 | 89.4007 | 96.8356 | 104.8077 | 112.645 | 120.5094
| Nanticoke (Jarvis)Wind2070RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2070 | 89.9037 | 97.4962 | 105.6763 | 113.686 | 121.726
| Nanticoke (Jarvis)Wind2075RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2075 | 90.0839 | 97.7467 | 106.0197 | 114.1039 | 122.2211
| Nanticoke (Jarvis)Wind2080RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2080 | 90.2641 | 97.9972 | 106.3631 | 114.5218 | 122.7162
| Nanticoke (Jarvis)Wind2085RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2085 | 90.5389 | 98.3682 | 106.8479 | 115.1108 | 123.4071
| Nanticoke (Jarvis)Wind2090RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2090 | 90.8136 | 98.7392 | 107.3327 | 115.6997 | 124.0979
| Nanticoke (Jarvis)Wind2095RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2095 | 90.8136 | 98.7392 | 107.3327 | 115.6997 | 124.0979
| Nanticoke (Jarvis)Wind2100RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2100 | 90.8136 | 98.7392 | 107.3327 | 115.6997 | 124.0979
| Nanticoke (Port Dover)Ice Accretion2023RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
| Nanticoke (Port Dover)Ice Accretion2025RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2025 | 22.9175 | 27.5192 | 33.3427 | 37.7989 | 42.2402
| Nanticoke (Port Dover)Ice Accretion2030RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2030 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
| Nanticoke (Port Dover)Ice Accretion2035RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2035 | 22.6651 | 27.2464 | 33.048 | 37.4787 | 41.8975
| Nanticoke (Port Dover)Ice Accretion2040RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2040 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
| Nanticoke (Port Dover)Ice Accretion2045RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2045 | 22.4127 | 26.9736 | 32.7533 | 37.1585 | 41.5548
| Nanticoke (Port Dover)Ice Accretion2050RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2050 | 21.7945 | 26.2954 | 31.9872 | 36.3223 | 40.6466
| Nanticoke (Port Dover)Ice Accretion2055RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2055 | 21.3024 | 25.7536 | 31.3684 | 35.6461 | 39.9097
| Nanticoke (Port Dover)Ice Accretion2060RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2060 | 20.8103 | 25.2117 | 30.7496 | 34.9699 | 39.1729
| Nanticoke (Port Dover)Ice Accretion2065RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2065 | 20.3181 | 24.6699 | 30.1308 | 34.2937 | 38.436
| Nanticoke (Port Dover)Ice Accretion2070RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2070 | 19.826 | 24.1281 | 29.512 | 33.6175 | 37.6992
| Nanticoke (Port Dover)Ice Accretion2075RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2075 | 19.5895 | 23.8647 | 29.2117 | 33.2909 | 37.3422
| Nanticoke (Port Dover)Ice Accretion2080RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2080 | 19.3529 | 23.6013 | 28.9113 | 32.9644 | 36.9852
| Nanticoke (Port Dover)Ice Accretion2085RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2085 | 19.1163 | 23.3379 | 28.611 | 32.6378 | 36.6282
| Nanticoke (Port Dover)Ice Accretion2090RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2090 | 18.8797 | 23.0746 | 28.3107 | 32.3112 | 36.2712
| Nanticoke (Port Dover)Ice Accretion2095RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2095 | 18.6431 | 22.8112 | 28.0103 | 31.9846 | 35.9142
| Nanticoke (Port Dover)Ice Accretion2100RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2100 | 18.4065 | 22.5478 | 27.71 | 31.6581 | 35.5572
| Nanticoke (Port Dover)Ice Accretion2023RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
| Nanticoke (Port Dover)Ice Accretion2025RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2025 | 22.9175 | 27.5192 | 33.3427 | 37.7989 | 42.2402
| Nanticoke (Port Dover)Ice Accretion2030RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2030 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
| Nanticoke (Port Dover)Ice Accretion2035RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2035 | 22.6651 | 27.2464 | 33.048 | 37.4787 | 41.8975
| Nanticoke (Port Dover)Ice Accretion2040RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2040 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
| Nanticoke (Port Dover)Ice Accretion2045RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2045 | 22.4127 | 26.9736 | 32.7533 | 37.1585 | 41.5548
| Nanticoke (Port Dover)Ice Accretion2050RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2050 | 21.7945 | 26.2954 | 31.9872 | 36.3223 | 40.6466
| Nanticoke (Port Dover)Ice Accretion2055RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2055 | 21.3024 | 25.7536 | 31.3684 | 35.6461 | 39.9097
| Nanticoke (Port Dover)Ice Accretion2060RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2060 | 20.8103 | 25.2117 | 30.7496 | 34.9699 | 39.1729
| Nanticoke (Port Dover)Ice Accretion2065RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2065 | 20.3181 | 24.6699 | 30.1308 | 34.2937 | 38.436
| Nanticoke (Port Dover)Ice Accretion2070RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2070 | 19.826 | 24.1281 | 29.512 | 33.6175 | 37.6992
| Nanticoke (Port Dover)Ice Accretion2075RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2075 | 19.4712 | 23.733 | 29.0615 | 33.1276 | 37.1637
| Nanticoke (Port Dover)Ice Accretion2080RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2080 | 19.1163 | 23.3379 | 28.611 | 32.6378 | 36.6282
| Nanticoke (Port Dover)Ice Accretion2085RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2085 | 18.7614 | 22.9429 | 28.1605 | 32.1479 | 36.0927
| Nanticoke (Port Dover)Ice Accretion2090RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2090 | 17.4365 | 21.4002 | 26.3613 | 30.1341 | 33.8722
| Nanticoke (Port Dover)Ice Accretion2095RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2095 | 16.4665 | 20.2526 | 25.0127 | 28.6101 | 32.1871
| Nanticoke (Port Dover)Ice Accretion2100RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2100 | 15.4965 | 19.1049 | 23.664 | 27.0861 | 30.5021
| Nanticoke (Port Dover)Ice Accretion2023RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
| Nanticoke (Port Dover)Ice Accretion2025RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2025 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
| Nanticoke (Port Dover)Ice Accretion2030RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2030 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
| Nanticoke (Port Dover)Ice Accretion2035RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2035 | 22.2866 | 26.8372 | 32.606 | 36.9985 | 41.3834
| Nanticoke (Port Dover)Ice Accretion2040RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2040 | 21.4664 | 25.9342 | 31.5747 | 35.8715 | 40.1554
| Nanticoke (Port Dover)Ice Accretion2045RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2045 | 20.6462 | 25.0311 | 30.5433 | 34.7445 | 38.9273
| Nanticoke (Port Dover)Ice Accretion2050RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2050 | 19.3529 | 23.6013 | 28.9113 | 32.9644 | 36.9852
| Nanticoke (Port Dover)Ice Accretion2055RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2055 | 18.8797 | 23.0746 | 28.3107 | 32.3112 | 36.2712
| Nanticoke (Port Dover)Ice Accretion2060RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2060 | 17.4365 | 21.4002 | 26.3613 | 30.1341 | 33.8722
| Nanticoke (Port Dover)Ice Accretion2065RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2065 | 16.4665 | 20.2526 | 25.0127 | 28.6101 | 32.1871
| Nanticoke (Port Dover)Ice Accretion2070RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2070 | 15.0312 | 18.5876 | 23.052 | 26.4073 | 29.7595
| Nanticoke (Port Dover)Ice Accretion2075RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2075 | 14.5659 | 18.0702 | 22.44 | 25.7286 | 29.017
| Nanticoke (Port Dover)Ice Accretion2080RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2080 | 14.1006 | 17.5528 | 21.828 | 25.0498 | 28.2744
| Nanticoke (Port Dover)Ice Accretion2085RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2085 | 13.0596 | 16.297 | 20.332 | 23.3594 | 26.3894
| Nanticoke (Port Dover)Ice Accretion2090RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2090 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
| Nanticoke (Port Dover)Ice Accretion2095RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2095 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
| Nanticoke (Port Dover)Ice Accretion2100RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2100 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
| Nanticoke (Port Dover)Wind2023RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2023 | 88.6477 | 95.5809 | 102.8976 | 110.1877 | 117.4893
| Nanticoke (Port Dover)Wind2025RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2025 | 88.724 | 95.6821 | 103.0319 | 110.3515 | 117.6792
| Nanticoke (Port Dover)Wind2030RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2030 | 88.8004 | 95.7833 | 103.1662 | 110.5152 | 117.8692
| Nanticoke (Port Dover)Wind2035RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2035 | 88.8767 | 95.8845 | 103.3005 | 110.6789 | 118.0591
| Nanticoke (Port Dover)Wind2040RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2040 | 88.953 | 95.9857 | 103.4348 | 110.8426 | 118.249
| Nanticoke (Port Dover)Wind2045RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2045 | 89.0294 | 96.0869 | 103.5691 | 111.0063 | 118.4389
| Nanticoke (Port Dover)Wind2050RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2050 | 89.185 | 96.2943 | 103.8442 | 111.3381 | 118.8289
| Nanticoke (Port Dover)Wind2055RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2055 | 89.2642 | 96.4005 | 103.9849 | 111.5062 | 119.0289
| Nanticoke (Port Dover)Wind2060RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2060 | 89.3435 | 96.5068 | 104.1257 | 111.6742 | 119.2289
| Nanticoke (Port Dover)Wind2065RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2065 | 89.4228 | 96.613 | 104.2664 | 111.8423 | 119.4289
| Nanticoke (Port Dover)Wind2070RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2070 | 89.502 | 96.7193 | 104.4072 | 112.0104 | 119.6289
| Nanticoke (Port Dover)Wind2075RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2075 | 89.6224 | 96.8742 | 104.6061 | 112.2469 | 119.906
| Nanticoke (Port Dover)Wind2080RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2080 | 89.7428 | 97.0291 | 104.805 | 112.4833 | 120.1831
| Nanticoke (Port Dover)Wind2085RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2085 | 89.8631 | 97.1841 | 105.0039 | 112.7198 | 120.4603
| Nanticoke (Port Dover)Wind2090RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2090 | 89.9835 | 97.339 | 105.2028 | 112.9563 | 120.7374
| Nanticoke (Port Dover)Wind2095RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2095 | 90.1039 | 97.4939 | 105.4017 | 113.1927 | 121.0145
| Nanticoke (Port Dover)Wind2100RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2100 | 90.2242 | 97.6489 | 105.6006 | 113.4292 | 121.2917
| Nanticoke (Port Dover)Wind2023RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2023 | 88.6477 | 95.5809 | 102.8976 | 110.1877 | 117.4893
| Nanticoke (Port Dover)Wind2025RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2025 | 88.724 | 95.6821 | 103.0319 | 110.3515 | 117.6792
| Nanticoke (Port Dover)Wind2030RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2030 | 88.8004 | 95.7833 | 103.1662 | 110.5152 | 117.8692
| Nanticoke (Port Dover)Wind2035RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2035 | 88.8767 | 95.8845 | 103.3005 | 110.6789 | 118.0591
| Nanticoke (Port Dover)Wind2040RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2040 | 88.953 | 95.9857 | 103.4348 | 110.8426 | 118.249
| Nanticoke (Port Dover)Wind2045RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2045 | 89.0294 | 96.0869 | 103.5691 | 111.0063 | 118.4389
| Nanticoke (Port Dover)Wind2050RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2050 | 89.185 | 96.2943 | 103.8442 | 111.3381 | 118.8289
| Nanticoke (Port Dover)Wind2055RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2055 | 89.2642 | 96.4005 | 103.9849 | 111.5062 | 119.0289
| Nanticoke (Port Dover)Wind2060RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2060 | 89.3435 | 96.5068 | 104.1257 | 111.6742 | 119.2289
| Nanticoke (Port Dover)Wind2065RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2065 | 89.4228 | 96.613 | 104.2664 | 111.8423 | 119.4289
| Nanticoke (Port Dover)Wind2070RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2070 | 89.502 | 96.7193 | 104.4072 | 112.0104 | 119.6289
| Nanticoke (Port Dover)Wind2075RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2075 | 89.6826 | 96.9517 | 104.7056 | 112.3651 | 120.0446
| Nanticoke (Port Dover)Wind2080RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2080 | 89.8631 | 97.1841 | 105.0039 | 112.7198 | 120.4603
| Nanticoke (Port Dover)Wind2085RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2085 | 90.0437 | 97.4165 | 105.3022 | 113.0745 | 120.876
| Nanticoke (Port Dover)Wind2090RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2090 | 90.4826 | 97.9841 | 106.0256 | 113.9349 | 121.8731
| Nanticoke (Port Dover)Wind2095RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2095 | 90.741 | 98.3192 | 106.4506 | 114.4406 | 122.4545
| Nanticoke (Port Dover)Wind2100RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2100 | 90.9993 | 98.6544 | 106.8756 | 114.9462 | 123.0359
| Nanticoke (Port Dover)Wind2023RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2023 | 88.6477 | 95.5809 | 102.8976 | 110.1877 | 117.4893
| Nanticoke (Port Dover)Wind2025RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2025 | 88.8004 | 95.7833 | 103.1662 | 110.5152 | 117.8692
| Nanticoke (Port Dover)Wind2030RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2030 | 88.953 | 95.9857 | 103.4348 | 110.8426 | 118.249
| Nanticoke (Port Dover)Wind2035RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2035 | 89.1057 | 96.188 | 103.7034 | 111.17 | 118.6289
| Nanticoke (Port Dover)Wind2040RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2040 | 89.2378 | 96.3651 | 103.938 | 111.4501 | 118.9622
| Nanticoke (Port Dover)Wind2045RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2045 | 89.3699 | 96.5422 | 104.1726 | 111.7303 | 119.2955
| Nanticoke (Port Dover)Wind2050RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2050 | 89.7428 | 97.0291 | 104.805 | 112.4833 | 120.1831
| Nanticoke (Port Dover)Wind2055RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2055 | 89.9835 | 97.339 | 105.2028 | 112.9563 | 120.7374
| Nanticoke (Port Dover)Wind2060RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2060 | 90.4826 | 97.9841 | 106.0256 | 113.9349 | 121.8731
| Nanticoke (Port Dover)Wind2065RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2065 | 90.741 | 98.3192 | 106.4506 | 114.4406 | 122.4545
| Nanticoke (Port Dover)Wind2070RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2070 | 91.149 | 98.8663 | 107.168 | 115.3064 | 123.4661
| Nanticoke (Port Dover)Wind2075RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2075 | 91.2988 | 99.0781 | 107.4604 | 115.6666 | 123.8963
| Nanticoke (Port Dover)Wind2080RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2080 | 91.4485 | 99.29 | 107.7528 | 116.0267 | 124.3266
| Nanticoke (Port Dover)Wind2085RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2085 | 91.792 | 99.7405 | 108.3495 | 116.7361 | 125.1638
| Nanticoke (Port Dover)Wind2090RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2090 | 92.1355 | 100.1911 | 108.9462 | 117.4456 | 126.001
| Nanticoke (Port Dover)Wind2095RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2095 | 92.1355 | 100.1911 | 108.9462 | 117.4456 | 126.001
| Nanticoke (Port Dover)Wind2100RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2100 | 92.1355 | 100.1911 | 108.9462 | 117.4456 | 126.001
| NapaneeIce Accretion2023RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2023 | 18.1825 | 21.6663 | 26.078 | 29.4681 | 32.8583
| NapaneeIce Accretion2025RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2025 | 18.2126 | 21.7095 | 26.1343 | 29.5367 | 32.9347
| NapaneeIce Accretion2030RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2030 | 18.2428 | 21.7526 | 26.1907 | 29.6052 | 33.0112
| NapaneeIce Accretion2035RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2035 | 18.2729 | 21.7958 | 26.247 | 29.6738 | 33.0876
| NapaneeIce Accretion2040RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2040 | 18.3031 | 21.839 | 26.3033 | 29.7424 | 33.164
| NapaneeIce Accretion2045RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2045 | 18.3332 | 21.8821 | 26.3597 | 29.8109 | 33.2405
| NapaneeIce Accretion2050RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2050 | 18.2874 | 21.8476 | 26.338 | 29.7972 | 33.2317
| NapaneeIce Accretion2055RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2055 | 18.2114 | 21.7699 | 26.26 | 29.7149 | 33.1466
| NapaneeIce Accretion2060RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2060 | 18.1354 | 21.6922 | 26.182 | 29.6327 | 33.0614
| NapaneeIce Accretion2065RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2065 | 18.0594 | 21.6145 | 26.104 | 29.5504 | 32.9762
| NapaneeIce Accretion2070RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2070 | 17.9834 | 21.5368 | 26.026 | 29.4681 | 32.891
| NapaneeIce Accretion2075RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2075 | 18.0196 | 21.6088 | 26.143 | 29.615 | 33.0712
| NapaneeIce Accretion2080RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2080 | 18.0558 | 21.6807 | 26.26 | 29.7619 | 33.2514
| NapaneeIce Accretion2085RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2085 | 18.092 | 21.7526 | 26.377 | 29.9088 | 33.4316
| NapaneeIce Accretion2090RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2090 | 18.1282 | 21.8246 | 26.494 | 30.0557 | 33.6118
| NapaneeIce Accretion2095RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2095 | 18.1644 | 21.8965 | 26.611 | 30.2026 | 33.7919
| NapaneeIce Accretion2100RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2100 | 18.2006 | 21.9684 | 26.728 | 30.3495 | 33.9721
| NapaneeIce Accretion2023RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2023 | 18.1825 | 21.6663 | 26.078 | 29.4681 | 32.8583
| NapaneeIce Accretion2025RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2025 | 18.2126 | 21.7095 | 26.1343 | 29.5367 | 32.9347
| NapaneeIce Accretion2030RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2030 | 18.2428 | 21.7526 | 26.1907 | 29.6052 | 33.0112
| NapaneeIce Accretion2035RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2035 | 18.2729 | 21.7958 | 26.247 | 29.6738 | 33.0876
| NapaneeIce Accretion2040RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2040 | 18.3031 | 21.839 | 26.3033 | 29.7424 | 33.164
| NapaneeIce Accretion2045RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2045 | 18.3332 | 21.8821 | 26.3597 | 29.8109 | 33.2405
| NapaneeIce Accretion2050RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2050 | 18.2874 | 21.8476 | 26.338 | 29.7972 | 33.2317
| NapaneeIce Accretion2055RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2055 | 18.2114 | 21.7699 | 26.26 | 29.7149 | 33.1466
| NapaneeIce Accretion2060RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2060 | 18.1354 | 21.6922 | 26.182 | 29.6327 | 33.0614
| NapaneeIce Accretion2065RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2065 | 18.0594 | 21.6145 | 26.104 | 29.5504 | 32.9762
| NapaneeIce Accretion2070RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2070 | 17.9834 | 21.5368 | 26.026 | 29.4681 | 32.891
| NapaneeIce Accretion2075RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2075 | 18.0377 | 21.6447 | 26.2015 | 29.6885 | 33.1613
| NapaneeIce Accretion2080RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2080 | 18.092 | 21.7526 | 26.377 | 29.9088 | 33.4316
| NapaneeIce Accretion2085RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2085 | 18.1463 | 21.8605 | 26.5525 | 30.1292 | 33.7018
| NapaneeIce Accretion2090RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2090 | 18.0076 | 21.7742 | 26.5287 | 30.1439 | 33.7646
| NapaneeIce Accretion2095RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2095 | 17.8146 | 21.58 | 26.3293 | 29.9382 | 33.5572
| NapaneeIce Accretion2100RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2100 | 17.6216 | 21.3858 | 26.13 | 29.7326 | 33.3497
| NapaneeIce Accretion2023RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2023 | 18.1825 | 21.6663 | 26.078 | 29.4681 | 32.8583
| NapaneeIce Accretion2025RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2025 | 18.2428 | 21.7526 | 26.1907 | 29.6052 | 33.0112
| NapaneeIce Accretion2030RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2030 | 18.3031 | 21.839 | 26.3033 | 29.7424 | 33.164
| NapaneeIce Accretion2035RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2035 | 18.3634 | 21.9253 | 26.416 | 29.8795 | 33.3169
| NapaneeIce Accretion2040RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2040 | 18.2367 | 21.7958 | 26.286 | 29.7424 | 33.175
| NapaneeIce Accretion2045RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2045 | 18.1101 | 21.6663 | 26.156 | 29.6052 | 33.033
| NapaneeIce Accretion2050RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2050 | 18.0558 | 21.6807 | 26.26 | 29.7619 | 33.2514
| NapaneeIce Accretion2055RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2055 | 18.1282 | 21.8246 | 26.494 | 30.0557 | 33.6118
| NapaneeIce Accretion2060RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2060 | 18.0076 | 21.7742 | 26.5287 | 30.1439 | 33.7646
| NapaneeIce Accretion2065RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2065 | 17.8146 | 21.58 | 26.3293 | 29.9382 | 33.5572
| NapaneeIce Accretion2070RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2070 | 17.2779 | 20.9973 | 25.6793 | 29.2429 | 32.8037
| NapaneeIce Accretion2075RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2075 | 16.9341 | 20.6089 | 25.2287 | 28.7532 | 32.2577
| NapaneeIce Accretion2080RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2080 | 16.5904 | 20.2205 | 24.778 | 28.2636 | 31.7117
| NapaneeIce Accretion2085RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2085 | 15.8938 | 19.4004 | 23.803 | 27.1618 | 30.4996
| NapaneeIce Accretion2090RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2090 | 15.1973 | 18.5804 | 22.828 | 26.0601 | 29.2874
| NapaneeIce Accretion2095RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2095 | 15.1973 | 18.5804 | 22.828 | 26.0601 | 29.2874
| NapaneeIce Accretion2100RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2100 | 15.1973 | 18.5804 | 22.828 | 26.0601 | 29.2874
| NapaneeWind2023RCP4.5 | Napanee | Wind | RCP4.5 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.3568
| NapaneeWind2025RCP4.5 | Napanee | Wind | RCP4.5 | 2025 | 85.0176 | 91.5972 | 98.5341 | 105.4647 | 112.3885
| NapaneeWind2030RCP4.5 | Napanee | Wind | RCP4.5 | 2030 | 85.0331 | 91.617 | 98.5586 | 105.4927 | 112.4201
| NapaneeWind2035RCP4.5 | Napanee | Wind | RCP4.5 | 2035 | 85.0486 | 91.6367 | 98.5831 | 105.5206 | 112.4518
| NapaneeWind2040RCP4.5 | Napanee | Wind | RCP4.5 | 2040 | 85.0641 | 91.6565 | 98.6076 | 105.5486 | 112.4834
| NapaneeWind2045RCP4.5 | Napanee | Wind | RCP4.5 | 2045 | 85.0796 | 91.6762 | 98.6321 | 105.5765 | 112.5151
| NapaneeWind2050RCP4.5 | Napanee | Wind | RCP4.5 | 2050 | 85.1747 | 91.7944 | 98.7781 | 105.745 | 112.7076
| NapaneeWind2055RCP4.5 | Napanee | Wind | RCP4.5 | 2055 | 85.2542 | 91.8928 | 98.8996 | 105.8855 | 112.8685
| NapaneeWind2060RCP4.5 | Napanee | Wind | RCP4.5 | 2060 | 85.3338 | 91.9912 | 99.0212 | 106.026 | 113.0294
| NapaneeWind2065RCP4.5 | Napanee | Wind | RCP4.5 | 2065 | 85.4133 | 92.0897 | 99.1427 | 106.1666 | 113.1902
| NapaneeWind2070RCP4.5 | Napanee | Wind | RCP4.5 | 2070 | 85.4929 | 92.1881 | 99.2642 | 106.3071 | 113.3511
| NapaneeWind2075RCP4.5 | Napanee | Wind | RCP4.5 | 2075 | 85.5549 | 92.2671 | 99.3638 | 106.4259 | 113.4889
| NapaneeWind2080RCP4.5 | Napanee | Wind | RCP4.5 | 2080 | 85.617 | 92.3461 | 99.4635 | 106.5448 | 113.6267
| NapaneeWind2085RCP4.5 | Napanee | Wind | RCP4.5 | 2085 | 85.679 | 92.4251 | 99.5631 | 106.6636 | 113.7645
| NapaneeWind2090RCP4.5 | Napanee | Wind | RCP4.5 | 2090 | 85.7411 | 92.5041 | 99.6627 | 106.7824 | 113.9023
| NapaneeWind2095RCP4.5 | Napanee | Wind | RCP4.5 | 2095 | 85.8032 | 92.5831 | 99.7624 | 106.9013 | 114.0401
| NapaneeWind2100RCP4.5 | Napanee | Wind | RCP4.5 | 2100 | 85.8652 | 92.662 | 99.862 | 107.0201 | 114.1778
| NapaneeWind2023RCP6.0 | Napanee | Wind | RCP6.0 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.3568
| NapaneeWind2025RCP6.0 | Napanee | Wind | RCP6.0 | 2025 | 85.0176 | 91.5972 | 98.5341 | 105.4647 | 112.3885
| NapaneeWind2030RCP6.0 | Napanee | Wind | RCP6.0 | 2030 | 85.0331 | 91.617 | 98.5586 | 105.4927 | 112.4201
| NapaneeWind2035RCP6.0 | Napanee | Wind | RCP6.0 | 2035 | 85.0486 | 91.6367 | 98.5831 | 105.5206 | 112.4518
| NapaneeWind2040RCP6.0 | Napanee | Wind | RCP6.0 | 2040 | 85.0641 | 91.6565 | 98.6076 | 105.5486 | 112.4834
| NapaneeWind2045RCP6.0 | Napanee | Wind | RCP6.0 | 2045 | 85.0796 | 91.6762 | 98.6321 | 105.5765 | 112.5151
| NapaneeWind2050RCP6.0 | Napanee | Wind | RCP6.0 | 2050 | 85.1747 | 91.7944 | 98.7781 | 105.745 | 112.7076
| NapaneeWind2055RCP6.0 | Napanee | Wind | RCP6.0 | 2055 | 85.2542 | 91.8928 | 98.8996 | 105.8855 | 112.8685
| NapaneeWind2060RCP6.0 | Napanee | Wind | RCP6.0 | 2060 | 85.3338 | 91.9912 | 99.0212 | 106.026 | 113.0294
| NapaneeWind2065RCP6.0 | Napanee | Wind | RCP6.0 | 2065 | 85.4133 | 92.0897 | 99.1427 | 106.1666 | 113.1902
| NapaneeWind2070RCP6.0 | Napanee | Wind | RCP6.0 | 2070 | 85.4929 | 92.1881 | 99.2642 | 106.3071 | 113.3511
| NapaneeWind2075RCP6.0 | Napanee | Wind | RCP6.0 | 2075 | 85.586 | 92.3066 | 99.4136 | 106.4853 | 113.5578
| NapaneeWind2080RCP6.0 | Napanee | Wind | RCP6.0 | 2080 | 85.679 | 92.4251 | 99.5631 | 106.6636 | 113.7645
| NapaneeWind2085RCP6.0 | Napanee | Wind | RCP6.0 | 2085 | 85.7721 | 92.5436 | 99.7125 | 106.8419 | 113.9712
| NapaneeWind2090RCP6.0 | Napanee | Wind | RCP6.0 | 2090 | 86.0091 | 92.817 | 100.0253 | 107.1914 | 114.3603
| NapaneeWind2095RCP6.0 | Napanee | Wind | RCP6.0 | 2095 | 86.1529 | 92.9719 | 100.1887 | 107.3627 | 114.5428
| NapaneeWind2100RCP6.0 | Napanee | Wind | RCP6.0 | 2100 | 86.2968 | 93.1269 | 100.352 | 107.5339 | 114.7253
| NapaneeWind2023RCP8.5 | Napanee | Wind | RCP8.5 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.3568
| NapaneeWind2025RCP8.5 | Napanee | Wind | RCP8.5 | 2025 | 85.0331 | 91.617 | 98.5586 | 105.4927 | 112.4201
| NapaneeWind2030RCP8.5 | Napanee | Wind | RCP8.5 | 2030 | 85.0641 | 91.6565 | 98.6076 | 105.5486 | 112.4834
| NapaneeWind2035RCP8.5 | Napanee | Wind | RCP8.5 | 2035 | 85.0952 | 91.696 | 98.6566 | 105.6045 | 112.5467
| NapaneeWind2040RCP8.5 | Napanee | Wind | RCP8.5 | 2040 | 85.2277 | 91.86 | 98.8591 | 105.8387 | 112.8149
| NapaneeWind2045RCP8.5 | Napanee | Wind | RCP8.5 | 2045 | 85.3603 | 92.0241 | 99.0617 | 106.0729 | 113.083
| NapaneeWind2050RCP8.5 | Napanee | Wind | RCP8.5 | 2050 | 85.617 | 92.3461 | 99.4635 | 106.5448 | 113.6267
| NapaneeWind2055RCP8.5 | Napanee | Wind | RCP8.5 | 2055 | 85.7411 | 92.5041 | 99.6627 | 106.7824 | 113.9023
| NapaneeWind2060RCP8.5 | Napanee | Wind | RCP8.5 | 2060 | 86.0091 | 92.817 | 100.0253 | 107.1914 | 114.3603
| NapaneeWind2065RCP8.5 | Napanee | Wind | RCP8.5 | 2065 | 86.1529 | 92.9719 | 100.1887 | 107.3627 | 114.5428
| NapaneeWind2070RCP8.5 | Napanee | Wind | RCP8.5 | 2070 | 86.3081 | 93.142 | 100.3749 | 107.5619 | 114.7588
| NapaneeWind2075RCP8.5 | Napanee | Wind | RCP8.5 | 2075 | 86.3193 | 93.1572 | 100.3977 | 107.5899 | 114.7923
| NapaneeWind2080RCP8.5 | Napanee | Wind | RCP8.5 | 2080 | 86.3306 | 93.1724 | 100.4206 | 107.6178 | 114.8258
| NapaneeWind2085RCP8.5 | Napanee | Wind | RCP8.5 | 2085 | 86.4279 | 93.3091 | 100.6117 | 107.8538 | 115.1051
| NapaneeWind2090RCP8.5 | Napanee | Wind | RCP8.5 | 2090 | 86.5253 | 93.4458 | 100.8028 | 108.0897 | 115.3844
| NapaneeWind2095RCP8.5 | Napanee | Wind | RCP8.5 | 2095 | 86.5253 | 93.4458 | 100.8028 | 108.0897 | 115.3844
| NapaneeWind2100RCP8.5 | Napanee | Wind | RCP8.5 | 2100 | 86.5253 | 93.4458 | 100.8028 | 108.0897 | 115.3844
| New LiskeardIce Accretion2023RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2023 | 14.7519 | 17.6458 | 21.32 | 24.1142 | 26.9136
| New LiskeardIce Accretion2025RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2025 | 14.7311 | 17.6209 | 21.2867 | 24.0765 | 26.8716
| New LiskeardIce Accretion2030RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2030 | 14.7102 | 17.596 | 21.2533 | 24.0389 | 26.8296
| New LiskeardIce Accretion2035RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2035 | 14.6893 | 17.5711 | 21.22 | 24.0012 | 26.7876
| New LiskeardIce Accretion2040RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2040 | 14.6684 | 17.5462 | 21.1867 | 23.9635 | 26.7456
| New LiskeardIce Accretion2045RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2045 | 14.6476 | 17.5213 | 21.1533 | 23.9259 | 26.7036
| New LiskeardIce Accretion2050RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2050 | 14.635 | 17.5064 | 21.128 | 23.8972 | 26.6717
| New LiskeardIce Accretion2055RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2055 | 14.6434 | 17.5163 | 21.136 | 23.9063 | 26.6818
| New LiskeardIce Accretion2060RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2060 | 14.6517 | 17.5263 | 21.144 | 23.9153 | 26.6918
| New LiskeardIce Accretion2065RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2065 | 14.6601 | 17.5362 | 21.152 | 23.9244 | 26.7019
| New LiskeardIce Accretion2070RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2070 | 14.6684 | 17.5462 | 21.16 | 23.9334 | 26.712
| New LiskeardIce Accretion2075RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2075 | 14.7055 | 17.5988 | 21.2367 | 24.0276 | 26.8212
| New LiskeardIce Accretion2080RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2080 | 14.7427 | 17.6513 | 21.3133 | 24.1217 | 26.9304
| New LiskeardIce Accretion2085RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2085 | 14.7798 | 17.7039 | 21.39 | 24.2159 | 27.0396
| New LiskeardIce Accretion2090RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2090 | 14.8169 | 17.7565 | 21.4667 | 24.3101 | 27.1488
| New LiskeardIce Accretion2095RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2095 | 14.854 | 17.809 | 21.5433 | 24.4042 | 27.258
| New LiskeardIce Accretion2100RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2100 | 14.8911 | 17.8616 | 21.62 | 24.4984 | 27.3672
| New LiskeardIce Accretion2023RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2023 | 14.7519 | 17.6458 | 21.32 | 24.1142 | 26.9136
| New LiskeardIce Accretion2025RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2025 | 14.7311 | 17.6209 | 21.2867 | 24.0765 | 26.8716
| New LiskeardIce Accretion2030RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2030 | 14.7102 | 17.596 | 21.2533 | 24.0389 | 26.8296
| New LiskeardIce Accretion2035RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2035 | 14.6893 | 17.5711 | 21.22 | 24.0012 | 26.7876
| New LiskeardIce Accretion2040RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2040 | 14.6684 | 17.5462 | 21.1867 | 23.9635 | 26.7456
| New LiskeardIce Accretion2045RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2045 | 14.6476 | 17.5213 | 21.1533 | 23.9259 | 26.7036
| New LiskeardIce Accretion2050RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2050 | 14.635 | 17.5064 | 21.128 | 23.8972 | 26.6717
| New LiskeardIce Accretion2055RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2055 | 14.6434 | 17.5163 | 21.136 | 23.9063 | 26.6818
| New LiskeardIce Accretion2060RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2060 | 14.6517 | 17.5263 | 21.144 | 23.9153 | 26.6918
| New LiskeardIce Accretion2065RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2065 | 14.6601 | 17.5362 | 21.152 | 23.9244 | 26.7019
| New LiskeardIce Accretion2070RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2070 | 14.6684 | 17.5462 | 21.16 | 23.9334 | 26.712
| New LiskeardIce Accretion2075RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2075 | 14.7241 | 17.625 | 21.275 | 24.0746 | 26.8758
| New LiskeardIce Accretion2080RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2080 | 14.7798 | 17.7039 | 21.39 | 24.2159 | 27.0396
| New LiskeardIce Accretion2085RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2085 | 14.8354 | 17.7828 | 21.505 | 24.3571 | 27.2034
| New LiskeardIce Accretion2090RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2090 | 14.9375 | 17.9225 | 21.7067 | 24.6039 | 27.4848
| New LiskeardIce Accretion2095RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2095 | 14.9839 | 17.9833 | 21.7933 | 24.7093 | 27.6024
| New LiskeardIce Accretion2100RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2100 | 15.0303 | 18.0442 | 21.88 | 24.8148 | 27.72
| New LiskeardIce Accretion2023RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2023 | 14.7519 | 17.6458 | 21.32 | 24.1142 | 26.9136
| New LiskeardIce Accretion2025RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2025 | 14.7102 | 17.596 | 21.2533 | 24.0389 | 26.8296
| New LiskeardIce Accretion2030RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2030 | 14.6684 | 17.5462 | 21.1867 | 23.9635 | 26.7456
| New LiskeardIce Accretion2035RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2035 | 14.6267 | 17.4964 | 21.12 | 23.8882 | 26.6616
| New LiskeardIce Accretion2040RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2040 | 14.6406 | 17.513 | 21.1333 | 23.9033 | 26.6784
| New LiskeardIce Accretion2045RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2045 | 14.6545 | 17.5296 | 21.1467 | 23.9183 | 26.6952
| New LiskeardIce Accretion2050RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2050 | 14.7427 | 17.6513 | 21.3133 | 24.1217 | 26.9304
| New LiskeardIce Accretion2055RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2055 | 14.8169 | 17.7565 | 21.4667 | 24.3101 | 27.1488
| New LiskeardIce Accretion2060RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2060 | 14.9375 | 17.9225 | 21.7067 | 24.6039 | 27.4848
| New LiskeardIce Accretion2065RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2065 | 14.9839 | 17.9833 | 21.7933 | 24.7093 | 27.6024
| New LiskeardIce Accretion2070RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2070 | 14.8633 | 17.8616 | 21.6667 | 24.5737 | 27.4596
| New LiskeardIce Accretion2075RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2075 | 14.6963 | 17.679 | 21.4533 | 24.3327 | 27.1992
| New LiskeardIce Accretion2080RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2080 | 14.5293 | 17.4964 | 21.24 | 24.0916 | 26.9388
| New LiskeardIce Accretion2085RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2085 | 14.5641 | 17.5711 | 21.36 | 24.2611 | 27.1404
| New LiskeardIce Accretion2090RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2090 | 14.5989 | 17.6458 | 21.48 | 24.4306 | 27.342
| New LiskeardIce Accretion2095RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2095 | 14.5989 | 17.6458 | 21.48 | 24.4306 | 27.342
| New LiskeardIce Accretion2100RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2100 | 14.5989 | 17.6458 | 21.48 | 24.4306 | 27.342
| New LiskeardWind2023RCP4.5 | New Liskeard | Wind | RCP4.5 | 2023 | 76.1156 | 81.9218 | 88.0088 | 94.1129 | 100.2197
| New LiskeardWind2025RCP4.5 | New Liskeard | Wind | RCP4.5 | 2025 | 76.122 | 81.9259 | 88.0132 | 94.1176 | 100.223
| New LiskeardWind2030RCP4.5 | New Liskeard | Wind | RCP4.5 | 2030 | 76.1283 | 81.93 | 88.0176 | 94.1223 | 100.2264
| New LiskeardWind2035RCP4.5 | New Liskeard | Wind | RCP4.5 | 2035 | 76.1346 | 81.9341 | 88.022 | 94.127 | 100.2297
| New LiskeardWind2040RCP4.5 | New Liskeard | Wind | RCP4.5 | 2040 | 76.141 | 81.9382 | 88.0264 | 94.1318 | 100.2331
| New LiskeardWind2045RCP4.5 | New Liskeard | Wind | RCP4.5 | 2045 | 76.1473 | 81.9423 | 88.0308 | 94.1365 | 100.2364
| New LiskeardWind2050RCP4.5 | New Liskeard | Wind | RCP4.5 | 2050 | 76.1551 | 81.9448 | 88.0246 | 94.1261 | 100.2197
| New LiskeardWind2055RCP4.5 | New Liskeard | Wind | RCP4.5 | 2055 | 76.1567 | 81.9431 | 88.0141 | 94.111 | 100.1996
| New LiskeardWind2060RCP4.5 | New Liskeard | Wind | RCP4.5 | 2060 | 76.1582 | 81.9415 | 88.0035 | 94.096 | 100.1796
| New LiskeardWind2065RCP4.5 | New Liskeard | Wind | RCP4.5 | 2065 | 76.1597 | 81.9398 | 87.993 | 94.0809 | 100.1595
| New LiskeardWind2070RCP4.5 | New Liskeard | Wind | RCP4.5 | 2070 | 76.1612 | 81.9382 | 87.9824 | 94.0658 | 100.1394
| New LiskeardWind2075RCP4.5 | New Liskeard | Wind | RCP4.5 | 2075 | 76.2182 | 82.0078 | 88.0689 | 94.1647 | 100.2514
| New LiskeardWind2080RCP4.5 | New Liskeard | Wind | RCP4.5 | 2080 | 76.2752 | 82.0773 | 88.1555 | 94.2636 | 100.3635
| New LiskeardWind2085RCP4.5 | New Liskeard | Wind | RCP4.5 | 2085 | 76.3322 | 82.1469 | 88.242 | 94.3624 | 100.4755
| New LiskeardWind2090RCP4.5 | New Liskeard | Wind | RCP4.5 | 2090 | 76.3892 | 82.2165 | 88.3285 | 94.4613 | 100.5875
| New LiskeardWind2095RCP4.5 | New Liskeard | Wind | RCP4.5 | 2095 | 76.4462 | 82.286 | 88.4151 | 94.5602 | 100.6995
| New LiskeardWind2100RCP4.5 | New Liskeard | Wind | RCP4.5 | 2100 | 76.5032 | 82.3556 | 88.5016 | 94.659 | 100.8116
| New LiskeardWind2023RCP6.0 | New Liskeard | Wind | RCP6.0 | 2023 | 76.1156 | 81.9218 | 88.0088 | 94.1129 | 100.2197
| New LiskeardWind2025RCP6.0 | New Liskeard | Wind | RCP6.0 | 2025 | 76.122 | 81.9259 | 88.0132 | 94.1176 | 100.223
| New LiskeardWind2030RCP6.0 | New Liskeard | Wind | RCP6.0 | 2030 | 76.1283 | 81.93 | 88.0176 | 94.1223 | 100.2264
| New LiskeardWind2035RCP6.0 | New Liskeard | Wind | RCP6.0 | 2035 | 76.1346 | 81.9341 | 88.022 | 94.127 | 100.2297
| New LiskeardWind2040RCP6.0 | New Liskeard | Wind | RCP6.0 | 2040 | 76.141 | 81.9382 | 88.0264 | 94.1318 | 100.2331
| New LiskeardWind2045RCP6.0 | New Liskeard | Wind | RCP6.0 | 2045 | 76.1473 | 81.9423 | 88.0308 | 94.1365 | 100.2364
| New LiskeardWind2050RCP6.0 | New Liskeard | Wind | RCP6.0 | 2050 | 76.1551 | 81.9448 | 88.0246 | 94.1261 | 100.2197
| New LiskeardWind2055RCP6.0 | New Liskeard | Wind | RCP6.0 | 2055 | 76.1567 | 81.9431 | 88.0141 | 94.111 | 100.1996
| New LiskeardWind2060RCP6.0 | New Liskeard | Wind | RCP6.0 | 2060 | 76.1582 | 81.9415 | 88.0035 | 94.096 | 100.1796
| New LiskeardWind2065RCP6.0 | New Liskeard | Wind | RCP6.0 | 2065 | 76.1597 | 81.9398 | 87.993 | 94.0809 | 100.1595
| New LiskeardWind2070RCP6.0 | New Liskeard | Wind | RCP6.0 | 2070 | 76.1612 | 81.9382 | 87.9824 | 94.0658 | 100.1394
| New LiskeardWind2075RCP6.0 | New Liskeard | Wind | RCP6.0 | 2075 | 76.2467 | 82.0426 | 88.1122 | 94.2141 | 100.3075
| New LiskeardWind2080RCP6.0 | New Liskeard | Wind | RCP6.0 | 2080 | 76.3322 | 82.1469 | 88.242 | 94.3624 | 100.4755
| New LiskeardWind2085RCP6.0 | New Liskeard | Wind | RCP6.0 | 2085 | 76.4177 | 82.2512 | 88.3718 | 94.5107 | 100.6435
| New LiskeardWind2090RCP6.0 | New Liskeard | Wind | RCP6.0 | 2090 | 76.493 | 82.331 | 88.4576 | 94.6026 | 100.7413
| New LiskeardWind2095RCP6.0 | New Liskeard | Wind | RCP6.0 | 2095 | 76.4829 | 82.3065 | 88.4136 | 94.5461 | 100.6711
| New LiskeardWind2100RCP6.0 | New Liskeard | Wind | RCP6.0 | 2100 | 76.4728 | 82.2819 | 88.3696 | 94.4896 | 100.6009
| New LiskeardWind2023RCP8.5 | New Liskeard | Wind | RCP8.5 | 2023 | 76.1156 | 81.9218 | 88.0088 | 94.1129 | 100.2197
| New LiskeardWind2025RCP8.5 | New Liskeard | Wind | RCP8.5 | 2025 | 76.1283 | 81.93 | 88.0176 | 94.1223 | 100.2264
| New LiskeardWind2030RCP8.5 | New Liskeard | Wind | RCP8.5 | 2030 | 76.141 | 81.9382 | 88.0264 | 94.1318 | 100.2331
| New LiskeardWind2035RCP8.5 | New Liskeard | Wind | RCP8.5 | 2035 | 76.1536 | 81.9464 | 88.0352 | 94.1412 | 100.2397
| New LiskeardWind2040RCP8.5 | New Liskeard | Wind | RCP8.5 | 2040 | 76.1562 | 81.9437 | 88.0176 | 94.1161 | 100.2063
| New LiskeardWind2045RCP8.5 | New Liskeard | Wind | RCP8.5 | 2045 | 76.1587 | 81.9409 | 88 | 94.0909 | 100.1729
| New LiskeardWind2050RCP8.5 | New Liskeard | Wind | RCP8.5 | 2050 | 76.2752 | 82.0773 | 88.1555 | 94.2636 | 100.3635
| New LiskeardWind2055RCP8.5 | New Liskeard | Wind | RCP8.5 | 2055 | 76.3892 | 82.2165 | 88.3285 | 94.4613 | 100.5875
| New LiskeardWind2060RCP8.5 | New Liskeard | Wind | RCP8.5 | 2060 | 76.493 | 82.331 | 88.4576 | 94.6026 | 100.7413
| New LiskeardWind2065RCP8.5 | New Liskeard | Wind | RCP8.5 | 2065 | 76.4829 | 82.3065 | 88.4136 | 94.5461 | 100.6711
| New LiskeardWind2070RCP8.5 | New Liskeard | Wind | RCP8.5 | 2070 | 76.5488 | 82.3665 | 88.4635 | 94.59 | 100.7112
| New LiskeardWind2075RCP8.5 | New Liskeard | Wind | RCP8.5 | 2075 | 76.6247 | 82.4511 | 88.5573 | 94.6904 | 100.8216
| New LiskeardWind2080RCP8.5 | New Liskeard | Wind | RCP8.5 | 2080 | 76.7007 | 82.5356 | 88.6512 | 94.7909 | 100.932
| New LiskeardWind2085RCP8.5 | New Liskeard | Wind | RCP8.5 | 2085 | 76.8299 | 82.7075 | 88.8756 | 95.0592 | 101.248
| New LiskeardWind2090RCP8.5 | New Liskeard | Wind | RCP8.5 | 2090 | 76.9591 | 82.8794 | 89.1 | 95.3276 | 101.564
| New LiskeardWind2095RCP8.5 | New Liskeard | Wind | RCP8.5 | 2095 | 76.9591 | 82.8794 | 89.1 | 95.3276 | 101.564
| New LiskeardWind2100RCP8.5 | New Liskeard | Wind | RCP8.5 | 2100 | 76.9591 | 82.8794 | 89.1 | 95.3276 | 101.564
| NewcastleIce Accretion2023RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| NewcastleIce Accretion2025RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| NewcastleIce Accretion2030RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| NewcastleIce Accretion2035RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| NewcastleIce Accretion2040RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| NewcastleIce Accretion2045RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| NewcastleIce Accretion2050RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| NewcastleIce Accretion2055RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| NewcastleIce Accretion2060RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| NewcastleIce Accretion2065RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| NewcastleIce Accretion2070RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| NewcastleIce Accretion2075RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
| NewcastleIce Accretion2080RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| NewcastleIce Accretion2085RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| NewcastleIce Accretion2090RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| NewcastleIce Accretion2095RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
| NewcastleIce Accretion2100RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
| NewcastleIce Accretion2023RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| NewcastleIce Accretion2025RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| NewcastleIce Accretion2030RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| NewcastleIce Accretion2035RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| NewcastleIce Accretion2040RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| NewcastleIce Accretion2045RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| NewcastleIce Accretion2050RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| NewcastleIce Accretion2055RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| NewcastleIce Accretion2060RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| NewcastleIce Accretion2065RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| NewcastleIce Accretion2070RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| NewcastleIce Accretion2075RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
| NewcastleIce Accretion2080RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| NewcastleIce Accretion2085RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
| NewcastleIce Accretion2090RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| NewcastleIce Accretion2095RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| NewcastleIce Accretion2100RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
| NewcastleIce Accretion2023RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| NewcastleIce Accretion2025RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| NewcastleIce Accretion2030RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| NewcastleIce Accretion2035RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
| NewcastleIce Accretion2040RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
| NewcastleIce Accretion2045RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
| NewcastleIce Accretion2050RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| NewcastleIce Accretion2055RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| NewcastleIce Accretion2060RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| NewcastleIce Accretion2065RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| NewcastleIce Accretion2070RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
| NewcastleIce Accretion2075RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
| NewcastleIce Accretion2080RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
| NewcastleIce Accretion2085RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
| NewcastleIce Accretion2090RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| NewcastleIce Accretion2095RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| NewcastleIce Accretion2100RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| NewcastleWind2023RCP4.5 | Newcastle | Wind | RCP4.5 | 2023 | 85.6899 | 92.2541 | 99.1584 | 106.0677 | 112.9729
| NewcastleWind2025RCP4.5 | Newcastle | Wind | RCP4.5 | 2025 | 85.7056 | 92.2879 | 99.2129 | 106.1401 | 113.0631
| NewcastleWind2030RCP4.5 | Newcastle | Wind | RCP4.5 | 2030 | 85.7213 | 92.3217 | 99.2673 | 106.2125 | 113.1534
| NewcastleWind2035RCP4.5 | Newcastle | Wind | RCP4.5 | 2035 | 85.7369 | 92.3554 | 99.3217 | 106.2849 | 113.2437
| NewcastleWind2040RCP4.5 | Newcastle | Wind | RCP4.5 | 2040 | 85.7526 | 92.3892 | 99.3762 | 106.3573 | 113.334
| NewcastleWind2045RCP4.5 | Newcastle | Wind | RCP4.5 | 2045 | 85.7683 | 92.4229 | 99.4306 | 106.4296 | 113.4243
| NewcastleWind2050RCP4.5 | Newcastle | Wind | RCP4.5 | 2050 | 85.8677 | 92.5617 | 99.6178 | 106.6567 | 113.6952
| NewcastleWind2055RCP4.5 | Newcastle | Wind | RCP4.5 | 2055 | 85.9515 | 92.6666 | 99.7504 | 106.8113 | 113.8757
| NewcastleWind2060RCP4.5 | Newcastle | Wind | RCP4.5 | 2060 | 86.0353 | 92.7716 | 99.8831 | 106.966 | 114.0563
| NewcastleWind2065RCP4.5 | Newcastle | Wind | RCP4.5 | 2065 | 86.1191 | 92.8765 | 100.0157 | 107.1207 | 114.2369
| NewcastleWind2070RCP4.5 | Newcastle | Wind | RCP4.5 | 2070 | 86.2028 | 92.9815 | 100.1484 | 107.2753 | 114.4175
| NewcastleWind2075RCP4.5 | Newcastle | Wind | RCP4.5 | 2075 | 86.3482 | 93.1687 | 100.3877 | 107.5596 | 114.7466
| NewcastleWind2080RCP4.5 | Newcastle | Wind | RCP4.5 | 2080 | 86.4935 | 93.3559 | 100.6269 | 107.8438 | 115.0758
| NewcastleWind2085RCP4.5 | Newcastle | Wind | RCP4.5 | 2085 | 86.6388 | 93.5431 | 100.8662 | 108.128 | 115.405
| NewcastleWind2090RCP4.5 | Newcastle | Wind | RCP4.5 | 2090 | 86.7841 | 93.7303 | 101.1054 | 108.4123 | 115.7342
| NewcastleWind2095RCP4.5 | Newcastle | Wind | RCP4.5 | 2095 | 86.9295 | 93.9175 | 101.3447 | 108.6965 | 116.0633
| NewcastleWind2100RCP4.5 | Newcastle | Wind | RCP4.5 | 2100 | 87.0748 | 94.1047 | 101.5839 | 108.9808 | 116.3925
| NewcastleWind2023RCP6.0 | Newcastle | Wind | RCP6.0 | 2023 | 85.6899 | 92.2541 | 99.1584 | 106.0677 | 112.9729
| NewcastleWind2025RCP6.0 | Newcastle | Wind | RCP6.0 | 2025 | 85.7056 | 92.2879 | 99.2129 | 106.1401 | 113.0631
| NewcastleWind2030RCP6.0 | Newcastle | Wind | RCP6.0 | 2030 | 85.7213 | 92.3217 | 99.2673 | 106.2125 | 113.1534
| NewcastleWind2035RCP6.0 | Newcastle | Wind | RCP6.0 | 2035 | 85.7369 | 92.3554 | 99.3217 | 106.2849 | 113.2437
| NewcastleWind2040RCP6.0 | Newcastle | Wind | RCP6.0 | 2040 | 85.7526 | 92.3892 | 99.3762 | 106.3573 | 113.334
| NewcastleWind2045RCP6.0 | Newcastle | Wind | RCP6.0 | 2045 | 85.7683 | 92.4229 | 99.4306 | 106.4296 | 113.4243
| NewcastleWind2050RCP6.0 | Newcastle | Wind | RCP6.0 | 2050 | 85.8677 | 92.5617 | 99.6178 | 106.6567 | 113.6952
| NewcastleWind2055RCP6.0 | Newcastle | Wind | RCP6.0 | 2055 | 85.9515 | 92.6666 | 99.7504 | 106.8113 | 113.8757
| NewcastleWind2060RCP6.0 | Newcastle | Wind | RCP6.0 | 2060 | 86.0353 | 92.7716 | 99.8831 | 106.966 | 114.0563
| NewcastleWind2065RCP6.0 | Newcastle | Wind | RCP6.0 | 2065 | 86.1191 | 92.8765 | 100.0157 | 107.1207 | 114.2369
| NewcastleWind2070RCP6.0 | Newcastle | Wind | RCP6.0 | 2070 | 86.2028 | 92.9815 | 100.1484 | 107.2753 | 114.4175
| NewcastleWind2075RCP6.0 | Newcastle | Wind | RCP6.0 | 2075 | 86.4208 | 93.2623 | 100.5073 | 107.7017 | 114.9112
| NewcastleWind2080RCP6.0 | Newcastle | Wind | RCP6.0 | 2080 | 86.6388 | 93.5431 | 100.8662 | 108.128 | 115.405
| NewcastleWind2085RCP6.0 | Newcastle | Wind | RCP6.0 | 2085 | 86.8568 | 93.8239 | 101.225 | 108.5544 | 115.8988
| NewcastleWind2090RCP6.0 | Newcastle | Wind | RCP6.0 | 2090 | 87.525 | 94.6572 | 102.267 | 109.7753 | 117.3029
| NewcastleWind2095RCP6.0 | Newcastle | Wind | RCP6.0 | 2095 | 87.9752 | 95.2096 | 102.9501 | 110.5697 | 118.2133
| NewcastleWind2100RCP6.0 | Newcastle | Wind | RCP6.0 | 2100 | 88.4254 | 95.762 | 103.6332 | 111.3642 | 119.1237
| NewcastleWind2023RCP8.5 | Newcastle | Wind | RCP8.5 | 2023 | 85.6899 | 92.2541 | 99.1584 | 106.0677 | 112.9729
| NewcastleWind2025RCP8.5 | Newcastle | Wind | RCP8.5 | 2025 | 85.7213 | 92.3217 | 99.2673 | 106.2125 | 113.1534
| NewcastleWind2030RCP8.5 | Newcastle | Wind | RCP8.5 | 2030 | 85.7526 | 92.3892 | 99.3762 | 106.3573 | 113.334
| NewcastleWind2035RCP8.5 | Newcastle | Wind | RCP8.5 | 2035 | 85.784 | 92.4567 | 99.4851 | 106.502 | 113.5146
| NewcastleWind2040RCP8.5 | Newcastle | Wind | RCP8.5 | 2040 | 85.9236 | 92.6316 | 99.7062 | 106.7598 | 113.8155
| NewcastleWind2045RCP8.5 | Newcastle | Wind | RCP8.5 | 2045 | 86.0632 | 92.8066 | 99.9273 | 107.0175 | 114.1165
| NewcastleWind2050RCP8.5 | Newcastle | Wind | RCP8.5 | 2050 | 86.4935 | 93.3559 | 100.6269 | 107.8438 | 115.0758
| NewcastleWind2055RCP8.5 | Newcastle | Wind | RCP8.5 | 2055 | 86.7841 | 93.7303 | 101.1054 | 108.4123 | 115.7342
| NewcastleWind2060RCP8.5 | Newcastle | Wind | RCP8.5 | 2060 | 87.525 | 94.6572 | 102.267 | 109.7753 | 117.3029
| NewcastleWind2065RCP8.5 | Newcastle | Wind | RCP8.5 | 2065 | 87.9752 | 95.2096 | 102.9501 | 110.5697 | 118.2133
| NewcastleWind2070RCP8.5 | Newcastle | Wind | RCP8.5 | 2070 | 88.5594 | 95.9431 | 103.8741 | 111.6608 | 119.4698
| NewcastleWind2075RCP8.5 | Newcastle | Wind | RCP8.5 | 2075 | 88.6933 | 96.1241 | 104.115 | 111.9574 | 119.8159
| NewcastleWind2080RCP8.5 | Newcastle | Wind | RCP8.5 | 2080 | 88.8272 | 96.3052 | 104.3559 | 112.254 | 120.162
| NewcastleWind2085RCP8.5 | Newcastle | Wind | RCP8.5 | 2085 | 89.1136 | 96.7103 | 104.9103 | 112.932 | 120.969
| NewcastleWind2090RCP8.5 | Newcastle | Wind | RCP8.5 | 2090 | 89.4 | 97.1154 | 105.4647 | 113.6099 | 121.7759
| NewcastleWind2095RCP8.5 | Newcastle | Wind | RCP8.5 | 2095 | 89.4 | 97.1154 | 105.4647 | 113.6099 | 121.7759
| NewcastleWind2100RCP8.5 | Newcastle | Wind | RCP8.5 | 2100 | 89.4 | 97.1154 | 105.4647 | 113.6099 | 121.7759
| NewmarketIce Accretion2023RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
| NewmarketIce Accretion2025RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2025 | 17.4222 | 20.9229 | 25.3542 | 28.7444 | 32.1247
| NewmarketIce Accretion2030RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2030 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
| NewmarketIce Accretion2035RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2035 | 17.5092 | 21.0612 | 25.5625 | 28.9986 | 32.4292
| NewmarketIce Accretion2040RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2040 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
| NewmarketIce Accretion2045RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2045 | 17.5962 | 21.1996 | 25.7708 | 29.2529 | 32.7338
| NewmarketIce Accretion2050RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2050 | 17.5214 | 21.1484 | 25.745 | 29.2444 | 32.7411
| NewmarketIce Accretion2055RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2055 | 17.4031 | 21.0281 | 25.615 | 29.1088 | 32.5962
| NewmarketIce Accretion2060RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2060 | 17.2848 | 20.9077 | 25.485 | 28.9732 | 32.4513
| NewmarketIce Accretion2065RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2065 | 17.1665 | 20.7873 | 25.355 | 28.8376 | 32.3064
| NewmarketIce Accretion2070RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2070 | 17.0482 | 20.667 | 25.225 | 28.702 | 32.1615
| NewmarketIce Accretion2075RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2075 | 17.0105 | 20.6497 | 25.2333 | 28.7255 | 32.2035
| NewmarketIce Accretion2080RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2080 | 16.9728 | 20.6324 | 25.2417 | 28.7491 | 32.2455
| NewmarketIce Accretion2085RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2085 | 16.9352 | 20.6151 | 25.25 | 28.7726 | 32.2875
| NewmarketIce Accretion2090RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2090 | 16.8975 | 20.5978 | 25.2583 | 28.7962 | 32.3295
| NewmarketIce Accretion2095RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2095 | 16.8598 | 20.5805 | 25.2667 | 28.8197 | 32.3715
| NewmarketIce Accretion2100RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2100 | 16.8221 | 20.5633 | 25.275 | 28.8432 | 32.4135
| NewmarketIce Accretion2023RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
| NewmarketIce Accretion2025RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2025 | 17.4222 | 20.9229 | 25.3542 | 28.7444 | 32.1247
| NewmarketIce Accretion2030RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2030 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
| NewmarketIce Accretion2035RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2035 | 17.5092 | 21.0612 | 25.5625 | 28.9986 | 32.4292
| NewmarketIce Accretion2040RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2040 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
| NewmarketIce Accretion2045RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2045 | 17.5962 | 21.1996 | 25.7708 | 29.2529 | 32.7338
| NewmarketIce Accretion2050RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2050 | 17.5214 | 21.1484 | 25.745 | 29.2444 | 32.7411
| NewmarketIce Accretion2055RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2055 | 17.4031 | 21.0281 | 25.615 | 29.1088 | 32.5962
| NewmarketIce Accretion2060RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2060 | 17.2848 | 20.9077 | 25.485 | 28.9732 | 32.4513
| NewmarketIce Accretion2065RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2065 | 17.1665 | 20.7873 | 25.355 | 28.8376 | 32.3064
| NewmarketIce Accretion2070RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2070 | 17.0482 | 20.667 | 25.225 | 28.702 | 32.1615
| NewmarketIce Accretion2075RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2075 | 16.9917 | 20.6411 | 25.2375 | 28.7373 | 32.2245
| NewmarketIce Accretion2080RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2080 | 16.9352 | 20.6151 | 25.25 | 28.7726 | 32.2875
| NewmarketIce Accretion2085RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2085 | 16.8786 | 20.5892 | 25.2625 | 28.8079 | 32.3505
| NewmarketIce Accretion2090RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2090 | 16.5147 | 20.2382 | 24.925 | 28.4854 | 32.0355
| NewmarketIce Accretion2095RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2095 | 16.2074 | 19.9131 | 24.575 | 28.1276 | 31.6575
| NewmarketIce Accretion2100RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2100 | 15.9001 | 19.588 | 24.225 | 27.7697 | 31.2795
| NewmarketIce Accretion2023RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
| NewmarketIce Accretion2025RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2025 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
| NewmarketIce Accretion2030RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2030 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
| NewmarketIce Accretion2035RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2035 | 17.6397 | 21.2687 | 25.875 | 29.38 | 32.886
| NewmarketIce Accretion2040RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2040 | 17.4425 | 21.0682 | 25.6583 | 29.154 | 32.6445
| NewmarketIce Accretion2045RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2045 | 17.2454 | 20.8676 | 25.4417 | 28.928 | 32.403
| NewmarketIce Accretion2050RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2050 | 16.9728 | 20.6324 | 25.2417 | 28.7491 | 32.2455
| NewmarketIce Accretion2055RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2055 | 16.8975 | 20.5978 | 25.2583 | 28.7962 | 32.3295
| NewmarketIce Accretion2060RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2060 | 16.5147 | 20.2382 | 24.925 | 28.4854 | 32.0355
| NewmarketIce Accretion2065RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2065 | 16.2074 | 19.9131 | 24.575 | 28.1276 | 31.6575
| NewmarketIce Accretion2070RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2070 | 15.5116 | 19.173 | 23.775 | 27.2801 | 30.765
| NewmarketIce Accretion2075RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2075 | 15.1231 | 18.758 | 23.325 | 26.7904 | 30.2505
| NewmarketIce Accretion2080RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2080 | 14.7345 | 18.343 | 22.875 | 26.3007 | 29.736
| NewmarketIce Accretion2085RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2085 | 13.9691 | 17.4404 | 21.8 | 25.1001 | 28.3972
| NewmarketIce Accretion2090RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2090 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
| NewmarketIce Accretion2095RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2095 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
| NewmarketIce Accretion2100RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2100 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
| NewmarketWind2023RCP4.5 | Newmarket | Wind | RCP4.5 | 2023 | 76.2676 | 82.1428 | 88.3256 | 94.5084 | 100.6912
| NewmarketWind2025RCP4.5 | Newmarket | Wind | RCP4.5 | 2025 | 76.2917 | 82.1769 | 88.3725 | 94.5665 | 100.7614
| NewmarketWind2030RCP4.5 | Newmarket | Wind | RCP4.5 | 2030 | 76.3157 | 82.211 | 88.4195 | 94.6245 | 100.8316
| NewmarketWind2035RCP4.5 | Newmarket | Wind | RCP4.5 | 2035 | 76.3398 | 82.2451 | 88.4664 | 94.6826 | 100.9019
| NewmarketWind2040RCP4.5 | Newmarket | Wind | RCP4.5 | 2040 | 76.3639 | 82.2792 | 88.5133 | 94.7407 | 100.9721
| NewmarketWind2045RCP4.5 | Newmarket | Wind | RCP4.5 | 2045 | 76.3879 | 82.3133 | 88.5603 | 94.7987 | 101.0423
| NewmarketWind2050RCP4.5 | Newmarket | Wind | RCP4.5 | 2050 | 76.4621 | 82.3949 | 88.6512 | 94.8982 | 101.1506
| NewmarketWind2055RCP4.5 | Newmarket | Wind | RCP4.5 | 2055 | 76.5123 | 82.4423 | 88.6952 | 94.9396 | 101.1888
| NewmarketWind2060RCP4.5 | Newmarket | Wind | RCP4.5 | 2060 | 76.5624 | 82.4898 | 88.7392 | 94.9811 | 101.2269
| NewmarketWind2065RCP4.5 | Newmarket | Wind | RCP4.5 | 2065 | 76.6126 | 82.5373 | 88.7832 | 95.0225 | 101.265
| NewmarketWind2070RCP4.5 | Newmarket | Wind | RCP4.5 | 2070 | 76.6627 | 82.5847 | 88.8272 | 95.0639 | 101.3031
| NewmarketWind2075RCP4.5 | Newmarket | Wind | RCP4.5 | 2075 | 76.7362 | 82.6857 | 88.9621 | 95.2271 | 101.4954
| NewmarketWind2080RCP4.5 | Newmarket | Wind | RCP4.5 | 2080 | 76.8096 | 82.7866 | 89.0971 | 95.3904 | 101.6877
| NewmarketWind2085RCP4.5 | Newmarket | Wind | RCP4.5 | 2085 | 76.8831 | 82.8876 | 89.232 | 95.5536 | 101.88
| NewmarketWind2090RCP4.5 | Newmarket | Wind | RCP4.5 | 2090 | 76.9565 | 82.9885 | 89.3669 | 95.7168 | 102.0723
| NewmarketWind2095RCP4.5 | Newmarket | Wind | RCP4.5 | 2095 | 77.03 | 83.0894 | 89.5019 | 95.88 | 102.2645
| NewmarketWind2100RCP4.5 | Newmarket | Wind | RCP4.5 | 2100 | 77.1035 | 83.1904 | 89.6368 | 96.0432 | 102.4568
| NewmarketWind2023RCP6.0 | Newmarket | Wind | RCP6.0 | 2023 | 76.2676 | 82.1428 | 88.3256 | 94.5084 | 100.6912
| NewmarketWind2025RCP6.0 | Newmarket | Wind | RCP6.0 | 2025 | 76.2917 | 82.1769 | 88.3725 | 94.5665 | 100.7614
| NewmarketWind2030RCP6.0 | Newmarket | Wind | RCP6.0 | 2030 | 76.3157 | 82.211 | 88.4195 | 94.6245 | 100.8316
| NewmarketWind2035RCP6.0 | Newmarket | Wind | RCP6.0 | 2035 | 76.3398 | 82.2451 | 88.4664 | 94.6826 | 100.9019
| NewmarketWind2040RCP6.0 | Newmarket | Wind | RCP6.0 | 2040 | 76.3639 | 82.2792 | 88.5133 | 94.7407 | 100.9721
| NewmarketWind2045RCP6.0 | Newmarket | Wind | RCP6.0 | 2045 | 76.3879 | 82.3133 | 88.5603 | 94.7987 | 101.0423
| NewmarketWind2050RCP6.0 | Newmarket | Wind | RCP6.0 | 2050 | 76.4621 | 82.3949 | 88.6512 | 94.8982 | 101.1506
| NewmarketWind2055RCP6.0 | Newmarket | Wind | RCP6.0 | 2055 | 76.5123 | 82.4423 | 88.6952 | 94.9396 | 101.1888
| NewmarketWind2060RCP6.0 | Newmarket | Wind | RCP6.0 | 2060 | 76.5624 | 82.4898 | 88.7392 | 94.9811 | 101.2269
| NewmarketWind2065RCP6.0 | Newmarket | Wind | RCP6.0 | 2065 | 76.6126 | 82.5373 | 88.7832 | 95.0225 | 101.265
| NewmarketWind2070RCP6.0 | Newmarket | Wind | RCP6.0 | 2070 | 76.6627 | 82.5847 | 88.8272 | 95.0639 | 101.3031
| NewmarketWind2075RCP6.0 | Newmarket | Wind | RCP6.0 | 2075 | 76.7729 | 82.7361 | 89.0296 | 95.3088 | 101.5916
| NewmarketWind2080RCP6.0 | Newmarket | Wind | RCP6.0 | 2080 | 76.8831 | 82.8876 | 89.232 | 95.5536 | 101.88
| NewmarketWind2085RCP6.0 | Newmarket | Wind | RCP6.0 | 2085 | 76.9933 | 83.039 | 89.4344 | 95.7984 | 102.1684
| NewmarketWind2090RCP6.0 | Newmarket | Wind | RCP6.0 | 2090 | 77.3593 | 83.5068 | 90.0269 | 96.4983 | 102.9785
| NewmarketWind2095RCP6.0 | Newmarket | Wind | RCP6.0 | 2095 | 77.6151 | 83.8233 | 90.4171 | 96.9534 | 103.5001
| NewmarketWind2100RCP6.0 | Newmarket | Wind | RCP6.0 | 2100 | 77.8709 | 84.1397 | 90.8072 | 97.4085 | 104.0218
| NewmarketWind2023RCP8.5 | Newmarket | Wind | RCP8.5 | 2023 | 76.2676 | 82.1428 | 88.3256 | 94.5084 | 100.6912
| NewmarketWind2025RCP8.5 | Newmarket | Wind | RCP8.5 | 2025 | 76.3157 | 82.211 | 88.4195 | 94.6245 | 100.8316
| NewmarketWind2030RCP8.5 | Newmarket | Wind | RCP8.5 | 2030 | 76.3639 | 82.2792 | 88.5133 | 94.7407 | 100.9721
| NewmarketWind2035RCP8.5 | Newmarket | Wind | RCP8.5 | 2035 | 76.412 | 82.3474 | 88.6072 | 94.8568 | 101.1125
| NewmarketWind2040RCP8.5 | Newmarket | Wind | RCP8.5 | 2040 | 76.4956 | 82.4265 | 88.6805 | 94.9258 | 101.1761
| NewmarketWind2045RCP8.5 | Newmarket | Wind | RCP8.5 | 2045 | 76.5791 | 82.5056 | 88.7539 | 94.9949 | 101.2396
| NewmarketWind2050RCP8.5 | Newmarket | Wind | RCP8.5 | 2050 | 76.8096 | 82.7866 | 89.0971 | 95.3904 | 101.6877
| NewmarketWind2055RCP8.5 | Newmarket | Wind | RCP8.5 | 2055 | 76.9565 | 82.9885 | 89.3669 | 95.7168 | 102.0723
| NewmarketWind2060RCP8.5 | Newmarket | Wind | RCP8.5 | 2060 | 77.3593 | 83.5068 | 90.0269 | 96.4983 | 102.9785
| NewmarketWind2065RCP8.5 | Newmarket | Wind | RCP8.5 | 2065 | 77.6151 | 83.8233 | 90.4171 | 96.9534 | 103.5001
| NewmarketWind2070RCP8.5 | Newmarket | Wind | RCP8.5 | 2070 | 78.0659 | 84.4016 | 91.1533 | 97.826 | 104.51
| NewmarketWind2075RCP8.5 | Newmarket | Wind | RCP8.5 | 2075 | 78.261 | 84.6635 | 91.4995 | 98.2434 | 104.9983
| NewmarketWind2080RCP8.5 | Newmarket | Wind | RCP8.5 | 2080 | 78.456 | 84.9254 | 91.8456 | 98.6608 | 105.4865
| NewmarketWind2085RCP8.5 | Newmarket | Wind | RCP8.5 | 2085 | 78.5548 | 85.0563 | 92.0216 | 98.868 | 105.7323
| NewmarketWind2090RCP8.5 | Newmarket | Wind | RCP8.5 | 2090 | 78.6536 | 85.1873 | 92.1976 | 99.0752 | 105.978
| NewmarketWind2095RCP8.5 | Newmarket | Wind | RCP8.5 | 2095 | 78.6536 | 85.1873 | 92.1976 | 99.0752 | 105.978
| NewmarketWind2100RCP8.5 | Newmarket | Wind | RCP8.5 | 2100 | 78.6536 | 85.1873 | 92.1976 | 99.0752 | 105.978
| Niagara FallsIce Accretion2023RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2023 | 20.7501 | 24.8253 | 29.97 | 33.9339 | 37.8378
| Niagara FallsIce Accretion2025RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2025 | 20.7084 | 24.7838 | 29.935 | 33.8943 | 37.8
| Niagara FallsIce Accretion2030RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2030 | 20.6666 | 24.7423 | 29.9 | 33.8548 | 37.7622
| Niagara FallsIce Accretion2035RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2035 | 20.6249 | 24.7008 | 29.865 | 33.8152 | 37.7244
| Niagara FallsIce Accretion2040RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2040 | 20.5831 | 24.6593 | 29.83 | 33.7757 | 37.6866
| Niagara FallsIce Accretion2045RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2045 | 20.5414 | 24.6178 | 29.795 | 33.7361 | 37.6488
| Niagara FallsIce Accretion2050RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2050 | 20.1531 | 24.1879 | 29.31 | 33.2017 | 37.0742
| Niagara FallsIce Accretion2055RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2055 | 19.8066 | 23.7994 | 28.86 | 32.7067 | 36.5375
| Niagara FallsIce Accretion2060RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2060 | 19.46 | 23.411 | 28.41 | 32.2118 | 36.0007
| Niagara FallsIce Accretion2065RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2065 | 19.1135 | 23.0225 | 27.96 | 31.7168 | 35.464
| Niagara FallsIce Accretion2070RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2070 | 18.767 | 22.6341 | 27.51 | 31.2219 | 34.9272
| Niagara FallsIce Accretion2075RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2075 | 18.6139 | 22.4806 | 27.355 | 31.0637 | 34.7634
| Niagara FallsIce Accretion2080RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2080 | 18.4608 | 22.327 | 27.2 | 30.9055 | 34.5996
| Niagara FallsIce Accretion2085RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2085 | 18.3077 | 22.1734 | 27.045 | 30.7473 | 34.4358
| Niagara FallsIce Accretion2090RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2090 | 18.1546 | 22.0199 | 26.89 | 30.5891 | 34.272
| Niagara FallsIce Accretion2095RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2095 | 18.0015 | 21.8663 | 26.735 | 30.4309 | 34.1082
| Niagara FallsIce Accretion2100RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2100 | 17.8485 | 21.7128 | 26.58 | 30.2727 | 33.9444
| Niagara FallsIce Accretion2023RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2023 | 20.7501 | 24.8253 | 29.97 | 33.9339 | 37.8378
| Niagara FallsIce Accretion2025RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2025 | 20.7084 | 24.7838 | 29.935 | 33.8943 | 37.8
| Niagara FallsIce Accretion2030RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2030 | 20.6666 | 24.7423 | 29.9 | 33.8548 | 37.7622
| Niagara FallsIce Accretion2035RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2035 | 20.6249 | 24.7008 | 29.865 | 33.8152 | 37.7244
| Niagara FallsIce Accretion2040RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2040 | 20.5831 | 24.6593 | 29.83 | 33.7757 | 37.6866
| Niagara FallsIce Accretion2045RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2045 | 20.5414 | 24.6178 | 29.795 | 33.7361 | 37.6488
| Niagara FallsIce Accretion2050RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2050 | 20.1531 | 24.1879 | 29.31 | 33.2017 | 37.0742
| Niagara FallsIce Accretion2055RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2055 | 19.8066 | 23.7994 | 28.86 | 32.7067 | 36.5375
| Niagara FallsIce Accretion2060RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2060 | 19.46 | 23.411 | 28.41 | 32.2118 | 36.0007
| Niagara FallsIce Accretion2065RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2065 | 19.1135 | 23.0225 | 27.96 | 31.7168 | 35.464
| Niagara FallsIce Accretion2070RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2070 | 18.767 | 22.6341 | 27.51 | 31.2219 | 34.9272
| Niagara FallsIce Accretion2075RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2075 | 18.5373 | 22.4038 | 27.2775 | 30.9846 | 34.6815
| Niagara FallsIce Accretion2080RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2080 | 18.3077 | 22.1734 | 27.045 | 30.7473 | 34.4358
| Niagara FallsIce Accretion2085RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2085 | 18.0781 | 21.9431 | 26.8125 | 30.51 | 34.1901
| Niagara FallsIce Accretion2090RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2090 | 17.2848 | 21.082 | 25.85 | 29.4704 | 33.075
| Niagara FallsIce Accretion2095RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2095 | 16.7212 | 20.4512 | 25.12 | 28.6681 | 32.2056
| Niagara FallsIce Accretion2100RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2100 | 16.1575 | 19.8204 | 24.39 | 27.8658 | 31.3362
| Niagara FallsIce Accretion2023RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2023 | 20.7501 | 24.8253 | 29.97 | 33.9339 | 37.8378
| Niagara FallsIce Accretion2025RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2025 | 20.6666 | 24.7423 | 29.9 | 33.8548 | 37.7622
| Niagara FallsIce Accretion2030RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2030 | 20.5831 | 24.6593 | 29.83 | 33.7757 | 37.6866
| Niagara FallsIce Accretion2035RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2035 | 20.4996 | 24.5763 | 29.76 | 33.6966 | 37.611
| Niagara FallsIce Accretion2040RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2040 | 19.9221 | 23.9289 | 29.01 | 32.8717 | 36.7164
| Niagara FallsIce Accretion2045RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2045 | 19.3445 | 23.2815 | 28.26 | 32.0468 | 35.8218
| Niagara FallsIce Accretion2050RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2050 | 18.4608 | 22.327 | 27.2 | 30.9055 | 34.5996
| Niagara FallsIce Accretion2055RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2055 | 18.1546 | 22.0199 | 26.89 | 30.5891 | 34.272
| Niagara FallsIce Accretion2060RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2060 | 17.2848 | 21.082 | 25.85 | 29.4704 | 33.075
| Niagara FallsIce Accretion2065RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2065 | 16.7212 | 20.4512 | 25.12 | 28.6681 | 32.2056
| Niagara FallsIce Accretion2070RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2070 | 15.9418 | 19.588 | 24.14 | 27.6059 | 31.0464
| Niagara FallsIce Accretion2075RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2075 | 15.7261 | 19.3556 | 23.89 | 27.346 | 30.7566
| Niagara FallsIce Accretion2080RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2080 | 15.5104 | 19.1232 | 23.64 | 27.0861 | 30.4668
| Niagara FallsIce Accretion2085RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2085 | 14.8946 | 18.426 | 22.83 | 26.1878 | 29.484
| Niagara FallsIce Accretion2090RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2090 | 14.2788 | 17.7288 | 22.02 | 25.2894 | 28.5012
| Niagara FallsIce Accretion2095RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2095 | 14.2788 | 17.7288 | 22.02 | 25.2894 | 28.5012
| Niagara FallsIce Accretion2100RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2100 | 14.2788 | 17.7288 | 22.02 | 25.2894 | 28.5012
| Niagara FallsWind2023RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2023 | 87.3758 | 94.2648 | 101.55 | 108.7976 | 116.052
| Niagara FallsWind2025RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2025 | 87.3729 | 94.2679 | 101.5617 | 108.8154 | 116.0767
| Niagara FallsWind2030RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2030 | 87.37 | 94.271 | 101.5733 | 108.8333 | 116.1014
| Niagara FallsWind2035RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2035 | 87.3672 | 94.2741 | 101.585 | 108.8511 | 116.1261
| Niagara FallsWind2040RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2040 | 87.3643 | 94.2772 | 101.5967 | 108.8689 | 116.1508
| Niagara FallsWind2045RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2045 | 87.3614 | 94.2803 | 101.6083 | 108.8868 | 116.1755
| Niagara FallsWind2050RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2050 | 87.3602 | 94.2964 | 101.65 | 108.9474 | 116.2549
| Niagara FallsWind2055RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2055 | 87.362 | 94.3094 | 101.68 | 108.9902 | 116.3096
| Niagara FallsWind2060RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2060 | 87.3637 | 94.3225 | 101.71 | 109.033 | 116.3644
| Niagara FallsWind2065RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2065 | 87.3654 | 94.3355 | 101.74 | 109.0758 | 116.4191
| Niagara FallsWind2070RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2070 | 87.3672 | 94.3485 | 101.77 | 109.1186 | 116.4738
| Niagara FallsWind2075RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2075 | 87.3873 | 94.3795 | 101.815 | 109.1757 | 116.5422
| Niagara FallsWind2080RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2080 | 87.4074 | 94.4105 | 101.86 | 109.2327 | 116.6106
| Niagara FallsWind2085RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2085 | 87.4276 | 94.4415 | 101.905 | 109.2898 | 116.679
| Niagara FallsWind2090RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2090 | 87.4477 | 94.4725 | 101.95 | 109.3469 | 116.7474
| Niagara FallsWind2095RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2095 | 87.4679 | 94.5035 | 101.995 | 109.4039 | 116.8158
| Niagara FallsWind2100RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2100 | 87.488 | 94.5345 | 102.04 | 109.461 | 116.8842
| Niagara FallsWind2023RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2023 | 87.3758 | 94.2648 | 101.55 | 108.7976 | 116.052
| Niagara FallsWind2025RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2025 | 87.3729 | 94.2679 | 101.5617 | 108.8154 | 116.0767
| Niagara FallsWind2030RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2030 | 87.37 | 94.271 | 101.5733 | 108.8333 | 116.1014
| Niagara FallsWind2035RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2035 | 87.3672 | 94.2741 | 101.585 | 108.8511 | 116.1261
| Niagara FallsWind2040RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2040 | 87.3643 | 94.2772 | 101.5967 | 108.8689 | 116.1508
| Niagara FallsWind2045RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2045 | 87.3614 | 94.2803 | 101.6083 | 108.8868 | 116.1755
| Niagara FallsWind2050RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2050 | 87.3602 | 94.2964 | 101.65 | 108.9474 | 116.2549
| Niagara FallsWind2055RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2055 | 87.362 | 94.3094 | 101.68 | 108.9902 | 116.3096
| Niagara FallsWind2060RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2060 | 87.3637 | 94.3225 | 101.71 | 109.033 | 116.3644
| Niagara FallsWind2065RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2065 | 87.3654 | 94.3355 | 101.74 | 109.0758 | 116.4191
| Niagara FallsWind2070RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2070 | 87.3672 | 94.3485 | 101.77 | 109.1186 | 116.4738
| Niagara FallsWind2075RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2075 | 87.3974 | 94.395 | 101.8375 | 109.2042 | 116.5764
| Niagara FallsWind2080RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2080 | 87.4276 | 94.4415 | 101.905 | 109.2898 | 116.679
| Niagara FallsWind2085RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2085 | 87.4578 | 94.488 | 101.9725 | 109.3754 | 116.7816
| Niagara FallsWind2090RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2090 | 87.5888 | 94.6771 | 102.23 | 109.6928 | 117.1654
| Niagara FallsWind2095RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2095 | 87.6895 | 94.8197 | 102.42 | 109.9247 | 117.4466
| Niagara FallsWind2100RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2100 | 87.7903 | 94.9623 | 102.61 | 110.1565 | 117.7278
| Niagara FallsWind2023RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2023 | 87.3758 | 94.2648 | 101.55 | 108.7976 | 116.052
| Niagara FallsWind2025RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2025 | 87.37 | 94.271 | 101.5733 | 108.8333 | 116.1014
| Niagara FallsWind2030RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2030 | 87.3643 | 94.2772 | 101.5967 | 108.8689 | 116.1508
| Niagara FallsWind2035RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2035 | 87.3585 | 94.2834 | 101.62 | 108.9046 | 116.2002
| Niagara FallsWind2040RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2040 | 87.3614 | 94.3051 | 101.67 | 108.9759 | 116.2914
| Niagara FallsWind2045RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2045 | 87.3643 | 94.3268 | 101.72 | 109.0473 | 116.3826
| Niagara FallsWind2050RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2050 | 87.4074 | 94.4105 | 101.86 | 109.2327 | 116.6106
| Niagara FallsWind2055RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2055 | 87.4477 | 94.4725 | 101.95 | 109.3469 | 116.7474
| Niagara FallsWind2060RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2060 | 87.5888 | 94.6771 | 102.23 | 109.6928 | 117.1654
| Niagara FallsWind2065RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2065 | 87.6895 | 94.8197 | 102.42 | 109.9247 | 117.4466
| Niagara FallsWind2070RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2070 | 87.7931 | 94.9871 | 102.6667 | 110.2385 | 117.8304
| Niagara FallsWind2075RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2075 | 87.796 | 95.0119 | 102.7233 | 110.3206 | 117.933
| Niagara FallsWind2080RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2080 | 87.7989 | 95.0367 | 102.78 | 110.4026 | 118.0356
| Niagara FallsWind2085RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2085 | 87.8334 | 95.1437 | 102.975 | 110.6701 | 118.3776
| Niagara FallsWind2090RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2090 | 87.868 | 95.2506 | 103.17 | 110.9376 | 118.7196
| Niagara FallsWind2095RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2095 | 87.868 | 95.2506 | 103.17 | 110.9376 | 118.7196
| Niagara FallsWind2100RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2100 | 87.868 | 95.2506 | 103.17 | 110.9376 | 118.7196
| North BayIce Accretion2023RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2023 | 15.6913 | 18.753 | 22.638 | 25.5809 | 28.5516
| North BayIce Accretion2025RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2025 | 15.7908 | 18.8778 | 22.7993 | 25.7715 | 28.7641
| North BayIce Accretion2030RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2030 | 15.8903 | 19.0026 | 22.9607 | 25.9621 | 28.9766
| North BayIce Accretion2035RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2035 | 15.9898 | 19.1273 | 23.122 | 26.1527 | 29.1892
| North BayIce Accretion2040RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2040 | 16.0894 | 19.2521 | 23.2833 | 26.3433 | 29.4017
| North BayIce Accretion2045RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2045 | 16.1889 | 19.3769 | 23.4447 | 26.5339 | 29.6142
| North BayIce Accretion2050RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2050 | 16.4139 | 19.6806 | 23.848 | 27.0129 | 30.1704
| North BayIce Accretion2055RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2055 | 16.5394 | 19.8596 | 24.09 | 27.3013 | 30.5142
| North BayIce Accretion2060RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2060 | 16.665 | 20.0385 | 24.332 | 27.5896 | 30.8579
| North BayIce Accretion2065RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2065 | 16.7905 | 20.2175 | 24.574 | 27.878 | 31.2016
| North BayIce Accretion2070RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2070 | 16.916 | 20.3964 | 24.816 | 28.1664 | 31.5454
| North BayIce Accretion2075RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2075 | 16.8548 | 20.3356 | 24.7573 | 28.1084 | 31.4853
| North BayIce Accretion2080RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2080 | 16.7936 | 20.2747 | 24.6987 | 28.0504 | 31.4252
| North BayIce Accretion2085RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2085 | 16.7323 | 20.2138 | 24.64 | 27.9924 | 31.3652
| North BayIce Accretion2090RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2090 | 16.6711 | 20.153 | 24.5813 | 27.9344 | 31.3051
| North BayIce Accretion2095RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2095 | 16.6098 | 20.0921 | 24.5227 | 27.8763 | 31.2451
| North BayIce Accretion2100RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2100 | 16.5486 | 20.0312 | 24.464 | 27.8183 | 31.185
| North BayIce Accretion2023RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2023 | 15.6913 | 18.753 | 22.638 | 25.5809 | 28.5516
| North BayIce Accretion2025RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2025 | 15.7908 | 18.8778 | 22.7993 | 25.7715 | 28.7641
| North BayIce Accretion2030RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2030 | 15.8903 | 19.0026 | 22.9607 | 25.9621 | 28.9766
| North BayIce Accretion2035RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2035 | 15.9898 | 19.1273 | 23.122 | 26.1527 | 29.1892
| North BayIce Accretion2040RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2040 | 16.0894 | 19.2521 | 23.2833 | 26.3433 | 29.4017
| North BayIce Accretion2045RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2045 | 16.1889 | 19.3769 | 23.4447 | 26.5339 | 29.6142
| North BayIce Accretion2050RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2050 | 16.4139 | 19.6806 | 23.848 | 27.0129 | 30.1704
| North BayIce Accretion2055RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2055 | 16.5394 | 19.8596 | 24.09 | 27.3013 | 30.5142
| North BayIce Accretion2060RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2060 | 16.665 | 20.0385 | 24.332 | 27.5896 | 30.8579
| North BayIce Accretion2065RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2065 | 16.7905 | 20.2175 | 24.574 | 27.878 | 31.2016
| North BayIce Accretion2070RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2070 | 16.916 | 20.3964 | 24.816 | 28.1664 | 31.5454
| North BayIce Accretion2075RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2075 | 16.8242 | 20.3051 | 24.728 | 28.0794 | 31.4553
| North BayIce Accretion2080RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2080 | 16.7323 | 20.2138 | 24.64 | 27.9924 | 31.3652
| North BayIce Accretion2085RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2085 | 16.6405 | 20.1225 | 24.552 | 27.9053 | 31.2751
| North BayIce Accretion2090RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2090 | 16.5282 | 20.0251 | 24.4713 | 27.8432 | 31.222
| North BayIce Accretion2095RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2095 | 16.5078 | 20.019 | 24.4787 | 27.8681 | 31.2589
| North BayIce Accretion2100RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2100 | 16.4874 | 20.013 | 24.486 | 27.8929 | 31.2959
| North BayIce Accretion2023RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2023 | 15.6913 | 18.753 | 22.638 | 25.5809 | 28.5516
| North BayIce Accretion2025RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2025 | 15.8903 | 19.0026 | 22.9607 | 25.9621 | 28.9766
| North BayIce Accretion2030RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2030 | 16.0894 | 19.2521 | 23.2833 | 26.3433 | 29.4017
| North BayIce Accretion2035RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2035 | 16.2884 | 19.5017 | 23.606 | 26.7245 | 29.8267
| North BayIce Accretion2040RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2040 | 16.4976 | 19.7999 | 24.0093 | 27.2051 | 30.3996
| North BayIce Accretion2045RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2045 | 16.7068 | 20.0982 | 24.4127 | 27.6858 | 30.9725
| North BayIce Accretion2050RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2050 | 16.7936 | 20.2747 | 24.6987 | 28.0504 | 31.4252
| North BayIce Accretion2055RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2055 | 16.6711 | 20.153 | 24.5813 | 27.9344 | 31.3051
| North BayIce Accretion2060RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2060 | 16.5282 | 20.0251 | 24.4713 | 27.8432 | 31.222
| North BayIce Accretion2065RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2065 | 16.5078 | 20.019 | 24.4787 | 27.8681 | 31.2589
| North BayIce Accretion2070RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2070 | 16.0689 | 19.5199 | 23.8847 | 27.2134 | 30.5382
| North BayIce Accretion2075RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2075 | 15.6505 | 19.0269 | 23.2833 | 26.5339 | 29.7805
| North BayIce Accretion2080RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2080 | 15.2321 | 18.5339 | 22.682 | 25.8544 | 29.0228
| North BayIce Accretion2085RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2085 | 14.9948 | 18.2874 | 22.44 | 25.5934 | 28.7595
| North BayIce Accretion2090RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2090 | 14.7575 | 18.0409 | 22.198 | 25.3323 | 28.4962
| North BayIce Accretion2095RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2095 | 14.7575 | 18.0409 | 22.198 | 25.3323 | 28.4962
| North BayIce Accretion2100RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2100 | 14.7575 | 18.0409 | 22.198 | 25.3323 | 28.4962
| North BayWind2023RCP4.5 | North Bay | Wind | RCP4.5 | 2023 | 73.1273 | 78.745 | 84.6552 | 90.5721 | 96.4878
| North BayWind2025RCP4.5 | North Bay | Wind | RCP4.5 | 2025 | 73.1515 | 78.771 | 84.6818 | 90.6005 | 96.5165
| North BayWind2030RCP4.5 | North Bay | Wind | RCP4.5 | 2030 | 73.1756 | 78.797 | 84.7084 | 90.629 | 96.5452
| North BayWind2035RCP4.5 | North Bay | Wind | RCP4.5 | 2035 | 73.1998 | 78.8231 | 84.735 | 90.6575 | 96.574
| North BayWind2040RCP4.5 | North Bay | Wind | RCP4.5 | 2040 | 73.224 | 78.8491 | 84.7616 | 90.6859 | 96.6027
| North BayWind2045RCP4.5 | North Bay | Wind | RCP4.5 | 2045 | 73.2482 | 78.8752 | 84.7882 | 90.7144 | 96.6314
| North BayWind2050RCP4.5 | North Bay | Wind | RCP4.5 | 2050 | 73.2143 | 78.8215 | 84.709 | 90.6152 | 96.5108
| North BayWind2055RCP4.5 | North Bay | Wind | RCP4.5 | 2055 | 73.1563 | 78.7418 | 84.6031 | 90.4876 | 96.3614
| North BayWind2060RCP4.5 | North Bay | Wind | RCP4.5 | 2060 | 73.0983 | 78.6622 | 84.4973 | 90.36 | 96.212
| North BayWind2065RCP4.5 | North Bay | Wind | RCP4.5 | 2065 | 73.0403 | 78.5825 | 84.3914 | 90.2323 | 96.0626
| North BayWind2070RCP4.5 | North Bay | Wind | RCP4.5 | 2070 | 72.9822 | 78.5028 | 84.2856 | 90.1047 | 95.9132
| North BayWind2075RCP4.5 | North Bay | Wind | RCP4.5 | 2075 | 73.0439 | 78.5822 | 84.3864 | 90.223 | 96.0505
| North BayWind2080RCP4.5 | North Bay | Wind | RCP4.5 | 2080 | 73.1055 | 78.6616 | 84.4872 | 90.3414 | 96.1877
| North BayWind2085RCP4.5 | North Bay | Wind | RCP4.5 | 2085 | 73.1672 | 78.7411 | 84.588 | 90.4597 | 96.325
| North BayWind2090RCP4.5 | North Bay | Wind | RCP4.5 | 2090 | 73.2288 | 78.8205 | 84.6888 | 90.5781 | 96.4622
| North BayWind2095RCP4.5 | North Bay | Wind | RCP4.5 | 2095 | 73.2905 | 78.8999 | 84.7896 | 90.6964 | 96.5995
| North BayWind2100RCP4.5 | North Bay | Wind | RCP4.5 | 2100 | 73.3521 | 78.9793 | 84.8904 | 90.8148 | 96.7368
| North BayWind2023RCP6.0 | North Bay | Wind | RCP6.0 | 2023 | 73.1273 | 78.745 | 84.6552 | 90.5721 | 96.4878
| North BayWind2025RCP6.0 | North Bay | Wind | RCP6.0 | 2025 | 73.1515 | 78.771 | 84.6818 | 90.6005 | 96.5165
| North BayWind2030RCP6.0 | North Bay | Wind | RCP6.0 | 2030 | 73.1756 | 78.797 | 84.7084 | 90.629 | 96.5452
| North BayWind2035RCP6.0 | North Bay | Wind | RCP6.0 | 2035 | 73.1998 | 78.8231 | 84.735 | 90.6575 | 96.574
| North BayWind2040RCP6.0 | North Bay | Wind | RCP6.0 | 2040 | 73.224 | 78.8491 | 84.7616 | 90.6859 | 96.6027
| North BayWind2045RCP6.0 | North Bay | Wind | RCP6.0 | 2045 | 73.2482 | 78.8752 | 84.7882 | 90.7144 | 96.6314
| North BayWind2050RCP6.0 | North Bay | Wind | RCP6.0 | 2050 | 73.2143 | 78.8215 | 84.709 | 90.6152 | 96.5108
| North BayWind2055RCP6.0 | North Bay | Wind | RCP6.0 | 2055 | 73.1563 | 78.7418 | 84.6031 | 90.4876 | 96.3614
| North BayWind2060RCP6.0 | North Bay | Wind | RCP6.0 | 2060 | 73.0983 | 78.6622 | 84.4973 | 90.36 | 96.212
| North BayWind2065RCP6.0 | North Bay | Wind | RCP6.0 | 2065 | 73.0403 | 78.5825 | 84.3914 | 90.2323 | 96.0626
| North BayWind2070RCP6.0 | North Bay | Wind | RCP6.0 | 2070 | 72.9822 | 78.5028 | 84.2856 | 90.1047 | 95.9132
| North BayWind2075RCP6.0 | North Bay | Wind | RCP6.0 | 2075 | 73.0747 | 78.6219 | 84.4368 | 90.2822 | 96.1191
| North BayWind2080RCP6.0 | North Bay | Wind | RCP6.0 | 2080 | 73.1672 | 78.7411 | 84.588 | 90.4597 | 96.325
| North BayWind2085RCP6.0 | North Bay | Wind | RCP6.0 | 2085 | 73.2597 | 78.8602 | 84.7392 | 90.6372 | 96.5309
| North BayWind2090RCP6.0 | North Bay | Wind | RCP6.0 | 2090 | 73.3497 | 78.9741 | 84.882 | 90.8028 | 96.7208
| North BayWind2095RCP6.0 | North Bay | Wind | RCP6.0 | 2095 | 73.3473 | 78.9689 | 84.8736 | 90.7908 | 96.7048
| North BayWind2100RCP6.0 | North Bay | Wind | RCP6.0 | 2100 | 73.3449 | 78.9637 | 84.8652 | 90.7788 | 96.6889
| North BayWind2023RCP8.5 | North Bay | Wind | RCP8.5 | 2023 | 73.1273 | 78.745 | 84.6552 | 90.5721 | 96.4878
| North BayWind2025RCP8.5 | North Bay | Wind | RCP8.5 | 2025 | 73.1756 | 78.797 | 84.7084 | 90.629 | 96.5452
| North BayWind2030RCP8.5 | North Bay | Wind | RCP8.5 | 2030 | 73.224 | 78.8491 | 84.7616 | 90.6859 | 96.6027
| North BayWind2035RCP8.5 | North Bay | Wind | RCP8.5 | 2035 | 73.2724 | 78.9012 | 84.8148 | 90.7428 | 96.6601
| North BayWind2040RCP8.5 | North Bay | Wind | RCP8.5 | 2040 | 73.1756 | 78.7684 | 84.6384 | 90.5301 | 96.4112
| North BayWind2045RCP8.5 | North Bay | Wind | RCP8.5 | 2045 | 73.0789 | 78.6356 | 84.462 | 90.3174 | 96.1622
| North BayWind2050RCP8.5 | North Bay | Wind | RCP8.5 | 2050 | 73.1055 | 78.6616 | 84.4872 | 90.3414 | 96.1877
| North BayWind2055RCP8.5 | North Bay | Wind | RCP8.5 | 2055 | 73.2288 | 78.8205 | 84.6888 | 90.5781 | 96.4622
| North BayWind2060RCP8.5 | North Bay | Wind | RCP8.5 | 2060 | 73.3497 | 78.9741 | 84.882 | 90.8028 | 96.7208
| North BayWind2065RCP8.5 | North Bay | Wind | RCP8.5 | 2065 | 73.3473 | 78.9689 | 84.8736 | 90.7908 | 96.7048
| North BayWind2070RCP8.5 | North Bay | Wind | RCP8.5 | 2070 | 73.6229 | 79.3178 | 85.316 | 91.3061 | 97.2985
| North BayWind2075RCP8.5 | North Bay | Wind | RCP8.5 | 2075 | 73.901 | 79.672 | 85.7668 | 91.8334 | 97.9082
| North BayWind2080RCP8.5 | North Bay | Wind | RCP8.5 | 2080 | 74.179 | 80.0261 | 86.2176 | 92.3607 | 98.5179
| North BayWind2085RCP8.5 | North Bay | Wind | RCP8.5 | 2085 | 74.4365 | 80.3035 | 86.5116 | 92.6798 | 98.853
| North BayWind2090RCP8.5 | North Bay | Wind | RCP8.5 | 2090 | 74.694 | 80.5808 | 86.8056 | 92.9988 | 99.1882
| North BayWind2095RCP8.5 | North Bay | Wind | RCP8.5 | 2095 | 74.694 | 80.5808 | 86.8056 | 92.9988 | 99.1882
| North BayWind2100RCP8.5 | North Bay | Wind | RCP8.5 | 2100 | 74.694 | 80.5808 | 86.8056 | 92.9988 | 99.1882
| North YorkIce Accretion2023RCP4.5 | North York | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| North YorkIce Accretion2025RCP4.5 | North York | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| North YorkIce Accretion2030RCP4.5 | North York | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| North YorkIce Accretion2035RCP4.5 | North York | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| North YorkIce Accretion2040RCP4.5 | North York | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| North YorkIce Accretion2045RCP4.5 | North York | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| North YorkIce Accretion2050RCP4.5 | North York | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| North YorkIce Accretion2055RCP4.5 | North York | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| North YorkIce Accretion2060RCP4.5 | North York | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| North YorkIce Accretion2065RCP4.5 | North York | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| North YorkIce Accretion2070RCP4.5 | North York | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| North YorkIce Accretion2075RCP4.5 | North York | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
| North YorkIce Accretion2080RCP4.5 | North York | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| North YorkIce Accretion2085RCP4.5 | North York | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| North YorkIce Accretion2090RCP4.5 | North York | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| North YorkIce Accretion2095RCP4.5 | North York | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
| North YorkIce Accretion2100RCP4.5 | North York | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
| North YorkIce Accretion2023RCP6.0 | North York | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| North YorkIce Accretion2025RCP6.0 | North York | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| North YorkIce Accretion2030RCP6.0 | North York | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| North YorkIce Accretion2035RCP6.0 | North York | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| North YorkIce Accretion2040RCP6.0 | North York | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| North YorkIce Accretion2045RCP6.0 | North York | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| North YorkIce Accretion2050RCP6.0 | North York | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| North YorkIce Accretion2055RCP6.0 | North York | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| North YorkIce Accretion2060RCP6.0 | North York | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| North YorkIce Accretion2065RCP6.0 | North York | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| North YorkIce Accretion2070RCP6.0 | North York | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| North YorkIce Accretion2075RCP6.0 | North York | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
| North YorkIce Accretion2080RCP6.0 | North York | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| North YorkIce Accretion2085RCP6.0 | North York | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
| North YorkIce Accretion2090RCP6.0 | North York | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| North YorkIce Accretion2095RCP6.0 | North York | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| North YorkIce Accretion2100RCP6.0 | North York | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
| North YorkIce Accretion2023RCP8.5 | North York | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| North YorkIce Accretion2025RCP8.5 | North York | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| North YorkIce Accretion2030RCP8.5 | North York | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| North YorkIce Accretion2035RCP8.5 | North York | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
| North YorkIce Accretion2040RCP8.5 | North York | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
| North YorkIce Accretion2045RCP8.5 | North York | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
| North YorkIce Accretion2050RCP8.5 | North York | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| North YorkIce Accretion2055RCP8.5 | North York | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| North YorkIce Accretion2060RCP8.5 | North York | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| North YorkIce Accretion2065RCP8.5 | North York | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| North YorkIce Accretion2070RCP8.5 | North York | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
| North YorkIce Accretion2075RCP8.5 | North York | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
| North YorkIce Accretion2080RCP8.5 | North York | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
| North YorkIce Accretion2085RCP8.5 | North York | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
| North YorkIce Accretion2090RCP8.5 | North York | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| North YorkIce Accretion2095RCP8.5 | North York | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| North YorkIce Accretion2100RCP8.5 | North York | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| North YorkWind2023RCP4.5 | North York | Wind | RCP4.5 | 2023 | 83.9588 | 90.3904 | 97.1552 | 103.9249 | 110.6906
| North YorkWind2025RCP4.5 | North York | Wind | RCP4.5 | 2025 | 83.9742 | 90.4235 | 97.2086 | 103.9959 | 110.779
| North YorkWind2030RCP4.5 | North York | Wind | RCP4.5 | 2030 | 83.9895 | 90.4566 | 97.2619 | 104.0668 | 110.8675
| North YorkWind2035RCP4.5 | North York | Wind | RCP4.5 | 2035 | 84.0049 | 90.4897 | 97.3152 | 104.1377 | 110.956
| North YorkWind2040RCP4.5 | North York | Wind | RCP4.5 | 2040 | 84.0202 | 90.5227 | 97.3686 | 104.2086 | 111.0444
| North YorkWind2045RCP4.5 | North York | Wind | RCP4.5 | 2045 | 84.0356 | 90.5558 | 97.4219 | 104.2795 | 111.1329
| North YorkWind2050RCP4.5 | North York | Wind | RCP4.5 | 2050 | 84.133 | 90.6917 | 97.6053 | 104.502 | 111.3983
| North YorkWind2055RCP4.5 | North York | Wind | RCP4.5 | 2055 | 84.2151 | 90.7946 | 97.7353 | 104.6535 | 111.5752
| North YorkWind2060RCP4.5 | North York | Wind | RCP4.5 | 2060 | 84.2972 | 90.8974 | 97.8652 | 104.8051 | 111.7521
| North YorkWind2065RCP4.5 | North York | Wind | RCP4.5 | 2065 | 84.3793 | 91.0002 | 97.9952 | 104.9566 | 111.9291
| North YorkWind2070RCP4.5 | North York | Wind | RCP4.5 | 2070 | 84.4614 | 91.1031 | 98.1252 | 105.1081 | 112.106
| North YorkWind2075RCP4.5 | North York | Wind | RCP4.5 | 2075 | 84.6037 | 91.2865 | 98.3596 | 105.3866 | 112.4285
| North YorkWind2080RCP4.5 | North York | Wind | RCP4.5 | 2080 | 84.7461 | 91.4699 | 98.594 | 105.6651 | 112.7511
| North YorkWind2085RCP4.5 | North York | Wind | RCP4.5 | 2085 | 84.8885 | 91.6534 | 98.8285 | 105.9436 | 113.0736
| North YorkWind2090RCP4.5 | North York | Wind | RCP4.5 | 2090 | 85.0309 | 91.8368 | 99.0629 | 106.2221 | 113.3961
| North YorkWind2095RCP4.5 | North York | Wind | RCP4.5 | 2095 | 85.1733 | 92.0202 | 99.2973 | 106.5006 | 113.7186
| North YorkWind2100RCP4.5 | North York | Wind | RCP4.5 | 2100 | 85.3157 | 92.2036 | 99.5317 | 106.7792 | 114.0412
| North YorkWind2023RCP6.0 | North York | Wind | RCP6.0 | 2023 | 83.9588 | 90.3904 | 97.1552 | 103.9249 | 110.6906
| North YorkWind2025RCP6.0 | North York | Wind | RCP6.0 | 2025 | 83.9742 | 90.4235 | 97.2086 | 103.9959 | 110.779
| North YorkWind2030RCP6.0 | North York | Wind | RCP6.0 | 2030 | 83.9895 | 90.4566 | 97.2619 | 104.0668 | 110.8675
| North YorkWind2035RCP6.0 | North York | Wind | RCP6.0 | 2035 | 84.0049 | 90.4897 | 97.3152 | 104.1377 | 110.956
| North YorkWind2040RCP6.0 | North York | Wind | RCP6.0 | 2040 | 84.0202 | 90.5227 | 97.3686 | 104.2086 | 111.0444
| North YorkWind2045RCP6.0 | North York | Wind | RCP6.0 | 2045 | 84.0356 | 90.5558 | 97.4219 | 104.2795 | 111.1329
| North YorkWind2050RCP6.0 | North York | Wind | RCP6.0 | 2050 | 84.133 | 90.6917 | 97.6053 | 104.502 | 111.3983
| North YorkWind2055RCP6.0 | North York | Wind | RCP6.0 | 2055 | 84.2151 | 90.7946 | 97.7353 | 104.6535 | 111.5752
| North YorkWind2060RCP6.0 | North York | Wind | RCP6.0 | 2060 | 84.2972 | 90.8974 | 97.8652 | 104.8051 | 111.7521
| North YorkWind2065RCP6.0 | North York | Wind | RCP6.0 | 2065 | 84.3793 | 91.0002 | 97.9952 | 104.9566 | 111.9291
| North YorkWind2070RCP6.0 | North York | Wind | RCP6.0 | 2070 | 84.4614 | 91.1031 | 98.1252 | 105.1081 | 112.106
| North YorkWind2075RCP6.0 | North York | Wind | RCP6.0 | 2075 | 84.6749 | 91.3782 | 98.4768 | 105.5259 | 112.5898
| North YorkWind2080RCP6.0 | North York | Wind | RCP6.0 | 2080 | 84.8885 | 91.6534 | 98.8285 | 105.9436 | 113.0736
| North YorkWind2085RCP6.0 | North York | Wind | RCP6.0 | 2085 | 85.1021 | 91.9285 | 99.1801 | 106.3614 | 113.5574
| North YorkWind2090RCP6.0 | North York | Wind | RCP6.0 | 2090 | 85.7568 | 92.7449 | 100.201 | 107.5576 | 114.9332
| North YorkWind2095RCP6.0 | North York | Wind | RCP6.0 | 2095 | 86.1979 | 93.2862 | 100.8703 | 108.336 | 115.8252
| North YorkWind2100RCP6.0 | North York | Wind | RCP6.0 | 2100 | 86.6391 | 93.8274 | 101.5396 | 109.1144 | 116.7172
| North YorkWind2023RCP8.5 | North York | Wind | RCP8.5 | 2023 | 83.9588 | 90.3904 | 97.1552 | 103.9249 | 110.6906
| North YorkWind2025RCP8.5 | North York | Wind | RCP8.5 | 2025 | 83.9895 | 90.4566 | 97.2619 | 104.0668 | 110.8675
| North YorkWind2030RCP8.5 | North York | Wind | RCP8.5 | 2030 | 84.0202 | 90.5227 | 97.3686 | 104.2086 | 111.0444
| North YorkWind2035RCP8.5 | North York | Wind | RCP8.5 | 2035 | 84.0509 | 90.5889 | 97.4753 | 104.3505 | 111.2214
| North YorkWind2040RCP8.5 | North York | Wind | RCP8.5 | 2040 | 84.1878 | 90.7603 | 97.6919 | 104.603 | 111.5162
| North YorkWind2045RCP8.5 | North York | Wind | RCP8.5 | 2045 | 84.3246 | 90.9317 | 97.9086 | 104.8556 | 111.8111
| North YorkWind2050RCP8.5 | North York | Wind | RCP8.5 | 2050 | 84.7461 | 91.4699 | 98.594 | 105.6651 | 112.7511
| North YorkWind2055RCP8.5 | North York | Wind | RCP8.5 | 2055 | 85.0309 | 91.8368 | 99.0629 | 106.2221 | 113.3961
| North YorkWind2060RCP8.5 | North York | Wind | RCP8.5 | 2060 | 85.7568 | 92.7449 | 100.201 | 107.5576 | 114.9332
| North YorkWind2065RCP8.5 | North York | Wind | RCP8.5 | 2065 | 86.1979 | 93.2862 | 100.8703 | 108.336 | 115.8252
| North YorkWind2070RCP8.5 | North York | Wind | RCP8.5 | 2070 | 86.7703 | 94.0048 | 101.7756 | 109.405 | 117.0563
| North YorkWind2075RCP8.5 | North York | Wind | RCP8.5 | 2075 | 86.9015 | 94.1822 | 102.0117 | 109.6957 | 117.3954
| North YorkWind2080RCP8.5 | North York | Wind | RCP8.5 | 2080 | 87.0327 | 94.3597 | 102.2477 | 109.9863 | 117.7345
| North YorkWind2085RCP8.5 | North York | Wind | RCP8.5 | 2085 | 87.3133 | 94.7566 | 102.7909 | 110.6505 | 118.5252
| North YorkWind2090RCP8.5 | North York | Wind | RCP8.5 | 2090 | 87.5939 | 95.1535 | 103.3341 | 111.3148 | 119.3158
| North YorkWind2095RCP8.5 | North York | Wind | RCP8.5 | 2095 | 87.5939 | 95.1535 | 103.3341 | 111.3148 | 119.3158
| North YorkWind2100RCP8.5 | North York | Wind | RCP8.5 | 2100 | 87.5939 | 95.1535 | 103.3341 | 111.3148 | 119.3158
| NorwoodIce Accretion2023RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3065 | 31.563
| NorwoodIce Accretion2025RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2025 | 17.544 | 20.9091 | 25.1667 | 28.4148 | 31.6837
| NorwoodIce Accretion2030RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2030 | 17.6049 | 20.9852 | 25.2583 | 28.5231 | 31.8045
| NorwoodIce Accretion2035RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2035 | 17.6658 | 21.0613 | 25.35 | 28.6314 | 31.9252
| NorwoodIce Accretion2040RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2040 | 17.7267 | 21.1373 | 25.4417 | 28.7397 | 32.046
| NorwoodIce Accretion2045RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2045 | 17.7876 | 21.2134 | 25.5333 | 28.848 | 32.1667
| NorwoodIce Accretion2050RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2050 | 17.8032 | 21.248 | 25.595 | 28.928 | 32.2623
| NorwoodIce Accretion2055RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2055 | 17.758 | 21.2065 | 25.565 | 28.8997 | 32.2371
| NorwoodIce Accretion2060RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2060 | 17.7128 | 21.165 | 25.535 | 28.8715 | 32.2119
| NorwoodIce Accretion2065RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2065 | 17.6675 | 21.1235 | 25.505 | 28.8432 | 32.1867
| NorwoodIce Accretion2070RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2070 | 17.6223 | 21.082 | 25.475 | 28.815 | 32.1615
| NorwoodIce Accretion2075RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2075 | 17.6919 | 21.1927 | 25.6375 | 29.0175 | 32.403
| NorwoodIce Accretion2080RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2080 | 17.7615 | 21.3033 | 25.8 | 29.2199 | 32.6445
| NorwoodIce Accretion2085RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2085 | 17.8311 | 21.414 | 25.9625 | 29.4224 | 32.886
| NorwoodIce Accretion2090RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2090 | 17.9006 | 21.5247 | 26.125 | 29.6248 | 33.1275
| NorwoodIce Accretion2095RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2095 | 17.9702 | 21.6353 | 26.2875 | 29.8273 | 33.369
| NorwoodIce Accretion2100RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2100 | 18.0398 | 21.746 | 26.45 | 30.0297 | 33.6105
| NorwoodIce Accretion2023RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3065 | 31.563
| NorwoodIce Accretion2025RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2025 | 17.544 | 20.9091 | 25.1667 | 28.4148 | 31.6837
| NorwoodIce Accretion2030RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2030 | 17.6049 | 20.9852 | 25.2583 | 28.5231 | 31.8045
| NorwoodIce Accretion2035RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2035 | 17.6658 | 21.0613 | 25.35 | 28.6314 | 31.9252
| NorwoodIce Accretion2040RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2040 | 17.7267 | 21.1373 | 25.4417 | 28.7397 | 32.046
| NorwoodIce Accretion2045RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2045 | 17.7876 | 21.2134 | 25.5333 | 28.848 | 32.1667
| NorwoodIce Accretion2050RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2050 | 17.8032 | 21.248 | 25.595 | 28.928 | 32.2623
| NorwoodIce Accretion2055RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2055 | 17.758 | 21.2065 | 25.565 | 28.8997 | 32.2371
| NorwoodIce Accretion2060RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2060 | 17.7128 | 21.165 | 25.535 | 28.8715 | 32.2119
| NorwoodIce Accretion2065RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2065 | 17.6675 | 21.1235 | 25.505 | 28.8432 | 32.1867
| NorwoodIce Accretion2070RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2070 | 17.6223 | 21.082 | 25.475 | 28.815 | 32.1615
| NorwoodIce Accretion2075RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2075 | 17.7267 | 21.248 | 25.7188 | 29.1187 | 32.5237
| NorwoodIce Accretion2080RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2080 | 17.8311 | 21.414 | 25.9625 | 29.4224 | 32.886
| NorwoodIce Accretion2085RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2085 | 17.9354 | 21.58 | 26.2063 | 29.7261 | 33.2482
| NorwoodIce Accretion2090RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2090 | 17.7499 | 21.4486 | 26.1333 | 29.7002 | 33.264
| NorwoodIce Accretion2095RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2095 | 17.4599 | 21.1512 | 25.8167 | 29.3706 | 32.9175
| NorwoodIce Accretion2100RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2100 | 17.17 | 20.8537 | 25.5 | 29.041 | 32.571
| NorwoodIce Accretion2023RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3065 | 31.563
| NorwoodIce Accretion2025RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2025 | 17.6049 | 20.9852 | 25.2583 | 28.5231 | 31.8045
| NorwoodIce Accretion2030RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2030 | 17.7267 | 21.1373 | 25.4417 | 28.7397 | 32.046
| NorwoodIce Accretion2035RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2035 | 17.8485 | 21.2895 | 25.625 | 28.9562 | 32.2875
| NorwoodIce Accretion2040RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2040 | 17.7731 | 21.2203 | 25.575 | 28.9092 | 32.2455
| NorwoodIce Accretion2045RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2045 | 17.6977 | 21.1512 | 25.525 | 28.8621 | 32.2035
| NorwoodIce Accretion2050RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2050 | 17.7615 | 21.3033 | 25.8 | 29.2199 | 32.6445
| NorwoodIce Accretion2055RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2055 | 17.9006 | 21.5247 | 26.125 | 29.6248 | 33.1275
| NorwoodIce Accretion2060RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2060 | 17.7499 | 21.4486 | 26.1333 | 29.7002 | 33.264
| NorwoodIce Accretion2065RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2065 | 17.4599 | 21.1512 | 25.8167 | 29.3706 | 32.9175
| NorwoodIce Accretion2070RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2070 | 16.8801 | 20.5287 | 25.1417 | 28.6455 | 32.151
| NorwoodIce Accretion2075RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2075 | 16.5901 | 20.2036 | 24.7833 | 28.25 | 31.731
| NorwoodIce Accretion2080RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2080 | 16.3002 | 19.8785 | 24.425 | 27.8545 | 31.311
| NorwoodIce Accretion2085RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2085 | 15.6826 | 19.1626 | 23.5875 | 26.9222 | 30.2715
| NorwoodIce Accretion2090RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2090 | 15.0651 | 18.4468 | 22.75 | 25.99 | 29.232
| NorwoodIce Accretion2095RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2095 | 15.0651 | 18.4468 | 22.75 | 25.99 | 29.232
| NorwoodIce Accretion2100RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2100 | 15.0651 | 18.4468 | 22.75 | 25.99 | 29.232
| NorwoodWind2023RCP4.5 | Norwood | Wind | RCP4.5 | 2023 | 74.4377 | 80.2119 | 86.301 | 92.3697 | 98.4518
| NorwoodWind2025RCP4.5 | Norwood | Wind | RCP4.5 | 2025 | 74.4674 | 80.2559 | 86.3612 | 92.4464 | 98.5433
| NorwoodWind2030RCP4.5 | Norwood | Wind | RCP4.5 | 2030 | 74.4971 | 80.2999 | 86.4214 | 92.523 | 98.6348
| NorwoodWind2035RCP4.5 | Norwood | Wind | RCP4.5 | 2035 | 74.5268 | 80.3439 | 86.4816 | 92.5997 | 98.7263
| NorwoodWind2040RCP4.5 | Norwood | Wind | RCP4.5 | 2040 | 74.5565 | 80.3879 | 86.5418 | 92.6764 | 98.8178
| NorwoodWind2045RCP4.5 | Norwood | Wind | RCP4.5 | 2045 | 74.5862 | 80.4319 | 86.602 | 92.7531 | 98.9093
| NorwoodWind2050RCP4.5 | Norwood | Wind | RCP4.5 | 2050 | 74.5922 | 80.4311 | 86.5951 | 92.7414 | 98.891
| NorwoodWind2055RCP4.5 | Norwood | Wind | RCP4.5 | 2055 | 74.5684 | 80.3863 | 86.528 | 92.6531 | 98.7812
| NorwoodWind2060RCP4.5 | Norwood | Wind | RCP4.5 | 2060 | 74.5446 | 80.3415 | 86.461 | 92.5648 | 98.6714
| NorwoodWind2065RCP4.5 | Norwood | Wind | RCP4.5 | 2065 | 74.5209 | 80.2967 | 86.3939 | 92.4764 | 98.5616
| NorwoodWind2070RCP4.5 | Norwood | Wind | RCP4.5 | 2070 | 74.4971 | 80.2519 | 86.3268 | 92.3881 | 98.4518
| NorwoodWind2075RCP4.5 | Norwood | Wind | RCP4.5 | 2075 | 74.4748 | 80.2266 | 86.2967 | 92.3543 | 98.4158
| NorwoodWind2080RCP4.5 | Norwood | Wind | RCP4.5 | 2080 | 74.4526 | 80.2013 | 86.2666 | 92.3206 | 98.3799
| NorwoodWind2085RCP4.5 | Norwood | Wind | RCP4.5 | 2085 | 74.4303 | 80.176 | 86.2365 | 92.2869 | 98.3439
| NorwoodWind2090RCP4.5 | Norwood | Wind | RCP4.5 | 2090 | 74.408 | 80.1506 | 86.2064 | 92.2531 | 98.308
| NorwoodWind2095RCP4.5 | Norwood | Wind | RCP4.5 | 2095 | 74.3857 | 80.1253 | 86.1763 | 92.2194 | 98.272
| NorwoodWind2100RCP4.5 | Norwood | Wind | RCP4.5 | 2100 | 74.3635 | 80.1 | 86.1462 | 92.1856 | 98.2361
| NorwoodWind2023RCP6.0 | Norwood | Wind | RCP6.0 | 2023 | 74.4377 | 80.2119 | 86.301 | 92.3697 | 98.4518
| NorwoodWind2025RCP6.0 | Norwood | Wind | RCP6.0 | 2025 | 74.4674 | 80.2559 | 86.3612 | 92.4464 | 98.5433
| NorwoodWind2030RCP6.0 | Norwood | Wind | RCP6.0 | 2030 | 74.4971 | 80.2999 | 86.4214 | 92.523 | 98.6348
| NorwoodWind2035RCP6.0 | Norwood | Wind | RCP6.0 | 2035 | 74.5268 | 80.3439 | 86.4816 | 92.5997 | 98.7263
| NorwoodWind2040RCP6.0 | Norwood | Wind | RCP6.0 | 2040 | 74.5565 | 80.3879 | 86.5418 | 92.6764 | 98.8178
| NorwoodWind2045RCP6.0 | Norwood | Wind | RCP6.0 | 2045 | 74.5862 | 80.4319 | 86.602 | 92.7531 | 98.9093
| NorwoodWind2050RCP6.0 | Norwood | Wind | RCP6.0 | 2050 | 74.5922 | 80.4311 | 86.5951 | 92.7414 | 98.891
| NorwoodWind2055RCP6.0 | Norwood | Wind | RCP6.0 | 2055 | 74.5684 | 80.3863 | 86.528 | 92.6531 | 98.7812
| NorwoodWind2060RCP6.0 | Norwood | Wind | RCP6.0 | 2060 | 74.5446 | 80.3415 | 86.461 | 92.5648 | 98.6714
| NorwoodWind2065RCP6.0 | Norwood | Wind | RCP6.0 | 2065 | 74.5209 | 80.2967 | 86.3939 | 92.4764 | 98.5616
| NorwoodWind2070RCP6.0 | Norwood | Wind | RCP6.0 | 2070 | 74.4971 | 80.2519 | 86.3268 | 92.3881 | 98.4518
| NorwoodWind2075RCP6.0 | Norwood | Wind | RCP6.0 | 2075 | 74.4637 | 80.2139 | 86.2817 | 92.3375 | 98.3978
| NorwoodWind2080RCP6.0 | Norwood | Wind | RCP6.0 | 2080 | 74.4303 | 80.176 | 86.2365 | 92.2869 | 98.3439
| NorwoodWind2085RCP6.0 | Norwood | Wind | RCP6.0 | 2085 | 74.3969 | 80.138 | 86.1913 | 92.2362 | 98.29
| NorwoodWind2090RCP6.0 | Norwood | Wind | RCP6.0 | 2090 | 74.3511 | 80.076 | 86.1061 | 92.1304 | 98.1642
| NorwoodWind2095RCP6.0 | Norwood | Wind | RCP6.0 | 2095 | 74.3387 | 80.052 | 86.0659 | 92.0752 | 98.0923
| NorwoodWind2100RCP6.0 | Norwood | Wind | RCP6.0 | 2100 | 74.3263 | 80.028 | 86.0258 | 92.02 | 98.0204
| NorwoodWind2023RCP8.5 | Norwood | Wind | RCP8.5 | 2023 | 74.4377 | 80.2119 | 86.301 | 92.3697 | 98.4518
| NorwoodWind2025RCP8.5 | Norwood | Wind | RCP8.5 | 2025 | 74.4971 | 80.2999 | 86.4214 | 92.523 | 98.6348
| NorwoodWind2030RCP8.5 | Norwood | Wind | RCP8.5 | 2030 | 74.5565 | 80.3879 | 86.5418 | 92.6764 | 98.8178
| NorwoodWind2035RCP8.5 | Norwood | Wind | RCP8.5 | 2035 | 74.6159 | 80.4759 | 86.6622 | 92.8298 | 99.0008
| NorwoodWind2040RCP8.5 | Norwood | Wind | RCP8.5 | 2040 | 74.5763 | 80.4012 | 86.5504 | 92.6825 | 98.8178
| NorwoodWind2045RCP8.5 | Norwood | Wind | RCP8.5 | 2045 | 74.5367 | 80.3266 | 86.4386 | 92.5353 | 98.6348
| NorwoodWind2050RCP8.5 | Norwood | Wind | RCP8.5 | 2050 | 74.4526 | 80.2013 | 86.2666 | 92.3206 | 98.3799
| NorwoodWind2055RCP8.5 | Norwood | Wind | RCP8.5 | 2055 | 74.408 | 80.1506 | 86.2064 | 92.2531 | 98.308
| NorwoodWind2060RCP8.5 | Norwood | Wind | RCP8.5 | 2060 | 74.3511 | 80.076 | 86.1061 | 92.1304 | 98.1642
| NorwoodWind2065RCP8.5 | Norwood | Wind | RCP8.5 | 2065 | 74.3387 | 80.052 | 86.0659 | 92.0752 | 98.0923
| NorwoodWind2070RCP8.5 | Norwood | Wind | RCP8.5 | 2070 | 74.2941 | 79.9853 | 85.9713 | 91.9556 | 97.9452
| NorwoodWind2075RCP8.5 | Norwood | Wind | RCP8.5 | 2075 | 74.262 | 79.9427 | 85.9169 | 91.8912 | 97.8701
| NorwoodWind2080RCP8.5 | Norwood | Wind | RCP8.5 | 2080 | 74.2298 | 79.9 | 85.8624 | 91.8268 | 97.7949
| NorwoodWind2085RCP8.5 | Norwood | Wind | RCP8.5 | 2085 | 74.1889 | 79.872 | 85.8495 | 91.8314 | 97.8096
| NorwoodWind2090RCP8.5 | Norwood | Wind | RCP8.5 | 2090 | 74.1481 | 79.844 | 85.8366 | 91.836 | 97.8243
| NorwoodWind2095RCP8.5 | Norwood | Wind | RCP8.5 | 2095 | 74.1481 | 79.844 | 85.8366 | 91.836 | 97.8243
| NorwoodWind2100RCP8.5 | Norwood | Wind | RCP8.5 | 2100 | 74.1481 | 79.844 | 85.8366 | 91.836 | 97.8243
| OakvilleIce Accretion2023RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| OakvilleIce Accretion2025RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
| OakvilleIce Accretion2030RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| OakvilleIce Accretion2035RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
| OakvilleIce Accretion2040RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| OakvilleIce Accretion2045RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
| OakvilleIce Accretion2050RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
| OakvilleIce Accretion2055RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
| OakvilleIce Accretion2060RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
| OakvilleIce Accretion2065RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
| OakvilleIce Accretion2070RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
| OakvilleIce Accretion2075RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2075 | 15.5377 | 18.8894 | 23.1125 | 26.329 | 29.5313
| OakvilleIce Accretion2080RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2080 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
| OakvilleIce Accretion2085RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2085 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
| OakvilleIce Accretion2090RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2090 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
| OakvilleIce Accretion2095RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2095 | 15.3405 | 18.7511 | 23.0625 | 26.329 | 29.5942
| OakvilleIce Accretion2100RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2100 | 15.2912 | 18.7165 | 23.05 | 26.329 | 29.61
| OakvilleIce Accretion2023RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| OakvilleIce Accretion2025RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
| OakvilleIce Accretion2030RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| OakvilleIce Accretion2035RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
| OakvilleIce Accretion2040RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| OakvilleIce Accretion2045RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
| OakvilleIce Accretion2050RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
| OakvilleIce Accretion2055RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
| OakvilleIce Accretion2060RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
| OakvilleIce Accretion2065RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
| OakvilleIce Accretion2070RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
| OakvilleIce Accretion2075RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2075 | 15.513 | 18.8721 | 23.1062 | 26.329 | 29.5391
| OakvilleIce Accretion2080RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2080 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
| OakvilleIce Accretion2085RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2085 | 15.3652 | 18.7684 | 23.0688 | 26.329 | 29.5864
| OakvilleIce Accretion2090RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2090 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
| OakvilleIce Accretion2095RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2095 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
| OakvilleIce Accretion2100RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2100 | 14.2127 | 17.596 | 21.825 | 25.0577 | 28.2555
| OakvilleIce Accretion2023RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| OakvilleIce Accretion2025RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2025 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| OakvilleIce Accretion2030RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2030 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| OakvilleIce Accretion2035RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2035 | 16.6133 | 20.0652 | 24.425 | 27.7415 | 31.059
| OakvilleIce Accretion2040RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2040 | 16.2712 | 19.6848 | 23.9917 | 27.2707 | 30.5445
| OakvilleIce Accretion2045RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2045 | 15.9291 | 19.3044 | 23.5583 | 26.7998 | 30.03
| OakvilleIce Accretion2050RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2050 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
| OakvilleIce Accretion2055RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2055 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
| OakvilleIce Accretion2060RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2060 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
| OakvilleIce Accretion2065RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2065 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
| OakvilleIce Accretion2070RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2070 | 13.8125 | 17.1464 | 21.325 | 24.5022 | 27.657
| OakvilleIce Accretion2075RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2075 | 13.4124 | 16.6968 | 20.825 | 23.9466 | 27.0585
| OakvilleIce Accretion2080RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2080 | 13.0123 | 16.2473 | 20.325 | 23.391 | 26.46
| OakvilleIce Accretion2085RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2085 | 12.1338 | 15.1994 | 19.0625 | 21.9785 | 24.885
| OakvilleIce Accretion2090RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2090 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| OakvilleIce Accretion2095RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2095 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| OakvilleIce Accretion2100RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2100 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| OakvilleWind2023RCP4.5 | Oakville | Wind | RCP4.5 | 2023 | 85.9036 | 92.5764 | 99.6138 | 106.6397 | 113.6613
| OakvilleWind2025RCP4.5 | Oakville | Wind | RCP4.5 | 2025 | 85.935 | 92.6224 | 99.6798 | 106.7227 | 113.761
| OakvilleWind2030RCP4.5 | Oakville | Wind | RCP4.5 | 2030 | 85.9663 | 92.6685 | 99.7458 | 106.8057 | 113.8607
| OakvilleWind2035RCP4.5 | Oakville | Wind | RCP4.5 | 2035 | 85.9977 | 92.7145 | 99.8118 | 106.8887 | 113.9604
| OakvilleWind2040RCP4.5 | Oakville | Wind | RCP4.5 | 2040 | 86.029 | 92.7605 | 99.8778 | 106.9716 | 114.0601
| OakvilleWind2045RCP4.5 | Oakville | Wind | RCP4.5 | 2045 | 86.0604 | 92.8066 | 99.9438 | 107.0546 | 114.1598
| OakvilleWind2050RCP4.5 | Oakville | Wind | RCP4.5 | 2050 | 86.1601 | 92.9355 | 100.1108 | 107.2541 | 114.3926
| OakvilleWind2055RCP4.5 | Oakville | Wind | RCP4.5 | 2055 | 86.2285 | 93.0183 | 100.2118 | 107.3706 | 114.5258
| OakvilleWind2060RCP4.5 | Oakville | Wind | RCP4.5 | 2060 | 86.2969 | 93.1012 | 100.3127 | 107.4872 | 114.659
| OakvilleWind2065RCP4.5 | Oakville | Wind | RCP4.5 | 2065 | 86.3653 | 93.184 | 100.4137 | 107.6037 | 114.7922
| OakvilleWind2070RCP4.5 | Oakville | Wind | RCP4.5 | 2070 | 86.4336 | 93.2669 | 100.5147 | 107.7202 | 114.9253
| OakvilleWind2075RCP4.5 | Oakville | Wind | RCP4.5 | 2075 | 86.5277 | 93.3989 | 100.6946 | 107.9391 | 115.1849
| OakvilleWind2080RCP4.5 | Oakville | Wind | RCP4.5 | 2080 | 86.6217 | 93.5308 | 100.8744 | 108.1581 | 115.4445
| OakvilleWind2085RCP4.5 | Oakville | Wind | RCP4.5 | 2085 | 86.7157 | 93.6628 | 101.0542 | 108.377 | 115.7041
| OakvilleWind2090RCP4.5 | Oakville | Wind | RCP4.5 | 2090 | 86.8098 | 93.7948 | 101.2341 | 108.5959 | 115.9636
| OakvilleWind2095RCP4.5 | Oakville | Wind | RCP4.5 | 2095 | 86.9038 | 93.9267 | 101.4139 | 108.8148 | 116.2232
| OakvilleWind2100RCP4.5 | Oakville | Wind | RCP4.5 | 2100 | 86.9978 | 94.0587 | 101.5938 | 109.0337 | 116.4828
| OakvilleWind2023RCP6.0 | Oakville | Wind | RCP6.0 | 2023 | 85.9036 | 92.5764 | 99.6138 | 106.6397 | 113.6613
| OakvilleWind2025RCP6.0 | Oakville | Wind | RCP6.0 | 2025 | 85.935 | 92.6224 | 99.6798 | 106.7227 | 113.761
| OakvilleWind2030RCP6.0 | Oakville | Wind | RCP6.0 | 2030 | 85.9663 | 92.6685 | 99.7458 | 106.8057 | 113.8607
| OakvilleWind2035RCP6.0 | Oakville | Wind | RCP6.0 | 2035 | 85.9977 | 92.7145 | 99.8118 | 106.8887 | 113.9604
| OakvilleWind2040RCP6.0 | Oakville | Wind | RCP6.0 | 2040 | 86.029 | 92.7605 | 99.8778 | 106.9716 | 114.0601
| OakvilleWind2045RCP6.0 | Oakville | Wind | RCP6.0 | 2045 | 86.0604 | 92.8066 | 99.9438 | 107.0546 | 114.1598
| OakvilleWind2050RCP6.0 | Oakville | Wind | RCP6.0 | 2050 | 86.1601 | 92.9355 | 100.1108 | 107.2541 | 114.3926
| OakvilleWind2055RCP6.0 | Oakville | Wind | RCP6.0 | 2055 | 86.2285 | 93.0183 | 100.2118 | 107.3706 | 114.5258
| OakvilleWind2060RCP6.0 | Oakville | Wind | RCP6.0 | 2060 | 86.2969 | 93.1012 | 100.3127 | 107.4872 | 114.659
| OakvilleWind2065RCP6.0 | Oakville | Wind | RCP6.0 | 2065 | 86.3653 | 93.184 | 100.4137 | 107.6037 | 114.7922
| OakvilleWind2070RCP6.0 | Oakville | Wind | RCP6.0 | 2070 | 86.4336 | 93.2669 | 100.5147 | 107.7202 | 114.9253
| OakvilleWind2075RCP6.0 | Oakville | Wind | RCP6.0 | 2075 | 86.5747 | 93.4649 | 100.7845 | 108.0486 | 115.3147
| OakvilleWind2080RCP6.0 | Oakville | Wind | RCP6.0 | 2080 | 86.7157 | 93.6628 | 101.0542 | 108.377 | 115.7041
| OakvilleWind2085RCP6.0 | Oakville | Wind | RCP6.0 | 2085 | 86.8568 | 93.8608 | 101.324 | 108.7054 | 116.0934
| OakvilleWind2090RCP6.0 | Oakville | Wind | RCP6.0 | 2090 | 87.2942 | 94.4393 | 102.0789 | 109.6093 | 117.1524
| OakvilleWind2095RCP6.0 | Oakville | Wind | RCP6.0 | 2095 | 87.5905 | 94.8198 | 102.564 | 110.1849 | 117.8221
| OakvilleWind2100RCP6.0 | Oakville | Wind | RCP6.0 | 2100 | 87.8869 | 95.2004 | 103.0491 | 110.7604 | 118.4917
| OakvilleWind2023RCP8.5 | Oakville | Wind | RCP8.5 | 2023 | 85.9036 | 92.5764 | 99.6138 | 106.6397 | 113.6613
| OakvilleWind2025RCP8.5 | Oakville | Wind | RCP8.5 | 2025 | 85.9663 | 92.6685 | 99.7458 | 106.8057 | 113.8607
| OakvilleWind2030RCP8.5 | Oakville | Wind | RCP8.5 | 2030 | 86.029 | 92.7605 | 99.8778 | 106.9716 | 114.0601
| OakvilleWind2035RCP8.5 | Oakville | Wind | RCP8.5 | 2035 | 86.0917 | 92.8526 | 100.0098 | 107.1376 | 114.2595
| OakvilleWind2040RCP8.5 | Oakville | Wind | RCP8.5 | 2040 | 86.2057 | 92.9907 | 100.1781 | 107.3318 | 114.4814
| OakvilleWind2045RCP8.5 | Oakville | Wind | RCP8.5 | 2045 | 86.3197 | 93.1288 | 100.3464 | 107.526 | 114.7034
| OakvilleWind2050RCP8.5 | Oakville | Wind | RCP8.5 | 2050 | 86.6217 | 93.5308 | 100.8744 | 108.1581 | 115.4445
| OakvilleWind2055RCP8.5 | Oakville | Wind | RCP8.5 | 2055 | 86.8098 | 93.7948 | 101.2341 | 108.5959 | 115.9636
| OakvilleWind2060RCP8.5 | Oakville | Wind | RCP8.5 | 2060 | 87.2942 | 94.4393 | 102.0789 | 109.6093 | 117.1524
| OakvilleWind2065RCP8.5 | Oakville | Wind | RCP8.5 | 2065 | 87.5905 | 94.8198 | 102.564 | 110.1849 | 117.8221
| OakvilleWind2070RCP8.5 | Oakville | Wind | RCP8.5 | 2070 | 88.055 | 95.4428 | 103.3857 | 111.1735 | 118.9845
| OakvilleWind2075RCP8.5 | Oakville | Wind | RCP8.5 | 2075 | 88.2231 | 95.6853 | 103.7223 | 111.5867 | 119.4774
| OakvilleWind2080RCP8.5 | Oakville | Wind | RCP8.5 | 2080 | 88.3912 | 95.9277 | 104.0589 | 111.9998 | 119.9702
| OakvilleWind2085RCP8.5 | Oakville | Wind | RCP8.5 | 2085 | 88.6605 | 96.2776 | 104.5093 | 112.54 | 120.6022
| OakvilleWind2090RCP8.5 | Oakville | Wind | RCP8.5 | 2090 | 88.9298 | 96.6275 | 104.9598 | 113.0803 | 121.2342
| OakvilleWind2095RCP8.5 | Oakville | Wind | RCP8.5 | 2095 | 88.9298 | 96.6275 | 104.9598 | 113.0803 | 121.2342
| OakvilleWind2100RCP8.5 | Oakville | Wind | RCP8.5 | 2100 | 88.9298 | 96.6275 | 104.9598 | 113.0803 | 121.2342
| OrangevilleIce Accretion2023RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2023 | 16.8005 | 20.159 | 24.432 | 27.6895 | 30.9355
| OrangevilleIce Accretion2025RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2025 | 16.8228 | 20.1989 | 24.492 | 27.7664 | 31.0262
| OrangevilleIce Accretion2030RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2030 | 16.845 | 20.2387 | 24.552 | 27.8432 | 31.117
| OrangevilleIce Accretion2035RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2035 | 16.8673 | 20.2786 | 24.612 | 27.92 | 31.2077
| OrangevilleIce Accretion2040RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2040 | 16.8896 | 20.3184 | 24.672 | 27.9969 | 31.2984
| OrangevilleIce Accretion2045RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2045 | 16.9118 | 20.3582 | 24.732 | 28.0737 | 31.3891
| OrangevilleIce Accretion2050RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2050 | 16.8974 | 20.3702 | 24.7776 | 28.1451 | 31.4919
| OrangevilleIce Accretion2055RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2055 | 16.8606 | 20.3423 | 24.7632 | 28.1397 | 31.504
| OrangevilleIce Accretion2060RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2060 | 16.8239 | 20.3144 | 24.7488 | 28.1343 | 31.5161
| OrangevilleIce Accretion2065RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2065 | 16.7871 | 20.2865 | 24.7344 | 28.1289 | 31.5282
| OrangevilleIce Accretion2070RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2070 | 16.7504 | 20.2586 | 24.72 | 28.1234 | 31.5403
| OrangevilleIce Accretion2075RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2075 | 16.7281 | 20.262 | 24.752 | 28.1777 | 31.6159
| OrangevilleIce Accretion2080RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2080 | 16.7059 | 20.2653 | 24.784 | 28.2319 | 31.6915
| OrangevilleIce Accretion2085RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2085 | 16.6836 | 20.2686 | 24.816 | 28.2862 | 31.7671
| OrangevilleIce Accretion2090RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2090 | 16.6613 | 20.2719 | 24.848 | 28.3404 | 31.8427
| OrangevilleIce Accretion2095RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2095 | 16.6391 | 20.2752 | 24.88 | 28.3946 | 31.9183
| OrangevilleIce Accretion2100RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2100 | 16.6168 | 20.2786 | 24.912 | 28.4489 | 31.9939
| OrangevilleIce Accretion2023RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2023 | 16.8005 | 20.159 | 24.432 | 27.6895 | 30.9355
| OrangevilleIce Accretion2025RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2025 | 16.8228 | 20.1989 | 24.492 | 27.7664 | 31.0262
| OrangevilleIce Accretion2030RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2030 | 16.845 | 20.2387 | 24.552 | 27.8432 | 31.117
| OrangevilleIce Accretion2035RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2035 | 16.8673 | 20.2786 | 24.612 | 27.92 | 31.2077
| OrangevilleIce Accretion2040RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2040 | 16.8896 | 20.3184 | 24.672 | 27.9969 | 31.2984
| OrangevilleIce Accretion2045RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2045 | 16.9118 | 20.3582 | 24.732 | 28.0737 | 31.3891
| OrangevilleIce Accretion2050RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2050 | 16.8974 | 20.3702 | 24.7776 | 28.1451 | 31.4919
| OrangevilleIce Accretion2055RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2055 | 16.8606 | 20.3423 | 24.7632 | 28.1397 | 31.504
| OrangevilleIce Accretion2060RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2060 | 16.8239 | 20.3144 | 24.7488 | 28.1343 | 31.5161
| OrangevilleIce Accretion2065RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2065 | 16.7871 | 20.2865 | 24.7344 | 28.1289 | 31.5282
| OrangevilleIce Accretion2070RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2070 | 16.7504 | 20.2586 | 24.72 | 28.1234 | 31.5403
| OrangevilleIce Accretion2075RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2075 | 16.717 | 20.2636 | 24.768 | 28.2048 | 31.6537
| OrangevilleIce Accretion2080RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2080 | 16.6836 | 20.2686 | 24.816 | 28.2862 | 31.7671
| OrangevilleIce Accretion2085RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2085 | 16.6502 | 20.2736 | 24.864 | 28.3675 | 31.8805
| OrangevilleIce Accretion2090RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2090 | 16.3997 | 20.0661 | 24.704 | 28.241 | 31.7722
| OrangevilleIce Accretion2095RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2095 | 16.1826 | 19.8536 | 24.496 | 28.033 | 31.5504
| OrangevilleIce Accretion2100RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2100 | 15.9655 | 19.6411 | 24.288 | 27.8251 | 31.3286
| OrangevilleIce Accretion2023RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2023 | 16.8005 | 20.159 | 24.432 | 27.6895 | 30.9355
| OrangevilleIce Accretion2025RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2025 | 16.845 | 20.2387 | 24.552 | 27.8432 | 31.117
| OrangevilleIce Accretion2030RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2030 | 16.8896 | 20.3184 | 24.672 | 27.9969 | 31.2984
| OrangevilleIce Accretion2035RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2035 | 16.9341 | 20.3981 | 24.792 | 28.1506 | 31.4798
| OrangevilleIce Accretion2040RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2040 | 16.8729 | 20.3516 | 24.768 | 28.1415 | 31.5
| OrangevilleIce Accretion2045RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2045 | 16.8116 | 20.3051 | 24.744 | 28.1325 | 31.5202
| OrangevilleIce Accretion2050RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2050 | 16.7059 | 20.2653 | 24.784 | 28.2319 | 31.6915
| OrangevilleIce Accretion2055RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2055 | 16.6613 | 20.2719 | 24.848 | 28.3404 | 31.8427
| OrangevilleIce Accretion2060RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2060 | 16.3997 | 20.0661 | 24.704 | 28.241 | 31.7722
| OrangevilleIce Accretion2065RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2065 | 16.1826 | 19.8536 | 24.496 | 28.033 | 31.5504
| OrangevilleIce Accretion2070RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2070 | 15.5758 | 19.2095 | 23.8 | 27.2918 | 30.7642
| OrangevilleIce Accretion2075RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2075 | 15.1861 | 18.7779 | 23.312 | 26.7584 | 30.1997
| OrangevilleIce Accretion2080RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2080 | 14.7965 | 18.3463 | 22.824 | 26.225 | 29.6352
| OrangevilleIce Accretion2085RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2085 | 14.1619 | 17.6292 | 22.008 | 25.3301 | 28.6524
| OrangevilleIce Accretion2090RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2090 | 13.5272 | 16.9121 | 21.192 | 24.4351 | 27.6696
| OrangevilleIce Accretion2095RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2095 | 13.5272 | 16.9121 | 21.192 | 24.4351 | 27.6696
| OrangevilleIce Accretion2100RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2100 | 13.5272 | 16.9121 | 21.192 | 24.4351 | 27.6696
| OrangevilleWind2023RCP4.5 | Orangeville | Wind | RCP4.5 | 2023 | 79.6946 | 85.8509 | 92.3312 | 98.8042 | 105.2785
| OrangevilleWind2025RCP4.5 | Orangeville | Wind | RCP4.5 | 2025 | 79.7025 | 85.8652 | 92.3542 | 98.8338 | 105.317
| OrangevilleWind2030RCP4.5 | Orangeville | Wind | RCP4.5 | 2030 | 79.7105 | 85.8794 | 92.3772 | 98.8633 | 105.3555
| OrangevilleWind2035RCP4.5 | Orangeville | Wind | RCP4.5 | 2035 | 79.7184 | 85.8937 | 92.4002 | 98.8928 | 105.3939
| OrangevilleWind2040RCP4.5 | Orangeville | Wind | RCP4.5 | 2040 | 79.7264 | 85.9079 | 92.4232 | 98.9224 | 105.4324
| OrangevilleWind2045RCP4.5 | Orangeville | Wind | RCP4.5 | 2045 | 79.7343 | 85.9222 | 92.4462 | 98.9519 | 105.4708
| OrangevilleWind2050RCP4.5 | Orangeville | Wind | RCP4.5 | 2050 | 79.7963 | 85.9946 | 92.5318 | 99.0484 | 105.5806
| OrangevilleWind2055RCP4.5 | Orangeville | Wind | RCP4.5 | 2055 | 79.8503 | 86.0528 | 92.5943 | 99.1153 | 105.6519
| OrangevilleWind2060RCP4.5 | Orangeville | Wind | RCP4.5 | 2060 | 79.9043 | 86.111 | 92.6569 | 99.1822 | 105.7232
| OrangevilleWind2065RCP4.5 | Orangeville | Wind | RCP4.5 | 2065 | 79.9583 | 86.1692 | 92.7194 | 99.2492 | 105.7946
| OrangevilleWind2070RCP4.5 | Orangeville | Wind | RCP4.5 | 2070 | 80.0124 | 86.2274 | 92.782 | 99.3161 | 105.8659
| OrangevilleWind2075RCP4.5 | Orangeville | Wind | RCP4.5 | 2075 | 80.0799 | 86.3186 | 92.9047 | 99.4671 | 106.0424
| OrangevilleWind2080RCP4.5 | Orangeville | Wind | RCP4.5 | 2080 | 80.1474 | 86.4099 | 93.0273 | 99.618 | 106.219
| OrangevilleWind2085RCP4.5 | Orangeville | Wind | RCP4.5 | 2085 | 80.2149 | 86.5012 | 93.15 | 99.7689 | 106.3955
| OrangevilleWind2090RCP4.5 | Orangeville | Wind | RCP4.5 | 2090 | 80.2825 | 86.5924 | 93.2727 | 99.9199 | 106.5721
| OrangevilleWind2095RCP4.5 | Orangeville | Wind | RCP4.5 | 2095 | 80.35 | 86.6837 | 93.3953 | 100.0708 | 106.7486
| OrangevilleWind2100RCP4.5 | Orangeville | Wind | RCP4.5 | 2100 | 80.4175 | 86.775 | 93.518 | 100.2218 | 106.9252
| OrangevilleWind2023RCP6.0 | Orangeville | Wind | RCP6.0 | 2023 | 79.6946 | 85.8509 | 92.3312 | 98.8042 | 105.2785
| OrangevilleWind2025RCP6.0 | Orangeville | Wind | RCP6.0 | 2025 | 79.7025 | 85.8652 | 92.3542 | 98.8338 | 105.317
| OrangevilleWind2030RCP6.0 | Orangeville | Wind | RCP6.0 | 2030 | 79.7105 | 85.8794 | 92.3772 | 98.8633 | 105.3555
| OrangevilleWind2035RCP6.0 | Orangeville | Wind | RCP6.0 | 2035 | 79.7184 | 85.8937 | 92.4002 | 98.8928 | 105.3939
| OrangevilleWind2040RCP6.0 | Orangeville | Wind | RCP6.0 | 2040 | 79.7264 | 85.9079 | 92.4232 | 98.9224 | 105.4324
| OrangevilleWind2045RCP6.0 | Orangeville | Wind | RCP6.0 | 2045 | 79.7343 | 85.9222 | 92.4462 | 98.9519 | 105.4708
| OrangevilleWind2050RCP6.0 | Orangeville | Wind | RCP6.0 | 2050 | 79.7963 | 85.9946 | 92.5318 | 99.0484 | 105.5806
| OrangevilleWind2055RCP6.0 | Orangeville | Wind | RCP6.0 | 2055 | 79.8503 | 86.0528 | 92.5943 | 99.1153 | 105.6519
| OrangevilleWind2060RCP6.0 | Orangeville | Wind | RCP6.0 | 2060 | 79.9043 | 86.111 | 92.6569 | 99.1822 | 105.7232
| OrangevilleWind2065RCP6.0 | Orangeville | Wind | RCP6.0 | 2065 | 79.9583 | 86.1692 | 92.7194 | 99.2492 | 105.7946
| OrangevilleWind2070RCP6.0 | Orangeville | Wind | RCP6.0 | 2070 | 80.0124 | 86.2274 | 92.782 | 99.3161 | 105.8659
| OrangevilleWind2075RCP6.0 | Orangeville | Wind | RCP6.0 | 2075 | 80.1136 | 86.3643 | 92.966 | 99.5425 | 106.1307
| OrangevilleWind2080RCP6.0 | Orangeville | Wind | RCP6.0 | 2080 | 80.2149 | 86.5012 | 93.15 | 99.7689 | 106.3955
| OrangevilleWind2085RCP6.0 | Orangeville | Wind | RCP6.0 | 2085 | 80.3162 | 86.6381 | 93.334 | 99.9954 | 106.6603
| OrangevilleWind2090RCP6.0 | Orangeville | Wind | RCP6.0 | 2090 | 80.7962 | 87.2427 | 94.0915 | 100.8879 | 107.6838
| OrangevilleWind2095RCP6.0 | Orangeville | Wind | RCP6.0 | 2095 | 81.1748 | 87.7104 | 94.6649 | 101.554 | 108.4424
| OrangevilleWind2100RCP6.0 | Orangeville | Wind | RCP6.0 | 2100 | 81.5535 | 88.1781 | 95.2384 | 102.2201 | 109.2011
| OrangevilleWind2023RCP8.5 | Orangeville | Wind | RCP8.5 | 2023 | 79.6946 | 85.8509 | 92.3312 | 98.8042 | 105.2785
| OrangevilleWind2025RCP8.5 | Orangeville | Wind | RCP8.5 | 2025 | 79.7105 | 85.8794 | 92.3772 | 98.8633 | 105.3555
| OrangevilleWind2030RCP8.5 | Orangeville | Wind | RCP8.5 | 2030 | 79.7264 | 85.9079 | 92.4232 | 98.9224 | 105.4324
| OrangevilleWind2035RCP8.5 | Orangeville | Wind | RCP8.5 | 2035 | 79.7423 | 85.9365 | 92.4692 | 98.9814 | 105.5093
| OrangevilleWind2040RCP8.5 | Orangeville | Wind | RCP8.5 | 2040 | 79.8323 | 86.0334 | 92.5735 | 99.093 | 105.6281
| OrangevilleWind2045RCP8.5 | Orangeville | Wind | RCP8.5 | 2045 | 79.9223 | 86.1304 | 92.6777 | 99.2046 | 105.747
| OrangevilleWind2050RCP8.5 | Orangeville | Wind | RCP8.5 | 2050 | 80.1474 | 86.4099 | 93.0273 | 99.618 | 106.219
| OrangevilleWind2055RCP8.5 | Orangeville | Wind | RCP8.5 | 2055 | 80.2825 | 86.5924 | 93.2727 | 99.9199 | 106.5721
| OrangevilleWind2060RCP8.5 | Orangeville | Wind | RCP8.5 | 2060 | 80.7962 | 87.2427 | 94.0915 | 100.8879 | 107.6838
| OrangevilleWind2065RCP8.5 | Orangeville | Wind | RCP8.5 | 2065 | 81.1748 | 87.7104 | 94.6649 | 101.554 | 108.4424
| OrangevilleWind2070RCP8.5 | Orangeville | Wind | RCP8.5 | 2070 | 81.7627 | 88.4462 | 95.5819 | 102.6204 | 109.666
| OrangevilleWind2075RCP8.5 | Orangeville | Wind | RCP8.5 | 2075 | 81.9719 | 88.7143 | 95.9253 | 103.0207 | 110.131
| OrangevilleWind2080RCP8.5 | Orangeville | Wind | RCP8.5 | 2080 | 82.1811 | 88.9824 | 96.2688 | 103.4211 | 110.596
| OrangevilleWind2085RCP8.5 | Orangeville | Wind | RCP8.5 | 2085 | 82.3558 | 89.1963 | 96.531 | 103.7262 | 110.9473
| OrangevilleWind2090RCP8.5 | Orangeville | Wind | RCP8.5 | 2090 | 82.5306 | 89.4102 | 96.7932 | 104.0314 | 111.2987
| OrangevilleWind2095RCP8.5 | Orangeville | Wind | RCP8.5 | 2095 | 82.5306 | 89.4102 | 96.7932 | 104.0314 | 111.2987
| OrangevilleWind2100RCP8.5 | Orangeville | Wind | RCP8.5 | 2100 | 82.5306 | 89.4102 | 96.7932 | 104.0314 | 111.2987
| OrilliaIce Accretion2023RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2023 | 15.0178 | 17.9131 | 21.582 | 24.3877 | 27.221
| OrilliaIce Accretion2025RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2025 | 14.9999 | 17.9009 | 21.5747 | 24.3877 | 27.221
| OrilliaIce Accretion2030RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2030 | 14.982 | 17.8887 | 21.5673 | 24.3877 | 27.221
| OrilliaIce Accretion2035RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2035 | 14.9642 | 17.8765 | 21.56 | 24.3877 | 27.221
| OrilliaIce Accretion2040RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2040 | 14.9463 | 17.8644 | 21.5527 | 24.3877 | 27.221
| OrilliaIce Accretion2045RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2045 | 14.9285 | 17.8522 | 21.5453 | 24.3877 | 27.221
| OrilliaIce Accretion2050RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2050 | 14.9075 | 17.851 | 21.5732 | 24.4324 | 27.282
| OrilliaIce Accretion2055RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2055 | 14.9045 | 17.8619 | 21.6084 | 24.4772 | 27.343
| OrilliaIce Accretion2060RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2060 | 14.9014 | 17.8729 | 21.6436 | 24.5219 | 27.404
| OrilliaIce Accretion2065RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2065 | 14.8983 | 17.8838 | 21.6788 | 24.5667 | 27.465
| OrilliaIce Accretion2070RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2070 | 14.8953 | 17.8948 | 21.714 | 24.6114 | 27.526
| OrilliaIce Accretion2075RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2075 | 14.9387 | 17.9648 | 21.813 | 24.7316 | 27.6692
| OrilliaIce Accretion2080RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2080 | 14.982 | 18.0348 | 21.912 | 24.8517 | 27.8124
| OrilliaIce Accretion2085RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2085 | 15.0254 | 18.1048 | 22.011 | 24.9719 | 27.9556
| OrilliaIce Accretion2090RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2090 | 15.0688 | 18.1748 | 22.11 | 25.092 | 28.0988
| OrilliaIce Accretion2095RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2095 | 15.1122 | 18.2448 | 22.209 | 25.2122 | 28.2421
| OrilliaIce Accretion2100RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2100 | 15.1555 | 18.3148 | 22.308 | 25.3323 | 28.3853
| OrilliaIce Accretion2023RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2023 | 15.0178 | 17.9131 | 21.582 | 24.3877 | 27.221
| OrilliaIce Accretion2025RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2025 | 14.9999 | 17.9009 | 21.5747 | 24.3877 | 27.221
| OrilliaIce Accretion2030RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2030 | 14.982 | 17.8887 | 21.5673 | 24.3877 | 27.221
| OrilliaIce Accretion2035RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2035 | 14.9642 | 17.8765 | 21.56 | 24.3877 | 27.221
| OrilliaIce Accretion2040RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2040 | 14.9463 | 17.8644 | 21.5527 | 24.3877 | 27.221
| OrilliaIce Accretion2045RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2045 | 14.9285 | 17.8522 | 21.5453 | 24.3877 | 27.221
| OrilliaIce Accretion2050RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2050 | 14.9075 | 17.851 | 21.5732 | 24.4324 | 27.282
| OrilliaIce Accretion2055RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2055 | 14.9045 | 17.8619 | 21.6084 | 24.4772 | 27.343
| OrilliaIce Accretion2060RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2060 | 14.9014 | 17.8729 | 21.6436 | 24.5219 | 27.404
| OrilliaIce Accretion2065RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2065 | 14.8983 | 17.8838 | 21.6788 | 24.5667 | 27.465
| OrilliaIce Accretion2070RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2070 | 14.8953 | 17.8948 | 21.714 | 24.6114 | 27.526
| OrilliaIce Accretion2075RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2075 | 14.9603 | 17.9998 | 21.8625 | 24.7916 | 27.7408
| OrilliaIce Accretion2080RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2080 | 15.0254 | 18.1048 | 22.011 | 24.9719 | 27.9556
| OrilliaIce Accretion2085RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2085 | 15.0905 | 18.2098 | 22.1595 | 25.1521 | 28.1704
| OrilliaIce Accretion2090RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2090 | 15.13 | 18.327 | 22.3667 | 25.4318 | 28.5146
| OrilliaIce Accretion2095RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2095 | 15.1045 | 18.3391 | 22.4253 | 25.5312 | 28.644
| OrilliaIce Accretion2100RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2100 | 15.079 | 18.3513 | 22.484 | 25.6307 | 28.7734
| OrilliaIce Accretion2023RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2023 | 15.0178 | 17.9131 | 21.582 | 24.3877 | 27.221
| OrilliaIce Accretion2025RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2025 | 14.982 | 17.8887 | 21.5673 | 24.3877 | 27.221
| OrilliaIce Accretion2030RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2030 | 14.9463 | 17.8644 | 21.5527 | 24.3877 | 27.221
| OrilliaIce Accretion2035RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2035 | 14.9106 | 17.84 | 21.538 | 24.3877 | 27.221
| OrilliaIce Accretion2040RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2040 | 14.9055 | 17.8583 | 21.5967 | 24.4622 | 27.3227
| OrilliaIce Accretion2045RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2045 | 14.9004 | 17.8765 | 21.6553 | 24.5368 | 27.4243
| OrilliaIce Accretion2050RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2050 | 14.982 | 18.0348 | 21.912 | 24.8517 | 27.8124
| OrilliaIce Accretion2055RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2055 | 15.0688 | 18.1748 | 22.11 | 25.092 | 28.0988
| OrilliaIce Accretion2060RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2060 | 15.13 | 18.327 | 22.3667 | 25.4318 | 28.5146
| OrilliaIce Accretion2065RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2065 | 15.1045 | 18.3391 | 22.4253 | 25.5312 | 28.644
| OrilliaIce Accretion2070RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2070 | 14.8034 | 18.0591 | 22.1687 | 25.2909 | 28.413
| OrilliaIce Accretion2075RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2075 | 14.5279 | 17.767 | 21.8533 | 24.9512 | 28.0526
| OrilliaIce Accretion2080RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2080 | 14.2523 | 17.4748 | 21.538 | 24.6114 | 27.6923
| OrilliaIce Accretion2085RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2085 | 13.6782 | 16.8266 | 20.79 | 23.791 | 26.7914
| OrilliaIce Accretion2090RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2090 | 13.1042 | 16.1784 | 20.042 | 22.9706 | 25.8905
| OrilliaIce Accretion2095RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2095 | 13.1042 | 16.1784 | 20.042 | 22.9706 | 25.8905
| OrilliaIce Accretion2100RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2100 | 13.1042 | 16.1784 | 20.042 | 22.9706 | 25.8905
| OrilliaWind2023RCP4.5 | Orillia | Wind | RCP4.5 | 2023 | 76.4728 | 82.3965 | 88.6424 | 94.8756 | 101.1125
| OrilliaWind2025RCP4.5 | Orillia | Wind | RCP4.5 | 2025 | 76.5513 | 82.4906 | 88.7539 | 95.0027 | 101.2546
| OrilliaWind2030RCP4.5 | Orillia | Wind | RCP4.5 | 2030 | 76.6298 | 82.5847 | 88.8653 | 95.1298 | 101.3968
| OrilliaWind2035RCP4.5 | Orillia | Wind | RCP4.5 | 2035 | 76.7083 | 82.6789 | 88.9768 | 95.257 | 101.5389
| OrilliaWind2040RCP4.5 | Orillia | Wind | RCP4.5 | 2040 | 76.7868 | 82.773 | 89.0883 | 95.3841 | 101.681
| OrilliaWind2045RCP4.5 | Orillia | Wind | RCP4.5 | 2045 | 76.8654 | 82.8671 | 89.1997 | 95.5112 | 101.8231
| OrilliaWind2050RCP4.5 | Orillia | Wind | RCP4.5 | 2050 | 77.0533 | 83.0922 | 89.4696 | 95.821 | 102.1739
| OrilliaWind2055RCP4.5 | Orillia | Wind | RCP4.5 | 2055 | 77.1627 | 83.2231 | 89.628 | 96.0037 | 102.3826
| OrilliaWind2060RCP4.5 | Orillia | Wind | RCP4.5 | 2060 | 77.2721 | 83.354 | 89.7864 | 96.1863 | 102.5912
| OrilliaWind2065RCP4.5 | Orillia | Wind | RCP4.5 | 2065 | 77.3816 | 83.485 | 89.9448 | 96.369 | 102.7999
| OrilliaWind2070RCP4.5 | Orillia | Wind | RCP4.5 | 2070 | 77.491 | 83.6159 | 90.1032 | 96.5517 | 103.0086
| OrilliaWind2075RCP4.5 | Orillia | Wind | RCP4.5 | 2075 | 77.5252 | 83.665 | 90.1721 | 96.6364 | 103.1089
| OrilliaWind2080RCP4.5 | Orillia | Wind | RCP4.5 | 2080 | 77.5594 | 83.7141 | 90.2411 | 96.7212 | 103.2092
| OrilliaWind2085RCP4.5 | Orillia | Wind | RCP4.5 | 2085 | 77.5936 | 83.7632 | 90.31 | 96.8059 | 103.3095
| OrilliaWind2090RCP4.5 | Orillia | Wind | RCP4.5 | 2090 | 77.6278 | 83.8123 | 90.3789 | 96.8906 | 103.4099
| OrilliaWind2095RCP4.5 | Orillia | Wind | RCP4.5 | 2095 | 77.662 | 83.8614 | 90.4479 | 96.9754 | 103.5102
| OrilliaWind2100RCP4.5 | Orillia | Wind | RCP4.5 | 2100 | 77.6961 | 83.9106 | 90.5168 | 97.0601 | 103.6105
| OrilliaWind2023RCP6.0 | Orillia | Wind | RCP6.0 | 2023 | 76.4728 | 82.3965 | 88.6424 | 94.8756 | 101.1125
| OrilliaWind2025RCP6.0 | Orillia | Wind | RCP6.0 | 2025 | 76.5513 | 82.4906 | 88.7539 | 95.0027 | 101.2546
| OrilliaWind2030RCP6.0 | Orillia | Wind | RCP6.0 | 2030 | 76.6298 | 82.5847 | 88.8653 | 95.1298 | 101.3968
| OrilliaWind2035RCP6.0 | Orillia | Wind | RCP6.0 | 2035 | 76.7083 | 82.6789 | 88.9768 | 95.257 | 101.5389
| OrilliaWind2040RCP6.0 | Orillia | Wind | RCP6.0 | 2040 | 76.7868 | 82.773 | 89.0883 | 95.3841 | 101.681
| OrilliaWind2045RCP6.0 | Orillia | Wind | RCP6.0 | 2045 | 76.8654 | 82.8671 | 89.1997 | 95.5112 | 101.8231
| OrilliaWind2050RCP6.0 | Orillia | Wind | RCP6.0 | 2050 | 77.0533 | 83.0922 | 89.4696 | 95.821 | 102.1739
| OrilliaWind2055RCP6.0 | Orillia | Wind | RCP6.0 | 2055 | 77.1627 | 83.2231 | 89.628 | 96.0037 | 102.3826
| OrilliaWind2060RCP6.0 | Orillia | Wind | RCP6.0 | 2060 | 77.2721 | 83.354 | 89.7864 | 96.1863 | 102.5912
| OrilliaWind2065RCP6.0 | Orillia | Wind | RCP6.0 | 2065 | 77.3816 | 83.485 | 89.9448 | 96.369 | 102.7999
| OrilliaWind2070RCP6.0 | Orillia | Wind | RCP6.0 | 2070 | 77.491 | 83.6159 | 90.1032 | 96.5517 | 103.0086
| OrilliaWind2075RCP6.0 | Orillia | Wind | RCP6.0 | 2075 | 77.5423 | 83.6896 | 90.2066 | 96.6788 | 103.1591
| OrilliaWind2080RCP6.0 | Orillia | Wind | RCP6.0 | 2080 | 77.5936 | 83.7632 | 90.31 | 96.8059 | 103.3095
| OrilliaWind2085RCP6.0 | Orillia | Wind | RCP6.0 | 2085 | 77.6449 | 83.8369 | 90.4134 | 96.933 | 103.46
| OrilliaWind2090RCP6.0 | Orillia | Wind | RCP6.0 | 2090 | 77.8101 | 84.0633 | 90.7133 | 97.2955 | 103.8847
| OrilliaWind2095RCP6.0 | Orillia | Wind | RCP6.0 | 2095 | 77.9241 | 84.2161 | 90.9099 | 97.5309 | 104.1589
| OrilliaWind2100RCP6.0 | Orillia | Wind | RCP6.0 | 2100 | 78.0381 | 84.3689 | 91.1064 | 97.7663 | 104.4331
| OrilliaWind2023RCP8.5 | Orillia | Wind | RCP8.5 | 2023 | 76.4728 | 82.3965 | 88.6424 | 94.8756 | 101.1125
| OrilliaWind2025RCP8.5 | Orillia | Wind | RCP8.5 | 2025 | 76.6298 | 82.5847 | 88.8653 | 95.1298 | 101.3968
| OrilliaWind2030RCP8.5 | Orillia | Wind | RCP8.5 | 2030 | 76.7868 | 82.773 | 89.0883 | 95.3841 | 101.681
| OrilliaWind2035RCP8.5 | Orillia | Wind | RCP8.5 | 2035 | 76.9439 | 82.9612 | 89.3112 | 95.6383 | 101.9652
| OrilliaWind2040RCP8.5 | Orillia | Wind | RCP8.5 | 2040 | 77.1263 | 83.1794 | 89.5752 | 95.9428 | 102.313
| OrilliaWind2045RCP8.5 | Orillia | Wind | RCP8.5 | 2045 | 77.3086 | 83.3977 | 89.8392 | 96.2472 | 102.6608
| OrilliaWind2050RCP8.5 | Orillia | Wind | RCP8.5 | 2050 | 77.5594 | 83.7141 | 90.2411 | 96.7212 | 103.2092
| OrilliaWind2055RCP8.5 | Orillia | Wind | RCP8.5 | 2055 | 77.6278 | 83.8123 | 90.3789 | 96.8906 | 103.4099
| OrilliaWind2060RCP8.5 | Orillia | Wind | RCP8.5 | 2060 | 77.8101 | 84.0633 | 90.7133 | 97.2955 | 103.8847
| OrilliaWind2065RCP8.5 | Orillia | Wind | RCP8.5 | 2065 | 77.9241 | 84.2161 | 90.9099 | 97.5309 | 104.1589
| OrilliaWind2070RCP8.5 | Orillia | Wind | RCP8.5 | 2070 | 78.0254 | 84.3634 | 91.1123 | 97.7789 | 104.4565
| OrilliaWind2075RCP8.5 | Orillia | Wind | RCP8.5 | 2075 | 78.0128 | 84.3579 | 91.1181 | 97.7914 | 104.4799
| OrilliaWind2080RCP8.5 | Orillia | Wind | RCP8.5 | 2080 | 78.0001 | 84.3525 | 91.124 | 97.804 | 104.5033
| OrilliaWind2085RCP8.5 | Orillia | Wind | RCP8.5 | 2085 | 78.0989 | 84.4793 | 91.2912 | 98.0017 | 104.7341
| OrilliaWind2090RCP8.5 | Orillia | Wind | RCP8.5 | 2090 | 78.1977 | 84.6062 | 91.4584 | 98.1995 | 104.9648
| OrilliaWind2095RCP8.5 | Orillia | Wind | RCP8.5 | 2095 | 78.1977 | 84.6062 | 91.4584 | 98.1995 | 104.9648
| OrilliaWind2100RCP8.5 | Orillia | Wind | RCP8.5 | 2100 | 78.1977 | 84.6062 | 91.4584 | 98.1995 | 104.9648
| OshawaIce Accretion2023RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| OshawaIce Accretion2025RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| OshawaIce Accretion2030RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| OshawaIce Accretion2035RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| OshawaIce Accretion2040RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| OshawaIce Accretion2045RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| OshawaIce Accretion2050RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| OshawaIce Accretion2055RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| OshawaIce Accretion2060RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| OshawaIce Accretion2065RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| OshawaIce Accretion2070RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| OshawaIce Accretion2075RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
| OshawaIce Accretion2080RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| OshawaIce Accretion2085RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| OshawaIce Accretion2090RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| OshawaIce Accretion2095RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
| OshawaIce Accretion2100RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
| OshawaIce Accretion2023RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| OshawaIce Accretion2025RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| OshawaIce Accretion2030RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| OshawaIce Accretion2035RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| OshawaIce Accretion2040RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| OshawaIce Accretion2045RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| OshawaIce Accretion2050RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| OshawaIce Accretion2055RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| OshawaIce Accretion2060RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| OshawaIce Accretion2065RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| OshawaIce Accretion2070RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| OshawaIce Accretion2075RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
| OshawaIce Accretion2080RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| OshawaIce Accretion2085RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
| OshawaIce Accretion2090RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| OshawaIce Accretion2095RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| OshawaIce Accretion2100RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
| OshawaIce Accretion2023RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| OshawaIce Accretion2025RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| OshawaIce Accretion2030RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| OshawaIce Accretion2035RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
| OshawaIce Accretion2040RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
| OshawaIce Accretion2045RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
| OshawaIce Accretion2050RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| OshawaIce Accretion2055RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| OshawaIce Accretion2060RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| OshawaIce Accretion2065RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| OshawaIce Accretion2070RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
| OshawaIce Accretion2075RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
| OshawaIce Accretion2080RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
| OshawaIce Accretion2085RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
| OshawaIce Accretion2090RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| OshawaIce Accretion2095RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| OshawaIce Accretion2100RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| OshawaWind2023RCP4.5 | Oshawa | Wind | RCP4.5 | 2023 | 84.8244 | 91.3223 | 98.1568 | 104.9963 | 111.8317
| OshawaWind2025RCP4.5 | Oshawa | Wind | RCP4.5 | 2025 | 84.8399 | 91.3557 | 98.2107 | 105.068 | 111.9211
| OshawaWind2030RCP4.5 | Oshawa | Wind | RCP4.5 | 2030 | 84.8554 | 91.3891 | 98.2646 | 105.1396 | 112.0105
| OshawaWind2035RCP4.5 | Oshawa | Wind | RCP4.5 | 2035 | 84.8709 | 91.4225 | 98.3185 | 105.2113 | 112.0998
| OshawaWind2040RCP4.5 | Oshawa | Wind | RCP4.5 | 2040 | 84.8864 | 91.456 | 98.3724 | 105.2829 | 112.1892
| OshawaWind2045RCP4.5 | Oshawa | Wind | RCP4.5 | 2045 | 84.9019 | 91.4894 | 98.4263 | 105.3546 | 112.2786
| OshawaWind2050RCP4.5 | Oshawa | Wind | RCP4.5 | 2050 | 85.0004 | 91.6267 | 98.6115 | 105.5793 | 112.5467
| OshawaWind2055RCP4.5 | Oshawa | Wind | RCP4.5 | 2055 | 85.0833 | 91.7306 | 98.7428 | 105.7324 | 112.7255
| OshawaWind2060RCP4.5 | Oshawa | Wind | RCP4.5 | 2060 | 85.1662 | 91.8345 | 98.8742 | 105.8855 | 112.9042
| OshawaWind2065RCP4.5 | Oshawa | Wind | RCP4.5 | 2065 | 85.2492 | 91.9384 | 99.0055 | 106.0386 | 113.083
| OshawaWind2070RCP4.5 | Oshawa | Wind | RCP4.5 | 2070 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2617
| OshawaWind2075RCP4.5 | Oshawa | Wind | RCP4.5 | 2075 | 85.476 | 92.2276 | 99.3736 | 106.4731 | 113.5876
| OshawaWind2080RCP4.5 | Oshawa | Wind | RCP4.5 | 2080 | 85.6198 | 92.4129 | 99.6105 | 106.7545 | 113.9134
| OshawaWind2085RCP4.5 | Oshawa | Wind | RCP4.5 | 2085 | 85.7637 | 92.5982 | 99.8473 | 107.0358 | 114.2393
| OshawaWind2090RCP4.5 | Oshawa | Wind | RCP4.5 | 2090 | 85.9075 | 92.7836 | 100.0841 | 107.3172 | 114.5651
| OshawaWind2095RCP4.5 | Oshawa | Wind | RCP4.5 | 2095 | 86.0514 | 92.9689 | 100.321 | 107.5986 | 114.891
| OshawaWind2100RCP4.5 | Oshawa | Wind | RCP4.5 | 2100 | 86.1952 | 93.1542 | 100.5578 | 107.88 | 115.2168
| OshawaWind2023RCP6.0 | Oshawa | Wind | RCP6.0 | 2023 | 84.8244 | 91.3223 | 98.1568 | 104.9963 | 111.8317
| OshawaWind2025RCP6.0 | Oshawa | Wind | RCP6.0 | 2025 | 84.8399 | 91.3557 | 98.2107 | 105.068 | 111.9211
| OshawaWind2030RCP6.0 | Oshawa | Wind | RCP6.0 | 2030 | 84.8554 | 91.3891 | 98.2646 | 105.1396 | 112.0105
| OshawaWind2035RCP6.0 | Oshawa | Wind | RCP6.0 | 2035 | 84.8709 | 91.4225 | 98.3185 | 105.2113 | 112.0998
| OshawaWind2040RCP6.0 | Oshawa | Wind | RCP6.0 | 2040 | 84.8864 | 91.456 | 98.3724 | 105.2829 | 112.1892
| OshawaWind2045RCP6.0 | Oshawa | Wind | RCP6.0 | 2045 | 84.9019 | 91.4894 | 98.4263 | 105.3546 | 112.2786
| OshawaWind2050RCP6.0 | Oshawa | Wind | RCP6.0 | 2050 | 85.0004 | 91.6267 | 98.6115 | 105.5793 | 112.5467
| OshawaWind2055RCP6.0 | Oshawa | Wind | RCP6.0 | 2055 | 85.0833 | 91.7306 | 98.7428 | 105.7324 | 112.7255
| OshawaWind2060RCP6.0 | Oshawa | Wind | RCP6.0 | 2060 | 85.1662 | 91.8345 | 98.8742 | 105.8855 | 112.9042
| OshawaWind2065RCP6.0 | Oshawa | Wind | RCP6.0 | 2065 | 85.2492 | 91.9384 | 99.0055 | 106.0386 | 113.083
| OshawaWind2070RCP6.0 | Oshawa | Wind | RCP6.0 | 2070 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2617
| OshawaWind2075RCP6.0 | Oshawa | Wind | RCP6.0 | 2075 | 85.5479 | 92.3203 | 99.4921 | 106.6138 | 113.7505
| OshawaWind2080RCP6.0 | Oshawa | Wind | RCP6.0 | 2080 | 85.7637 | 92.5982 | 99.8473 | 107.0358 | 114.2393
| OshawaWind2085RCP6.0 | Oshawa | Wind | RCP6.0 | 2085 | 85.9794 | 92.8762 | 100.2026 | 107.4579 | 114.7281
| OshawaWind2090RCP6.0 | Oshawa | Wind | RCP6.0 | 2090 | 86.6409 | 93.701 | 101.234 | 108.6664 | 116.118
| OshawaWind2095RCP6.0 | Oshawa | Wind | RCP6.0 | 2095 | 87.0866 | 94.2479 | 101.9102 | 109.4529 | 117.0193
| OshawaWind2100RCP6.0 | Oshawa | Wind | RCP6.0 | 2100 | 87.5322 | 94.7947 | 102.5864 | 110.2393 | 117.9205
| OshawaWind2023RCP8.5 | Oshawa | Wind | RCP8.5 | 2023 | 84.8244 | 91.3223 | 98.1568 | 104.9963 | 111.8317
| OshawaWind2025RCP8.5 | Oshawa | Wind | RCP8.5 | 2025 | 84.8554 | 91.3891 | 98.2646 | 105.1396 | 112.0105
| OshawaWind2030RCP8.5 | Oshawa | Wind | RCP8.5 | 2030 | 84.8864 | 91.456 | 98.3724 | 105.2829 | 112.1892
| OshawaWind2035RCP8.5 | Oshawa | Wind | RCP8.5 | 2035 | 84.9175 | 91.5228 | 98.4802 | 105.4262 | 112.368
| OshawaWind2040RCP8.5 | Oshawa | Wind | RCP8.5 | 2040 | 85.0557 | 91.696 | 98.6991 | 105.6814 | 112.6659
| OshawaWind2045RCP8.5 | Oshawa | Wind | RCP8.5 | 2045 | 85.1939 | 91.8691 | 98.9179 | 105.9366 | 112.9638
| OshawaWind2050RCP8.5 | Oshawa | Wind | RCP8.5 | 2050 | 85.6198 | 92.4129 | 99.6105 | 106.7545 | 113.9134
| OshawaWind2055RCP8.5 | Oshawa | Wind | RCP8.5 | 2055 | 85.9075 | 92.7836 | 100.0841 | 107.3172 | 114.5651
| OshawaWind2060RCP8.5 | Oshawa | Wind | RCP8.5 | 2060 | 86.6409 | 93.701 | 101.234 | 108.6664 | 116.118
| OshawaWind2065RCP8.5 | Oshawa | Wind | RCP8.5 | 2065 | 87.0866 | 94.2479 | 101.9102 | 109.4529 | 117.0193
| OshawaWind2070RCP8.5 | Oshawa | Wind | RCP8.5 | 2070 | 87.6648 | 94.974 | 102.8249 | 110.5329 | 118.2631
| OshawaWind2075RCP8.5 | Oshawa | Wind | RCP8.5 | 2075 | 87.7974 | 95.1532 | 103.0633 | 110.8265 | 118.6057
| OshawaWind2080RCP8.5 | Oshawa | Wind | RCP8.5 | 2080 | 87.93 | 95.3324 | 103.3018 | 111.1201 | 118.9483
| OshawaWind2085RCP8.5 | Oshawa | Wind | RCP8.5 | 2085 | 88.2135 | 95.7335 | 103.8506 | 111.7912 | 119.7471
| OshawaWind2090RCP8.5 | Oshawa | Wind | RCP8.5 | 2090 | 88.4969 | 96.1345 | 104.3994 | 112.4624 | 120.5459
| OshawaWind2095RCP8.5 | Oshawa | Wind | RCP8.5 | 2095 | 88.4969 | 96.1345 | 104.3994 | 112.4624 | 120.5459
| OshawaWind2100RCP8.5 | Oshawa | Wind | RCP8.5 | 2100 | 88.4969 | 96.1345 | 104.3994 | 112.4624 | 120.5459
| Ottawa (Barrhaven)Ice Accretion2023RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
| Ottawa (Barrhaven)Ice Accretion2025RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
| Ottawa (Barrhaven)Ice Accretion2030RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
| Ottawa (Barrhaven)Ice Accretion2035RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
| Ottawa (Barrhaven)Ice Accretion2040RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
| Ottawa (Barrhaven)Ice Accretion2045RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
| Ottawa (Barrhaven)Ice Accretion2050RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
| Ottawa (Barrhaven)Ice Accretion2055RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
| Ottawa (Barrhaven)Ice Accretion2060RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
| Ottawa (Barrhaven)Ice Accretion2065RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
| Ottawa (Barrhaven)Ice Accretion2070RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
| Ottawa (Barrhaven)Ice Accretion2075RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2075 | 20.6423 | 24.7215 | 29.87 | 33.8039 | 37.7496
| Ottawa (Barrhaven)Ice Accretion2080RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2080 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
| Ottawa (Barrhaven)Ice Accretion2085RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2085 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
| Ottawa (Barrhaven)Ice Accretion2090RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2090 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
| Ottawa (Barrhaven)Ice Accretion2095RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2095 | 20.9624 | 25.2029 | 30.55 | 34.6401 | 38.7576
| Ottawa (Barrhaven)Ice Accretion2100RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2100 | 21.0424 | 25.3233 | 30.72 | 34.8492 | 39.0096
| Ottawa (Barrhaven)Ice Accretion2023RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
| Ottawa (Barrhaven)Ice Accretion2025RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
| Ottawa (Barrhaven)Ice Accretion2030RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
| Ottawa (Barrhaven)Ice Accretion2035RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
| Ottawa (Barrhaven)Ice Accretion2040RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
| Ottawa (Barrhaven)Ice Accretion2045RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
| Ottawa (Barrhaven)Ice Accretion2050RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
| Ottawa (Barrhaven)Ice Accretion2055RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
| Ottawa (Barrhaven)Ice Accretion2060RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
| Ottawa (Barrhaven)Ice Accretion2065RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
| Ottawa (Barrhaven)Ice Accretion2070RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
| Ottawa (Barrhaven)Ice Accretion2075RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2075 | 20.6823 | 24.7817 | 29.955 | 33.9085 | 37.8756
| Ottawa (Barrhaven)Ice Accretion2080RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2080 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
| Ottawa (Barrhaven)Ice Accretion2085RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2085 | 20.9224 | 25.1428 | 30.465 | 34.5356 | 38.6316
| Ottawa (Barrhaven)Ice Accretion2090RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2090 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
| Ottawa (Barrhaven)Ice Accretion2095RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2095 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
| Ottawa (Barrhaven)Ice Accretion2100RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2100 | 21.439 | 25.9458 | 31.65 | 36.0018 | 40.3326
| Ottawa (Barrhaven)Ice Accretion2023RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
| Ottawa (Barrhaven)Ice Accretion2025RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2025 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
| Ottawa (Barrhaven)Ice Accretion2030RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2030 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
| Ottawa (Barrhaven)Ice Accretion2035RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2035 | 20.2074 | 24.0285 | 28.86 | 32.5779 | 36.288
| Ottawa (Barrhaven)Ice Accretion2040RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2040 | 20.3257 | 24.2194 | 29.14 | 32.9169 | 36.6912
| Ottawa (Barrhaven)Ice Accretion2045RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2045 | 20.444 | 24.4103 | 29.42 | 33.2559 | 37.0944
| Ottawa (Barrhaven)Ice Accretion2050RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2050 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
| Ottawa (Barrhaven)Ice Accretion2055RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2055 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
| Ottawa (Barrhaven)Ice Accretion2060RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2060 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
| Ottawa (Barrhaven)Ice Accretion2065RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2065 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
| Ottawa (Barrhaven)Ice Accretion2070RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2070 | 21.2372 | 25.7383 | 31.44 | 35.7871 | 40.1184
| Ottawa (Barrhaven)Ice Accretion2075RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2075 | 21.0354 | 25.5308 | 31.23 | 35.5724 | 39.9042
| Ottawa (Barrhaven)Ice Accretion2080RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2080 | 20.8336 | 25.3233 | 31.02 | 35.3577 | 39.69
| Ottawa (Barrhaven)Ice Accretion2085RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2085 | 20.0926 | 24.5016 | 30.09 | 34.3237 | 38.5749
| Ottawa (Barrhaven)Ice Accretion2090RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2090 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
| Ottawa (Barrhaven)Ice Accretion2095RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2095 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
| Ottawa (Barrhaven)Ice Accretion2100RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2100 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
| Ottawa (Barrhaven)Wind2023RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2023 | 77.8688 | 83.9427 | 90.351 | 96.743 | 103.1335
| Ottawa (Barrhaven)Wind2025RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2025 | 77.8986 | 83.9776 | 90.3915 | 96.7895 | 103.1848
| Ottawa (Barrhaven)Wind2030RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2030 | 77.9284 | 84.0125 | 90.432 | 96.8361 | 103.2361
| Ottawa (Barrhaven)Wind2035RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2035 | 77.9582 | 84.0474 | 90.4725 | 96.8826 | 103.2874
| Ottawa (Barrhaven)Wind2040RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2040 | 77.988 | 84.0822 | 90.513 | 96.9292 | 103.3387
| Ottawa (Barrhaven)Wind2045RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2045 | 78.0178 | 84.1171 | 90.5535 | 96.9757 | 103.39
| Ottawa (Barrhaven)Wind2050RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2050 | 77.9745 | 84.0515 | 90.4626 | 96.8624 | 103.2546
| Ottawa (Barrhaven)Wind2055RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2055 | 77.9015 | 83.9511 | 90.3312 | 96.7025 | 103.0679
| Ottawa (Barrhaven)Wind2060RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2060 | 77.8284 | 83.8507 | 90.1998 | 96.5427 | 102.8811
| Ottawa (Barrhaven)Wind2065RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2065 | 77.7554 | 83.7502 | 90.0684 | 96.3828 | 102.6944
| Ottawa (Barrhaven)Wind2070RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2070 | 77.6823 | 83.6498 | 89.937 | 96.223 | 102.5077
| Ottawa (Barrhaven)Wind2075RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2075 | 77.7018 | 83.6819 | 89.9835 | 96.2823 | 102.5812
| Ottawa (Barrhaven)Wind2080RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2080 | 77.7212 | 83.7139 | 90.03 | 96.3417 | 102.6547
| Ottawa (Barrhaven)Wind2085RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2085 | 77.7406 | 83.746 | 90.0765 | 96.4011 | 102.7283
| Ottawa (Barrhaven)Wind2090RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2090 | 77.76 | 83.7781 | 90.123 | 96.4605 | 102.8018
| Ottawa (Barrhaven)Wind2095RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2095 | 77.7795 | 83.8102 | 90.1695 | 96.5199 | 102.8753
| Ottawa (Barrhaven)Wind2100RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2100 | 77.7989 | 83.8423 | 90.216 | 96.5793 | 102.9488
| Ottawa (Barrhaven)Wind2023RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2023 | 77.8688 | 83.9427 | 90.351 | 96.743 | 103.1335
| Ottawa (Barrhaven)Wind2025RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2025 | 77.8986 | 83.9776 | 90.3915 | 96.7895 | 103.1848
| Ottawa (Barrhaven)Wind2030RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2030 | 77.9284 | 84.0125 | 90.432 | 96.8361 | 103.2361
| Ottawa (Barrhaven)Wind2035RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2035 | 77.9582 | 84.0474 | 90.4725 | 96.8826 | 103.2874
| Ottawa (Barrhaven)Wind2040RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2040 | 77.988 | 84.0822 | 90.513 | 96.9292 | 103.3387
| Ottawa (Barrhaven)Wind2045RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2045 | 78.0178 | 84.1171 | 90.5535 | 96.9757 | 103.39
| Ottawa (Barrhaven)Wind2050RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2050 | 77.9745 | 84.0515 | 90.4626 | 96.8624 | 103.2546
| Ottawa (Barrhaven)Wind2055RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2055 | 77.9015 | 83.9511 | 90.3312 | 96.7025 | 103.0679
| Ottawa (Barrhaven)Wind2060RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2060 | 77.8284 | 83.8507 | 90.1998 | 96.5427 | 102.8811
| Ottawa (Barrhaven)Wind2065RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2065 | 77.7554 | 83.7502 | 90.0684 | 96.3828 | 102.6944
| Ottawa (Barrhaven)Wind2070RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2070 | 77.6823 | 83.6498 | 89.937 | 96.223 | 102.5077
| Ottawa (Barrhaven)Wind2075RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2075 | 77.7115 | 83.6979 | 90.0067 | 96.312 | 102.618
| Ottawa (Barrhaven)Wind2080RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2080 | 77.7406 | 83.746 | 90.0765 | 96.4011 | 102.7283
| Ottawa (Barrhaven)Wind2085RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2085 | 77.7698 | 83.7942 | 90.1462 | 96.4902 | 102.8385
| Ottawa (Barrhaven)Wind2090RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2090 | 77.6797 | 83.6916 | 90.03 | 96.361 | 102.6958
| Ottawa (Barrhaven)Wind2095RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2095 | 77.5606 | 83.541 | 89.844 | 96.1427 | 102.4427
| Ottawa (Barrhaven)Wind2100RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2100 | 77.4414 | 83.3903 | 89.658 | 95.9244 | 102.1896
| Ottawa (Barrhaven)Wind2023RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2023 | 77.8688 | 83.9427 | 90.351 | 96.743 | 103.1335
| Ottawa (Barrhaven)Wind2025RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2025 | 77.9284 | 84.0125 | 90.432 | 96.8361 | 103.2361
| Ottawa (Barrhaven)Wind2030RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2030 | 77.988 | 84.0822 | 90.513 | 96.9292 | 103.3387
| Ottawa (Barrhaven)Wind2035RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2035 | 78.0476 | 84.152 | 90.594 | 97.0223 | 103.4413
| Ottawa (Barrhaven)Wind2040RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2040 | 77.9258 | 83.9846 | 90.375 | 96.7558 | 103.1301
| Ottawa (Barrhaven)Wind2045RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2045 | 77.8041 | 83.8172 | 90.156 | 96.4894 | 102.8189
| Ottawa (Barrhaven)Wind2050RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2050 | 77.7212 | 83.7139 | 90.03 | 96.3417 | 102.6547
| Ottawa (Barrhaven)Wind2055RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2055 | 77.76 | 83.7781 | 90.123 | 96.4605 | 102.8018
| Ottawa (Barrhaven)Wind2060RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2060 | 77.6797 | 83.6916 | 90.03 | 96.361 | 102.6958
| Ottawa (Barrhaven)Wind2065RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2065 | 77.5606 | 83.541 | 89.844 | 96.1427 | 102.4427
| Ottawa (Barrhaven)Wind2070RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2070 | 77.5165 | 83.4908 | 89.784 | 96.0721 | 102.364
| Ottawa (Barrhaven)Wind2075RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2075 | 77.5917 | 83.5912 | 89.91 | 96.2198 | 102.5384
| Ottawa (Barrhaven)Wind2080RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2080 | 77.6668 | 83.6916 | 90.036 | 96.3674 | 102.7129
| Ottawa (Barrhaven)Wind2085RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2085 | 77.6435 | 83.6498 | 89.9775 | 96.2952 | 102.6205
| Ottawa (Barrhaven)Wind2090RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2090 | 77.6202 | 83.6079 | 89.919 | 96.223 | 102.5282
| Ottawa (Barrhaven)Wind2095RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2095 | 77.6202 | 83.6079 | 89.919 | 96.223 | 102.5282
| Ottawa (Barrhaven)Wind2100RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2100 | 77.6202 | 83.6079 | 89.919 | 96.223 | 102.5282
| Ottawa (Kanata)Ice Accretion2023RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2023 | 19.2694 | 22.8914 | 27.496 | 31.0072 | 34.5391
| Ottawa (Kanata)Ice Accretion2025RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2025 | 19.2661 | 22.8837 | 27.482 | 30.9914 | 34.5156
| Ottawa (Kanata)Ice Accretion2030RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2030 | 19.2629 | 22.8759 | 27.468 | 30.9756 | 34.4921
| Ottawa (Kanata)Ice Accretion2035RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2035 | 19.2596 | 22.8682 | 27.454 | 30.9597 | 34.4686
| Ottawa (Kanata)Ice Accretion2040RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2040 | 19.2564 | 22.8604 | 27.44 | 30.9439 | 34.445
| Ottawa (Kanata)Ice Accretion2045RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2045 | 19.2531 | 22.8527 | 27.426 | 30.9281 | 34.4215
| Ottawa (Kanata)Ice Accretion2050RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2050 | 19.2616 | 22.8775 | 27.4736 | 30.9945 | 34.4968
| Ottawa (Kanata)Ice Accretion2055RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2055 | 19.2733 | 22.91 | 27.5352 | 31.0768 | 34.5956
| Ottawa (Kanata)Ice Accretion2060RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2060 | 19.285 | 22.9425 | 27.5968 | 31.1591 | 34.6944
| Ottawa (Kanata)Ice Accretion2065RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2065 | 19.2966 | 22.9751 | 27.6584 | 31.2413 | 34.7931
| Ottawa (Kanata)Ice Accretion2070RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2070 | 19.3083 | 23.0076 | 27.72 | 31.3236 | 34.8919
| Ottawa (Kanata)Ice Accretion2075RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2075 | 19.3798 | 23.1199 | 27.8787 | 31.5187 | 35.1271
| Ottawa (Kanata)Ice Accretion2080RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2080 | 19.4512 | 23.2323 | 28.0373 | 31.7138 | 35.3623
| Ottawa (Kanata)Ice Accretion2085RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2085 | 19.5227 | 23.3446 | 28.196 | 31.9089 | 35.5975
| Ottawa (Kanata)Ice Accretion2090RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2090 | 19.5941 | 23.4569 | 28.3547 | 32.1041 | 35.8327
| Ottawa (Kanata)Ice Accretion2095RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2095 | 19.6655 | 23.5692 | 28.5133 | 32.2992 | 36.0679
| Ottawa (Kanata)Ice Accretion2100RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2100 | 19.737 | 23.6816 | 28.672 | 32.4943 | 36.3031
| Ottawa (Kanata)Ice Accretion2023RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2023 | 19.2694 | 22.8914 | 27.496 | 31.0072 | 34.5391
| Ottawa (Kanata)Ice Accretion2025RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2025 | 19.2661 | 22.8837 | 27.482 | 30.9914 | 34.5156
| Ottawa (Kanata)Ice Accretion2030RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2030 | 19.2629 | 22.8759 | 27.468 | 30.9756 | 34.4921
| Ottawa (Kanata)Ice Accretion2035RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2035 | 19.2596 | 22.8682 | 27.454 | 30.9597 | 34.4686
| Ottawa (Kanata)Ice Accretion2040RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2040 | 19.2564 | 22.8604 | 27.44 | 30.9439 | 34.445
| Ottawa (Kanata)Ice Accretion2045RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2045 | 19.2531 | 22.8527 | 27.426 | 30.9281 | 34.4215
| Ottawa (Kanata)Ice Accretion2050RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2050 | 19.2616 | 22.8775 | 27.4736 | 30.9945 | 34.4968
| Ottawa (Kanata)Ice Accretion2055RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2055 | 19.2733 | 22.91 | 27.5352 | 31.0768 | 34.5956
| Ottawa (Kanata)Ice Accretion2060RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2060 | 19.285 | 22.9425 | 27.5968 | 31.1591 | 34.6944
| Ottawa (Kanata)Ice Accretion2065RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2065 | 19.2966 | 22.9751 | 27.6584 | 31.2413 | 34.7931
| Ottawa (Kanata)Ice Accretion2070RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2070 | 19.3083 | 23.0076 | 27.72 | 31.3236 | 34.8919
| Ottawa (Kanata)Ice Accretion2075RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2075 | 19.4155 | 23.1761 | 27.958 | 31.6163 | 35.2447
| Ottawa (Kanata)Ice Accretion2080RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2080 | 19.5227 | 23.3446 | 28.196 | 31.9089 | 35.5975
| Ottawa (Kanata)Ice Accretion2085RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2085 | 19.6298 | 23.5131 | 28.434 | 32.2016 | 35.9503
| Ottawa (Kanata)Ice Accretion2090RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2090 | 19.7435 | 23.7358 | 28.7933 | 32.6525 | 36.503
| Ottawa (Kanata)Ice Accretion2095RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2095 | 19.75 | 23.79 | 28.9147 | 32.8107 | 36.703
| Ottawa (Kanata)Ice Accretion2100RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2100 | 19.7565 | 23.8442 | 29.036 | 32.9689 | 36.9029
| Ottawa (Kanata)Ice Accretion2023RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2023 | 19.2694 | 22.8914 | 27.496 | 31.0072 | 34.5391
| Ottawa (Kanata)Ice Accretion2025RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2025 | 19.2629 | 22.8759 | 27.468 | 30.9756 | 34.4921
| Ottawa (Kanata)Ice Accretion2030RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2030 | 19.2564 | 22.8604 | 27.44 | 30.9439 | 34.445
| Ottawa (Kanata)Ice Accretion2035RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2035 | 19.2499 | 22.8449 | 27.412 | 30.9123 | 34.398
| Ottawa (Kanata)Ice Accretion2040RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2040 | 19.2694 | 22.8991 | 27.5147 | 31.0494 | 34.5626
| Ottawa (Kanata)Ice Accretion2045RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2045 | 19.2889 | 22.9534 | 27.6173 | 31.1865 | 34.7273
| Ottawa (Kanata)Ice Accretion2050RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2050 | 19.4512 | 23.2323 | 28.0373 | 31.7138 | 35.3623
| Ottawa (Kanata)Ice Accretion2055RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2055 | 19.5941 | 23.4569 | 28.3547 | 32.1041 | 35.8327
| Ottawa (Kanata)Ice Accretion2060RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2060 | 19.7435 | 23.7358 | 28.7933 | 32.6525 | 36.503
| Ottawa (Kanata)Ice Accretion2065RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2065 | 19.75 | 23.79 | 28.9147 | 32.8107 | 36.703
| Ottawa (Kanata)Ice Accretion2070RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2070 | 19.6525 | 23.759 | 28.9707 | 32.9267 | 36.8794
| Ottawa (Kanata)Ice Accretion2075RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2075 | 19.5486 | 23.6738 | 28.9053 | 32.8845 | 36.8558
| Ottawa (Kanata)Ice Accretion2080RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2080 | 19.4447 | 23.5886 | 28.84 | 32.8423 | 36.8323
| Ottawa (Kanata)Ice Accretion2085RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2085 | 18.831 | 22.8914 | 28.028 | 31.9406 | 35.8445
| Ottawa (Kanata)Ice Accretion2090RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2090 | 18.2173 | 22.1942 | 27.216 | 31.0388 | 34.8566
| Ottawa (Kanata)Ice Accretion2095RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2095 | 18.2173 | 22.1942 | 27.216 | 31.0388 | 34.8566
| Ottawa (Kanata)Ice Accretion2100RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2100 | 18.2173 | 22.1942 | 27.216 | 31.0388 | 34.8566
| Ottawa (Kanata)Wind2023RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2023 | 78.0554 | 84.1771 | 90.639 | 97.08 | 103.5234
| Ottawa (Kanata)Wind2025RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2025 | 78.146 | 84.2929 | 90.7875 | 97.255 | 103.7269
| Ottawa (Kanata)Wind2030RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2030 | 78.2367 | 84.4087 | 90.936 | 97.4299 | 103.9304
| Ottawa (Kanata)Wind2035RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2035 | 78.3274 | 84.5244 | 91.0845 | 97.6049 | 104.1339
| Ottawa (Kanata)Wind2040RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2040 | 78.418 | 84.6402 | 91.233 | 97.7798 | 104.3374
| Ottawa (Kanata)Wind2045RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2045 | 78.5087 | 84.756 | 91.3815 | 97.9548 | 104.5408
| Ottawa (Kanata)Wind2050RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2050 | 78.5108 | 84.7513 | 91.3698 | 97.9352 | 104.5145
| Ottawa (Kanata)Wind2055RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2055 | 78.4222 | 84.6307 | 91.2096 | 97.7406 | 104.2847
| Ottawa (Kanata)Wind2060RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2060 | 78.3336 | 84.5102 | 91.0494 | 97.5461 | 104.0549
| Ottawa (Kanata)Wind2065RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2065 | 78.245 | 84.3897 | 90.8892 | 97.3516 | 103.825
| Ottawa (Kanata)Wind2070RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2070 | 78.1564 | 84.2692 | 90.729 | 97.1571 | 103.5952
| Ottawa (Kanata)Wind2075RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2075 | 78.1991 | 84.325 | 90.7995 | 97.2405 | 103.6927
| Ottawa (Kanata)Wind2080RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2080 | 78.2419 | 84.3808 | 90.87 | 97.324 | 103.7902
| Ottawa (Kanata)Wind2085RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2085 | 78.2846 | 84.4366 | 90.9405 | 97.4075 | 103.8876
| Ottawa (Kanata)Wind2090RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2090 | 78.3274 | 84.4924 | 91.011 | 97.4909 | 103.9851
| Ottawa (Kanata)Wind2095RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2095 | 78.3701 | 84.5482 | 91.0815 | 97.5744 | 104.0826
| Ottawa (Kanata)Wind2100RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2100 | 78.4128 | 84.604 | 91.152 | 97.6578 | 104.18
| Ottawa (Kanata)Wind2023RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2023 | 78.0554 | 84.1771 | 90.639 | 97.08 | 103.5234
| Ottawa (Kanata)Wind2025RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2025 | 78.146 | 84.2929 | 90.7875 | 97.255 | 103.7269
| Ottawa (Kanata)Wind2030RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2030 | 78.2367 | 84.4087 | 90.936 | 97.4299 | 103.9304
| Ottawa (Kanata)Wind2035RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2035 | 78.3274 | 84.5244 | 91.0845 | 97.6049 | 104.1339
| Ottawa (Kanata)Wind2040RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2040 | 78.418 | 84.6402 | 91.233 | 97.7798 | 104.3374
| Ottawa (Kanata)Wind2045RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2045 | 78.5087 | 84.756 | 91.3815 | 97.9548 | 104.5408
| Ottawa (Kanata)Wind2050RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2050 | 78.5108 | 84.7513 | 91.3698 | 97.9352 | 104.5145
| Ottawa (Kanata)Wind2055RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2055 | 78.4222 | 84.6307 | 91.2096 | 97.7406 | 104.2847
| Ottawa (Kanata)Wind2060RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2060 | 78.3336 | 84.5102 | 91.0494 | 97.5461 | 104.0549
| Ottawa (Kanata)Wind2065RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2065 | 78.245 | 84.3897 | 90.8892 | 97.3516 | 103.825
| Ottawa (Kanata)Wind2070RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2070 | 78.1564 | 84.2692 | 90.729 | 97.1571 | 103.5952
| Ottawa (Kanata)Wind2075RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2075 | 78.2205 | 84.3529 | 90.8347 | 97.2823 | 103.7414
| Ottawa (Kanata)Wind2080RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2080 | 78.2846 | 84.4366 | 90.9405 | 97.4075 | 103.8876
| Ottawa (Kanata)Wind2085RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2085 | 78.3487 | 84.5203 | 91.0462 | 97.5326 | 104.0338
| Ottawa (Kanata)Wind2090RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2090 | 78.2263 | 84.3612 | 90.84 | 97.2919 | 103.7525
| Ottawa (Kanata)Wind2095RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2095 | 78.0398 | 84.1185 | 90.528 | 96.926 | 103.325
| Ottawa (Kanata)Wind2100RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2100 | 77.8533 | 83.8758 | 90.216 | 96.56 | 102.8975
| Ottawa (Kanata)Wind2023RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2023 | 78.0554 | 84.1771 | 90.639 | 97.08 | 103.5234
| Ottawa (Kanata)Wind2025RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2025 | 78.2367 | 84.4087 | 90.936 | 97.4299 | 103.9304
| Ottawa (Kanata)Wind2030RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2030 | 78.418 | 84.6402 | 91.233 | 97.7798 | 104.3374
| Ottawa (Kanata)Wind2035RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2035 | 78.5994 | 84.8718 | 91.53 | 98.1297 | 104.7443
| Ottawa (Kanata)Wind2040RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2040 | 78.4517 | 84.6709 | 91.263 | 97.8055 | 104.3613
| Ottawa (Kanata)Wind2045RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2045 | 78.304 | 84.47 | 90.996 | 97.4813 | 103.9783
| Ottawa (Kanata)Wind2050RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2050 | 78.2419 | 84.3808 | 90.87 | 97.324 | 103.7902
| Ottawa (Kanata)Wind2055RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2055 | 78.3274 | 84.4924 | 91.011 | 97.4909 | 103.9851
| Ottawa (Kanata)Wind2060RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2060 | 78.2263 | 84.3612 | 90.84 | 97.2919 | 103.7525
| Ottawa (Kanata)Wind2065RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2065 | 78.0398 | 84.1185 | 90.528 | 96.926 | 103.325
| Ottawa (Kanata)Wind2070RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2070 | 77.8222 | 83.82 | 90.129 | 96.4445 | 102.7539
| Ottawa (Kanata)Wind2075RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2075 | 77.7911 | 83.7642 | 90.042 | 96.3289 | 102.6103
| Ottawa (Kanata)Wind2080RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2080 | 77.76 | 83.7084 | 89.955 | 96.2133 | 102.4666
| Ottawa (Kanata)Wind2085RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2085 | 77.5463 | 83.4489 | 89.64 | 95.8522 | 102.0562
| Ottawa (Kanata)Wind2090RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2090 | 77.3326 | 83.1894 | 89.325 | 95.4911 | 101.6458
| Ottawa (Kanata)Wind2095RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2095 | 77.3326 | 83.1894 | 89.325 | 95.4911 | 101.6458
| Ottawa (Kanata)Wind2100RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2100 | 77.3326 | 83.1894 | 89.325 | 95.4911 | 101.6458
| Ottawa (M-C Int'l Airport)Ice Accretion2023RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
| Ottawa (M-C Int'l Airport)Ice Accretion2025RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
| Ottawa (M-C Int'l Airport)Ice Accretion2030RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
| Ottawa (M-C Int'l Airport)Ice Accretion2035RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
| Ottawa (M-C Int'l Airport)Ice Accretion2040RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
| Ottawa (M-C Int'l Airport)Ice Accretion2045RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
| Ottawa (M-C Int'l Airport)Ice Accretion2050RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
| Ottawa (M-C Int'l Airport)Ice Accretion2055RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
| Ottawa (M-C Int'l Airport)Ice Accretion2060RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
| Ottawa (M-C Int'l Airport)Ice Accretion2065RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
| Ottawa (M-C Int'l Airport)Ice Accretion2070RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
| Ottawa (M-C Int'l Airport)Ice Accretion2075RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2075 | 20.6423 | 24.7215 | 29.87 | 33.8039 | 37.7496
| Ottawa (M-C Int'l Airport)Ice Accretion2080RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2080 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
| Ottawa (M-C Int'l Airport)Ice Accretion2085RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2085 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
| Ottawa (M-C Int'l Airport)Ice Accretion2090RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2090 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
| Ottawa (M-C Int'l Airport)Ice Accretion2095RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2095 | 20.9624 | 25.2029 | 30.55 | 34.6401 | 38.7576
| Ottawa (M-C Int'l Airport)Ice Accretion2100RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2100 | 21.0424 | 25.3233 | 30.72 | 34.8492 | 39.0096
| Ottawa (M-C Int'l Airport)Ice Accretion2023RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
| Ottawa (M-C Int'l Airport)Ice Accretion2025RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
| Ottawa (M-C Int'l Airport)Ice Accretion2030RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
| Ottawa (M-C Int'l Airport)Ice Accretion2035RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
| Ottawa (M-C Int'l Airport)Ice Accretion2040RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
| Ottawa (M-C Int'l Airport)Ice Accretion2045RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
| Ottawa (M-C Int'l Airport)Ice Accretion2050RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
| Ottawa (M-C Int'l Airport)Ice Accretion2055RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
| Ottawa (M-C Int'l Airport)Ice Accretion2060RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
| Ottawa (M-C Int'l Airport)Ice Accretion2065RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
| Ottawa (M-C Int'l Airport)Ice Accretion2070RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
| Ottawa (M-C Int'l Airport)Ice Accretion2075RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2075 | 20.6823 | 24.7817 | 29.955 | 33.9085 | 37.8756
| Ottawa (M-C Int'l Airport)Ice Accretion2080RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2080 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
| Ottawa (M-C Int'l Airport)Ice Accretion2085RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2085 | 20.9224 | 25.1428 | 30.465 | 34.5356 | 38.6316
| Ottawa (M-C Int'l Airport)Ice Accretion2090RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2090 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
| Ottawa (M-C Int'l Airport)Ice Accretion2095RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2095 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
| Ottawa (M-C Int'l Airport)Ice Accretion2100RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2100 | 21.439 | 25.9458 | 31.65 | 36.0018 | 40.3326
| Ottawa (M-C Int'l Airport)Ice Accretion2023RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
| Ottawa (M-C Int'l Airport)Ice Accretion2025RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2025 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
| Ottawa (M-C Int'l Airport)Ice Accretion2030RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2030 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
| Ottawa (M-C Int'l Airport)Ice Accretion2035RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2035 | 20.2074 | 24.0285 | 28.86 | 32.5779 | 36.288
| Ottawa (M-C Int'l Airport)Ice Accretion2040RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2040 | 20.3257 | 24.2194 | 29.14 | 32.9169 | 36.6912
| Ottawa (M-C Int'l Airport)Ice Accretion2045RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2045 | 20.444 | 24.4103 | 29.42 | 33.2559 | 37.0944
| Ottawa (M-C Int'l Airport)Ice Accretion2050RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2050 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
| Ottawa (M-C Int'l Airport)Ice Accretion2055RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2055 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
| Ottawa (M-C Int'l Airport)Ice Accretion2060RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2060 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
| Ottawa (M-C Int'l Airport)Ice Accretion2065RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2065 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
| Ottawa (M-C Int'l Airport)Ice Accretion2070RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2070 | 21.2372 | 25.7383 | 31.44 | 35.7871 | 40.1184
| Ottawa (M-C Int'l Airport)Ice Accretion2075RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2075 | 21.0354 | 25.5308 | 31.23 | 35.5724 | 39.9042
| Ottawa (M-C Int'l Airport)Ice Accretion2080RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2080 | 20.8336 | 25.3233 | 31.02 | 35.3577 | 39.69
| Ottawa (M-C Int'l Airport)Ice Accretion2085RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2085 | 20.0926 | 24.5016 | 30.09 | 34.3237 | 38.5749
| Ottawa (M-C Int'l Airport)Ice Accretion2090RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2090 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
| Ottawa (M-C Int'l Airport)Ice Accretion2095RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2095 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
| Ottawa (M-C Int'l Airport)Ice Accretion2100RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2100 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
| Ottawa (M-C Int'l Airport)Wind2023RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2023 | 77.8688 | 83.9427 | 90.351 | 96.743 | 103.1335
| Ottawa (M-C Int'l Airport)Wind2025RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2025 | 77.8986 | 83.9776 | 90.3915 | 96.7895 | 103.1848
| Ottawa (M-C Int'l Airport)Wind2030RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2030 | 77.9284 | 84.0125 | 90.432 | 96.8361 | 103.2361
| Ottawa (M-C Int'l Airport)Wind2035RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2035 | 77.9582 | 84.0474 | 90.4725 | 96.8826 | 103.2874
| Ottawa (M-C Int'l Airport)Wind2040RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2040 | 77.988 | 84.0822 | 90.513 | 96.9292 | 103.3387
| Ottawa (M-C Int'l Airport)Wind2045RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2045 | 78.0178 | 84.1171 | 90.5535 | 96.9757 | 103.39
| Ottawa (M-C Int'l Airport)Wind2050RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2050 | 77.9745 | 84.0515 | 90.4626 | 96.8624 | 103.2546
| Ottawa (M-C Int'l Airport)Wind2055RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2055 | 77.9015 | 83.9511 | 90.3312 | 96.7025 | 103.0679
| Ottawa (M-C Int'l Airport)Wind2060RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2060 | 77.8284 | 83.8507 | 90.1998 | 96.5427 | 102.8811
| Ottawa (M-C Int'l Airport)Wind2065RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2065 | 77.7554 | 83.7502 | 90.0684 | 96.3828 | 102.6944
| Ottawa (M-C Int'l Airport)Wind2070RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2070 | 77.6823 | 83.6498 | 89.937 | 96.223 | 102.5077
| Ottawa (M-C Int'l Airport)Wind2075RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2075 | 77.7018 | 83.6819 | 89.9835 | 96.2823 | 102.5812
| Ottawa (M-C Int'l Airport)Wind2080RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2080 | 77.7212 | 83.7139 | 90.03 | 96.3417 | 102.6547
| Ottawa (M-C Int'l Airport)Wind2085RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2085 | 77.7406 | 83.746 | 90.0765 | 96.4011 | 102.7283
| Ottawa (M-C Int'l Airport)Wind2090RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2090 | 77.76 | 83.7781 | 90.123 | 96.4605 | 102.8018
| Ottawa (M-C Int'l Airport)Wind2095RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2095 | 77.7795 | 83.8102 | 90.1695 | 96.5199 | 102.8753
| Ottawa (M-C Int'l Airport)Wind2100RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2100 | 77.7989 | 83.8423 | 90.216 | 96.5793 | 102.9488
| Ottawa (M-C Int'l Airport)Wind2023RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2023 | 77.8688 | 83.9427 | 90.351 | 96.743 | 103.1335
| Ottawa (M-C Int'l Airport)Wind2025RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2025 | 77.8986 | 83.9776 | 90.3915 | 96.7895 | 103.1848
| Ottawa (M-C Int'l Airport)Wind2030RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2030 | 77.9284 | 84.0125 | 90.432 | 96.8361 | 103.2361
| Ottawa (M-C Int'l Airport)Wind2035RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2035 | 77.9582 | 84.0474 | 90.4725 | 96.8826 | 103.2874
| Ottawa (M-C Int'l Airport)Wind2040RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2040 | 77.988 | 84.0822 | 90.513 | 96.9292 | 103.3387
| Ottawa (M-C Int'l Airport)Wind2045RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2045 | 78.0178 | 84.1171 | 90.5535 | 96.9757 | 103.39
| Ottawa (M-C Int'l Airport)Wind2050RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2050 | 77.9745 | 84.0515 | 90.4626 | 96.8624 | 103.2546
| Ottawa (M-C Int'l Airport)Wind2055RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2055 | 77.9015 | 83.9511 | 90.3312 | 96.7025 | 103.0679
| Ottawa (M-C Int'l Airport)Wind2060RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2060 | 77.8284 | 83.8507 | 90.1998 | 96.5427 | 102.8811
| Ottawa (M-C Int'l Airport)Wind2065RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2065 | 77.7554 | 83.7502 | 90.0684 | 96.3828 | 102.6944
| Ottawa (M-C Int'l Airport)Wind2070RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2070 | 77.6823 | 83.6498 | 89.937 | 96.223 | 102.5077
| Ottawa (M-C Int'l Airport)Wind2075RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2075 | 77.7115 | 83.6979 | 90.0067 | 96.312 | 102.618
| Ottawa (M-C Int'l Airport)Wind2080RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2080 | 77.7406 | 83.746 | 90.0765 | 96.4011 | 102.7283
| Ottawa (M-C Int'l Airport)Wind2085RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2085 | 77.7698 | 83.7942 | 90.1462 | 96.4902 | 102.8385
| Ottawa (M-C Int'l Airport)Wind2090RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2090 | 77.6797 | 83.6916 | 90.03 | 96.361 | 102.6958
| Ottawa (M-C Int'l Airport)Wind2095RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2095 | 77.5606 | 83.541 | 89.844 | 96.1427 | 102.4427
| Ottawa (M-C Int'l Airport)Wind2100RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2100 | 77.4414 | 83.3903 | 89.658 | 95.9244 | 102.1896
| Ottawa (M-C Int'l Airport)Wind2023RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2023 | 77.8688 | 83.9427 | 90.351 | 96.743 | 103.1335
| Ottawa (M-C Int'l Airport)Wind2025RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2025 | 77.9284 | 84.0125 | 90.432 | 96.8361 | 103.2361
| Ottawa (M-C Int'l Airport)Wind2030RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2030 | 77.988 | 84.0822 | 90.513 | 96.9292 | 103.3387
| Ottawa (M-C Int'l Airport)Wind2035RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2035 | 78.0476 | 84.152 | 90.594 | 97.0223 | 103.4413
| Ottawa (M-C Int'l Airport)Wind2040RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2040 | 77.9258 | 83.9846 | 90.375 | 96.7558 | 103.1301
| Ottawa (M-C Int'l Airport)Wind2045RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2045 | 77.8041 | 83.8172 | 90.156 | 96.4894 | 102.8189
| Ottawa (M-C Int'l Airport)Wind2050RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2050 | 77.7212 | 83.7139 | 90.03 | 96.3417 | 102.6547
| Ottawa (M-C Int'l Airport)Wind2055RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2055 | 77.76 | 83.7781 | 90.123 | 96.4605 | 102.8018
| Ottawa (M-C Int'l Airport)Wind2060RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2060 | 77.6797 | 83.6916 | 90.03 | 96.361 | 102.6958
| Ottawa (M-C Int'l Airport)Wind2065RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2065 | 77.5606 | 83.541 | 89.844 | 96.1427 | 102.4427
| Ottawa (M-C Int'l Airport)Wind2070RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2070 | 77.5165 | 83.4908 | 89.784 | 96.0721 | 102.364
| Ottawa (M-C Int'l Airport)Wind2075RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2075 | 77.5917 | 83.5912 | 89.91 | 96.2198 | 102.5384
| Ottawa (M-C Int'l Airport)Wind2080RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2080 | 77.6668 | 83.6916 | 90.036 | 96.3674 | 102.7129
| Ottawa (M-C Int'l Airport)Wind2085RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2085 | 77.6435 | 83.6498 | 89.9775 | 96.2952 | 102.6205
| Ottawa (M-C Int'l Airport)Wind2090RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2090 | 77.6202 | 83.6079 | 89.919 | 96.223 | 102.5282
| Ottawa (M-C Int'l Airport)Wind2095RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2095 | 77.6202 | 83.6079 | 89.919 | 96.223 | 102.5282
| Ottawa (M-C Int'l Airport)Wind2100RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2100 | 77.6202 | 83.6079 | 89.919 | 96.223 | 102.5282
| Ottawa (Orleans)Ice Accretion2023RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
| Ottawa (Orleans)Ice Accretion2025RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
| Ottawa (Orleans)Ice Accretion2030RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
| Ottawa (Orleans)Ice Accretion2035RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
| Ottawa (Orleans)Ice Accretion2040RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
| Ottawa (Orleans)Ice Accretion2045RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
| Ottawa (Orleans)Ice Accretion2050RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
| Ottawa (Orleans)Ice Accretion2055RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
| Ottawa (Orleans)Ice Accretion2060RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
| Ottawa (Orleans)Ice Accretion2065RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
| Ottawa (Orleans)Ice Accretion2070RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
| Ottawa (Orleans)Ice Accretion2075RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2075 | 20.6423 | 24.7215 | 29.87 | 33.8039 | 37.7496
| Ottawa (Orleans)Ice Accretion2080RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2080 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
| Ottawa (Orleans)Ice Accretion2085RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2085 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
| Ottawa (Orleans)Ice Accretion2090RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2090 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
| Ottawa (Orleans)Ice Accretion2095RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2095 | 20.9624 | 25.2029 | 30.55 | 34.6401 | 38.7576
| Ottawa (Orleans)Ice Accretion2100RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2100 | 21.0424 | 25.3233 | 30.72 | 34.8492 | 39.0096
| Ottawa (Orleans)Ice Accretion2023RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
| Ottawa (Orleans)Ice Accretion2025RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
| Ottawa (Orleans)Ice Accretion2030RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
| Ottawa (Orleans)Ice Accretion2035RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
| Ottawa (Orleans)Ice Accretion2040RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
| Ottawa (Orleans)Ice Accretion2045RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
| Ottawa (Orleans)Ice Accretion2050RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
| Ottawa (Orleans)Ice Accretion2055RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
| Ottawa (Orleans)Ice Accretion2060RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
| Ottawa (Orleans)Ice Accretion2065RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
| Ottawa (Orleans)Ice Accretion2070RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
| Ottawa (Orleans)Ice Accretion2075RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2075 | 20.6823 | 24.7817 | 29.955 | 33.9085 | 37.8756
| Ottawa (Orleans)Ice Accretion2080RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2080 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
| Ottawa (Orleans)Ice Accretion2085RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2085 | 20.9224 | 25.1428 | 30.465 | 34.5356 | 38.6316
| Ottawa (Orleans)Ice Accretion2090RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2090 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
| Ottawa (Orleans)Ice Accretion2095RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2095 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
| Ottawa (Orleans)Ice Accretion2100RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2100 | 21.439 | 25.9458 | 31.65 | 36.0018 | 40.3326
| Ottawa (Orleans)Ice Accretion2023RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
| Ottawa (Orleans)Ice Accretion2025RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2025 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
| Ottawa (Orleans)Ice Accretion2030RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2030 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
| Ottawa (Orleans)Ice Accretion2035RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2035 | 20.2074 | 24.0285 | 28.86 | 32.5779 | 36.288
| Ottawa (Orleans)Ice Accretion2040RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2040 | 20.3257 | 24.2194 | 29.14 | 32.9169 | 36.6912
| Ottawa (Orleans)Ice Accretion2045RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2045 | 20.444 | 24.4103 | 29.42 | 33.2559 | 37.0944
| Ottawa (Orleans)Ice Accretion2050RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2050 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
| Ottawa (Orleans)Ice Accretion2055RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2055 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
| Ottawa (Orleans)Ice Accretion2060RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2060 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
| Ottawa (Orleans)Ice Accretion2065RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2065 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
| Ottawa (Orleans)Ice Accretion2070RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2070 | 21.2372 | 25.7383 | 31.44 | 35.7871 | 40.1184
| Ottawa (Orleans)Ice Accretion2075RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2075 | 21.0354 | 25.5308 | 31.23 | 35.5724 | 39.9042
| Ottawa (Orleans)Ice Accretion2080RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2080 | 20.8336 | 25.3233 | 31.02 | 35.3577 | 39.69
| Ottawa (Orleans)Ice Accretion2085RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2085 | 20.0926 | 24.5016 | 30.09 | 34.3237 | 38.5749
| Ottawa (Orleans)Ice Accretion2090RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2090 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
| Ottawa (Orleans)Ice Accretion2095RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2095 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
| Ottawa (Orleans)Ice Accretion2100RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2100 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
| Ottawa (Orleans)Wind2023RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2023 | 79.5993 | 85.8081 | 92.3588 | 98.8928 | 105.4254
| Ottawa (Orleans)Wind2025RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2025 | 79.6297 | 85.8438 | 92.4002 | 98.9404 | 105.4778
| Ottawa (Orleans)Wind2030RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2030 | 79.6602 | 85.8794 | 92.4416 | 98.988 | 105.5303
| Ottawa (Orleans)Wind2035RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2035 | 79.6906 | 85.9151 | 92.483 | 99.0356 | 105.5827
| Ottawa (Orleans)Wind2040RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2040 | 79.7211 | 85.9507 | 92.5244 | 99.0831 | 105.6351
| Ottawa (Orleans)Wind2045RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2045 | 79.7515 | 85.9864 | 92.5658 | 99.1307 | 105.6876
| Ottawa (Orleans)Wind2050RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2050 | 79.7073 | 85.9194 | 92.4729 | 99.0149 | 105.5491
| Ottawa (Orleans)Wind2055RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2055 | 79.6326 | 85.8167 | 92.3386 | 98.8515 | 105.3583
| Ottawa (Orleans)Wind2060RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2060 | 79.558 | 85.714 | 92.2042 | 98.6881 | 105.1674
| Ottawa (Orleans)Wind2065RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2065 | 79.4833 | 85.6113 | 92.0699 | 98.5247 | 104.9765
| Ottawa (Orleans)Wind2070RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2070 | 79.4086 | 85.5087 | 91.9356 | 98.3612 | 104.7856
| Ottawa (Orleans)Wind2075RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2075 | 79.4285 | 85.5415 | 91.9831 | 98.422 | 104.8608
| Ottawa (Orleans)Wind2080RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2080 | 79.4483 | 85.5743 | 92.0307 | 98.4827 | 104.9359
| Ottawa (Orleans)Wind2085RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2085 | 79.4682 | 85.6071 | 92.0782 | 98.5434 | 105.0111
| Ottawa (Orleans)Wind2090RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2090 | 79.488 | 85.6399 | 92.1257 | 98.6041 | 105.0863
| Ottawa (Orleans)Wind2095RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2095 | 79.5079 | 85.6727 | 92.1733 | 98.6648 | 105.1614
| Ottawa (Orleans)Wind2100RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2100 | 79.5278 | 85.7055 | 92.2208 | 98.7255 | 105.2366
| Ottawa (Orleans)Wind2023RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2023 | 79.5993 | 85.8081 | 92.3588 | 98.8928 | 105.4254
| Ottawa (Orleans)Wind2025RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2025 | 79.6297 | 85.8438 | 92.4002 | 98.9404 | 105.4778
| Ottawa (Orleans)Wind2030RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2030 | 79.6602 | 85.8794 | 92.4416 | 98.988 | 105.5303
| Ottawa (Orleans)Wind2035RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2035 | 79.6906 | 85.9151 | 92.483 | 99.0356 | 105.5827
| Ottawa (Orleans)Wind2040RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2040 | 79.7211 | 85.9507 | 92.5244 | 99.0831 | 105.6351
| Ottawa (Orleans)Wind2045RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2045 | 79.7515 | 85.9864 | 92.5658 | 99.1307 | 105.6876
| Ottawa (Orleans)Wind2050RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2050 | 79.7073 | 85.9194 | 92.4729 | 99.0149 | 105.5491
| Ottawa (Orleans)Wind2055RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2055 | 79.6326 | 85.8167 | 92.3386 | 98.8515 | 105.3583
| Ottawa (Orleans)Wind2060RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2060 | 79.558 | 85.714 | 92.2042 | 98.6881 | 105.1674
| Ottawa (Orleans)Wind2065RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2065 | 79.4833 | 85.6113 | 92.0699 | 98.5247 | 104.9765
| Ottawa (Orleans)Wind2070RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2070 | 79.4086 | 85.5087 | 91.9356 | 98.3612 | 104.7856
| Ottawa (Orleans)Wind2075RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2075 | 79.4384 | 85.5579 | 92.0069 | 98.4523 | 104.8984
| Ottawa (Orleans)Wind2080RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2080 | 79.4682 | 85.6071 | 92.0782 | 98.5434 | 105.0111
| Ottawa (Orleans)Wind2085RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2085 | 79.498 | 85.6563 | 92.1495 | 98.6344 | 105.1238
| Ottawa (Orleans)Wind2090RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2090 | 79.406 | 85.5514 | 92.0307 | 98.5023 | 104.9779
| Ottawa (Orleans)Wind2095RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2095 | 79.2842 | 85.3974 | 91.8405 | 98.2792 | 104.7192
| Ottawa (Orleans)Wind2100RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2100 | 79.1623 | 85.2434 | 91.6504 | 98.0561 | 104.4605
| Ottawa (Orleans)Wind2023RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2023 | 79.5993 | 85.8081 | 92.3588 | 98.8928 | 105.4254
| Ottawa (Orleans)Wind2025RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2025 | 79.6602 | 85.8794 | 92.4416 | 98.988 | 105.5303
| Ottawa (Orleans)Wind2030RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2030 | 79.7211 | 85.9507 | 92.5244 | 99.0831 | 105.6351
| Ottawa (Orleans)Wind2035RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2035 | 79.782 | 86.022 | 92.6072 | 99.1783 | 105.74
| Ottawa (Orleans)Wind2040RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2040 | 79.6575 | 85.8509 | 92.3833 | 98.9059 | 105.4219
| Ottawa (Orleans)Wind2045RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2045 | 79.5331 | 85.6798 | 92.1595 | 98.6336 | 105.1037
| Ottawa (Orleans)Wind2050RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2050 | 79.4483 | 85.5743 | 92.0307 | 98.4827 | 104.9359
| Ottawa (Orleans)Wind2055RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2055 | 79.488 | 85.6399 | 92.1257 | 98.6041 | 105.0863
| Ottawa (Orleans)Wind2060RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2060 | 79.406 | 85.5514 | 92.0307 | 98.5023 | 104.9779
| Ottawa (Orleans)Wind2065RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2065 | 79.2842 | 85.3974 | 91.8405 | 98.2792 | 104.7192
| Ottawa (Orleans)Wind2070RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2070 | 79.2391 | 85.3461 | 91.7792 | 98.207 | 104.6388
| Ottawa (Orleans)Wind2075RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2075 | 79.3159 | 85.4488 | 91.908 | 98.358 | 104.8171
| Ottawa (Orleans)Wind2080RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2080 | 79.3927 | 85.5514 | 92.0368 | 98.5089 | 104.9954
| Ottawa (Orleans)Wind2085RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2085 | 79.3689 | 85.5087 | 91.977 | 98.4351 | 104.901
| Ottawa (Orleans)Wind2090RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2090 | 79.3451 | 85.4659 | 91.9172 | 98.3612 | 104.8066
| Ottawa (Orleans)Wind2095RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2095 | 79.3451 | 85.4659 | 91.9172 | 98.3612 | 104.8066
| Ottawa (Orleans)Wind2100RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2100 | 79.3451 | 85.4659 | 91.9172 | 98.3612 | 104.8066
| Ottawa (city hall)Ice Accretion2023RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
| Ottawa (city hall)Ice Accretion2025RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
| Ottawa (city hall)Ice Accretion2030RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
| Ottawa (city hall)Ice Accretion2035RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
| Ottawa (city hall)Ice Accretion2040RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
| Ottawa (city hall)Ice Accretion2045RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
| Ottawa (city hall)Ice Accretion2050RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
| Ottawa (city hall)Ice Accretion2055RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
| Ottawa (city hall)Ice Accretion2060RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
| Ottawa (city hall)Ice Accretion2065RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
| Ottawa (city hall)Ice Accretion2070RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
| Ottawa (city hall)Ice Accretion2075RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2075 | 20.6423 | 24.7215 | 29.87 | 33.8039 | 37.7496
| Ottawa (city hall)Ice Accretion2080RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2080 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
| Ottawa (city hall)Ice Accretion2085RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2085 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
| Ottawa (city hall)Ice Accretion2090RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2090 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
| Ottawa (city hall)Ice Accretion2095RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2095 | 20.9624 | 25.2029 | 30.55 | 34.6401 | 38.7576
| Ottawa (city hall)Ice Accretion2100RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2100 | 21.0424 | 25.3233 | 30.72 | 34.8492 | 39.0096
| Ottawa (city hall)Ice Accretion2023RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
| Ottawa (city hall)Ice Accretion2025RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
| Ottawa (city hall)Ice Accretion2030RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
| Ottawa (city hall)Ice Accretion2035RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
| Ottawa (city hall)Ice Accretion2040RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
| Ottawa (city hall)Ice Accretion2045RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
| Ottawa (city hall)Ice Accretion2050RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
| Ottawa (city hall)Ice Accretion2055RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
| Ottawa (city hall)Ice Accretion2060RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
| Ottawa (city hall)Ice Accretion2065RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
| Ottawa (city hall)Ice Accretion2070RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
| Ottawa (city hall)Ice Accretion2075RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2075 | 20.6823 | 24.7817 | 29.955 | 33.9085 | 37.8756
| Ottawa (city hall)Ice Accretion2080RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2080 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
| Ottawa (city hall)Ice Accretion2085RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2085 | 20.9224 | 25.1428 | 30.465 | 34.5356 | 38.6316
| Ottawa (city hall)Ice Accretion2090RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2090 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
| Ottawa (city hall)Ice Accretion2095RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2095 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
| Ottawa (city hall)Ice Accretion2100RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2100 | 21.439 | 25.9458 | 31.65 | 36.0018 | 40.3326
| Ottawa (city hall)Ice Accretion2023RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
| Ottawa (city hall)Ice Accretion2025RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2025 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
| Ottawa (city hall)Ice Accretion2030RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2030 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
| Ottawa (city hall)Ice Accretion2035RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2035 | 20.2074 | 24.0285 | 28.86 | 32.5779 | 36.288
| Ottawa (city hall)Ice Accretion2040RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2040 | 20.3257 | 24.2194 | 29.14 | 32.9169 | 36.6912
| Ottawa (city hall)Ice Accretion2045RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2045 | 20.444 | 24.4103 | 29.42 | 33.2559 | 37.0944
| Ottawa (city hall)Ice Accretion2050RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2050 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
| Ottawa (city hall)Ice Accretion2055RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2055 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
| Ottawa (city hall)Ice Accretion2060RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2060 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
| Ottawa (city hall)Ice Accretion2065RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2065 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
| Ottawa (city hall)Ice Accretion2070RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2070 | 21.2372 | 25.7383 | 31.44 | 35.7871 | 40.1184
| Ottawa (city hall)Ice Accretion2075RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2075 | 21.0354 | 25.5308 | 31.23 | 35.5724 | 39.9042
| Ottawa (city hall)Ice Accretion2080RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2080 | 20.8336 | 25.3233 | 31.02 | 35.3577 | 39.69
| Ottawa (city hall)Ice Accretion2085RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2085 | 20.0926 | 24.5016 | 30.09 | 34.3237 | 38.5749
| Ottawa (city hall)Ice Accretion2090RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2090 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
| Ottawa (city hall)Ice Accretion2095RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2095 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
| Ottawa (city hall)Ice Accretion2100RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2100 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
| Ottawa (city hall)Wind2023RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2023 | 77.8688 | 83.9427 | 90.351 | 96.743 | 103.1335
| Ottawa (city hall)Wind2025RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2025 | 77.8986 | 83.9776 | 90.3915 | 96.7895 | 103.1848
| Ottawa (city hall)Wind2030RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2030 | 77.9284 | 84.0125 | 90.432 | 96.8361 | 103.2361
| Ottawa (city hall)Wind2035RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2035 | 77.9582 | 84.0474 | 90.4725 | 96.8826 | 103.2874
| Ottawa (city hall)Wind2040RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2040 | 77.988 | 84.0822 | 90.513 | 96.9292 | 103.3387
| Ottawa (city hall)Wind2045RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2045 | 78.0178 | 84.1171 | 90.5535 | 96.9757 | 103.39
| Ottawa (city hall)Wind2050RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2050 | 77.9745 | 84.0515 | 90.4626 | 96.8624 | 103.2546
| Ottawa (city hall)Wind2055RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2055 | 77.9015 | 83.9511 | 90.3312 | 96.7025 | 103.0679
| Ottawa (city hall)Wind2060RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2060 | 77.8284 | 83.8507 | 90.1998 | 96.5427 | 102.8811
| Ottawa (city hall)Wind2065RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2065 | 77.7554 | 83.7502 | 90.0684 | 96.3828 | 102.6944
| Ottawa (city hall)Wind2070RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2070 | 77.6823 | 83.6498 | 89.937 | 96.223 | 102.5077
| Ottawa (city hall)Wind2075RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2075 | 77.7018 | 83.6819 | 89.9835 | 96.2823 | 102.5812
| Ottawa (city hall)Wind2080RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2080 | 77.7212 | 83.7139 | 90.03 | 96.3417 | 102.6547
| Ottawa (city hall)Wind2085RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2085 | 77.7406 | 83.746 | 90.0765 | 96.4011 | 102.7283
| Ottawa (city hall)Wind2090RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2090 | 77.76 | 83.7781 | 90.123 | 96.4605 | 102.8018
| Ottawa (city hall)Wind2095RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2095 | 77.7795 | 83.8102 | 90.1695 | 96.5199 | 102.8753
| Ottawa (city hall)Wind2100RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2100 | 77.7989 | 83.8423 | 90.216 | 96.5793 | 102.9488
| Ottawa (city hall)Wind2023RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2023 | 77.8688 | 83.9427 | 90.351 | 96.743 | 103.1335
| Ottawa (city hall)Wind2025RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2025 | 77.8986 | 83.9776 | 90.3915 | 96.7895 | 103.1848
| Ottawa (city hall)Wind2030RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2030 | 77.9284 | 84.0125 | 90.432 | 96.8361 | 103.2361
| Ottawa (city hall)Wind2035RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2035 | 77.9582 | 84.0474 | 90.4725 | 96.8826 | 103.2874
| Ottawa (city hall)Wind2040RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2040 | 77.988 | 84.0822 | 90.513 | 96.9292 | 103.3387
| Ottawa (city hall)Wind2045RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2045 | 78.0178 | 84.1171 | 90.5535 | 96.9757 | 103.39
| Ottawa (city hall)Wind2050RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2050 | 77.9745 | 84.0515 | 90.4626 | 96.8624 | 103.2546
| Ottawa (city hall)Wind2055RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2055 | 77.9015 | 83.9511 | 90.3312 | 96.7025 | 103.0679
| Ottawa (city hall)Wind2060RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2060 | 77.8284 | 83.8507 | 90.1998 | 96.5427 | 102.8811
| Ottawa (city hall)Wind2065RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2065 | 77.7554 | 83.7502 | 90.0684 | 96.3828 | 102.6944
| Ottawa (city hall)Wind2070RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2070 | 77.6823 | 83.6498 | 89.937 | 96.223 | 102.5077
| Ottawa (city hall)Wind2075RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2075 | 77.7115 | 83.6979 | 90.0067 | 96.312 | 102.618
| Ottawa (city hall)Wind2080RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2080 | 77.7406 | 83.746 | 90.0765 | 96.4011 | 102.7283
| Ottawa (city hall)Wind2085RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2085 | 77.7698 | 83.7942 | 90.1462 | 96.4902 | 102.8385
| Ottawa (city hall)Wind2090RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2090 | 77.6797 | 83.6916 | 90.03 | 96.361 | 102.6958
| Ottawa (city hall)Wind2095RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2095 | 77.5606 | 83.541 | 89.844 | 96.1427 | 102.4427
| Ottawa (city hall)Wind2100RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2100 | 77.4414 | 83.3903 | 89.658 | 95.9244 | 102.1896
| Ottawa (city hall)Wind2023RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2023 | 77.8688 | 83.9427 | 90.351 | 96.743 | 103.1335
| Ottawa (city hall)Wind2025RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2025 | 77.9284 | 84.0125 | 90.432 | 96.8361 | 103.2361
| Ottawa (city hall)Wind2030RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2030 | 77.988 | 84.0822 | 90.513 | 96.9292 | 103.3387
| Ottawa (city hall)Wind2035RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2035 | 78.0476 | 84.152 | 90.594 | 97.0223 | 103.4413
| Ottawa (city hall)Wind2040RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2040 | 77.9258 | 83.9846 | 90.375 | 96.7558 | 103.1301
| Ottawa (city hall)Wind2045RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2045 | 77.8041 | 83.8172 | 90.156 | 96.4894 | 102.8189
| Ottawa (city hall)Wind2050RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2050 | 77.7212 | 83.7139 | 90.03 | 96.3417 | 102.6547
| Ottawa (city hall)Wind2055RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2055 | 77.76 | 83.7781 | 90.123 | 96.4605 | 102.8018
| Ottawa (city hall)Wind2060RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2060 | 77.6797 | 83.6916 | 90.03 | 96.361 | 102.6958
| Ottawa (city hall)Wind2065RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2065 | 77.5606 | 83.541 | 89.844 | 96.1427 | 102.4427
| Ottawa (city hall)Wind2070RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2070 | 77.5165 | 83.4908 | 89.784 | 96.0721 | 102.364
| Ottawa (city hall)Wind2075RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2075 | 77.5917 | 83.5912 | 89.91 | 96.2198 | 102.5384
| Ottawa (city hall)Wind2080RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2080 | 77.6668 | 83.6916 | 90.036 | 96.3674 | 102.7129
| Ottawa (city hall)Wind2085RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2085 | 77.6435 | 83.6498 | 89.9775 | 96.2952 | 102.6205
| Ottawa (city hall)Wind2090RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2090 | 77.6202 | 83.6079 | 89.919 | 96.223 | 102.5282
| Ottawa (city hall)Wind2095RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2095 | 77.6202 | 83.6079 | 89.919 | 96.223 | 102.5282
| Ottawa (city hall)Wind2100RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2100 | 77.6202 | 83.6079 | 89.919 | 96.223 | 102.5282
| Owen SoundIce Accretion2023RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2023 | 14.6858 | 17.552 | 21.189 | 23.991 | 26.7511
| Owen SoundIce Accretion2025RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2025 | 14.6956 | 17.5753 | 21.2275 | 24.0385 | 26.8128
| Owen SoundIce Accretion2030RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2030 | 14.7053 | 17.5985 | 21.266 | 24.0859 | 26.8745
| Owen SoundIce Accretion2035RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2035 | 14.7151 | 17.6217 | 21.3045 | 24.1334 | 26.9363
| Owen SoundIce Accretion2040RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2040 | 14.7248 | 17.645 | 21.343 | 24.1809 | 26.998
| Owen SoundIce Accretion2045RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2045 | 14.7345 | 17.6682 | 21.3815 | 24.2283 | 27.0598
| Owen SoundIce Accretion2050RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2050 | 14.6917 | 17.6426 | 21.378 | 24.2378 | 27.0845
| Owen SoundIce Accretion2055RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2055 | 14.6391 | 17.5938 | 21.336 | 24.1999 | 27.0474
| Owen SoundIce Accretion2060RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2060 | 14.5865 | 17.545 | 21.294 | 24.1619 | 27.0104
| Owen SoundIce Accretion2065RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2065 | 14.5339 | 17.4962 | 21.252 | 24.1239 | 26.9733
| Owen SoundIce Accretion2070RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2070 | 14.4813 | 17.4474 | 21.21 | 24.0859 | 26.9363
| Owen SoundIce Accretion2075RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2075 | 14.4277 | 17.4097 | 21.189 | 24.0741 | 26.9363
| Owen SoundIce Accretion2080RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2080 | 14.3741 | 17.3719 | 21.168 | 24.0622 | 26.9363
| Owen SoundIce Accretion2085RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2085 | 14.3205 | 17.3341 | 21.147 | 24.0504 | 26.9363
| Owen SoundIce Accretion2090RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2090 | 14.2669 | 17.2964 | 21.126 | 24.0385 | 26.9363
| Owen SoundIce Accretion2095RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2095 | 14.2134 | 17.2586 | 21.105 | 24.0266 | 26.9363
| Owen SoundIce Accretion2100RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2100 | 14.1598 | 17.2208 | 21.084 | 24.0148 | 26.9363
| Owen SoundIce Accretion2023RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2023 | 14.6858 | 17.552 | 21.189 | 23.991 | 26.7511
| Owen SoundIce Accretion2025RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2025 | 14.6956 | 17.5753 | 21.2275 | 24.0385 | 26.8128
| Owen SoundIce Accretion2030RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2030 | 14.7053 | 17.5985 | 21.266 | 24.0859 | 26.8745
| Owen SoundIce Accretion2035RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2035 | 14.7151 | 17.6217 | 21.3045 | 24.1334 | 26.9363
| Owen SoundIce Accretion2040RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2040 | 14.7248 | 17.645 | 21.343 | 24.1809 | 26.998
| Owen SoundIce Accretion2045RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2045 | 14.7345 | 17.6682 | 21.3815 | 24.2283 | 27.0598
| Owen SoundIce Accretion2050RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2050 | 14.6917 | 17.6426 | 21.378 | 24.2378 | 27.0845
| Owen SoundIce Accretion2055RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2055 | 14.6391 | 17.5938 | 21.336 | 24.1999 | 27.0474
| Owen SoundIce Accretion2060RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2060 | 14.5865 | 17.545 | 21.294 | 24.1619 | 27.0104
| Owen SoundIce Accretion2065RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2065 | 14.5339 | 17.4962 | 21.252 | 24.1239 | 26.9733
| Owen SoundIce Accretion2070RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2070 | 14.4813 | 17.4474 | 21.21 | 24.0859 | 26.9363
| Owen SoundIce Accretion2075RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2075 | 14.4009 | 17.3908 | 21.1785 | 24.0682 | 26.9363
| Owen SoundIce Accretion2080RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2080 | 14.3205 | 17.3341 | 21.147 | 24.0504 | 26.9363
| Owen SoundIce Accretion2085RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2085 | 14.2401 | 17.2775 | 21.1155 | 24.0326 | 26.9363
| Owen SoundIce Accretion2090RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2090 | 13.9114 | 16.9594 | 20.797 | 23.7142 | 26.6188
| Owen SoundIce Accretion2095RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2095 | 13.6629 | 16.6979 | 20.51 | 23.4136 | 26.3012
| Owen SoundIce Accretion2100RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2100 | 13.4145 | 16.4365 | 20.223 | 23.113 | 25.9837
| Owen SoundIce Accretion2023RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2023 | 14.6858 | 17.552 | 21.189 | 23.991 | 26.7511
| Owen SoundIce Accretion2025RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2025 | 14.7053 | 17.5985 | 21.266 | 24.0859 | 26.8745
| Owen SoundIce Accretion2030RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2030 | 14.7248 | 17.645 | 21.343 | 24.1809 | 26.998
| Owen SoundIce Accretion2035RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2035 | 14.7443 | 17.6914 | 21.42 | 24.2758 | 27.1215
| Owen SoundIce Accretion2040RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2040 | 14.6566 | 17.6101 | 21.35 | 24.2125 | 27.0598
| Owen SoundIce Accretion2045RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2045 | 14.5689 | 17.5288 | 21.28 | 24.1492 | 26.998
| Owen SoundIce Accretion2050RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2050 | 14.3741 | 17.3719 | 21.168 | 24.0622 | 26.9363
| Owen SoundIce Accretion2055RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2055 | 14.2669 | 17.2964 | 21.126 | 24.0385 | 26.9363
| Owen SoundIce Accretion2060RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2060 | 13.9114 | 16.9594 | 20.797 | 23.7142 | 26.6188
| Owen SoundIce Accretion2065RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2065 | 13.6629 | 16.6979 | 20.51 | 23.4136 | 26.3012
| Owen SoundIce Accretion2070RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2070 | 13.0443 | 16.024 | 19.761 | 22.6147 | 25.4457
| Owen SoundIce Accretion2075RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2075 | 12.6741 | 15.6115 | 19.299 | 22.1164 | 24.9077
| Owen SoundIce Accretion2080RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2080 | 12.304 | 15.199 | 18.837 | 21.618 | 24.3697
| Owen SoundIce Accretion2085RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2085 | 11.6756 | 14.4756 | 17.9865 | 20.657 | 23.3113
| Owen SoundIce Accretion2090RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2090 | 11.0473 | 13.7523 | 17.136 | 19.6959 | 22.2529
| Owen SoundIce Accretion2095RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2095 | 11.0473 | 13.7523 | 17.136 | 19.6959 | 22.2529
| Owen SoundIce Accretion2100RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2100 | 11.0473 | 13.7523 | 17.136 | 19.6959 | 22.2529
| Owen SoundWind2023RCP4.5 | Owen Sound | Wind | RCP4.5 | 2023 | 82.0308 | 88.2528 | 94.772 | 101.3247 | 107.8668
| Owen SoundWind2025RCP4.5 | Owen Sound | Wind | RCP4.5 | 2025 | 82.106 | 88.3456 | 94.8892 | 101.4603 | 108.0238
| Owen SoundWind2030RCP4.5 | Owen Sound | Wind | RCP4.5 | 2030 | 82.1812 | 88.4384 | 95.0063 | 101.5958 | 108.1809
| Owen SoundWind2035RCP4.5 | Owen Sound | Wind | RCP4.5 | 2035 | 82.2564 | 88.5311 | 95.1235 | 101.7313 | 108.3379
| Owen SoundWind2040RCP4.5 | Owen Sound | Wind | RCP4.5 | 2040 | 82.3316 | 88.6239 | 95.2407 | 101.8669 | 108.4949
| Owen SoundWind2045RCP4.5 | Owen Sound | Wind | RCP4.5 | 2045 | 82.4068 | 88.7167 | 95.3578 | 102.0024 | 108.652
| Owen SoundWind2050RCP4.5 | Owen Sound | Wind | RCP4.5 | 2050 | 82.4787 | 88.8006 | 95.456 | 102.1135 | 108.7765
| Owen SoundWind2055RCP4.5 | Owen Sound | Wind | RCP4.5 | 2055 | 82.4754 | 88.7918 | 95.437 | 102.0891 | 108.744
| Owen SoundWind2060RCP4.5 | Owen Sound | Wind | RCP4.5 | 2060 | 82.4722 | 88.7829 | 95.418 | 102.0647 | 108.7115
| Owen SoundWind2065RCP4.5 | Owen Sound | Wind | RCP4.5 | 2065 | 82.4689 | 88.7741 | 95.399 | 102.0403 | 108.6791
| Owen SoundWind2070RCP4.5 | Owen Sound | Wind | RCP4.5 | 2070 | 82.4656 | 88.7652 | 95.38 | 102.0159 | 108.6466
| Owen SoundWind2075RCP4.5 | Owen Sound | Wind | RCP4.5 | 2075 | 82.4834 | 88.7844 | 95.4006 | 102.038 | 108.67
| Owen SoundWind2080RCP4.5 | Owen Sound | Wind | RCP4.5 | 2080 | 82.5011 | 88.8035 | 95.4212 | 102.06 | 108.6935
| Owen SoundWind2085RCP4.5 | Owen Sound | Wind | RCP4.5 | 2085 | 82.5189 | 88.8227 | 95.4417 | 102.082 | 108.717
| Owen SoundWind2090RCP4.5 | Owen Sound | Wind | RCP4.5 | 2090 | 82.5367 | 88.8418 | 95.4623 | 102.104 | 108.7404
| Owen SoundWind2095RCP4.5 | Owen Sound | Wind | RCP4.5 | 2095 | 82.5545 | 88.861 | 95.4829 | 102.1261 | 108.7639
| Owen SoundWind2100RCP4.5 | Owen Sound | Wind | RCP4.5 | 2100 | 82.5722 | 88.8801 | 95.5035 | 102.1481 | 108.7873
| Owen SoundWind2023RCP6.0 | Owen Sound | Wind | RCP6.0 | 2023 | 82.0308 | 88.2528 | 94.772 | 101.3247 | 107.8668
| Owen SoundWind2025RCP6.0 | Owen Sound | Wind | RCP6.0 | 2025 | 82.106 | 88.3456 | 94.8892 | 101.4603 | 108.0238
| Owen SoundWind2030RCP6.0 | Owen Sound | Wind | RCP6.0 | 2030 | 82.1812 | 88.4384 | 95.0063 | 101.5958 | 108.1809
| Owen SoundWind2035RCP6.0 | Owen Sound | Wind | RCP6.0 | 2035 | 82.2564 | 88.5311 | 95.1235 | 101.7313 | 108.3379
| Owen SoundWind2040RCP6.0 | Owen Sound | Wind | RCP6.0 | 2040 | 82.3316 | 88.6239 | 95.2407 | 101.8669 | 108.4949
| Owen SoundWind2045RCP6.0 | Owen Sound | Wind | RCP6.0 | 2045 | 82.4068 | 88.7167 | 95.3578 | 102.0024 | 108.652
| Owen SoundWind2050RCP6.0 | Owen Sound | Wind | RCP6.0 | 2050 | 82.4787 | 88.8006 | 95.456 | 102.1135 | 108.7765
| Owen SoundWind2055RCP6.0 | Owen Sound | Wind | RCP6.0 | 2055 | 82.4754 | 88.7918 | 95.437 | 102.0891 | 108.744
| Owen SoundWind2060RCP6.0 | Owen Sound | Wind | RCP6.0 | 2060 | 82.4722 | 88.7829 | 95.418 | 102.0647 | 108.7115
| Owen SoundWind2065RCP6.0 | Owen Sound | Wind | RCP6.0 | 2065 | 82.4689 | 88.7741 | 95.399 | 102.0403 | 108.6791
| Owen SoundWind2070RCP6.0 | Owen Sound | Wind | RCP6.0 | 2070 | 82.4656 | 88.7652 | 95.38 | 102.0159 | 108.6466
| Owen SoundWind2075RCP6.0 | Owen Sound | Wind | RCP6.0 | 2075 | 82.4923 | 88.794 | 95.4109 | 102.049 | 108.6818
| Owen SoundWind2080RCP6.0 | Owen Sound | Wind | RCP6.0 | 2080 | 82.5189 | 88.8227 | 95.4417 | 102.082 | 108.717
| Owen SoundWind2085RCP6.0 | Owen Sound | Wind | RCP6.0 | 2085 | 82.5456 | 88.8514 | 95.4726 | 102.115 | 108.7522
| Owen SoundWind2090RCP6.0 | Owen Sound | Wind | RCP6.0 | 2090 | 82.7035 | 89.0391 | 95.6967 | 102.3683 | 109.0328
| Owen SoundWind2095RCP6.0 | Owen Sound | Wind | RCP6.0 | 2095 | 82.8347 | 89.1982 | 95.8898 | 102.5886 | 109.2783
| Owen SoundWind2100RCP6.0 | Owen Sound | Wind | RCP6.0 | 2100 | 82.966 | 89.3572 | 96.083 | 102.8088 | 109.5238
| Owen SoundWind2023RCP8.5 | Owen Sound | Wind | RCP8.5 | 2023 | 82.0308 | 88.2528 | 94.772 | 101.3247 | 107.8668
| Owen SoundWind2025RCP8.5 | Owen Sound | Wind | RCP8.5 | 2025 | 82.1812 | 88.4384 | 95.0063 | 101.5958 | 108.1809
| Owen SoundWind2030RCP8.5 | Owen Sound | Wind | RCP8.5 | 2030 | 82.3316 | 88.6239 | 95.2407 | 101.8669 | 108.4949
| Owen SoundWind2035RCP8.5 | Owen Sound | Wind | RCP8.5 | 2035 | 82.482 | 88.8094 | 95.475 | 102.1379 | 108.809
| Owen SoundWind2040RCP8.5 | Owen Sound | Wind | RCP8.5 | 2040 | 82.4765 | 88.7947 | 95.4433 | 102.0973 | 108.7549
| Owen SoundWind2045RCP8.5 | Owen Sound | Wind | RCP8.5 | 2045 | 82.4711 | 88.78 | 95.4117 | 102.0566 | 108.7007
| Owen SoundWind2050RCP8.5 | Owen Sound | Wind | RCP8.5 | 2050 | 82.5011 | 88.8035 | 95.4212 | 102.06 | 108.6935
| Owen SoundWind2055RCP8.5 | Owen Sound | Wind | RCP8.5 | 2055 | 82.5367 | 88.8418 | 95.4623 | 102.104 | 108.7404
| Owen SoundWind2060RCP8.5 | Owen Sound | Wind | RCP8.5 | 2060 | 82.7035 | 89.0391 | 95.6967 | 102.3683 | 109.0328
| Owen SoundWind2065RCP8.5 | Owen Sound | Wind | RCP8.5 | 2065 | 82.8347 | 89.1982 | 95.8898 | 102.5886 | 109.2783
| Owen SoundWind2070RCP8.5 | Owen Sound | Wind | RCP8.5 | 2070 | 83.0343 | 89.4397 | 96.178 | 102.9172 | 109.6501
| Owen SoundWind2075RCP8.5 | Owen Sound | Wind | RCP8.5 | 2075 | 83.1027 | 89.5221 | 96.273 | 103.0257 | 109.7765
| Owen SoundWind2080RCP8.5 | Owen Sound | Wind | RCP8.5 | 2080 | 83.1711 | 89.6046 | 96.368 | 103.1341 | 109.9028
| Owen SoundWind2085RCP8.5 | Owen Sound | Wind | RCP8.5 | 2085 | 83.4869 | 90.0287 | 96.9332 | 103.8151 | 110.6988
| Owen SoundWind2090RCP8.5 | Owen Sound | Wind | RCP8.5 | 2090 | 83.8027 | 90.4527 | 97.4985 | 104.4962 | 111.4948
| Owen SoundWind2095RCP8.5 | Owen Sound | Wind | RCP8.5 | 2095 | 83.8027 | 90.4527 | 97.4985 | 104.4962 | 111.4948
| Owen SoundWind2100RCP8.5 | Owen Sound | Wind | RCP8.5 | 2100 | 83.8027 | 90.4527 | 97.4985 | 104.4962 | 111.4948
| Pagwa RiverIce Accretion2023RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2023 | 9.3626 | 11.1676 | 13.468 | 15.2188 | 16.9697
| Pagwa RiverIce Accretion2025RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2025 | 9.4259 | 11.245 | 13.5612 | 15.3241 | 17.0898
| Pagwa RiverIce Accretion2030RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2030 | 9.4893 | 11.3223 | 13.6543 | 15.4294 | 17.2099
| Pagwa RiverIce Accretion2035RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2035 | 9.5526 | 11.3996 | 13.7475 | 15.5347 | 17.33
| Pagwa RiverIce Accretion2040RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2040 | 9.6159 | 11.477 | 13.8407 | 15.64 | 17.4502
| Pagwa RiverIce Accretion2045RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2045 | 9.6792 | 11.5543 | 13.9338 | 15.7452 | 17.5703
| Pagwa RiverIce Accretion2050RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2050 | 9.7624 | 11.6532 | 14.0504 | 15.877 | 17.7166
| Pagwa RiverIce Accretion2055RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2055 | 9.7823 | 11.6748 | 14.0738 | 15.9034 | 17.7428
| Pagwa RiverIce Accretion2060RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2060 | 9.8022 | 11.6964 | 14.0972 | 15.9298 | 17.769
| Pagwa RiverIce Accretion2065RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2065 | 9.8221 | 11.7179 | 14.1206 | 15.9563 | 17.7952
| Pagwa RiverIce Accretion2070RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2070 | 9.842 | 11.7395 | 14.144 | 15.9827 | 17.8214
| Pagwa RiverIce Accretion2075RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2075 | 9.8405 | 11.7413 | 14.1483 | 15.9901 | 17.8296
| Pagwa RiverIce Accretion2080RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2080 | 9.839 | 11.7431 | 14.1527 | 15.9974 | 17.8378
| Pagwa RiverIce Accretion2085RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2085 | 9.8375 | 11.7449 | 14.157 | 16.0048 | 17.846
| Pagwa RiverIce Accretion2090RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2090 | 9.836 | 11.7467 | 14.1613 | 16.0121 | 17.8542
| Pagwa RiverIce Accretion2095RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2095 | 9.8345 | 11.7485 | 14.1657 | 16.0194 | 17.8624
| Pagwa RiverIce Accretion2100RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2100 | 9.833 | 11.7503 | 14.17 | 16.0268 | 17.8706
| Pagwa RiverIce Accretion2023RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2023 | 9.3626 | 11.1676 | 13.468 | 15.2188 | 16.9697
| Pagwa RiverIce Accretion2025RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2025 | 9.4259 | 11.245 | 13.5612 | 15.3241 | 17.0898
| Pagwa RiverIce Accretion2030RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2030 | 9.4893 | 11.3223 | 13.6543 | 15.4294 | 17.2099
| Pagwa RiverIce Accretion2035RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2035 | 9.5526 | 11.3996 | 13.7475 | 15.5347 | 17.33
| Pagwa RiverIce Accretion2040RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2040 | 9.6159 | 11.477 | 13.8407 | 15.64 | 17.4502
| Pagwa RiverIce Accretion2045RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2045 | 9.6792 | 11.5543 | 13.9338 | 15.7452 | 17.5703
| Pagwa RiverIce Accretion2050RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2050 | 9.7624 | 11.6532 | 14.0504 | 15.877 | 17.7166
| Pagwa RiverIce Accretion2055RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2055 | 9.7823 | 11.6748 | 14.0738 | 15.9034 | 17.7428
| Pagwa RiverIce Accretion2060RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2060 | 9.8022 | 11.6964 | 14.0972 | 15.9298 | 17.769
| Pagwa RiverIce Accretion2065RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2065 | 9.8221 | 11.7179 | 14.1206 | 15.9563 | 17.7952
| Pagwa RiverIce Accretion2070RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2070 | 9.842 | 11.7395 | 14.144 | 15.9827 | 17.8214
| Pagwa RiverIce Accretion2075RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2075 | 9.8398 | 11.7422 | 14.1505 | 15.9937 | 17.8337
| Pagwa RiverIce Accretion2080RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2080 | 9.8375 | 11.7449 | 14.157 | 16.0048 | 17.846
| Pagwa RiverIce Accretion2085RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2085 | 9.8353 | 11.7476 | 14.1635 | 16.0158 | 17.8583
| Pagwa RiverIce Accretion2090RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2090 | 9.7395 | 11.6388 | 14.0357 | 15.875 | 17.7068
| Pagwa RiverIce Accretion2095RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2095 | 9.6461 | 11.5273 | 13.9013 | 15.7232 | 17.543
| Pagwa RiverIce Accretion2100RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2100 | 9.5526 | 11.4158 | 13.767 | 15.5714 | 17.3792
| Pagwa RiverIce Accretion2023RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2023 | 9.3626 | 11.1676 | 13.468 | 15.2188 | 16.9697
| Pagwa RiverIce Accretion2025RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2025 | 9.4893 | 11.3223 | 13.6543 | 15.4294 | 17.2099
| Pagwa RiverIce Accretion2030RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2030 | 9.6159 | 11.477 | 13.8407 | 15.64 | 17.4502
| Pagwa RiverIce Accretion2035RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2035 | 9.7425 | 11.6316 | 14.027 | 15.8505 | 17.6904
| Pagwa RiverIce Accretion2040RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2040 | 9.7757 | 11.6676 | 14.066 | 15.8946 | 17.7341
| Pagwa RiverIce Accretion2045RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2045 | 9.8089 | 11.7036 | 14.105 | 15.9386 | 17.7778
| Pagwa RiverIce Accretion2050RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2050 | 9.839 | 11.7431 | 14.1527 | 15.9974 | 17.8378
| Pagwa RiverIce Accretion2055RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2055 | 9.836 | 11.7467 | 14.1613 | 16.0121 | 17.8542
| Pagwa RiverIce Accretion2060RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2060 | 9.7395 | 11.6388 | 14.0357 | 15.875 | 17.7068
| Pagwa RiverIce Accretion2065RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2065 | 9.6461 | 11.5273 | 13.9013 | 15.7232 | 17.543
| Pagwa RiverIce Accretion2070RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2070 | 9.5254 | 11.3942 | 13.7497 | 15.5567 | 17.3628
| Pagwa RiverIce Accretion2075RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2075 | 9.4983 | 11.3727 | 13.7323 | 15.542 | 17.3464
| Pagwa RiverIce Accretion2080RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2080 | 9.4712 | 11.3511 | 13.715 | 15.5273 | 17.33
| Pagwa RiverIce Accretion2085RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2085 | 9.2812 | 11.1353 | 13.468 | 15.2556 | 17.0352
| Pagwa RiverIce Accretion2090RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2090 | 9.0912 | 10.9195 | 13.221 | 14.9838 | 16.7404
| Pagwa RiverIce Accretion2095RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2095 | 9.0912 | 10.9195 | 13.221 | 14.9838 | 16.7404
| Pagwa RiverIce Accretion2100RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2100 | 9.0912 | 10.9195 | 13.221 | 14.9838 | 16.7404
| Pagwa RiverWind2023RCP4.5 | Pagwa River | Wind | RCP4.5 | 2023 | 69.3549 | 74.6381 | 80.184 | 85.7455 | 91.3003
| Pagwa RiverWind2025RCP4.5 | Pagwa River | Wind | RCP4.5 | 2025 | 69.4712 | 74.7819 | 80.3627 | 85.9524 | 91.5374
| Pagwa RiverWind2030RCP4.5 | Pagwa River | Wind | RCP4.5 | 2030 | 69.5875 | 74.9258 | 80.5413 | 86.1593 | 91.7746
| Pagwa RiverWind2035RCP4.5 | Pagwa River | Wind | RCP4.5 | 2035 | 69.7038 | 75.0696 | 80.72 | 86.3661 | 92.0117
| Pagwa RiverWind2040RCP4.5 | Pagwa River | Wind | RCP4.5 | 2040 | 69.82 | 75.2134 | 80.8987 | 86.573 | 92.2488
| Pagwa RiverWind2045RCP4.5 | Pagwa River | Wind | RCP4.5 | 2045 | 69.9363 | 75.3573 | 81.0773 | 86.7799 | 92.4859
| Pagwa RiverWind2050RCP4.5 | Pagwa River | Wind | RCP4.5 | 2050 | 70.1852 | 75.6574 | 81.44 | 87.1973 | 92.9583
| Pagwa RiverWind2055RCP4.5 | Pagwa River | Wind | RCP4.5 | 2055 | 70.3179 | 75.8136 | 81.624 | 87.4079 | 93.1936
| Pagwa RiverWind2060RCP4.5 | Pagwa River | Wind | RCP4.5 | 2060 | 70.4505 | 75.9698 | 81.808 | 87.6184 | 93.4289
| Pagwa RiverWind2065RCP4.5 | Pagwa River | Wind | RCP4.5 | 2065 | 70.5831 | 76.1261 | 81.992 | 87.829 | 93.6642
| Pagwa RiverWind2070RCP4.5 | Pagwa River | Wind | RCP4.5 | 2070 | 70.7158 | 76.2823 | 82.176 | 88.0396 | 93.8995
| Pagwa RiverWind2075RCP4.5 | Pagwa River | Wind | RCP4.5 | 2075 | 70.7641 | 76.3381 | 82.24 | 88.1109 | 93.9786
| Pagwa RiverWind2080RCP4.5 | Pagwa River | Wind | RCP4.5 | 2080 | 70.8125 | 76.3939 | 82.304 | 88.1823 | 94.0576
| Pagwa RiverWind2085RCP4.5 | Pagwa River | Wind | RCP4.5 | 2085 | 70.8608 | 76.4497 | 82.368 | 88.2536 | 94.1366
| Pagwa RiverWind2090RCP4.5 | Pagwa River | Wind | RCP4.5 | 2090 | 70.9092 | 76.5055 | 82.432 | 88.3249 | 94.2157
| Pagwa RiverWind2095RCP4.5 | Pagwa River | Wind | RCP4.5 | 2095 | 70.9575 | 76.5613 | 82.496 | 88.3963 | 94.2947
| Pagwa RiverWind2100RCP4.5 | Pagwa River | Wind | RCP4.5 | 2100 | 71.0059 | 76.6171 | 82.56 | 88.4676 | 94.3738
| Pagwa RiverWind2023RCP6.0 | Pagwa River | Wind | RCP6.0 | 2023 | 69.3549 | 74.6381 | 80.184 | 85.7455 | 91.3003
| Pagwa RiverWind2025RCP6.0 | Pagwa River | Wind | RCP6.0 | 2025 | 69.4712 | 74.7819 | 80.3627 | 85.9524 | 91.5374
| Pagwa RiverWind2030RCP6.0 | Pagwa River | Wind | RCP6.0 | 2030 | 69.5875 | 74.9258 | 80.5413 | 86.1593 | 91.7746
| Pagwa RiverWind2035RCP6.0 | Pagwa River | Wind | RCP6.0 | 2035 | 69.7038 | 75.0696 | 80.72 | 86.3661 | 92.0117
| Pagwa RiverWind2040RCP6.0 | Pagwa River | Wind | RCP6.0 | 2040 | 69.82 | 75.2134 | 80.8987 | 86.573 | 92.2488
| Pagwa RiverWind2045RCP6.0 | Pagwa River | Wind | RCP6.0 | 2045 | 69.9363 | 75.3573 | 81.0773 | 86.7799 | 92.4859
| Pagwa RiverWind2050RCP6.0 | Pagwa River | Wind | RCP6.0 | 2050 | 70.1852 | 75.6574 | 81.44 | 87.1973 | 92.9583
| Pagwa RiverWind2055RCP6.0 | Pagwa River | Wind | RCP6.0 | 2055 | 70.3179 | 75.8136 | 81.624 | 87.4079 | 93.1936
| Pagwa RiverWind2060RCP6.0 | Pagwa River | Wind | RCP6.0 | 2060 | 70.4505 | 75.9698 | 81.808 | 87.6184 | 93.4289
| Pagwa RiverWind2065RCP6.0 | Pagwa River | Wind | RCP6.0 | 2065 | 70.5831 | 76.1261 | 81.992 | 87.829 | 93.6642
| Pagwa RiverWind2070RCP6.0 | Pagwa River | Wind | RCP6.0 | 2070 | 70.7158 | 76.2823 | 82.176 | 88.0396 | 93.8995
| Pagwa RiverWind2075RCP6.0 | Pagwa River | Wind | RCP6.0 | 2075 | 70.7883 | 76.366 | 82.272 | 88.1466 | 94.0181
| Pagwa RiverWind2080RCP6.0 | Pagwa River | Wind | RCP6.0 | 2080 | 70.8608 | 76.4497 | 82.368 | 88.2536 | 94.1366
| Pagwa RiverWind2085RCP6.0 | Pagwa River | Wind | RCP6.0 | 2085 | 70.9334 | 76.5334 | 82.464 | 88.3606 | 94.2552
| Pagwa RiverWind2090RCP6.0 | Pagwa River | Wind | RCP6.0 | 2090 | 71.0427 | 76.6494 | 82.584 | 88.4847 | 94.3859
| Pagwa RiverWind2095RCP6.0 | Pagwa River | Wind | RCP6.0 | 2095 | 71.0796 | 76.6816 | 82.608 | 88.5018 | 94.3981
| Pagwa RiverWind2100RCP6.0 | Pagwa River | Wind | RCP6.0 | 2100 | 71.1164 | 76.7138 | 82.632 | 88.519 | 94.4102
| Pagwa RiverWind2023RCP8.5 | Pagwa River | Wind | RCP8.5 | 2023 | 69.3549 | 74.6381 | 80.184 | 85.7455 | 91.3003
| Pagwa RiverWind2025RCP8.5 | Pagwa River | Wind | RCP8.5 | 2025 | 69.5875 | 74.9258 | 80.5413 | 86.1593 | 91.7746
| Pagwa RiverWind2030RCP8.5 | Pagwa River | Wind | RCP8.5 | 2030 | 69.82 | 75.2134 | 80.8987 | 86.573 | 92.2488
| Pagwa RiverWind2035RCP8.5 | Pagwa River | Wind | RCP8.5 | 2035 | 70.0526 | 75.5011 | 81.256 | 86.9867 | 92.723
| Pagwa RiverWind2040RCP8.5 | Pagwa River | Wind | RCP8.5 | 2040 | 70.2737 | 75.7615 | 81.5627 | 87.3377 | 93.1152
| Pagwa RiverWind2045RCP8.5 | Pagwa River | Wind | RCP8.5 | 2045 | 70.4947 | 76.0219 | 81.8693 | 87.6886 | 93.5074
| Pagwa RiverWind2050RCP8.5 | Pagwa River | Wind | RCP8.5 | 2050 | 70.8125 | 76.3939 | 82.304 | 88.1823 | 94.0576
| Pagwa RiverWind2055RCP8.5 | Pagwa River | Wind | RCP8.5 | 2055 | 70.9092 | 76.5055 | 82.432 | 88.3249 | 94.2157
| Pagwa RiverWind2060RCP8.5 | Pagwa River | Wind | RCP8.5 | 2060 | 71.0427 | 76.6494 | 82.584 | 88.4847 | 94.3859
| Pagwa RiverWind2065RCP8.5 | Pagwa River | Wind | RCP8.5 | 2065 | 71.0796 | 76.6816 | 82.608 | 88.5018 | 94.3981
| Pagwa RiverWind2070RCP8.5 | Pagwa River | Wind | RCP8.5 | 2070 | 71.1371 | 76.7386 | 82.6613 | 88.5503 | 94.4467
| Pagwa RiverWind2075RCP8.5 | Pagwa River | Wind | RCP8.5 | 2075 | 71.1579 | 76.7634 | 82.6907 | 88.5817 | 94.4832
| Pagwa RiverWind2080RCP8.5 | Pagwa River | Wind | RCP8.5 | 2080 | 71.1786 | 76.7882 | 82.72 | 88.6131 | 94.5197
| Pagwa RiverWind2085RCP8.5 | Pagwa River | Wind | RCP8.5 | 2085 | 71.3271 | 76.9631 | 82.928 | 88.8528 | 94.7842
| Pagwa RiverWind2090RCP8.5 | Pagwa River | Wind | RCP8.5 | 2090 | 71.4756 | 77.1379 | 83.136 | 89.0925 | 95.0486
| Pagwa RiverWind2095RCP8.5 | Pagwa River | Wind | RCP8.5 | 2095 | 71.4756 | 77.1379 | 83.136 | 89.0925 | 95.0486
| Pagwa RiverWind2100RCP8.5 | Pagwa River | Wind | RCP8.5 | 2100 | 71.4756 | 77.1379 | 83.136 | 89.0925 | 95.0486
| ParisIce Accretion2023RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
| ParisIce Accretion2025RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2025 | 20.3952 | 24.4642 | 29.605 | 33.5328 | 37.4661
| ParisIce Accretion2030RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2030 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
| ParisIce Accretion2035RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2035 | 20.3117 | 24.3895 | 29.535 | 33.4763 | 37.4031
| ParisIce Accretion2040RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2040 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
| ParisIce Accretion2045RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2045 | 20.2282 | 24.3148 | 29.465 | 33.4198 | 37.3401
| ParisIce Accretion2050RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2050 | 20.0571 | 24.153 | 29.316 | 33.2762 | 37.2028
| ParisIce Accretion2055RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2055 | 19.9276 | 24.0285 | 29.202 | 33.161 | 37.0969
| ParisIce Accretion2060RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2060 | 19.7982 | 23.904 | 29.088 | 33.0457 | 36.9911
| ParisIce Accretion2065RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2065 | 19.6688 | 23.7795 | 28.974 | 32.9305 | 36.8852
| ParisIce Accretion2070RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2070 | 19.5394 | 23.655 | 28.86 | 32.8152 | 36.7794
| ParisIce Accretion2075RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2075 | 19.4837 | 23.6135 | 28.84 | 32.8095 | 36.7857
| ParisIce Accretion2080RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2080 | 19.428 | 23.572 | 28.82 | 32.8039 | 36.792
| ParisIce Accretion2085RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2085 | 19.3724 | 23.5305 | 28.8 | 32.7982 | 36.7983
| ParisIce Accretion2090RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2090 | 19.3167 | 23.489 | 28.78 | 32.7926 | 36.8046
| ParisIce Accretion2095RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2095 | 19.261 | 23.4475 | 28.76 | 32.7869 | 36.8109
| ParisIce Accretion2100RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2100 | 19.2054 | 23.406 | 28.74 | 32.7813 | 36.8172
| ParisIce Accretion2023RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
| ParisIce Accretion2025RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2025 | 20.3952 | 24.4642 | 29.605 | 33.5328 | 37.4661
| ParisIce Accretion2030RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2030 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
| ParisIce Accretion2035RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2035 | 20.3117 | 24.3895 | 29.535 | 33.4763 | 37.4031
| ParisIce Accretion2040RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2040 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
| ParisIce Accretion2045RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2045 | 20.2282 | 24.3148 | 29.465 | 33.4198 | 37.3401
| ParisIce Accretion2050RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2050 | 20.0571 | 24.153 | 29.316 | 33.2762 | 37.2028
| ParisIce Accretion2055RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2055 | 19.9276 | 24.0285 | 29.202 | 33.161 | 37.0969
| ParisIce Accretion2060RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2060 | 19.7982 | 23.904 | 29.088 | 33.0457 | 36.9911
| ParisIce Accretion2065RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2065 | 19.6688 | 23.7795 | 28.974 | 32.9305 | 36.8852
| ParisIce Accretion2070RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2070 | 19.5394 | 23.655 | 28.86 | 32.8152 | 36.7794
| ParisIce Accretion2075RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2075 | 19.4559 | 23.5927 | 28.83 | 32.8067 | 36.7888
| ParisIce Accretion2080RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2080 | 19.3724 | 23.5305 | 28.8 | 32.7982 | 36.7983
| ParisIce Accretion2085RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2085 | 19.2889 | 23.4682 | 28.77 | 32.7898 | 36.8077
| ParisIce Accretion2090RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2090 | 18.7739 | 22.9412 | 28.21 | 32.2163 | 36.1998
| ParisIce Accretion2095RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2095 | 18.3425 | 22.4764 | 27.68 | 31.6513 | 35.5824
| ParisIce Accretion2100RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2100 | 17.9111 | 22.0116 | 27.15 | 31.0863 | 34.965
| ParisIce Accretion2023RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
| ParisIce Accretion2025RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2025 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
| ParisIce Accretion2030RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2030 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
| ParisIce Accretion2035RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2035 | 20.1865 | 24.2775 | 29.43 | 33.3915 | 37.3086
| ParisIce Accretion2040RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2040 | 19.9708 | 24.07 | 29.24 | 33.1994 | 37.1322
| ParisIce Accretion2045RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2045 | 19.7551 | 23.8625 | 29.05 | 33.0073 | 36.9558
| ParisIce Accretion2050RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2050 | 19.428 | 23.572 | 28.82 | 32.8039 | 36.792
| ParisIce Accretion2055RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2055 | 19.3167 | 23.489 | 28.78 | 32.7926 | 36.8046
| ParisIce Accretion2060RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2060 | 18.7739 | 22.9412 | 28.21 | 32.2163 | 36.1998
| ParisIce Accretion2065RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2065 | 18.3425 | 22.4764 | 27.68 | 31.6513 | 35.5824
| ParisIce Accretion2070RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2070 | 17.5353 | 21.6049 | 26.71 | 30.6117 | 34.461
| ParisIce Accretion2075RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2075 | 17.1596 | 21.1982 | 26.27 | 30.1371 | 33.957
| ParisIce Accretion2080RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2080 | 16.7838 | 20.7915 | 25.83 | 29.6625 | 33.453
| ParisIce Accretion2085RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2085 | 15.8549 | 19.7208 | 24.57 | 28.2387 | 31.9032
| ParisIce Accretion2090RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2090 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
| ParisIce Accretion2095RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2095 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
| ParisIce Accretion2100RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2100 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
| ParisWind2023RCP4.5 | Paris | Wind | RCP4.5 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
| ParisWind2025RCP4.5 | Paris | Wind | RCP4.5 | 2025 | 87.206 | 94.102 | 101.4083 | 108.6746 | 115.9494
| ParisWind2030RCP4.5 | Paris | Wind | RCP4.5 | 2030 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
| ParisWind2035RCP4.5 | Paris | Wind | RCP4.5 | 2035 | 87.3672 | 94.316 | 101.685 | 109.0063 | 116.337
| ParisWind2040RCP4.5 | Paris | Wind | RCP4.5 | 2040 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
| ParisWind2045RCP4.5 | Paris | Wind | RCP4.5 | 2045 | 87.5283 | 94.5299 | 101.9617 | 109.338 | 116.7246
| ParisWind2050RCP4.5 | Paris | Wind | RCP4.5 | 2050 | 87.678 | 94.7205 | 102.206 | 109.6258 | 117.0575
| ParisWind2055RCP4.5 | Paris | Wind | RCP4.5 | 2055 | 87.7471 | 94.8042 | 102.312 | 109.7478 | 117.1966
| ParisWind2060RCP4.5 | Paris | Wind | RCP4.5 | 2060 | 87.8162 | 94.8879 | 102.418 | 109.8697 | 117.3356
| ParisWind2065RCP4.5 | Paris | Wind | RCP4.5 | 2065 | 87.8852 | 94.9716 | 102.524 | 109.9917 | 117.4747
| ParisWind2070RCP4.5 | Paris | Wind | RCP4.5 | 2070 | 87.9543 | 95.0553 | 102.63 | 110.1137 | 117.6138
| ParisWind2075RCP4.5 | Paris | Wind | RCP4.5 | 2075 | 88.0407 | 95.1746 | 102.7917 | 110.3117 | 117.8494
| ParisWind2080RCP4.5 | Paris | Wind | RCP4.5 | 2080 | 88.127 | 95.294 | 102.9533 | 110.5096 | 118.085
| ParisWind2085RCP4.5 | Paris | Wind | RCP4.5 | 2085 | 88.2134 | 95.4134 | 103.115 | 110.7075 | 118.3206
| ParisWind2090RCP4.5 | Paris | Wind | RCP4.5 | 2090 | 88.2997 | 95.5327 | 103.2767 | 110.9055 | 118.5562
| ParisWind2095RCP4.5 | Paris | Wind | RCP4.5 | 2095 | 88.3861 | 95.6521 | 103.4383 | 111.1034 | 118.7918
| ParisWind2100RCP4.5 | Paris | Wind | RCP4.5 | 2100 | 88.4724 | 95.7714 | 103.6 | 111.3014 | 119.0274
| ParisWind2023RCP6.0 | Paris | Wind | RCP6.0 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
| ParisWind2025RCP6.0 | Paris | Wind | RCP6.0 | 2025 | 87.206 | 94.102 | 101.4083 | 108.6746 | 115.9494
| ParisWind2030RCP6.0 | Paris | Wind | RCP6.0 | 2030 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
| ParisWind2035RCP6.0 | Paris | Wind | RCP6.0 | 2035 | 87.3672 | 94.316 | 101.685 | 109.0063 | 116.337
| ParisWind2040RCP6.0 | Paris | Wind | RCP6.0 | 2040 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
| ParisWind2045RCP6.0 | Paris | Wind | RCP6.0 | 2045 | 87.5283 | 94.5299 | 101.9617 | 109.338 | 116.7246
| ParisWind2050RCP6.0 | Paris | Wind | RCP6.0 | 2050 | 87.678 | 94.7205 | 102.206 | 109.6258 | 117.0575
| ParisWind2055RCP6.0 | Paris | Wind | RCP6.0 | 2055 | 87.7471 | 94.8042 | 102.312 | 109.7478 | 117.1966
| ParisWind2060RCP6.0 | Paris | Wind | RCP6.0 | 2060 | 87.8162 | 94.8879 | 102.418 | 109.8697 | 117.3356
| ParisWind2065RCP6.0 | Paris | Wind | RCP6.0 | 2065 | 87.8852 | 94.9716 | 102.524 | 109.9917 | 117.4747
| ParisWind2070RCP6.0 | Paris | Wind | RCP6.0 | 2070 | 87.9543 | 95.0553 | 102.63 | 110.1137 | 117.6138
| ParisWind2075RCP6.0 | Paris | Wind | RCP6.0 | 2075 | 88.0838 | 95.2343 | 102.8725 | 110.4106 | 117.9672
| ParisWind2080RCP6.0 | Paris | Wind | RCP6.0 | 2080 | 88.2134 | 95.4134 | 103.115 | 110.7075 | 118.3206
| ParisWind2085RCP6.0 | Paris | Wind | RCP6.0 | 2085 | 88.3429 | 95.5924 | 103.3575 | 111.0045 | 118.674
| ParisWind2090RCP6.0 | Paris | Wind | RCP6.0 | 2090 | 88.8264 | 96.2271 | 104.18 | 111.9862 | 119.8216
| ParisWind2095RCP6.0 | Paris | Wind | RCP6.0 | 2095 | 89.1805 | 96.6828 | 104.76 | 112.671 | 120.6158
| ParisWind2100RCP6.0 | Paris | Wind | RCP6.0 | 2100 | 89.5345 | 97.1385 | 105.34 | 113.3558 | 121.41
| ParisWind2023RCP8.5 | Paris | Wind | RCP8.5 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
| ParisWind2025RCP8.5 | Paris | Wind | RCP8.5 | 2025 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
| ParisWind2030RCP8.5 | Paris | Wind | RCP8.5 | 2030 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
| ParisWind2035RCP8.5 | Paris | Wind | RCP8.5 | 2035 | 87.6089 | 94.6368 | 102.1 | 109.5038 | 116.9184
| ParisWind2040RCP8.5 | Paris | Wind | RCP8.5 | 2040 | 87.7241 | 94.7763 | 102.2767 | 109.7071 | 117.1502
| ParisWind2045RCP8.5 | Paris | Wind | RCP8.5 | 2045 | 87.8392 | 94.9158 | 102.4533 | 109.9104 | 117.382
| ParisWind2050RCP8.5 | Paris | Wind | RCP8.5 | 2050 | 88.127 | 95.294 | 102.9533 | 110.5096 | 118.085
| ParisWind2055RCP8.5 | Paris | Wind | RCP8.5 | 2055 | 88.2997 | 95.5327 | 103.2767 | 110.9055 | 118.5562
| ParisWind2060RCP8.5 | Paris | Wind | RCP8.5 | 2060 | 88.8264 | 96.2271 | 104.18 | 111.9862 | 119.8216
| ParisWind2065RCP8.5 | Paris | Wind | RCP8.5 | 2065 | 89.1805 | 96.6828 | 104.76 | 112.671 | 120.6158
| ParisWind2070RCP8.5 | Paris | Wind | RCP8.5 | 2070 | 89.759 | 97.4392 | 105.7367 | 113.8337 | 121.9724
| ParisWind2075RCP8.5 | Paris | Wind | RCP8.5 | 2075 | 89.9835 | 97.7399 | 106.1333 | 114.3117 | 122.5348
| ParisWind2080RCP8.5 | Paris | Wind | RCP8.5 | 2080 | 90.208 | 98.0406 | 106.53 | 114.7896 | 123.0972
| ParisWind2085RCP8.5 | Paris | Wind | RCP8.5 | 2085 | 90.6484 | 98.6172 | 107.285 | 115.6937 | 124.1517
| ParisWind2090RCP8.5 | Paris | Wind | RCP8.5 | 2090 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
| ParisWind2095RCP8.5 | Paris | Wind | RCP8.5 | 2095 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
| ParisWind2100RCP8.5 | Paris | Wind | RCP8.5 | 2100 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
| ParkhillIce Accretion2023RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2023 | 16.4331 | 19.7009 | 23.808 | 26.9573 | 30.0888
| ParkhillIce Accretion2025RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2025 | 16.4498 | 19.7341 | 23.868 | 27.0341 | 30.1846
| ParkhillIce Accretion2030RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2030 | 16.4665 | 19.7673 | 23.928 | 27.111 | 30.2803
| ParkhillIce Accretion2035RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2035 | 16.4832 | 19.8005 | 23.988 | 27.1878 | 30.3761
| ParkhillIce Accretion2040RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2040 | 16.4999 | 19.8337 | 24.048 | 27.2646 | 30.4718
| ParkhillIce Accretion2045RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2045 | 16.5166 | 19.8669 | 24.108 | 27.3415 | 30.5676
| ParkhillIce Accretion2050RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2050 | 16.4665 | 19.8523 | 24.1392 | 27.402 | 30.6634
| ParkhillIce Accretion2055RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2055 | 16.3997 | 19.8045 | 24.1104 | 27.3858 | 30.6634
| ParkhillIce Accretion2060RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2060 | 16.3329 | 19.7567 | 24.0816 | 27.3695 | 30.6634
| ParkhillIce Accretion2065RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2065 | 16.2661 | 19.7088 | 24.0528 | 27.3532 | 30.6634
| ParkhillIce Accretion2070RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2070 | 16.1993 | 19.661 | 24.024 | 27.337 | 30.6634
| ParkhillIce Accretion2075RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2075 | 16.1687 | 19.6478 | 24.036 | 27.3641 | 30.7087
| ParkhillIce Accretion2080RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2080 | 16.1381 | 19.6345 | 24.048 | 27.3912 | 30.7541
| ParkhillIce Accretion2085RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2085 | 16.1074 | 19.6212 | 24.06 | 27.4183 | 30.7994
| ParkhillIce Accretion2090RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2090 | 16.0768 | 19.6079 | 24.072 | 27.4454 | 30.8448
| ParkhillIce Accretion2095RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2095 | 16.0462 | 19.5946 | 24.084 | 27.4726 | 30.8902
| ParkhillIce Accretion2100RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2100 | 16.0156 | 19.5814 | 24.096 | 27.4997 | 30.9355
| ParkhillIce Accretion2023RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2023 | 16.4331 | 19.7009 | 23.808 | 26.9573 | 30.0888
| ParkhillIce Accretion2025RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2025 | 16.4498 | 19.7341 | 23.868 | 27.0341 | 30.1846
| ParkhillIce Accretion2030RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2030 | 16.4665 | 19.7673 | 23.928 | 27.111 | 30.2803
| ParkhillIce Accretion2035RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2035 | 16.4832 | 19.8005 | 23.988 | 27.1878 | 30.3761
| ParkhillIce Accretion2040RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2040 | 16.4999 | 19.8337 | 24.048 | 27.2646 | 30.4718
| ParkhillIce Accretion2045RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2045 | 16.5166 | 19.8669 | 24.108 | 27.3415 | 30.5676
| ParkhillIce Accretion2050RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2050 | 16.4665 | 19.8523 | 24.1392 | 27.402 | 30.6634
| ParkhillIce Accretion2055RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2055 | 16.3997 | 19.8045 | 24.1104 | 27.3858 | 30.6634
| ParkhillIce Accretion2060RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2060 | 16.3329 | 19.7567 | 24.0816 | 27.3695 | 30.6634
| ParkhillIce Accretion2065RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2065 | 16.2661 | 19.7088 | 24.0528 | 27.3532 | 30.6634
| ParkhillIce Accretion2070RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2070 | 16.1993 | 19.661 | 24.024 | 27.337 | 30.6634
| ParkhillIce Accretion2075RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2075 | 16.1534 | 19.6411 | 24.042 | 27.3776 | 30.7314
| ParkhillIce Accretion2080RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2080 | 16.1074 | 19.6212 | 24.06 | 27.4183 | 30.7994
| ParkhillIce Accretion2085RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2085 | 16.0615 | 19.6013 | 24.078 | 27.459 | 30.8675
| ParkhillIce Accretion2090RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2090 | 15.8152 | 19.3822 | 23.888 | 27.2918 | 30.7138
| ParkhillIce Accretion2095RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2095 | 15.6148 | 19.183 | 23.68 | 27.0838 | 30.492
| ParkhillIce Accretion2100RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2100 | 15.4144 | 18.9838 | 23.472 | 26.8759 | 30.2702
| ParkhillIce Accretion2023RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2023 | 16.4331 | 19.7009 | 23.808 | 26.9573 | 30.0888
| ParkhillIce Accretion2025RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2025 | 16.4665 | 19.7673 | 23.928 | 27.111 | 30.2803
| ParkhillIce Accretion2030RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2030 | 16.4999 | 19.8337 | 24.048 | 27.2646 | 30.4718
| ParkhillIce Accretion2035RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2035 | 16.5333 | 19.9001 | 24.168 | 27.4183 | 30.6634
| ParkhillIce Accretion2040RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2040 | 16.422 | 19.8204 | 24.12 | 27.3912 | 30.6634
| ParkhillIce Accretion2045RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2045 | 16.3106 | 19.7407 | 24.072 | 27.3641 | 30.6634
| ParkhillIce Accretion2050RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2050 | 16.1381 | 19.6345 | 24.048 | 27.3912 | 30.7541
| ParkhillIce Accretion2055RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2055 | 16.0768 | 19.6079 | 24.072 | 27.4454 | 30.8448
| ParkhillIce Accretion2060RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2060 | 15.8152 | 19.3822 | 23.888 | 27.2918 | 30.7138
| ParkhillIce Accretion2065RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2065 | 15.6148 | 19.183 | 23.68 | 27.0838 | 30.492
| ParkhillIce Accretion2070RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2070 | 15.0525 | 18.5787 | 23.016 | 26.3787 | 29.7259
| ParkhillIce Accretion2075RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2075 | 14.6907 | 18.1737 | 22.56 | 25.8815 | 29.1816
| ParkhillIce Accretion2080RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2080 | 14.3289 | 17.7686 | 22.104 | 25.3843 | 28.6373
| ParkhillIce Accretion2085RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2085 | 13.5773 | 16.8822 | 21.048 | 24.2046 | 27.337
| ParkhillIce Accretion2090RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2090 | 12.8258 | 15.9958 | 19.992 | 23.0249 | 26.0366
| ParkhillIce Accretion2095RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2095 | 12.8258 | 15.9958 | 19.992 | 23.0249 | 26.0366
| ParkhillIce Accretion2100RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2100 | 12.8258 | 15.9958 | 19.992 | 23.0249 | 26.0366
| ParkhillWind2023RCP4.5 | Parkhill | Wind | RCP4.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| ParkhillWind2025RCP4.5 | Parkhill | Wind | RCP4.5 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
| ParkhillWind2030RCP4.5 | Parkhill | Wind | RCP4.5 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| ParkhillWind2035RCP4.5 | Parkhill | Wind | RCP4.5 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
| ParkhillWind2040RCP4.5 | Parkhill | Wind | RCP4.5 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| ParkhillWind2045RCP4.5 | Parkhill | Wind | RCP4.5 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
| ParkhillWind2050RCP4.5 | Parkhill | Wind | RCP4.5 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
| ParkhillWind2055RCP4.5 | Parkhill | Wind | RCP4.5 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
| ParkhillWind2060RCP4.5 | Parkhill | Wind | RCP4.5 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
| ParkhillWind2065RCP4.5 | Parkhill | Wind | RCP4.5 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
| ParkhillWind2070RCP4.5 | Parkhill | Wind | RCP4.5 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
| ParkhillWind2075RCP4.5 | Parkhill | Wind | RCP4.5 | 2075 | 86.3504 | 93.3577 | 100.8387 | 108.226 | 115.6228
| ParkhillWind2080RCP4.5 | Parkhill | Wind | RCP4.5 | 2080 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
| ParkhillWind2085RCP4.5 | Parkhill | Wind | RCP4.5 | 2085 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
| ParkhillWind2090RCP4.5 | Parkhill | Wind | RCP4.5 | 2090 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
| ParkhillWind2095RCP4.5 | Parkhill | Wind | RCP4.5 | 2095 | 86.7678 | 93.9167 | 101.5705 | 109.1068 | 116.6655
| ParkhillWind2100RCP4.5 | Parkhill | Wind | RCP4.5 | 2100 | 86.8722 | 94.0565 | 101.7534 | 109.327 | 116.9262
| ParkhillWind2023RCP6.0 | Parkhill | Wind | RCP6.0 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| ParkhillWind2025RCP6.0 | Parkhill | Wind | RCP6.0 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
| ParkhillWind2030RCP6.0 | Parkhill | Wind | RCP6.0 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| ParkhillWind2035RCP6.0 | Parkhill | Wind | RCP6.0 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
| ParkhillWind2040RCP6.0 | Parkhill | Wind | RCP6.0 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| ParkhillWind2045RCP6.0 | Parkhill | Wind | RCP6.0 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
| ParkhillWind2050RCP6.0 | Parkhill | Wind | RCP6.0 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
| ParkhillWind2055RCP6.0 | Parkhill | Wind | RCP6.0 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
| ParkhillWind2060RCP6.0 | Parkhill | Wind | RCP6.0 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
| ParkhillWind2065RCP6.0 | Parkhill | Wind | RCP6.0 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
| ParkhillWind2070RCP6.0 | Parkhill | Wind | RCP6.0 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
| ParkhillWind2075RCP6.0 | Parkhill | Wind | RCP6.0 | 2075 | 86.4026 | 93.4276 | 100.9302 | 108.3361 | 115.7531
| ParkhillWind2080RCP6.0 | Parkhill | Wind | RCP6.0 | 2080 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
| ParkhillWind2085RCP6.0 | Parkhill | Wind | RCP6.0 | 2085 | 86.7157 | 93.8469 | 101.479 | 108.9967 | 116.5351
| ParkhillWind2090RCP6.0 | Parkhill | Wind | RCP6.0 | 2090 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
| ParkhillWind2095RCP6.0 | Parkhill | Wind | RCP6.0 | 2095 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
| ParkhillWind2100RCP6.0 | Parkhill | Wind | RCP6.0 | 2100 | 87.7861 | 95.1502 | 103.0568 | 110.8265 | 118.6131
| ParkhillWind2023RCP8.5 | Parkhill | Wind | RCP8.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| ParkhillWind2025RCP8.5 | Parkhill | Wind | RCP8.5 | 2025 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| ParkhillWind2030RCP8.5 | Parkhill | Wind | RCP8.5 | 2030 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| ParkhillWind2035RCP8.5 | Parkhill | Wind | RCP8.5 | 2035 | 86.0768 | 93.0084 | 100.3912 | 107.7017 | 115.0269
| ParkhillWind2040RCP8.5 | Parkhill | Wind | RCP8.5 | 2040 | 86.1332 | 93.0782 | 100.4794 | 107.8031 | 115.1386
| ParkhillWind2045RCP8.5 | Parkhill | Wind | RCP8.5 | 2045 | 86.1896 | 93.1481 | 100.5676 | 107.9044 | 115.2504
| ParkhillWind2050RCP8.5 | Parkhill | Wind | RCP8.5 | 2050 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
| ParkhillWind2055RCP8.5 | Parkhill | Wind | RCP8.5 | 2055 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
| ParkhillWind2060RCP8.5 | Parkhill | Wind | RCP8.5 | 2060 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
| ParkhillWind2065RCP8.5 | Parkhill | Wind | RCP8.5 | 2065 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
| ParkhillWind2070RCP8.5 | Parkhill | Wind | RCP8.5 | 2070 | 88.0541 | 95.5026 | 103.5207 | 111.3788 | 119.2611
| ParkhillWind2075RCP8.5 | Parkhill | Wind | RCP8.5 | 2075 | 88.322 | 95.855 | 103.9845 | 111.9311 | 119.9091
| ParkhillWind2080RCP8.5 | Parkhill | Wind | RCP8.5 | 2080 | 88.59 | 96.2074 | 104.4484 | 112.4833 | 120.5571
| ParkhillWind2085RCP8.5 | Parkhill | Wind | RCP8.5 | 2085 | 88.9454 | 96.6585 | 105.0217 | 113.1649 | 121.3447
| ParkhillWind2090RCP8.5 | Parkhill | Wind | RCP8.5 | 2090 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| ParkhillWind2095RCP8.5 | Parkhill | Wind | RCP8.5 | 2095 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| ParkhillWind2100RCP8.5 | Parkhill | Wind | RCP8.5 | 2100 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| Parry SoundIce Accretion2023RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2023 | 14.0839 | 16.8324 | 20.32 | 22.9842 | 25.6536
| Parry SoundIce Accretion2025RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2025 | 14.1396 | 16.9126 | 20.4333 | 23.1198 | 25.8132
| Parry SoundIce Accretion2030RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2030 | 14.1953 | 16.9929 | 20.5467 | 23.2554 | 25.9728
| Parry SoundIce Accretion2035RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2035 | 14.2509 | 17.0731 | 20.66 | 23.391 | 26.1324
| Parry SoundIce Accretion2040RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2040 | 14.3066 | 17.1533 | 20.7733 | 23.5266 | 26.292
| Parry SoundIce Accretion2045RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2045 | 14.3623 | 17.2336 | 20.8867 | 23.6622 | 26.4516
| Parry SoundIce Accretion2050RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2050 | 14.4179 | 17.3304 | 21.032 | 23.843 | 26.6717
| Parry SoundIce Accretion2055RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2055 | 14.4179 | 17.347 | 21.064 | 23.8882 | 26.7322
| Parry SoundIce Accretion2060RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2060 | 14.4179 | 17.3636 | 21.096 | 23.9334 | 26.7926
| Parry SoundIce Accretion2065RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2065 | 14.4179 | 17.3802 | 21.128 | 23.9786 | 26.8531
| Parry SoundIce Accretion2070RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2070 | 14.4179 | 17.3968 | 21.16 | 24.0238 | 26.9136
| Parry SoundIce Accretion2075RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2075 | 14.4643 | 17.466 | 21.26 | 24.1443 | 27.0522
| Parry SoundIce Accretion2080RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2080 | 14.5107 | 17.5351 | 21.36 | 24.2649 | 27.1908
| Parry SoundIce Accretion2085RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2085 | 14.5571 | 17.6043 | 21.46 | 24.3854 | 27.3294
| Parry SoundIce Accretion2090RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2090 | 14.6035 | 17.6735 | 21.56 | 24.5059 | 27.468
| Parry SoundIce Accretion2095RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2095 | 14.6499 | 17.7426 | 21.66 | 24.6265 | 27.6066
| Parry SoundIce Accretion2100RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2100 | 14.6963 | 17.8118 | 21.76 | 24.747 | 27.7452
| Parry SoundIce Accretion2023RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2023 | 14.0839 | 16.8324 | 20.32 | 22.9842 | 25.6536
| Parry SoundIce Accretion2025RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2025 | 14.1396 | 16.9126 | 20.4333 | 23.1198 | 25.8132
| Parry SoundIce Accretion2030RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2030 | 14.1953 | 16.9929 | 20.5467 | 23.2554 | 25.9728
| Parry SoundIce Accretion2035RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2035 | 14.2509 | 17.0731 | 20.66 | 23.391 | 26.1324
| Parry SoundIce Accretion2040RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2040 | 14.3066 | 17.1533 | 20.7733 | 23.5266 | 26.292
| Parry SoundIce Accretion2045RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2045 | 14.3623 | 17.2336 | 20.8867 | 23.6622 | 26.4516
| Parry SoundIce Accretion2050RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2050 | 14.4179 | 17.3304 | 21.032 | 23.843 | 26.6717
| Parry SoundIce Accretion2055RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2055 | 14.4179 | 17.347 | 21.064 | 23.8882 | 26.7322
| Parry SoundIce Accretion2060RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2060 | 14.4179 | 17.3636 | 21.096 | 23.9334 | 26.7926
| Parry SoundIce Accretion2065RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2065 | 14.4179 | 17.3802 | 21.128 | 23.9786 | 26.8531
| Parry SoundIce Accretion2070RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2070 | 14.4179 | 17.3968 | 21.16 | 24.0238 | 26.9136
| Parry SoundIce Accretion2075RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2075 | 14.4875 | 17.5005 | 21.31 | 24.2046 | 27.1215
| Parry SoundIce Accretion2080RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2080 | 14.5571 | 17.6043 | 21.46 | 24.3854 | 27.3294
| Parry SoundIce Accretion2085RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2085 | 14.6267 | 17.7081 | 21.61 | 24.5662 | 27.5373
| Parry SoundIce Accretion2090RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2090 | 14.6592 | 17.8063 | 21.78 | 24.7997 | 27.8208
| Parry SoundIce Accretion2095RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2095 | 14.622 | 17.8007 | 21.8 | 24.8525 | 27.8964
| Parry SoundIce Accretion2100RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2100 | 14.5849 | 17.7952 | 21.82 | 24.9052 | 27.972
| Parry SoundIce Accretion2023RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2023 | 14.0839 | 16.8324 | 20.32 | 22.9842 | 25.6536
| Parry SoundIce Accretion2025RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2025 | 14.1953 | 16.9929 | 20.5467 | 23.2554 | 25.9728
| Parry SoundIce Accretion2030RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2030 | 14.3066 | 17.1533 | 20.7733 | 23.5266 | 26.292
| Parry SoundIce Accretion2035RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2035 | 14.4179 | 17.3138 | 21 | 23.7978 | 26.6112
| Parry SoundIce Accretion2040RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2040 | 14.4179 | 17.3415 | 21.0533 | 23.8731 | 26.712
| Parry SoundIce Accretion2045RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2045 | 14.4179 | 17.3691 | 21.1067 | 23.9485 | 26.8128
| Parry SoundIce Accretion2050RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2050 | 14.5107 | 17.5351 | 21.36 | 24.2649 | 27.1908
| Parry SoundIce Accretion2055RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2055 | 14.6035 | 17.6735 | 21.56 | 24.5059 | 27.468
| Parry SoundIce Accretion2060RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2060 | 14.6592 | 17.8063 | 21.78 | 24.7997 | 27.8208
| Parry SoundIce Accretion2065RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2065 | 14.622 | 17.8007 | 21.8 | 24.8525 | 27.8964
| Parry SoundIce Accretion2070RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2070 | 14.3205 | 17.4964 | 21.4867 | 24.5361 | 27.5688
| Parry SoundIce Accretion2075RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2075 | 14.0561 | 17.1976 | 21.1533 | 24.1669 | 27.1656
| Parry SoundIce Accretion2080RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2080 | 13.7917 | 16.8988 | 20.82 | 23.7978 | 26.7624
| Parry SoundIce Accretion2085RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2085 | 13.235 | 16.2514 | 20.06 | 22.9616 | 25.8426
| Parry SoundIce Accretion2090RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2090 | 12.6783 | 15.604 | 19.3 | 22.1254 | 24.9228
| Parry SoundIce Accretion2095RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2095 | 12.6783 | 15.604 | 19.3 | 22.1254 | 24.9228
| Parry SoundIce Accretion2100RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2100 | 12.6783 | 15.604 | 19.3 | 22.1254 | 24.9228
| Parry SoundWind2023RCP4.5 | Parry Sound | Wind | RCP4.5 | 2023 | 78.1875 | 84.2524 | 90.648 | 97.0319 | 103.4105
| Parry SoundWind2025RCP4.5 | Parry Sound | Wind | RCP4.5 | 2025 | 78.26 | 84.3417 | 90.7575 | 97.1587 | 103.5559
| Parry SoundWind2030RCP4.5 | Parry Sound | Wind | RCP4.5 | 2030 | 78.3325 | 84.431 | 90.867 | 97.2855 | 103.7012
| Parry SoundWind2035RCP4.5 | Parry Sound | Wind | RCP4.5 | 2035 | 78.4051 | 84.5203 | 90.9765 | 97.4123 | 103.8466
| Parry SoundWind2040RCP4.5 | Parry Sound | Wind | RCP4.5 | 2040 | 78.4776 | 84.6095 | 91.086 | 97.5391 | 103.9919
| Parry SoundWind2045RCP4.5 | Parry Sound | Wind | RCP4.5 | 2045 | 78.5501 | 84.6988 | 91.1955 | 97.6659 | 104.1373
| Parry SoundWind2050RCP4.5 | Parry Sound | Wind | RCP4.5 | 2050 | 78.6942 | 84.8818 | 91.4256 | 97.9352 | 104.4489
| Parry SoundWind2055RCP4.5 | Parry Sound | Wind | RCP4.5 | 2055 | 78.7657 | 84.9756 | 91.5462 | 98.0777 | 104.6151
| Parry SoundWind2060RCP4.5 | Parry Sound | Wind | RCP4.5 | 2060 | 78.8372 | 85.0693 | 91.6668 | 98.2202 | 104.7813
| Parry SoundWind2065RCP4.5 | Parry Sound | Wind | RCP4.5 | 2065 | 78.9087 | 85.1631 | 91.7874 | 98.3627 | 104.9475
| Parry SoundWind2070RCP4.5 | Parry Sound | Wind | RCP4.5 | 2070 | 78.9801 | 85.2568 | 91.908 | 98.5053 | 105.1137
| Parry SoundWind2075RCP4.5 | Parry Sound | Wind | RCP4.5 | 2075 | 78.9685 | 85.2471 | 91.902 | 98.5037 | 105.1154
| Parry SoundWind2080RCP4.5 | Parry Sound | Wind | RCP4.5 | 2080 | 78.9568 | 85.2373 | 91.896 | 98.5021 | 105.1171
| Parry SoundWind2085RCP4.5 | Parry Sound | Wind | RCP4.5 | 2085 | 78.9452 | 85.2275 | 91.89 | 98.5005 | 105.1188
| Parry SoundWind2090RCP4.5 | Parry Sound | Wind | RCP4.5 | 2090 | 78.9335 | 85.2178 | 91.884 | 98.4989 | 105.1205
| Parry SoundWind2095RCP4.5 | Parry Sound | Wind | RCP4.5 | 2095 | 78.9219 | 85.208 | 91.878 | 98.4972 | 105.1222
| Parry SoundWind2100RCP4.5 | Parry Sound | Wind | RCP4.5 | 2100 | 78.9102 | 85.1982 | 91.872 | 98.4956 | 105.124
| Parry SoundWind2023RCP6.0 | Parry Sound | Wind | RCP6.0 | 2023 | 78.1875 | 84.2524 | 90.648 | 97.0319 | 103.4105
| Parry SoundWind2025RCP6.0 | Parry Sound | Wind | RCP6.0 | 2025 | 78.26 | 84.3417 | 90.7575 | 97.1587 | 103.5559
| Parry SoundWind2030RCP6.0 | Parry Sound | Wind | RCP6.0 | 2030 | 78.3325 | 84.431 | 90.867 | 97.2855 | 103.7012
| Parry SoundWind2035RCP6.0 | Parry Sound | Wind | RCP6.0 | 2035 | 78.4051 | 84.5203 | 90.9765 | 97.4123 | 103.8466
| Parry SoundWind2040RCP6.0 | Parry Sound | Wind | RCP6.0 | 2040 | 78.4776 | 84.6095 | 91.086 | 97.5391 | 103.9919
| Parry SoundWind2045RCP6.0 | Parry Sound | Wind | RCP6.0 | 2045 | 78.5501 | 84.6988 | 91.1955 | 97.6659 | 104.1373
| Parry SoundWind2050RCP6.0 | Parry Sound | Wind | RCP6.0 | 2050 | 78.6942 | 84.8818 | 91.4256 | 97.9352 | 104.4489
| Parry SoundWind2055RCP6.0 | Parry Sound | Wind | RCP6.0 | 2055 | 78.7657 | 84.9756 | 91.5462 | 98.0777 | 104.6151
| Parry SoundWind2060RCP6.0 | Parry Sound | Wind | RCP6.0 | 2060 | 78.8372 | 85.0693 | 91.6668 | 98.2202 | 104.7813
| Parry SoundWind2065RCP6.0 | Parry Sound | Wind | RCP6.0 | 2065 | 78.9087 | 85.1631 | 91.7874 | 98.3627 | 104.9475
| Parry SoundWind2070RCP6.0 | Parry Sound | Wind | RCP6.0 | 2070 | 78.9801 | 85.2568 | 91.908 | 98.5053 | 105.1137
| Parry SoundWind2075RCP6.0 | Parry Sound | Wind | RCP6.0 | 2075 | 78.9627 | 85.2422 | 91.899 | 98.5029 | 105.1163
| Parry SoundWind2080RCP6.0 | Parry Sound | Wind | RCP6.0 | 2080 | 78.9452 | 85.2275 | 91.89 | 98.5005 | 105.1188
| Parry SoundWind2085RCP6.0 | Parry Sound | Wind | RCP6.0 | 2085 | 78.9277 | 85.2129 | 91.881 | 98.498 | 105.1214
| Parry SoundWind2090RCP6.0 | Parry Sound | Wind | RCP6.0 | 2090 | 78.9957 | 85.3126 | 92.022 | 98.6722 | 105.3292
| Parry SoundWind2095RCP6.0 | Parry Sound | Wind | RCP6.0 | 2095 | 79.0812 | 85.427 | 92.172 | 98.8487 | 105.5344
| Parry SoundWind2100RCP6.0 | Parry Sound | Wind | RCP6.0 | 2100 | 79.1667 | 85.5414 | 92.322 | 99.0253 | 105.7396
| Parry SoundWind2023RCP8.5 | Parry Sound | Wind | RCP8.5 | 2023 | 78.1875 | 84.2524 | 90.648 | 97.0319 | 103.4105
| Parry SoundWind2025RCP8.5 | Parry Sound | Wind | RCP8.5 | 2025 | 78.3325 | 84.431 | 90.867 | 97.2855 | 103.7012
| Parry SoundWind2030RCP8.5 | Parry Sound | Wind | RCP8.5 | 2030 | 78.4776 | 84.6095 | 91.086 | 97.5391 | 103.9919
| Parry SoundWind2035RCP8.5 | Parry Sound | Wind | RCP8.5 | 2035 | 78.6227 | 84.7881 | 91.305 | 97.7927 | 104.2826
| Parry SoundWind2040RCP8.5 | Parry Sound | Wind | RCP8.5 | 2040 | 78.7418 | 84.9443 | 91.506 | 98.0302 | 104.5597
| Parry SoundWind2045RCP8.5 | Parry Sound | Wind | RCP8.5 | 2045 | 78.861 | 85.1006 | 91.707 | 98.2677 | 104.8367
| Parry SoundWind2050RCP8.5 | Parry Sound | Wind | RCP8.5 | 2050 | 78.9568 | 85.2373 | 91.896 | 98.5021 | 105.1171
| Parry SoundWind2055RCP8.5 | Parry Sound | Wind | RCP8.5 | 2055 | 78.9335 | 85.2178 | 91.884 | 98.4989 | 105.1205
| Parry SoundWind2060RCP8.5 | Parry Sound | Wind | RCP8.5 | 2060 | 78.9957 | 85.3126 | 92.022 | 98.6722 | 105.3292
| Parry SoundWind2065RCP8.5 | Parry Sound | Wind | RCP8.5 | 2065 | 79.0812 | 85.427 | 92.172 | 98.8487 | 105.5344
| Parry SoundWind2070RCP8.5 | Parry Sound | Wind | RCP8.5 | 2070 | 79.1485 | 85.5581 | 92.388 | 99.1312 | 105.8866
| Parry SoundWind2075RCP8.5 | Parry Sound | Wind | RCP8.5 | 2075 | 79.1304 | 85.5749 | 92.454 | 99.2372 | 106.0337
| Parry SoundWind2080RCP8.5 | Parry Sound | Wind | RCP8.5 | 2080 | 79.1123 | 85.5916 | 92.52 | 99.3431 | 106.1807
| Parry SoundWind2085RCP8.5 | Parry Sound | Wind | RCP8.5 | 2085 | 79.3454 | 85.9013 | 92.916 | 99.815 | 106.7296
| Parry SoundWind2090RCP8.5 | Parry Sound | Wind | RCP8.5 | 2090 | 79.5785 | 86.211 | 93.312 | 100.2868 | 107.2786
| Parry SoundWind2095RCP8.5 | Parry Sound | Wind | RCP8.5 | 2095 | 79.5785 | 86.211 | 93.312 | 100.2868 | 107.2786
| Parry SoundWind2100RCP8.5 | Parry Sound | Wind | RCP8.5 | 2100 | 79.5785 | 86.211 | 93.312 | 100.2868 | 107.2786
| Pelham (Fonthill)Ice Accretion2023RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
| Pelham (Fonthill)Ice Accretion2025RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2025 | 21.9182 | 26.3121 | 31.8773 | 36.1299 | 40.3738
| Pelham (Fonthill)Ice Accretion2030RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2030 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
| Pelham (Fonthill)Ice Accretion2035RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2035 | 21.7104 | 26.0819 | 31.632 | 35.8526 | 40.0781
| Pelham (Fonthill)Ice Accretion2040RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2040 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
| Pelham (Fonthill)Ice Accretion2045RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2045 | 21.5026 | 25.8517 | 31.3867 | 35.5754 | 39.7824
| Pelham (Fonthill)Ice Accretion2050RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2050 | 20.9221 | 25.2001 | 30.6368 | 34.7425 | 38.8765
| Pelham (Fonthill)Ice Accretion2055RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2055 | 20.4456 | 24.6636 | 30.0096 | 34.0483 | 38.1185
| Pelham (Fonthill)Ice Accretion2060RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2060 | 19.9691 | 24.1271 | 29.3824 | 33.354 | 37.3605
| Pelham (Fonthill)Ice Accretion2065RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2065 | 19.4926 | 23.5906 | 28.7552 | 32.6597 | 36.6025
| Pelham (Fonthill)Ice Accretion2070RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2070 | 19.0161 | 23.0541 | 28.128 | 31.9654 | 35.8445
| Pelham (Fonthill)Ice Accretion2075RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2075 | 18.8379 | 22.8682 | 27.9307 | 31.7605 | 35.6294
| Pelham (Fonthill)Ice Accretion2080RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2080 | 18.6598 | 22.6822 | 27.7333 | 31.5556 | 35.4144
| Pelham (Fonthill)Ice Accretion2085RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2085 | 18.4817 | 22.4963 | 27.536 | 31.3507 | 35.1994
| Pelham (Fonthill)Ice Accretion2090RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2090 | 18.3035 | 22.3104 | 27.3387 | 31.1458 | 34.9843
| Pelham (Fonthill)Ice Accretion2095RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2095 | 18.1254 | 22.1245 | 27.1413 | 30.9409 | 34.7693
| Pelham (Fonthill)Ice Accretion2100RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2100 | 17.9473 | 21.9386 | 26.944 | 30.736 | 34.5542
| Pelham (Fonthill)Ice Accretion2023RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
| Pelham (Fonthill)Ice Accretion2025RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2025 | 21.9182 | 26.3121 | 31.8773 | 36.1299 | 40.3738
| Pelham (Fonthill)Ice Accretion2030RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2030 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
| Pelham (Fonthill)Ice Accretion2035RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2035 | 21.7104 | 26.0819 | 31.632 | 35.8526 | 40.0781
| Pelham (Fonthill)Ice Accretion2040RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2040 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
| Pelham (Fonthill)Ice Accretion2045RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2045 | 21.5026 | 25.8517 | 31.3867 | 35.5754 | 39.7824
| Pelham (Fonthill)Ice Accretion2050RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2050 | 20.9221 | 25.2001 | 30.6368 | 34.7425 | 38.8765
| Pelham (Fonthill)Ice Accretion2055RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2055 | 20.4456 | 24.6636 | 30.0096 | 34.0483 | 38.1185
| Pelham (Fonthill)Ice Accretion2060RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2060 | 19.9691 | 24.1271 | 29.3824 | 33.354 | 37.3605
| Pelham (Fonthill)Ice Accretion2065RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2065 | 19.4926 | 23.5906 | 28.7552 | 32.6597 | 36.6025
| Pelham (Fonthill)Ice Accretion2070RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2070 | 19.0161 | 23.0541 | 28.128 | 31.9654 | 35.8445
| Pelham (Fonthill)Ice Accretion2075RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2075 | 18.7489 | 22.7752 | 27.832 | 31.6581 | 35.5219
| Pelham (Fonthill)Ice Accretion2080RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2080 | 18.4817 | 22.4963 | 27.536 | 31.3507 | 35.1994
| Pelham (Fonthill)Ice Accretion2085RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2085 | 18.2145 | 22.2174 | 27.24 | 31.0434 | 34.8768
| Pelham (Fonthill)Ice Accretion2090RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2090 | 17.2199 | 21.1063 | 25.9733 | 29.6633 | 33.3581
| Pelham (Fonthill)Ice Accretion2095RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2095 | 16.4925 | 20.2741 | 25.0027 | 28.5905 | 32.1619
| Pelham (Fonthill)Ice Accretion2100RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2100 | 15.7651 | 19.4419 | 24.032 | 27.5178 | 30.9658
| Pelham (Fonthill)Ice Accretion2023RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
| Pelham (Fonthill)Ice Accretion2025RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2025 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
| Pelham (Fonthill)Ice Accretion2030RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2030 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
| Pelham (Fonthill)Ice Accretion2035RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2035 | 21.3987 | 25.7366 | 31.264 | 35.4368 | 39.6346
| Pelham (Fonthill)Ice Accretion2040RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2040 | 20.6045 | 24.8425 | 30.2187 | 34.2797 | 38.3712
| Pelham (Fonthill)Ice Accretion2045RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2045 | 19.8103 | 23.9483 | 29.1733 | 33.1226 | 37.1078
| Pelham (Fonthill)Ice Accretion2050RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2050 | 18.6598 | 22.6822 | 27.7333 | 31.5556 | 35.4144
| Pelham (Fonthill)Ice Accretion2055RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2055 | 18.3035 | 22.3104 | 27.3387 | 31.1458 | 34.9843
| Pelham (Fonthill)Ice Accretion2060RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2060 | 17.2199 | 21.1063 | 25.9733 | 29.6633 | 33.3581
| Pelham (Fonthill)Ice Accretion2065RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2065 | 16.4925 | 20.2741 | 25.0027 | 28.5905 | 32.1619
| Pelham (Fonthill)Ice Accretion2070RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2070 | 15.4014 | 19.0258 | 23.5627 | 26.9995 | 30.4013
| Pelham (Fonthill)Ice Accretion2075RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2075 | 15.0377 | 18.6097 | 23.0933 | 26.4812 | 29.8368
| Pelham (Fonthill)Ice Accretion2080RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2080 | 14.674 | 18.1936 | 22.624 | 25.9629 | 29.2723
| Pelham (Fonthill)Ice Accretion2085RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2085 | 13.8501 | 17.2242 | 21.456 | 24.643 | 27.8006
| Pelham (Fonthill)Ice Accretion2090RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2090 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
| Pelham (Fonthill)Ice Accretion2095RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2095 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
| Pelham (Fonthill)Ice Accretion2100RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2100 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
| Pelham (Fonthill)Wind2023RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2023 | 88.11 | 95.1229 | 102.5655 | 109.9612 | 117.3507
| Pelham (Fonthill)Wind2025RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2025 | 88.0809 | 95.0932 | 102.5335 | 109.927 | 117.3142
| Pelham (Fonthill)Wind2030RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2030 | 88.0519 | 95.0634 | 102.5015 | 109.8928 | 117.2778
| Pelham (Fonthill)Wind2035RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2035 | 88.0228 | 95.0337 | 102.4695 | 109.8586 | 117.2413
| Pelham (Fonthill)Wind2040RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2040 | 87.9937 | 95.0039 | 102.4376 | 109.8243 | 117.2048
| Pelham (Fonthill)Wind2045RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2045 | 87.9647 | 94.9742 | 102.4056 | 109.7901 | 117.1684
| Pelham (Fonthill)Wind2050RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2050 | 87.9931 | 95.0177 | 102.4685 | 109.8661 | 117.2609
| Pelham (Fonthill)Wind2055RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2055 | 88.0507 | 95.091 | 102.5635 | 109.9764 | 117.3898
| Pelham (Fonthill)Wind2060RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2060 | 88.1083 | 95.1642 | 102.6584 | 110.0866 | 117.5188
| Pelham (Fonthill)Wind2065RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2065 | 88.1658 | 95.2375 | 102.7534 | 110.1968 | 117.6477
| Pelham (Fonthill)Wind2070RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2070 | 88.2234 | 95.3108 | 102.8483 | 110.307 | 117.7767
| Pelham (Fonthill)Wind2075RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2075 | 88.3048 | 95.4251 | 103.0049 | 110.498 | 118.0051
| Pelham (Fonthill)Wind2080RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2080 | 88.3862 | 95.5393 | 103.1614 | 110.6889 | 118.2334
| Pelham (Fonthill)Wind2085RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2085 | 88.4676 | 95.6536 | 103.3179 | 110.8798 | 118.4618
| Pelham (Fonthill)Wind2090RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2090 | 88.549 | 95.7679 | 103.4745 | 111.0707 | 118.6901
| Pelham (Fonthill)Wind2095RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2095 | 88.6304 | 95.8822 | 103.6311 | 111.2617 | 118.9185
| Pelham (Fonthill)Wind2100RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2100 | 88.7118 | 95.9965 | 103.7876 | 111.4526 | 119.1469
| Pelham (Fonthill)Wind2023RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2023 | 88.11 | 95.1229 | 102.5655 | 109.9612 | 117.3507
| Pelham (Fonthill)Wind2025RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2025 | 88.0809 | 95.0932 | 102.5335 | 109.927 | 117.3142
| Pelham (Fonthill)Wind2030RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2030 | 88.0519 | 95.0634 | 102.5015 | 109.8928 | 117.2778
| Pelham (Fonthill)Wind2035RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2035 | 88.0228 | 95.0337 | 102.4695 | 109.8586 | 117.2413
| Pelham (Fonthill)Wind2040RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2040 | 87.9937 | 95.0039 | 102.4376 | 109.8243 | 117.2048
| Pelham (Fonthill)Wind2045RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2045 | 87.9647 | 94.9742 | 102.4056 | 109.7901 | 117.1684
| Pelham (Fonthill)Wind2050RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2050 | 87.9931 | 95.0177 | 102.4685 | 109.8661 | 117.2609
| Pelham (Fonthill)Wind2055RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2055 | 88.0507 | 95.091 | 102.5635 | 109.9764 | 117.3898
| Pelham (Fonthill)Wind2060RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2060 | 88.1083 | 95.1642 | 102.6584 | 110.0866 | 117.5188
| Pelham (Fonthill)Wind2065RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2065 | 88.1658 | 95.2375 | 102.7534 | 110.1968 | 117.6477
| Pelham (Fonthill)Wind2070RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2070 | 88.2234 | 95.3108 | 102.8483 | 110.307 | 117.7767
| Pelham (Fonthill)Wind2075RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2075 | 88.3455 | 95.4822 | 103.0831 | 110.5934 | 118.1192
| Pelham (Fonthill)Wind2080RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2080 | 88.4676 | 95.6536 | 103.3179 | 110.8798 | 118.4618
| Pelham (Fonthill)Wind2085RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2085 | 88.5897 | 95.825 | 103.5528 | 111.1662 | 118.8043
| Pelham (Fonthill)Wind2090RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2090 | 88.8978 | 96.2344 | 104.0872 | 111.8092 | 119.5614
| Pelham (Fonthill)Wind2095RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2095 | 89.0839 | 96.4724 | 104.3869 | 112.1659 | 119.9759
| Pelham (Fonthill)Wind2100RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2100 | 89.2699 | 96.7103 | 104.6865 | 112.5225 | 120.3904
| Pelham (Fonthill)Wind2023RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2023 | 88.11 | 95.1229 | 102.5655 | 109.9612 | 117.3507
| Pelham (Fonthill)Wind2025RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2025 | 88.0519 | 95.0634 | 102.5015 | 109.8928 | 117.2778
| Pelham (Fonthill)Wind2030RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2030 | 87.9937 | 95.0039 | 102.4376 | 109.8243 | 117.2048
| Pelham (Fonthill)Wind2035RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2035 | 87.9356 | 94.9444 | 102.3736 | 109.7559 | 117.1319
| Pelham (Fonthill)Wind2040RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2040 | 88.0315 | 95.0666 | 102.5318 | 109.9396 | 117.3468
| Pelham (Fonthill)Wind2045RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2045 | 88.1274 | 95.1887 | 102.6901 | 110.1233 | 117.5618
| Pelham (Fonthill)Wind2050RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2050 | 88.3862 | 95.5393 | 103.1614 | 110.6889 | 118.2334
| Pelham (Fonthill)Wind2055RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2055 | 88.549 | 95.7679 | 103.4745 | 111.0707 | 118.6901
| Pelham (Fonthill)Wind2060RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2060 | 88.8978 | 96.2344 | 104.0872 | 111.8092 | 119.5614
| Pelham (Fonthill)Wind2065RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2065 | 89.0839 | 96.4724 | 104.3869 | 112.1659 | 119.9759
| Pelham (Fonthill)Wind2070RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2070 | 89.331 | 96.8137 | 104.8515 | 112.7386 | 120.6514
| Pelham (Fonthill)Wind2075RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2075 | 89.392 | 96.917 | 105.0164 | 112.9548 | 120.9124
| Pelham (Fonthill)Wind2080RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2080 | 89.4531 | 97.0203 | 105.1814 | 113.1709 | 121.1733
| Pelham (Fonthill)Wind2085RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2085 | 89.5185 | 97.1283 | 105.338 | 113.3654 | 121.4151
| Pelham (Fonthill)Wind2090RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2090 | 89.5839 | 97.2363 | 105.4945 | 113.56 | 121.6569
| Pelham (Fonthill)Wind2095RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2095 | 89.5839 | 97.2363 | 105.4945 | 113.56 | 121.6569
| Pelham (Fonthill)Wind2100RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2100 | 89.5839 | 97.2363 | 105.4945 | 113.56 | 121.6569
| PembrokeIce Accretion2023RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2023 | 14.0283 | 16.7162 | 20.12 | 22.713 | 25.326
| PembrokeIce Accretion2025RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2025 | 14.1628 | 16.885 | 20.33 | 22.9578 | 25.599
| PembrokeIce Accretion2030RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2030 | 14.2973 | 17.0537 | 20.54 | 23.2027 | 25.872
| PembrokeIce Accretion2035RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2035 | 14.4318 | 17.2225 | 20.75 | 23.4475 | 26.145
| PembrokeIce Accretion2040RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2040 | 14.5664 | 17.3913 | 20.96 | 23.6923 | 26.418
| PembrokeIce Accretion2045RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2045 | 14.7009 | 17.56 | 21.17 | 23.9372 | 26.691
| PembrokeIce Accretion2050RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2050 | 14.8327 | 17.7388 | 21.412 | 24.2227 | 27.0245
| PembrokeIce Accretion2055RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2055 | 14.8299 | 17.7487 | 21.444 | 24.2634 | 27.085
| PembrokeIce Accretion2060RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2060 | 14.8271 | 17.7587 | 21.476 | 24.304 | 27.1454
| PembrokeIce Accretion2065RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2065 | 14.8243 | 17.7686 | 21.508 | 24.3447 | 27.2059
| PembrokeIce Accretion2070RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2070 | 14.8215 | 17.7786 | 21.54 | 24.3854 | 27.2664
| PembrokeIce Accretion2075RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2075 | 14.8285 | 17.8007 | 21.5767 | 24.4381 | 27.3294
| PembrokeIce Accretion2080RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2080 | 14.8354 | 17.8229 | 21.6133 | 24.4909 | 27.3924
| PembrokeIce Accretion2085RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2085 | 14.8424 | 17.845 | 21.65 | 24.5436 | 27.4554
| PembrokeIce Accretion2090RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2090 | 14.8494 | 17.8671 | 21.6867 | 24.5963 | 27.5184
| PembrokeIce Accretion2095RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2095 | 14.8563 | 17.8893 | 21.7233 | 24.6491 | 27.5814
| PembrokeIce Accretion2100RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2100 | 14.8633 | 17.9114 | 21.76 | 24.7018 | 27.6444
| PembrokeIce Accretion2023RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2023 | 14.0283 | 16.7162 | 20.12 | 22.713 | 25.326
| PembrokeIce Accretion2025RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2025 | 14.1628 | 16.885 | 20.33 | 22.9578 | 25.599
| PembrokeIce Accretion2030RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2030 | 14.2973 | 17.0537 | 20.54 | 23.2027 | 25.872
| PembrokeIce Accretion2035RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2035 | 14.4318 | 17.2225 | 20.75 | 23.4475 | 26.145
| PembrokeIce Accretion2040RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2040 | 14.5664 | 17.3913 | 20.96 | 23.6923 | 26.418
| PembrokeIce Accretion2045RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2045 | 14.7009 | 17.56 | 21.17 | 23.9372 | 26.691
| PembrokeIce Accretion2050RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2050 | 14.8327 | 17.7388 | 21.412 | 24.2227 | 27.0245
| PembrokeIce Accretion2055RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2055 | 14.8299 | 17.7487 | 21.444 | 24.2634 | 27.085
| PembrokeIce Accretion2060RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2060 | 14.8271 | 17.7587 | 21.476 | 24.304 | 27.1454
| PembrokeIce Accretion2065RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2065 | 14.8243 | 17.7686 | 21.508 | 24.3447 | 27.2059
| PembrokeIce Accretion2070RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2070 | 14.8215 | 17.7786 | 21.54 | 24.3854 | 27.2664
| PembrokeIce Accretion2075RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2075 | 14.832 | 17.8118 | 21.595 | 24.4645 | 27.3609
| PembrokeIce Accretion2080RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2080 | 14.8424 | 17.845 | 21.65 | 24.5436 | 27.4554
| PembrokeIce Accretion2085RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2085 | 14.8528 | 17.8782 | 21.705 | 24.6227 | 27.5499
| PembrokeIce Accretion2090RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2090 | 14.6592 | 17.6569 | 21.4467 | 24.3477 | 27.2412
| PembrokeIce Accretion2095RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2095 | 14.455 | 17.4023 | 21.1333 | 23.9937 | 26.838
| PembrokeIce Accretion2100RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2100 | 14.2509 | 17.1478 | 20.82 | 23.6396 | 26.4348
| PembrokeIce Accretion2023RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2023 | 14.0283 | 16.7162 | 20.12 | 22.713 | 25.326
| PembrokeIce Accretion2025RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2025 | 14.2973 | 17.0537 | 20.54 | 23.2027 | 25.872
| PembrokeIce Accretion2030RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2030 | 14.5664 | 17.3913 | 20.96 | 23.6923 | 26.418
| PembrokeIce Accretion2035RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2035 | 14.8354 | 17.7288 | 21.38 | 24.182 | 26.964
| PembrokeIce Accretion2040RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2040 | 14.8308 | 17.7454 | 21.4333 | 24.2498 | 27.0648
| PembrokeIce Accretion2045RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2045 | 14.8262 | 17.762 | 21.4867 | 24.3176 | 27.1656
| PembrokeIce Accretion2050RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2050 | 14.8354 | 17.8229 | 21.6133 | 24.4909 | 27.3924
| PembrokeIce Accretion2055RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2055 | 14.8494 | 17.8671 | 21.6867 | 24.5963 | 27.5184
| PembrokeIce Accretion2060RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2060 | 14.6592 | 17.6569 | 21.4467 | 24.3477 | 27.2412
| PembrokeIce Accretion2065RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2065 | 14.455 | 17.4023 | 21.1333 | 23.9937 | 26.838
| PembrokeIce Accretion2070RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2070 | 14.2231 | 17.1367 | 20.8267 | 23.6547 | 26.46
| PembrokeIce Accretion2075RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2075 | 14.1953 | 17.1257 | 20.8333 | 23.6697 | 26.4852
| PembrokeIce Accretion2080RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2080 | 14.1674 | 17.1146 | 20.84 | 23.6848 | 26.5104
| PembrokeIce Accretion2085RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2085 | 13.8891 | 16.8241 | 20.54 | 23.3797 | 26.1954
| PembrokeIce Accretion2090RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2090 | 13.6108 | 16.5336 | 20.24 | 23.0746 | 25.8804
| PembrokeIce Accretion2095RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2095 | 13.6108 | 16.5336 | 20.24 | 23.0746 | 25.8804
| PembrokeIce Accretion2100RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2100 | 13.6108 | 16.5336 | 20.24 | 23.0746 | 25.8804
| PembrokeWind2023RCP4.5 | Pembroke | Wind | RCP4.5 | 2023 | 76.7577 | 82.6127 | 88.7686 | 94.9348 | 101.0947
| PembrokeWind2025RCP4.5 | Pembroke | Wind | RCP4.5 | 2025 | 76.7436 | 82.5962 | 88.7493 | 94.9142 | 101.0728
| PembrokeWind2030RCP4.5 | Pembroke | Wind | RCP4.5 | 2030 | 76.7295 | 82.5796 | 88.73 | 94.8935 | 101.0508
| PembrokeWind2035RCP4.5 | Pembroke | Wind | RCP4.5 | 2035 | 76.7154 | 82.5631 | 88.7107 | 94.8729 | 101.0288
| PembrokeWind2040RCP4.5 | Pembroke | Wind | RCP4.5 | 2040 | 76.7014 | 82.5465 | 88.6915 | 94.8523 | 101.0068
| PembrokeWind2045RCP4.5 | Pembroke | Wind | RCP4.5 | 2045 | 76.6873 | 82.53 | 88.6722 | 94.8316 | 100.9848
| PembrokeWind2050RCP4.5 | Pembroke | Wind | RCP4.5 | 2050 | 76.747 | 82.5978 | 88.749 | 94.9157 | 101.0785
| PembrokeWind2055RCP4.5 | Pembroke | Wind | RCP4.5 | 2055 | 76.8207 | 82.6823 | 88.8451 | 95.0205 | 101.1942
| PembrokeWind2060RCP4.5 | Pembroke | Wind | RCP4.5 | 2060 | 76.8945 | 82.7667 | 88.9413 | 95.1252 | 101.3098
| PembrokeWind2065RCP4.5 | Pembroke | Wind | RCP4.5 | 2065 | 76.9683 | 82.8511 | 89.0374 | 95.23 | 101.4255
| PembrokeWind2070RCP4.5 | Pembroke | Wind | RCP4.5 | 2070 | 77.0421 | 82.9355 | 89.1335 | 95.3348 | 101.5412
| PembrokeWind2075RCP4.5 | Pembroke | Wind | RCP4.5 | 2075 | 77.0882 | 82.9949 | 89.2077 | 95.4236 | 101.6426
| PembrokeWind2080RCP4.5 | Pembroke | Wind | RCP4.5 | 2080 | 77.1343 | 83.0542 | 89.2818 | 95.5125 | 101.7441
| PembrokeWind2085RCP4.5 | Pembroke | Wind | RCP4.5 | 2085 | 77.1804 | 83.1135 | 89.356 | 95.6014 | 101.8455
| PembrokeWind2090RCP4.5 | Pembroke | Wind | RCP4.5 | 2090 | 77.2265 | 83.1728 | 89.4302 | 95.6903 | 101.947
| PembrokeWind2095RCP4.5 | Pembroke | Wind | RCP4.5 | 2095 | 77.2726 | 83.2321 | 89.5043 | 95.7792 | 102.0485
| PembrokeWind2100RCP4.5 | Pembroke | Wind | RCP4.5 | 2100 | 77.3187 | 83.2915 | 89.5785 | 95.868 | 102.1499
| PembrokeWind2023RCP6.0 | Pembroke | Wind | RCP6.0 | 2023 | 76.7577 | 82.6127 | 88.7686 | 94.9348 | 101.0947
| PembrokeWind2025RCP6.0 | Pembroke | Wind | RCP6.0 | 2025 | 76.7436 | 82.5962 | 88.7493 | 94.9142 | 101.0728
| PembrokeWind2030RCP6.0 | Pembroke | Wind | RCP6.0 | 2030 | 76.7295 | 82.5796 | 88.73 | 94.8935 | 101.0508
| PembrokeWind2035RCP6.0 | Pembroke | Wind | RCP6.0 | 2035 | 76.7154 | 82.5631 | 88.7107 | 94.8729 | 101.0288
| PembrokeWind2040RCP6.0 | Pembroke | Wind | RCP6.0 | 2040 | 76.7014 | 82.5465 | 88.6915 | 94.8523 | 101.0068
| PembrokeWind2045RCP6.0 | Pembroke | Wind | RCP6.0 | 2045 | 76.6873 | 82.53 | 88.6722 | 94.8316 | 100.9848
| PembrokeWind2050RCP6.0 | Pembroke | Wind | RCP6.0 | 2050 | 76.747 | 82.5978 | 88.749 | 94.9157 | 101.0785
| PembrokeWind2055RCP6.0 | Pembroke | Wind | RCP6.0 | 2055 | 76.8207 | 82.6823 | 88.8451 | 95.0205 | 101.1942
| PembrokeWind2060RCP6.0 | Pembroke | Wind | RCP6.0 | 2060 | 76.8945 | 82.7667 | 88.9413 | 95.1252 | 101.3098
| PembrokeWind2065RCP6.0 | Pembroke | Wind | RCP6.0 | 2065 | 76.9683 | 82.8511 | 89.0374 | 95.23 | 101.4255
| PembrokeWind2070RCP6.0 | Pembroke | Wind | RCP6.0 | 2070 | 77.0421 | 82.9355 | 89.1335 | 95.3348 | 101.5412
| PembrokeWind2075RCP6.0 | Pembroke | Wind | RCP6.0 | 2075 | 77.1112 | 83.0245 | 89.2447 | 95.4681 | 101.6934
| PembrokeWind2080RCP6.0 | Pembroke | Wind | RCP6.0 | 2080 | 77.1804 | 83.1135 | 89.356 | 95.6014 | 101.8455
| PembrokeWind2085RCP6.0 | Pembroke | Wind | RCP6.0 | 2085 | 77.2496 | 83.2025 | 89.4672 | 95.7347 | 101.9977
| PembrokeWind2090RCP6.0 | Pembroke | Wind | RCP6.0 | 2090 | 77.352 | 83.3246 | 89.6111 | 95.8998 | 102.1804
| PembrokeWind2095RCP6.0 | Pembroke | Wind | RCP6.0 | 2095 | 77.3853 | 83.3577 | 89.6438 | 95.9315 | 102.2108
| PembrokeWind2100RCP6.0 | Pembroke | Wind | RCP6.0 | 2100 | 77.4186 | 83.3908 | 89.6764 | 95.9633 | 102.2412
| PembrokeWind2023RCP8.5 | Pembroke | Wind | RCP8.5 | 2023 | 76.7577 | 82.6127 | 88.7686 | 94.9348 | 101.0947
| PembrokeWind2025RCP8.5 | Pembroke | Wind | RCP8.5 | 2025 | 76.7295 | 82.5796 | 88.73 | 94.8935 | 101.0508
| PembrokeWind2030RCP8.5 | Pembroke | Wind | RCP8.5 | 2030 | 76.7014 | 82.5465 | 88.6915 | 94.8523 | 101.0068
| PembrokeWind2035RCP8.5 | Pembroke | Wind | RCP8.5 | 2035 | 76.6732 | 82.5134 | 88.6529 | 94.811 | 100.9628
| PembrokeWind2040RCP8.5 | Pembroke | Wind | RCP8.5 | 2040 | 76.7961 | 82.6541 | 88.8131 | 94.9856 | 101.1556
| PembrokeWind2045RCP8.5 | Pembroke | Wind | RCP8.5 | 2045 | 76.9191 | 82.7948 | 88.9733 | 95.1602 | 101.3484
| PembrokeWind2050RCP8.5 | Pembroke | Wind | RCP8.5 | 2050 | 77.1343 | 83.0542 | 89.2818 | 95.5125 | 101.7441
| PembrokeWind2055RCP8.5 | Pembroke | Wind | RCP8.5 | 2055 | 77.2265 | 83.1728 | 89.4302 | 95.6903 | 101.947
| PembrokeWind2060RCP8.5 | Pembroke | Wind | RCP8.5 | 2060 | 77.352 | 83.3246 | 89.6111 | 95.8998 | 102.1804
| PembrokeWind2065RCP8.5 | Pembroke | Wind | RCP8.5 | 2065 | 77.3853 | 83.3577 | 89.6438 | 95.9315 | 102.2108
| PembrokeWind2070RCP8.5 | Pembroke | Wind | RCP8.5 | 2070 | 77.4109 | 83.3742 | 89.6497 | 95.9284 | 102.2007
| PembrokeWind2075RCP8.5 | Pembroke | Wind | RCP8.5 | 2075 | 77.4033 | 83.3577 | 89.623 | 95.8934 | 102.1601
| PembrokeWind2080RCP8.5 | Pembroke | Wind | RCP8.5 | 2080 | 77.3956 | 83.3411 | 89.5963 | 95.8585 | 102.1195
| PembrokeWind2085RCP8.5 | Pembroke | Wind | RCP8.5 | 2085 | 77.3456 | 83.2666 | 89.4939 | 95.7252 | 101.9622
| PembrokeWind2090RCP8.5 | Pembroke | Wind | RCP8.5 | 2090 | 77.2957 | 83.1921 | 89.3916 | 95.5919 | 101.805
| PembrokeWind2095RCP8.5 | Pembroke | Wind | RCP8.5 | 2095 | 77.2957 | 83.1921 | 89.3916 | 95.5919 | 101.805
| PembrokeWind2100RCP8.5 | Pembroke | Wind | RCP8.5 | 2100 | 77.2957 | 83.1921 | 89.3916 | 95.5919 | 101.805
| PenetanguisheneIce Accretion2023RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2023 | 13.6525 | 16.2846 | 19.62 | 22.1706 | 24.7464
| PenetanguisheneIce Accretion2025RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2025 | 13.6363 | 16.2735 | 19.6133 | 22.1706 | 24.7464
| PenetanguisheneIce Accretion2030RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2030 | 13.62 | 16.2625 | 19.6067 | 22.1706 | 24.7464
| PenetanguisheneIce Accretion2035RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2035 | 13.6038 | 16.2514 | 19.6 | 22.1706 | 24.7464
| PenetanguisheneIce Accretion2040RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2040 | 13.5876 | 16.2403 | 19.5933 | 22.1706 | 24.7464
| PenetanguisheneIce Accretion2045RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2045 | 13.5713 | 16.2293 | 19.5867 | 22.1706 | 24.7464
| PenetanguisheneIce Accretion2050RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2050 | 13.5523 | 16.2282 | 19.612 | 22.2113 | 24.8018
| PenetanguisheneIce Accretion2055RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2055 | 13.5495 | 16.2381 | 19.644 | 22.252 | 24.8573
| PenetanguisheneIce Accretion2060RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2060 | 13.5467 | 16.2481 | 19.676 | 22.2926 | 24.9127
| PenetanguisheneIce Accretion2065RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2065 | 13.5439 | 16.258 | 19.708 | 22.3333 | 24.9682
| PenetanguisheneIce Accretion2070RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2070 | 13.5412 | 16.268 | 19.74 | 22.374 | 25.0236
| PenetanguisheneIce Accretion2075RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2075 | 13.5806 | 16.3316 | 19.83 | 22.4832 | 25.1538
| PenetanguisheneIce Accretion2080RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2080 | 13.62 | 16.3953 | 19.92 | 22.5925 | 25.284
| PenetanguisheneIce Accretion2085RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2085 | 13.6595 | 16.4589 | 20.01 | 22.7017 | 25.4142
| PenetanguisheneIce Accretion2090RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2090 | 13.6989 | 16.5225 | 20.1 | 22.8109 | 25.5444
| PenetanguisheneIce Accretion2095RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2095 | 13.7383 | 16.5862 | 20.19 | 22.9202 | 25.6746
| PenetanguisheneIce Accretion2100RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2100 | 13.7778 | 16.6498 | 20.28 | 23.0294 | 25.8048
| PenetanguisheneIce Accretion2023RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2023 | 13.6525 | 16.2846 | 19.62 | 22.1706 | 24.7464
| PenetanguisheneIce Accretion2025RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2025 | 13.6363 | 16.2735 | 19.6133 | 22.1706 | 24.7464
| PenetanguisheneIce Accretion2030RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2030 | 13.62 | 16.2625 | 19.6067 | 22.1706 | 24.7464
| PenetanguisheneIce Accretion2035RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2035 | 13.6038 | 16.2514 | 19.6 | 22.1706 | 24.7464
| PenetanguisheneIce Accretion2040RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2040 | 13.5876 | 16.2403 | 19.5933 | 22.1706 | 24.7464
| PenetanguisheneIce Accretion2045RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2045 | 13.5713 | 16.2293 | 19.5867 | 22.1706 | 24.7464
| PenetanguisheneIce Accretion2050RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2050 | 13.5523 | 16.2282 | 19.612 | 22.2113 | 24.8018
| PenetanguisheneIce Accretion2055RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2055 | 13.5495 | 16.2381 | 19.644 | 22.252 | 24.8573
| PenetanguisheneIce Accretion2060RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2060 | 13.5467 | 16.2481 | 19.676 | 22.2926 | 24.9127
| PenetanguisheneIce Accretion2065RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2065 | 13.5439 | 16.258 | 19.708 | 22.3333 | 24.9682
| PenetanguisheneIce Accretion2070RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2070 | 13.5412 | 16.268 | 19.74 | 22.374 | 25.0236
| PenetanguisheneIce Accretion2075RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2075 | 13.6003 | 16.3634 | 19.875 | 22.5378 | 25.2189
| PenetanguisheneIce Accretion2080RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2080 | 13.6595 | 16.4589 | 20.01 | 22.7017 | 25.4142
| PenetanguisheneIce Accretion2085RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2085 | 13.7186 | 16.5543 | 20.145 | 22.8655 | 25.6095
| PenetanguisheneIce Accretion2090RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2090 | 13.7546 | 16.6609 | 20.3333 | 23.1198 | 25.9224
| PenetanguisheneIce Accretion2095RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2095 | 13.7314 | 16.6719 | 20.3867 | 23.2102 | 26.04
| PenetanguisheneIce Accretion2100RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2100 | 13.7082 | 16.683 | 20.44 | 23.3006 | 26.1576
| PenetanguisheneIce Accretion2023RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2023 | 13.6525 | 16.2846 | 19.62 | 22.1706 | 24.7464
| PenetanguisheneIce Accretion2025RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2025 | 13.62 | 16.2625 | 19.6067 | 22.1706 | 24.7464
| PenetanguisheneIce Accretion2030RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2030 | 13.5876 | 16.2403 | 19.5933 | 22.1706 | 24.7464
| PenetanguisheneIce Accretion2035RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2035 | 13.5551 | 16.2182 | 19.58 | 22.1706 | 24.7464
| PenetanguisheneIce Accretion2040RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2040 | 13.5504 | 16.2348 | 19.6333 | 22.2384 | 24.8388
| PenetanguisheneIce Accretion2045RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2045 | 13.5458 | 16.2514 | 19.6867 | 22.3062 | 24.9312
| PenetanguisheneIce Accretion2050RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2050 | 13.62 | 16.3953 | 19.92 | 22.5925 | 25.284
| PenetanguisheneIce Accretion2055RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2055 | 13.6989 | 16.5225 | 20.1 | 22.8109 | 25.5444
| PenetanguisheneIce Accretion2060RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2060 | 13.7546 | 16.6609 | 20.3333 | 23.1198 | 25.9224
| PenetanguisheneIce Accretion2065RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2065 | 13.7314 | 16.6719 | 20.3867 | 23.2102 | 26.04
| PenetanguisheneIce Accretion2070RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2070 | 13.4577 | 16.4174 | 20.1533 | 22.9917 | 25.83
| PenetanguisheneIce Accretion2075RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2075 | 13.2072 | 16.1518 | 19.8667 | 22.6829 | 25.5024
| PenetanguisheneIce Accretion2080RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2080 | 12.9567 | 15.8862 | 19.58 | 22.374 | 25.1748
| PenetanguisheneIce Accretion2085RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2085 | 12.4348 | 15.2969 | 18.9 | 21.6282 | 24.3558
| PenetanguisheneIce Accretion2090RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2090 | 11.9129 | 14.7076 | 18.22 | 20.8824 | 23.5368
| PenetanguisheneIce Accretion2095RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2095 | 11.9129 | 14.7076 | 18.22 | 20.8824 | 23.5368
| PenetanguisheneIce Accretion2100RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2100 | 11.9129 | 14.7076 | 18.22 | 20.8824 | 23.5368
| PenetanguisheneWind2023RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2023 | 81.6868 | 88.0145 | 94.6862 | 101.3444 | 108.0066
| PenetanguisheneWind2025RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2025 | 81.7707 | 88.115 | 94.8053 | 101.4802 | 108.1584
| PenetanguisheneWind2030RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2030 | 81.8546 | 88.2155 | 94.9243 | 101.616 | 108.3102
| PenetanguisheneWind2035RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2035 | 81.9384 | 88.3161 | 95.0434 | 101.7518 | 108.462
| PenetanguisheneWind2040RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2040 | 82.0223 | 88.4166 | 95.1625 | 101.8875 | 108.6138
| PenetanguisheneWind2045RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2045 | 82.1062 | 88.5171 | 95.2815 | 102.0233 | 108.7656
| PenetanguisheneWind2050RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2050 | 82.3069 | 88.7575 | 95.5698 | 102.3542 | 109.1403
| PenetanguisheneWind2055RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2055 | 82.4238 | 88.8974 | 95.739 | 102.5494 | 109.3632
| PenetanguisheneWind2060RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2060 | 82.5407 | 89.0373 | 95.9082 | 102.7445 | 109.5861
| PenetanguisheneWind2065RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2065 | 82.6576 | 89.1771 | 96.0774 | 102.9396 | 109.809
| PenetanguisheneWind2070RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2070 | 82.7745 | 89.317 | 96.2466 | 103.1347 | 110.0319
| PenetanguisheneWind2075RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2075 | 82.811 | 89.3695 | 96.3202 | 103.2253 | 110.139
| PenetanguisheneWind2080RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2080 | 82.8475 | 89.4219 | 96.3939 | 103.3158 | 110.2462
| PenetanguisheneWind2085RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2085 | 82.884 | 89.4744 | 96.4675 | 103.4063 | 110.3534
| PenetanguisheneWind2090RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2090 | 82.9206 | 89.5268 | 96.5411 | 103.4968 | 110.4605
| PenetanguisheneWind2095RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2095 | 82.9571 | 89.5793 | 96.6148 | 103.5873 | 110.5677
| PenetanguisheneWind2100RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2100 | 82.9936 | 89.6317 | 96.6884 | 103.6779 | 110.6748
| PenetanguisheneWind2023RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2023 | 81.6868 | 88.0145 | 94.6862 | 101.3444 | 108.0066
| PenetanguisheneWind2025RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2025 | 81.7707 | 88.115 | 94.8053 | 101.4802 | 108.1584
| PenetanguisheneWind2030RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2030 | 81.8546 | 88.2155 | 94.9243 | 101.616 | 108.3102
| PenetanguisheneWind2035RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2035 | 81.9384 | 88.3161 | 95.0434 | 101.7518 | 108.462
| PenetanguisheneWind2040RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2040 | 82.0223 | 88.4166 | 95.1625 | 101.8875 | 108.6138
| PenetanguisheneWind2045RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2045 | 82.1062 | 88.5171 | 95.2815 | 102.0233 | 108.7656
| PenetanguisheneWind2050RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2050 | 82.3069 | 88.7575 | 95.5698 | 102.3542 | 109.1403
| PenetanguisheneWind2055RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2055 | 82.4238 | 88.8974 | 95.739 | 102.5494 | 109.3632
| PenetanguisheneWind2060RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2060 | 82.5407 | 89.0373 | 95.9082 | 102.7445 | 109.5861
| PenetanguisheneWind2065RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2065 | 82.6576 | 89.1771 | 96.0774 | 102.9396 | 109.809
| PenetanguisheneWind2070RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2070 | 82.7745 | 89.317 | 96.2466 | 103.1347 | 110.0319
| PenetanguisheneWind2075RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2075 | 82.8292 | 89.3957 | 96.3571 | 103.2705 | 110.1926
| PenetanguisheneWind2080RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2080 | 82.884 | 89.4744 | 96.4675 | 103.4063 | 110.3534
| PenetanguisheneWind2085RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2085 | 82.9388 | 89.553 | 96.578 | 103.5421 | 110.5141
| PenetanguisheneWind2090RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2090 | 83.1154 | 89.7949 | 96.8983 | 103.9293 | 110.9678
| PenetanguisheneWind2095RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2095 | 83.2371 | 89.9581 | 97.1083 | 104.1808 | 111.2607
| PenetanguisheneWind2100RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2100 | 83.3589 | 90.1213 | 97.3182 | 104.4322 | 111.5536
| PenetanguisheneWind2023RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2023 | 81.6868 | 88.0145 | 94.6862 | 101.3444 | 108.0066
| PenetanguisheneWind2025RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2025 | 81.8546 | 88.2155 | 94.9243 | 101.616 | 108.3102
| PenetanguisheneWind2030RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2030 | 82.0223 | 88.4166 | 95.1625 | 101.8875 | 108.6138
| PenetanguisheneWind2035RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2035 | 82.1901 | 88.6177 | 95.4006 | 102.1591 | 108.9174
| PenetanguisheneWind2040RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2040 | 82.3849 | 88.8508 | 95.6826 | 102.4843 | 109.2889
| PenetanguisheneWind2045RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2045 | 82.5797 | 89.0839 | 95.9646 | 102.8095 | 109.6604
| PenetanguisheneWind2050RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2050 | 82.8475 | 89.4219 | 96.3939 | 103.3158 | 110.2462
| PenetanguisheneWind2055RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2055 | 82.9206 | 89.5268 | 96.5411 | 103.4968 | 110.4605
| PenetanguisheneWind2060RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2060 | 83.1154 | 89.7949 | 96.8983 | 103.9293 | 110.9678
| PenetanguisheneWind2065RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2065 | 83.2371 | 89.9581 | 97.1083 | 104.1808 | 111.2607
| PenetanguisheneWind2070RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2070 | 83.3453 | 90.1154 | 97.3245 | 104.4456 | 111.5786
| PenetanguisheneWind2075RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2075 | 83.3318 | 90.1096 | 97.3307 | 104.459 | 111.6036
| PenetanguisheneWind2080RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2080 | 83.3183 | 90.1038 | 97.337 | 104.4724 | 111.6286
| PenetanguisheneWind2085RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2085 | 83.4238 | 90.2393 | 97.5156 | 104.6837 | 111.875
| PenetanguisheneWind2090RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2090 | 83.5293 | 90.3748 | 97.6942 | 104.8949 | 112.1215
| PenetanguisheneWind2095RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2095 | 83.5293 | 90.3748 | 97.6942 | 104.8949 | 112.1215
| PenetanguisheneWind2100RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2100 | 83.5293 | 90.3748 | 97.6942 | 104.8949 | 112.1215
| PerthIce Accretion2023RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2023 | 17.9473 | 21.3426 | 25.636 | 28.9393 | 32.2358
| PerthIce Accretion2025RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2025 | 17.9412 | 21.339 | 25.6403 | 28.9491 | 32.2468
| PerthIce Accretion2030RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2030 | 17.9352 | 21.3354 | 25.6447 | 28.9589 | 32.2577
| PerthIce Accretion2035RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2035 | 17.9292 | 21.3318 | 25.649 | 28.9687 | 32.2686
| PerthIce Accretion2040RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2040 | 17.9231 | 21.3282 | 25.6533 | 28.9785 | 32.2795
| PerthIce Accretion2045RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2045 | 17.9171 | 21.3246 | 25.6577 | 28.9883 | 32.2904
| PerthIce Accretion2050RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2050 | 17.9147 | 21.3426 | 25.7036 | 29.0568 | 32.3734
| PerthIce Accretion2055RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2055 | 17.9183 | 21.3642 | 25.7452 | 29.1156 | 32.4455
| PerthIce Accretion2060RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2060 | 17.9219 | 21.3858 | 25.7868 | 29.1743 | 32.5176
| PerthIce Accretion2065RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2065 | 17.9256 | 21.4074 | 25.8284 | 29.2331 | 32.5896
| PerthIce Accretion2070RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2070 | 17.9292 | 21.4289 | 25.87 | 29.2919 | 32.6617
| PerthIce Accretion2075RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2075 | 18.0106 | 21.5476 | 26.0347 | 29.4877 | 32.8965
| PerthIce Accretion2080RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2080 | 18.092 | 21.6663 | 26.1993 | 29.6836 | 33.1313
| PerthIce Accretion2085RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2085 | 18.1734 | 21.785 | 26.364 | 29.8795 | 33.3661
| PerthIce Accretion2090RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2090 | 18.2548 | 21.9037 | 26.5287 | 30.0753 | 33.6008
| PerthIce Accretion2095RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2095 | 18.3362 | 22.0224 | 26.6933 | 30.2712 | 33.8356
| PerthIce Accretion2100RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2100 | 18.4177 | 22.1411 | 26.858 | 30.4671 | 34.0704
| PerthIce Accretion2023RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2023 | 17.9473 | 21.3426 | 25.636 | 28.9393 | 32.2358
| PerthIce Accretion2025RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2025 | 17.9412 | 21.339 | 25.6403 | 28.9491 | 32.2468
| PerthIce Accretion2030RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2030 | 17.9352 | 21.3354 | 25.6447 | 28.9589 | 32.2577
| PerthIce Accretion2035RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2035 | 17.9292 | 21.3318 | 25.649 | 28.9687 | 32.2686
| PerthIce Accretion2040RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2040 | 17.9231 | 21.3282 | 25.6533 | 28.9785 | 32.2795
| PerthIce Accretion2045RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2045 | 17.9171 | 21.3246 | 25.6577 | 28.9883 | 32.2904
| PerthIce Accretion2050RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2050 | 17.9147 | 21.3426 | 25.7036 | 29.0568 | 32.3734
| PerthIce Accretion2055RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2055 | 17.9183 | 21.3642 | 25.7452 | 29.1156 | 32.4455
| PerthIce Accretion2060RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2060 | 17.9219 | 21.3858 | 25.7868 | 29.1743 | 32.5176
| PerthIce Accretion2065RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2065 | 17.9256 | 21.4074 | 25.8284 | 29.2331 | 32.5896
| PerthIce Accretion2070RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2070 | 17.9292 | 21.4289 | 25.87 | 29.2919 | 32.6617
| PerthIce Accretion2075RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2075 | 18.0513 | 21.607 | 26.117 | 29.5857 | 33.0139
| PerthIce Accretion2080RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2080 | 18.1734 | 21.785 | 26.364 | 29.8795 | 33.3661
| PerthIce Accretion2085RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2085 | 18.2955 | 21.963 | 26.611 | 30.1733 | 33.7182
| PerthIce Accretion2090RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2090 | 18.4056 | 22.1627 | 26.9273 | 30.5552 | 34.1905
| PerthIce Accretion2095RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2095 | 18.3935 | 22.1842 | 26.9967 | 30.6433 | 34.3106
| PerthIce Accretion2100RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2100 | 18.3815 | 22.2058 | 27.066 | 30.7315 | 34.4308
| PerthIce Accretion2023RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2023 | 17.9473 | 21.3426 | 25.636 | 28.9393 | 32.2358
| PerthIce Accretion2025RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2025 | 17.9352 | 21.3354 | 25.6447 | 28.9589 | 32.2577
| PerthIce Accretion2030RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2030 | 17.9231 | 21.3282 | 25.6533 | 28.9785 | 32.2795
| PerthIce Accretion2035RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2035 | 17.9111 | 21.321 | 25.662 | 28.9981 | 32.3014
| PerthIce Accretion2040RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2040 | 17.9171 | 21.357 | 25.7313 | 29.096 | 32.4215
| PerthIce Accretion2045RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2045 | 17.9231 | 21.393 | 25.8007 | 29.1939 | 32.5416
| PerthIce Accretion2050RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2050 | 18.092 | 21.6663 | 26.1993 | 29.6836 | 33.1313
| PerthIce Accretion2055RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2055 | 18.2548 | 21.9037 | 26.5287 | 30.0753 | 33.6008
| PerthIce Accretion2060RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2060 | 18.4056 | 22.1627 | 26.9273 | 30.5552 | 34.1905
| PerthIce Accretion2065RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2065 | 18.3935 | 22.1842 | 26.9967 | 30.6433 | 34.3106
| PerthIce Accretion2070RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2070 | 18.1885 | 22.0044 | 26.8493 | 30.5062 | 34.1905
| PerthIce Accretion2075RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2075 | 17.9955 | 21.803 | 26.6327 | 30.281 | 33.9503
| PerthIce Accretion2080RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2080 | 17.8025 | 21.6016 | 26.416 | 30.0557 | 33.71
| PerthIce Accretion2085RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2085 | 17.0608 | 20.7492 | 25.415 | 28.954 | 32.4979
| PerthIce Accretion2090RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2090 | 16.319 | 19.8968 | 24.414 | 27.8522 | 31.2858
| PerthIce Accretion2095RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2095 | 16.319 | 19.8968 | 24.414 | 27.8522 | 31.2858
| PerthIce Accretion2100RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2100 | 16.319 | 19.8968 | 24.414 | 27.8522 | 31.2858
| PerthWind2023RCP4.5 | Perth | Wind | RCP4.5 | 2023 | 76.5564 | 82.5275 | 88.8272 | 95.1016 | 101.3834
| PerthWind2025RCP4.5 | Perth | Wind | RCP4.5 | 2025 | 76.6665 | 82.6598 | 88.9871 | 95.2868 | 101.5941
| PerthWind2030RCP4.5 | Perth | Wind | RCP4.5 | 2030 | 76.7767 | 82.7921 | 89.1469 | 95.472 | 101.8047
| PerthWind2035RCP4.5 | Perth | Wind | RCP4.5 | 2035 | 76.8869 | 82.9244 | 89.3068 | 95.6571 | 102.0154
| PerthWind2040RCP4.5 | Perth | Wind | RCP4.5 | 2040 | 76.9971 | 83.0567 | 89.4667 | 95.8423 | 102.2261
| PerthWind2045RCP4.5 | Perth | Wind | RCP4.5 | 2045 | 77.1073 | 83.189 | 89.6265 | 96.0275 | 102.4368
| PerthWind2050RCP4.5 | Perth | Wind | RCP4.5 | 2050 | 77.2022 | 83.2984 | 89.7547 | 96.1731 | 102.5993
| PerthWind2055RCP4.5 | Perth | Wind | RCP4.5 | 2055 | 77.187 | 83.2755 | 89.723 | 96.1336 | 102.5511
| PerthWind2060RCP4.5 | Perth | Wind | RCP4.5 | 2060 | 77.1718 | 83.2526 | 89.6914 | 96.094 | 102.503
| PerthWind2065RCP4.5 | Perth | Wind | RCP4.5 | 2065 | 77.1566 | 83.2296 | 89.6597 | 96.0545 | 102.4548
| PerthWind2070RCP4.5 | Perth | Wind | RCP4.5 | 2070 | 77.1414 | 83.2067 | 89.628 | 96.015 | 102.4067
| PerthWind2075RCP4.5 | Perth | Wind | RCP4.5 | 2075 | 77.1693 | 83.2436 | 89.6779 | 96.0746 | 102.4752
| PerthWind2080RCP4.5 | Perth | Wind | RCP4.5 | 2080 | 77.1972 | 83.2804 | 89.7277 | 96.1342 | 102.5438
| PerthWind2085RCP4.5 | Perth | Wind | RCP4.5 | 2085 | 77.225 | 83.3172 | 89.7776 | 96.1939 | 102.6123
| PerthWind2090RCP4.5 | Perth | Wind | RCP4.5 | 2090 | 77.2529 | 83.354 | 89.8275 | 96.2535 | 102.6809
| PerthWind2095RCP4.5 | Perth | Wind | RCP4.5 | 2095 | 77.2808 | 83.3909 | 89.8773 | 96.3131 | 102.7494
| PerthWind2100RCP4.5 | Perth | Wind | RCP4.5 | 2100 | 77.3086 | 83.4277 | 89.9272 | 96.3728 | 102.818
| PerthWind2023RCP6.0 | Perth | Wind | RCP6.0 | 2023 | 76.5564 | 82.5275 | 88.8272 | 95.1016 | 101.3834
| PerthWind2025RCP6.0 | Perth | Wind | RCP6.0 | 2025 | 76.6665 | 82.6598 | 88.9871 | 95.2868 | 101.5941
| PerthWind2030RCP6.0 | Perth | Wind | RCP6.0 | 2030 | 76.7767 | 82.7921 | 89.1469 | 95.472 | 101.8047
| PerthWind2035RCP6.0 | Perth | Wind | RCP6.0 | 2035 | 76.8869 | 82.9244 | 89.3068 | 95.6571 | 102.0154
| PerthWind2040RCP6.0 | Perth | Wind | RCP6.0 | 2040 | 76.9971 | 83.0567 | 89.4667 | 95.8423 | 102.2261
| PerthWind2045RCP6.0 | Perth | Wind | RCP6.0 | 2045 | 77.1073 | 83.189 | 89.6265 | 96.0275 | 102.4368
| PerthWind2050RCP6.0 | Perth | Wind | RCP6.0 | 2050 | 77.2022 | 83.2984 | 89.7547 | 96.1731 | 102.5993
| PerthWind2055RCP6.0 | Perth | Wind | RCP6.0 | 2055 | 77.187 | 83.2755 | 89.723 | 96.1336 | 102.5511
| PerthWind2060RCP6.0 | Perth | Wind | RCP6.0 | 2060 | 77.1718 | 83.2526 | 89.6914 | 96.094 | 102.503
| PerthWind2065RCP6.0 | Perth | Wind | RCP6.0 | 2065 | 77.1566 | 83.2296 | 89.6597 | 96.0545 | 102.4548
| PerthWind2070RCP6.0 | Perth | Wind | RCP6.0 | 2070 | 77.1414 | 83.2067 | 89.628 | 96.015 | 102.4067
| PerthWind2075RCP6.0 | Perth | Wind | RCP6.0 | 2075 | 77.1832 | 83.262 | 89.7028 | 96.1044 | 102.5095
| PerthWind2080RCP6.0 | Perth | Wind | RCP6.0 | 2080 | 77.225 | 83.3172 | 89.7776 | 96.1939 | 102.6123
| PerthWind2085RCP6.0 | Perth | Wind | RCP6.0 | 2085 | 77.2668 | 83.3725 | 89.8524 | 96.2833 | 102.7151
| PerthWind2090RCP6.0 | Perth | Wind | RCP6.0 | 2090 | 77.2529 | 83.3431 | 89.7981 | 96.2127 | 102.624
| PerthWind2095RCP6.0 | Perth | Wind | RCP6.0 | 2095 | 77.1972 | 83.2586 | 89.6691 | 96.0526 | 102.4301
| PerthWind2100RCP6.0 | Perth | Wind | RCP6.0 | 2100 | 77.1414 | 83.174 | 89.54 | 95.8925 | 102.2361
| PerthWind2023RCP8.5 | Perth | Wind | RCP8.5 | 2023 | 76.5564 | 82.5275 | 88.8272 | 95.1016 | 101.3834
| PerthWind2025RCP8.5 | Perth | Wind | RCP8.5 | 2025 | 76.7767 | 82.7921 | 89.1469 | 95.472 | 101.8047
| PerthWind2030RCP8.5 | Perth | Wind | RCP8.5 | 2030 | 76.9971 | 83.0567 | 89.4667 | 95.8423 | 102.2261
| PerthWind2035RCP8.5 | Perth | Wind | RCP8.5 | 2035 | 77.2174 | 83.3213 | 89.7864 | 96.2127 | 102.6474
| PerthWind2040RCP8.5 | Perth | Wind | RCP8.5 | 2040 | 77.1921 | 83.2831 | 89.7336 | 96.1468 | 102.5672
| PerthWind2045RCP8.5 | Perth | Wind | RCP8.5 | 2045 | 77.1668 | 83.2449 | 89.6808 | 96.0809 | 102.4869
| PerthWind2050RCP8.5 | Perth | Wind | RCP8.5 | 2050 | 77.1972 | 83.2804 | 89.7277 | 96.1342 | 102.5438
| PerthWind2055RCP8.5 | Perth | Wind | RCP8.5 | 2055 | 77.2529 | 83.354 | 89.8275 | 96.2535 | 102.6809
| PerthWind2060RCP8.5 | Perth | Wind | RCP8.5 | 2060 | 77.2529 | 83.3431 | 89.7981 | 96.2127 | 102.624
| PerthWind2065RCP8.5 | Perth | Wind | RCP8.5 | 2065 | 77.1972 | 83.2586 | 89.6691 | 96.0526 | 102.4301
| PerthWind2070RCP8.5 | Perth | Wind | RCP8.5 | 2070 | 77.1744 | 83.204 | 89.5664 | 95.9177 | 102.2595
| PerthWind2075RCP8.5 | Perth | Wind | RCP8.5 | 2075 | 77.2073 | 83.234 | 89.5928 | 95.9428 | 102.2829
| PerthWind2080RCP8.5 | Perth | Wind | RCP8.5 | 2080 | 77.2402 | 83.264 | 89.6192 | 95.9679 | 102.3063
| PerthWind2085RCP8.5 | Perth | Wind | RCP8.5 | 2085 | 77.2668 | 83.3049 | 89.6764 | 96.0338 | 102.3866
| PerthWind2090RCP8.5 | Perth | Wind | RCP8.5 | 2090 | 77.2934 | 83.3459 | 89.7336 | 96.0997 | 102.4668
| PerthWind2095RCP8.5 | Perth | Wind | RCP8.5 | 2095 | 77.2934 | 83.3459 | 89.7336 | 96.0997 | 102.4668
| PerthWind2100RCP8.5 | Perth | Wind | RCP8.5 | 2100 | 77.2934 | 83.3459 | 89.7336 | 96.0997 | 102.4668
| PetawawaIce Accretion2023RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2023 | 14.0283 | 16.7162 | 20.12 | 22.713 | 25.326
| PetawawaIce Accretion2025RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2025 | 14.1628 | 16.885 | 20.33 | 22.9578 | 25.599
| PetawawaIce Accretion2030RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2030 | 14.2973 | 17.0537 | 20.54 | 23.2027 | 25.872
| PetawawaIce Accretion2035RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2035 | 14.4318 | 17.2225 | 20.75 | 23.4475 | 26.145
| PetawawaIce Accretion2040RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2040 | 14.5664 | 17.3913 | 20.96 | 23.6923 | 26.418
| PetawawaIce Accretion2045RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2045 | 14.7009 | 17.56 | 21.17 | 23.9372 | 26.691
| PetawawaIce Accretion2050RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2050 | 14.8327 | 17.7388 | 21.412 | 24.2227 | 27.0245
| PetawawaIce Accretion2055RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2055 | 14.8299 | 17.7487 | 21.444 | 24.2634 | 27.085
| PetawawaIce Accretion2060RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2060 | 14.8271 | 17.7587 | 21.476 | 24.304 | 27.1454
| PetawawaIce Accretion2065RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2065 | 14.8243 | 17.7686 | 21.508 | 24.3447 | 27.2059
| PetawawaIce Accretion2070RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2070 | 14.8215 | 17.7786 | 21.54 | 24.3854 | 27.2664
| PetawawaIce Accretion2075RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2075 | 14.8285 | 17.8007 | 21.5767 | 24.4381 | 27.3294
| PetawawaIce Accretion2080RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2080 | 14.8354 | 17.8229 | 21.6133 | 24.4909 | 27.3924
| PetawawaIce Accretion2085RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2085 | 14.8424 | 17.845 | 21.65 | 24.5436 | 27.4554
| PetawawaIce Accretion2090RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2090 | 14.8494 | 17.8671 | 21.6867 | 24.5963 | 27.5184
| PetawawaIce Accretion2095RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2095 | 14.8563 | 17.8893 | 21.7233 | 24.6491 | 27.5814
| PetawawaIce Accretion2100RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2100 | 14.8633 | 17.9114 | 21.76 | 24.7018 | 27.6444
| PetawawaIce Accretion2023RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2023 | 14.0283 | 16.7162 | 20.12 | 22.713 | 25.326
| PetawawaIce Accretion2025RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2025 | 14.1628 | 16.885 | 20.33 | 22.9578 | 25.599
| PetawawaIce Accretion2030RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2030 | 14.2973 | 17.0537 | 20.54 | 23.2027 | 25.872
| PetawawaIce Accretion2035RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2035 | 14.4318 | 17.2225 | 20.75 | 23.4475 | 26.145
| PetawawaIce Accretion2040RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2040 | 14.5664 | 17.3913 | 20.96 | 23.6923 | 26.418
| PetawawaIce Accretion2045RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2045 | 14.7009 | 17.56 | 21.17 | 23.9372 | 26.691
| PetawawaIce Accretion2050RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2050 | 14.8327 | 17.7388 | 21.412 | 24.2227 | 27.0245
| PetawawaIce Accretion2055RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2055 | 14.8299 | 17.7487 | 21.444 | 24.2634 | 27.085
| PetawawaIce Accretion2060RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2060 | 14.8271 | 17.7587 | 21.476 | 24.304 | 27.1454
| PetawawaIce Accretion2065RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2065 | 14.8243 | 17.7686 | 21.508 | 24.3447 | 27.2059
| PetawawaIce Accretion2070RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2070 | 14.8215 | 17.7786 | 21.54 | 24.3854 | 27.2664
| PetawawaIce Accretion2075RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2075 | 14.832 | 17.8118 | 21.595 | 24.4645 | 27.3609
| PetawawaIce Accretion2080RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2080 | 14.8424 | 17.845 | 21.65 | 24.5436 | 27.4554
| PetawawaIce Accretion2085RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2085 | 14.8528 | 17.8782 | 21.705 | 24.6227 | 27.5499
| PetawawaIce Accretion2090RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2090 | 14.6592 | 17.6569 | 21.4467 | 24.3477 | 27.2412
| PetawawaIce Accretion2095RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2095 | 14.455 | 17.4023 | 21.1333 | 23.9937 | 26.838
| PetawawaIce Accretion2100RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2100 | 14.2509 | 17.1478 | 20.82 | 23.6396 | 26.4348
| PetawawaIce Accretion2023RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2023 | 14.0283 | 16.7162 | 20.12 | 22.713 | 25.326
| PetawawaIce Accretion2025RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2025 | 14.2973 | 17.0537 | 20.54 | 23.2027 | 25.872
| PetawawaIce Accretion2030RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2030 | 14.5664 | 17.3913 | 20.96 | 23.6923 | 26.418
| PetawawaIce Accretion2035RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2035 | 14.8354 | 17.7288 | 21.38 | 24.182 | 26.964
| PetawawaIce Accretion2040RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2040 | 14.8308 | 17.7454 | 21.4333 | 24.2498 | 27.0648
| PetawawaIce Accretion2045RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2045 | 14.8262 | 17.762 | 21.4867 | 24.3176 | 27.1656
| PetawawaIce Accretion2050RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2050 | 14.8354 | 17.8229 | 21.6133 | 24.4909 | 27.3924
| PetawawaIce Accretion2055RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2055 | 14.8494 | 17.8671 | 21.6867 | 24.5963 | 27.5184
| PetawawaIce Accretion2060RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2060 | 14.6592 | 17.6569 | 21.4467 | 24.3477 | 27.2412
| PetawawaIce Accretion2065RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2065 | 14.455 | 17.4023 | 21.1333 | 23.9937 | 26.838
| PetawawaIce Accretion2070RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2070 | 14.2231 | 17.1367 | 20.8267 | 23.6547 | 26.46
| PetawawaIce Accretion2075RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2075 | 14.1953 | 17.1257 | 20.8333 | 23.6697 | 26.4852
| PetawawaIce Accretion2080RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2080 | 14.1674 | 17.1146 | 20.84 | 23.6848 | 26.5104
| PetawawaIce Accretion2085RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2085 | 13.8891 | 16.8241 | 20.54 | 23.3797 | 26.1954
| PetawawaIce Accretion2090RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2090 | 13.6108 | 16.5336 | 20.24 | 23.0746 | 25.8804
| PetawawaIce Accretion2095RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2095 | 13.6108 | 16.5336 | 20.24 | 23.0746 | 25.8804
| PetawawaIce Accretion2100RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2100 | 13.6108 | 16.5336 | 20.24 | 23.0746 | 25.8804
| PetawawaWind2023RCP4.5 | Petawawa | Wind | RCP4.5 | 2023 | 76.7577 | 82.6127 | 88.7686 | 94.9348 | 101.0947
| PetawawaWind2025RCP4.5 | Petawawa | Wind | RCP4.5 | 2025 | 76.7436 | 82.5962 | 88.7493 | 94.9142 | 101.0728
| PetawawaWind2030RCP4.5 | Petawawa | Wind | RCP4.5 | 2030 | 76.7295 | 82.5796 | 88.73 | 94.8935 | 101.0508
| PetawawaWind2035RCP4.5 | Petawawa | Wind | RCP4.5 | 2035 | 76.7154 | 82.5631 | 88.7107 | 94.8729 | 101.0288
| PetawawaWind2040RCP4.5 | Petawawa | Wind | RCP4.5 | 2040 | 76.7014 | 82.5465 | 88.6915 | 94.8523 | 101.0068
| PetawawaWind2045RCP4.5 | Petawawa | Wind | RCP4.5 | 2045 | 76.6873 | 82.53 | 88.6722 | 94.8316 | 100.9848
| PetawawaWind2050RCP4.5 | Petawawa | Wind | RCP4.5 | 2050 | 76.747 | 82.5978 | 88.749 | 94.9157 | 101.0785
| PetawawaWind2055RCP4.5 | Petawawa | Wind | RCP4.5 | 2055 | 76.8207 | 82.6823 | 88.8451 | 95.0205 | 101.1942
| PetawawaWind2060RCP4.5 | Petawawa | Wind | RCP4.5 | 2060 | 76.8945 | 82.7667 | 88.9413 | 95.1252 | 101.3098
| PetawawaWind2065RCP4.5 | Petawawa | Wind | RCP4.5 | 2065 | 76.9683 | 82.8511 | 89.0374 | 95.23 | 101.4255
| PetawawaWind2070RCP4.5 | Petawawa | Wind | RCP4.5 | 2070 | 77.0421 | 82.9355 | 89.1335 | 95.3348 | 101.5412
| PetawawaWind2075RCP4.5 | Petawawa | Wind | RCP4.5 | 2075 | 77.0882 | 82.9949 | 89.2077 | 95.4236 | 101.6426
| PetawawaWind2080RCP4.5 | Petawawa | Wind | RCP4.5 | 2080 | 77.1343 | 83.0542 | 89.2818 | 95.5125 | 101.7441
| PetawawaWind2085RCP4.5 | Petawawa | Wind | RCP4.5 | 2085 | 77.1804 | 83.1135 | 89.356 | 95.6014 | 101.8455
| PetawawaWind2090RCP4.5 | Petawawa | Wind | RCP4.5 | 2090 | 77.2265 | 83.1728 | 89.4302 | 95.6903 | 101.947
| PetawawaWind2095RCP4.5 | Petawawa | Wind | RCP4.5 | 2095 | 77.2726 | 83.2321 | 89.5043 | 95.7792 | 102.0485
| PetawawaWind2100RCP4.5 | Petawawa | Wind | RCP4.5 | 2100 | 77.3187 | 83.2915 | 89.5785 | 95.868 | 102.1499
| PetawawaWind2023RCP6.0 | Petawawa | Wind | RCP6.0 | 2023 | 76.7577 | 82.6127 | 88.7686 | 94.9348 | 101.0947
| PetawawaWind2025RCP6.0 | Petawawa | Wind | RCP6.0 | 2025 | 76.7436 | 82.5962 | 88.7493 | 94.9142 | 101.0728
| PetawawaWind2030RCP6.0 | Petawawa | Wind | RCP6.0 | 2030 | 76.7295 | 82.5796 | 88.73 | 94.8935 | 101.0508
| PetawawaWind2035RCP6.0 | Petawawa | Wind | RCP6.0 | 2035 | 76.7154 | 82.5631 | 88.7107 | 94.8729 | 101.0288
| PetawawaWind2040RCP6.0 | Petawawa | Wind | RCP6.0 | 2040 | 76.7014 | 82.5465 | 88.6915 | 94.8523 | 101.0068
| PetawawaWind2045RCP6.0 | Petawawa | Wind | RCP6.0 | 2045 | 76.6873 | 82.53 | 88.6722 | 94.8316 | 100.9848
| PetawawaWind2050RCP6.0 | Petawawa | Wind | RCP6.0 | 2050 | 76.747 | 82.5978 | 88.749 | 94.9157 | 101.0785
| PetawawaWind2055RCP6.0 | Petawawa | Wind | RCP6.0 | 2055 | 76.8207 | 82.6823 | 88.8451 | 95.0205 | 101.1942
| PetawawaWind2060RCP6.0 | Petawawa | Wind | RCP6.0 | 2060 | 76.8945 | 82.7667 | 88.9413 | 95.1252 | 101.3098
| PetawawaWind2065RCP6.0 | Petawawa | Wind | RCP6.0 | 2065 | 76.9683 | 82.8511 | 89.0374 | 95.23 | 101.4255
| PetawawaWind2070RCP6.0 | Petawawa | Wind | RCP6.0 | 2070 | 77.0421 | 82.9355 | 89.1335 | 95.3348 | 101.5412
| PetawawaWind2075RCP6.0 | Petawawa | Wind | RCP6.0 | 2075 | 77.1112 | 83.0245 | 89.2447 | 95.4681 | 101.6934
| PetawawaWind2080RCP6.0 | Petawawa | Wind | RCP6.0 | 2080 | 77.1804 | 83.1135 | 89.356 | 95.6014 | 101.8455
| PetawawaWind2085RCP6.0 | Petawawa | Wind | RCP6.0 | 2085 | 77.2496 | 83.2025 | 89.4672 | 95.7347 | 101.9977
| PetawawaWind2090RCP6.0 | Petawawa | Wind | RCP6.0 | 2090 | 77.352 | 83.3246 | 89.6111 | 95.8998 | 102.1804
| PetawawaWind2095RCP6.0 | Petawawa | Wind | RCP6.0 | 2095 | 77.3853 | 83.3577 | 89.6438 | 95.9315 | 102.2108
| PetawawaWind2100RCP6.0 | Petawawa | Wind | RCP6.0 | 2100 | 77.4186 | 83.3908 | 89.6764 | 95.9633 | 102.2412
| PetawawaWind2023RCP8.5 | Petawawa | Wind | RCP8.5 | 2023 | 76.7577 | 82.6127 | 88.7686 | 94.9348 | 101.0947
| PetawawaWind2025RCP8.5 | Petawawa | Wind | RCP8.5 | 2025 | 76.7295 | 82.5796 | 88.73 | 94.8935 | 101.0508
| PetawawaWind2030RCP8.5 | Petawawa | Wind | RCP8.5 | 2030 | 76.7014 | 82.5465 | 88.6915 | 94.8523 | 101.0068
| PetawawaWind2035RCP8.5 | Petawawa | Wind | RCP8.5 | 2035 | 76.6732 | 82.5134 | 88.6529 | 94.811 | 100.9628
| PetawawaWind2040RCP8.5 | Petawawa | Wind | RCP8.5 | 2040 | 76.7961 | 82.6541 | 88.8131 | 94.9856 | 101.1556
| PetawawaWind2045RCP8.5 | Petawawa | Wind | RCP8.5 | 2045 | 76.9191 | 82.7948 | 88.9733 | 95.1602 | 101.3484
| PetawawaWind2050RCP8.5 | Petawawa | Wind | RCP8.5 | 2050 | 77.1343 | 83.0542 | 89.2818 | 95.5125 | 101.7441
| PetawawaWind2055RCP8.5 | Petawawa | Wind | RCP8.5 | 2055 | 77.2265 | 83.1728 | 89.4302 | 95.6903 | 101.947
| PetawawaWind2060RCP8.5 | Petawawa | Wind | RCP8.5 | 2060 | 77.352 | 83.3246 | 89.6111 | 95.8998 | 102.1804
| PetawawaWind2065RCP8.5 | Petawawa | Wind | RCP8.5 | 2065 | 77.3853 | 83.3577 | 89.6438 | 95.9315 | 102.2108
| PetawawaWind2070RCP8.5 | Petawawa | Wind | RCP8.5 | 2070 | 77.4109 | 83.3742 | 89.6497 | 95.9284 | 102.2007
| PetawawaWind2075RCP8.5 | Petawawa | Wind | RCP8.5 | 2075 | 77.4033 | 83.3577 | 89.623 | 95.8934 | 102.1601
| PetawawaWind2080RCP8.5 | Petawawa | Wind | RCP8.5 | 2080 | 77.3956 | 83.3411 | 89.5963 | 95.8585 | 102.1195
| PetawawaWind2085RCP8.5 | Petawawa | Wind | RCP8.5 | 2085 | 77.3456 | 83.2666 | 89.4939 | 95.7252 | 101.9622
| PetawawaWind2090RCP8.5 | Petawawa | Wind | RCP8.5 | 2090 | 77.2957 | 83.1921 | 89.3916 | 95.5919 | 101.805
| PetawawaWind2095RCP8.5 | Petawawa | Wind | RCP8.5 | 2095 | 77.2957 | 83.1921 | 89.3916 | 95.5919 | 101.805
| PetawawaWind2100RCP8.5 | Petawawa | Wind | RCP8.5 | 2100 | 77.2957 | 83.1921 | 89.3916 | 95.5919 | 101.805
| PeterboroughIce Accretion2023RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2023 | 17.5875 | 20.999 | 25.325 | 28.6172 | 31.941
| PeterboroughIce Accretion2025RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2025 | 17.6542 | 21.0958 | 25.4625 | 28.7867 | 32.1352
| PeterboroughIce Accretion2030RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2030 | 17.7209 | 21.1927 | 25.6 | 28.9562 | 32.3295
| PeterboroughIce Accretion2035RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2035 | 17.7876 | 21.2895 | 25.7375 | 29.1257 | 32.5237
| PeterboroughIce Accretion2040RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2040 | 17.8543 | 21.3863 | 25.875 | 29.2952 | 32.718
| PeterboroughIce Accretion2045RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2045 | 17.9209 | 21.4832 | 26.0125 | 29.4647 | 32.9123
| PeterboroughIce Accretion2050RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2050 | 17.8867 | 21.4804 | 26.045 | 29.5212 | 32.9931
| PeterboroughIce Accretion2055RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2055 | 17.7858 | 21.3808 | 25.94 | 29.4082 | 32.8797
| PeterboroughIce Accretion2060RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2060 | 17.6849 | 21.2812 | 25.835 | 29.2952 | 32.7663
| PeterboroughIce Accretion2065RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2065 | 17.584 | 21.1816 | 25.73 | 29.1822 | 32.6529
| PeterboroughIce Accretion2070RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2070 | 17.4831 | 21.082 | 25.625 | 29.0692 | 32.5395
| PeterboroughIce Accretion2075RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2075 | 17.5237 | 21.1615 | 25.7542 | 29.2387 | 32.7442
| PeterboroughIce Accretion2080RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2080 | 17.5643 | 21.2411 | 25.8833 | 29.4082 | 32.949
| PeterboroughIce Accretion2085RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2085 | 17.6049 | 21.3206 | 26.0125 | 29.5777 | 33.1538
| PeterboroughIce Accretion2090RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2090 | 17.6455 | 21.4002 | 26.1417 | 29.7472 | 33.3585
| PeterboroughIce Accretion2095RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2095 | 17.6861 | 21.4797 | 26.2708 | 29.9167 | 33.5632
| PeterboroughIce Accretion2100RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2100 | 17.7267 | 21.5592 | 26.4 | 30.0862 | 33.768
| PeterboroughIce Accretion2023RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2023 | 17.5875 | 20.999 | 25.325 | 28.6172 | 31.941
| PeterboroughIce Accretion2025RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2025 | 17.6542 | 21.0958 | 25.4625 | 28.7867 | 32.1352
| PeterboroughIce Accretion2030RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2030 | 17.7209 | 21.1927 | 25.6 | 28.9562 | 32.3295
| PeterboroughIce Accretion2035RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2035 | 17.7876 | 21.2895 | 25.7375 | 29.1257 | 32.5237
| PeterboroughIce Accretion2040RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2040 | 17.8543 | 21.3863 | 25.875 | 29.2952 | 32.718
| PeterboroughIce Accretion2045RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2045 | 17.9209 | 21.4832 | 26.0125 | 29.4647 | 32.9123
| PeterboroughIce Accretion2050RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2050 | 17.8867 | 21.4804 | 26.045 | 29.5212 | 32.9931
| PeterboroughIce Accretion2055RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2055 | 17.7858 | 21.3808 | 25.94 | 29.4082 | 32.8797
| PeterboroughIce Accretion2060RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2060 | 17.6849 | 21.2812 | 25.835 | 29.2952 | 32.7663
| PeterboroughIce Accretion2065RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2065 | 17.584 | 21.1816 | 25.73 | 29.1822 | 32.6529
| PeterboroughIce Accretion2070RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2070 | 17.4831 | 21.082 | 25.625 | 29.0692 | 32.5395
| PeterboroughIce Accretion2075RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2075 | 17.544 | 21.2013 | 25.8187 | 29.3235 | 32.8466
| PeterboroughIce Accretion2080RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2080 | 17.6049 | 21.3206 | 26.0125 | 29.5777 | 33.1538
| PeterboroughIce Accretion2085RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2085 | 17.6658 | 21.4399 | 26.2063 | 29.832 | 33.4609
| PeterboroughIce Accretion2090RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2090 | 17.3498 | 21.1512 | 25.95 | 29.606 | 33.243
| PeterboroughIce Accretion2095RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2095 | 16.9728 | 20.7431 | 25.5 | 29.1257 | 32.718
| PeterboroughIce Accretion2100RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2100 | 16.5959 | 20.335 | 25.05 | 28.6455 | 32.193
| PeterboroughIce Accretion2023RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2023 | 17.5875 | 20.999 | 25.325 | 28.6172 | 31.941
| PeterboroughIce Accretion2025RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2025 | 17.7209 | 21.1927 | 25.6 | 28.9562 | 32.3295
| PeterboroughIce Accretion2030RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2030 | 17.8543 | 21.3863 | 25.875 | 29.2952 | 32.718
| PeterboroughIce Accretion2035RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2035 | 17.9876 | 21.58 | 26.15 | 29.6342 | 33.1065
| PeterboroughIce Accretion2040RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2040 | 17.8195 | 21.414 | 25.975 | 29.4459 | 32.9175
| PeterboroughIce Accretion2045RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2045 | 17.6513 | 21.248 | 25.8 | 29.2576 | 32.7285
| PeterboroughIce Accretion2050RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2050 | 17.5643 | 21.2411 | 25.8833 | 29.4082 | 32.949
| PeterboroughIce Accretion2055RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2055 | 17.6455 | 21.4002 | 26.1417 | 29.7472 | 33.3585
| PeterboroughIce Accretion2060RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2060 | 17.3498 | 21.1512 | 25.95 | 29.606 | 33.243
| PeterboroughIce Accretion2065RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2065 | 16.9728 | 20.7431 | 25.5 | 29.1257 | 32.718
| PeterboroughIce Accretion2070RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2070 | 16.2306 | 19.9338 | 24.6083 | 28.1558 | 31.6785
| PeterboroughIce Accretion2075RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2075 | 15.8653 | 19.5327 | 24.1667 | 27.6662 | 31.164
| PeterboroughIce Accretion2080RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2080 | 15.5 | 19.1315 | 23.725 | 27.1765 | 30.6495
| PeterboroughIce Accretion2085RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2085 | 14.9259 | 18.4779 | 22.9625 | 26.3431 | 29.736
| PeterboroughIce Accretion2090RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2090 | 14.3518 | 17.8242 | 22.2 | 25.5097 | 28.8225
| PeterboroughIce Accretion2095RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2095 | 14.3518 | 17.8242 | 22.2 | 25.5097 | 28.8225
| PeterboroughIce Accretion2100RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2100 | 14.3518 | 17.8242 | 22.2 | 25.5097 | 28.8225
| PeterboroughWind2023RCP4.5 | Peterborough | Wind | RCP4.5 | 2023 | 76.184 | 81.9709 | 88.044 | 94.1412 | 100.2297
| PeterboroughWind2025RCP4.5 | Peterborough | Wind | RCP4.5 | 2025 | 76.1891 | 81.9832 | 88.0645 | 94.1678 | 100.2632
| PeterboroughWind2030RCP4.5 | Peterborough | Wind | RCP4.5 | 2030 | 76.1941 | 81.9955 | 88.0851 | 94.1945 | 100.2966
| PeterboroughWind2035RCP4.5 | Peterborough | Wind | RCP4.5 | 2035 | 76.1992 | 82.0078 | 88.1056 | 94.2212 | 100.33
| PeterboroughWind2040RCP4.5 | Peterborough | Wind | RCP4.5 | 2040 | 76.2043 | 82.02 | 88.1261 | 94.2479 | 100.3635
| PeterboroughWind2045RCP4.5 | Peterborough | Wind | RCP4.5 | 2045 | 76.2093 | 82.0323 | 88.1467 | 94.2746 | 100.3969
| PeterboroughWind2050RCP4.5 | Peterborough | Wind | RCP4.5 | 2050 | 76.3208 | 82.1805 | 88.3397 | 94.5046 | 100.6651
| PeterboroughWind2055RCP4.5 | Peterborough | Wind | RCP4.5 | 2055 | 76.4272 | 82.3163 | 88.5122 | 94.708 | 100.8998
| PeterboroughWind2060RCP4.5 | Peterborough | Wind | RCP4.5 | 2060 | 76.5336 | 82.4522 | 88.6846 | 94.9114 | 101.1346
| PeterboroughWind2065RCP4.5 | Peterborough | Wind | RCP4.5 | 2065 | 76.6399 | 82.588 | 88.8571 | 95.1148 | 101.3693
| PeterboroughWind2070RCP4.5 | Peterborough | Wind | RCP4.5 | 2070 | 76.7463 | 82.7239 | 89.0296 | 95.3182 | 101.6041
| PeterboroughWind2075RCP4.5 | Peterborough | Wind | RCP4.5 | 2075 | 76.8476 | 82.8562 | 89.2012 | 95.5238 | 101.8449
| PeterboroughWind2080RCP4.5 | Peterborough | Wind | RCP4.5 | 2080 | 76.9489 | 82.9885 | 89.3728 | 95.7293 | 102.0856
| PeterboroughWind2085RCP4.5 | Peterborough | Wind | RCP4.5 | 2085 | 77.0503 | 83.1208 | 89.5444 | 95.9349 | 102.3264
| PeterboroughWind2090RCP4.5 | Peterborough | Wind | RCP4.5 | 2090 | 77.1516 | 83.2531 | 89.716 | 96.1405 | 102.5672
| PeterboroughWind2095RCP4.5 | Peterborough | Wind | RCP4.5 | 2095 | 77.2529 | 83.3854 | 89.8876 | 96.3461 | 102.8079
| PeterboroughWind2100RCP4.5 | Peterborough | Wind | RCP4.5 | 2100 | 77.3542 | 83.5177 | 90.0592 | 96.5517 | 103.0487
| PeterboroughWind2023RCP6.0 | Peterborough | Wind | RCP6.0 | 2023 | 76.184 | 81.9709 | 88.044 | 94.1412 | 100.2297
| PeterboroughWind2025RCP6.0 | Peterborough | Wind | RCP6.0 | 2025 | 76.1891 | 81.9832 | 88.0645 | 94.1678 | 100.2632
| PeterboroughWind2030RCP6.0 | Peterborough | Wind | RCP6.0 | 2030 | 76.1941 | 81.9955 | 88.0851 | 94.1945 | 100.2966
| PeterboroughWind2035RCP6.0 | Peterborough | Wind | RCP6.0 | 2035 | 76.1992 | 82.0078 | 88.1056 | 94.2212 | 100.33
| PeterboroughWind2040RCP6.0 | Peterborough | Wind | RCP6.0 | 2040 | 76.2043 | 82.02 | 88.1261 | 94.2479 | 100.3635
| PeterboroughWind2045RCP6.0 | Peterborough | Wind | RCP6.0 | 2045 | 76.2093 | 82.0323 | 88.1467 | 94.2746 | 100.3969
| PeterboroughWind2050RCP6.0 | Peterborough | Wind | RCP6.0 | 2050 | 76.3208 | 82.1805 | 88.3397 | 94.5046 | 100.6651
| PeterboroughWind2055RCP6.0 | Peterborough | Wind | RCP6.0 | 2055 | 76.4272 | 82.3163 | 88.5122 | 94.708 | 100.8998
| PeterboroughWind2060RCP6.0 | Peterborough | Wind | RCP6.0 | 2060 | 76.5336 | 82.4522 | 88.6846 | 94.9114 | 101.1346
| PeterboroughWind2065RCP6.0 | Peterborough | Wind | RCP6.0 | 2065 | 76.6399 | 82.588 | 88.8571 | 95.1148 | 101.3693
| PeterboroughWind2070RCP6.0 | Peterborough | Wind | RCP6.0 | 2070 | 76.7463 | 82.7239 | 89.0296 | 95.3182 | 101.6041
| PeterboroughWind2075RCP6.0 | Peterborough | Wind | RCP6.0 | 2075 | 76.8983 | 82.9223 | 89.287 | 95.6265 | 101.9652
| PeterboroughWind2080RCP6.0 | Peterborough | Wind | RCP6.0 | 2080 | 77.0503 | 83.1208 | 89.5444 | 95.9349 | 102.3264
| PeterboroughWind2085RCP6.0 | Peterborough | Wind | RCP6.0 | 2085 | 77.2022 | 83.3193 | 89.8018 | 96.2433 | 102.6876
| PeterboroughWind2090RCP6.0 | Peterborough | Wind | RCP6.0 | 2090 | 77.6506 | 83.886 | 90.5197 | 97.0915 | 103.6673
| PeterboroughWind2095RCP6.0 | Peterborough | Wind | RCP6.0 | 2095 | 77.9469 | 84.2543 | 90.9803 | 97.6314 | 104.286
| PeterboroughWind2100RCP6.0 | Peterborough | Wind | RCP6.0 | 2100 | 78.2433 | 84.6226 | 91.4408 | 98.1712 | 104.9046
| PeterboroughWind2023RCP8.5 | Peterborough | Wind | RCP8.5 | 2023 | 76.184 | 81.9709 | 88.044 | 94.1412 | 100.2297
| PeterboroughWind2025RCP8.5 | Peterborough | Wind | RCP8.5 | 2025 | 76.1941 | 81.9955 | 88.0851 | 94.1945 | 100.2966
| PeterboroughWind2030RCP8.5 | Peterborough | Wind | RCP8.5 | 2030 | 76.2043 | 82.02 | 88.1261 | 94.2479 | 100.3635
| PeterboroughWind2035RCP8.5 | Peterborough | Wind | RCP8.5 | 2035 | 76.2144 | 82.0446 | 88.1672 | 94.3012 | 100.4304
| PeterboroughWind2040RCP8.5 | Peterborough | Wind | RCP8.5 | 2040 | 76.3917 | 82.271 | 88.4547 | 94.6402 | 100.8216
| PeterboroughWind2045RCP8.5 | Peterborough | Wind | RCP8.5 | 2045 | 76.569 | 82.4974 | 88.7421 | 94.9792 | 101.2128
| PeterboroughWind2050RCP8.5 | Peterborough | Wind | RCP8.5 | 2050 | 76.9489 | 82.9885 | 89.3728 | 95.7293 | 102.0856
| PeterboroughWind2055RCP8.5 | Peterborough | Wind | RCP8.5 | 2055 | 77.1516 | 83.2531 | 89.716 | 96.1405 | 102.5672
| PeterboroughWind2060RCP8.5 | Peterborough | Wind | RCP8.5 | 2060 | 77.6506 | 83.886 | 90.5197 | 97.0915 | 103.6673
| PeterboroughWind2065RCP8.5 | Peterborough | Wind | RCP8.5 | 2065 | 77.9469 | 84.2543 | 90.9803 | 97.6314 | 104.286
| PeterboroughWind2070RCP8.5 | Peterborough | Wind | RCP8.5 | 2070 | 78.2458 | 84.6417 | 91.4789 | 98.2214 | 104.9748
| PeterboroughWind2075RCP8.5 | Peterborough | Wind | RCP8.5 | 2075 | 78.2483 | 84.6608 | 91.5171 | 98.2717 | 105.0451
| PeterboroughWind2080RCP8.5 | Peterborough | Wind | RCP8.5 | 2080 | 78.2508 | 84.6798 | 91.5552 | 98.3219 | 105.1153
| PeterboroughWind2085RCP8.5 | Peterborough | Wind | RCP8.5 | 2085 | 78.4218 | 84.9254 | 91.8984 | 98.7503 | 105.6219
| PeterboroughWind2090RCP8.5 | Peterborough | Wind | RCP8.5 | 2090 | 78.5928 | 85.1709 | 92.2416 | 99.1787 | 106.1285
| PeterboroughWind2095RCP8.5 | Peterborough | Wind | RCP8.5 | 2095 | 78.5928 | 85.1709 | 92.2416 | 99.1787 | 106.1285
| PeterboroughWind2100RCP8.5 | Peterborough | Wind | RCP8.5 | 2100 | 78.5928 | 85.1709 | 92.2416 | 99.1787 | 106.1285
| PetroliaIce Accretion2023RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2023 | 14.7422 | 17.6939 | 21.428 | 24.2634 | 27.1102
| PetroliaIce Accretion2025RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2025 | 14.6835 | 17.6361 | 21.3693 | 24.2054 | 27.0501
| PetroliaIce Accretion2030RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2030 | 14.6248 | 17.5783 | 21.3107 | 24.1473 | 26.99
| PetroliaIce Accretion2035RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2035 | 14.5661 | 17.5205 | 21.252 | 24.0893 | 26.93
| PetroliaIce Accretion2040RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2040 | 14.5075 | 17.4626 | 21.1933 | 24.0313 | 26.8699
| PetroliaIce Accretion2045RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2045 | 14.4488 | 17.4048 | 21.1347 | 23.9733 | 26.8099
| PetroliaIce Accretion2050RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2050 | 14.1207 | 17.0475 | 20.7328 | 23.5424 | 26.3451
| PetroliaIce Accretion2055RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2055 | 13.8512 | 16.7481 | 20.3896 | 23.1695 | 25.9404
| PetroliaIce Accretion2060RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2060 | 13.5818 | 16.4486 | 20.0464 | 22.7966 | 25.5357
| PetroliaIce Accretion2065RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2065 | 13.3124 | 16.1491 | 19.7032 | 22.4237 | 25.131
| PetroliaIce Accretion2070RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2070 | 13.0429 | 15.8497 | 19.36 | 22.0508 | 24.7262
| PetroliaIce Accretion2075RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2075 | 12.9205 | 15.7219 | 19.228 | 21.9099 | 24.5784
| PetroliaIce Accretion2080RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2080 | 12.798 | 15.594 | 19.096 | 21.7691 | 24.4306
| PetroliaIce Accretion2085RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2085 | 12.6755 | 15.4662 | 18.964 | 21.6282 | 24.2827
| PetroliaIce Accretion2090RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2090 | 12.5531 | 15.3384 | 18.832 | 21.4873 | 24.1349
| PetroliaIce Accretion2095RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2095 | 12.4306 | 15.2106 | 18.7 | 21.3465 | 23.987
| PetroliaIce Accretion2100RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2100 | 12.3081 | 15.0828 | 18.568 | 21.2056 | 23.8392
| PetroliaIce Accretion2023RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2023 | 14.7422 | 17.6939 | 21.428 | 24.2634 | 27.1102
| PetroliaIce Accretion2025RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2025 | 14.6835 | 17.6361 | 21.3693 | 24.2054 | 27.0501
| PetroliaIce Accretion2030RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2030 | 14.6248 | 17.5783 | 21.3107 | 24.1473 | 26.99
| PetroliaIce Accretion2035RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2035 | 14.5661 | 17.5205 | 21.252 | 24.0893 | 26.93
| PetroliaIce Accretion2040RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2040 | 14.5075 | 17.4626 | 21.1933 | 24.0313 | 26.8699
| PetroliaIce Accretion2045RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2045 | 14.4488 | 17.4048 | 21.1347 | 23.9733 | 26.8099
| PetroliaIce Accretion2050RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2050 | 14.1207 | 17.0475 | 20.7328 | 23.5424 | 26.3451
| PetroliaIce Accretion2055RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2055 | 13.8512 | 16.7481 | 20.3896 | 23.1695 | 25.9404
| PetroliaIce Accretion2060RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2060 | 13.5818 | 16.4486 | 20.0464 | 22.7966 | 25.5357
| PetroliaIce Accretion2065RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2065 | 13.3124 | 16.1491 | 19.7032 | 22.4237 | 25.131
| PetroliaIce Accretion2070RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2070 | 13.0429 | 15.8497 | 19.36 | 22.0508 | 24.7262
| PetroliaIce Accretion2075RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2075 | 12.8592 | 15.6579 | 19.162 | 21.8395 | 24.5045
| PetroliaIce Accretion2080RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2080 | 12.6755 | 15.4662 | 18.964 | 21.6282 | 24.2827
| PetroliaIce Accretion2085RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2085 | 12.4918 | 15.2745 | 18.766 | 21.4169 | 24.061
| PetroliaIce Accretion2090RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2090 | 11.9356 | 14.6628 | 18.084 | 20.6669 | 23.2478
| PetroliaIce Accretion2095RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2095 | 11.5631 | 14.2428 | 17.6 | 20.1283 | 22.6565
| PetroliaIce Accretion2100RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2100 | 11.1906 | 13.8228 | 17.116 | 19.5897 | 22.0651
| PetroliaIce Accretion2023RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2023 | 14.7422 | 17.6939 | 21.428 | 24.2634 | 27.1102
| PetroliaIce Accretion2025RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2025 | 14.6248 | 17.5783 | 21.3107 | 24.1473 | 26.99
| PetroliaIce Accretion2030RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2030 | 14.5075 | 17.4626 | 21.1933 | 24.0313 | 26.8699
| PetroliaIce Accretion2035RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2035 | 14.3901 | 17.347 | 21.076 | 23.9153 | 26.7498
| PetroliaIce Accretion2040RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2040 | 13.941 | 16.8479 | 20.504 | 23.2938 | 26.0753
| PetroliaIce Accretion2045RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2045 | 13.492 | 16.3488 | 19.932 | 22.6723 | 25.4008
| PetroliaIce Accretion2050RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2050 | 12.798 | 15.594 | 19.096 | 21.7691 | 24.4306
| PetroliaIce Accretion2055RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2055 | 12.5531 | 15.3384 | 18.832 | 21.4873 | 24.1349
| PetroliaIce Accretion2060RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2060 | 11.9356 | 14.6628 | 18.084 | 20.6669 | 23.2478
| PetroliaIce Accretion2065RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2065 | 11.5631 | 14.2428 | 17.6 | 20.1283 | 22.6565
| PetroliaIce Accretion2070RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2070 | 10.8997 | 13.5063 | 16.7567 | 19.2085 | 21.6493
| PetroliaIce Accretion2075RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2075 | 10.6089 | 13.1898 | 16.3973 | 18.8273 | 21.2335
| PetroliaIce Accretion2080RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2080 | 10.318 | 12.8733 | 16.038 | 18.4461 | 20.8177
| PetroliaIce Accretion2085RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2085 | 9.6138 | 12.0333 | 15.037 | 17.3026 | 19.5565
| PetroliaIce Accretion2090RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2090 | 8.9096 | 11.1934 | 14.036 | 16.159 | 18.2952
| PetroliaIce Accretion2095RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2095 | 8.9096 | 11.1934 | 14.036 | 16.159 | 18.2952
| PetroliaIce Accretion2100RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2100 | 8.9096 | 11.1934 | 14.036 | 16.159 | 18.2952
| PetroliaWind2023RCP4.5 | Petrolia | Wind | RCP4.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
| PetroliaWind2025RCP4.5 | Petrolia | Wind | RCP4.5 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
| PetroliaWind2030RCP4.5 | Petrolia | Wind | RCP4.5 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
| PetroliaWind2035RCP4.5 | Petrolia | Wind | RCP4.5 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
| PetroliaWind2040RCP4.5 | Petrolia | Wind | RCP4.5 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
| PetroliaWind2045RCP4.5 | Petrolia | Wind | RCP4.5 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
| PetroliaWind2050RCP4.5 | Petrolia | Wind | RCP4.5 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
| PetroliaWind2055RCP4.5 | Petrolia | Wind | RCP4.5 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
| PetroliaWind2060RCP4.5 | Petrolia | Wind | RCP4.5 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
| PetroliaWind2065RCP4.5 | Petrolia | Wind | RCP4.5 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
| PetroliaWind2070RCP4.5 | Petrolia | Wind | RCP4.5 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
| PetroliaWind2075RCP4.5 | Petrolia | Wind | RCP4.5 | 2075 | 85.7411 | 92.542 | 99.746 | 106.9048 | 114.0736
| PetroliaWind2080RCP4.5 | Petrolia | Wind | RCP4.5 | 2080 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
| PetroliaWind2085RCP4.5 | Petrolia | Wind | RCP4.5 | 2085 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
| PetroliaWind2090RCP4.5 | Petrolia | Wind | RCP4.5 | 2090 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
| PetroliaWind2095RCP4.5 | Petrolia | Wind | RCP4.5 | 2095 | 86.3278 | 93.3015 | 100.7326 | 108.0792 | 115.444
| PetroliaWind2100RCP4.5 | Petrolia | Wind | RCP4.5 | 2100 | 86.4745 | 93.4914 | 100.9792 | 108.3728 | 115.7866
| PetroliaWind2023RCP6.0 | Petrolia | Wind | RCP6.0 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
| PetroliaWind2025RCP6.0 | Petrolia | Wind | RCP6.0 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
| PetroliaWind2030RCP6.0 | Petrolia | Wind | RCP6.0 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
| PetroliaWind2035RCP6.0 | Petrolia | Wind | RCP6.0 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
| PetroliaWind2040RCP6.0 | Petrolia | Wind | RCP6.0 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
| PetroliaWind2045RCP6.0 | Petrolia | Wind | RCP6.0 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
| PetroliaWind2050RCP6.0 | Petrolia | Wind | RCP6.0 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
| PetroliaWind2055RCP6.0 | Petrolia | Wind | RCP6.0 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
| PetroliaWind2060RCP6.0 | Petrolia | Wind | RCP6.0 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
| PetroliaWind2065RCP6.0 | Petrolia | Wind | RCP6.0 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
| PetroliaWind2070RCP6.0 | Petrolia | Wind | RCP6.0 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
| PetroliaWind2075RCP6.0 | Petrolia | Wind | RCP6.0 | 2075 | 85.8144 | 92.637 | 99.8693 | 107.0516 | 114.2449
| PetroliaWind2080RCP6.0 | Petrolia | Wind | RCP6.0 | 2080 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
| PetroliaWind2085RCP6.0 | Petrolia | Wind | RCP6.0 | 2085 | 86.2545 | 93.2066 | 100.6093 | 107.9324 | 115.2727
| PetroliaWind2090RCP6.0 | Petrolia | Wind | RCP6.0 | 2090 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
| PetroliaWind2095RCP6.0 | Petrolia | Wind | RCP6.0 | 2095 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
| PetroliaWind2100RCP6.0 | Petrolia | Wind | RCP6.0 | 2100 | 87.5746 | 94.8494 | 102.6452 | 110.3127 | 117.9987
| PetroliaWind2023RCP8.5 | Petrolia | Wind | RCP8.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
| PetroliaWind2025RCP8.5 | Petrolia | Wind | RCP8.5 | 2025 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
| PetroliaWind2030RCP8.5 | Petrolia | Wind | RCP8.5 | 2030 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
| PetroliaWind2035RCP8.5 | Petrolia | Wind | RCP8.5 | 2035 | 85.586 | 92.3248 | 99.4504 | 106.5378 | 113.6304
| PetroliaWind2040RCP8.5 | Petrolia | Wind | RCP8.5 | 2040 | 85.5888 | 92.3339 | 99.4667 | 106.5622 | 113.6639
| PetroliaWind2045RCP8.5 | Petrolia | Wind | RCP8.5 | 2045 | 85.5916 | 92.343 | 99.4831 | 106.5867 | 113.6974
| PetroliaWind2050RCP8.5 | Petrolia | Wind | RCP8.5 | 2050 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
| PetroliaWind2055RCP8.5 | Petrolia | Wind | RCP8.5 | 2055 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
| PetroliaWind2060RCP8.5 | Petrolia | Wind | RCP8.5 | 2060 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
| PetroliaWind2065RCP8.5 | Petrolia | Wind | RCP8.5 | 2065 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
| PetroliaWind2070RCP8.5 | Petrolia | Wind | RCP8.5 | 2070 | 87.882 | 95.2383 | 103.1385 | 110.8929 | 118.669
| PetroliaWind2075RCP8.5 | Petrolia | Wind | RCP8.5 | 2075 | 88.1895 | 95.6271 | 103.6317 | 111.4732 | 119.3393
| PetroliaWind2080RCP8.5 | Petrolia | Wind | RCP8.5 | 2080 | 88.4969 | 96.016 | 104.125 | 112.0534 | 120.0096
| PetroliaWind2085RCP8.5 | Petrolia | Wind | RCP8.5 | 2085 | 88.8396 | 96.4489 | 104.664 | 112.6826 | 120.7358
| PetroliaWind2090RCP8.5 | Petrolia | Wind | RCP8.5 | 2090 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
| PetroliaWind2095RCP8.5 | Petrolia | Wind | RCP8.5 | 2095 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
| PetroliaWind2100RCP8.5 | Petrolia | Wind | RCP8.5 | 2100 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
| Pickering (Dunbarton)Ice Accretion2023RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| Pickering (Dunbarton)Ice Accretion2025RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| Pickering (Dunbarton)Ice Accretion2030RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| Pickering (Dunbarton)Ice Accretion2035RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| Pickering (Dunbarton)Ice Accretion2040RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| Pickering (Dunbarton)Ice Accretion2045RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| Pickering (Dunbarton)Ice Accretion2050RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| Pickering (Dunbarton)Ice Accretion2055RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| Pickering (Dunbarton)Ice Accretion2060RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| Pickering (Dunbarton)Ice Accretion2065RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| Pickering (Dunbarton)Ice Accretion2070RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| Pickering (Dunbarton)Ice Accretion2075RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
| Pickering (Dunbarton)Ice Accretion2080RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| Pickering (Dunbarton)Ice Accretion2085RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| Pickering (Dunbarton)Ice Accretion2090RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| Pickering (Dunbarton)Ice Accretion2095RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
| Pickering (Dunbarton)Ice Accretion2100RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
| Pickering (Dunbarton)Ice Accretion2023RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| Pickering (Dunbarton)Ice Accretion2025RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| Pickering (Dunbarton)Ice Accretion2030RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| Pickering (Dunbarton)Ice Accretion2035RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| Pickering (Dunbarton)Ice Accretion2040RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| Pickering (Dunbarton)Ice Accretion2045RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| Pickering (Dunbarton)Ice Accretion2050RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| Pickering (Dunbarton)Ice Accretion2055RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| Pickering (Dunbarton)Ice Accretion2060RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| Pickering (Dunbarton)Ice Accretion2065RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| Pickering (Dunbarton)Ice Accretion2070RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| Pickering (Dunbarton)Ice Accretion2075RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
| Pickering (Dunbarton)Ice Accretion2080RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| Pickering (Dunbarton)Ice Accretion2085RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
| Pickering (Dunbarton)Ice Accretion2090RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| Pickering (Dunbarton)Ice Accretion2095RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| Pickering (Dunbarton)Ice Accretion2100RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
| Pickering (Dunbarton)Ice Accretion2023RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| Pickering (Dunbarton)Ice Accretion2025RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| Pickering (Dunbarton)Ice Accretion2030RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| Pickering (Dunbarton)Ice Accretion2035RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
| Pickering (Dunbarton)Ice Accretion2040RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
| Pickering (Dunbarton)Ice Accretion2045RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
| Pickering (Dunbarton)Ice Accretion2050RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| Pickering (Dunbarton)Ice Accretion2055RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| Pickering (Dunbarton)Ice Accretion2060RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| Pickering (Dunbarton)Ice Accretion2065RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| Pickering (Dunbarton)Ice Accretion2070RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
| Pickering (Dunbarton)Ice Accretion2075RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
| Pickering (Dunbarton)Ice Accretion2080RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
| Pickering (Dunbarton)Ice Accretion2085RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
| Pickering (Dunbarton)Ice Accretion2090RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| Pickering (Dunbarton)Ice Accretion2095RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| Pickering (Dunbarton)Ice Accretion2100RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| Pickering (Dunbarton)Wind2023RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2023 | 84.8244 | 91.3223 | 98.1568 | 104.9963 | 111.8317
| Pickering (Dunbarton)Wind2025RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2025 | 84.8399 | 91.3557 | 98.2107 | 105.068 | 111.9211
| Pickering (Dunbarton)Wind2030RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2030 | 84.8554 | 91.3891 | 98.2646 | 105.1396 | 112.0105
| Pickering (Dunbarton)Wind2035RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2035 | 84.8709 | 91.4225 | 98.3185 | 105.2113 | 112.0998
| Pickering (Dunbarton)Wind2040RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2040 | 84.8864 | 91.456 | 98.3724 | 105.2829 | 112.1892
| Pickering (Dunbarton)Wind2045RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2045 | 84.9019 | 91.4894 | 98.4263 | 105.3546 | 112.2786
| Pickering (Dunbarton)Wind2050RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2050 | 85.0004 | 91.6267 | 98.6115 | 105.5793 | 112.5467
| Pickering (Dunbarton)Wind2055RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2055 | 85.0833 | 91.7306 | 98.7428 | 105.7324 | 112.7255
| Pickering (Dunbarton)Wind2060RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2060 | 85.1662 | 91.8345 | 98.8742 | 105.8855 | 112.9042
| Pickering (Dunbarton)Wind2065RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2065 | 85.2492 | 91.9384 | 99.0055 | 106.0386 | 113.083
| Pickering (Dunbarton)Wind2070RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2070 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2617
| Pickering (Dunbarton)Wind2075RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2075 | 85.476 | 92.2276 | 99.3736 | 106.4731 | 113.5876
| Pickering (Dunbarton)Wind2080RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2080 | 85.6198 | 92.4129 | 99.6105 | 106.7545 | 113.9134
| Pickering (Dunbarton)Wind2085RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2085 | 85.7637 | 92.5982 | 99.8473 | 107.0358 | 114.2393
| Pickering (Dunbarton)Wind2090RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2090 | 85.9075 | 92.7836 | 100.0841 | 107.3172 | 114.5651
| Pickering (Dunbarton)Wind2095RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2095 | 86.0514 | 92.9689 | 100.321 | 107.5986 | 114.891
| Pickering (Dunbarton)Wind2100RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2100 | 86.1952 | 93.1542 | 100.5578 | 107.88 | 115.2168
| Pickering (Dunbarton)Wind2023RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2023 | 84.8244 | 91.3223 | 98.1568 | 104.9963 | 111.8317
| Pickering (Dunbarton)Wind2025RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2025 | 84.8399 | 91.3557 | 98.2107 | 105.068 | 111.9211
| Pickering (Dunbarton)Wind2030RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2030 | 84.8554 | 91.3891 | 98.2646 | 105.1396 | 112.0105
| Pickering (Dunbarton)Wind2035RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2035 | 84.8709 | 91.4225 | 98.3185 | 105.2113 | 112.0998
| Pickering (Dunbarton)Wind2040RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2040 | 84.8864 | 91.456 | 98.3724 | 105.2829 | 112.1892
| Pickering (Dunbarton)Wind2045RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2045 | 84.9019 | 91.4894 | 98.4263 | 105.3546 | 112.2786
| Pickering (Dunbarton)Wind2050RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2050 | 85.0004 | 91.6267 | 98.6115 | 105.5793 | 112.5467
| Pickering (Dunbarton)Wind2055RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2055 | 85.0833 | 91.7306 | 98.7428 | 105.7324 | 112.7255
| Pickering (Dunbarton)Wind2060RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2060 | 85.1662 | 91.8345 | 98.8742 | 105.8855 | 112.9042
| Pickering (Dunbarton)Wind2065RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2065 | 85.2492 | 91.9384 | 99.0055 | 106.0386 | 113.083
| Pickering (Dunbarton)Wind2070RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2070 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2617
| Pickering (Dunbarton)Wind2075RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2075 | 85.5479 | 92.3203 | 99.4921 | 106.6138 | 113.7505
| Pickering (Dunbarton)Wind2080RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2080 | 85.7637 | 92.5982 | 99.8473 | 107.0358 | 114.2393
| Pickering (Dunbarton)Wind2085RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2085 | 85.9794 | 92.8762 | 100.2026 | 107.4579 | 114.7281
| Pickering (Dunbarton)Wind2090RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2090 | 86.6409 | 93.701 | 101.234 | 108.6664 | 116.118
| Pickering (Dunbarton)Wind2095RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2095 | 87.0866 | 94.2479 | 101.9102 | 109.4529 | 117.0193
| Pickering (Dunbarton)Wind2100RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2100 | 87.5322 | 94.7947 | 102.5864 | 110.2393 | 117.9205
| Pickering (Dunbarton)Wind2023RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2023 | 84.8244 | 91.3223 | 98.1568 | 104.9963 | 111.8317
| Pickering (Dunbarton)Wind2025RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2025 | 84.8554 | 91.3891 | 98.2646 | 105.1396 | 112.0105
| Pickering (Dunbarton)Wind2030RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2030 | 84.8864 | 91.456 | 98.3724 | 105.2829 | 112.1892
| Pickering (Dunbarton)Wind2035RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2035 | 84.9175 | 91.5228 | 98.4802 | 105.4262 | 112.368
| Pickering (Dunbarton)Wind2040RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2040 | 85.0557 | 91.696 | 98.6991 | 105.6814 | 112.6659
| Pickering (Dunbarton)Wind2045RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2045 | 85.1939 | 91.8691 | 98.9179 | 105.9366 | 112.9638
| Pickering (Dunbarton)Wind2050RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2050 | 85.6198 | 92.4129 | 99.6105 | 106.7545 | 113.9134
| Pickering (Dunbarton)Wind2055RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2055 | 85.9075 | 92.7836 | 100.0841 | 107.3172 | 114.5651
| Pickering (Dunbarton)Wind2060RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2060 | 86.6409 | 93.701 | 101.234 | 108.6664 | 116.118
| Pickering (Dunbarton)Wind2065RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2065 | 87.0866 | 94.2479 | 101.9102 | 109.4529 | 117.0193
| Pickering (Dunbarton)Wind2070RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2070 | 87.6648 | 94.974 | 102.8249 | 110.5329 | 118.2631
| Pickering (Dunbarton)Wind2075RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2075 | 87.7974 | 95.1532 | 103.0633 | 110.8265 | 118.6057
| Pickering (Dunbarton)Wind2080RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2080 | 87.93 | 95.3324 | 103.3018 | 111.1201 | 118.9483
| Pickering (Dunbarton)Wind2085RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2085 | 88.2135 | 95.7335 | 103.8506 | 111.7912 | 119.7471
| Pickering (Dunbarton)Wind2090RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2090 | 88.4969 | 96.1345 | 104.3994 | 112.4624 | 120.5459
| Pickering (Dunbarton)Wind2095RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2095 | 88.4969 | 96.1345 | 104.3994 | 112.4624 | 120.5459
| Pickering (Dunbarton)Wind2100RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2100 | 88.4969 | 96.1345 | 104.3994 | 112.4624 | 120.5459
| PictonIce Accretion2023RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| PictonIce Accretion2025RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
| PictonIce Accretion2030RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| PictonIce Accretion2035RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
| PictonIce Accretion2040RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| PictonIce Accretion2045RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
| PictonIce Accretion2050RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
| PictonIce Accretion2055RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
| PictonIce Accretion2060RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
| PictonIce Accretion2065RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
| PictonIce Accretion2070RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
| PictonIce Accretion2075RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2075 | 16.8859 | 20.3972 | 24.8292 | 28.2123 | 31.5682
| PictonIce Accretion2080RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2080 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
| PictonIce Accretion2085RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2085 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
| PictonIce Accretion2090RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2090 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
| PictonIce Accretion2095RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2095 | 16.7235 | 20.3142 | 24.8458 | 28.2877 | 31.7152
| PictonIce Accretion2100RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.2935 | 24.85 | 28.3065 | 31.752
| PictonIce Accretion2023RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| PictonIce Accretion2025RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
| PictonIce Accretion2030RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| PictonIce Accretion2035RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
| PictonIce Accretion2040RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| PictonIce Accretion2045RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
| PictonIce Accretion2050RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
| PictonIce Accretion2055RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
| PictonIce Accretion2060RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
| PictonIce Accretion2065RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
| PictonIce Accretion2070RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
| PictonIce Accretion2075RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2075 | 16.8656 | 20.3869 | 24.8313 | 28.2217 | 31.5866
| PictonIce Accretion2080RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2080 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
| PictonIce Accretion2085RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2085 | 16.7438 | 20.3246 | 24.8438 | 28.2782 | 31.6969
| PictonIce Accretion2090RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2090 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
| PictonIce Accretion2095RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2095 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
| PictonIce Accretion2100RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2100 | 15.6565 | 19.173 | 23.6 | 26.9505 | 30.2715
| PictonIce Accretion2023RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| PictonIce Accretion2025RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2025 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| PictonIce Accretion2030RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2030 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| PictonIce Accretion2035RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2035 | 17.6745 | 21.2272 | 25.725 | 29.154 | 32.571
| PictonIce Accretion2040RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2040 | 17.4251 | 20.9575 | 25.425 | 28.8338 | 32.2245
| PictonIce Accretion2045RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2045 | 17.1758 | 20.6877 | 25.125 | 28.5137 | 31.878
| PictonIce Accretion2050RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2050 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
| PictonIce Accretion2055RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2055 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
| PictonIce Accretion2060RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2060 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
| PictonIce Accretion2065RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2065 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
| PictonIce Accretion2070RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2070 | 15.2216 | 18.6888 | 23.05 | 26.3478 | 29.631
| PictonIce Accretion2075RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2075 | 14.7867 | 18.2047 | 22.5 | 25.7452 | 28.9905
| PictonIce Accretion2080RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2080 | 14.3518 | 17.7205 | 21.95 | 25.1425 | 28.35
| PictonIce Accretion2085RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2085 | 13.6908 | 16.9424 | 21.025 | 24.0972 | 27.1845
| PictonIce Accretion2090RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2090 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| PictonIce Accretion2095RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2095 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| PictonIce Accretion2100RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2100 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| PictonWind2023RCP4.5 | Picton | Wind | RCP4.5 | 2023 | 91.2096 | 98.2554 | 105.6615 | 113.069 | 120.478
| PictonWind2025RCP4.5 | Picton | Wind | RCP4.5 | 2025 | 91.1749 | 98.218 | 105.6248 | 113.0297 | 120.4381
| PictonWind2030RCP4.5 | Picton | Wind | RCP4.5 | 2030 | 91.1401 | 98.1806 | 105.588 | 112.9904 | 120.3982
| PictonWind2035RCP4.5 | Picton | Wind | RCP4.5 | 2035 | 91.1054 | 98.1431 | 105.5513 | 112.9511 | 120.3583
| PictonWind2040RCP4.5 | Picton | Wind | RCP4.5 | 2040 | 91.0706 | 98.1057 | 105.5145 | 112.9117 | 120.3184
| PictonWind2045RCP4.5 | Picton | Wind | RCP4.5 | 2045 | 91.0359 | 98.0683 | 105.4778 | 112.8724 | 120.2785
| PictonWind2050RCP4.5 | Picton | Wind | RCP4.5 | 2050 | 91.1299 | 98.2027 | 105.6657 | 113.1027 | 120.5547
| PictonWind2055RCP4.5 | Picton | Wind | RCP4.5 | 2055 | 91.2586 | 98.3746 | 105.8904 | 113.3724 | 120.8707
| PictonWind2060RCP4.5 | Picton | Wind | RCP4.5 | 2060 | 91.3874 | 98.5464 | 106.1151 | 113.642 | 121.1867
| PictonWind2065RCP4.5 | Picton | Wind | RCP4.5 | 2065 | 91.5161 | 98.7183 | 106.3398 | 113.9117 | 121.5027
| PictonWind2070RCP4.5 | Picton | Wind | RCP4.5 | 2070 | 91.6448 | 98.8902 | 106.5645 | 114.1813 | 121.8187
| PictonWind2075RCP4.5 | Picton | Wind | RCP4.5 | 2075 | 91.7098 | 98.9797 | 106.6835 | 114.3255 | 121.9883
| PictonWind2080RCP4.5 | Picton | Wind | RCP4.5 | 2080 | 91.7748 | 99.0692 | 106.8025 | 114.4697 | 122.1578
| PictonWind2085RCP4.5 | Picton | Wind | RCP4.5 | 2085 | 91.8398 | 99.1587 | 106.9215 | 114.6139 | 122.3274
| PictonWind2090RCP4.5 | Picton | Wind | RCP4.5 | 2090 | 91.9048 | 99.2482 | 107.0405 | 114.758 | 122.497
| PictonWind2095RCP4.5 | Picton | Wind | RCP4.5 | 2095 | 91.9697 | 99.3377 | 107.1595 | 114.9022 | 122.6666
| PictonWind2100RCP4.5 | Picton | Wind | RCP4.5 | 2100 | 92.0347 | 99.4272 | 107.2785 | 115.0464 | 122.8361
| PictonWind2023RCP6.0 | Picton | Wind | RCP6.0 | 2023 | 91.2096 | 98.2554 | 105.6615 | 113.069 | 120.478
| PictonWind2025RCP6.0 | Picton | Wind | RCP6.0 | 2025 | 91.1749 | 98.218 | 105.6248 | 113.0297 | 120.4381
| PictonWind2030RCP6.0 | Picton | Wind | RCP6.0 | 2030 | 91.1401 | 98.1806 | 105.588 | 112.9904 | 120.3982
| PictonWind2035RCP6.0 | Picton | Wind | RCP6.0 | 2035 | 91.1054 | 98.1431 | 105.5513 | 112.9511 | 120.3583
| PictonWind2040RCP6.0 | Picton | Wind | RCP6.0 | 2040 | 91.0706 | 98.1057 | 105.5145 | 112.9117 | 120.3184
| PictonWind2045RCP6.0 | Picton | Wind | RCP6.0 | 2045 | 91.0359 | 98.0683 | 105.4778 | 112.8724 | 120.2785
| PictonWind2050RCP6.0 | Picton | Wind | RCP6.0 | 2050 | 91.1299 | 98.2027 | 105.6657 | 113.1027 | 120.5547
| PictonWind2055RCP6.0 | Picton | Wind | RCP6.0 | 2055 | 91.2586 | 98.3746 | 105.8904 | 113.3724 | 120.8707
| PictonWind2060RCP6.0 | Picton | Wind | RCP6.0 | 2060 | 91.3874 | 98.5464 | 106.1151 | 113.642 | 121.1867
| PictonWind2065RCP6.0 | Picton | Wind | RCP6.0 | 2065 | 91.5161 | 98.7183 | 106.3398 | 113.9117 | 121.5027
| PictonWind2070RCP6.0 | Picton | Wind | RCP6.0 | 2070 | 91.6448 | 98.8902 | 106.5645 | 114.1813 | 121.8187
| PictonWind2075RCP6.0 | Picton | Wind | RCP6.0 | 2075 | 91.7423 | 99.0244 | 106.743 | 114.3976 | 122.0731
| PictonWind2080RCP6.0 | Picton | Wind | RCP6.0 | 2080 | 91.8398 | 99.1587 | 106.9215 | 114.6139 | 122.3274
| PictonWind2085RCP6.0 | Picton | Wind | RCP6.0 | 2085 | 91.9372 | 99.293 | 107.1 | 114.8301 | 122.5818
| PictonWind2090RCP6.0 | Picton | Wind | RCP6.0 | 2090 | 92.346 | 99.8048 | 107.7405 | 115.5857 | 123.4466
| PictonWind2095RCP6.0 | Picton | Wind | RCP6.0 | 2095 | 92.6573 | 100.1824 | 108.2025 | 116.125 | 124.0571
| PictonWind2100RCP6.0 | Picton | Wind | RCP6.0 | 2100 | 92.9686 | 100.56 | 108.6645 | 116.6642 | 124.6676
| PictonWind2023RCP8.5 | Picton | Wind | RCP8.5 | 2023 | 91.2096 | 98.2554 | 105.6615 | 113.069 | 120.478
| PictonWind2025RCP8.5 | Picton | Wind | RCP8.5 | 2025 | 91.1401 | 98.1806 | 105.588 | 112.9904 | 120.3982
| PictonWind2030RCP8.5 | Picton | Wind | RCP8.5 | 2030 | 91.0706 | 98.1057 | 105.5145 | 112.9117 | 120.3184
| PictonWind2035RCP8.5 | Picton | Wind | RCP8.5 | 2035 | 91.0011 | 98.0308 | 105.441 | 112.8331 | 120.2386
| PictonWind2040RCP8.5 | Picton | Wind | RCP8.5 | 2040 | 91.2157 | 98.3173 | 105.8155 | 113.2825 | 120.7653
| PictonWind2045RCP8.5 | Picton | Wind | RCP8.5 | 2045 | 91.4303 | 98.6037 | 106.19 | 113.7319 | 121.292
| PictonWind2050RCP8.5 | Picton | Wind | RCP8.5 | 2050 | 91.7748 | 99.0692 | 106.8025 | 114.4697 | 122.1578
| PictonWind2055RCP8.5 | Picton | Wind | RCP8.5 | 2055 | 91.9048 | 99.2482 | 107.0405 | 114.758 | 122.497
| PictonWind2060RCP8.5 | Picton | Wind | RCP8.5 | 2060 | 92.346 | 99.8048 | 107.7405 | 115.5857 | 123.4466
| PictonWind2065RCP8.5 | Picton | Wind | RCP8.5 | 2065 | 92.6573 | 100.1824 | 108.2025 | 116.125 | 124.0571
| PictonWind2070RCP8.5 | Picton | Wind | RCP8.5 | 2070 | 92.8839 | 100.4656 | 108.556 | 116.5444 | 124.5399
| PictonWind2075RCP8.5 | Picton | Wind | RCP8.5 | 2075 | 92.7993 | 100.3712 | 108.4475 | 116.4246 | 124.4122
| PictonWind2080RCP8.5 | Picton | Wind | RCP8.5 | 2080 | 92.7147 | 100.2768 | 108.339 | 116.3047 | 124.2845
| PictonWind2085RCP8.5 | Picton | Wind | RCP8.5 | 2085 | 92.9368 | 100.6137 | 108.822 | 116.9058 | 125.0087
| PictonWind2090RCP8.5 | Picton | Wind | RCP8.5 | 2090 | 93.159 | 100.9506 | 109.305 | 117.5069 | 125.7329
| PictonWind2095RCP8.5 | Picton | Wind | RCP8.5 | 2095 | 93.159 | 100.9506 | 109.305 | 117.5069 | 125.7329
| PictonWind2100RCP8.5 | Picton | Wind | RCP8.5 | 2100 | 93.159 | 100.9506 | 109.305 | 117.5069 | 125.7329
| PlattsvilleIce Accretion2023RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2023 | 18.3933 | 22.0514 | 26.676 | 30.2049 | 33.7478
| PlattsvilleIce Accretion2025RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2025 | 18.3557 | 22.0178 | 26.6445 | 30.1795 | 33.7195
| PlattsvilleIce Accretion2030RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2030 | 18.3181 | 21.9842 | 26.613 | 30.154 | 33.6911
| PlattsvilleIce Accretion2035RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2035 | 18.2806 | 21.9506 | 26.5815 | 30.1286 | 33.6628
| PlattsvilleIce Accretion2040RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2040 | 18.243 | 21.917 | 26.55 | 30.1032 | 33.6344
| PlattsvilleIce Accretion2045RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2045 | 18.2054 | 21.8834 | 26.5185 | 30.0778 | 33.6061
| PlattsvilleIce Accretion2050RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2050 | 18.0514 | 21.7377 | 26.3844 | 29.9486 | 33.4825
| PlattsvilleIce Accretion2055RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2055 | 17.9349 | 21.6257 | 26.2818 | 29.8449 | 33.3872
| PlattsvilleIce Accretion2060RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2060 | 17.8184 | 21.5136 | 26.1792 | 29.7411 | 33.292
| PlattsvilleIce Accretion2065RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2065 | 17.7019 | 21.4016 | 26.0766 | 29.6374 | 33.1967
| PlattsvilleIce Accretion2070RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2070 | 17.5854 | 21.2895 | 25.974 | 29.5337 | 33.1015
| PlattsvilleIce Accretion2075RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2075 | 17.5353 | 21.2522 | 25.956 | 29.5286 | 33.1071
| PlattsvilleIce Accretion2080RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2080 | 17.4852 | 21.2148 | 25.938 | 29.5235 | 33.1128
| PlattsvilleIce Accretion2085RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2085 | 17.4351 | 21.1775 | 25.92 | 29.5184 | 33.1185
| PlattsvilleIce Accretion2090RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2090 | 17.385 | 21.1401 | 25.902 | 29.5133 | 33.1241
| PlattsvilleIce Accretion2095RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2095 | 17.3349 | 21.1028 | 25.884 | 29.5083 | 33.1298
| PlattsvilleIce Accretion2100RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2100 | 17.2848 | 21.0654 | 25.866 | 29.5032 | 33.1355
| PlattsvilleIce Accretion2023RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2023 | 18.3933 | 22.0514 | 26.676 | 30.2049 | 33.7478
| PlattsvilleIce Accretion2025RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2025 | 18.3557 | 22.0178 | 26.6445 | 30.1795 | 33.7195
| PlattsvilleIce Accretion2030RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2030 | 18.3181 | 21.9842 | 26.613 | 30.154 | 33.6911
| PlattsvilleIce Accretion2035RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2035 | 18.2806 | 21.9506 | 26.5815 | 30.1286 | 33.6628
| PlattsvilleIce Accretion2040RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2040 | 18.243 | 21.917 | 26.55 | 30.1032 | 33.6344
| PlattsvilleIce Accretion2045RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2045 | 18.2054 | 21.8834 | 26.5185 | 30.0778 | 33.6061
| PlattsvilleIce Accretion2050RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2050 | 18.0514 | 21.7377 | 26.3844 | 29.9486 | 33.4825
| PlattsvilleIce Accretion2055RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2055 | 17.9349 | 21.6257 | 26.2818 | 29.8449 | 33.3872
| PlattsvilleIce Accretion2060RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2060 | 17.8184 | 21.5136 | 26.1792 | 29.7411 | 33.292
| PlattsvilleIce Accretion2065RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2065 | 17.7019 | 21.4016 | 26.0766 | 29.6374 | 33.1967
| PlattsvilleIce Accretion2070RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2070 | 17.5854 | 21.2895 | 25.974 | 29.5337 | 33.1015
| PlattsvilleIce Accretion2075RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2075 | 17.5103 | 21.2335 | 25.947 | 29.5261 | 33.11
| PlattsvilleIce Accretion2080RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2080 | 17.4351 | 21.1775 | 25.92 | 29.5184 | 33.1185
| PlattsvilleIce Accretion2085RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2085 | 17.36 | 21.1214 | 25.893 | 29.5108 | 33.127
| PlattsvilleIce Accretion2090RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2090 | 16.8965 | 20.6471 | 25.389 | 28.9947 | 32.5798
| PlattsvilleIce Accretion2095RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2095 | 16.5083 | 20.2288 | 24.912 | 28.4862 | 32.0242
| PlattsvilleIce Accretion2100RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2100 | 16.12 | 19.8104 | 24.435 | 27.9777 | 31.4685
| PlattsvilleIce Accretion2023RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2023 | 18.3933 | 22.0514 | 26.676 | 30.2049 | 33.7478
| PlattsvilleIce Accretion2025RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2025 | 18.3181 | 21.9842 | 26.613 | 30.154 | 33.6911
| PlattsvilleIce Accretion2030RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2030 | 18.243 | 21.917 | 26.55 | 30.1032 | 33.6344
| PlattsvilleIce Accretion2035RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2035 | 18.1678 | 21.8498 | 26.487 | 30.0523 | 33.5777
| PlattsvilleIce Accretion2040RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2040 | 17.9737 | 21.663 | 26.316 | 29.8795 | 33.419
| PlattsvilleIce Accretion2045RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2045 | 17.7796 | 21.4763 | 26.145 | 29.7066 | 33.2602
| PlattsvilleIce Accretion2050RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2050 | 17.4852 | 21.2148 | 25.938 | 29.5235 | 33.1128
| PlattsvilleIce Accretion2055RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2055 | 17.385 | 21.1401 | 25.902 | 29.5133 | 33.1241
| PlattsvilleIce Accretion2060RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2060 | 16.8965 | 20.6471 | 25.389 | 28.9947 | 32.5798
| PlattsvilleIce Accretion2065RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2065 | 16.5083 | 20.2288 | 24.912 | 28.4862 | 32.0242
| PlattsvilleIce Accretion2070RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2070 | 15.7818 | 19.4444 | 24.039 | 27.5505 | 31.0149
| PlattsvilleIce Accretion2075RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2075 | 15.4436 | 19.0784 | 23.643 | 27.1234 | 30.5613
| PlattsvilleIce Accretion2080RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2080 | 15.1054 | 18.7124 | 23.247 | 26.6962 | 30.1077
| PlattsvilleIce Accretion2085RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2085 | 14.2694 | 17.7487 | 22.113 | 25.4148 | 28.7129
| PlattsvilleIce Accretion2090RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2090 | 13.4333 | 16.7851 | 20.979 | 24.1334 | 27.3181
| PlattsvilleIce Accretion2095RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2095 | 13.4333 | 16.7851 | 20.979 | 24.1334 | 27.3181
| PlattsvilleIce Accretion2100RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2100 | 13.4333 | 16.7851 | 20.979 | 24.1334 | 27.3181
| PlattsvilleWind2023RCP4.5 | Plattsville | Wind | RCP4.5 | 2023 | 85.3829 | 92.1152 | 99.2446 | 106.3385 | 113.4405
| PlattsvilleWind2025RCP4.5 | Plattsville | Wind | RCP4.5 | 2025 | 85.4618 | 92.22 | 99.3802 | 106.5011 | 113.6304
| PlattsvilleWind2030RCP4.5 | Plattsville | Wind | RCP4.5 | 2030 | 85.5408 | 92.3248 | 99.5157 | 106.6636 | 113.8203
| PlattsvilleWind2035RCP4.5 | Plattsville | Wind | RCP4.5 | 2035 | 85.6198 | 92.4296 | 99.6513 | 106.8261 | 114.0103
| PlattsvilleWind2040RCP4.5 | Plattsville | Wind | RCP4.5 | 2040 | 85.6988 | 92.5344 | 99.7869 | 106.9887 | 114.2002
| PlattsvilleWind2045RCP4.5 | Plattsville | Wind | RCP4.5 | 2045 | 85.7778 | 92.6393 | 99.9224 | 107.1512 | 114.3901
| PlattsvilleWind2050RCP4.5 | Plattsville | Wind | RCP4.5 | 2050 | 85.9244 | 92.8261 | 100.1619 | 107.4333 | 114.7163
| PlattsvilleWind2055RCP4.5 | Plattsville | Wind | RCP4.5 | 2055 | 85.9921 | 92.9081 | 100.2658 | 107.5528 | 114.8526
| PlattsvilleWind2060RCP4.5 | Plattsville | Wind | RCP4.5 | 2060 | 86.0598 | 92.9901 | 100.3696 | 107.6723 | 114.9889
| PlattsvilleWind2065RCP4.5 | Plattsville | Wind | RCP4.5 | 2065 | 86.1275 | 93.0722 | 100.4735 | 107.7919 | 115.1252
| PlattsvilleWind2070RCP4.5 | Plattsville | Wind | RCP4.5 | 2070 | 86.1952 | 93.1542 | 100.5774 | 107.9114 | 115.2615
| PlattsvilleWind2075RCP4.5 | Plattsville | Wind | RCP4.5 | 2075 | 86.2799 | 93.2712 | 100.7358 | 108.1054 | 115.4924
| PlattsvilleWind2080RCP4.5 | Plattsville | Wind | RCP4.5 | 2080 | 86.3645 | 93.3881 | 100.8943 | 108.2994 | 115.7233
| PlattsvilleWind2085RCP4.5 | Plattsville | Wind | RCP4.5 | 2085 | 86.4491 | 93.5051 | 101.0527 | 108.4934 | 115.9542
| PlattsvilleWind2090RCP4.5 | Plattsville | Wind | RCP4.5 | 2090 | 86.5337 | 93.622 | 101.2111 | 108.6874 | 116.1851
| PlattsvilleWind2095RCP4.5 | Plattsville | Wind | RCP4.5 | 2095 | 86.6183 | 93.739 | 101.3696 | 108.8814 | 116.416
| PlattsvilleWind2100RCP4.5 | Plattsville | Wind | RCP4.5 | 2100 | 86.703 | 93.856 | 101.528 | 109.0754 | 116.6469
| PlattsvilleWind2023RCP6.0 | Plattsville | Wind | RCP6.0 | 2023 | 85.3829 | 92.1152 | 99.2446 | 106.3385 | 113.4405
| PlattsvilleWind2025RCP6.0 | Plattsville | Wind | RCP6.0 | 2025 | 85.4618 | 92.22 | 99.3802 | 106.5011 | 113.6304
| PlattsvilleWind2030RCP6.0 | Plattsville | Wind | RCP6.0 | 2030 | 85.5408 | 92.3248 | 99.5157 | 106.6636 | 113.8203
| PlattsvilleWind2035RCP6.0 | Plattsville | Wind | RCP6.0 | 2035 | 85.6198 | 92.4296 | 99.6513 | 106.8261 | 114.0103
| PlattsvilleWind2040RCP6.0 | Plattsville | Wind | RCP6.0 | 2040 | 85.6988 | 92.5344 | 99.7869 | 106.9887 | 114.2002
| PlattsvilleWind2045RCP6.0 | Plattsville | Wind | RCP6.0 | 2045 | 85.7778 | 92.6393 | 99.9224 | 107.1512 | 114.3901
| PlattsvilleWind2050RCP6.0 | Plattsville | Wind | RCP6.0 | 2050 | 85.9244 | 92.8261 | 100.1619 | 107.4333 | 114.7163
| PlattsvilleWind2055RCP6.0 | Plattsville | Wind | RCP6.0 | 2055 | 85.9921 | 92.9081 | 100.2658 | 107.5528 | 114.8526
| PlattsvilleWind2060RCP6.0 | Plattsville | Wind | RCP6.0 | 2060 | 86.0598 | 92.9901 | 100.3696 | 107.6723 | 114.9889
| PlattsvilleWind2065RCP6.0 | Plattsville | Wind | RCP6.0 | 2065 | 86.1275 | 93.0722 | 100.4735 | 107.7919 | 115.1252
| PlattsvilleWind2070RCP6.0 | Plattsville | Wind | RCP6.0 | 2070 | 86.1952 | 93.1542 | 100.5774 | 107.9114 | 115.2615
| PlattsvilleWind2075RCP6.0 | Plattsville | Wind | RCP6.0 | 2075 | 86.3222 | 93.3296 | 100.815 | 108.2024 | 115.6079
| PlattsvilleWind2080RCP6.0 | Plattsville | Wind | RCP6.0 | 2080 | 86.4491 | 93.5051 | 101.0527 | 108.4934 | 115.9542
| PlattsvilleWind2085RCP6.0 | Plattsville | Wind | RCP6.0 | 2085 | 86.576 | 93.6805 | 101.2904 | 108.7844 | 116.3005
| PlattsvilleWind2090RCP6.0 | Plattsville | Wind | RCP6.0 | 2090 | 87.0499 | 94.3026 | 102.0964 | 109.7465 | 117.4252
| PlattsvilleWind2095RCP6.0 | Plattsville | Wind | RCP6.0 | 2095 | 87.3969 | 94.7491 | 102.6648 | 110.4176 | 118.2035
| PlattsvilleWind2100RCP6.0 | Plattsville | Wind | RCP6.0 | 2100 | 87.7438 | 95.1957 | 103.2332 | 111.0887 | 118.9818
| PlattsvilleWind2023RCP8.5 | Plattsville | Wind | RCP8.5 | 2023 | 85.3829 | 92.1152 | 99.2446 | 106.3385 | 113.4405
| PlattsvilleWind2025RCP8.5 | Plattsville | Wind | RCP8.5 | 2025 | 85.5408 | 92.3248 | 99.5157 | 106.6636 | 113.8203
| PlattsvilleWind2030RCP8.5 | Plattsville | Wind | RCP8.5 | 2030 | 85.6988 | 92.5344 | 99.7869 | 106.9887 | 114.2002
| PlattsvilleWind2035RCP8.5 | Plattsville | Wind | RCP8.5 | 2035 | 85.8567 | 92.7441 | 100.058 | 107.3137 | 114.58
| PlattsvilleWind2040RCP8.5 | Plattsville | Wind | RCP8.5 | 2040 | 85.9696 | 92.8808 | 100.2311 | 107.513 | 114.8072
| PlattsvilleWind2045RCP8.5 | Plattsville | Wind | RCP8.5 | 2045 | 86.0824 | 93.0175 | 100.4043 | 107.7122 | 115.0344
| PlattsvilleWind2050RCP8.5 | Plattsville | Wind | RCP8.5 | 2050 | 86.3645 | 93.3881 | 100.8943 | 108.2994 | 115.7233
| PlattsvilleWind2055RCP8.5 | Plattsville | Wind | RCP8.5 | 2055 | 86.5337 | 93.622 | 101.2111 | 108.6874 | 116.1851
| PlattsvilleWind2060RCP8.5 | Plattsville | Wind | RCP8.5 | 2060 | 87.0499 | 94.3026 | 102.0964 | 109.7465 | 117.4252
| PlattsvilleWind2065RCP8.5 | Plattsville | Wind | RCP8.5 | 2065 | 87.3969 | 94.7491 | 102.6648 | 110.4176 | 118.2035
| PlattsvilleWind2070RCP8.5 | Plattsville | Wind | RCP8.5 | 2070 | 87.9638 | 95.4904 | 103.6219 | 111.5571 | 119.533
| PlattsvilleWind2075RCP8.5 | Plattsville | Wind | RCP8.5 | 2075 | 88.1838 | 95.7851 | 104.0107 | 112.0254 | 120.0841
| PlattsvilleWind2080RCP8.5 | Plattsville | Wind | RCP8.5 | 2080 | 88.4038 | 96.0798 | 104.3994 | 112.4938 | 120.6353
| PlattsvilleWind2085RCP8.5 | Plattsville | Wind | RCP8.5 | 2085 | 88.8354 | 96.6449 | 105.1393 | 113.3799 | 121.6687
| PlattsvilleWind2090RCP8.5 | Plattsville | Wind | RCP8.5 | 2090 | 89.267 | 97.2099 | 105.8792 | 114.2659 | 122.7021
| PlattsvilleWind2095RCP8.5 | Plattsville | Wind | RCP8.5 | 2095 | 89.267 | 97.2099 | 105.8792 | 114.2659 | 122.7021
| PlattsvilleWind2100RCP8.5 | Plattsville | Wind | RCP8.5 | 2100 | 89.267 | 97.2099 | 105.8792 | 114.2659 | 122.7021
| Point AlexanderIce Accretion2023RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2023 | 14.4458 | 17.2806 | 20.88 | 23.6396 | 26.3844
| Point AlexanderIce Accretion2025RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2025 | 14.5014 | 17.347 | 20.9567 | 23.7225 | 26.4768
| Point AlexanderIce Accretion2030RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2030 | 14.5571 | 17.4134 | 21.0333 | 23.8053 | 26.5692
| Point AlexanderIce Accretion2035RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2035 | 14.6128 | 17.4798 | 21.11 | 23.8882 | 26.6616
| Point AlexanderIce Accretion2040RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2040 | 14.6684 | 17.5462 | 21.1867 | 23.9711 | 26.754
| Point AlexanderIce Accretion2045RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2045 | 14.7241 | 17.6126 | 21.2633 | 24.0539 | 26.8464
| Point AlexanderIce Accretion2050RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2050 | 14.777 | 17.6856 | 21.364 | 24.173 | 26.9892
| Point AlexanderIce Accretion2055RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2055 | 14.7742 | 17.6923 | 21.388 | 24.2091 | 27.0396
| Point AlexanderIce Accretion2060RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2060 | 14.7714 | 17.6989 | 21.412 | 24.2453 | 27.09
| Point AlexanderIce Accretion2065RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2065 | 14.7686 | 17.7056 | 21.436 | 24.2814 | 27.1404
| Point AlexanderIce Accretion2070RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2070 | 14.7659 | 17.7122 | 21.46 | 24.3176 | 27.1908
| Point AlexanderIce Accretion2075RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2075 | 14.7496 | 17.7011 | 21.4567 | 24.3176 | 27.1908
| Point AlexanderIce Accretion2080RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2080 | 14.7334 | 17.6901 | 21.4533 | 24.3176 | 27.1908
| Point AlexanderIce Accretion2085RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2085 | 14.7171 | 17.679 | 21.45 | 24.3176 | 27.1908
| Point AlexanderIce Accretion2090RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2090 | 14.7009 | 17.6679 | 21.4467 | 24.3176 | 27.1908
| Point AlexanderIce Accretion2095RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2095 | 14.6847 | 17.6569 | 21.4433 | 24.3176 | 27.1908
| Point AlexanderIce Accretion2100RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2100 | 14.6684 | 17.6458 | 21.44 | 24.3176 | 27.1908
| Point AlexanderIce Accretion2023RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2023 | 14.4458 | 17.2806 | 20.88 | 23.6396 | 26.3844
| Point AlexanderIce Accretion2025RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2025 | 14.5014 | 17.347 | 20.9567 | 23.7225 | 26.4768
| Point AlexanderIce Accretion2030RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2030 | 14.5571 | 17.4134 | 21.0333 | 23.8053 | 26.5692
| Point AlexanderIce Accretion2035RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2035 | 14.6128 | 17.4798 | 21.11 | 23.8882 | 26.6616
| Point AlexanderIce Accretion2040RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2040 | 14.6684 | 17.5462 | 21.1867 | 23.9711 | 26.754
| Point AlexanderIce Accretion2045RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2045 | 14.7241 | 17.6126 | 21.2633 | 24.0539 | 26.8464
| Point AlexanderIce Accretion2050RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2050 | 14.777 | 17.6856 | 21.364 | 24.173 | 26.9892
| Point AlexanderIce Accretion2055RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2055 | 14.7742 | 17.6923 | 21.388 | 24.2091 | 27.0396
| Point AlexanderIce Accretion2060RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2060 | 14.7714 | 17.6989 | 21.412 | 24.2453 | 27.09
| Point AlexanderIce Accretion2065RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2065 | 14.7686 | 17.7056 | 21.436 | 24.2814 | 27.1404
| Point AlexanderIce Accretion2070RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2070 | 14.7659 | 17.7122 | 21.46 | 24.3176 | 27.1908
| Point AlexanderIce Accretion2075RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2075 | 14.7415 | 17.6956 | 21.455 | 24.3176 | 27.1908
| Point AlexanderIce Accretion2080RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2080 | 14.7171 | 17.679 | 21.45 | 24.3176 | 27.1908
| Point AlexanderIce Accretion2085RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2085 | 14.6928 | 17.6624 | 21.445 | 24.3176 | 27.1908
| Point AlexanderIce Accretion2090RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2090 | 14.6777 | 17.6901 | 21.5267 | 24.4457 | 27.3588
| Point AlexanderIce Accretion2095RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2095 | 14.687 | 17.7343 | 21.6133 | 24.5737 | 27.5268
| Point AlexanderIce Accretion2100RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2100 | 14.6963 | 17.7786 | 21.7 | 24.7018 | 27.6948
| Point AlexanderIce Accretion2023RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2023 | 14.4458 | 17.2806 | 20.88 | 23.6396 | 26.3844
| Point AlexanderIce Accretion2025RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2025 | 14.5571 | 17.4134 | 21.0333 | 23.8053 | 26.5692
| Point AlexanderIce Accretion2030RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2030 | 14.6684 | 17.5462 | 21.1867 | 23.9711 | 26.754
| Point AlexanderIce Accretion2035RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2035 | 14.7798 | 17.679 | 21.34 | 24.1368 | 26.9388
| Point AlexanderIce Accretion2040RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2040 | 14.7751 | 17.6901 | 21.38 | 24.1971 | 27.0228
| Point AlexanderIce Accretion2045RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2045 | 14.7705 | 17.7011 | 21.42 | 24.2573 | 27.1068
| Point AlexanderIce Accretion2050RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2050 | 14.7334 | 17.6901 | 21.4533 | 24.3176 | 27.1908
| Point AlexanderIce Accretion2055RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2055 | 14.7009 | 17.6679 | 21.4467 | 24.3176 | 27.1908
| Point AlexanderIce Accretion2060RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2060 | 14.6777 | 17.6901 | 21.5267 | 24.4457 | 27.3588
| Point AlexanderIce Accretion2065RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2065 | 14.687 | 17.7343 | 21.6133 | 24.5737 | 27.5268
| Point AlexanderIce Accretion2070RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2070 | 14.6684 | 17.7675 | 21.7 | 24.7093 | 27.7116
| Point AlexanderIce Accretion2075RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2075 | 14.6406 | 17.7565 | 21.7 | 24.7169 | 27.7284
| Point AlexanderIce Accretion2080RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2080 | 14.6128 | 17.7454 | 21.7 | 24.7244 | 27.7452
| Point AlexanderIce Accretion2085RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2085 | 14.3623 | 17.4715 | 21.4 | 24.3967 | 27.3924
| Point AlexanderIce Accretion2090RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2090 | 14.1118 | 17.1976 | 21.1 | 24.069 | 27.0396
| Point AlexanderIce Accretion2095RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2095 | 14.1118 | 17.1976 | 21.1 | 24.069 | 27.0396
| Point AlexanderIce Accretion2100RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2100 | 14.1118 | 17.1976 | 21.1 | 24.069 | 27.0396
| Point AlexanderWind2023RCP4.5 | Point Alexander | Wind | RCP4.5 | 2023 | 77.3571 | 83.2997 | 89.5429 | 95.7919 | 102.0383
| Point AlexanderWind2025RCP4.5 | Point Alexander | Wind | RCP4.5 | 2025 | 77.4173 | 83.3604 | 89.6037 | 95.8538 | 102.1026
| Point AlexanderWind2030RCP4.5 | Point Alexander | Wind | RCP4.5 | 2030 | 77.4775 | 83.4211 | 89.6645 | 95.9157 | 102.1668
| Point AlexanderWind2035RCP4.5 | Point Alexander | Wind | RCP4.5 | 2035 | 77.5377 | 83.4818 | 89.7253 | 95.9776 | 102.2311
| Point AlexanderWind2040RCP4.5 | Point Alexander | Wind | RCP4.5 | 2040 | 77.5979 | 83.5425 | 89.7862 | 96.0395 | 102.2954
| Point AlexanderWind2045RCP4.5 | Point Alexander | Wind | RCP4.5 | 2045 | 77.6581 | 83.6032 | 89.847 | 96.1014 | 102.3596
| Point AlexanderWind2050RCP4.5 | Point Alexander | Wind | RCP4.5 | 2050 | 77.7937 | 83.755 | 90.0164 | 96.289 | 102.5639
| Point AlexanderWind2055RCP4.5 | Point Alexander | Wind | RCP4.5 | 2055 | 77.869 | 83.846 | 90.125 | 96.4147 | 102.7039
| Point AlexanderWind2060RCP4.5 | Point Alexander | Wind | RCP4.5 | 2060 | 77.9443 | 83.9371 | 90.2335 | 96.5404 | 102.8439
| Point AlexanderWind2065RCP4.5 | Point Alexander | Wind | RCP4.5 | 2065 | 78.0196 | 84.0281 | 90.3421 | 96.6661 | 102.9839
| Point AlexanderWind2070RCP4.5 | Point Alexander | Wind | RCP4.5 | 2070 | 78.0949 | 84.1192 | 90.4507 | 96.7918 | 103.1239
| Point AlexanderWind2075RCP4.5 | Point Alexander | Wind | RCP4.5 | 2075 | 78.1884 | 84.2336 | 90.5916 | 96.9537 | 103.31
| Point AlexanderWind2080RCP4.5 | Point Alexander | Wind | RCP4.5 | 2080 | 78.2819 | 84.3481 | 90.7325 | 97.1156 | 103.496
| Point AlexanderWind2085RCP4.5 | Point Alexander | Wind | RCP4.5 | 2085 | 78.3754 | 84.4626 | 90.8734 | 97.2774 | 103.682
| Point AlexanderWind2090RCP4.5 | Point Alexander | Wind | RCP4.5 | 2090 | 78.4689 | 84.5771 | 91.0144 | 97.4393 | 103.868
| Point AlexanderWind2095RCP4.5 | Point Alexander | Wind | RCP4.5 | 2095 | 78.5624 | 84.6916 | 91.1553 | 97.6012 | 104.054
| Point AlexanderWind2100RCP4.5 | Point Alexander | Wind | RCP4.5 | 2100 | 78.6559 | 84.8061 | 91.2962 | 97.7631 | 104.24
| Point AlexanderWind2023RCP6.0 | Point Alexander | Wind | RCP6.0 | 2023 | 77.3571 | 83.2997 | 89.5429 | 95.7919 | 102.0383
| Point AlexanderWind2025RCP6.0 | Point Alexander | Wind | RCP6.0 | 2025 | 77.4173 | 83.3604 | 89.6037 | 95.8538 | 102.1026
| Point AlexanderWind2030RCP6.0 | Point Alexander | Wind | RCP6.0 | 2030 | 77.4775 | 83.4211 | 89.6645 | 95.9157 | 102.1668
| Point AlexanderWind2035RCP6.0 | Point Alexander | Wind | RCP6.0 | 2035 | 77.5377 | 83.4818 | 89.7253 | 95.9776 | 102.2311
| Point AlexanderWind2040RCP6.0 | Point Alexander | Wind | RCP6.0 | 2040 | 77.5979 | 83.5425 | 89.7862 | 96.0395 | 102.2954
| Point AlexanderWind2045RCP6.0 | Point Alexander | Wind | RCP6.0 | 2045 | 77.6581 | 83.6032 | 89.847 | 96.1014 | 102.3596
| Point AlexanderWind2050RCP6.0 | Point Alexander | Wind | RCP6.0 | 2050 | 77.7937 | 83.755 | 90.0164 | 96.289 | 102.5639
| Point AlexanderWind2055RCP6.0 | Point Alexander | Wind | RCP6.0 | 2055 | 77.869 | 83.846 | 90.125 | 96.4147 | 102.7039
| Point AlexanderWind2060RCP6.0 | Point Alexander | Wind | RCP6.0 | 2060 | 77.9443 | 83.9371 | 90.2335 | 96.5404 | 102.8439
| Point AlexanderWind2065RCP6.0 | Point Alexander | Wind | RCP6.0 | 2065 | 78.0196 | 84.0281 | 90.3421 | 96.6661 | 102.9839
| Point AlexanderWind2070RCP6.0 | Point Alexander | Wind | RCP6.0 | 2070 | 78.0949 | 84.1192 | 90.4507 | 96.7918 | 103.1239
| Point AlexanderWind2075RCP6.0 | Point Alexander | Wind | RCP6.0 | 2075 | 78.2352 | 84.2909 | 90.6621 | 97.0346 | 103.403
| Point AlexanderWind2080RCP6.0 | Point Alexander | Wind | RCP6.0 | 2080 | 78.3754 | 84.4626 | 90.8734 | 97.2774 | 103.682
| Point AlexanderWind2085RCP6.0 | Point Alexander | Wind | RCP6.0 | 2085 | 78.5157 | 84.6344 | 91.0848 | 97.5203 | 103.961
| Point AlexanderWind2090RCP6.0 | Point Alexander | Wind | RCP6.0 | 2090 | 78.7481 | 84.9303 | 91.4653 | 97.9663 | 104.4767
| Point AlexanderWind2095RCP6.0 | Point Alexander | Wind | RCP6.0 | 2095 | 78.8403 | 85.0545 | 91.6344 | 98.1694 | 104.7135
| Point AlexanderWind2100RCP6.0 | Point Alexander | Wind | RCP6.0 | 2100 | 78.9326 | 85.1786 | 91.8035 | 98.3726 | 104.9502
| Point AlexanderWind2023RCP8.5 | Point Alexander | Wind | RCP8.5 | 2023 | 77.3571 | 83.2997 | 89.5429 | 95.7919 | 102.0383
| Point AlexanderWind2025RCP8.5 | Point Alexander | Wind | RCP8.5 | 2025 | 77.4775 | 83.4211 | 89.6645 | 95.9157 | 102.1668
| Point AlexanderWind2030RCP8.5 | Point Alexander | Wind | RCP8.5 | 2030 | 77.5979 | 83.5425 | 89.7862 | 96.0395 | 102.2954
| Point AlexanderWind2035RCP8.5 | Point Alexander | Wind | RCP8.5 | 2035 | 77.7183 | 83.6639 | 89.9078 | 96.1633 | 102.4239
| Point AlexanderWind2040RCP8.5 | Point Alexander | Wind | RCP8.5 | 2040 | 77.8439 | 83.8157 | 90.0888 | 96.3728 | 102.6572
| Point AlexanderWind2045RCP8.5 | Point Alexander | Wind | RCP8.5 | 2045 | 77.9694 | 83.9674 | 90.2697 | 96.5823 | 102.8906
| Point AlexanderWind2050RCP8.5 | Point Alexander | Wind | RCP8.5 | 2050 | 78.2819 | 84.3481 | 90.7325 | 97.1156 | 103.496
| Point AlexanderWind2055RCP8.5 | Point Alexander | Wind | RCP8.5 | 2055 | 78.4689 | 84.5771 | 91.0144 | 97.4393 | 103.868
| Point AlexanderWind2060RCP8.5 | Point Alexander | Wind | RCP8.5 | 2060 | 78.7481 | 84.9303 | 91.4653 | 97.9663 | 104.4767
| Point AlexanderWind2065RCP8.5 | Point Alexander | Wind | RCP8.5 | 2065 | 78.8403 | 85.0545 | 91.6344 | 98.1694 | 104.7135
| Point AlexanderWind2070RCP8.5 | Point Alexander | Wind | RCP8.5 | 2070 | 78.9556 | 85.1841 | 91.7798 | 98.3313 | 104.8893
| Point AlexanderWind2075RCP8.5 | Point Alexander | Wind | RCP8.5 | 2075 | 78.9787 | 85.1896 | 91.756 | 98.2901 | 104.8285
| Point AlexanderWind2080RCP8.5 | Point Alexander | Wind | RCP8.5 | 2080 | 79.0017 | 85.1952 | 91.7323 | 98.2488 | 104.7676
| Point AlexanderWind2085RCP8.5 | Point Alexander | Wind | RCP8.5 | 2085 | 79.0517 | 85.2531 | 91.799 | 98.3202 | 104.8488
| Point AlexanderWind2090RCP8.5 | Point Alexander | Wind | RCP8.5 | 2090 | 79.1016 | 85.311 | 91.8658 | 98.3916 | 104.9299
| Point AlexanderWind2095RCP8.5 | Point Alexander | Wind | RCP8.5 | 2095 | 79.1016 | 85.311 | 91.8658 | 98.3916 | 104.9299
| Point AlexanderWind2100RCP8.5 | Point Alexander | Wind | RCP8.5 | 2100 | 79.1016 | 85.311 | 91.8658 | 98.3916 | 104.9299
| Port BurwellIce Accretion2023RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2023 | 20.3326 | 24.402 | 29.55 | 33.4932 | 37.422
| Port BurwellIce Accretion2025RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2025 | 20.2213 | 24.2816 | 29.42 | 33.352 | 37.2708
| Port BurwellIce Accretion2030RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2030 | 20.11 | 24.1613 | 29.29 | 33.2107 | 37.1196
| Port BurwellIce Accretion2035RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2035 | 19.9986 | 24.0409 | 29.16 | 33.0695 | 36.9684
| Port BurwellIce Accretion2040RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2040 | 19.8873 | 23.9206 | 29.03 | 32.9282 | 36.8172
| Port BurwellIce Accretion2045RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2045 | 19.7759 | 23.8002 | 28.9 | 32.7869 | 36.666
| Port BurwellIce Accretion2050RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2050 | 19.2304 | 23.2018 | 28.224 | 32.0491 | 35.8646
| Port BurwellIce Accretion2055RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2055 | 18.7962 | 22.7237 | 27.678 | 31.4524 | 35.2145
| Port BurwellIce Accretion2060RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2060 | 18.362 | 22.2457 | 27.132 | 30.8558 | 34.5643
| Port BurwellIce Accretion2065RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2065 | 17.9278 | 21.7676 | 26.586 | 30.2591 | 33.9142
| Port BurwellIce Accretion2070RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2070 | 17.4936 | 21.2895 | 26.04 | 29.6625 | 33.264
| Port BurwellIce Accretion2075RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2075 | 17.2848 | 21.0571 | 25.775 | 29.3743 | 32.949
| Port BurwellIce Accretion2080RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2080 | 17.0761 | 20.8247 | 25.51 | 29.0862 | 32.634
| Port BurwellIce Accretion2085RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2085 | 16.8673 | 20.5923 | 25.245 | 28.798 | 32.319
| Port BurwellIce Accretion2090RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2090 | 16.6586 | 20.3599 | 24.98 | 28.5099 | 32.004
| Port BurwellIce Accretion2095RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2095 | 16.4498 | 20.1275 | 24.715 | 28.2218 | 31.689
| Port BurwellIce Accretion2100RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2100 | 16.241 | 19.8951 | 24.45 | 27.9336 | 31.374
| Port BurwellIce Accretion2023RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2023 | 20.3326 | 24.402 | 29.55 | 33.4932 | 37.422
| Port BurwellIce Accretion2025RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2025 | 20.2213 | 24.2816 | 29.42 | 33.352 | 37.2708
| Port BurwellIce Accretion2030RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2030 | 20.11 | 24.1613 | 29.29 | 33.2107 | 37.1196
| Port BurwellIce Accretion2035RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2035 | 19.9986 | 24.0409 | 29.16 | 33.0695 | 36.9684
| Port BurwellIce Accretion2040RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2040 | 19.8873 | 23.9206 | 29.03 | 32.9282 | 36.8172
| Port BurwellIce Accretion2045RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2045 | 19.7759 | 23.8002 | 28.9 | 32.7869 | 36.666
| Port BurwellIce Accretion2050RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2050 | 19.2304 | 23.2018 | 28.224 | 32.0491 | 35.8646
| Port BurwellIce Accretion2055RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2055 | 18.7962 | 22.7237 | 27.678 | 31.4524 | 35.2145
| Port BurwellIce Accretion2060RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2060 | 18.362 | 22.2457 | 27.132 | 30.8558 | 34.5643
| Port BurwellIce Accretion2065RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2065 | 17.9278 | 21.7676 | 26.586 | 30.2591 | 33.9142
| Port BurwellIce Accretion2070RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2070 | 17.4936 | 21.2895 | 26.04 | 29.6625 | 33.264
| Port BurwellIce Accretion2075RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2075 | 17.1804 | 20.9409 | 25.6425 | 29.2303 | 32.7915
| Port BurwellIce Accretion2080RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2080 | 16.8673 | 20.5923 | 25.245 | 28.798 | 32.319
| Port BurwellIce Accretion2085RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2085 | 16.5542 | 20.2437 | 24.8475 | 28.3658 | 31.8465
| Port BurwellIce Accretion2090RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2090 | 15.3852 | 18.8825 | 23.26 | 26.5889 | 29.8872
| Port BurwellIce Accretion2095RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2095 | 14.5293 | 17.8699 | 22.07 | 25.2442 | 28.4004
| Port BurwellIce Accretion2100RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2100 | 13.6734 | 16.8573 | 20.88 | 23.8995 | 26.9136
| Port BurwellIce Accretion2023RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2023 | 20.3326 | 24.402 | 29.55 | 33.4932 | 37.422
| Port BurwellIce Accretion2025RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2025 | 20.11 | 24.1613 | 29.29 | 33.2107 | 37.1196
| Port BurwellIce Accretion2030RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2030 | 19.8873 | 23.9206 | 29.03 | 32.9282 | 36.8172
| Port BurwellIce Accretion2035RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2035 | 19.6646 | 23.6799 | 28.77 | 32.6457 | 36.5148
| Port BurwellIce Accretion2040RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2040 | 18.9409 | 22.8831 | 27.86 | 31.6513 | 35.4312
| Port BurwellIce Accretion2045RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2045 | 18.2173 | 22.0863 | 26.95 | 30.6569 | 34.3476
| Port BurwellIce Accretion2050RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2050 | 17.0761 | 20.8247 | 25.51 | 29.0862 | 32.634
| Port BurwellIce Accretion2055RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2055 | 16.6586 | 20.3599 | 24.98 | 28.5099 | 32.004
| Port BurwellIce Accretion2060RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2060 | 15.3852 | 18.8825 | 23.26 | 26.5889 | 29.8872
| Port BurwellIce Accretion2065RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2065 | 14.5293 | 17.8699 | 22.07 | 25.2442 | 28.4004
| Port BurwellIce Accretion2070RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2070 | 13.2628 | 16.4008 | 20.34 | 23.3006 | 26.2584
| Port BurwellIce Accretion2075RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2075 | 12.8523 | 15.9443 | 19.8 | 22.7017 | 25.6032
| Port BurwellIce Accretion2080RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2080 | 12.4417 | 15.4878 | 19.26 | 22.1028 | 24.948
| Port BurwellIce Accretion2085RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2085 | 11.5232 | 14.3797 | 17.94 | 20.6112 | 23.2848
| Port BurwellIce Accretion2090RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2090 | 10.6047 | 13.2717 | 16.62 | 19.1196 | 21.6216
| Port BurwellIce Accretion2095RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2095 | 10.6047 | 13.2717 | 16.62 | 19.1196 | 21.6216
| Port BurwellIce Accretion2100RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2100 | 10.6047 | 13.2717 | 16.62 | 19.1196 | 21.6216
| Port BurwellWind2023RCP4.5 | Port Burwell | Wind | RCP4.5 | 2023 | 88.6477 | 95.5809 | 102.8976 | 110.1877 | 117.4893
| Port BurwellWind2025RCP4.5 | Port Burwell | Wind | RCP4.5 | 2025 | 88.724 | 95.6821 | 103.0319 | 110.3515 | 117.6792
| Port BurwellWind2030RCP4.5 | Port Burwell | Wind | RCP4.5 | 2030 | 88.8004 | 95.7833 | 103.1662 | 110.5152 | 117.8692
| Port BurwellWind2035RCP4.5 | Port Burwell | Wind | RCP4.5 | 2035 | 88.8767 | 95.8845 | 103.3005 | 110.6789 | 118.0591
| Port BurwellWind2040RCP4.5 | Port Burwell | Wind | RCP4.5 | 2040 | 88.953 | 95.9857 | 103.4348 | 110.8426 | 118.249
| Port BurwellWind2045RCP4.5 | Port Burwell | Wind | RCP4.5 | 2045 | 89.0294 | 96.0869 | 103.5691 | 111.0063 | 118.4389
| Port BurwellWind2050RCP4.5 | Port Burwell | Wind | RCP4.5 | 2050 | 89.185 | 96.2943 | 103.8442 | 111.3381 | 118.8289
| Port BurwellWind2055RCP4.5 | Port Burwell | Wind | RCP4.5 | 2055 | 89.2642 | 96.4005 | 103.9849 | 111.5062 | 119.0289
| Port BurwellWind2060RCP4.5 | Port Burwell | Wind | RCP4.5 | 2060 | 89.3435 | 96.5068 | 104.1257 | 111.6742 | 119.2289
| Port BurwellWind2065RCP4.5 | Port Burwell | Wind | RCP4.5 | 2065 | 89.4228 | 96.613 | 104.2664 | 111.8423 | 119.4289
| Port BurwellWind2070RCP4.5 | Port Burwell | Wind | RCP4.5 | 2070 | 89.502 | 96.7193 | 104.4072 | 112.0104 | 119.6289
| Port BurwellWind2075RCP4.5 | Port Burwell | Wind | RCP4.5 | 2075 | 89.6224 | 96.8742 | 104.6061 | 112.2469 | 119.906
| Port BurwellWind2080RCP4.5 | Port Burwell | Wind | RCP4.5 | 2080 | 89.7428 | 97.0291 | 104.805 | 112.4833 | 120.1831
| Port BurwellWind2085RCP4.5 | Port Burwell | Wind | RCP4.5 | 2085 | 89.8631 | 97.1841 | 105.0039 | 112.7198 | 120.4603
| Port BurwellWind2090RCP4.5 | Port Burwell | Wind | RCP4.5 | 2090 | 89.9835 | 97.339 | 105.2028 | 112.9563 | 120.7374
| Port BurwellWind2095RCP4.5 | Port Burwell | Wind | RCP4.5 | 2095 | 90.1039 | 97.4939 | 105.4017 | 113.1927 | 121.0145
| Port BurwellWind2100RCP4.5 | Port Burwell | Wind | RCP4.5 | 2100 | 90.2242 | 97.6489 | 105.6006 | 113.4292 | 121.2917
| Port BurwellWind2023RCP6.0 | Port Burwell | Wind | RCP6.0 | 2023 | 88.6477 | 95.5809 | 102.8976 | 110.1877 | 117.4893
| Port BurwellWind2025RCP6.0 | Port Burwell | Wind | RCP6.0 | 2025 | 88.724 | 95.6821 | 103.0319 | 110.3515 | 117.6792
| Port BurwellWind2030RCP6.0 | Port Burwell | Wind | RCP6.0 | 2030 | 88.8004 | 95.7833 | 103.1662 | 110.5152 | 117.8692
| Port BurwellWind2035RCP6.0 | Port Burwell | Wind | RCP6.0 | 2035 | 88.8767 | 95.8845 | 103.3005 | 110.6789 | 118.0591
| Port BurwellWind2040RCP6.0 | Port Burwell | Wind | RCP6.0 | 2040 | 88.953 | 95.9857 | 103.4348 | 110.8426 | 118.249
| Port BurwellWind2045RCP6.0 | Port Burwell | Wind | RCP6.0 | 2045 | 89.0294 | 96.0869 | 103.5691 | 111.0063 | 118.4389
| Port BurwellWind2050RCP6.0 | Port Burwell | Wind | RCP6.0 | 2050 | 89.185 | 96.2943 | 103.8442 | 111.3381 | 118.8289
| Port BurwellWind2055RCP6.0 | Port Burwell | Wind | RCP6.0 | 2055 | 89.2642 | 96.4005 | 103.9849 | 111.5062 | 119.0289
| Port BurwellWind2060RCP6.0 | Port Burwell | Wind | RCP6.0 | 2060 | 89.3435 | 96.5068 | 104.1257 | 111.6742 | 119.2289
| Port BurwellWind2065RCP6.0 | Port Burwell | Wind | RCP6.0 | 2065 | 89.4228 | 96.613 | 104.2664 | 111.8423 | 119.4289
| Port BurwellWind2070RCP6.0 | Port Burwell | Wind | RCP6.0 | 2070 | 89.502 | 96.7193 | 104.4072 | 112.0104 | 119.6289
| Port BurwellWind2075RCP6.0 | Port Burwell | Wind | RCP6.0 | 2075 | 89.6826 | 96.9517 | 104.7056 | 112.3651 | 120.0446
| Port BurwellWind2080RCP6.0 | Port Burwell | Wind | RCP6.0 | 2080 | 89.8631 | 97.1841 | 105.0039 | 112.7198 | 120.4603
| Port BurwellWind2085RCP6.0 | Port Burwell | Wind | RCP6.0 | 2085 | 90.0437 | 97.4165 | 105.3022 | 113.0745 | 120.876
| Port BurwellWind2090RCP6.0 | Port Burwell | Wind | RCP6.0 | 2090 | 90.4826 | 97.9841 | 106.0256 | 113.9349 | 121.8731
| Port BurwellWind2095RCP6.0 | Port Burwell | Wind | RCP6.0 | 2095 | 90.741 | 98.3192 | 106.4506 | 114.4406 | 122.4545
| Port BurwellWind2100RCP6.0 | Port Burwell | Wind | RCP6.0 | 2100 | 90.9993 | 98.6544 | 106.8756 | 114.9462 | 123.0359
| Port BurwellWind2023RCP8.5 | Port Burwell | Wind | RCP8.5 | 2023 | 88.6477 | 95.5809 | 102.8976 | 110.1877 | 117.4893
| Port BurwellWind2025RCP8.5 | Port Burwell | Wind | RCP8.5 | 2025 | 88.8004 | 95.7833 | 103.1662 | 110.5152 | 117.8692
| Port BurwellWind2030RCP8.5 | Port Burwell | Wind | RCP8.5 | 2030 | 88.953 | 95.9857 | 103.4348 | 110.8426 | 118.249
| Port BurwellWind2035RCP8.5 | Port Burwell | Wind | RCP8.5 | 2035 | 89.1057 | 96.188 | 103.7034 | 111.17 | 118.6289
| Port BurwellWind2040RCP8.5 | Port Burwell | Wind | RCP8.5 | 2040 | 89.2378 | 96.3651 | 103.938 | 111.4501 | 118.9622
| Port BurwellWind2045RCP8.5 | Port Burwell | Wind | RCP8.5 | 2045 | 89.3699 | 96.5422 | 104.1726 | 111.7303 | 119.2955
| Port BurwellWind2050RCP8.5 | Port Burwell | Wind | RCP8.5 | 2050 | 89.7428 | 97.0291 | 104.805 | 112.4833 | 120.1831
| Port BurwellWind2055RCP8.5 | Port Burwell | Wind | RCP8.5 | 2055 | 89.9835 | 97.339 | 105.2028 | 112.9563 | 120.7374
| Port BurwellWind2060RCP8.5 | Port Burwell | Wind | RCP8.5 | 2060 | 90.4826 | 97.9841 | 106.0256 | 113.9349 | 121.8731
| Port BurwellWind2065RCP8.5 | Port Burwell | Wind | RCP8.5 | 2065 | 90.741 | 98.3192 | 106.4506 | 114.4406 | 122.4545
| Port BurwellWind2070RCP8.5 | Port Burwell | Wind | RCP8.5 | 2070 | 91.149 | 98.8663 | 107.168 | 115.3064 | 123.4661
| Port BurwellWind2075RCP8.5 | Port Burwell | Wind | RCP8.5 | 2075 | 91.2988 | 99.0781 | 107.4604 | 115.6666 | 123.8963
| Port BurwellWind2080RCP8.5 | Port Burwell | Wind | RCP8.5 | 2080 | 91.4485 | 99.29 | 107.7528 | 116.0267 | 124.3266
| Port BurwellWind2085RCP8.5 | Port Burwell | Wind | RCP8.5 | 2085 | 91.792 | 99.7405 | 108.3495 | 116.7361 | 125.1638
| Port BurwellWind2090RCP8.5 | Port Burwell | Wind | RCP8.5 | 2090 | 92.1355 | 100.1911 | 108.9462 | 117.4456 | 126.001
| Port BurwellWind2095RCP8.5 | Port Burwell | Wind | RCP8.5 | 2095 | 92.1355 | 100.1911 | 108.9462 | 117.4456 | 126.001
| Port BurwellWind2100RCP8.5 | Port Burwell | Wind | RCP8.5 | 2100 | 92.1355 | 100.1911 | 108.9462 | 117.4456 | 126.001
| Port ColborneIce Accretion2023RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2023 | 20.6458 | 24.7755 | 30 | 34.0017 | 37.989
| Port ColborneIce Accretion2025RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2025 | 20.5483 | 24.6676 | 29.885 | 33.8717 | 37.8504
| Port ColborneIce Accretion2030RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2030 | 20.4509 | 24.5597 | 29.77 | 33.7418 | 37.7118
| Port ColborneIce Accretion2035RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2035 | 20.3535 | 24.4518 | 29.655 | 33.6118 | 37.5732
| Port ColborneIce Accretion2040RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2040 | 20.2561 | 24.3439 | 29.54 | 33.4819 | 37.4346
| Port ColborneIce Accretion2045RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2045 | 20.1587 | 24.236 | 29.425 | 33.352 | 37.296
| Port ColborneIce Accretion2050RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2050 | 19.6145 | 23.6251 | 28.722 | 32.5711 | 36.4468
| Port ColborneIce Accretion2055RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2055 | 19.1678 | 23.1221 | 28.134 | 31.9202 | 35.7361
| Port ColborneIce Accretion2060RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2060 | 18.721 | 22.6192 | 27.546 | 31.2694 | 35.0255
| Port ColborneIce Accretion2065RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2065 | 18.2743 | 22.1162 | 26.958 | 30.6185 | 34.3148
| Port ColborneIce Accretion2070RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2070 | 17.8276 | 21.6132 | 26.37 | 29.9676 | 33.6042
| Port ColborneIce Accretion2075RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2075 | 17.6606 | 21.4389 | 26.185 | 29.7755 | 33.4026
| Port ColborneIce Accretion2080RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2080 | 17.4936 | 21.2646 | 26 | 29.5834 | 33.201
| Port ColborneIce Accretion2085RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2085 | 17.3266 | 21.0903 | 25.815 | 29.3913 | 32.9994
| Port ColborneIce Accretion2090RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2090 | 17.1596 | 20.916 | 25.63 | 29.1992 | 32.7978
| Port ColborneIce Accretion2095RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2095 | 16.9926 | 20.7417 | 25.445 | 29.0071 | 32.5962
| Port ColborneIce Accretion2100RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2100 | 16.8256 | 20.5674 | 25.26 | 28.815 | 32.3946
| Port ColborneIce Accretion2023RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2023 | 20.6458 | 24.7755 | 30 | 34.0017 | 37.989
| Port ColborneIce Accretion2025RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2025 | 20.5483 | 24.6676 | 29.885 | 33.8717 | 37.8504
| Port ColborneIce Accretion2030RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2030 | 20.4509 | 24.5597 | 29.77 | 33.7418 | 37.7118
| Port ColborneIce Accretion2035RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2035 | 20.3535 | 24.4518 | 29.655 | 33.6118 | 37.5732
| Port ColborneIce Accretion2040RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2040 | 20.2561 | 24.3439 | 29.54 | 33.4819 | 37.4346
| Port ColborneIce Accretion2045RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2045 | 20.1587 | 24.236 | 29.425 | 33.352 | 37.296
| Port ColborneIce Accretion2050RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2050 | 19.6145 | 23.6251 | 28.722 | 32.5711 | 36.4468
| Port ColborneIce Accretion2055RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2055 | 19.1678 | 23.1221 | 28.134 | 31.9202 | 35.7361
| Port ColborneIce Accretion2060RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2060 | 18.721 | 22.6192 | 27.546 | 31.2694 | 35.0255
| Port ColborneIce Accretion2065RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2065 | 18.2743 | 22.1162 | 26.958 | 30.6185 | 34.3148
| Port ColborneIce Accretion2070RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2070 | 17.8276 | 21.6132 | 26.37 | 29.9676 | 33.6042
| Port ColborneIce Accretion2075RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2075 | 17.5771 | 21.3517 | 26.0925 | 29.6794 | 33.3018
| Port ColborneIce Accretion2080RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2080 | 17.3266 | 21.0903 | 25.815 | 29.3913 | 32.9994
| Port ColborneIce Accretion2085RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2085 | 17.0761 | 20.8288 | 25.5375 | 29.1031 | 32.697
| Port ColborneIce Accretion2090RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2090 | 16.1436 | 19.7872 | 24.35 | 27.8093 | 31.2732
| Port ColborneIce Accretion2095RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2095 | 15.4617 | 19.007 | 23.44 | 26.8036 | 30.1518
| Port ColborneIce Accretion2100RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2100 | 14.7798 | 18.2268 | 22.53 | 25.7979 | 29.0304
| Port ColborneIce Accretion2023RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2023 | 20.6458 | 24.7755 | 30 | 34.0017 | 37.989
| Port ColborneIce Accretion2025RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2025 | 20.4509 | 24.5597 | 29.77 | 33.7418 | 37.7118
| Port ColborneIce Accretion2030RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2030 | 20.2561 | 24.3439 | 29.54 | 33.4819 | 37.4346
| Port ColborneIce Accretion2035RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2035 | 20.0612 | 24.1281 | 29.31 | 33.222 | 37.1574
| Port ColborneIce Accretion2040RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2040 | 19.3167 | 23.2898 | 28.33 | 32.1372 | 35.973
| Port ColborneIce Accretion2045RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2045 | 18.5721 | 22.4515 | 27.35 | 31.0524 | 34.7886
| Port ColborneIce Accretion2050RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2050 | 17.4936 | 21.2646 | 26 | 29.5834 | 33.201
| Port ColborneIce Accretion2055RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2055 | 17.1596 | 20.916 | 25.63 | 29.1992 | 32.7978
| Port ColborneIce Accretion2060RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2060 | 16.1436 | 19.7872 | 24.35 | 27.8093 | 31.2732
| Port ColborneIce Accretion2065RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2065 | 15.4617 | 19.007 | 23.44 | 26.8036 | 30.1518
| Port ColborneIce Accretion2070RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2070 | 14.4388 | 17.8367 | 22.09 | 25.312 | 28.5012
| Port ColborneIce Accretion2075RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2075 | 14.0978 | 17.4466 | 21.65 | 24.8261 | 27.972
| Port ColborneIce Accretion2080RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2080 | 13.7569 | 17.0565 | 21.21 | 24.3402 | 27.4428
| Port ColborneIce Accretion2085RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2085 | 12.9845 | 16.1476 | 20.115 | 23.1029 | 26.0631
| Port ColborneIce Accretion2090RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2090 | 12.2121 | 15.2388 | 19.02 | 21.8655 | 24.6834
| Port ColborneIce Accretion2095RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2095 | 12.2121 | 15.2388 | 19.02 | 21.8655 | 24.6834
| Port ColborneIce Accretion2100RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2100 | 12.2121 | 15.2388 | 19.02 | 21.8655 | 24.6834
| Port ColborneWind2023RCP4.5 | Port Colborne | Wind | RCP4.5 | 2023 | 88.9824 | 96.0647 | 103.581 | 111.05 | 118.5126
| Port ColborneWind2025RCP4.5 | Port Colborne | Wind | RCP4.5 | 2025 | 88.953 | 96.0347 | 103.5487 | 111.0154 | 118.4758
| Port ColborneWind2030RCP4.5 | Port Colborne | Wind | RCP4.5 | 2030 | 88.9237 | 96.0046 | 103.5164 | 110.9808 | 118.4389
| Port ColborneWind2035RCP4.5 | Port Colborne | Wind | RCP4.5 | 2035 | 88.8943 | 95.9746 | 103.4841 | 110.9463 | 118.4021
| Port ColborneWind2040RCP4.5 | Port Colborne | Wind | RCP4.5 | 2040 | 88.8649 | 95.9446 | 103.4518 | 110.9117 | 118.3653
| Port ColborneWind2045RCP4.5 | Port Colborne | Wind | RCP4.5 | 2045 | 88.8356 | 95.9145 | 103.4195 | 110.8771 | 118.3285
| Port ColborneWind2050RCP4.5 | Port Colborne | Wind | RCP4.5 | 2050 | 88.8644 | 95.9585 | 103.4831 | 110.9539 | 118.4219
| Port ColborneWind2055RCP4.5 | Port Colborne | Wind | RCP4.5 | 2055 | 88.9225 | 96.0325 | 103.579 | 111.0652 | 118.5521
| Port ColborneWind2060RCP4.5 | Port Colborne | Wind | RCP4.5 | 2060 | 88.9806 | 96.1065 | 103.6748 | 111.1766 | 118.6823
| Port ColborneWind2065RCP4.5 | Port Colborne | Wind | RCP4.5 | 2065 | 89.0388 | 96.1805 | 103.7707 | 111.2879 | 118.8126
| Port ColborneWind2070RCP4.5 | Port Colborne | Wind | RCP4.5 | 2070 | 89.0969 | 96.2544 | 103.8666 | 111.3992 | 118.9428
| Port ColborneWind2075RCP4.5 | Port Colborne | Wind | RCP4.5 | 2075 | 89.1791 | 96.3699 | 104.0247 | 111.592 | 119.1734
| Port ColborneWind2080RCP4.5 | Port Colborne | Wind | RCP4.5 | 2080 | 89.2613 | 96.4853 | 104.1828 | 111.7848 | 119.4041
| Port ColborneWind2085RCP4.5 | Port Colborne | Wind | RCP4.5 | 2085 | 89.3435 | 96.6007 | 104.3409 | 111.9776 | 119.6347
| Port ColborneWind2090RCP4.5 | Port Colborne | Wind | RCP4.5 | 2090 | 89.4257 | 96.7161 | 104.499 | 112.1705 | 119.8653
| Port ColborneWind2095RCP4.5 | Port Colborne | Wind | RCP4.5 | 2095 | 89.5079 | 96.8315 | 104.6571 | 112.3633 | 120.0959
| Port ColborneWind2100RCP4.5 | Port Colborne | Wind | RCP4.5 | 2100 | 89.5901 | 96.9469 | 104.8152 | 112.5561 | 120.3265
| Port ColborneWind2023RCP6.0 | Port Colborne | Wind | RCP6.0 | 2023 | 88.9824 | 96.0647 | 103.581 | 111.05 | 118.5126
| Port ColborneWind2025RCP6.0 | Port Colborne | Wind | RCP6.0 | 2025 | 88.953 | 96.0347 | 103.5487 | 111.0154 | 118.4758
| Port ColborneWind2030RCP6.0 | Port Colborne | Wind | RCP6.0 | 2030 | 88.9237 | 96.0046 | 103.5164 | 110.9808 | 118.4389
| Port ColborneWind2035RCP6.0 | Port Colborne | Wind | RCP6.0 | 2035 | 88.8943 | 95.9746 | 103.4841 | 110.9463 | 118.4021
| Port ColborneWind2040RCP6.0 | Port Colborne | Wind | RCP6.0 | 2040 | 88.8649 | 95.9446 | 103.4518 | 110.9117 | 118.3653
| Port ColborneWind2045RCP6.0 | Port Colborne | Wind | RCP6.0 | 2045 | 88.8356 | 95.9145 | 103.4195 | 110.8771 | 118.3285
| Port ColborneWind2050RCP6.0 | Port Colborne | Wind | RCP6.0 | 2050 | 88.8644 | 95.9585 | 103.4831 | 110.9539 | 118.4219
| Port ColborneWind2055RCP6.0 | Port Colborne | Wind | RCP6.0 | 2055 | 88.9225 | 96.0325 | 103.579 | 111.0652 | 118.5521
| Port ColborneWind2060RCP6.0 | Port Colborne | Wind | RCP6.0 | 2060 | 88.9806 | 96.1065 | 103.6748 | 111.1766 | 118.6823
| Port ColborneWind2065RCP6.0 | Port Colborne | Wind | RCP6.0 | 2065 | 89.0388 | 96.1805 | 103.7707 | 111.2879 | 118.8126
| Port ColborneWind2070RCP6.0 | Port Colborne | Wind | RCP6.0 | 2070 | 89.0969 | 96.2544 | 103.8666 | 111.3992 | 118.9428
| Port ColborneWind2075RCP6.0 | Port Colborne | Wind | RCP6.0 | 2075 | 89.2202 | 96.4276 | 104.1038 | 111.6884 | 119.2887
| Port ColborneWind2080RCP6.0 | Port Colborne | Wind | RCP6.0 | 2080 | 89.3435 | 96.6007 | 104.3409 | 111.9776 | 119.6347
| Port ColborneWind2085RCP6.0 | Port Colborne | Wind | RCP6.0 | 2085 | 89.4668 | 96.7738 | 104.5781 | 112.2669 | 119.9806
| Port ColborneWind2090RCP6.0 | Port Colborne | Wind | RCP6.0 | 2090 | 89.778 | 97.1872 | 105.1178 | 112.9162 | 120.7452
| Port ColborneWind2095RCP6.0 | Port Colborne | Wind | RCP6.0 | 2095 | 89.9659 | 97.4275 | 105.4204 | 113.2764 | 121.1638
| Port ColborneWind2100RCP6.0 | Port Colborne | Wind | RCP6.0 | 2100 | 90.1538 | 97.6679 | 105.723 | 113.6366 | 121.5824
| Port ColborneWind2023RCP8.5 | Port Colborne | Wind | RCP8.5 | 2023 | 88.9824 | 96.0647 | 103.581 | 111.05 | 118.5126
| Port ColborneWind2025RCP8.5 | Port Colborne | Wind | RCP8.5 | 2025 | 88.9237 | 96.0046 | 103.5164 | 110.9808 | 118.4389
| Port ColborneWind2030RCP8.5 | Port Colborne | Wind | RCP8.5 | 2030 | 88.8649 | 95.9446 | 103.4518 | 110.9117 | 118.3653
| Port ColborneWind2035RCP8.5 | Port Colborne | Wind | RCP8.5 | 2035 | 88.8062 | 95.8845 | 103.3872 | 110.8426 | 118.2916
| Port ColborneWind2040RCP8.5 | Port Colborne | Wind | RCP8.5 | 2040 | 88.9031 | 96.0078 | 103.547 | 111.0281 | 118.5087
| Port ColborneWind2045RCP8.5 | Port Colborne | Wind | RCP8.5 | 2045 | 89 | 96.1311 | 103.7068 | 111.2137 | 118.7258
| Port ColborneWind2050RCP8.5 | Port Colborne | Wind | RCP8.5 | 2050 | 89.2613 | 96.4853 | 104.1828 | 111.7848 | 119.4041
| Port ColborneWind2055RCP8.5 | Port Colborne | Wind | RCP8.5 | 2055 | 89.4257 | 96.7161 | 104.499 | 112.1705 | 119.8653
| Port ColborneWind2060RCP8.5 | Port Colborne | Wind | RCP8.5 | 2060 | 89.778 | 97.1872 | 105.1178 | 112.9162 | 120.7452
| Port ColborneWind2065RCP8.5 | Port Colborne | Wind | RCP8.5 | 2065 | 89.9659 | 97.4275 | 105.4204 | 113.2764 | 121.1638
| Port ColborneWind2070RCP8.5 | Port Colborne | Wind | RCP8.5 | 2070 | 90.2154 | 97.7722 | 105.8896 | 113.8548 | 121.8459
| Port ColborneWind2075RCP8.5 | Port Colborne | Wind | RCP8.5 | 2075 | 90.2771 | 97.8765 | 106.0562 | 114.0731 | 122.1095
| Port ColborneWind2080RCP8.5 | Port Colborne | Wind | RCP8.5 | 2080 | 90.3387 | 97.9809 | 106.2228 | 114.2914 | 122.3731
| Port ColborneWind2085RCP8.5 | Port Colborne | Wind | RCP8.5 | 2085 | 90.4048 | 98.09 | 106.3809 | 114.4879 | 122.6173
| Port ColborneWind2090RCP8.5 | Port Colborne | Wind | RCP8.5 | 2090 | 90.4709 | 98.1991 | 106.539 | 114.6843 | 122.8614
| Port ColborneWind2095RCP8.5 | Port Colborne | Wind | RCP8.5 | 2095 | 90.4709 | 98.1991 | 106.539 | 114.6843 | 122.8614
| Port ColborneWind2100RCP8.5 | Port Colborne | Wind | RCP8.5 | 2100 | 90.4709 | 98.1991 | 106.539 | 114.6843 | 122.8614
| Port ElginIce Accretion2023RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2023 | 13.9865 | 16.7162 | 20.18 | 22.8486 | 25.4772
| Port ElginIce Accretion2025RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2025 | 13.9958 | 16.7383 | 20.2167 | 22.8938 | 25.536
| Port ElginIce Accretion2030RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2030 | 14.0051 | 16.7605 | 20.2533 | 22.939 | 25.5948
| Port ElginIce Accretion2035RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2035 | 14.0143 | 16.7826 | 20.29 | 22.9842 | 25.6536
| Port ElginIce Accretion2040RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2040 | 14.0236 | 16.8047 | 20.3267 | 23.0294 | 25.7124
| Port ElginIce Accretion2045RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2045 | 14.0329 | 16.8269 | 20.3633 | 23.0746 | 25.7712
| Port ElginIce Accretion2050RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2050 | 13.9921 | 16.8025 | 20.36 | 23.0836 | 25.7947
| Port ElginIce Accretion2055RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2055 | 13.942 | 16.756 | 20.32 | 23.0475 | 25.7594
| Port ElginIce Accretion2060RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2060 | 13.8919 | 16.7096 | 20.28 | 23.0113 | 25.7242
| Port ElginIce Accretion2065RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2065 | 13.8418 | 16.6631 | 20.24 | 22.9752 | 25.6889
| Port ElginIce Accretion2070RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2070 | 13.7917 | 16.6166 | 20.2 | 22.939 | 25.6536
| Port ElginIce Accretion2075RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2075 | 13.7406 | 16.5806 | 20.18 | 22.9277 | 25.6536
| Port ElginIce Accretion2080RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2080 | 13.6896 | 16.5447 | 20.16 | 22.9164 | 25.6536
| Port ElginIce Accretion2085RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2085 | 13.6386 | 16.5087 | 20.14 | 22.9051 | 25.6536
| Port ElginIce Accretion2090RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2090 | 13.5876 | 16.4727 | 20.12 | 22.8938 | 25.6536
| Port ElginIce Accretion2095RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2095 | 13.5365 | 16.4368 | 20.1 | 22.8825 | 25.6536
| Port ElginIce Accretion2100RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2100 | 13.4855 | 16.4008 | 20.08 | 22.8712 | 25.6536
| Port ElginIce Accretion2023RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2023 | 13.9865 | 16.7162 | 20.18 | 22.8486 | 25.4772
| Port ElginIce Accretion2025RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2025 | 13.9958 | 16.7383 | 20.2167 | 22.8938 | 25.536
| Port ElginIce Accretion2030RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2030 | 14.0051 | 16.7605 | 20.2533 | 22.939 | 25.5948
| Port ElginIce Accretion2035RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2035 | 14.0143 | 16.7826 | 20.29 | 22.9842 | 25.6536
| Port ElginIce Accretion2040RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2040 | 14.0236 | 16.8047 | 20.3267 | 23.0294 | 25.7124
| Port ElginIce Accretion2045RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2045 | 14.0329 | 16.8269 | 20.3633 | 23.0746 | 25.7712
| Port ElginIce Accretion2050RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2050 | 13.9921 | 16.8025 | 20.36 | 23.0836 | 25.7947
| Port ElginIce Accretion2055RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2055 | 13.942 | 16.756 | 20.32 | 23.0475 | 25.7594
| Port ElginIce Accretion2060RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2060 | 13.8919 | 16.7096 | 20.28 | 23.0113 | 25.7242
| Port ElginIce Accretion2065RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2065 | 13.8418 | 16.6631 | 20.24 | 22.9752 | 25.6889
| Port ElginIce Accretion2070RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2070 | 13.7917 | 16.6166 | 20.2 | 22.939 | 25.6536
| Port ElginIce Accretion2075RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2075 | 13.7151 | 16.5626 | 20.17 | 22.922 | 25.6536
| Port ElginIce Accretion2080RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2080 | 13.6386 | 16.5087 | 20.14 | 22.9051 | 25.6536
| Port ElginIce Accretion2085RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2085 | 13.562 | 16.4547 | 20.11 | 22.8881 | 25.6536
| Port ElginIce Accretion2090RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2090 | 13.2489 | 16.1518 | 19.8067 | 22.5849 | 25.3512
| Port ElginIce Accretion2095RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2095 | 13.0123 | 15.9028 | 19.5333 | 22.2987 | 25.0488
| Port ElginIce Accretion2100RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2100 | 12.7757 | 15.6538 | 19.26 | 22.0124 | 24.7464
| Port ElginIce Accretion2023RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2023 | 13.9865 | 16.7162 | 20.18 | 22.8486 | 25.4772
| Port ElginIce Accretion2025RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2025 | 14.0051 | 16.7605 | 20.2533 | 22.939 | 25.5948
| Port ElginIce Accretion2030RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2030 | 14.0236 | 16.8047 | 20.3267 | 23.0294 | 25.7124
| Port ElginIce Accretion2035RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2035 | 14.0422 | 16.849 | 20.4 | 23.1198 | 25.83
| Port ElginIce Accretion2040RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2040 | 13.9587 | 16.7715 | 20.3333 | 23.0595 | 25.7712
| Port ElginIce Accretion2045RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2045 | 13.8752 | 16.6941 | 20.2667 | 22.9993 | 25.7124
| Port ElginIce Accretion2050RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2050 | 13.6896 | 16.5447 | 20.16 | 22.9164 | 25.6536
| Port ElginIce Accretion2055RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2055 | 13.5876 | 16.4727 | 20.12 | 22.8938 | 25.6536
| Port ElginIce Accretion2060RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2060 | 13.2489 | 16.1518 | 19.8067 | 22.5849 | 25.3512
| Port ElginIce Accretion2065RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2065 | 13.0123 | 15.9028 | 19.5333 | 22.2987 | 25.0488
| Port ElginIce Accretion2070RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2070 | 12.4232 | 15.2609 | 18.82 | 21.5378 | 24.234
| Port ElginIce Accretion2075RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2075 | 12.0706 | 14.8681 | 18.38 | 21.0632 | 23.7216
| Port ElginIce Accretion2080RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2080 | 11.718 | 14.4752 | 17.94 | 20.5886 | 23.2092
| Port ElginIce Accretion2085RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2085 | 11.1196 | 13.7863 | 17.13 | 19.6733 | 22.2012
| Port ElginIce Accretion2090RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2090 | 10.5212 | 13.0974 | 16.32 | 18.758 | 21.1932
| Port ElginIce Accretion2095RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2095 | 10.5212 | 13.0974 | 16.32 | 18.758 | 21.1932
| Port ElginIce Accretion2100RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2100 | 10.5212 | 13.0974 | 16.32 | 18.758 | 21.1932
| Port ElginWind2023RCP4.5 | Port Elgin | Wind | RCP4.5 | 2023 | 85.4848 | 91.9687 | 98.7624 | 105.591 | 112.4086
| Port ElginWind2025RCP4.5 | Port Elgin | Wind | RCP4.5 | 2025 | 85.5631 | 92.0654 | 98.8845 | 105.7323 | 112.5722
| Port ElginWind2030RCP4.5 | Port Elgin | Wind | RCP4.5 | 2030 | 85.6415 | 92.1621 | 99.0066 | 105.8735 | 112.7359
| Port ElginWind2035RCP4.5 | Port Elgin | Wind | RCP4.5 | 2035 | 85.7198 | 92.2587 | 99.1287 | 106.0147 | 112.8995
| Port ElginWind2040RCP4.5 | Port Elgin | Wind | RCP4.5 | 2040 | 85.7982 | 92.3554 | 99.2508 | 106.156 | 113.0631
| Port ElginWind2045RCP4.5 | Port Elgin | Wind | RCP4.5 | 2045 | 85.8766 | 92.4521 | 99.3729 | 106.2972 | 113.2268
| Port ElginWind2050RCP4.5 | Port Elgin | Wind | RCP4.5 | 2050 | 85.9515 | 92.5396 | 99.4752 | 106.413 | 113.3566
| Port ElginWind2055RCP4.5 | Port Elgin | Wind | RCP4.5 | 2055 | 85.9481 | 92.5304 | 99.4554 | 106.3876 | 113.3227
| Port ElginWind2060RCP4.5 | Port Elgin | Wind | RCP4.5 | 2060 | 85.9447 | 92.5211 | 99.4356 | 106.3622 | 113.2889
| Port ElginWind2065RCP4.5 | Port Elgin | Wind | RCP4.5 | 2065 | 85.9412 | 92.5119 | 99.4158 | 106.3368 | 113.255
| Port ElginWind2070RCP4.5 | Port Elgin | Wind | RCP4.5 | 2070 | 85.9378 | 92.5027 | 99.396 | 106.3113 | 113.2212
| Port ElginWind2075RCP4.5 | Port Elgin | Wind | RCP4.5 | 2075 | 85.9564 | 92.5227 | 99.4175 | 106.3343 | 113.2456
| Port ElginWind2080RCP4.5 | Port Elgin | Wind | RCP4.5 | 2080 | 85.9749 | 92.5426 | 99.4389 | 106.3573 | 113.2701
| Port ElginWind2085RCP4.5 | Port Elgin | Wind | RCP4.5 | 2085 | 85.9934 | 92.5626 | 99.4604 | 106.3802 | 113.2945
| Port ElginWind2090RCP4.5 | Port Elgin | Wind | RCP4.5 | 2090 | 86.0119 | 92.5825 | 99.4818 | 106.4032 | 113.319
| Port ElginWind2095RCP4.5 | Port Elgin | Wind | RCP4.5 | 2095 | 86.0304 | 92.6025 | 99.5033 | 106.4261 | 113.3434
| Port ElginWind2100RCP4.5 | Port Elgin | Wind | RCP4.5 | 2100 | 86.049 | 92.6224 | 99.5247 | 106.4491 | 113.3679
| Port ElginWind2023RCP6.0 | Port Elgin | Wind | RCP6.0 | 2023 | 85.4848 | 91.9687 | 98.7624 | 105.591 | 112.4086
| Port ElginWind2025RCP6.0 | Port Elgin | Wind | RCP6.0 | 2025 | 85.5631 | 92.0654 | 98.8845 | 105.7323 | 112.5722
| Port ElginWind2030RCP6.0 | Port Elgin | Wind | RCP6.0 | 2030 | 85.6415 | 92.1621 | 99.0066 | 105.8735 | 112.7359
| Port ElginWind2035RCP6.0 | Port Elgin | Wind | RCP6.0 | 2035 | 85.7198 | 92.2587 | 99.1287 | 106.0147 | 112.8995
| Port ElginWind2040RCP6.0 | Port Elgin | Wind | RCP6.0 | 2040 | 85.7982 | 92.3554 | 99.2508 | 106.156 | 113.0631
| Port ElginWind2045RCP6.0 | Port Elgin | Wind | RCP6.0 | 2045 | 85.8766 | 92.4521 | 99.3729 | 106.2972 | 113.2268
| Port ElginWind2050RCP6.0 | Port Elgin | Wind | RCP6.0 | 2050 | 85.9515 | 92.5396 | 99.4752 | 106.413 | 113.3566
| Port ElginWind2055RCP6.0 | Port Elgin | Wind | RCP6.0 | 2055 | 85.9481 | 92.5304 | 99.4554 | 106.3876 | 113.3227
| Port ElginWind2060RCP6.0 | Port Elgin | Wind | RCP6.0 | 2060 | 85.9447 | 92.5211 | 99.4356 | 106.3622 | 113.2889
| Port ElginWind2065RCP6.0 | Port Elgin | Wind | RCP6.0 | 2065 | 85.9412 | 92.5119 | 99.4158 | 106.3368 | 113.255
| Port ElginWind2070RCP6.0 | Port Elgin | Wind | RCP6.0 | 2070 | 85.9378 | 92.5027 | 99.396 | 106.3113 | 113.2212
| Port ElginWind2075RCP6.0 | Port Elgin | Wind | RCP6.0 | 2075 | 85.9656 | 92.5327 | 99.4282 | 106.3458 | 113.2578
| Port ElginWind2080RCP6.0 | Port Elgin | Wind | RCP6.0 | 2080 | 85.9934 | 92.5626 | 99.4604 | 106.3802 | 113.2945
| Port ElginWind2085RCP6.0 | Port Elgin | Wind | RCP6.0 | 2085 | 86.0212 | 92.5925 | 99.4925 | 106.4146 | 113.3312
| Port ElginWind2090RCP6.0 | Port Elgin | Wind | RCP6.0 | 2090 | 86.1857 | 92.7881 | 99.726 | 106.6786 | 113.6237
| Port ElginWind2095RCP6.0 | Port Elgin | Wind | RCP6.0 | 2095 | 86.3225 | 92.9539 | 99.9273 | 106.9081 | 113.8795
| Port ElginWind2100RCP6.0 | Port Elgin | Wind | RCP6.0 | 2100 | 86.4593 | 93.1196 | 100.1286 | 107.1376 | 114.1353
| Port ElginWind2023RCP8.5 | Port Elgin | Wind | RCP8.5 | 2023 | 85.4848 | 91.9687 | 98.7624 | 105.591 | 112.4086
| Port ElginWind2025RCP8.5 | Port Elgin | Wind | RCP8.5 | 2025 | 85.6415 | 92.1621 | 99.0066 | 105.8735 | 112.7359
| Port ElginWind2030RCP8.5 | Port Elgin | Wind | RCP8.5 | 2030 | 85.7982 | 92.3554 | 99.2508 | 106.156 | 113.0631
| Port ElginWind2035RCP8.5 | Port Elgin | Wind | RCP8.5 | 2035 | 85.9549 | 92.5488 | 99.495 | 106.4385 | 113.3904
| Port ElginWind2040RCP8.5 | Port Elgin | Wind | RCP8.5 | 2040 | 85.9492 | 92.5334 | 99.462 | 106.3961 | 113.334
| Port ElginWind2045RCP8.5 | Port Elgin | Wind | RCP8.5 | 2045 | 85.9435 | 92.5181 | 99.429 | 106.3537 | 113.2776
| Port ElginWind2050RCP8.5 | Port Elgin | Wind | RCP8.5 | 2050 | 85.9749 | 92.5426 | 99.4389 | 106.3573 | 113.2701
| Port ElginWind2055RCP8.5 | Port Elgin | Wind | RCP8.5 | 2055 | 86.0119 | 92.5825 | 99.4818 | 106.4032 | 113.319
| Port ElginWind2060RCP8.5 | Port Elgin | Wind | RCP8.5 | 2060 | 86.1857 | 92.7881 | 99.726 | 106.6786 | 113.6237
| Port ElginWind2065RCP8.5 | Port Elgin | Wind | RCP8.5 | 2065 | 86.3225 | 92.9539 | 99.9273 | 106.9081 | 113.8795
| Port ElginWind2070RCP8.5 | Port Elgin | Wind | RCP8.5 | 2070 | 86.5305 | 93.2055 | 100.2276 | 107.2506 | 114.267
| Port ElginWind2075RCP8.5 | Port Elgin | Wind | RCP8.5 | 2075 | 86.6018 | 93.2915 | 100.3266 | 107.3636 | 114.3987
| Port ElginWind2080RCP8.5 | Port Elgin | Wind | RCP8.5 | 2080 | 86.673 | 93.3774 | 100.4256 | 107.4766 | 114.5303
| Port ElginWind2085RCP8.5 | Port Elgin | Wind | RCP8.5 | 2085 | 87.0021 | 93.8193 | 101.0147 | 108.1863 | 115.3598
| Port ElginWind2090RCP8.5 | Port Elgin | Wind | RCP8.5 | 2090 | 87.3312 | 94.2613 | 101.6037 | 108.896 | 116.1894
| Port ElginWind2095RCP8.5 | Port Elgin | Wind | RCP8.5 | 2095 | 87.3312 | 94.2613 | 101.6037 | 108.896 | 116.1894
| Port ElginWind2100RCP8.5 | Port Elgin | Wind | RCP8.5 | 2100 | 87.3312 | 94.2613 | 101.6037 | 108.896 | 116.1894
| Port HopeIce Accretion2023RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2023 | 17.5875 | 20.999 | 25.325 | 28.6172 | 31.941
| Port HopeIce Accretion2025RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2025 | 17.6542 | 21.0958 | 25.4625 | 28.7867 | 32.1352
| Port HopeIce Accretion2030RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2030 | 17.7209 | 21.1927 | 25.6 | 28.9562 | 32.3295
| Port HopeIce Accretion2035RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2035 | 17.7876 | 21.2895 | 25.7375 | 29.1257 | 32.5237
| Port HopeIce Accretion2040RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2040 | 17.8543 | 21.3863 | 25.875 | 29.2952 | 32.718
| Port HopeIce Accretion2045RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2045 | 17.9209 | 21.4832 | 26.0125 | 29.4647 | 32.9123
| Port HopeIce Accretion2050RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2050 | 17.8867 | 21.4804 | 26.045 | 29.5212 | 32.9931
| Port HopeIce Accretion2055RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2055 | 17.7858 | 21.3808 | 25.94 | 29.4082 | 32.8797
| Port HopeIce Accretion2060RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2060 | 17.6849 | 21.2812 | 25.835 | 29.2952 | 32.7663
| Port HopeIce Accretion2065RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2065 | 17.584 | 21.1816 | 25.73 | 29.1822 | 32.6529
| Port HopeIce Accretion2070RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2070 | 17.4831 | 21.082 | 25.625 | 29.0692 | 32.5395
| Port HopeIce Accretion2075RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2075 | 17.5237 | 21.1615 | 25.7542 | 29.2387 | 32.7442
| Port HopeIce Accretion2080RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2080 | 17.5643 | 21.2411 | 25.8833 | 29.4082 | 32.949
| Port HopeIce Accretion2085RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2085 | 17.6049 | 21.3206 | 26.0125 | 29.5777 | 33.1538
| Port HopeIce Accretion2090RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2090 | 17.6455 | 21.4002 | 26.1417 | 29.7472 | 33.3585
| Port HopeIce Accretion2095RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2095 | 17.6861 | 21.4797 | 26.2708 | 29.9167 | 33.5632
| Port HopeIce Accretion2100RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2100 | 17.7267 | 21.5592 | 26.4 | 30.0862 | 33.768
| Port HopeIce Accretion2023RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2023 | 17.5875 | 20.999 | 25.325 | 28.6172 | 31.941
| Port HopeIce Accretion2025RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2025 | 17.6542 | 21.0958 | 25.4625 | 28.7867 | 32.1352
| Port HopeIce Accretion2030RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2030 | 17.7209 | 21.1927 | 25.6 | 28.9562 | 32.3295
| Port HopeIce Accretion2035RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2035 | 17.7876 | 21.2895 | 25.7375 | 29.1257 | 32.5237
| Port HopeIce Accretion2040RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2040 | 17.8543 | 21.3863 | 25.875 | 29.2952 | 32.718
| Port HopeIce Accretion2045RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2045 | 17.9209 | 21.4832 | 26.0125 | 29.4647 | 32.9123
| Port HopeIce Accretion2050RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2050 | 17.8867 | 21.4804 | 26.045 | 29.5212 | 32.9931
| Port HopeIce Accretion2055RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2055 | 17.7858 | 21.3808 | 25.94 | 29.4082 | 32.8797
| Port HopeIce Accretion2060RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2060 | 17.6849 | 21.2812 | 25.835 | 29.2952 | 32.7663
| Port HopeIce Accretion2065RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2065 | 17.584 | 21.1816 | 25.73 | 29.1822 | 32.6529
| Port HopeIce Accretion2070RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2070 | 17.4831 | 21.082 | 25.625 | 29.0692 | 32.5395
| Port HopeIce Accretion2075RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2075 | 17.544 | 21.2013 | 25.8187 | 29.3235 | 32.8466
| Port HopeIce Accretion2080RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2080 | 17.6049 | 21.3206 | 26.0125 | 29.5777 | 33.1538
| Port HopeIce Accretion2085RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2085 | 17.6658 | 21.4399 | 26.2063 | 29.832 | 33.4609
| Port HopeIce Accretion2090RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2090 | 17.3498 | 21.1512 | 25.95 | 29.606 | 33.243
| Port HopeIce Accretion2095RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2095 | 16.9728 | 20.7431 | 25.5 | 29.1257 | 32.718
| Port HopeIce Accretion2100RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2100 | 16.5959 | 20.335 | 25.05 | 28.6455 | 32.193
| Port HopeIce Accretion2023RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2023 | 17.5875 | 20.999 | 25.325 | 28.6172 | 31.941
| Port HopeIce Accretion2025RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2025 | 17.7209 | 21.1927 | 25.6 | 28.9562 | 32.3295
| Port HopeIce Accretion2030RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2030 | 17.8543 | 21.3863 | 25.875 | 29.2952 | 32.718
| Port HopeIce Accretion2035RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2035 | 17.9876 | 21.58 | 26.15 | 29.6342 | 33.1065
| Port HopeIce Accretion2040RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2040 | 17.8195 | 21.414 | 25.975 | 29.4459 | 32.9175
| Port HopeIce Accretion2045RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2045 | 17.6513 | 21.248 | 25.8 | 29.2576 | 32.7285
| Port HopeIce Accretion2050RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2050 | 17.5643 | 21.2411 | 25.8833 | 29.4082 | 32.949
| Port HopeIce Accretion2055RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2055 | 17.6455 | 21.4002 | 26.1417 | 29.7472 | 33.3585
| Port HopeIce Accretion2060RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2060 | 17.3498 | 21.1512 | 25.95 | 29.606 | 33.243
| Port HopeIce Accretion2065RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2065 | 16.9728 | 20.7431 | 25.5 | 29.1257 | 32.718
| Port HopeIce Accretion2070RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2070 | 16.2306 | 19.9338 | 24.6083 | 28.1558 | 31.6785
| Port HopeIce Accretion2075RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2075 | 15.8653 | 19.5327 | 24.1667 | 27.6662 | 31.164
| Port HopeIce Accretion2080RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2080 | 15.5 | 19.1315 | 23.725 | 27.1765 | 30.6495
| Port HopeIce Accretion2085RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2085 | 14.9259 | 18.4779 | 22.9625 | 26.3431 | 29.736
| Port HopeIce Accretion2090RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2090 | 14.3518 | 17.8242 | 22.2 | 25.5097 | 28.8225
| Port HopeIce Accretion2095RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2095 | 14.3518 | 17.8242 | 22.2 | 25.5097 | 28.8225
| Port HopeIce Accretion2100RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2100 | 14.3518 | 17.8242 | 22.2 | 25.5097 | 28.8225
| Port HopeWind2023RCP4.5 | Port Hope | Wind | RCP4.5 | 2023 | 85.707 | 92.2173 | 99.0495 | 105.9088 | 112.7584
| Port HopeWind2025RCP4.5 | Port Hope | Wind | RCP4.5 | 2025 | 85.7127 | 92.2311 | 99.0726 | 105.9388 | 112.796
| Port HopeWind2030RCP4.5 | Port Hope | Wind | RCP4.5 | 2030 | 85.7184 | 92.2449 | 99.0957 | 105.9688 | 112.8337
| Port HopeWind2035RCP4.5 | Port Hope | Wind | RCP4.5 | 2035 | 85.7241 | 92.2587 | 99.1188 | 105.9989 | 112.8713
| Port HopeWind2040RCP4.5 | Port Hope | Wind | RCP4.5 | 2040 | 85.7298 | 92.2726 | 99.1419 | 106.0289 | 112.9089
| Port HopeWind2045RCP4.5 | Port Hope | Wind | RCP4.5 | 2045 | 85.7355 | 92.2864 | 99.165 | 106.0589 | 112.9465
| Port HopeWind2050RCP4.5 | Port Hope | Wind | RCP4.5 | 2050 | 85.8609 | 92.453 | 99.3821 | 106.3177 | 113.2482
| Port HopeWind2055RCP4.5 | Port Hope | Wind | RCP4.5 | 2055 | 85.9806 | 92.6058 | 99.5762 | 106.5465 | 113.5123
| Port HopeWind2060RCP4.5 | Port Hope | Wind | RCP4.5 | 2060 | 86.1003 | 92.7587 | 99.7702 | 106.7753 | 113.7764
| Port HopeWind2065RCP4.5 | Port Hope | Wind | RCP4.5 | 2065 | 86.2199 | 92.9115 | 99.9643 | 107.0041 | 114.0405
| Port HopeWind2070RCP4.5 | Port Hope | Wind | RCP4.5 | 2070 | 86.3396 | 93.0644 | 100.1583 | 107.2329 | 114.3046
| Port HopeWind2075RCP4.5 | Port Hope | Wind | RCP4.5 | 2075 | 86.4536 | 93.2132 | 100.3514 | 107.4642 | 114.5755
| Port HopeWind2080RCP4.5 | Port Hope | Wind | RCP4.5 | 2080 | 86.5676 | 93.362 | 100.5444 | 107.6955 | 114.8463
| Port HopeWind2085RCP4.5 | Port Hope | Wind | RCP4.5 | 2085 | 86.6815 | 93.5109 | 100.7375 | 107.9268 | 115.1172
| Port HopeWind2090RCP4.5 | Port Hope | Wind | RCP4.5 | 2090 | 86.7955 | 93.6597 | 100.9305 | 108.1581 | 115.3881
| Port HopeWind2095RCP4.5 | Port Hope | Wind | RCP4.5 | 2095 | 86.9095 | 93.8086 | 101.1236 | 108.3893 | 115.6589
| Port HopeWind2100RCP4.5 | Port Hope | Wind | RCP4.5 | 2100 | 87.0235 | 93.9574 | 101.3166 | 108.6206 | 115.9298
| Port HopeWind2023RCP6.0 | Port Hope | Wind | RCP6.0 | 2023 | 85.707 | 92.2173 | 99.0495 | 105.9088 | 112.7584
| Port HopeWind2025RCP6.0 | Port Hope | Wind | RCP6.0 | 2025 | 85.7127 | 92.2311 | 99.0726 | 105.9388 | 112.796
| Port HopeWind2030RCP6.0 | Port Hope | Wind | RCP6.0 | 2030 | 85.7184 | 92.2449 | 99.0957 | 105.9688 | 112.8337
| Port HopeWind2035RCP6.0 | Port Hope | Wind | RCP6.0 | 2035 | 85.7241 | 92.2587 | 99.1188 | 105.9989 | 112.8713
| Port HopeWind2040RCP6.0 | Port Hope | Wind | RCP6.0 | 2040 | 85.7298 | 92.2726 | 99.1419 | 106.0289 | 112.9089
| Port HopeWind2045RCP6.0 | Port Hope | Wind | RCP6.0 | 2045 | 85.7355 | 92.2864 | 99.165 | 106.0589 | 112.9465
| Port HopeWind2050RCP6.0 | Port Hope | Wind | RCP6.0 | 2050 | 85.8609 | 92.453 | 99.3821 | 106.3177 | 113.2482
| Port HopeWind2055RCP6.0 | Port Hope | Wind | RCP6.0 | 2055 | 85.9806 | 92.6058 | 99.5762 | 106.5465 | 113.5123
| Port HopeWind2060RCP6.0 | Port Hope | Wind | RCP6.0 | 2060 | 86.1003 | 92.7587 | 99.7702 | 106.7753 | 113.7764
| Port HopeWind2065RCP6.0 | Port Hope | Wind | RCP6.0 | 2065 | 86.2199 | 92.9115 | 99.9643 | 107.0041 | 114.0405
| Port HopeWind2070RCP6.0 | Port Hope | Wind | RCP6.0 | 2070 | 86.3396 | 93.0644 | 100.1583 | 107.2329 | 114.3046
| Port HopeWind2075RCP6.0 | Port Hope | Wind | RCP6.0 | 2075 | 86.5106 | 93.2876 | 100.4479 | 107.5799 | 114.7109
| Port HopeWind2080RCP6.0 | Port Hope | Wind | RCP6.0 | 2080 | 86.6815 | 93.5109 | 100.7375 | 107.9268 | 115.1172
| Port HopeWind2085RCP6.0 | Port Hope | Wind | RCP6.0 | 2085 | 86.8525 | 93.7342 | 101.027 | 108.2737 | 115.5235
| Port HopeWind2090RCP6.0 | Port Hope | Wind | RCP6.0 | 2090 | 87.3569 | 94.3718 | 101.8347 | 109.228 | 116.6258
| Port HopeWind2095RCP6.0 | Port Hope | Wind | RCP6.0 | 2095 | 87.6903 | 94.7861 | 102.3528 | 109.8353 | 117.3217
| Port HopeWind2100RCP6.0 | Port Hope | Wind | RCP6.0 | 2100 | 88.0237 | 95.2004 | 102.8709 | 110.4426 | 118.0177
| Port HopeWind2023RCP8.5 | Port Hope | Wind | RCP8.5 | 2023 | 85.707 | 92.2173 | 99.0495 | 105.9088 | 112.7584
| Port HopeWind2025RCP8.5 | Port Hope | Wind | RCP8.5 | 2025 | 85.7184 | 92.2449 | 99.0957 | 105.9688 | 112.8337
| Port HopeWind2030RCP8.5 | Port Hope | Wind | RCP8.5 | 2030 | 85.7298 | 92.2726 | 99.1419 | 106.0289 | 112.9089
| Port HopeWind2035RCP8.5 | Port Hope | Wind | RCP8.5 | 2035 | 85.7412 | 92.3002 | 99.1881 | 106.0889 | 112.9841
| Port HopeWind2040RCP8.5 | Port Hope | Wind | RCP8.5 | 2040 | 85.9407 | 92.5549 | 99.5115 | 106.4702 | 113.4243
| Port HopeWind2045RCP8.5 | Port Hope | Wind | RCP8.5 | 2045 | 86.1401 | 92.8096 | 99.8349 | 106.8516 | 113.8645
| Port HopeWind2050RCP8.5 | Port Hope | Wind | RCP8.5 | 2050 | 86.5676 | 93.362 | 100.5444 | 107.6955 | 114.8463
| Port HopeWind2055RCP8.5 | Port Hope | Wind | RCP8.5 | 2055 | 86.7955 | 93.6597 | 100.9305 | 108.1581 | 115.3881
| Port HopeWind2060RCP8.5 | Port Hope | Wind | RCP8.5 | 2060 | 87.3569 | 94.3718 | 101.8347 | 109.228 | 116.6258
| Port HopeWind2065RCP8.5 | Port Hope | Wind | RCP8.5 | 2065 | 87.6903 | 94.7861 | 102.3528 | 109.8353 | 117.3217
| Port HopeWind2070RCP8.5 | Port Hope | Wind | RCP8.5 | 2070 | 88.0265 | 95.2219 | 102.9138 | 110.4991 | 118.0967
| Port HopeWind2075RCP8.5 | Port Hope | Wind | RCP8.5 | 2075 | 88.0294 | 95.2433 | 102.9567 | 110.5556 | 118.1757
| Port HopeWind2080RCP8.5 | Port Hope | Wind | RCP8.5 | 2080 | 88.0322 | 95.2648 | 102.9996 | 110.6121 | 118.2547
| Port HopeWind2085RCP8.5 | Port Hope | Wind | RCP8.5 | 2085 | 88.2245 | 95.541 | 103.3857 | 111.0941 | 118.8247
| Port HopeWind2090RCP8.5 | Port Hope | Wind | RCP8.5 | 2090 | 88.4169 | 95.8172 | 103.7718 | 111.5761 | 119.3946
| Port HopeWind2095RCP8.5 | Port Hope | Wind | RCP8.5 | 2095 | 88.4169 | 95.8172 | 103.7718 | 111.5761 | 119.3946
| Port HopeWind2100RCP8.5 | Port Hope | Wind | RCP8.5 | 2100 | 88.4169 | 95.8172 | 103.7718 | 111.5761 | 119.3946
| Port PerryIce Accretion2023RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
| Port PerryIce Accretion2025RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
| Port PerryIce Accretion2030RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
| Port PerryIce Accretion2035RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
| Port PerryIce Accretion2040RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
| Port PerryIce Accretion2045RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
| Port PerryIce Accretion2050RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
| Port PerryIce Accretion2055RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
| Port PerryIce Accretion2060RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
| Port PerryIce Accretion2065RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
| Port PerryIce Accretion2070RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
| Port PerryIce Accretion2075RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2075 | 17.2744 | 20.8814 | 25.4167 | 28.8762 | 32.34
| Port PerryIce Accretion2080RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2080 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
| Port PerryIce Accretion2085RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2085 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
| Port PerryIce Accretion2090RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2090 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
| Port PerryIce Accretion2095RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2095 | 17.2048 | 20.9091 | 25.5833 | 29.121 | 32.676
| Port PerryIce Accretion2100RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2100 | 17.1874 | 20.916 | 25.625 | 29.1822 | 32.76
| Port PerryIce Accretion2023RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
| Port PerryIce Accretion2025RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
| Port PerryIce Accretion2030RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
| Port PerryIce Accretion2035RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
| Port PerryIce Accretion2040RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
| Port PerryIce Accretion2045RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
| Port PerryIce Accretion2050RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
| Port PerryIce Accretion2055RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
| Port PerryIce Accretion2060RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
| Port PerryIce Accretion2065RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
| Port PerryIce Accretion2070RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
| Port PerryIce Accretion2075RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2075 | 17.2657 | 20.8849 | 25.4375 | 28.9068 | 32.382
| Port PerryIce Accretion2080RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2080 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
| Port PerryIce Accretion2085RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2085 | 17.2135 | 20.9056 | 25.5625 | 29.0904 | 32.634
| Port PerryIce Accretion2090RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2090 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
| Port PerryIce Accretion2095RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2095 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
| Port PerryIce Accretion2100RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2100 | 16.2654 | 19.8992 | 24.5 | 27.9957 | 31.4685
| Port PerryIce Accretion2023RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
| Port PerryIce Accretion2025RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2025 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
| Port PerryIce Accretion2030RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2030 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
| Port PerryIce Accretion2035RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2035 | 17.6919 | 21.2272 | 25.725 | 29.154 | 32.6025
| Port PerryIce Accretion2040RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2040 | 17.5585 | 21.1097 | 25.6083 | 29.041 | 32.487
| Port PerryIce Accretion2045RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2045 | 17.4251 | 20.9921 | 25.4917 | 28.928 | 32.3715
| Port PerryIce Accretion2050RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2050 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
| Port PerryIce Accretion2055RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2055 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
| Port PerryIce Accretion2060RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2060 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
| Port PerryIce Accretion2065RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2065 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
| Port PerryIce Accretion2070RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2070 | 15.9987 | 19.6226 | 24.2083 | 27.685 | 31.143
| Port PerryIce Accretion2075RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2075 | 15.7319 | 19.3459 | 23.9167 | 27.3742 | 30.8175
| Port PerryIce Accretion2080RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2080 | 15.4652 | 19.0693 | 23.625 | 27.0635 | 30.492
| Port PerryIce Accretion2085RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2085 | 14.8911 | 18.426 | 22.8875 | 26.2584 | 29.6258
| Port PerryIce Accretion2090RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2090 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
| Port PerryIce Accretion2095RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2095 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
| Port PerryIce Accretion2100RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2100 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
| Port PerryWind2023RCP4.5 | Port Perry | Wind | RCP4.5 | 2023 | 76.488 | 82.3883 | 88.5896 | 94.7909 | 101.0022
| Port PerryWind2025RCP4.5 | Port Perry | Wind | RCP4.5 | 2025 | 76.5222 | 82.4333 | 88.6497 | 94.8646 | 101.0874
| Port PerryWind2030RCP4.5 | Port Perry | Wind | RCP4.5 | 2030 | 76.5564 | 82.4784 | 88.7099 | 94.9384 | 101.1727
| Port PerryWind2035RCP4.5 | Port Perry | Wind | RCP4.5 | 2035 | 76.5905 | 82.5234 | 88.77 | 95.0121 | 101.258
| Port PerryWind2040RCP4.5 | Port Perry | Wind | RCP4.5 | 2040 | 76.6247 | 82.5684 | 88.8301 | 95.0859 | 101.3433
| Port PerryWind2045RCP4.5 | Port Perry | Wind | RCP4.5 | 2045 | 76.6589 | 82.6134 | 88.8903 | 95.1597 | 101.4285
| Port PerryWind2050RCP4.5 | Port Perry | Wind | RCP4.5 | 2050 | 76.7615 | 82.7386 | 89.0437 | 95.337 | 101.6302
| Port PerryWind2055RCP4.5 | Port Perry | Wind | RCP4.5 | 2055 | 76.8299 | 82.8188 | 89.137 | 95.4406 | 101.7466
| Port PerryWind2060RCP4.5 | Port Perry | Wind | RCP4.5 | 2060 | 76.8983 | 82.899 | 89.2302 | 95.5442 | 101.8629
| Port PerryWind2065RCP4.5 | Port Perry | Wind | RCP4.5 | 2065 | 76.9667 | 82.9792 | 89.3235 | 95.6477 | 101.9793
| Port PerryWind2070RCP4.5 | Port Perry | Wind | RCP4.5 | 2070 | 77.0351 | 83.0594 | 89.4168 | 95.7513 | 102.0957
| Port PerryWind2075RCP4.5 | Port Perry | Wind | RCP4.5 | 2075 | 77.1098 | 83.1522 | 89.5312 | 95.8863 | 102.2495
| Port PerryWind2080RCP4.5 | Port Perry | Wind | RCP4.5 | 2080 | 77.1845 | 83.2449 | 89.6456 | 96.0212 | 102.4033
| Port PerryWind2085RCP4.5 | Port Perry | Wind | RCP4.5 | 2085 | 77.2592 | 83.3377 | 89.76 | 96.1562 | 102.5571
| Port PerryWind2090RCP4.5 | Port Perry | Wind | RCP4.5 | 2090 | 77.3339 | 83.4304 | 89.8744 | 96.2912 | 102.711
| Port PerryWind2095RCP4.5 | Port Perry | Wind | RCP4.5 | 2095 | 77.4087 | 83.5232 | 89.9888 | 96.4261 | 102.8648
| Port PerryWind2100RCP4.5 | Port Perry | Wind | RCP4.5 | 2100 | 77.4834 | 83.6159 | 90.1032 | 96.5611 | 103.0186
| Port PerryWind2023RCP6.0 | Port Perry | Wind | RCP6.0 | 2023 | 76.488 | 82.3883 | 88.5896 | 94.7909 | 101.0022
| Port PerryWind2025RCP6.0 | Port Perry | Wind | RCP6.0 | 2025 | 76.5222 | 82.4333 | 88.6497 | 94.8646 | 101.0874
| Port PerryWind2030RCP6.0 | Port Perry | Wind | RCP6.0 | 2030 | 76.5564 | 82.4784 | 88.7099 | 94.9384 | 101.1727
| Port PerryWind2035RCP6.0 | Port Perry | Wind | RCP6.0 | 2035 | 76.5905 | 82.5234 | 88.77 | 95.0121 | 101.258
| Port PerryWind2040RCP6.0 | Port Perry | Wind | RCP6.0 | 2040 | 76.6247 | 82.5684 | 88.8301 | 95.0859 | 101.3433
| Port PerryWind2045RCP6.0 | Port Perry | Wind | RCP6.0 | 2045 | 76.6589 | 82.6134 | 88.8903 | 95.1597 | 101.4285
| Port PerryWind2050RCP6.0 | Port Perry | Wind | RCP6.0 | 2050 | 76.7615 | 82.7386 | 89.0437 | 95.337 | 101.6302
| Port PerryWind2055RCP6.0 | Port Perry | Wind | RCP6.0 | 2055 | 76.8299 | 82.8188 | 89.137 | 95.4406 | 101.7466
| Port PerryWind2060RCP6.0 | Port Perry | Wind | RCP6.0 | 2060 | 76.8983 | 82.899 | 89.2302 | 95.5442 | 101.8629
| Port PerryWind2065RCP6.0 | Port Perry | Wind | RCP6.0 | 2065 | 76.9667 | 82.9792 | 89.3235 | 95.6477 | 101.9793
| Port PerryWind2070RCP6.0 | Port Perry | Wind | RCP6.0 | 2070 | 77.0351 | 83.0594 | 89.4168 | 95.7513 | 102.0957
| Port PerryWind2075RCP6.0 | Port Perry | Wind | RCP6.0 | 2075 | 77.1471 | 83.1985 | 89.5884 | 95.9537 | 102.3264
| Port PerryWind2080RCP6.0 | Port Perry | Wind | RCP6.0 | 2080 | 77.2592 | 83.3377 | 89.76 | 96.1562 | 102.5571
| Port PerryWind2085RCP6.0 | Port Perry | Wind | RCP6.0 | 2085 | 77.3713 | 83.4768 | 89.9316 | 96.3586 | 102.7879
| Port PerryWind2090RCP6.0 | Port Perry | Wind | RCP6.0 | 2090 | 77.7291 | 83.8969 | 90.4317 | 96.9252 | 103.4232
| Port PerryWind2095RCP6.0 | Port Perry | Wind | RCP6.0 | 2095 | 77.9748 | 84.1779 | 90.7603 | 97.2893 | 103.8279
| Port PerryWind2100RCP6.0 | Port Perry | Wind | RCP6.0 | 2100 | 78.2205 | 84.4589 | 91.0888 | 97.6533 | 104.2325
| Port PerryWind2023RCP8.5 | Port Perry | Wind | RCP8.5 | 2023 | 76.488 | 82.3883 | 88.5896 | 94.7909 | 101.0022
| Port PerryWind2025RCP8.5 | Port Perry | Wind | RCP8.5 | 2025 | 76.5564 | 82.4784 | 88.7099 | 94.9384 | 101.1727
| Port PerryWind2030RCP8.5 | Port Perry | Wind | RCP8.5 | 2030 | 76.6247 | 82.5684 | 88.8301 | 95.0859 | 101.3433
| Port PerryWind2035RCP8.5 | Port Perry | Wind | RCP8.5 | 2035 | 76.6931 | 82.6584 | 88.9504 | 95.2334 | 101.5138
| Port PerryWind2040RCP8.5 | Port Perry | Wind | RCP8.5 | 2040 | 76.8071 | 82.7921 | 89.1059 | 95.4061 | 101.7078
| Port PerryWind2045RCP8.5 | Port Perry | Wind | RCP8.5 | 2045 | 76.9211 | 82.9257 | 89.2613 | 95.5787 | 101.9017
| Port PerryWind2050RCP8.5 | Port Perry | Wind | RCP8.5 | 2050 | 77.1845 | 83.2449 | 89.6456 | 96.0212 | 102.4033
| Port PerryWind2055RCP8.5 | Port Perry | Wind | RCP8.5 | 2055 | 77.3339 | 83.4304 | 89.8744 | 96.2912 | 102.711
| Port PerryWind2060RCP8.5 | Port Perry | Wind | RCP8.5 | 2060 | 77.7291 | 83.8969 | 90.4317 | 96.9252 | 103.4232
| Port PerryWind2065RCP8.5 | Port Perry | Wind | RCP8.5 | 2065 | 77.9748 | 84.1779 | 90.7603 | 97.2893 | 103.8279
| Port PerryWind2070RCP8.5 | Port Perry | Wind | RCP8.5 | 2070 | 78.3066 | 84.5707 | 91.2267 | 97.8165 | 104.4231
| Port PerryWind2075RCP8.5 | Port Perry | Wind | RCP8.5 | 2075 | 78.3927 | 84.6826 | 91.3645 | 97.9798 | 104.6137
| Port PerryWind2080RCP8.5 | Port Perry | Wind | RCP8.5 | 2080 | 78.4788 | 84.7944 | 91.5024 | 98.143 | 104.8043
| Port PerryWind2085RCP8.5 | Port Perry | Wind | RCP8.5 | 2085 | 78.6802 | 85.0768 | 91.8984 | 98.6279 | 105.3811
| Port PerryWind2090RCP8.5 | Port Perry | Wind | RCP8.5 | 2090 | 78.8815 | 85.3591 | 92.2944 | 99.1128 | 105.958
| Port PerryWind2095RCP8.5 | Port Perry | Wind | RCP8.5 | 2095 | 78.8815 | 85.3591 | 92.2944 | 99.1128 | 105.958
| Port PerryWind2100RCP8.5 | Port Perry | Wind | RCP8.5 | 2100 | 78.8815 | 85.3591 | 92.2944 | 99.1128 | 105.958
| Port StanleyIce Accretion2023RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2023 | 20.5831 | 24.7008 | 29.91 | 33.8661 | 37.8378
| Port StanleyIce Accretion2025RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2025 | 20.4614 | 24.568 | 29.765 | 33.7135 | 37.674
| Port StanleyIce Accretion2030RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2030 | 20.3396 | 24.4352 | 29.62 | 33.561 | 37.5102
| Port StanleyIce Accretion2035RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2035 | 20.2178 | 24.3024 | 29.475 | 33.4085 | 37.3464
| Port StanleyIce Accretion2040RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2040 | 20.096 | 24.1696 | 29.33 | 33.2559 | 37.1826
| Port StanleyIce Accretion2045RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2045 | 19.9743 | 24.0368 | 29.185 | 33.1033 | 37.0188
| Port StanleyIce Accretion2050RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2050 | 19.4642 | 23.4757 | 28.554 | 32.422 | 36.2804
| Port StanleyIce Accretion2055RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2055 | 19.0759 | 23.0474 | 28.068 | 31.8931 | 35.7059
| Port StanleyIce Accretion2060RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2060 | 18.6876 | 22.6192 | 27.582 | 31.3643 | 35.1313
| Port StanleyIce Accretion2065RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2065 | 18.2994 | 22.1909 | 27.096 | 30.8354 | 34.5568
| Port StanleyIce Accretion2070RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2070 | 17.9111 | 21.7626 | 26.61 | 30.3066 | 33.9822
| Port StanleyIce Accretion2075RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2075 | 17.7754 | 21.6257 | 26.47 | 30.1597 | 33.831
| Port StanleyIce Accretion2080RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2080 | 17.6397 | 21.4887 | 26.33 | 30.0128 | 33.6798
| Port StanleyIce Accretion2085RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2085 | 17.504 | 21.3517 | 26.19 | 29.8659 | 33.5286
| Port StanleyIce Accretion2090RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2090 | 17.3683 | 21.2148 | 26.05 | 29.719 | 33.3774
| Port StanleyIce Accretion2095RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2095 | 17.2326 | 21.0778 | 25.91 | 29.5721 | 33.2262
| Port StanleyIce Accretion2100RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2100 | 17.0969 | 20.9409 | 25.77 | 29.4252 | 33.075
| Port StanleyIce Accretion2023RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2023 | 20.5831 | 24.7008 | 29.91 | 33.8661 | 37.8378
| Port StanleyIce Accretion2025RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2025 | 20.4614 | 24.568 | 29.765 | 33.7135 | 37.674
| Port StanleyIce Accretion2030RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2030 | 20.3396 | 24.4352 | 29.62 | 33.561 | 37.5102
| Port StanleyIce Accretion2035RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2035 | 20.2178 | 24.3024 | 29.475 | 33.4085 | 37.3464
| Port StanleyIce Accretion2040RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2040 | 20.096 | 24.1696 | 29.33 | 33.2559 | 37.1826
| Port StanleyIce Accretion2045RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2045 | 19.9743 | 24.0368 | 29.185 | 33.1033 | 37.0188
| Port StanleyIce Accretion2050RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2050 | 19.4642 | 23.4757 | 28.554 | 32.422 | 36.2804
| Port StanleyIce Accretion2055RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2055 | 19.0759 | 23.0474 | 28.068 | 31.8931 | 35.7059
| Port StanleyIce Accretion2060RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2060 | 18.6876 | 22.6192 | 27.582 | 31.3643 | 35.1313
| Port StanleyIce Accretion2065RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2065 | 18.2994 | 22.1909 | 27.096 | 30.8354 | 34.5568
| Port StanleyIce Accretion2070RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2070 | 17.9111 | 21.7626 | 26.61 | 30.3066 | 33.9822
| Port StanleyIce Accretion2075RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2075 | 17.7075 | 21.5572 | 26.4 | 30.0862 | 33.7554
| Port StanleyIce Accretion2080RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2080 | 17.504 | 21.3517 | 26.19 | 29.8659 | 33.5286
| Port StanleyIce Accretion2085RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2085 | 17.3005 | 21.1463 | 25.98 | 29.6456 | 33.3018
| Port StanleyIce Accretion2090RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2090 | 16.6098 | 20.3931 | 25.15 | 28.7472 | 32.3316
| Port StanleyIce Accretion2095RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2095 | 16.1228 | 19.8453 | 24.53 | 28.0692 | 31.5882
| Port StanleyIce Accretion2100RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2100 | 15.6357 | 19.2975 | 23.91 | 27.3912 | 30.8448
| Port StanleyIce Accretion2023RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2023 | 20.5831 | 24.7008 | 29.91 | 33.8661 | 37.8378
| Port StanleyIce Accretion2025RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2025 | 20.3396 | 24.4352 | 29.62 | 33.561 | 37.5102
| Port StanleyIce Accretion2030RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2030 | 20.096 | 24.1696 | 29.33 | 33.2559 | 37.1826
| Port StanleyIce Accretion2035RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2035 | 19.8525 | 23.904 | 29.04 | 32.9508 | 36.855
| Port StanleyIce Accretion2040RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2040 | 19.2054 | 23.1902 | 28.23 | 32.0694 | 35.8974
| Port StanleyIce Accretion2045RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2045 | 18.5582 | 22.4764 | 27.42 | 31.188 | 34.9398
| Port StanleyIce Accretion2050RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2050 | 17.6397 | 21.4887 | 26.33 | 30.0128 | 33.6798
| Port StanleyIce Accretion2055RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2055 | 17.3683 | 21.2148 | 26.05 | 29.719 | 33.3774
| Port StanleyIce Accretion2060RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2060 | 16.6098 | 20.3931 | 25.15 | 28.7472 | 32.3316
| Port StanleyIce Accretion2065RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2065 | 16.1228 | 19.8453 | 24.53 | 28.0692 | 31.5882
| Port StanleyIce Accretion2070RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2070 | 15.3225 | 18.9655 | 23.55 | 26.9957 | 30.429
| Port StanleyIce Accretion2075RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2075 | 15.0094 | 18.6335 | 23.19 | 26.6002 | 30.0132
| Port StanleyIce Accretion2080RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2080 | 14.6963 | 18.3015 | 22.83 | 26.2047 | 29.5974
| Port StanleyIce Accretion2085RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2085 | 13.7673 | 17.2059 | 21.51 | 24.73 | 27.9531
| Port StanleyIce Accretion2090RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2090 | 12.8384 | 16.1103 | 20.19 | 23.2554 | 26.3088
| Port StanleyIce Accretion2095RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2095 | 12.8384 | 16.1103 | 20.19 | 23.2554 | 26.3088
| Port StanleyIce Accretion2100RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2100 | 12.8384 | 16.1103 | 20.19 | 23.2554 | 26.3088
| Port StanleyWind2023RCP4.5 | Port Stanley | Wind | RCP4.5 | 2023 | 87.9269 | 94.8505 | 102.1817 | 109.4749 | 116.775
| Port StanleyWind2025RCP4.5 | Port Stanley | Wind | RCP4.5 | 2025 | 88.0373 | 94.9977 | 102.3753 | 109.7073 | 117.0475
| Port StanleyWind2030RCP4.5 | Port Stanley | Wind | RCP4.5 | 2030 | 88.1478 | 95.1448 | 102.5689 | 109.9396 | 117.32
| Port StanleyWind2035RCP4.5 | Port Stanley | Wind | RCP4.5 | 2035 | 88.2583 | 95.292 | 102.7625 | 110.172 | 117.5925
| Port StanleyWind2040RCP4.5 | Port Stanley | Wind | RCP4.5 | 2040 | 88.3687 | 95.4391 | 102.956 | 110.4043 | 117.865
| Port StanleyWind2045RCP4.5 | Port Stanley | Wind | RCP4.5 | 2045 | 88.4792 | 95.5863 | 103.1496 | 110.6367 | 118.1375
| Port StanleyWind2050RCP4.5 | Port Stanley | Wind | RCP4.5 | 2050 | 88.642 | 95.8067 | 103.4442 | 110.9944 | 118.5597
| Port StanleyWind2055RCP4.5 | Port Stanley | Wind | RCP4.5 | 2055 | 88.6943 | 95.88 | 103.5452 | 111.1197 | 118.7093
| Port StanleyWind2060RCP4.5 | Port Stanley | Wind | RCP4.5 | 2060 | 88.7467 | 95.9533 | 103.6462 | 111.2451 | 118.859
| Port StanleyWind2065RCP4.5 | Port Stanley | Wind | RCP4.5 | 2065 | 88.799 | 96.0265 | 103.7472 | 111.3705 | 119.0087
| Port StanleyWind2070RCP4.5 | Port Stanley | Wind | RCP4.5 | 2070 | 88.8513 | 96.0998 | 103.8482 | 111.4958 | 119.1584
| Port StanleyWind2075RCP4.5 | Port Stanley | Wind | RCP4.5 | 2075 | 89.0054 | 96.3002 | 104.1074 | 111.8038 | 119.5172
| Port StanleyWind2080RCP4.5 | Port Stanley | Wind | RCP4.5 | 2080 | 89.1595 | 96.5006 | 104.3667 | 112.1118 | 119.8761
| Port StanleyWind2085RCP4.5 | Port Stanley | Wind | RCP4.5 | 2085 | 89.3135 | 96.7009 | 104.6259 | 112.4198 | 120.2349
| Port StanleyWind2090RCP4.5 | Port Stanley | Wind | RCP4.5 | 2090 | 89.4676 | 96.9013 | 104.8851 | 112.7278 | 120.5938
| Port StanleyWind2095RCP4.5 | Port Stanley | Wind | RCP4.5 | 2095 | 89.6217 | 97.1017 | 105.1444 | 113.0358 | 120.9527
| Port StanleyWind2100RCP4.5 | Port Stanley | Wind | RCP4.5 | 2100 | 89.7757 | 97.3021 | 105.4036 | 113.3438 | 121.3115
| Port StanleyWind2023RCP6.0 | Port Stanley | Wind | RCP6.0 | 2023 | 87.9269 | 94.8505 | 102.1817 | 109.4749 | 116.775
| Port StanleyWind2025RCP6.0 | Port Stanley | Wind | RCP6.0 | 2025 | 88.0373 | 94.9977 | 102.3753 | 109.7073 | 117.0475
| Port StanleyWind2030RCP6.0 | Port Stanley | Wind | RCP6.0 | 2030 | 88.1478 | 95.1448 | 102.5689 | 109.9396 | 117.32
| Port StanleyWind2035RCP6.0 | Port Stanley | Wind | RCP6.0 | 2035 | 88.2583 | 95.292 | 102.7625 | 110.172 | 117.5925
| Port StanleyWind2040RCP6.0 | Port Stanley | Wind | RCP6.0 | 2040 | 88.3687 | 95.4391 | 102.956 | 110.4043 | 117.865
| Port StanleyWind2045RCP6.0 | Port Stanley | Wind | RCP6.0 | 2045 | 88.4792 | 95.5863 | 103.1496 | 110.6367 | 118.1375
| Port StanleyWind2050RCP6.0 | Port Stanley | Wind | RCP6.0 | 2050 | 88.642 | 95.8067 | 103.4442 | 110.9944 | 118.5597
| Port StanleyWind2055RCP6.0 | Port Stanley | Wind | RCP6.0 | 2055 | 88.6943 | 95.88 | 103.5452 | 111.1197 | 118.7093
| Port StanleyWind2060RCP6.0 | Port Stanley | Wind | RCP6.0 | 2060 | 88.7467 | 95.9533 | 103.6462 | 111.2451 | 118.859
| Port StanleyWind2065RCP6.0 | Port Stanley | Wind | RCP6.0 | 2065 | 88.799 | 96.0265 | 103.7472 | 111.3705 | 119.0087
| Port StanleyWind2070RCP6.0 | Port Stanley | Wind | RCP6.0 | 2070 | 88.8513 | 96.0998 | 103.8482 | 111.4958 | 119.1584
| Port StanleyWind2075RCP6.0 | Port Stanley | Wind | RCP6.0 | 2075 | 89.0824 | 96.4004 | 104.2371 | 111.9578 | 119.6967
| Port StanleyWind2080RCP6.0 | Port Stanley | Wind | RCP6.0 | 2080 | 89.3135 | 96.7009 | 104.6259 | 112.4198 | 120.2349
| Port StanleyWind2085RCP6.0 | Port Stanley | Wind | RCP6.0 | 2085 | 89.5446 | 97.0015 | 105.0148 | 112.8818 | 120.7732
| Port StanleyWind2090RCP6.0 | Port Stanley | Wind | RCP6.0 | 2090 | 90.1566 | 97.7874 | 106.013 | 114.0607 | 122.1405
| Port StanleyWind2095RCP6.0 | Port Stanley | Wind | RCP6.0 | 2095 | 90.5374 | 98.2727 | 106.6223 | 114.7775 | 122.9695
| Port StanleyWind2100RCP6.0 | Port Stanley | Wind | RCP6.0 | 2100 | 90.9182 | 98.758 | 107.2317 | 115.4944 | 123.7985
| Port StanleyWind2023RCP8.5 | Port Stanley | Wind | RCP8.5 | 2023 | 87.9269 | 94.8505 | 102.1817 | 109.4749 | 116.775
| Port StanleyWind2025RCP8.5 | Port Stanley | Wind | RCP8.5 | 2025 | 88.1478 | 95.1448 | 102.5689 | 109.9396 | 117.32
| Port StanleyWind2030RCP8.5 | Port Stanley | Wind | RCP8.5 | 2030 | 88.3687 | 95.4391 | 102.956 | 110.4043 | 117.865
| Port StanleyWind2035RCP8.5 | Port Stanley | Wind | RCP8.5 | 2035 | 88.5897 | 95.7335 | 103.3432 | 110.869 | 118.41
| Port StanleyWind2040RCP8.5 | Port Stanley | Wind | RCP8.5 | 2040 | 88.6769 | 95.8556 | 103.5115 | 111.0779 | 118.6594
| Port StanleyWind2045RCP8.5 | Port Stanley | Wind | RCP8.5 | 2045 | 88.7641 | 95.9777 | 103.6799 | 111.2869 | 118.9089
| Port StanleyWind2050RCP8.5 | Port Stanley | Wind | RCP8.5 | 2050 | 89.1595 | 96.5006 | 104.3667 | 112.1118 | 119.8761
| Port StanleyWind2055RCP8.5 | Port Stanley | Wind | RCP8.5 | 2055 | 89.4676 | 96.9013 | 104.8851 | 112.7278 | 120.5938
| Port StanleyWind2060RCP8.5 | Port Stanley | Wind | RCP8.5 | 2060 | 90.1566 | 97.7874 | 106.013 | 114.0607 | 122.1405
| Port StanleyWind2065RCP8.5 | Port Stanley | Wind | RCP8.5 | 2065 | 90.5374 | 98.2727 | 106.6223 | 114.7775 | 122.9695
| Port StanleyWind2070RCP8.5 | Port Stanley | Wind | RCP8.5 | 2070 | 91.1537 | 99.0523 | 107.6054 | 115.9375 | 124.309
| Port StanleyWind2075RCP8.5 | Port Stanley | Wind | RCP8.5 | 2075 | 91.3892 | 99.3466 | 107.9791 | 116.3806 | 124.8194
| Port StanleyWind2080RCP8.5 | Port Stanley | Wind | RCP8.5 | 2080 | 91.6246 | 99.6409 | 108.3528 | 116.8237 | 125.3299
| Port StanleyWind2085RCP8.5 | Port Stanley | Wind | RCP8.5 | 2085 | 92.0258 | 100.1716 | 109.0497 | 117.6558 | 126.3086
| Port StanleyWind2090RCP8.5 | Port Stanley | Wind | RCP8.5 | 2090 | 92.427 | 100.7024 | 109.7466 | 118.4879 | 127.2873
| Port StanleyWind2095RCP8.5 | Port Stanley | Wind | RCP8.5 | 2095 | 92.427 | 100.7024 | 109.7466 | 118.4879 | 127.2873
| Port StanleyWind2100RCP8.5 | Port Stanley | Wind | RCP8.5 | 2100 | 92.427 | 100.7024 | 109.7466 | 118.4879 | 127.2873
| PrescottIce Accretion2023RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2023 | 20.6249 | 24.5763 | 29.61 | 33.4593 | 37.3086
| PrescottIce Accretion2025RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2025 | 20.6945 | 24.6801 | 29.755 | 33.6345 | 37.5102
| PrescottIce Accretion2030RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2030 | 20.764 | 24.7838 | 29.9 | 33.8096 | 37.7118
| PrescottIce Accretion2035RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2035 | 20.8336 | 24.8875 | 30.045 | 33.9847 | 37.9134
| PrescottIce Accretion2040RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2040 | 20.9032 | 24.9913 | 30.19 | 34.1599 | 38.115
| PrescottIce Accretion2045RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2045 | 20.9728 | 25.0951 | 30.335 | 34.335 | 38.3166
| PrescottIce Accretion2050RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2050 | 20.9046 | 25.0544 | 30.318 | 34.3339 | 38.3368
| PrescottIce Accretion2055RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2055 | 20.7668 | 24.91 | 30.156 | 34.1576 | 38.1553
| PrescottIce Accretion2060RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2060 | 20.6291 | 24.7655 | 29.994 | 33.9814 | 37.9739
| PrescottIce Accretion2065RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2065 | 20.4913 | 24.6211 | 29.832 | 33.8051 | 37.7924
| PrescottIce Accretion2070RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2070 | 20.3535 | 24.4767 | 29.67 | 33.6288 | 37.611
| PrescottIce Accretion2075RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2075 | 20.4231 | 24.5846 | 29.825 | 33.8209 | 37.8378
| PrescottIce Accretion2080RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2080 | 20.4927 | 24.6925 | 29.98 | 34.013 | 38.0646
| PrescottIce Accretion2085RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2085 | 20.5623 | 24.8004 | 30.135 | 34.2051 | 38.2914
| PrescottIce Accretion2090RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2090 | 20.6318 | 24.9083 | 30.29 | 34.3972 | 38.5182
| PrescottIce Accretion2095RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2095 | 20.7014 | 25.0162 | 30.445 | 34.5893 | 38.745
| PrescottIce Accretion2100RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2100 | 20.771 | 25.1241 | 30.6 | 34.7814 | 38.9718
| PrescottIce Accretion2023RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2023 | 20.6249 | 24.5763 | 29.61 | 33.4593 | 37.3086
| PrescottIce Accretion2025RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2025 | 20.6945 | 24.6801 | 29.755 | 33.6345 | 37.5102
| PrescottIce Accretion2030RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2030 | 20.764 | 24.7838 | 29.9 | 33.8096 | 37.7118
| PrescottIce Accretion2035RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2035 | 20.8336 | 24.8875 | 30.045 | 33.9847 | 37.9134
| PrescottIce Accretion2040RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2040 | 20.9032 | 24.9913 | 30.19 | 34.1599 | 38.115
| PrescottIce Accretion2045RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2045 | 20.9728 | 25.0951 | 30.335 | 34.335 | 38.3166
| PrescottIce Accretion2050RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2050 | 20.9046 | 25.0544 | 30.318 | 34.3339 | 38.3368
| PrescottIce Accretion2055RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2055 | 20.7668 | 24.91 | 30.156 | 34.1576 | 38.1553
| PrescottIce Accretion2060RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2060 | 20.6291 | 24.7655 | 29.994 | 33.9814 | 37.9739
| PrescottIce Accretion2065RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2065 | 20.4913 | 24.6211 | 29.832 | 33.8051 | 37.7924
| PrescottIce Accretion2070RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2070 | 20.3535 | 24.4767 | 29.67 | 33.6288 | 37.611
| PrescottIce Accretion2075RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2075 | 20.4579 | 24.6385 | 29.9025 | 33.9169 | 37.9512
| PrescottIce Accretion2080RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2080 | 20.5623 | 24.8004 | 30.135 | 34.2051 | 38.2914
| PrescottIce Accretion2085RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2085 | 20.6666 | 24.9622 | 30.3675 | 34.4932 | 38.6316
| PrescottIce Accretion2090RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2090 | 20.6249 | 24.9913 | 30.49 | 34.6797 | 38.8836
| PrescottIce Accretion2095RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2095 | 20.4788 | 24.8585 | 30.38 | 34.578 | 38.7954
| PrescottIce Accretion2100RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2100 | 20.3326 | 24.7257 | 30.27 | 34.4763 | 38.7072
| PrescottIce Accretion2023RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2023 | 20.6249 | 24.5763 | 29.61 | 33.4593 | 37.3086
| PrescottIce Accretion2025RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2025 | 20.764 | 24.7838 | 29.9 | 33.8096 | 37.7118
| PrescottIce Accretion2030RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2030 | 20.9032 | 24.9913 | 30.19 | 34.1599 | 38.115
| PrescottIce Accretion2035RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2035 | 21.0424 | 25.1988 | 30.48 | 34.5102 | 38.5182
| PrescottIce Accretion2040RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2040 | 20.8128 | 24.9581 | 30.21 | 34.2164 | 38.2158
| PrescottIce Accretion2045RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2045 | 20.5831 | 24.7174 | 29.94 | 33.9226 | 37.9134
| PrescottIce Accretion2050RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2050 | 20.4927 | 24.6925 | 29.98 | 34.013 | 38.0646
| PrescottIce Accretion2055RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2055 | 20.6318 | 24.9083 | 30.29 | 34.3972 | 38.5182
| PrescottIce Accretion2060RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2060 | 20.6249 | 24.9913 | 30.49 | 34.6797 | 38.8836
| PrescottIce Accretion2065RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2065 | 20.4788 | 24.8585 | 30.38 | 34.578 | 38.7954
| PrescottIce Accretion2070RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2070 | 20.0473 | 24.4103 | 29.91 | 34.0808 | 38.2662
| PrescottIce Accretion2075RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2075 | 19.762 | 24.0949 | 29.55 | 33.6853 | 37.8252
| PrescottIce Accretion2080RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2080 | 19.4767 | 23.7795 | 29.19 | 33.2898 | 37.3842
| PrescottIce Accretion2085RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2085 | 18.7148 | 22.8831 | 28.14 | 32.1202 | 36.0801
| PrescottIce Accretion2090RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2090 | 17.9528 | 21.9867 | 27.09 | 30.9507 | 34.776
| PrescottIce Accretion2095RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2095 | 17.9528 | 21.9867 | 27.09 | 30.9507 | 34.776
| PrescottIce Accretion2100RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2100 | 17.9528 | 21.9867 | 27.09 | 30.9507 | 34.776
| PrescottWind2023RCP4.5 | Prescott | Wind | RCP4.5 | 2023 | 81.0025 | 87.3376 | 94.0323 | 100.7041 | 107.3771
| PrescottWind2025RCP4.5 | Prescott | Wind | RCP4.5 | 2025 | 81.0065 | 87.3333 | 94.0153 | 100.6759 | 107.3399
| PrescottWind2030RCP4.5 | Prescott | Wind | RCP4.5 | 2030 | 81.0105 | 87.329 | 93.9982 | 100.6477 | 107.3028
| PrescottWind2035RCP4.5 | Prescott | Wind | RCP4.5 | 2035 | 81.0146 | 87.3246 | 93.9812 | 100.6195 | 107.2657
| PrescottWind2040RCP4.5 | Prescott | Wind | RCP4.5 | 2040 | 81.0186 | 87.3203 | 93.9641 | 100.5913 | 107.2286
| PrescottWind2045RCP4.5 | Prescott | Wind | RCP4.5 | 2045 | 81.0226 | 87.316 | 93.9471 | 100.5631 | 107.1915
| PrescottWind2050RCP4.5 | Prescott | Wind | RCP4.5 | 2050 | 80.9447 | 87.1871 | 93.7514 | 100.314 | 106.8851
| PrescottWind2055RCP4.5 | Prescott | Wind | RCP4.5 | 2055 | 80.8628 | 87.0626 | 93.5729 | 100.0931 | 106.6158
| PrescottWind2060RCP4.5 | Prescott | Wind | RCP4.5 | 2060 | 80.7809 | 86.938 | 93.3943 | 99.8722 | 106.3465
| PrescottWind2065RCP4.5 | Prescott | Wind | RCP4.5 | 2065 | 80.699 | 86.8135 | 93.2158 | 99.6513 | 106.0773
| PrescottWind2070RCP4.5 | Prescott | Wind | RCP4.5 | 2070 | 80.6171 | 86.6889 | 93.0372 | 99.4304 | 105.808
| PrescottWind2075RCP4.5 | Prescott | Wind | RCP4.5 | 2075 | 80.5836 | 86.6457 | 92.9845 | 99.369 | 105.739
| PrescottWind2080RCP4.5 | Prescott | Wind | RCP4.5 | 2080 | 80.5501 | 86.6024 | 92.9318 | 99.3077 | 105.6701
| PrescottWind2085RCP4.5 | Prescott | Wind | RCP4.5 | 2085 | 80.5167 | 86.5592 | 92.8791 | 99.2463 | 105.6012
| PrescottWind2090RCP4.5 | Prescott | Wind | RCP4.5 | 2090 | 80.4832 | 86.5159 | 92.8264 | 99.1849 | 105.5323
| PrescottWind2095RCP4.5 | Prescott | Wind | RCP4.5 | 2095 | 80.4498 | 86.4727 | 92.7737 | 99.1236 | 105.4634
| PrescottWind2100RCP4.5 | Prescott | Wind | RCP4.5 | 2100 | 80.4163 | 86.4295 | 92.721 | 99.0622 | 105.3945
| PrescottWind2023RCP6.0 | Prescott | Wind | RCP6.0 | 2023 | 81.0025 | 87.3376 | 94.0323 | 100.7041 | 107.3771
| PrescottWind2025RCP6.0 | Prescott | Wind | RCP6.0 | 2025 | 81.0065 | 87.3333 | 94.0153 | 100.6759 | 107.3399
| PrescottWind2030RCP6.0 | Prescott | Wind | RCP6.0 | 2030 | 81.0105 | 87.329 | 93.9982 | 100.6477 | 107.3028
| PrescottWind2035RCP6.0 | Prescott | Wind | RCP6.0 | 2035 | 81.0146 | 87.3246 | 93.9812 | 100.6195 | 107.2657
| PrescottWind2040RCP6.0 | Prescott | Wind | RCP6.0 | 2040 | 81.0186 | 87.3203 | 93.9641 | 100.5913 | 107.2286
| PrescottWind2045RCP6.0 | Prescott | Wind | RCP6.0 | 2045 | 81.0226 | 87.316 | 93.9471 | 100.5631 | 107.1915
| PrescottWind2050RCP6.0 | Prescott | Wind | RCP6.0 | 2050 | 80.9447 | 87.1871 | 93.7514 | 100.314 | 106.8851
| PrescottWind2055RCP6.0 | Prescott | Wind | RCP6.0 | 2055 | 80.8628 | 87.0626 | 93.5729 | 100.0931 | 106.6158
| PrescottWind2060RCP6.0 | Prescott | Wind | RCP6.0 | 2060 | 80.7809 | 86.938 | 93.3943 | 99.8722 | 106.3465
| PrescottWind2065RCP6.0 | Prescott | Wind | RCP6.0 | 2065 | 80.699 | 86.8135 | 93.2158 | 99.6513 | 106.0773
| PrescottWind2070RCP6.0 | Prescott | Wind | RCP6.0 | 2070 | 80.6171 | 86.6889 | 93.0372 | 99.4304 | 105.808
| PrescottWind2075RCP6.0 | Prescott | Wind | RCP6.0 | 2075 | 80.5669 | 86.6241 | 92.9582 | 99.3383 | 105.7046
| PrescottWind2080RCP6.0 | Prescott | Wind | RCP6.0 | 2080 | 80.5167 | 86.5592 | 92.8791 | 99.2463 | 105.6012
| PrescottWind2085RCP6.0 | Prescott | Wind | RCP6.0 | 2085 | 80.4665 | 86.4943 | 92.8 | 99.1543 | 105.4979
| PrescottWind2090RCP6.0 | Prescott | Wind | RCP6.0 | 2090 | 80.3467 | 86.3343 | 92.5877 | 98.8964 | 105.193
| PrescottWind2095RCP6.0 | Prescott | Wind | RCP6.0 | 2095 | 80.2771 | 86.2392 | 92.4544 | 98.7305 | 104.9916
| PrescottWind2100RCP6.0 | Prescott | Wind | RCP6.0 | 2100 | 80.2075 | 86.144 | 92.3211 | 98.5647 | 104.7902
| PrescottWind2023RCP8.5 | Prescott | Wind | RCP8.5 | 2023 | 81.0025 | 87.3376 | 94.0323 | 100.7041 | 107.3771
| PrescottWind2025RCP8.5 | Prescott | Wind | RCP8.5 | 2025 | 81.0105 | 87.329 | 93.9982 | 100.6477 | 107.3028
| PrescottWind2030RCP8.5 | Prescott | Wind | RCP8.5 | 2030 | 81.0186 | 87.3203 | 93.9641 | 100.5913 | 107.2286
| PrescottWind2035RCP8.5 | Prescott | Wind | RCP8.5 | 2035 | 81.0266 | 87.3117 | 93.93 | 100.535 | 107.1544
| PrescottWind2040RCP8.5 | Prescott | Wind | RCP8.5 | 2040 | 80.8901 | 87.1041 | 93.6324 | 100.1668 | 106.7056
| PrescottWind2045RCP8.5 | Prescott | Wind | RCP8.5 | 2045 | 80.7536 | 86.8965 | 93.3348 | 99.7986 | 106.2568
| PrescottWind2050RCP8.5 | Prescott | Wind | RCP8.5 | 2050 | 80.5501 | 86.6024 | 92.9318 | 99.3077 | 105.6701
| PrescottWind2055RCP8.5 | Prescott | Wind | RCP8.5 | 2055 | 80.4832 | 86.5159 | 92.8264 | 99.1849 | 105.5323
| PrescottWind2060RCP8.5 | Prescott | Wind | RCP8.5 | 2060 | 80.3467 | 86.3343 | 92.5877 | 98.8964 | 105.193
| PrescottWind2065RCP8.5 | Prescott | Wind | RCP8.5 | 2065 | 80.2771 | 86.2392 | 92.4544 | 98.7305 | 104.9916
| PrescottWind2070RCP8.5 | Prescott | Wind | RCP8.5 | 2070 | 80.336 | 86.3141 | 92.5443 | 98.8333 | 105.1118
| PrescottWind2075RCP8.5 | Prescott | Wind | RCP8.5 | 2075 | 80.4645 | 86.4842 | 92.7675 | 99.102 | 105.4334
| PrescottWind2080RCP8.5 | Prescott | Wind | RCP8.5 | 2080 | 80.593 | 86.6543 | 92.9907 | 99.3707 | 105.755
| PrescottWind2085RCP8.5 | Prescott | Wind | RCP8.5 | 2085 | 80.5769 | 86.6543 | 93.0093 | 99.4055 | 105.8027
| PrescottWind2090RCP8.5 | Prescott | Wind | RCP8.5 | 2090 | 80.5608 | 86.6543 | 93.0279 | 99.4403 | 105.8504
| PrescottWind2095RCP8.5 | Prescott | Wind | RCP8.5 | 2095 | 80.5608 | 86.6543 | 93.0279 | 99.4403 | 105.8504
| PrescottWind2100RCP8.5 | Prescott | Wind | RCP8.5 | 2100 | 80.5608 | 86.6543 | 93.0279 | 99.4403 | 105.8504
| PrincetonIce Accretion2023RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
| PrincetonIce Accretion2025RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2025 | 20.3952 | 24.4642 | 29.605 | 33.5328 | 37.4661
| PrincetonIce Accretion2030RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2030 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
| PrincetonIce Accretion2035RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2035 | 20.3117 | 24.3895 | 29.535 | 33.4763 | 37.4031
| PrincetonIce Accretion2040RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2040 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
| PrincetonIce Accretion2045RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2045 | 20.2282 | 24.3148 | 29.465 | 33.4198 | 37.3401
| PrincetonIce Accretion2050RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2050 | 20.0571 | 24.153 | 29.316 | 33.2762 | 37.2028
| PrincetonIce Accretion2055RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2055 | 19.9276 | 24.0285 | 29.202 | 33.161 | 37.0969
| PrincetonIce Accretion2060RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2060 | 19.7982 | 23.904 | 29.088 | 33.0457 | 36.9911
| PrincetonIce Accretion2065RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2065 | 19.6688 | 23.7795 | 28.974 | 32.9305 | 36.8852
| PrincetonIce Accretion2070RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2070 | 19.5394 | 23.655 | 28.86 | 32.8152 | 36.7794
| PrincetonIce Accretion2075RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2075 | 19.4837 | 23.6135 | 28.84 | 32.8095 | 36.7857
| PrincetonIce Accretion2080RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2080 | 19.428 | 23.572 | 28.82 | 32.8039 | 36.792
| PrincetonIce Accretion2085RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2085 | 19.3724 | 23.5305 | 28.8 | 32.7982 | 36.7983
| PrincetonIce Accretion2090RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2090 | 19.3167 | 23.489 | 28.78 | 32.7926 | 36.8046
| PrincetonIce Accretion2095RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2095 | 19.261 | 23.4475 | 28.76 | 32.7869 | 36.8109
| PrincetonIce Accretion2100RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2100 | 19.2054 | 23.406 | 28.74 | 32.7813 | 36.8172
| PrincetonIce Accretion2023RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
| PrincetonIce Accretion2025RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2025 | 20.3952 | 24.4642 | 29.605 | 33.5328 | 37.4661
| PrincetonIce Accretion2030RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2030 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
| PrincetonIce Accretion2035RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2035 | 20.3117 | 24.3895 | 29.535 | 33.4763 | 37.4031
| PrincetonIce Accretion2040RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2040 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
| PrincetonIce Accretion2045RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2045 | 20.2282 | 24.3148 | 29.465 | 33.4198 | 37.3401
| PrincetonIce Accretion2050RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2050 | 20.0571 | 24.153 | 29.316 | 33.2762 | 37.2028
| PrincetonIce Accretion2055RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2055 | 19.9276 | 24.0285 | 29.202 | 33.161 | 37.0969
| PrincetonIce Accretion2060RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2060 | 19.7982 | 23.904 | 29.088 | 33.0457 | 36.9911
| PrincetonIce Accretion2065RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2065 | 19.6688 | 23.7795 | 28.974 | 32.9305 | 36.8852
| PrincetonIce Accretion2070RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2070 | 19.5394 | 23.655 | 28.86 | 32.8152 | 36.7794
| PrincetonIce Accretion2075RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2075 | 19.4559 | 23.5927 | 28.83 | 32.8067 | 36.7888
| PrincetonIce Accretion2080RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2080 | 19.3724 | 23.5305 | 28.8 | 32.7982 | 36.7983
| PrincetonIce Accretion2085RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2085 | 19.2889 | 23.4682 | 28.77 | 32.7898 | 36.8077
| PrincetonIce Accretion2090RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2090 | 18.7739 | 22.9412 | 28.21 | 32.2163 | 36.1998
| PrincetonIce Accretion2095RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2095 | 18.3425 | 22.4764 | 27.68 | 31.6513 | 35.5824
| PrincetonIce Accretion2100RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2100 | 17.9111 | 22.0116 | 27.15 | 31.0863 | 34.965
| PrincetonIce Accretion2023RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
| PrincetonIce Accretion2025RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2025 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
| PrincetonIce Accretion2030RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2030 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
| PrincetonIce Accretion2035RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2035 | 20.1865 | 24.2775 | 29.43 | 33.3915 | 37.3086
| PrincetonIce Accretion2040RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2040 | 19.9708 | 24.07 | 29.24 | 33.1994 | 37.1322
| PrincetonIce Accretion2045RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2045 | 19.7551 | 23.8625 | 29.05 | 33.0073 | 36.9558
| PrincetonIce Accretion2050RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2050 | 19.428 | 23.572 | 28.82 | 32.8039 | 36.792
| PrincetonIce Accretion2055RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2055 | 19.3167 | 23.489 | 28.78 | 32.7926 | 36.8046
| PrincetonIce Accretion2060RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2060 | 18.7739 | 22.9412 | 28.21 | 32.2163 | 36.1998
| PrincetonIce Accretion2065RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2065 | 18.3425 | 22.4764 | 27.68 | 31.6513 | 35.5824
| PrincetonIce Accretion2070RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2070 | 17.5353 | 21.6049 | 26.71 | 30.6117 | 34.461
| PrincetonIce Accretion2075RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2075 | 17.1596 | 21.1982 | 26.27 | 30.1371 | 33.957
| PrincetonIce Accretion2080RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2080 | 16.7838 | 20.7915 | 25.83 | 29.6625 | 33.453
| PrincetonIce Accretion2085RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2085 | 15.8549 | 19.7208 | 24.57 | 28.2387 | 31.9032
| PrincetonIce Accretion2090RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2090 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
| PrincetonIce Accretion2095RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2095 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
| PrincetonIce Accretion2100RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2100 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
| PrincetonWind2023RCP4.5 | Princeton | Wind | RCP4.5 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
| PrincetonWind2025RCP4.5 | Princeton | Wind | RCP4.5 | 2025 | 87.206 | 94.102 | 101.4083 | 108.6746 | 115.9494
| PrincetonWind2030RCP4.5 | Princeton | Wind | RCP4.5 | 2030 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
| PrincetonWind2035RCP4.5 | Princeton | Wind | RCP4.5 | 2035 | 87.3672 | 94.316 | 101.685 | 109.0063 | 116.337
| PrincetonWind2040RCP4.5 | Princeton | Wind | RCP4.5 | 2040 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
| PrincetonWind2045RCP4.5 | Princeton | Wind | RCP4.5 | 2045 | 87.5283 | 94.5299 | 101.9617 | 109.338 | 116.7246
| PrincetonWind2050RCP4.5 | Princeton | Wind | RCP4.5 | 2050 | 87.678 | 94.7205 | 102.206 | 109.6258 | 117.0575
| PrincetonWind2055RCP4.5 | Princeton | Wind | RCP4.5 | 2055 | 87.7471 | 94.8042 | 102.312 | 109.7478 | 117.1966
| PrincetonWind2060RCP4.5 | Princeton | Wind | RCP4.5 | 2060 | 87.8162 | 94.8879 | 102.418 | 109.8697 | 117.3356
| PrincetonWind2065RCP4.5 | Princeton | Wind | RCP4.5 | 2065 | 87.8852 | 94.9716 | 102.524 | 109.9917 | 117.4747
| PrincetonWind2070RCP4.5 | Princeton | Wind | RCP4.5 | 2070 | 87.9543 | 95.0553 | 102.63 | 110.1137 | 117.6138
| PrincetonWind2075RCP4.5 | Princeton | Wind | RCP4.5 | 2075 | 88.0407 | 95.1746 | 102.7917 | 110.3117 | 117.8494
| PrincetonWind2080RCP4.5 | Princeton | Wind | RCP4.5 | 2080 | 88.127 | 95.294 | 102.9533 | 110.5096 | 118.085
| PrincetonWind2085RCP4.5 | Princeton | Wind | RCP4.5 | 2085 | 88.2134 | 95.4134 | 103.115 | 110.7075 | 118.3206
| PrincetonWind2090RCP4.5 | Princeton | Wind | RCP4.5 | 2090 | 88.2997 | 95.5327 | 103.2767 | 110.9055 | 118.5562
| PrincetonWind2095RCP4.5 | Princeton | Wind | RCP4.5 | 2095 | 88.3861 | 95.6521 | 103.4383 | 111.1034 | 118.7918
| PrincetonWind2100RCP4.5 | Princeton | Wind | RCP4.5 | 2100 | 88.4724 | 95.7714 | 103.6 | 111.3014 | 119.0274
| PrincetonWind2023RCP6.0 | Princeton | Wind | RCP6.0 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
| PrincetonWind2025RCP6.0 | Princeton | Wind | RCP6.0 | 2025 | 87.206 | 94.102 | 101.4083 | 108.6746 | 115.9494
| PrincetonWind2030RCP6.0 | Princeton | Wind | RCP6.0 | 2030 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
| PrincetonWind2035RCP6.0 | Princeton | Wind | RCP6.0 | 2035 | 87.3672 | 94.316 | 101.685 | 109.0063 | 116.337
| PrincetonWind2040RCP6.0 | Princeton | Wind | RCP6.0 | 2040 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
| PrincetonWind2045RCP6.0 | Princeton | Wind | RCP6.0 | 2045 | 87.5283 | 94.5299 | 101.9617 | 109.338 | 116.7246
| PrincetonWind2050RCP6.0 | Princeton | Wind | RCP6.0 | 2050 | 87.678 | 94.7205 | 102.206 | 109.6258 | 117.0575
| PrincetonWind2055RCP6.0 | Princeton | Wind | RCP6.0 | 2055 | 87.7471 | 94.8042 | 102.312 | 109.7478 | 117.1966
| PrincetonWind2060RCP6.0 | Princeton | Wind | RCP6.0 | 2060 | 87.8162 | 94.8879 | 102.418 | 109.8697 | 117.3356
| PrincetonWind2065RCP6.0 | Princeton | Wind | RCP6.0 | 2065 | 87.8852 | 94.9716 | 102.524 | 109.9917 | 117.4747
| PrincetonWind2070RCP6.0 | Princeton | Wind | RCP6.0 | 2070 | 87.9543 | 95.0553 | 102.63 | 110.1137 | 117.6138
| PrincetonWind2075RCP6.0 | Princeton | Wind | RCP6.0 | 2075 | 88.0838 | 95.2343 | 102.8725 | 110.4106 | 117.9672
| PrincetonWind2080RCP6.0 | Princeton | Wind | RCP6.0 | 2080 | 88.2134 | 95.4134 | 103.115 | 110.7075 | 118.3206
| PrincetonWind2085RCP6.0 | Princeton | Wind | RCP6.0 | 2085 | 88.3429 | 95.5924 | 103.3575 | 111.0045 | 118.674
| PrincetonWind2090RCP6.0 | Princeton | Wind | RCP6.0 | 2090 | 88.8264 | 96.2271 | 104.18 | 111.9862 | 119.8216
| PrincetonWind2095RCP6.0 | Princeton | Wind | RCP6.0 | 2095 | 89.1805 | 96.6828 | 104.76 | 112.671 | 120.6158
| PrincetonWind2100RCP6.0 | Princeton | Wind | RCP6.0 | 2100 | 89.5345 | 97.1385 | 105.34 | 113.3558 | 121.41
| PrincetonWind2023RCP8.5 | Princeton | Wind | RCP8.5 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
| PrincetonWind2025RCP8.5 | Princeton | Wind | RCP8.5 | 2025 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
| PrincetonWind2030RCP8.5 | Princeton | Wind | RCP8.5 | 2030 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
| PrincetonWind2035RCP8.5 | Princeton | Wind | RCP8.5 | 2035 | 87.6089 | 94.6368 | 102.1 | 109.5038 | 116.9184
| PrincetonWind2040RCP8.5 | Princeton | Wind | RCP8.5 | 2040 | 87.7241 | 94.7763 | 102.2767 | 109.7071 | 117.1502
| PrincetonWind2045RCP8.5 | Princeton | Wind | RCP8.5 | 2045 | 87.8392 | 94.9158 | 102.4533 | 109.9104 | 117.382
| PrincetonWind2050RCP8.5 | Princeton | Wind | RCP8.5 | 2050 | 88.127 | 95.294 | 102.9533 | 110.5096 | 118.085
| PrincetonWind2055RCP8.5 | Princeton | Wind | RCP8.5 | 2055 | 88.2997 | 95.5327 | 103.2767 | 110.9055 | 118.5562
| PrincetonWind2060RCP8.5 | Princeton | Wind | RCP8.5 | 2060 | 88.8264 | 96.2271 | 104.18 | 111.9862 | 119.8216
| PrincetonWind2065RCP8.5 | Princeton | Wind | RCP8.5 | 2065 | 89.1805 | 96.6828 | 104.76 | 112.671 | 120.6158
| PrincetonWind2070RCP8.5 | Princeton | Wind | RCP8.5 | 2070 | 89.759 | 97.4392 | 105.7367 | 113.8337 | 121.9724
| PrincetonWind2075RCP8.5 | Princeton | Wind | RCP8.5 | 2075 | 89.9835 | 97.7399 | 106.1333 | 114.3117 | 122.5348
| PrincetonWind2080RCP8.5 | Princeton | Wind | RCP8.5 | 2080 | 90.208 | 98.0406 | 106.53 | 114.7896 | 123.0972
| PrincetonWind2085RCP8.5 | Princeton | Wind | RCP8.5 | 2085 | 90.6484 | 98.6172 | 107.285 | 115.6937 | 124.1517
| PrincetonWind2090RCP8.5 | Princeton | Wind | RCP8.5 | 2090 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
| PrincetonWind2095RCP8.5 | Princeton | Wind | RCP8.5 | 2095 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
| PrincetonWind2100RCP8.5 | Princeton | Wind | RCP8.5 | 2100 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
| RaithIce Accretion2023RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2023 | 10.6464 | 12.7239 | 15.345 | 17.3568 | 19.3536
| RaithIce Accretion2025RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2025 | 10.6952 | 12.782 | 15.4175 | 17.4387 | 19.4481
| RaithIce Accretion2030RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2030 | 10.7439 | 12.8401 | 15.49 | 17.5206 | 19.5426
| RaithIce Accretion2035RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2035 | 10.7926 | 12.8982 | 15.5625 | 17.6026 | 19.6371
| RaithIce Accretion2040RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2040 | 10.8413 | 12.9563 | 15.635 | 17.6845 | 19.7316
| RaithIce Accretion2045RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2045 | 10.89 | 13.0144 | 15.7075 | 17.7664 | 19.8261
| RaithIce Accretion2050RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2050 | 10.922 | 13.0501 | 15.747 | 17.8077 | 19.8715
| RaithIce Accretion2055RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2055 | 10.9053 | 13.0277 | 15.714 | 17.767 | 19.8223
| RaithIce Accretion2060RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2060 | 10.8886 | 13.0053 | 15.681 | 17.7263 | 19.7732
| RaithIce Accretion2065RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2065 | 10.8719 | 12.9829 | 15.648 | 17.6856 | 19.724
| RaithIce Accretion2070RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2070 | 10.8552 | 12.9604 | 15.615 | 17.6449 | 19.6749
| RaithIce Accretion2075RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2075 | 10.923 | 13.0455 | 15.7225 | 17.7692 | 19.8135
| RaithIce Accretion2080RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2080 | 10.9909 | 13.1306 | 15.83 | 17.8935 | 19.9521
| RaithIce Accretion2085RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2085 | 11.0587 | 13.2157 | 15.9375 | 18.0178 | 20.0907
| RaithIce Accretion2090RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2090 | 11.1266 | 13.3007 | 16.045 | 18.1421 | 20.2293
| RaithIce Accretion2095RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2095 | 11.1944 | 13.3858 | 16.1525 | 18.2664 | 20.3679
| RaithIce Accretion2100RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2100 | 11.2623 | 13.4709 | 16.26 | 18.3907 | 20.5065
| RaithIce Accretion2023RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2023 | 10.6464 | 12.7239 | 15.345 | 17.3568 | 19.3536
| RaithIce Accretion2025RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2025 | 10.6952 | 12.782 | 15.4175 | 17.4387 | 19.4481
| RaithIce Accretion2030RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2030 | 10.7439 | 12.8401 | 15.49 | 17.5206 | 19.5426
| RaithIce Accretion2035RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2035 | 10.7926 | 12.8982 | 15.5625 | 17.6026 | 19.6371
| RaithIce Accretion2040RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2040 | 10.8413 | 12.9563 | 15.635 | 17.6845 | 19.7316
| RaithIce Accretion2045RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2045 | 10.89 | 13.0144 | 15.7075 | 17.7664 | 19.8261
| RaithIce Accretion2050RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2050 | 10.922 | 13.0501 | 15.747 | 17.8077 | 19.8715
| RaithIce Accretion2055RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2055 | 10.9053 | 13.0277 | 15.714 | 17.767 | 19.8223
| RaithIce Accretion2060RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2060 | 10.8886 | 13.0053 | 15.681 | 17.7263 | 19.7732
| RaithIce Accretion2065RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2065 | 10.8719 | 12.9829 | 15.648 | 17.6856 | 19.724
| RaithIce Accretion2070RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2070 | 10.8552 | 12.9604 | 15.615 | 17.6449 | 19.6749
| RaithIce Accretion2075RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2075 | 10.957 | 13.0881 | 15.7762 | 17.8314 | 19.8828
| RaithIce Accretion2080RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2080 | 11.0587 | 13.2157 | 15.9375 | 18.0178 | 20.0907
| RaithIce Accretion2085RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2085 | 11.1605 | 13.3433 | 16.0988 | 18.2043 | 20.2986
| RaithIce Accretion2090RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2090 | 11.2727 | 13.4833 | 16.275 | 18.4133 | 20.538
| RaithIce Accretion2095RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2095 | 11.2831 | 13.4958 | 16.29 | 18.4359 | 20.5695
| RaithIce Accretion2100RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2100 | 11.2936 | 13.5082 | 16.305 | 18.4585 | 20.601
| RaithIce Accretion2023RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2023 | 10.6464 | 12.7239 | 15.345 | 17.3568 | 19.3536
| RaithIce Accretion2025RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2025 | 10.7439 | 12.8401 | 15.49 | 17.5206 | 19.5426
| RaithIce Accretion2030RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2030 | 10.8413 | 12.9563 | 15.635 | 17.6845 | 19.7316
| RaithIce Accretion2035RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2035 | 10.9387 | 13.0725 | 15.78 | 17.8483 | 19.9206
| RaithIce Accretion2040RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2040 | 10.9109 | 13.0351 | 15.725 | 17.7805 | 19.8387
| RaithIce Accretion2045RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2045 | 10.883 | 12.9978 | 15.67 | 17.7127 | 19.7568
| RaithIce Accretion2050RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2050 | 10.9909 | 13.1306 | 15.83 | 17.8935 | 19.9521
| RaithIce Accretion2055RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2055 | 11.1266 | 13.3007 | 16.045 | 18.1421 | 20.2293
| RaithIce Accretion2060RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2060 | 11.2727 | 13.4833 | 16.275 | 18.4133 | 20.538
| RaithIce Accretion2065RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2065 | 11.2831 | 13.4958 | 16.29 | 18.4359 | 20.5695
| RaithIce Accretion2070RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2070 | 11.3423 | 13.5746 | 16.4 | 18.5659 | 20.7207
| RaithIce Accretion2075RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2075 | 11.391 | 13.641 | 16.495 | 18.6732 | 20.8404
| RaithIce Accretion2080RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2080 | 11.4397 | 13.7074 | 16.59 | 18.7806 | 20.9601
| RaithIce Accretion2085RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2085 | 11.231 | 13.4647 | 16.2975 | 18.4586 | 20.6105
| RaithIce Accretion2090RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2090 | 11.0222 | 13.2219 | 16.005 | 18.1365 | 20.2608
| RaithIce Accretion2095RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2095 | 11.0222 | 13.2219 | 16.005 | 18.1365 | 20.2608
| RaithIce Accretion2100RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2100 | 11.0222 | 13.2219 | 16.005 | 18.1365 | 20.2608
| RaithWind2023RCP4.5 | Raith | Wind | RCP4.5 | 2023 | 70.9401 | 76.4125 | 82.1804 | 87.9418 | 93.7044
| RaithWind2025RCP4.5 | Raith | Wind | RCP4.5 | 2025 | 71.0097 | 76.4901 | 82.2665 | 88.0369 | 93.8072
| RaithWind2030RCP4.5 | Raith | Wind | RCP4.5 | 2030 | 71.0793 | 76.5676 | 82.3526 | 88.1319 | 93.91
| RaithWind2035RCP4.5 | Raith | Wind | RCP4.5 | 2035 | 71.149 | 76.6451 | 82.4387 | 88.227 | 94.0128
| RaithWind2040RCP4.5 | Raith | Wind | RCP4.5 | 2040 | 71.2186 | 76.7226 | 82.5248 | 88.322 | 94.1157
| RaithWind2045RCP4.5 | Raith | Wind | RCP4.5 | 2045 | 71.2882 | 76.8002 | 82.6109 | 88.4171 | 94.2185
| RaithWind2050RCP4.5 | Raith | Wind | RCP4.5 | 2050 | 71.3947 | 76.9189 | 82.7429 | 88.5612 | 94.3755
| RaithWind2055RCP4.5 | Raith | Wind | RCP4.5 | 2055 | 71.4315 | 76.9601 | 82.7888 | 88.6104 | 94.4298
| RaithWind2060RCP4.5 | Raith | Wind | RCP4.5 | 2060 | 71.4683 | 77.0012 | 82.8348 | 88.6595 | 94.484
| RaithWind2065RCP4.5 | Raith | Wind | RCP4.5 | 2065 | 71.5051 | 77.0424 | 82.8807 | 88.7086 | 94.5382
| RaithWind2070RCP4.5 | Raith | Wind | RCP4.5 | 2070 | 71.5419 | 77.0836 | 82.9266 | 88.7578 | 94.5924
| RaithWind2075RCP4.5 | Raith | Wind | RCP4.5 | 2075 | 71.6328 | 77.1929 | 83.0578 | 88.9084 | 94.7622
| RaithWind2080RCP4.5 | Raith | Wind | RCP4.5 | 2080 | 71.7237 | 77.3022 | 83.189 | 89.059 | 94.9321
| RaithWind2085RCP4.5 | Raith | Wind | RCP4.5 | 2085 | 71.8145 | 77.4115 | 83.3202 | 89.2096 | 95.1019
| RaithWind2090RCP4.5 | Raith | Wind | RCP4.5 | 2090 | 71.9054 | 77.5208 | 83.4514 | 89.3603 | 95.2717
| RaithWind2095RCP4.5 | Raith | Wind | RCP4.5 | 2095 | 71.9963 | 77.6301 | 83.5826 | 89.5109 | 95.4415
| RaithWind2100RCP4.5 | Raith | Wind | RCP4.5 | 2100 | 72.0871 | 77.7394 | 83.7138 | 89.6615 | 95.6113
| RaithWind2023RCP6.0 | Raith | Wind | RCP6.0 | 2023 | 70.9401 | 76.4125 | 82.1804 | 87.9418 | 93.7044
| RaithWind2025RCP6.0 | Raith | Wind | RCP6.0 | 2025 | 71.0097 | 76.4901 | 82.2665 | 88.0369 | 93.8072
| RaithWind2030RCP6.0 | Raith | Wind | RCP6.0 | 2030 | 71.0793 | 76.5676 | 82.3526 | 88.1319 | 93.91
| RaithWind2035RCP6.0 | Raith | Wind | RCP6.0 | 2035 | 71.149 | 76.6451 | 82.4387 | 88.227 | 94.0128
| RaithWind2040RCP6.0 | Raith | Wind | RCP6.0 | 2040 | 71.2186 | 76.7226 | 82.5248 | 88.322 | 94.1157
| RaithWind2045RCP6.0 | Raith | Wind | RCP6.0 | 2045 | 71.2882 | 76.8002 | 82.6109 | 88.4171 | 94.2185
| RaithWind2050RCP6.0 | Raith | Wind | RCP6.0 | 2050 | 71.3947 | 76.9189 | 82.7429 | 88.5612 | 94.3755
| RaithWind2055RCP6.0 | Raith | Wind | RCP6.0 | 2055 | 71.4315 | 76.9601 | 82.7888 | 88.6104 | 94.4298
| RaithWind2060RCP6.0 | Raith | Wind | RCP6.0 | 2060 | 71.4683 | 77.0012 | 82.8348 | 88.6595 | 94.484
| RaithWind2065RCP6.0 | Raith | Wind | RCP6.0 | 2065 | 71.5051 | 77.0424 | 82.8807 | 88.7086 | 94.5382
| RaithWind2070RCP6.0 | Raith | Wind | RCP6.0 | 2070 | 71.5419 | 77.0836 | 82.9266 | 88.7578 | 94.5924
| RaithWind2075RCP6.0 | Raith | Wind | RCP6.0 | 2075 | 71.6782 | 77.2476 | 83.1234 | 88.9837 | 94.8471
| RaithWind2080RCP6.0 | Raith | Wind | RCP6.0 | 2080 | 71.8145 | 77.4115 | 83.3202 | 89.2096 | 95.1019
| RaithWind2085RCP6.0 | Raith | Wind | RCP6.0 | 2085 | 71.9508 | 77.5755 | 83.517 | 89.4356 | 95.3566
| RaithWind2090RCP6.0 | Raith | Wind | RCP6.0 | 2090 | 72.1296 | 77.8132 | 83.8259 | 89.8048 | 95.7858
| RaithWind2095RCP6.0 | Raith | Wind | RCP6.0 | 2095 | 72.1721 | 77.8869 | 83.9379 | 89.9481 | 95.9603
| RaithWind2100RCP6.0 | Raith | Wind | RCP6.0 | 2100 | 72.2146 | 77.9606 | 84.05 | 90.0914 | 96.1348
| RaithWind2023RCP8.5 | Raith | Wind | RCP8.5 | 2023 | 70.9401 | 76.4125 | 82.1804 | 87.9418 | 93.7044
| RaithWind2025RCP8.5 | Raith | Wind | RCP8.5 | 2025 | 71.0793 | 76.5676 | 82.3526 | 88.1319 | 93.91
| RaithWind2030RCP8.5 | Raith | Wind | RCP8.5 | 2030 | 71.2186 | 76.7226 | 82.5248 | 88.322 | 94.1157
| RaithWind2035RCP8.5 | Raith | Wind | RCP8.5 | 2035 | 71.3578 | 76.8777 | 82.697 | 88.5121 | 94.3213
| RaithWind2040RCP8.5 | Raith | Wind | RCP8.5 | 2040 | 71.4192 | 76.9463 | 82.7735 | 88.594 | 94.4117
| RaithWind2045RCP8.5 | Raith | Wind | RCP8.5 | 2045 | 71.4806 | 77.015 | 82.8501 | 88.6759 | 94.502
| RaithWind2050RCP8.5 | Raith | Wind | RCP8.5 | 2050 | 71.7237 | 77.3022 | 83.189 | 89.059 | 94.9321
| RaithWind2055RCP8.5 | Raith | Wind | RCP8.5 | 2055 | 71.9054 | 77.5208 | 83.4514 | 89.3603 | 95.2717
| RaithWind2060RCP8.5 | Raith | Wind | RCP8.5 | 2060 | 72.1296 | 77.8132 | 83.8259 | 89.8048 | 95.7858
| RaithWind2065RCP8.5 | Raith | Wind | RCP8.5 | 2065 | 72.1721 | 77.8869 | 83.9379 | 89.9481 | 95.9603
| RaithWind2070RCP8.5 | Raith | Wind | RCP8.5 | 2070 | 72.4058 | 78.1919 | 84.3288 | 90.4131 | 96.5025
| RaithWind2075RCP8.5 | Raith | Wind | RCP8.5 | 2075 | 72.5969 | 78.4232 | 84.6076 | 90.7349 | 96.8702
| RaithWind2080RCP8.5 | Raith | Wind | RCP8.5 | 2080 | 72.7881 | 78.6546 | 84.8864 | 91.0566 | 97.2379
| RaithWind2085RCP8.5 | Raith | Wind | RCP8.5 | 2085 | 72.7669 | 78.6279 | 84.8577 | 91.0259 | 97.2052
| RaithWind2090RCP8.5 | Raith | Wind | RCP8.5 | 2090 | 72.7456 | 78.6012 | 84.829 | 90.9952 | 97.1725
| RaithWind2095RCP8.5 | Raith | Wind | RCP8.5 | 2095 | 72.7456 | 78.6012 | 84.829 | 90.9952 | 97.1725
| RaithWind2100RCP8.5 | Raith | Wind | RCP8.5 | 2100 | 72.7456 | 78.6012 | 84.829 | 90.9952 | 97.1725
| Rayside-Balfour (Chelmsford)Ice Accretion2023RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2023 | 16.0587 | 19.1913 | 23.166 | 26.2024 | 29.2446
| Rayside-Balfour (Chelmsford)Ice Accretion2025RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2025 | 16.1353 | 19.2826 | 23.2797 | 26.3309 | 29.3878
| Rayside-Balfour (Chelmsford)Ice Accretion2030RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2030 | 16.2118 | 19.3739 | 23.3933 | 26.4593 | 29.531
| Rayside-Balfour (Chelmsford)Ice Accretion2035RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2035 | 16.2884 | 19.4652 | 23.507 | 26.5878 | 29.6743
| Rayside-Balfour (Chelmsford)Ice Accretion2040RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2040 | 16.3649 | 19.5565 | 23.6207 | 26.7162 | 29.8175
| Rayside-Balfour (Chelmsford)Ice Accretion2045RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2045 | 16.4415 | 19.6478 | 23.7343 | 26.8447 | 29.9607
| Rayside-Balfour (Chelmsford)Ice Accretion2050RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2050 | 16.5945 | 19.845 | 23.9888 | 27.1421 | 30.298
| Rayside-Balfour (Chelmsford)Ice Accretion2055RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2055 | 16.6711 | 19.9509 | 24.1296 | 27.3112 | 30.492
| Rayside-Balfour (Chelmsford)Ice Accretion2060RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2060 | 16.7476 | 20.0568 | 24.2704 | 27.4802 | 30.686
| Rayside-Balfour (Chelmsford)Ice Accretion2065RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2065 | 16.8242 | 20.1627 | 24.4112 | 27.6493 | 30.8801
| Rayside-Balfour (Chelmsford)Ice Accretion2070RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2070 | 16.9007 | 20.2686 | 24.552 | 27.8183 | 31.0741
| Rayside-Balfour (Chelmsford)Ice Accretion2075RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2075 | 16.814 | 20.1773 | 24.4493 | 27.7106 | 30.9586
| Rayside-Balfour (Chelmsford)Ice Accretion2080RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2080 | 16.7272 | 20.086 | 24.3467 | 27.6029 | 30.8431
| Rayside-Balfour (Chelmsford)Ice Accretion2085RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2085 | 16.6405 | 19.9947 | 24.244 | 27.4952 | 30.7276
| Rayside-Balfour (Chelmsford)Ice Accretion2090RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2090 | 16.5537 | 19.9034 | 24.1413 | 27.3874 | 30.6121
| Rayside-Balfour (Chelmsford)Ice Accretion2095RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2095 | 16.467 | 19.8121 | 24.0387 | 27.2797 | 30.4966
| Rayside-Balfour (Chelmsford)Ice Accretion2100RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2100 | 16.3802 | 19.7208 | 23.936 | 27.172 | 30.3811
| Rayside-Balfour (Chelmsford)Ice Accretion2023RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2023 | 16.0587 | 19.1913 | 23.166 | 26.2024 | 29.2446
| Rayside-Balfour (Chelmsford)Ice Accretion2025RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2025 | 16.1353 | 19.2826 | 23.2797 | 26.3309 | 29.3878
| Rayside-Balfour (Chelmsford)Ice Accretion2030RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2030 | 16.2118 | 19.3739 | 23.3933 | 26.4593 | 29.531
| Rayside-Balfour (Chelmsford)Ice Accretion2035RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2035 | 16.2884 | 19.4652 | 23.507 | 26.5878 | 29.6743
| Rayside-Balfour (Chelmsford)Ice Accretion2040RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2040 | 16.3649 | 19.5565 | 23.6207 | 26.7162 | 29.8175
| Rayside-Balfour (Chelmsford)Ice Accretion2045RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2045 | 16.4415 | 19.6478 | 23.7343 | 26.8447 | 29.9607
| Rayside-Balfour (Chelmsford)Ice Accretion2050RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2050 | 16.5945 | 19.845 | 23.9888 | 27.1421 | 30.298
| Rayside-Balfour (Chelmsford)Ice Accretion2055RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2055 | 16.6711 | 19.9509 | 24.1296 | 27.3112 | 30.492
| Rayside-Balfour (Chelmsford)Ice Accretion2060RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2060 | 16.7476 | 20.0568 | 24.2704 | 27.4802 | 30.686
| Rayside-Balfour (Chelmsford)Ice Accretion2065RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2065 | 16.8242 | 20.1627 | 24.4112 | 27.6493 | 30.8801
| Rayside-Balfour (Chelmsford)Ice Accretion2070RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2070 | 16.9007 | 20.2686 | 24.552 | 27.8183 | 31.0741
| Rayside-Balfour (Chelmsford)Ice Accretion2075RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2075 | 16.7706 | 20.1317 | 24.398 | 27.6567 | 30.9009
| Rayside-Balfour (Chelmsford)Ice Accretion2080RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2080 | 16.6405 | 19.9947 | 24.244 | 27.4952 | 30.7276
| Rayside-Balfour (Chelmsford)Ice Accretion2085RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2085 | 16.5103 | 19.8577 | 24.09 | 27.3336 | 30.5544
| Rayside-Balfour (Chelmsford)Ice Accretion2090RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2090 | 16.3853 | 19.7512 | 24.0093 | 27.2631 | 30.5012
| Rayside-Balfour (Chelmsford)Ice Accretion2095RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2095 | 16.3904 | 19.7817 | 24.0827 | 27.3543 | 30.6214
| Rayside-Balfour (Chelmsford)Ice Accretion2100RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2100 | 16.3955 | 19.8121 | 24.156 | 27.4454 | 30.7415
| Rayside-Balfour (Chelmsford)Ice Accretion2023RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2023 | 16.0587 | 19.1913 | 23.166 | 26.2024 | 29.2446
| Rayside-Balfour (Chelmsford)Ice Accretion2025RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2025 | 16.2118 | 19.3739 | 23.3933 | 26.4593 | 29.531
| Rayside-Balfour (Chelmsford)Ice Accretion2030RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2030 | 16.3649 | 19.5565 | 23.6207 | 26.7162 | 29.8175
| Rayside-Balfour (Chelmsford)Ice Accretion2035RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2035 | 16.518 | 19.7391 | 23.848 | 26.9731 | 30.1039
| Rayside-Balfour (Chelmsford)Ice Accretion2040RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2040 | 16.6456 | 19.9156 | 24.0827 | 27.2548 | 30.4273
| Rayside-Balfour (Chelmsford)Ice Accretion2045RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2045 | 16.7731 | 20.0921 | 24.3173 | 27.5366 | 30.7507
| Rayside-Balfour (Chelmsford)Ice Accretion2050RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2050 | 16.7272 | 20.086 | 24.3467 | 27.6029 | 30.8431
| Rayside-Balfour (Chelmsford)Ice Accretion2055RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2055 | 16.5537 | 19.9034 | 24.1413 | 27.3874 | 30.6121
| Rayside-Balfour (Chelmsford)Ice Accretion2060RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2060 | 16.3853 | 19.7512 | 24.0093 | 27.2631 | 30.5012
| Rayside-Balfour (Chelmsford)Ice Accretion2065RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2065 | 16.3904 | 19.7817 | 24.0827 | 27.3543 | 30.6214
| Rayside-Balfour (Chelmsford)Ice Accretion2070RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2070 | 16.0996 | 19.4895 | 23.782 | 27.0394 | 30.298
| Rayside-Balfour (Chelmsford)Ice Accretion2075RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2075 | 15.8036 | 19.1669 | 23.408 | 26.6333 | 29.8544
| Rayside-Balfour (Chelmsford)Ice Accretion2080RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2080 | 15.5076 | 18.8443 | 23.034 | 26.2273 | 29.4109
| Rayside-Balfour (Chelmsford)Ice Accretion2085RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2085 | 15.4464 | 18.8169 | 23.067 | 26.2895 | 29.5079
| Rayside-Balfour (Chelmsford)Ice Accretion2090RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2090 | 15.3852 | 18.7895 | 23.1 | 26.3516 | 29.605
| Rayside-Balfour (Chelmsford)Ice Accretion2095RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2095 | 15.3852 | 18.7895 | 23.1 | 26.3516 | 29.605
| Rayside-Balfour (Chelmsford)Ice Accretion2100RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2100 | 15.3852 | 18.7895 | 23.1 | 26.3516 | 29.605
| Rayside-Balfour (Chelmsford)Wind2023RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2023 | 79.1819 | 85.2901 | 91.7189 | 98.149 | 104.5803
| Rayside-Balfour (Chelmsford)Wind2025RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2025 | 79.288 | 85.4114 | 91.8569 | 98.3015 | 104.748
| Rayside-Balfour (Chelmsford)Wind2030RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2030 | 79.3941 | 85.5327 | 91.9949 | 98.4541 | 104.9157
| Rayside-Balfour (Chelmsford)Wind2035RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2035 | 79.5002 | 85.654 | 92.1329 | 98.6066 | 105.0834
| Rayside-Balfour (Chelmsford)Wind2040RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2040 | 79.6063 | 85.7753 | 92.271 | 98.7591 | 105.2511
| Rayside-Balfour (Chelmsford)Wind2045RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2045 | 79.7123 | 85.8966 | 92.409 | 98.9117 | 105.4189
| Rayside-Balfour (Chelmsford)Wind2050RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2050 | 79.8608 | 86.0552 | 92.5779 | 99.0896 | 105.6073
| Rayside-Balfour (Chelmsford)Wind2055RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2055 | 79.9033 | 86.0924 | 92.6089 | 99.1149 | 105.6281
| Rayside-Balfour (Chelmsford)Wind2060RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2060 | 79.9457 | 86.1296 | 92.6398 | 99.1402 | 105.6488
| Rayside-Balfour (Chelmsford)Wind2065RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2065 | 79.9881 | 86.1669 | 92.6708 | 99.1655 | 105.6696
| Rayside-Balfour (Chelmsford)Wind2070RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2070 | 80.0306 | 86.2041 | 92.7017 | 99.1908 | 105.6903
| Rayside-Balfour (Chelmsford)Wind2075RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2075 | 80.1144 | 86.3113 | 92.8382 | 99.3547 | 105.8788
| Rayside-Balfour (Chelmsford)Wind2080RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2080 | 80.1982 | 86.4185 | 92.9747 | 99.5186 | 106.0672
| Rayside-Balfour (Chelmsford)Wind2085RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2085 | 80.282 | 86.5257 | 93.1112 | 99.6825 | 106.2557
| Rayside-Balfour (Chelmsford)Wind2090RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2090 | 80.3658 | 86.6329 | 93.2477 | 99.8464 | 106.4442
| Rayside-Balfour (Chelmsford)Wind2095RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2095 | 80.4497 | 86.7401 | 93.3842 | 100.0103 | 106.6326
| Rayside-Balfour (Chelmsford)Wind2100RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2100 | 80.5335 | 86.8473 | 93.5207 | 100.1743 | 106.8211
| Rayside-Balfour (Chelmsford)Wind2023RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2023 | 79.1819 | 85.2901 | 91.7189 | 98.149 | 104.5803
| Rayside-Balfour (Chelmsford)Wind2025RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2025 | 79.288 | 85.4114 | 91.8569 | 98.3015 | 104.748
| Rayside-Balfour (Chelmsford)Wind2030RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2030 | 79.3941 | 85.5327 | 91.9949 | 98.4541 | 104.9157
| Rayside-Balfour (Chelmsford)Wind2035RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2035 | 79.5002 | 85.654 | 92.1329 | 98.6066 | 105.0834
| Rayside-Balfour (Chelmsford)Wind2040RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2040 | 79.6063 | 85.7753 | 92.271 | 98.7591 | 105.2511
| Rayside-Balfour (Chelmsford)Wind2045RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2045 | 79.7123 | 85.8966 | 92.409 | 98.9117 | 105.4189
| Rayside-Balfour (Chelmsford)Wind2050RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2050 | 79.8608 | 86.0552 | 92.5779 | 99.0896 | 105.6073
| Rayside-Balfour (Chelmsford)Wind2055RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2055 | 79.9033 | 86.0924 | 92.6089 | 99.1149 | 105.6281
| Rayside-Balfour (Chelmsford)Wind2060RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2060 | 79.9457 | 86.1296 | 92.6398 | 99.1402 | 105.6488
| Rayside-Balfour (Chelmsford)Wind2065RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2065 | 79.9881 | 86.1669 | 92.6708 | 99.1655 | 105.6696
| Rayside-Balfour (Chelmsford)Wind2070RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2070 | 80.0306 | 86.2041 | 92.7017 | 99.1908 | 105.6903
| Rayside-Balfour (Chelmsford)Wind2075RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2075 | 80.1563 | 86.3649 | 92.9064 | 99.4367 | 105.973
| Rayside-Balfour (Chelmsford)Wind2080RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2080 | 80.282 | 86.5257 | 93.1112 | 99.6825 | 106.2557
| Rayside-Balfour (Chelmsford)Wind2085RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2085 | 80.4077 | 86.6865 | 93.316 | 99.9284 | 106.5384
| Rayside-Balfour (Chelmsford)Wind2090RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2090 | 80.8425 | 87.2422 | 94.0212 | 100.7617 | 107.5023
| Rayside-Balfour (Chelmsford)Wind2095RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2095 | 81.1516 | 87.6372 | 94.5217 | 101.3492 | 108.1835
| Rayside-Balfour (Chelmsford)Wind2100RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2100 | 81.4607 | 88.0321 | 95.0222 | 101.9367 | 108.8648
| Rayside-Balfour (Chelmsford)Wind2023RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2023 | 79.1819 | 85.2901 | 91.7189 | 98.149 | 104.5803
| Rayside-Balfour (Chelmsford)Wind2025RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2025 | 79.3941 | 85.5327 | 91.9949 | 98.4541 | 104.9157
| Rayside-Balfour (Chelmsford)Wind2030RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2030 | 79.6063 | 85.7753 | 92.271 | 98.7591 | 105.2511
| Rayside-Balfour (Chelmsford)Wind2035RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2035 | 79.8184 | 86.0179 | 92.547 | 99.0642 | 105.5866
| Rayside-Balfour (Chelmsford)Wind2040RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2040 | 79.8891 | 86.08 | 92.5986 | 99.1064 | 105.6212
| Rayside-Balfour (Chelmsford)Wind2045RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2045 | 79.9599 | 86.1421 | 92.6501 | 99.1486 | 105.6557
| Rayside-Balfour (Chelmsford)Wind2050RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2050 | 80.1982 | 86.4185 | 92.9747 | 99.5186 | 106.0672
| Rayside-Balfour (Chelmsford)Wind2055RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2055 | 80.3658 | 86.6329 | 93.2477 | 99.8464 | 106.4442
| Rayside-Balfour (Chelmsford)Wind2060RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2060 | 80.8425 | 87.2422 | 94.0212 | 100.7617 | 107.5023
| Rayside-Balfour (Chelmsford)Wind2065RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2065 | 81.1516 | 87.6372 | 94.5217 | 101.3492 | 108.1835
| Rayside-Balfour (Chelmsford)Wind2070RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2070 | 81.6807 | 88.3058 | 95.365 | 102.3359 | 109.3178
| Rayside-Balfour (Chelmsford)Wind2075RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2075 | 81.9007 | 88.5794 | 95.7077 | 102.7351 | 109.7708
| Rayside-Balfour (Chelmsford)Wind2080RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2080 | 82.1207 | 88.853 | 96.0505 | 103.1343 | 110.2237
| Rayside-Balfour (Chelmsford)Wind2085RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2085 | 82.3486 | 89.1323 | 96.3872 | 103.5238 | 110.675
| Rayside-Balfour (Chelmsford)Wind2090RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2090 | 82.5765 | 89.4116 | 96.7239 | 103.9133 | 111.1263
| Rayside-Balfour (Chelmsford)Wind2095RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2095 | 82.5765 | 89.4116 | 96.7239 | 103.9133 | 111.1263
| Rayside-Balfour (Chelmsford)Wind2100RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2100 | 82.5765 | 89.4116 | 96.7239 | 103.9133 | 111.1263
| Red LakeIce Accretion2023RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2023 | 9.3619 | 11.132 | 13.37 | 15.0923 | 16.8109
| Red LakeIce Accretion2025RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2025 | 9.5519 | 11.3508 | 13.6267 | 15.3797 | 17.1284
| Red LakeIce Accretion2030RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2030 | 9.7418 | 11.5696 | 13.8833 | 15.6671 | 17.446
| Red LakeIce Accretion2035RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2035 | 9.9318 | 11.7885 | 14.14 | 15.9545 | 17.7635
| Red LakeIce Accretion2040RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2040 | 10.1218 | 12.0073 | 14.3967 | 16.2419 | 18.081
| Red LakeIce Accretion2045RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2045 | 10.3117 | 12.2262 | 14.6533 | 16.5293 | 18.3985
| Red LakeIce Accretion2050RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2050 | 10.605 | 12.5635 | 15.05 | 16.9717 | 18.8854
| Red LakeIce Accretion2055RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2055 | 10.7082 | 12.6821 | 15.19 | 17.1267 | 19.0547
| Red LakeIce Accretion2060RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2060 | 10.8115 | 12.8006 | 15.33 | 17.2818 | 19.2241
| Red LakeIce Accretion2065RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2065 | 10.9148 | 12.9191 | 15.47 | 17.4368 | 19.3934
| Red LakeIce Accretion2070RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2070 | 11.018 | 13.0376 | 15.61 | 17.5918 | 19.5628
| Red LakeIce Accretion2075RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2075 | 11.0911 | 13.1248 | 15.715 | 17.7079 | 19.6921
| Red LakeIce Accretion2080RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2080 | 11.1642 | 13.2119 | 15.82 | 17.8239 | 19.8215
| Red LakeIce Accretion2085RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2085 | 11.2372 | 13.2991 | 15.925 | 17.9399 | 19.9508
| Red LakeIce Accretion2090RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2090 | 11.3103 | 13.3862 | 16.03 | 18.0559 | 20.0802
| Red LakeIce Accretion2095RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2095 | 11.3833 | 13.4734 | 16.135 | 18.1719 | 20.2096
| Red LakeIce Accretion2100RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2100 | 11.4564 | 13.5605 | 16.24 | 18.2879 | 20.3389
| Red LakeIce Accretion2023RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2023 | 9.3619 | 11.132 | 13.37 | 15.0923 | 16.8109
| Red LakeIce Accretion2025RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2025 | 9.5519 | 11.3508 | 13.6267 | 15.3797 | 17.1284
| Red LakeIce Accretion2030RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2030 | 9.7418 | 11.5696 | 13.8833 | 15.6671 | 17.446
| Red LakeIce Accretion2035RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2035 | 9.9318 | 11.7885 | 14.14 | 15.9545 | 17.7635
| Red LakeIce Accretion2040RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2040 | 10.1218 | 12.0073 | 14.3967 | 16.2419 | 18.081
| Red LakeIce Accretion2045RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2045 | 10.3117 | 12.2262 | 14.6533 | 16.5293 | 18.3985
| Red LakeIce Accretion2050RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2050 | 10.605 | 12.5635 | 15.05 | 16.9717 | 18.8854
| Red LakeIce Accretion2055RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2055 | 10.7082 | 12.6821 | 15.19 | 17.1267 | 19.0547
| Red LakeIce Accretion2060RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2060 | 10.8115 | 12.8006 | 15.33 | 17.2818 | 19.2241
| Red LakeIce Accretion2065RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2065 | 10.9148 | 12.9191 | 15.47 | 17.4368 | 19.3934
| Red LakeIce Accretion2070RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2070 | 11.018 | 13.0376 | 15.61 | 17.5918 | 19.5628
| Red LakeIce Accretion2075RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2075 | 11.1276 | 13.1684 | 15.7675 | 17.7659 | 19.7568
| Red LakeIce Accretion2080RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2080 | 11.2372 | 13.2991 | 15.925 | 17.9399 | 19.9508
| Red LakeIce Accretion2085RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2085 | 11.3468 | 13.4298 | 16.0825 | 18.1139 | 20.1449
| Red LakeIce Accretion2090RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2090 | 11.307 | 13.3862 | 16.0347 | 18.0559 | 20.0861
| Red LakeIce Accretion2095RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2095 | 11.1577 | 13.2119 | 15.8293 | 17.8239 | 19.8332
| Red LakeIce Accretion2100RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2100 | 11.0083 | 13.0376 | 15.624 | 17.5918 | 19.5804
| Red LakeIce Accretion2023RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2023 | 9.3619 | 11.132 | 13.37 | 15.0923 | 16.8109
| Red LakeIce Accretion2025RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2025 | 9.7418 | 11.5696 | 13.8833 | 15.6671 | 17.446
| Red LakeIce Accretion2030RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2030 | 10.1218 | 12.0073 | 14.3967 | 16.2419 | 18.081
| Red LakeIce Accretion2035RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2035 | 10.5017 | 12.445 | 14.91 | 16.8167 | 18.716
| Red LakeIce Accretion2040RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2040 | 10.6738 | 12.6426 | 15.1433 | 17.0751 | 18.9983
| Red LakeIce Accretion2045RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2045 | 10.8459 | 12.8401 | 15.3767 | 17.3334 | 19.2805
| Red LakeIce Accretion2050RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2050 | 11.1642 | 13.2119 | 15.82 | 17.8239 | 19.8215
| Red LakeIce Accretion2055RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2055 | 11.3103 | 13.3862 | 16.03 | 18.0559 | 20.0802
| Red LakeIce Accretion2060RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2060 | 11.307 | 13.3862 | 16.0347 | 18.0559 | 20.0861
| Red LakeIce Accretion2065RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2065 | 11.1577 | 13.2119 | 15.8293 | 17.8239 | 19.8332
| Red LakeIce Accretion2070RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2070 | 10.9239 | 12.9331 | 15.4933 | 17.4495 | 19.4158
| Red LakeIce Accretion2075RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2075 | 10.8394 | 12.8285 | 15.3627 | 17.3071 | 19.2511
| Red LakeIce Accretion2080RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2080 | 10.755 | 12.7239 | 15.232 | 17.1647 | 19.0865
| Red LakeIce Accretion2085RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2085 | 10.6284 | 12.567 | 15.043 | 16.9432 | 18.8395
| Red LakeIce Accretion2090RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2090 | 10.5017 | 12.4102 | 14.854 | 16.7217 | 18.5926
| Red LakeIce Accretion2095RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2095 | 10.5017 | 12.4102 | 14.854 | 16.7217 | 18.5926
| Red LakeIce Accretion2100RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2100 | 10.5017 | 12.4102 | 14.854 | 16.7217 | 18.5926
| Red LakeWind2023RCP4.5 | Red Lake | Wind | RCP4.5 | 2023 | 69.1408 | 74.4 | 79.928 | 85.463 | 90.9994
| Red LakeWind2025RCP4.5 | Red Lake | Wind | RCP4.5 | 2025 | 69.2432 | 74.5153 | 80.0573 | 85.6071 | 91.1574
| Red LakeWind2030RCP4.5 | Red Lake | Wind | RCP4.5 | 2030 | 69.3457 | 74.6306 | 80.1867 | 85.7512 | 91.3155
| Red LakeWind2035RCP4.5 | Red Lake | Wind | RCP4.5 | 2035 | 69.4482 | 74.746 | 80.316 | 85.8953 | 91.4736
| Red LakeWind2040RCP4.5 | Red Lake | Wind | RCP4.5 | 2040 | 69.5506 | 74.8613 | 80.4453 | 86.0394 | 91.6317
| Red LakeWind2045RCP4.5 | Red Lake | Wind | RCP4.5 | 2045 | 69.6531 | 74.9766 | 80.5747 | 86.1835 | 91.7898
| Red LakeWind2050RCP4.5 | Red Lake | Wind | RCP4.5 | 2050 | 69.8454 | 75.1946 | 80.8192 | 86.4543 | 92.0865
| Red LakeWind2055RCP4.5 | Red Lake | Wind | RCP4.5 | 2055 | 69.9352 | 75.2973 | 80.9344 | 86.581 | 92.2251
| Red LakeWind2060RCP4.5 | Red Lake | Wind | RCP4.5 | 2060 | 70.025 | 75.3999 | 81.0496 | 86.7077 | 92.3637
| Red LakeWind2065RCP4.5 | Red Lake | Wind | RCP4.5 | 2065 | 70.1148 | 75.5026 | 81.1648 | 86.8344 | 92.5023
| Red LakeWind2070RCP4.5 | Red Lake | Wind | RCP4.5 | 2070 | 70.2046 | 75.6053 | 81.28 | 86.961 | 92.641
| Red LakeWind2075RCP4.5 | Red Lake | Wind | RCP4.5 | 2075 | 70.2598 | 75.6561 | 81.324 | 87.001 | 92.6759
| Red LakeWind2080RCP4.5 | Red Lake | Wind | RCP4.5 | 2080 | 70.3151 | 75.707 | 81.368 | 87.0409 | 92.7109
| Red LakeWind2085RCP4.5 | Red Lake | Wind | RCP4.5 | 2085 | 70.3704 | 75.7578 | 81.412 | 87.0809 | 92.7458
| Red LakeWind2090RCP4.5 | Red Lake | Wind | RCP4.5 | 2090 | 70.4256 | 75.8086 | 81.456 | 87.1208 | 92.7808
| Red LakeWind2095RCP4.5 | Red Lake | Wind | RCP4.5 | 2095 | 70.4809 | 75.8595 | 81.5 | 87.1608 | 92.8158
| Red LakeWind2100RCP4.5 | Red Lake | Wind | RCP4.5 | 2100 | 70.5362 | 75.9103 | 81.544 | 87.2007 | 92.8507
| Red LakeWind2023RCP6.0 | Red Lake | Wind | RCP6.0 | 2023 | 69.1408 | 74.4 | 79.928 | 85.463 | 90.9994
| Red LakeWind2025RCP6.0 | Red Lake | Wind | RCP6.0 | 2025 | 69.2432 | 74.5153 | 80.0573 | 85.6071 | 91.1574
| Red LakeWind2030RCP6.0 | Red Lake | Wind | RCP6.0 | 2030 | 69.3457 | 74.6306 | 80.1867 | 85.7512 | 91.3155
| Red LakeWind2035RCP6.0 | Red Lake | Wind | RCP6.0 | 2035 | 69.4482 | 74.746 | 80.316 | 85.8953 | 91.4736
| Red LakeWind2040RCP6.0 | Red Lake | Wind | RCP6.0 | 2040 | 69.5506 | 74.8613 | 80.4453 | 86.0394 | 91.6317
| Red LakeWind2045RCP6.0 | Red Lake | Wind | RCP6.0 | 2045 | 69.6531 | 74.9766 | 80.5747 | 86.1835 | 91.7898
| Red LakeWind2050RCP6.0 | Red Lake | Wind | RCP6.0 | 2050 | 69.8454 | 75.1946 | 80.8192 | 86.4543 | 92.0865
| Red LakeWind2055RCP6.0 | Red Lake | Wind | RCP6.0 | 2055 | 69.9352 | 75.2973 | 80.9344 | 86.581 | 92.2251
| Red LakeWind2060RCP6.0 | Red Lake | Wind | RCP6.0 | 2060 | 70.025 | 75.3999 | 81.0496 | 86.7077 | 92.3637
| Red LakeWind2065RCP6.0 | Red Lake | Wind | RCP6.0 | 2065 | 70.1148 | 75.5026 | 81.1648 | 86.8344 | 92.5023
| Red LakeWind2070RCP6.0 | Red Lake | Wind | RCP6.0 | 2070 | 70.2046 | 75.6053 | 81.28 | 86.961 | 92.641
| Red LakeWind2075RCP6.0 | Red Lake | Wind | RCP6.0 | 2075 | 70.2875 | 75.6815 | 81.346 | 87.021 | 92.6934
| Red LakeWind2080RCP6.0 | Red Lake | Wind | RCP6.0 | 2080 | 70.3704 | 75.7578 | 81.412 | 87.0809 | 92.7458
| Red LakeWind2085RCP6.0 | Red Lake | Wind | RCP6.0 | 2085 | 70.4533 | 75.8341 | 81.478 | 87.1408 | 92.7983
| Red LakeWind2090RCP6.0 | Red Lake | Wind | RCP6.0 | 2090 | 70.6858 | 76.1038 | 81.7947 | 87.4946 | 93.1942
| Red LakeWind2095RCP6.0 | Red Lake | Wind | RCP6.0 | 2095 | 70.8355 | 76.2972 | 82.0453 | 87.7885 | 93.5378
| Red LakeWind2100RCP6.0 | Red Lake | Wind | RCP6.0 | 2100 | 70.9852 | 76.4906 | 82.296 | 88.0824 | 93.8813
| Red LakeWind2023RCP8.5 | Red Lake | Wind | RCP8.5 | 2023 | 69.1408 | 74.4 | 79.928 | 85.463 | 90.9994
| Red LakeWind2025RCP8.5 | Red Lake | Wind | RCP8.5 | 2025 | 69.3457 | 74.6306 | 80.1867 | 85.7512 | 91.3155
| Red LakeWind2030RCP8.5 | Red Lake | Wind | RCP8.5 | 2030 | 69.5506 | 74.8613 | 80.4453 | 86.0394 | 91.6317
| Red LakeWind2035RCP8.5 | Red Lake | Wind | RCP8.5 | 2035 | 69.7556 | 75.0919 | 80.704 | 86.3276 | 91.9478
| Red LakeWind2040RCP8.5 | Red Lake | Wind | RCP8.5 | 2040 | 69.9052 | 75.263 | 80.896 | 86.5387 | 92.1789
| Red LakeWind2045RCP8.5 | Red Lake | Wind | RCP8.5 | 2045 | 70.0549 | 75.4342 | 81.088 | 86.7499 | 92.4099
| Red LakeWind2050RCP8.5 | Red Lake | Wind | RCP8.5 | 2050 | 70.3151 | 75.707 | 81.368 | 87.0409 | 92.7109
| Red LakeWind2055RCP8.5 | Red Lake | Wind | RCP8.5 | 2055 | 70.4256 | 75.8086 | 81.456 | 87.1208 | 92.7808
| Red LakeWind2060RCP8.5 | Red Lake | Wind | RCP8.5 | 2060 | 70.6858 | 76.1038 | 81.7947 | 87.4946 | 93.1942
| Red LakeWind2065RCP8.5 | Red Lake | Wind | RCP8.5 | 2065 | 70.8355 | 76.2972 | 82.0453 | 87.7885 | 93.5378
| Red LakeWind2070RCP8.5 | Red Lake | Wind | RCP8.5 | 2070 | 71.0819 | 76.5898 | 82.3973 | 88.188 | 93.9877
| Red LakeWind2075RCP8.5 | Red Lake | Wind | RCP8.5 | 2075 | 71.1786 | 76.689 | 82.4987 | 88.2935 | 94.0941
| Red LakeWind2080RCP8.5 | Red Lake | Wind | RCP8.5 | 2080 | 71.2753 | 76.7882 | 82.6 | 88.3991 | 94.2005
| Red LakeWind2085RCP8.5 | Red Lake | Wind | RCP8.5 | 2085 | 71.3996 | 76.9519 | 82.812 | 88.6559 | 94.5014
| Red LakeWind2090RCP8.5 | Red Lake | Wind | RCP8.5 | 2090 | 71.524 | 77.1156 | 83.024 | 88.9127 | 94.8024
| Red LakeWind2095RCP8.5 | Red Lake | Wind | RCP8.5 | 2095 | 71.524 | 77.1156 | 83.024 | 88.9127 | 94.8024
| Red LakeWind2100RCP8.5 | Red Lake | Wind | RCP8.5 | 2100 | 71.524 | 77.1156 | 83.024 | 88.9127 | 94.8024
| RenfrewIce Accretion2023RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2023 | 15.2933 | 18.2052 | 21.868 | 24.686 | 27.4982
| RenfrewIce Accretion2025RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2025 | 15.375 | 18.3056 | 22 | 24.8393 | 27.6692
| RenfrewIce Accretion2030RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2030 | 15.4566 | 18.4061 | 22.132 | 24.9926 | 27.8401
| RenfrewIce Accretion2035RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2035 | 15.5382 | 18.5065 | 22.264 | 25.1459 | 28.0111
| RenfrewIce Accretion2040RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2040 | 15.6199 | 18.6069 | 22.396 | 25.2992 | 28.182
| RenfrewIce Accretion2045RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2045 | 15.7015 | 18.7074 | 22.528 | 25.4525 | 28.3529
| RenfrewIce Accretion2050RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2050 | 15.7862 | 18.8261 | 22.6952 | 25.6555 | 28.5904
| RenfrewIce Accretion2055RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2055 | 15.7893 | 18.8443 | 22.7304 | 25.7052 | 28.6569
| RenfrewIce Accretion2060RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2060 | 15.7924 | 18.8626 | 22.7656 | 25.755 | 28.7235
| RenfrewIce Accretion2065RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2065 | 15.7954 | 18.8808 | 22.8008 | 25.8047 | 28.79
| RenfrewIce Accretion2070RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2070 | 15.7985 | 18.8991 | 22.836 | 25.8544 | 28.8565
| RenfrewIce Accretion2075RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2075 | 15.8189 | 18.9387 | 22.8983 | 25.9331 | 28.9489
| RenfrewIce Accretion2080RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2080 | 15.8393 | 18.9782 | 22.9607 | 26.0118 | 29.0413
| RenfrewIce Accretion2085RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2085 | 15.8597 | 19.0178 | 23.023 | 26.0906 | 29.1337
| RenfrewIce Accretion2090RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2090 | 15.8801 | 19.0574 | 23.0853 | 26.1693 | 29.2261
| RenfrewIce Accretion2095RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2095 | 15.9005 | 19.0969 | 23.1477 | 26.248 | 29.3185
| RenfrewIce Accretion2100RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2100 | 15.921 | 19.1365 | 23.21 | 26.3267 | 29.4109
| RenfrewIce Accretion2023RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2023 | 15.2933 | 18.2052 | 21.868 | 24.686 | 27.4982
| RenfrewIce Accretion2025RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2025 | 15.375 | 18.3056 | 22 | 24.8393 | 27.6692
| RenfrewIce Accretion2030RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2030 | 15.4566 | 18.4061 | 22.132 | 24.9926 | 27.8401
| RenfrewIce Accretion2035RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2035 | 15.5382 | 18.5065 | 22.264 | 25.1459 | 28.0111
| RenfrewIce Accretion2040RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2040 | 15.6199 | 18.6069 | 22.396 | 25.2992 | 28.182
| RenfrewIce Accretion2045RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2045 | 15.7015 | 18.7074 | 22.528 | 25.4525 | 28.3529
| RenfrewIce Accretion2050RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2050 | 15.7862 | 18.8261 | 22.6952 | 25.6555 | 28.5904
| RenfrewIce Accretion2055RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2055 | 15.7893 | 18.8443 | 22.7304 | 25.7052 | 28.6569
| RenfrewIce Accretion2060RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2060 | 15.7924 | 18.8626 | 22.7656 | 25.755 | 28.7235
| RenfrewIce Accretion2065RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2065 | 15.7954 | 18.8808 | 22.8008 | 25.8047 | 28.79
| RenfrewIce Accretion2070RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2070 | 15.7985 | 18.8991 | 22.836 | 25.8544 | 28.8565
| RenfrewIce Accretion2075RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2075 | 15.8291 | 18.9584 | 22.9295 | 25.9725 | 28.9951
| RenfrewIce Accretion2080RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2080 | 15.8597 | 19.0178 | 23.023 | 26.0906 | 29.1337
| RenfrewIce Accretion2085RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2085 | 15.8903 | 19.0771 | 23.1165 | 26.2087 | 29.2723
| RenfrewIce Accretion2090RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2090 | 15.8291 | 19.0452 | 23.1147 | 26.2273 | 29.3093
| RenfrewIce Accretion2095RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2095 | 15.7373 | 18.9539 | 23.0193 | 26.1279 | 29.2076
| RenfrewIce Accretion2100RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2100 | 15.6454 | 18.8626 | 22.924 | 26.0284 | 29.106
| RenfrewIce Accretion2023RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2023 | 15.2933 | 18.2052 | 21.868 | 24.686 | 27.4982
| RenfrewIce Accretion2025RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2025 | 15.4566 | 18.4061 | 22.132 | 24.9926 | 27.8401
| RenfrewIce Accretion2030RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2030 | 15.6199 | 18.6069 | 22.396 | 25.2992 | 28.182
| RenfrewIce Accretion2035RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2035 | 15.7832 | 18.8078 | 22.66 | 25.6058 | 28.5239
| RenfrewIce Accretion2040RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2040 | 15.7883 | 18.8382 | 22.7187 | 25.6887 | 28.6348
| RenfrewIce Accretion2045RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2045 | 15.7934 | 18.8687 | 22.7773 | 25.7715 | 28.7456
| RenfrewIce Accretion2050RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2050 | 15.8393 | 18.9782 | 22.9607 | 26.0118 | 29.0413
| RenfrewIce Accretion2055RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2055 | 15.8801 | 19.0574 | 23.0853 | 26.1693 | 29.2261
| RenfrewIce Accretion2060RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2060 | 15.8291 | 19.0452 | 23.1147 | 26.2273 | 29.3093
| RenfrewIce Accretion2065RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2065 | 15.7373 | 18.9539 | 23.0193 | 26.1279 | 29.2076
| RenfrewIce Accretion2070RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2070 | 15.6352 | 18.8869 | 22.9973 | 26.1361 | 29.2538
| RenfrewIce Accretion2075RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2075 | 15.625 | 18.9113 | 23.0707 | 26.2439 | 29.4017
| RenfrewIce Accretion2080RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2080 | 15.6148 | 18.9356 | 23.144 | 26.3516 | 29.5495
| RenfrewIce Accretion2085RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2085 | 15.0943 | 18.3513 | 22.484 | 25.6182 | 28.7595
| RenfrewIce Accretion2090RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2090 | 14.5738 | 17.767 | 21.824 | 24.8849 | 27.9695
| RenfrewIce Accretion2095RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2095 | 14.5738 | 17.767 | 21.824 | 24.8849 | 27.9695
| RenfrewIce Accretion2100RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2100 | 14.5738 | 17.767 | 21.824 | 24.8849 | 27.9695
| RenfrewWind2023RCP4.5 | Renfrew | Wind | RCP4.5 | 2023 | 75.9257 | 81.7418 | 87.8504 | 93.9717 | 100.0893
| RenfrewWind2025RCP4.5 | Renfrew | Wind | RCP4.5 | 2025 | 75.9244 | 81.7404 | 87.8504 | 93.9717 | 100.0909
| RenfrewWind2030RCP4.5 | Renfrew | Wind | RCP4.5 | 2030 | 75.9231 | 81.7391 | 87.8504 | 93.9717 | 100.0926
| RenfrewWind2035RCP4.5 | Renfrew | Wind | RCP4.5 | 2035 | 75.9219 | 81.7377 | 87.8504 | 93.9717 | 100.0943
| RenfrewWind2040RCP4.5 | Renfrew | Wind | RCP4.5 | 2040 | 75.9206 | 81.7363 | 87.8504 | 93.9717 | 100.096
| RenfrewWind2045RCP4.5 | Renfrew | Wind | RCP4.5 | 2045 | 75.9193 | 81.735 | 87.8504 | 93.9717 | 100.0976
| RenfrewWind2050RCP4.5 | Renfrew | Wind | RCP4.5 | 2050 | 75.8998 | 81.7123 | 87.824 | 93.9434 | 100.0652
| RenfrewWind2055RCP4.5 | Renfrew | Wind | RCP4.5 | 2055 | 75.8816 | 81.6911 | 87.7976 | 93.9152 | 100.0311
| RenfrewWind2060RCP4.5 | Renfrew | Wind | RCP4.5 | 2060 | 75.8634 | 81.6698 | 87.7712 | 93.8869 | 99.997
| RenfrewWind2065RCP4.5 | Renfrew | Wind | RCP4.5 | 2065 | 75.8451 | 81.6485 | 87.7448 | 93.8587 | 99.9629
| RenfrewWind2070RCP4.5 | Renfrew | Wind | RCP4.5 | 2070 | 75.8269 | 81.6272 | 87.7184 | 93.8304 | 99.9288
| RenfrewWind2075RCP4.5 | Renfrew | Wind | RCP4.5 | 2075 | 75.8687 | 81.6831 | 87.7917 | 93.9168 | 100.0307
| RenfrewWind2080RCP4.5 | Renfrew | Wind | RCP4.5 | 2080 | 75.9105 | 81.7391 | 87.8651 | 94.0031 | 100.1327
| RenfrewWind2085RCP4.5 | Renfrew | Wind | RCP4.5 | 2085 | 75.9523 | 81.795 | 87.9384 | 94.0894 | 100.2347
| RenfrewWind2090RCP4.5 | Renfrew | Wind | RCP4.5 | 2090 | 75.9941 | 81.8509 | 88.0117 | 94.1757 | 100.3367
| RenfrewWind2095RCP4.5 | Renfrew | Wind | RCP4.5 | 2095 | 76.0358 | 81.9068 | 88.0851 | 94.262 | 100.4387
| RenfrewWind2100RCP4.5 | Renfrew | Wind | RCP4.5 | 2100 | 76.0776 | 81.9628 | 88.1584 | 94.3483 | 100.5407
| RenfrewWind2023RCP6.0 | Renfrew | Wind | RCP6.0 | 2023 | 75.9257 | 81.7418 | 87.8504 | 93.9717 | 100.0893
| RenfrewWind2025RCP6.0 | Renfrew | Wind | RCP6.0 | 2025 | 75.9244 | 81.7404 | 87.8504 | 93.9717 | 100.0909
| RenfrewWind2030RCP6.0 | Renfrew | Wind | RCP6.0 | 2030 | 75.9231 | 81.7391 | 87.8504 | 93.9717 | 100.0926
| RenfrewWind2035RCP6.0 | Renfrew | Wind | RCP6.0 | 2035 | 75.9219 | 81.7377 | 87.8504 | 93.9717 | 100.0943
| RenfrewWind2040RCP6.0 | Renfrew | Wind | RCP6.0 | 2040 | 75.9206 | 81.7363 | 87.8504 | 93.9717 | 100.096
| RenfrewWind2045RCP6.0 | Renfrew | Wind | RCP6.0 | 2045 | 75.9193 | 81.735 | 87.8504 | 93.9717 | 100.0976
| RenfrewWind2050RCP6.0 | Renfrew | Wind | RCP6.0 | 2050 | 75.8998 | 81.7123 | 87.824 | 93.9434 | 100.0652
| RenfrewWind2055RCP6.0 | Renfrew | Wind | RCP6.0 | 2055 | 75.8816 | 81.6911 | 87.7976 | 93.9152 | 100.0311
| RenfrewWind2060RCP6.0 | Renfrew | Wind | RCP6.0 | 2060 | 75.8634 | 81.6698 | 87.7712 | 93.8869 | 99.997
| RenfrewWind2065RCP6.0 | Renfrew | Wind | RCP6.0 | 2065 | 75.8451 | 81.6485 | 87.7448 | 93.8587 | 99.9629
| RenfrewWind2070RCP6.0 | Renfrew | Wind | RCP6.0 | 2070 | 75.8269 | 81.6272 | 87.7184 | 93.8304 | 99.9288
| RenfrewWind2075RCP6.0 | Renfrew | Wind | RCP6.0 | 2075 | 75.8896 | 81.7111 | 87.8284 | 93.9599 | 100.0817
| RenfrewWind2080RCP6.0 | Renfrew | Wind | RCP6.0 | 2080 | 75.9523 | 81.795 | 87.9384 | 94.0894 | 100.2347
| RenfrewWind2085RCP6.0 | Renfrew | Wind | RCP6.0 | 2085 | 76.0149 | 81.8789 | 88.0484 | 94.2189 | 100.3877
| RenfrewWind2090RCP6.0 | Renfrew | Wind | RCP6.0 | 2090 | 75.9738 | 81.8209 | 87.9707 | 94.1223 | 100.2765
| RenfrewWind2095RCP6.0 | Renfrew | Wind | RCP6.0 | 2095 | 75.8699 | 81.679 | 87.7829 | 93.8964 | 100.0124
| RenfrewWind2100RCP6.0 | Renfrew | Wind | RCP6.0 | 2100 | 75.7661 | 81.5372 | 87.5952 | 93.6704 | 99.7482
| RenfrewWind2023RCP8.5 | Renfrew | Wind | RCP8.5 | 2023 | 75.9257 | 81.7418 | 87.8504 | 93.9717 | 100.0893
| RenfrewWind2025RCP8.5 | Renfrew | Wind | RCP8.5 | 2025 | 75.9231 | 81.7391 | 87.8504 | 93.9717 | 100.0926
| RenfrewWind2030RCP8.5 | Renfrew | Wind | RCP8.5 | 2030 | 75.9206 | 81.7363 | 87.8504 | 93.9717 | 100.096
| RenfrewWind2035RCP8.5 | Renfrew | Wind | RCP8.5 | 2035 | 75.9181 | 81.7336 | 87.8504 | 93.9717 | 100.0993
| RenfrewWind2040RCP8.5 | Renfrew | Wind | RCP8.5 | 2040 | 75.8877 | 81.6981 | 87.8064 | 93.9246 | 100.0424
| RenfrewWind2045RCP8.5 | Renfrew | Wind | RCP8.5 | 2045 | 75.8573 | 81.6627 | 87.7624 | 93.8775 | 99.9856
| RenfrewWind2050RCP8.5 | Renfrew | Wind | RCP8.5 | 2050 | 75.9105 | 81.7391 | 87.8651 | 94.0031 | 100.1327
| RenfrewWind2055RCP8.5 | Renfrew | Wind | RCP8.5 | 2055 | 75.9941 | 81.8509 | 88.0117 | 94.1757 | 100.3367
| RenfrewWind2060RCP8.5 | Renfrew | Wind | RCP8.5 | 2060 | 75.9738 | 81.8209 | 87.9707 | 94.1223 | 100.2765
| RenfrewWind2065RCP8.5 | Renfrew | Wind | RCP8.5 | 2065 | 75.8699 | 81.679 | 87.7829 | 93.8964 | 100.0124
| RenfrewWind2070RCP8.5 | Renfrew | Wind | RCP8.5 | 2070 | 75.7053 | 81.4499 | 87.4749 | 93.5229 | 99.5709
| RenfrewWind2075RCP8.5 | Renfrew | Wind | RCP8.5 | 2075 | 75.6445 | 81.3626 | 87.3547 | 93.3753 | 99.3937
| RenfrewWind2080RCP8.5 | Renfrew | Wind | RCP8.5 | 2080 | 75.5837 | 81.2753 | 87.2344 | 93.2278 | 99.2165
| RenfrewWind2085RCP8.5 | Renfrew | Wind | RCP8.5 | 2085 | 75.5989 | 81.3244 | 87.3268 | 93.3502 | 99.377
| RenfrewWind2090RCP8.5 | Renfrew | Wind | RCP8.5 | 2090 | 75.6141 | 81.3735 | 87.4192 | 93.4726 | 99.5375
| RenfrewWind2095RCP8.5 | Renfrew | Wind | RCP8.5 | 2095 | 75.6141 | 81.3735 | 87.4192 | 93.4726 | 99.5375
| RenfrewWind2100RCP8.5 | Renfrew | Wind | RCP8.5 | 2100 | 75.6141 | 81.3735 | 87.4192 | 93.4726 | 99.5375
| Richmond HillIce Accretion2023RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| Richmond HillIce Accretion2025RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| Richmond HillIce Accretion2030RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| Richmond HillIce Accretion2035RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| Richmond HillIce Accretion2040RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| Richmond HillIce Accretion2045RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| Richmond HillIce Accretion2050RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| Richmond HillIce Accretion2055RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| Richmond HillIce Accretion2060RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| Richmond HillIce Accretion2065RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| Richmond HillIce Accretion2070RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| Richmond HillIce Accretion2075RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
| Richmond HillIce Accretion2080RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| Richmond HillIce Accretion2085RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| Richmond HillIce Accretion2090RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| Richmond HillIce Accretion2095RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
| Richmond HillIce Accretion2100RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
| Richmond HillIce Accretion2023RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| Richmond HillIce Accretion2025RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| Richmond HillIce Accretion2030RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| Richmond HillIce Accretion2035RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| Richmond HillIce Accretion2040RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| Richmond HillIce Accretion2045RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| Richmond HillIce Accretion2050RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| Richmond HillIce Accretion2055RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| Richmond HillIce Accretion2060RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| Richmond HillIce Accretion2065RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| Richmond HillIce Accretion2070RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| Richmond HillIce Accretion2075RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
| Richmond HillIce Accretion2080RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| Richmond HillIce Accretion2085RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
| Richmond HillIce Accretion2090RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| Richmond HillIce Accretion2095RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| Richmond HillIce Accretion2100RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
| Richmond HillIce Accretion2023RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| Richmond HillIce Accretion2025RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| Richmond HillIce Accretion2030RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| Richmond HillIce Accretion2035RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
| Richmond HillIce Accretion2040RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
| Richmond HillIce Accretion2045RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
| Richmond HillIce Accretion2050RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| Richmond HillIce Accretion2055RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| Richmond HillIce Accretion2060RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| Richmond HillIce Accretion2065RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| Richmond HillIce Accretion2070RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
| Richmond HillIce Accretion2075RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
| Richmond HillIce Accretion2080RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
| Richmond HillIce Accretion2085RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
| Richmond HillIce Accretion2090RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| Richmond HillIce Accretion2095RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| Richmond HillIce Accretion2100RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| Richmond HillWind2023RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2023 | 79.631 | 85.7311 | 92.1472 | 98.568 | 104.9849
| Richmond HillWind2025RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2025 | 79.6456 | 85.7625 | 92.1978 | 98.6352 | 105.0688
| Richmond HillWind2030RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2030 | 79.6602 | 85.7939 | 92.2484 | 98.7025 | 105.1527
| Richmond HillWind2035RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2035 | 79.6747 | 85.8252 | 92.299 | 98.7698 | 105.2366
| Richmond HillWind2040RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2040 | 79.6893 | 85.8566 | 92.3496 | 98.837 | 105.3205
| Richmond HillWind2045RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2045 | 79.7039 | 85.888 | 92.4002 | 98.9043 | 105.4044
| Richmond HillWind2050RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2050 | 79.7963 | 86.0169 | 92.5741 | 99.1153 | 105.6561
| Richmond HillWind2055RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2055 | 79.8741 | 86.1144 | 92.6974 | 99.259 | 105.8239
| Richmond HillWind2060RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2060 | 79.952 | 86.212 | 92.8206 | 99.4027 | 105.9917
| Richmond HillWind2065RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2065 | 80.0298 | 86.3095 | 92.9439 | 99.5465 | 106.1595
| Richmond HillWind2070RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2070 | 80.1077 | 86.407 | 93.0672 | 99.6902 | 106.3273
| Richmond HillWind2075RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2075 | 80.2427 | 86.581 | 93.2895 | 99.9543 | 106.6332
| Richmond HillWind2080RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2080 | 80.3778 | 86.755 | 93.5119 | 100.2185 | 106.9391
| Richmond HillWind2085RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2085 | 80.5128 | 86.929 | 93.7342 | 100.4826 | 107.245
| Richmond HillWind2090RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2090 | 80.6479 | 87.1029 | 93.9565 | 100.7468 | 107.5509
| Richmond HillWind2095RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2095 | 80.7829 | 87.2769 | 94.1789 | 101.0109 | 107.8568
| Richmond HillWind2100RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2100 | 80.918 | 87.4509 | 94.4012 | 101.2751 | 108.1627
| Richmond HillWind2023RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2023 | 79.631 | 85.7311 | 92.1472 | 98.568 | 104.9849
| Richmond HillWind2025RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2025 | 79.6456 | 85.7625 | 92.1978 | 98.6352 | 105.0688
| Richmond HillWind2030RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2030 | 79.6602 | 85.7939 | 92.2484 | 98.7025 | 105.1527
| Richmond HillWind2035RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2035 | 79.6747 | 85.8252 | 92.299 | 98.7698 | 105.2366
| Richmond HillWind2040RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2040 | 79.6893 | 85.8566 | 92.3496 | 98.837 | 105.3205
| Richmond HillWind2045RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2045 | 79.7039 | 85.888 | 92.4002 | 98.9043 | 105.4044
| Richmond HillWind2050RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2050 | 79.7963 | 86.0169 | 92.5741 | 99.1153 | 105.6561
| Richmond HillWind2055RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2055 | 79.8741 | 86.1144 | 92.6974 | 99.259 | 105.8239
| Richmond HillWind2060RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2060 | 79.952 | 86.212 | 92.8206 | 99.4027 | 105.9917
| Richmond HillWind2065RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2065 | 80.0298 | 86.3095 | 92.9439 | 99.5465 | 106.1595
| Richmond HillWind2070RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2070 | 80.1077 | 86.407 | 93.0672 | 99.6902 | 106.3273
| Richmond HillWind2075RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2075 | 80.3103 | 86.668 | 93.4007 | 100.0864 | 106.7862
| Richmond HillWind2080RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2080 | 80.5128 | 86.929 | 93.7342 | 100.4826 | 107.245
| Richmond HillWind2085RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2085 | 80.7154 | 87.1899 | 94.0677 | 100.8789 | 107.7039
| Richmond HillWind2090RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2090 | 81.3364 | 87.9642 | 95.036 | 102.0134 | 109.0088
| Richmond HillWind2095RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2095 | 81.7547 | 88.4776 | 95.6708 | 102.7517 | 109.8548
| Richmond HillWind2100RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2100 | 82.1731 | 88.991 | 96.3056 | 103.49 | 110.7008
| Richmond HillWind2023RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2023 | 79.631 | 85.7311 | 92.1472 | 98.568 | 104.9849
| Richmond HillWind2025RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2025 | 79.6602 | 85.7939 | 92.2484 | 98.7025 | 105.1527
| Richmond HillWind2030RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2030 | 79.6893 | 85.8566 | 92.3496 | 98.837 | 105.3205
| Richmond HillWind2035RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2035 | 79.7184 | 85.9194 | 92.4508 | 98.9716 | 105.4883
| Richmond HillWind2040RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2040 | 79.8482 | 86.0819 | 92.6563 | 99.2111 | 105.768
| Richmond HillWind2045RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2045 | 79.9779 | 86.2445 | 92.8617 | 99.4507 | 106.0477
| Richmond HillWind2050RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2050 | 80.3778 | 86.755 | 93.5119 | 100.2185 | 106.9391
| Richmond HillWind2055RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2055 | 80.6479 | 87.1029 | 93.9565 | 100.7468 | 107.5509
| Richmond HillWind2060RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2060 | 81.3364 | 87.9642 | 95.036 | 102.0134 | 109.0088
| Richmond HillWind2065RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2065 | 81.7547 | 88.4776 | 95.6708 | 102.7517 | 109.8548
| Richmond HillWind2070RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2070 | 82.2976 | 89.1592 | 96.5295 | 103.7656 | 111.0225
| Richmond HillWind2075RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2075 | 82.422 | 89.3275 | 96.7533 | 104.0412 | 111.3441
| Richmond HillWind2080RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2080 | 82.5465 | 89.4958 | 96.9772 | 104.3169 | 111.6657
| Richmond HillWind2085RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2085 | 82.8126 | 89.8722 | 97.4924 | 104.9469 | 112.4156
| Richmond HillWind2090RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2090 | 83.0788 | 90.2487 | 98.0076 | 105.5769 | 113.1655
| Richmond HillWind2095RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2095 | 83.0788 | 90.2487 | 98.0076 | 105.5769 | 113.1655
| Richmond HillWind2100RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2100 | 83.0788 | 90.2487 | 98.0076 | 105.5769 | 113.1655
| RocklandIce Accretion2023RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
| RocklandIce Accretion2025RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
| RocklandIce Accretion2030RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
| RocklandIce Accretion2035RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
| RocklandIce Accretion2040RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
| RocklandIce Accretion2045RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
| RocklandIce Accretion2050RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
| RocklandIce Accretion2055RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
| RocklandIce Accretion2060RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
| RocklandIce Accretion2065RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
| RocklandIce Accretion2070RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
| RocklandIce Accretion2075RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2075 | 20.6423 | 24.7215 | 29.87 | 33.8039 | 37.7496
| RocklandIce Accretion2080RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2080 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
| RocklandIce Accretion2085RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2085 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
| RocklandIce Accretion2090RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2090 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
| RocklandIce Accretion2095RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2095 | 20.9624 | 25.2029 | 30.55 | 34.6401 | 38.7576
| RocklandIce Accretion2100RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2100 | 21.0424 | 25.3233 | 30.72 | 34.8492 | 39.0096
| RocklandIce Accretion2023RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
| RocklandIce Accretion2025RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
| RocklandIce Accretion2030RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
| RocklandIce Accretion2035RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
| RocklandIce Accretion2040RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
| RocklandIce Accretion2045RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
| RocklandIce Accretion2050RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
| RocklandIce Accretion2055RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
| RocklandIce Accretion2060RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
| RocklandIce Accretion2065RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
| RocklandIce Accretion2070RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
| RocklandIce Accretion2075RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2075 | 20.6823 | 24.7817 | 29.955 | 33.9085 | 37.8756
| RocklandIce Accretion2080RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2080 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
| RocklandIce Accretion2085RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2085 | 20.9224 | 25.1428 | 30.465 | 34.5356 | 38.6316
| RocklandIce Accretion2090RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2090 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
| RocklandIce Accretion2095RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2095 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
| RocklandIce Accretion2100RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2100 | 21.439 | 25.9458 | 31.65 | 36.0018 | 40.3326
| RocklandIce Accretion2023RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
| RocklandIce Accretion2025RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2025 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
| RocklandIce Accretion2030RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2030 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
| RocklandIce Accretion2035RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2035 | 20.2074 | 24.0285 | 28.86 | 32.5779 | 36.288
| RocklandIce Accretion2040RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2040 | 20.3257 | 24.2194 | 29.14 | 32.9169 | 36.6912
| RocklandIce Accretion2045RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2045 | 20.444 | 24.4103 | 29.42 | 33.2559 | 37.0944
| RocklandIce Accretion2050RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2050 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
| RocklandIce Accretion2055RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2055 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
| RocklandIce Accretion2060RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2060 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
| RocklandIce Accretion2065RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2065 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
| RocklandIce Accretion2070RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2070 | 21.2372 | 25.7383 | 31.44 | 35.7871 | 40.1184
| RocklandIce Accretion2075RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2075 | 21.0354 | 25.5308 | 31.23 | 35.5724 | 39.9042
| RocklandIce Accretion2080RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2080 | 20.8336 | 25.3233 | 31.02 | 35.3577 | 39.69
| RocklandIce Accretion2085RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2085 | 20.0926 | 24.5016 | 30.09 | 34.3237 | 38.5749
| RocklandIce Accretion2090RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2090 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
| RocklandIce Accretion2095RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2095 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
| RocklandIce Accretion2100RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2100 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
| RocklandWind2023RCP4.5 | Rockland | Wind | RCP4.5 | 2023 | 82.1949 | 88.6062 | 95.3705 | 102.1176 | 108.8632
| RocklandWind2025RCP4.5 | Rockland | Wind | RCP4.5 | 2025 | 82.2263 | 88.643 | 95.4133 | 102.1667 | 108.9173
| RocklandWind2030RCP4.5 | Rockland | Wind | RCP4.5 | 2030 | 82.2578 | 88.6798 | 95.456 | 102.2159 | 108.9715
| RocklandWind2035RCP4.5 | Rockland | Wind | RCP4.5 | 2035 | 82.2892 | 88.7167 | 95.4988 | 102.265 | 109.0256
| RocklandWind2040RCP4.5 | Rockland | Wind | RCP4.5 | 2040 | 82.3207 | 88.7535 | 95.5415 | 102.3141 | 109.0798
| RocklandWind2045RCP4.5 | Rockland | Wind | RCP4.5 | 2045 | 82.3521 | 88.7903 | 95.5842 | 102.3632 | 109.1339
| RocklandWind2050RCP4.5 | Rockland | Wind | RCP4.5 | 2050 | 82.3065 | 88.7211 | 95.4883 | 102.2436 | 108.991
| RocklandWind2055RCP4.5 | Rockland | Wind | RCP4.5 | 2055 | 82.2293 | 88.6151 | 95.3496 | 102.0749 | 108.7938
| RocklandWind2060RCP4.5 | Rockland | Wind | RCP4.5 | 2060 | 82.1522 | 88.509 | 95.2109 | 101.9062 | 108.5967
| RocklandWind2065RCP4.5 | Rockland | Wind | RCP4.5 | 2065 | 82.0751 | 88.403 | 95.0722 | 101.7374 | 108.3996
| RocklandWind2070RCP4.5 | Rockland | Wind | RCP4.5 | 2070 | 81.998 | 88.297 | 94.9335 | 101.5687 | 108.2025
| RocklandWind2075RCP4.5 | Rockland | Wind | RCP4.5 | 2075 | 82.0185 | 88.3309 | 94.9826 | 101.6314 | 108.2801
| RocklandWind2080RCP4.5 | Rockland | Wind | RCP4.5 | 2080 | 82.039 | 88.3647 | 95.0317 | 101.694 | 108.3578
| RocklandWind2085RCP4.5 | Rockland | Wind | RCP4.5 | 2085 | 82.0595 | 88.3986 | 95.0807 | 101.7567 | 108.4354
| RocklandWind2090RCP4.5 | Rockland | Wind | RCP4.5 | 2090 | 82.08 | 88.4325 | 95.1298 | 101.8194 | 108.513
| RocklandWind2095RCP4.5 | Rockland | Wind | RCP4.5 | 2095 | 82.1006 | 88.4663 | 95.1789 | 101.8821 | 108.5906
| RocklandWind2100RCP4.5 | Rockland | Wind | RCP4.5 | 2100 | 82.1211 | 88.5002 | 95.228 | 101.9448 | 108.6682
| RocklandWind2023RCP6.0 | Rockland | Wind | RCP6.0 | 2023 | 82.1949 | 88.6062 | 95.3705 | 102.1176 | 108.8632
| RocklandWind2025RCP6.0 | Rockland | Wind | RCP6.0 | 2025 | 82.2263 | 88.643 | 95.4133 | 102.1667 | 108.9173
| RocklandWind2030RCP6.0 | Rockland | Wind | RCP6.0 | 2030 | 82.2578 | 88.6798 | 95.456 | 102.2159 | 108.9715
| RocklandWind2035RCP6.0 | Rockland | Wind | RCP6.0 | 2035 | 82.2892 | 88.7167 | 95.4988 | 102.265 | 109.0256
| RocklandWind2040RCP6.0 | Rockland | Wind | RCP6.0 | 2040 | 82.3207 | 88.7535 | 95.5415 | 102.3141 | 109.0798
| RocklandWind2045RCP6.0 | Rockland | Wind | RCP6.0 | 2045 | 82.3521 | 88.7903 | 95.5842 | 102.3632 | 109.1339
| RocklandWind2050RCP6.0 | Rockland | Wind | RCP6.0 | 2050 | 82.3065 | 88.7211 | 95.4883 | 102.2436 | 108.991
| RocklandWind2055RCP6.0 | Rockland | Wind | RCP6.0 | 2055 | 82.2293 | 88.6151 | 95.3496 | 102.0749 | 108.7938
| RocklandWind2060RCP6.0 | Rockland | Wind | RCP6.0 | 2060 | 82.1522 | 88.509 | 95.2109 | 101.9062 | 108.5967
| RocklandWind2065RCP6.0 | Rockland | Wind | RCP6.0 | 2065 | 82.0751 | 88.403 | 95.0722 | 101.7374 | 108.3996
| RocklandWind2070RCP6.0 | Rockland | Wind | RCP6.0 | 2070 | 81.998 | 88.297 | 94.9335 | 101.5687 | 108.2025
| RocklandWind2075RCP6.0 | Rockland | Wind | RCP6.0 | 2075 | 82.0288 | 88.3478 | 95.0071 | 101.6627 | 108.319
| RocklandWind2080RCP6.0 | Rockland | Wind | RCP6.0 | 2080 | 82.0595 | 88.3986 | 95.0807 | 101.7567 | 108.4354
| RocklandWind2085RCP6.0 | Rockland | Wind | RCP6.0 | 2085 | 82.0903 | 88.4494 | 95.1544 | 101.8508 | 108.5518
| RocklandWind2090RCP6.0 | Rockland | Wind | RCP6.0 | 2090 | 81.9953 | 88.3412 | 95.0317 | 101.7144 | 108.4011
| RocklandWind2095RCP6.0 | Rockland | Wind | RCP6.0 | 2095 | 81.8695 | 88.1821 | 94.8353 | 101.484 | 108.1339
| RocklandWind2100RCP6.0 | Rockland | Wind | RCP6.0 | 2100 | 81.7437 | 88.0231 | 94.639 | 101.2536 | 107.8668
| RocklandWind2023RCP8.5 | Rockland | Wind | RCP8.5 | 2023 | 82.1949 | 88.6062 | 95.3705 | 102.1176 | 108.8632
| RocklandWind2025RCP8.5 | Rockland | Wind | RCP8.5 | 2025 | 82.2578 | 88.6798 | 95.456 | 102.2159 | 108.9715
| RocklandWind2030RCP8.5 | Rockland | Wind | RCP8.5 | 2030 | 82.3207 | 88.7535 | 95.5415 | 102.3141 | 109.0798
| RocklandWind2035RCP8.5 | Rockland | Wind | RCP8.5 | 2035 | 82.3836 | 88.8271 | 95.627 | 102.4124 | 109.1881
| RocklandWind2040RCP8.5 | Rockland | Wind | RCP8.5 | 2040 | 82.255 | 88.6504 | 95.3958 | 102.1311 | 108.8595
| RocklandWind2045RCP8.5 | Rockland | Wind | RCP8.5 | 2045 | 82.1265 | 88.4737 | 95.1647 | 101.8499 | 108.531
| RocklandWind2050RCP8.5 | Rockland | Wind | RCP8.5 | 2050 | 82.039 | 88.3647 | 95.0317 | 101.694 | 108.3578
| RocklandWind2055RCP8.5 | Rockland | Wind | RCP8.5 | 2055 | 82.08 | 88.4325 | 95.1298 | 101.8194 | 108.513
| RocklandWind2060RCP8.5 | Rockland | Wind | RCP8.5 | 2060 | 81.9953 | 88.3412 | 95.0317 | 101.7144 | 108.4011
| RocklandWind2065RCP8.5 | Rockland | Wind | RCP8.5 | 2065 | 81.8695 | 88.1821 | 94.8353 | 101.484 | 108.1339
| RocklandWind2070RCP8.5 | Rockland | Wind | RCP8.5 | 2070 | 81.823 | 88.1291 | 94.772 | 101.4094 | 108.0509
| RocklandWind2075RCP8.5 | Rockland | Wind | RCP8.5 | 2075 | 81.9023 | 88.2351 | 94.905 | 101.5653 | 108.235
| RocklandWind2080RCP8.5 | Rockland | Wind | RCP8.5 | 2080 | 81.9816 | 88.3412 | 95.038 | 101.7212 | 108.4191
| RocklandWind2085RCP8.5 | Rockland | Wind | RCP8.5 | 2085 | 81.957 | 88.297 | 94.9762 | 101.6449 | 108.3217
| RocklandWind2090RCP8.5 | Rockland | Wind | RCP8.5 | 2090 | 81.9324 | 88.2528 | 94.9145 | 101.5687 | 108.2242
| RocklandWind2095RCP8.5 | Rockland | Wind | RCP8.5 | 2095 | 81.9324 | 88.2528 | 94.9145 | 101.5687 | 108.2242
| RocklandWind2100RCP8.5 | Rockland | Wind | RCP8.5 | 2100 | 81.9324 | 88.2528 | 94.9145 | 101.5687 | 108.2242
| SarniaIce Accretion2023RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2023 | 14.5432 | 17.4931 | 21.208 | 24.0396 | 26.8607
| SarniaIce Accretion2025RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2025 | 14.5917 | 17.56 | 21.3033 | 24.1515 | 26.9947
| SarniaIce Accretion2030RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2030 | 14.6401 | 17.627 | 21.3987 | 24.2634 | 27.1286
| SarniaIce Accretion2035RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2035 | 14.6886 | 17.6939 | 21.494 | 24.3752 | 27.2626
| SarniaIce Accretion2040RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2040 | 14.7371 | 17.7609 | 21.5893 | 24.4871 | 27.3966
| SarniaIce Accretion2045RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2045 | 14.7856 | 17.8278 | 21.6847 | 24.599 | 27.5306
| SarniaIce Accretion2050RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2050 | 14.6167 | 17.6647 | 21.5248 | 24.4374 | 27.3707
| SarniaIce Accretion2055RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2055 | 14.3993 | 17.4346 | 21.2696 | 24.1639 | 27.0769
| SarniaIce Accretion2060RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2060 | 14.1819 | 17.2046 | 21.0144 | 23.8905 | 26.7831
| SarniaIce Accretion2065RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2065 | 13.9645 | 16.9745 | 20.7592 | 23.617 | 26.4892
| SarniaIce Accretion2070RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2070 | 13.7471 | 16.7444 | 20.504 | 23.3435 | 26.1954
| SarniaIce Accretion2075RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2075 | 13.5047 | 16.4675 | 20.1813 | 22.9914 | 25.8073
| SarniaIce Accretion2080RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2080 | 13.2624 | 16.1905 | 19.8587 | 22.6392 | 25.4192
| SarniaIce Accretion2085RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2085 | 13.02 | 15.9136 | 19.536 | 22.287 | 25.0312
| SarniaIce Accretion2090RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2090 | 12.7776 | 15.6366 | 19.2133 | 21.9348 | 24.6431
| SarniaIce Accretion2095RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2095 | 12.5352 | 15.3597 | 18.8907 | 21.5826 | 24.255
| SarniaIce Accretion2100RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2100 | 12.2928 | 15.0828 | 18.568 | 21.2304 | 23.8669
| SarniaIce Accretion2023RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2023 | 14.5432 | 17.4931 | 21.208 | 24.0396 | 26.8607
| SarniaIce Accretion2025RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2025 | 14.5917 | 17.56 | 21.3033 | 24.1515 | 26.9947
| SarniaIce Accretion2030RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2030 | 14.6401 | 17.627 | 21.3987 | 24.2634 | 27.1286
| SarniaIce Accretion2035RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2035 | 14.6886 | 17.6939 | 21.494 | 24.3752 | 27.2626
| SarniaIce Accretion2040RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2040 | 14.7371 | 17.7609 | 21.5893 | 24.4871 | 27.3966
| SarniaIce Accretion2045RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2045 | 14.7856 | 17.8278 | 21.6847 | 24.599 | 27.5306
| SarniaIce Accretion2050RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2050 | 14.6167 | 17.6647 | 21.5248 | 24.4374 | 27.3707
| SarniaIce Accretion2055RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2055 | 14.3993 | 17.4346 | 21.2696 | 24.1639 | 27.0769
| SarniaIce Accretion2060RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2060 | 14.1819 | 17.2046 | 21.0144 | 23.8905 | 26.7831
| SarniaIce Accretion2065RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2065 | 13.9645 | 16.9745 | 20.7592 | 23.617 | 26.4892
| SarniaIce Accretion2070RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2070 | 13.7471 | 16.7444 | 20.504 | 23.3435 | 26.1954
| SarniaIce Accretion2075RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2075 | 13.3836 | 16.329 | 20.02 | 22.8153 | 25.6133
| SarniaIce Accretion2080RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2080 | 13.02 | 15.9136 | 19.536 | 22.287 | 25.0312
| SarniaIce Accretion2085RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2085 | 12.6564 | 15.4982 | 19.052 | 21.7587 | 24.449
| SarniaIce Accretion2090RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2090 | 11.7774 | 14.4802 | 17.864 | 20.4349 | 22.9891
| SarniaIce Accretion2095RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2095 | 11.262 | 13.8776 | 17.16 | 19.6394 | 22.1113
| SarniaIce Accretion2100RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2100 | 10.7466 | 13.275 | 16.456 | 18.8439 | 21.2335
| SarniaIce Accretion2023RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2023 | 14.5432 | 17.4931 | 21.208 | 24.0396 | 26.8607
| SarniaIce Accretion2025RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2025 | 14.6401 | 17.627 | 21.3987 | 24.2634 | 27.1286
| SarniaIce Accretion2030RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2030 | 14.7371 | 17.7609 | 21.5893 | 24.4871 | 27.3966
| SarniaIce Accretion2035RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2035 | 14.834 | 17.8948 | 21.78 | 24.7108 | 27.6646
| SarniaIce Accretion2040RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2040 | 14.4717 | 17.5113 | 21.3547 | 24.2551 | 27.1748
| SarniaIce Accretion2045RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2045 | 14.1094 | 17.1279 | 20.9293 | 23.7993 | 26.6851
| SarniaIce Accretion2050RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2050 | 13.2624 | 16.1905 | 19.8587 | 22.6392 | 25.4192
| SarniaIce Accretion2055RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2055 | 12.7776 | 15.6366 | 19.2133 | 21.9348 | 24.6431
| SarniaIce Accretion2060RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2060 | 11.7774 | 14.4802 | 17.864 | 20.4349 | 22.9891
| SarniaIce Accretion2065RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2065 | 11.262 | 13.8776 | 17.16 | 19.6394 | 22.1113
| SarniaIce Accretion2070RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2070 | 10.3231 | 12.7942 | 15.8987 | 18.2307 | 20.559
| SarniaIce Accretion2075RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2075 | 9.8996 | 12.3133 | 15.3413 | 17.6175 | 19.8845
| SarniaIce Accretion2080RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2080 | 9.476 | 11.8325 | 14.784 | 17.0042 | 19.21
| SarniaIce Accretion2085RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2085 | 8.6647 | 10.8647 | 13.596 | 15.6618 | 17.7131
| SarniaIce Accretion2090RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2090 | 7.8533 | 9.8969 | 12.408 | 14.3194 | 16.2162
| SarniaIce Accretion2095RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2095 | 7.8533 | 9.8969 | 12.408 | 14.3194 | 16.2162
| SarniaIce Accretion2100RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2100 | 7.8533 | 9.8969 | 12.408 | 14.3194 | 16.2162
| SarniaWind2023RCP4.5 | Sarnia | Wind | RCP4.5 | 2023 | 85.0444 | 91.6139 | 98.5292 | 105.4367 | 112.3456
| SarniaWind2025RCP4.5 | Sarnia | Wind | RCP4.5 | 2025 | 85.105 | 91.6838 | 98.6109 | 105.5311 | 112.4499
| SarniaWind2030RCP4.5 | Sarnia | Wind | RCP4.5 | 2030 | 85.1657 | 91.7537 | 98.6925 | 105.6255 | 112.5542
| SarniaWind2035RCP4.5 | Sarnia | Wind | RCP4.5 | 2035 | 85.2263 | 91.8236 | 98.7742 | 105.7199 | 112.6584
| SarniaWind2040RCP4.5 | Sarnia | Wind | RCP4.5 | 2040 | 85.287 | 91.8934 | 98.8559 | 105.8142 | 112.7627
| SarniaWind2045RCP4.5 | Sarnia | Wind | RCP4.5 | 2045 | 85.3476 | 91.9633 | 98.9375 | 105.9086 | 112.867
| SarniaWind2050RCP4.5 | Sarnia | Wind | RCP4.5 | 2050 | 85.4083 | 92.0332 | 99.0192 | 106.0009 | 112.9713
| SarniaWind2055RCP4.5 | Sarnia | Wind | RCP4.5 | 2055 | 85.4083 | 92.0332 | 99.0192 | 105.9988 | 112.9713
| SarniaWind2060RCP4.5 | Sarnia | Wind | RCP4.5 | 2060 | 85.4083 | 92.0332 | 99.0192 | 105.9967 | 112.9713
| SarniaWind2065RCP4.5 | Sarnia | Wind | RCP4.5 | 2065 | 85.4083 | 92.0332 | 99.0192 | 105.9946 | 112.9713
| SarniaWind2070RCP4.5 | Sarnia | Wind | RCP4.5 | 2070 | 85.4083 | 92.0332 | 99.0192 | 105.9925 | 112.9713
| SarniaWind2075RCP4.5 | Sarnia | Wind | RCP4.5 | 2075 | 85.538 | 92.1957 | 99.2201 | 106.2284 | 113.2413
| SarniaWind2080RCP4.5 | Sarnia | Wind | RCP4.5 | 2080 | 85.6678 | 92.3582 | 99.421 | 106.4644 | 113.5112
| SarniaWind2085RCP4.5 | Sarnia | Wind | RCP4.5 | 2085 | 85.7975 | 92.5208 | 99.6219 | 106.7003 | 113.7812
| SarniaWind2090RCP4.5 | Sarnia | Wind | RCP4.5 | 2090 | 85.9273 | 92.6833 | 99.8228 | 106.9362 | 114.0512
| SarniaWind2095RCP4.5 | Sarnia | Wind | RCP4.5 | 2095 | 86.057 | 92.8458 | 100.0237 | 107.1722 | 114.3212
| SarniaWind2100RCP4.5 | Sarnia | Wind | RCP4.5 | 2100 | 86.1868 | 93.0084 | 100.2246 | 107.4081 | 114.5912
| SarniaWind2023RCP6.0 | Sarnia | Wind | RCP6.0 | 2023 | 85.0444 | 91.6139 | 98.5292 | 105.4367 | 112.3456
| SarniaWind2025RCP6.0 | Sarnia | Wind | RCP6.0 | 2025 | 85.105 | 91.6838 | 98.6109 | 105.5311 | 112.4499
| SarniaWind2030RCP6.0 | Sarnia | Wind | RCP6.0 | 2030 | 85.1657 | 91.7537 | 98.6925 | 105.6255 | 112.5542
| SarniaWind2035RCP6.0 | Sarnia | Wind | RCP6.0 | 2035 | 85.2263 | 91.8236 | 98.7742 | 105.7199 | 112.6584
| SarniaWind2040RCP6.0 | Sarnia | Wind | RCP6.0 | 2040 | 85.287 | 91.8934 | 98.8559 | 105.8142 | 112.7627
| SarniaWind2045RCP6.0 | Sarnia | Wind | RCP6.0 | 2045 | 85.3476 | 91.9633 | 98.9375 | 105.9086 | 112.867
| SarniaWind2050RCP6.0 | Sarnia | Wind | RCP6.0 | 2050 | 85.4083 | 92.0332 | 99.0192 | 106.0009 | 112.9713
| SarniaWind2055RCP6.0 | Sarnia | Wind | RCP6.0 | 2055 | 85.4083 | 92.0332 | 99.0192 | 105.9988 | 112.9713
| SarniaWind2060RCP6.0 | Sarnia | Wind | RCP6.0 | 2060 | 85.4083 | 92.0332 | 99.0192 | 105.9967 | 112.9713
| SarniaWind2065RCP6.0 | Sarnia | Wind | RCP6.0 | 2065 | 85.4083 | 92.0332 | 99.0192 | 105.9946 | 112.9713
| SarniaWind2070RCP6.0 | Sarnia | Wind | RCP6.0 | 2070 | 85.4083 | 92.0332 | 99.0192 | 105.9925 | 112.9713
| SarniaWind2075RCP6.0 | Sarnia | Wind | RCP6.0 | 2075 | 85.6029 | 92.277 | 99.3205 | 106.3464 | 113.3762
| SarniaWind2080RCP6.0 | Sarnia | Wind | RCP6.0 | 2080 | 85.7975 | 92.5208 | 99.6219 | 106.7003 | 113.7812
| SarniaWind2085RCP6.0 | Sarnia | Wind | RCP6.0 | 2085 | 85.9921 | 92.7646 | 99.9232 | 107.0542 | 114.1862
| SarniaWind2090RCP6.0 | Sarnia | Wind | RCP6.0 | 2090 | 86.4463 | 93.3304 | 100.6264 | 107.8765 | 115.1275
| SarniaWind2095RCP6.0 | Sarnia | Wind | RCP6.0 | 2095 | 86.7058 | 93.6524 | 101.0282 | 108.3448 | 115.6637
| SarniaWind2100RCP6.0 | Sarnia | Wind | RCP6.0 | 2100 | 86.9653 | 93.9745 | 101.43 | 108.8132 | 116.2
| SarniaWind2023RCP8.5 | Sarnia | Wind | RCP8.5 | 2023 | 85.0444 | 91.6139 | 98.5292 | 105.4367 | 112.3456
| SarniaWind2025RCP8.5 | Sarnia | Wind | RCP8.5 | 2025 | 85.1657 | 91.7537 | 98.6925 | 105.6255 | 112.5542
| SarniaWind2030RCP8.5 | Sarnia | Wind | RCP8.5 | 2030 | 85.287 | 91.8934 | 98.8559 | 105.8142 | 112.7627
| SarniaWind2035RCP8.5 | Sarnia | Wind | RCP8.5 | 2035 | 85.4083 | 92.0332 | 99.0192 | 106.003 | 112.9713
| SarniaWind2040RCP8.5 | Sarnia | Wind | RCP8.5 | 2040 | 85.4083 | 92.0332 | 99.0192 | 105.9995 | 112.9713
| SarniaWind2045RCP8.5 | Sarnia | Wind | RCP8.5 | 2045 | 85.4083 | 92.0332 | 99.0192 | 105.996 | 112.9713
| SarniaWind2050RCP8.5 | Sarnia | Wind | RCP8.5 | 2050 | 85.6678 | 92.3582 | 99.421 | 106.4644 | 113.5112
| SarniaWind2055RCP8.5 | Sarnia | Wind | RCP8.5 | 2055 | 85.9273 | 92.6833 | 99.8228 | 106.9362 | 114.0512
| SarniaWind2060RCP8.5 | Sarnia | Wind | RCP8.5 | 2060 | 86.4463 | 93.3304 | 100.6264 | 107.8765 | 115.1275
| SarniaWind2065RCP8.5 | Sarnia | Wind | RCP8.5 | 2065 | 86.7058 | 93.6524 | 101.0282 | 108.3448 | 115.6637
| SarniaWind2070RCP8.5 | Sarnia | Wind | RCP8.5 | 2070 | 87.2474 | 94.3238 | 101.8612 | 109.3131 | 116.7697
| SarniaWind2075RCP8.5 | Sarnia | Wind | RCP8.5 | 2075 | 87.5294 | 94.6732 | 102.2924 | 109.8129 | 117.3395
| SarniaWind2080RCP8.5 | Sarnia | Wind | RCP8.5 | 2080 | 87.8115 | 95.0226 | 102.7236 | 110.3127 | 117.9093
| SarniaWind2085RCP8.5 | Sarnia | Wind | RCP8.5 | 2085 | 87.968 | 95.2367 | 103.0176 | 110.6692 | 118.3394
| SarniaWind2090RCP8.5 | Sarnia | Wind | RCP8.5 | 2090 | 88.1246 | 95.4509 | 103.3116 | 111.0258 | 118.7695
| SarniaWind2095RCP8.5 | Sarnia | Wind | RCP8.5 | 2095 | 88.1246 | 95.4509 | 103.3116 | 111.0258 | 118.7695
| SarniaWind2100RCP8.5 | Sarnia | Wind | RCP8.5 | 2100 | 88.1246 | 95.4509 | 103.3116 | 111.0258 | 118.7695
| Sault Ste. MarieIce Accretion2023RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2023 | 14.8647 | 17.8218 | 21.582 | 24.4374 | 27.3042
| Sault Ste. MarieIce Accretion2025RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2025 | 14.8111 | 17.77 | 21.5307 | 24.3877 | 27.258
| Sault Ste. MarieIce Accretion2030RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2030 | 14.7575 | 17.7183 | 21.4793 | 24.3379 | 27.2118
| Sault Ste. MarieIce Accretion2035RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2035 | 14.7039 | 17.6665 | 21.428 | 24.2882 | 27.1656
| Sault Ste. MarieIce Accretion2040RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2040 | 14.6503 | 17.6148 | 21.3767 | 24.2385 | 27.1194
| Sault Ste. MarieIce Accretion2045RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2045 | 14.5968 | 17.5631 | 21.3253 | 24.1888 | 27.0732
| Sault Ste. MarieIce Accretion2050RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2050 | 14.6473 | 17.6574 | 21.4676 | 24.3727 | 27.2876
| Sault Ste. MarieIce Accretion2055RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2055 | 14.7514 | 17.8035 | 21.6612 | 24.6064 | 27.5481
| Sault Ste. MarieIce Accretion2060RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2060 | 14.8555 | 17.9496 | 21.8548 | 24.8401 | 27.8087
| Sault Ste. MarieIce Accretion2065RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2065 | 14.9596 | 18.0957 | 22.0484 | 25.0738 | 28.0693
| Sault Ste. MarieIce Accretion2070RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2070 | 15.0637 | 18.2417 | 22.242 | 25.3075 | 28.3298
| Sault Ste. MarieIce Accretion2075RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2075 | 15.028 | 18.2265 | 22.2493 | 25.3241 | 28.3668
| Sault Ste. MarieIce Accretion2080RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2080 | 14.9922 | 18.2113 | 22.2567 | 25.3406 | 28.4038
| Sault Ste. MarieIce Accretion2085RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2085 | 14.9565 | 18.1961 | 22.264 | 25.3572 | 28.4407
| Sault Ste. MarieIce Accretion2090RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2090 | 14.9208 | 18.1809 | 22.2713 | 25.3738 | 28.4777
| Sault Ste. MarieIce Accretion2095RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2095 | 14.8851 | 18.1657 | 22.2787 | 25.3903 | 28.5146
| Sault Ste. MarieIce Accretion2100RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2100 | 14.8494 | 18.1504 | 22.286 | 25.4069 | 28.5516
| Sault Ste. MarieIce Accretion2023RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2023 | 14.8647 | 17.8218 | 21.582 | 24.4374 | 27.3042
| Sault Ste. MarieIce Accretion2025RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2025 | 14.8111 | 17.77 | 21.5307 | 24.3877 | 27.258
| Sault Ste. MarieIce Accretion2030RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2030 | 14.7575 | 17.7183 | 21.4793 | 24.3379 | 27.2118
| Sault Ste. MarieIce Accretion2035RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2035 | 14.7039 | 17.6665 | 21.428 | 24.2882 | 27.1656
| Sault Ste. MarieIce Accretion2040RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2040 | 14.6503 | 17.6148 | 21.3767 | 24.2385 | 27.1194
| Sault Ste. MarieIce Accretion2045RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2045 | 14.5968 | 17.5631 | 21.3253 | 24.1888 | 27.0732
| Sault Ste. MarieIce Accretion2050RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2050 | 14.6473 | 17.6574 | 21.4676 | 24.3727 | 27.2876
| Sault Ste. MarieIce Accretion2055RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2055 | 14.7514 | 17.8035 | 21.6612 | 24.6064 | 27.5481
| Sault Ste. MarieIce Accretion2060RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2060 | 14.8555 | 17.9496 | 21.8548 | 24.8401 | 27.8087
| Sault Ste. MarieIce Accretion2065RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2065 | 14.9596 | 18.0957 | 22.0484 | 25.0738 | 28.0693
| Sault Ste. MarieIce Accretion2070RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2070 | 15.0637 | 18.2417 | 22.242 | 25.3075 | 28.3298
| Sault Ste. MarieIce Accretion2075RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2075 | 15.0101 | 18.2189 | 22.253 | 25.3323 | 28.3853
| Sault Ste. MarieIce Accretion2080RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2080 | 14.9565 | 18.1961 | 22.264 | 25.3572 | 28.4407
| Sault Ste. MarieIce Accretion2085RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2085 | 14.9029 | 18.1733 | 22.275 | 25.3821 | 28.4962
| Sault Ste. MarieIce Accretion2090RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2090 | 14.8494 | 18.193 | 22.3813 | 25.5478 | 28.7179
| Sault Ste. MarieIce Accretion2095RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2095 | 14.8494 | 18.2357 | 22.4767 | 25.6887 | 28.8842
| Sault Ste. MarieIce Accretion2100RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2100 | 14.8494 | 18.2783 | 22.572 | 25.8295 | 29.0506
| Sault Ste. MarieIce Accretion2023RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2023 | 14.8647 | 17.8218 | 21.582 | 24.4374 | 27.3042
| Sault Ste. MarieIce Accretion2025RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2025 | 14.7575 | 17.7183 | 21.4793 | 24.3379 | 27.2118
| Sault Ste. MarieIce Accretion2030RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2030 | 14.6503 | 17.6148 | 21.3767 | 24.2385 | 27.1194
| Sault Ste. MarieIce Accretion2035RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2035 | 14.5432 | 17.5113 | 21.274 | 24.1391 | 27.027
| Sault Ste. MarieIce Accretion2040RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2040 | 14.7167 | 17.7548 | 21.5967 | 24.5285 | 27.4613
| Sault Ste. MarieIce Accretion2045RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2045 | 14.8902 | 17.9983 | 21.9193 | 24.918 | 27.8956
| Sault Ste. MarieIce Accretion2050RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2050 | 14.9922 | 18.2113 | 22.2567 | 25.3406 | 28.4038
| Sault Ste. MarieIce Accretion2055RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2055 | 14.9208 | 18.1809 | 22.2713 | 25.3738 | 28.4777
| Sault Ste. MarieIce Accretion2060RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2060 | 14.8494 | 18.193 | 22.3813 | 25.5478 | 28.7179
| Sault Ste. MarieIce Accretion2065RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2065 | 14.8494 | 18.2357 | 22.4767 | 25.6887 | 28.8842
| Sault Ste. MarieIce Accretion2070RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2070 | 14.3442 | 17.6757 | 21.8533 | 25.0257 | 28.1635
| Sault Ste. MarieIce Accretion2075RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2075 | 13.839 | 17.0731 | 21.1347 | 24.2219 | 27.2765
| Sault Ste. MarieIce Accretion2080RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2080 | 13.3338 | 16.4705 | 20.416 | 23.4181 | 26.3894
| Sault Ste. MarieIce Accretion2085RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2085 | 13.1348 | 16.2605 | 20.185 | 23.1695 | 26.1261
| Sault Ste. MarieIce Accretion2090RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2090 | 12.9358 | 16.0505 | 19.954 | 22.9209 | 25.8628
| Sault Ste. MarieIce Accretion2095RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2095 | 12.9358 | 16.0505 | 19.954 | 22.9209 | 25.8628
| Sault Ste. MarieIce Accretion2100RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2100 | 12.9358 | 16.0505 | 19.954 | 22.9209 | 25.8628
| Sault Ste. MarieWind2023RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2023 | 85.4252 | 92.097 | 99.1466 | 106.1707 | 113.1947
| Sault Ste. MarieWind2025RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2025 | 85.4689 | 92.1486 | 99.2087 | 106.2424 | 113.2748
| Sault Ste. MarieWind2030RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2030 | 85.5126 | 92.2003 | 99.2707 | 106.3141 | 113.3548
| Sault Ste. MarieWind2035RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2035 | 85.5563 | 92.2519 | 99.3328 | 106.3857 | 113.4349
| Sault Ste. MarieWind2040RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2040 | 85.6001 | 92.3036 | 99.3949 | 106.4574 | 113.515
| Sault Ste. MarieWind2045RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2045 | 85.6438 | 92.3552 | 99.4569 | 106.529 | 113.595
| Sault Ste. MarieWind2050RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2050 | 85.6655 | 92.3649 | 99.4484 | 106.5063 | 113.5589
| Sault Ste. MarieWind2055RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2055 | 85.6435 | 92.323 | 99.3779 | 106.4119 | 113.4427
| Sault Ste. MarieWind2060RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2060 | 85.6215 | 92.2811 | 99.3073 | 106.3176 | 113.3265
| Sault Ste. MarieWind2065RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2065 | 85.5995 | 92.2391 | 99.2368 | 106.2232 | 113.2103
| Sault Ste. MarieWind2070RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2070 | 85.5775 | 92.1972 | 99.1662 | 106.1288 | 113.0942
| Sault Ste. MarieWind2075RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2075 | 85.6156 | 92.2443 | 99.2266 | 106.1987 | 113.1761
| Sault Ste. MarieWind2080RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2080 | 85.6537 | 92.2914 | 99.2871 | 106.2686 | 113.258
| Sault Ste. MarieWind2085RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2085 | 85.6917 | 92.3385 | 99.3475 | 106.3385 | 113.3399
| Sault Ste. MarieWind2090RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2090 | 85.7298 | 92.3856 | 99.4079 | 106.4084 | 113.4219
| Sault Ste. MarieWind2095RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2095 | 85.7679 | 92.4327 | 99.4684 | 106.4783 | 113.5038
| Sault Ste. MarieWind2100RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2100 | 85.806 | 92.4798 | 99.5288 | 106.5482 | 113.5857
| Sault Ste. MarieWind2023RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2023 | 85.4252 | 92.097 | 99.1466 | 106.1707 | 113.1947
| Sault Ste. MarieWind2025RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2025 | 85.4689 | 92.1486 | 99.2087 | 106.2424 | 113.2748
| Sault Ste. MarieWind2030RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2030 | 85.5126 | 92.2003 | 99.2707 | 106.3141 | 113.3548
| Sault Ste. MarieWind2035RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2035 | 85.5563 | 92.2519 | 99.3328 | 106.3857 | 113.4349
| Sault Ste. MarieWind2040RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2040 | 85.6001 | 92.3036 | 99.3949 | 106.4574 | 113.515
| Sault Ste. MarieWind2045RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2045 | 85.6438 | 92.3552 | 99.4569 | 106.529 | 113.595
| Sault Ste. MarieWind2050RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2050 | 85.6655 | 92.3649 | 99.4484 | 106.5063 | 113.5589
| Sault Ste. MarieWind2055RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2055 | 85.6435 | 92.323 | 99.3779 | 106.4119 | 113.4427
| Sault Ste. MarieWind2060RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2060 | 85.6215 | 92.2811 | 99.3073 | 106.3176 | 113.3265
| Sault Ste. MarieWind2065RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2065 | 85.5995 | 92.2391 | 99.2368 | 106.2232 | 113.2103
| Sault Ste. MarieWind2070RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2070 | 85.5775 | 92.1972 | 99.1662 | 106.1288 | 113.0942
| Sault Ste. MarieWind2075RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2075 | 85.6346 | 92.2679 | 99.2569 | 106.2337 | 113.217
| Sault Ste. MarieWind2080RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2080 | 85.6917 | 92.3385 | 99.3475 | 106.3385 | 113.3399
| Sault Ste. MarieWind2085RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2085 | 85.7489 | 92.4091 | 99.4382 | 106.4434 | 113.4628
| Sault Ste. MarieWind2090RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2090 | 86.184 | 92.9324 | 100.0678 | 107.1669 | 114.2784
| Sault Ste. MarieWind2095RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2095 | 86.5619 | 93.3851 | 100.6068 | 107.7856 | 114.9711
| Sault Ste. MarieWind2100RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2100 | 86.9399 | 93.8377 | 101.1458 | 108.4043 | 115.6637
| Sault Ste. MarieWind2023RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2023 | 85.4252 | 92.097 | 99.1466 | 106.1707 | 113.1947
| Sault Ste. MarieWind2025RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2025 | 85.5126 | 92.2003 | 99.2707 | 106.3141 | 113.3548
| Sault Ste. MarieWind2030RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2030 | 85.6001 | 92.3036 | 99.3949 | 106.4574 | 113.515
| Sault Ste. MarieWind2035RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2035 | 85.6875 | 92.4068 | 99.519 | 106.6007 | 113.6751
| Sault Ste. MarieWind2040RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2040 | 85.6508 | 92.337 | 99.4014 | 106.4434 | 113.4815
| Sault Ste. MarieWind2045RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2045 | 85.6142 | 92.2671 | 99.2838 | 106.2861 | 113.2878
| Sault Ste. MarieWind2050RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2050 | 85.6537 | 92.2914 | 99.2871 | 106.2686 | 113.258
| Sault Ste. MarieWind2055RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2055 | 85.7298 | 92.3856 | 99.4079 | 106.4084 | 113.4219
| Sault Ste. MarieWind2060RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2060 | 86.184 | 92.9324 | 100.0678 | 107.1669 | 114.2784
| Sault Ste. MarieWind2065RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2065 | 86.5619 | 93.3851 | 100.6068 | 107.7856 | 114.9711
| Sault Ste. MarieWind2070RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2070 | 87.1007 | 94.0261 | 101.3679 | 108.6559 | 115.9467
| Sault Ste. MarieWind2075RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2075 | 87.2615 | 94.2145 | 101.5901 | 108.9076 | 116.2298
| Sault Ste. MarieWind2080RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2080 | 87.4222 | 94.4028 | 101.8122 | 109.1593 | 116.5128
| Sault Ste. MarieWind2085RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2085 | 87.5576 | 94.5623 | 102.0033 | 109.3742 | 116.753
| Sault Ste. MarieWind2090RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2090 | 87.693 | 94.7218 | 102.1944 | 109.5892 | 116.9932
| Sault Ste. MarieWind2095RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2095 | 87.693 | 94.7218 | 102.1944 | 109.5892 | 116.9932
| Sault Ste. MarieWind2100RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2100 | 87.693 | 94.7218 | 102.1944 | 109.5892 | 116.9932
| ScarboroughIce Accretion2023RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| ScarboroughIce Accretion2025RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| ScarboroughIce Accretion2030RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| ScarboroughIce Accretion2035RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| ScarboroughIce Accretion2040RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| ScarboroughIce Accretion2045RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| ScarboroughIce Accretion2050RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| ScarboroughIce Accretion2055RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| ScarboroughIce Accretion2060RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| ScarboroughIce Accretion2065RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| ScarboroughIce Accretion2070RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| ScarboroughIce Accretion2075RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
| ScarboroughIce Accretion2080RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| ScarboroughIce Accretion2085RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| ScarboroughIce Accretion2090RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| ScarboroughIce Accretion2095RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
| ScarboroughIce Accretion2100RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
| ScarboroughIce Accretion2023RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| ScarboroughIce Accretion2025RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| ScarboroughIce Accretion2030RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| ScarboroughIce Accretion2035RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| ScarboroughIce Accretion2040RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| ScarboroughIce Accretion2045RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| ScarboroughIce Accretion2050RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| ScarboroughIce Accretion2055RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| ScarboroughIce Accretion2060RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| ScarboroughIce Accretion2065RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| ScarboroughIce Accretion2070RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| ScarboroughIce Accretion2075RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
| ScarboroughIce Accretion2080RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| ScarboroughIce Accretion2085RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
| ScarboroughIce Accretion2090RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| ScarboroughIce Accretion2095RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| ScarboroughIce Accretion2100RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
| ScarboroughIce Accretion2023RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| ScarboroughIce Accretion2025RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| ScarboroughIce Accretion2030RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| ScarboroughIce Accretion2035RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
| ScarboroughIce Accretion2040RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
| ScarboroughIce Accretion2045RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
| ScarboroughIce Accretion2050RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| ScarboroughIce Accretion2055RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| ScarboroughIce Accretion2060RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| ScarboroughIce Accretion2065RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| ScarboroughIce Accretion2070RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
| ScarboroughIce Accretion2075RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
| ScarboroughIce Accretion2080RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
| ScarboroughIce Accretion2085RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
| ScarboroughIce Accretion2090RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| ScarboroughIce Accretion2095RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| ScarboroughIce Accretion2100RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| ScarboroughWind2023RCP4.5 | Scarborough | Wind | RCP4.5 | 2023 | 83.0933 | 89.4586 | 96.1536 | 102.8535 | 109.5494
| ScarboroughWind2025RCP4.5 | Scarborough | Wind | RCP4.5 | 2025 | 83.1085 | 89.4913 | 96.2064 | 102.9237 | 109.637
| ScarboroughWind2030RCP4.5 | Scarborough | Wind | RCP4.5 | 2030 | 83.1237 | 89.524 | 96.2592 | 102.9939 | 109.7245
| ScarboroughWind2035RCP4.5 | Scarborough | Wind | RCP4.5 | 2035 | 83.1389 | 89.5568 | 96.312 | 103.0641 | 109.8121
| ScarboroughWind2040RCP4.5 | Scarborough | Wind | RCP4.5 | 2040 | 83.154 | 89.5895 | 96.3648 | 103.1343 | 109.8996
| ScarboroughWind2045RCP4.5 | Scarborough | Wind | RCP4.5 | 2045 | 83.1692 | 89.6222 | 96.4176 | 103.2045 | 109.9872
| ScarboroughWind2050RCP4.5 | Scarborough | Wind | RCP4.5 | 2050 | 83.2657 | 89.7568 | 96.599 | 103.4247 | 110.2499
| ScarboroughWind2055RCP4.5 | Scarborough | Wind | RCP4.5 | 2055 | 83.3469 | 89.8585 | 96.7277 | 103.5746 | 110.425
| ScarboroughWind2060RCP4.5 | Scarborough | Wind | RCP4.5 | 2060 | 83.4282 | 89.9603 | 96.8563 | 103.7246 | 110.6001
| ScarboroughWind2065RCP4.5 | Scarborough | Wind | RCP4.5 | 2065 | 83.5094 | 90.0621 | 96.985 | 103.8746 | 110.7752
| ScarboroughWind2070RCP4.5 | Scarborough | Wind | RCP4.5 | 2070 | 83.5906 | 90.1639 | 97.1136 | 104.0245 | 110.9503
| ScarboroughWind2075RCP4.5 | Scarborough | Wind | RCP4.5 | 2075 | 83.7315 | 90.3454 | 97.3456 | 104.3002 | 111.2695
| ScarboroughWind2080RCP4.5 | Scarborough | Wind | RCP4.5 | 2080 | 83.8725 | 90.5269 | 97.5776 | 104.5758 | 111.5887
| ScarboroughWind2085RCP4.5 | Scarborough | Wind | RCP4.5 | 2085 | 84.0134 | 90.7085 | 97.8096 | 104.8514 | 111.9079
| ScarboroughWind2090RCP4.5 | Scarborough | Wind | RCP4.5 | 2090 | 84.1543 | 90.89 | 98.0416 | 105.1271 | 112.2271
| ScarboroughWind2095RCP4.5 | Scarborough | Wind | RCP4.5 | 2095 | 84.2952 | 91.0716 | 98.2736 | 105.4027 | 112.5463
| ScarboroughWind2100RCP4.5 | Scarborough | Wind | RCP4.5 | 2100 | 84.4361 | 91.2531 | 98.5056 | 105.6783 | 112.8655
| ScarboroughWind2023RCP6.0 | Scarborough | Wind | RCP6.0 | 2023 | 83.0933 | 89.4586 | 96.1536 | 102.8535 | 109.5494
| ScarboroughWind2025RCP6.0 | Scarborough | Wind | RCP6.0 | 2025 | 83.1085 | 89.4913 | 96.2064 | 102.9237 | 109.637
| ScarboroughWind2030RCP6.0 | Scarborough | Wind | RCP6.0 | 2030 | 83.1237 | 89.524 | 96.2592 | 102.9939 | 109.7245
| ScarboroughWind2035RCP6.0 | Scarborough | Wind | RCP6.0 | 2035 | 83.1389 | 89.5568 | 96.312 | 103.0641 | 109.8121
| ScarboroughWind2040RCP6.0 | Scarborough | Wind | RCP6.0 | 2040 | 83.154 | 89.5895 | 96.3648 | 103.1343 | 109.8996
| ScarboroughWind2045RCP6.0 | Scarborough | Wind | RCP6.0 | 2045 | 83.1692 | 89.6222 | 96.4176 | 103.2045 | 109.9872
| ScarboroughWind2050RCP6.0 | Scarborough | Wind | RCP6.0 | 2050 | 83.2657 | 89.7568 | 96.599 | 103.4247 | 110.2499
| ScarboroughWind2055RCP6.0 | Scarborough | Wind | RCP6.0 | 2055 | 83.3469 | 89.8585 | 96.7277 | 103.5746 | 110.425
| ScarboroughWind2060RCP6.0 | Scarborough | Wind | RCP6.0 | 2060 | 83.4282 | 89.9603 | 96.8563 | 103.7246 | 110.6001
| ScarboroughWind2065RCP6.0 | Scarborough | Wind | RCP6.0 | 2065 | 83.5094 | 90.0621 | 96.985 | 103.8746 | 110.7752
| ScarboroughWind2070RCP6.0 | Scarborough | Wind | RCP6.0 | 2070 | 83.5906 | 90.1639 | 97.1136 | 104.0245 | 110.9503
| ScarboroughWind2075RCP6.0 | Scarborough | Wind | RCP6.0 | 2075 | 83.802 | 90.4362 | 97.4616 | 104.438 | 111.4291
| ScarboroughWind2080RCP6.0 | Scarborough | Wind | RCP6.0 | 2080 | 84.0134 | 90.7085 | 97.8096 | 104.8514 | 111.9079
| ScarboroughWind2085RCP6.0 | Scarborough | Wind | RCP6.0 | 2085 | 84.2248 | 90.9808 | 98.1576 | 105.2649 | 112.3867
| ScarboroughWind2090RCP6.0 | Scarborough | Wind | RCP6.0 | 2090 | 84.8727 | 91.7888 | 99.168 | 106.4487 | 113.7483
| ScarboroughWind2095RCP6.0 | Scarborough | Wind | RCP6.0 | 2095 | 85.3093 | 92.3244 | 99.8304 | 107.2191 | 114.6311
| ScarboroughWind2100RCP6.0 | Scarborough | Wind | RCP6.0 | 2100 | 85.7459 | 92.8601 | 100.4928 | 107.9895 | 115.5139
| ScarboroughWind2023RCP8.5 | Scarborough | Wind | RCP8.5 | 2023 | 83.0933 | 89.4586 | 96.1536 | 102.8535 | 109.5494
| ScarboroughWind2025RCP8.5 | Scarborough | Wind | RCP8.5 | 2025 | 83.1237 | 89.524 | 96.2592 | 102.9939 | 109.7245
| ScarboroughWind2030RCP8.5 | Scarborough | Wind | RCP8.5 | 2030 | 83.154 | 89.5895 | 96.3648 | 103.1343 | 109.8996
| ScarboroughWind2035RCP8.5 | Scarborough | Wind | RCP8.5 | 2035 | 83.1844 | 89.655 | 96.4704 | 103.2747 | 110.0748
| ScarboroughWind2040RCP8.5 | Scarborough | Wind | RCP8.5 | 2040 | 83.3198 | 89.8246 | 96.6848 | 103.5246 | 110.3666
| ScarboroughWind2045RCP8.5 | Scarborough | Wind | RCP8.5 | 2045 | 83.4552 | 89.9942 | 96.8992 | 103.7746 | 110.6584
| ScarboroughWind2050RCP8.5 | Scarborough | Wind | RCP8.5 | 2050 | 83.8725 | 90.5269 | 97.5776 | 104.5758 | 111.5887
| ScarboroughWind2055RCP8.5 | Scarborough | Wind | RCP8.5 | 2055 | 84.1543 | 90.89 | 98.0416 | 105.1271 | 112.2271
| ScarboroughWind2060RCP8.5 | Scarborough | Wind | RCP8.5 | 2060 | 84.8727 | 91.7888 | 99.168 | 106.4487 | 113.7483
| ScarboroughWind2065RCP8.5 | Scarborough | Wind | RCP8.5 | 2065 | 85.3093 | 92.3244 | 99.8304 | 107.2191 | 114.6311
| ScarboroughWind2070RCP8.5 | Scarborough | Wind | RCP8.5 | 2070 | 85.8757 | 93.0357 | 100.7264 | 108.2772 | 115.8495
| ScarboroughWind2075RCP8.5 | Scarborough | Wind | RCP8.5 | 2075 | 86.0056 | 93.2113 | 100.96 | 108.5648 | 116.1852
| ScarboroughWind2080RCP8.5 | Scarborough | Wind | RCP8.5 | 2080 | 86.1355 | 93.3869 | 101.1936 | 108.8524 | 116.5208
| ScarboroughWind2085RCP8.5 | Scarborough | Wind | RCP8.5 | 2085 | 86.4132 | 93.7797 | 101.7312 | 109.5098 | 117.3033
| ScarboroughWind2090RCP8.5 | Scarborough | Wind | RCP8.5 | 2090 | 86.6909 | 94.1725 | 102.2688 | 110.1672 | 118.0858
| ScarboroughWind2095RCP8.5 | Scarborough | Wind | RCP8.5 | 2095 | 86.6909 | 94.1725 | 102.2688 | 110.1672 | 118.0858
| ScarboroughWind2100RCP8.5 | Scarborough | Wind | RCP8.5 | 2100 | 86.6909 | 94.1725 | 102.2688 | 110.1672 | 118.0858
| SchreiberIce Accretion2023RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2023 | 13.0889 | 15.6272 | 18.846 | 21.3163 | 23.7686
| SchreiberIce Accretion2025RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2025 | 13.1035 | 15.6472 | 18.873 | 21.3468 | 23.8064
| SchreiberIce Accretion2030RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2030 | 13.1181 | 15.6671 | 18.9 | 21.3773 | 23.8442
| SchreiberIce Accretion2035RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2035 | 13.1327 | 15.687 | 18.927 | 21.4078 | 23.882
| SchreiberIce Accretion2040RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2040 | 13.1473 | 15.7069 | 18.954 | 21.4384 | 23.9198
| SchreiberIce Accretion2045RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2045 | 13.1619 | 15.7268 | 18.981 | 21.4689 | 23.9576
| SchreiberIce Accretion2050RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2050 | 13.2317 | 15.8185 | 19.098 | 21.6051 | 24.1134
| SchreiberIce Accretion2055RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2055 | 13.2868 | 15.8902 | 19.188 | 21.7109 | 24.2313
| SchreiberIce Accretion2060RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2060 | 13.3419 | 15.9619 | 19.278 | 21.8167 | 24.3492
| SchreiberIce Accretion2065RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2065 | 13.397 | 16.0336 | 19.368 | 21.9225 | 24.4672
| SchreiberIce Accretion2070RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2070 | 13.4521 | 16.1053 | 19.458 | 22.0282 | 24.5851
| SchreiberIce Accretion2075RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2075 | 13.4333 | 16.0879 | 19.44 | 22.0113 | 24.57
| SchreiberIce Accretion2080RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2080 | 13.4145 | 16.0705 | 19.422 | 21.9943 | 24.5549
| SchreiberIce Accretion2085RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2085 | 13.3957 | 16.053 | 19.404 | 21.9774 | 24.5398
| SchreiberIce Accretion2090RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2090 | 13.3769 | 16.0356 | 19.386 | 21.9604 | 24.5246
| SchreiberIce Accretion2095RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2095 | 13.3582 | 16.0182 | 19.368 | 21.9435 | 24.5095
| SchreiberIce Accretion2100RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2100 | 13.3394 | 16.0007 | 19.35 | 21.9265 | 24.4944
| SchreiberIce Accretion2023RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2023 | 13.0889 | 15.6272 | 18.846 | 21.3163 | 23.7686
| SchreiberIce Accretion2025RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2025 | 13.1035 | 15.6472 | 18.873 | 21.3468 | 23.8064
| SchreiberIce Accretion2030RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2030 | 13.1181 | 15.6671 | 18.9 | 21.3773 | 23.8442
| SchreiberIce Accretion2035RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2035 | 13.1327 | 15.687 | 18.927 | 21.4078 | 23.882
| SchreiberIce Accretion2040RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2040 | 13.1473 | 15.7069 | 18.954 | 21.4384 | 23.9198
| SchreiberIce Accretion2045RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2045 | 13.1619 | 15.7268 | 18.981 | 21.4689 | 23.9576
| SchreiberIce Accretion2050RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2050 | 13.2317 | 15.8185 | 19.098 | 21.6051 | 24.1134
| SchreiberIce Accretion2055RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2055 | 13.2868 | 15.8902 | 19.188 | 21.7109 | 24.2313
| SchreiberIce Accretion2060RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2060 | 13.3419 | 15.9619 | 19.278 | 21.8167 | 24.3492
| SchreiberIce Accretion2065RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2065 | 13.397 | 16.0336 | 19.368 | 21.9225 | 24.4672
| SchreiberIce Accretion2070RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2070 | 13.4521 | 16.1053 | 19.458 | 22.0282 | 24.5851
| SchreiberIce Accretion2075RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2075 | 13.4239 | 16.0792 | 19.431 | 22.0028 | 24.5624
| SchreiberIce Accretion2080RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2080 | 13.3957 | 16.053 | 19.404 | 21.9774 | 24.5398
| SchreiberIce Accretion2085RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2085 | 13.3676 | 16.0269 | 19.377 | 21.9519 | 24.5171
| SchreiberIce Accretion2090RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2090 | 13.2016 | 15.8414 | 19.164 | 21.7163 | 24.26
| SchreiberIce Accretion2095RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2095 | 13.0638 | 15.682 | 18.978 | 21.5062 | 24.0257
| SchreiberIce Accretion2100RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2100 | 12.926 | 15.5227 | 18.792 | 21.296 | 23.7913
| SchreiberIce Accretion2023RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2023 | 13.0889 | 15.6272 | 18.846 | 21.3163 | 23.7686
| SchreiberIce Accretion2025RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2025 | 13.1181 | 15.6671 | 18.9 | 21.3773 | 23.8442
| SchreiberIce Accretion2030RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2030 | 13.1473 | 15.7069 | 18.954 | 21.4384 | 23.9198
| SchreiberIce Accretion2035RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2035 | 13.1765 | 15.7468 | 19.008 | 21.4994 | 23.9954
| SchreiberIce Accretion2040RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2040 | 13.2684 | 15.8663 | 19.158 | 21.6757 | 24.192
| SchreiberIce Accretion2045RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2045 | 13.3602 | 15.9858 | 19.308 | 21.8519 | 24.3886
| SchreiberIce Accretion2050RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2050 | 13.4145 | 16.0705 | 19.422 | 21.9943 | 24.5549
| SchreiberIce Accretion2055RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2055 | 13.3769 | 16.0356 | 19.386 | 21.9604 | 24.5246
| SchreiberIce Accretion2060RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2060 | 13.2016 | 15.8414 | 19.164 | 21.7163 | 24.26
| SchreiberIce Accretion2065RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2065 | 13.0638 | 15.682 | 18.978 | 21.5062 | 24.0257
| SchreiberIce Accretion2070RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2070 | 12.8968 | 15.5027 | 18.792 | 21.3028 | 23.814
| SchreiberIce Accretion2075RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2075 | 12.8676 | 15.4828 | 18.792 | 21.3095 | 23.8367
| SchreiberIce Accretion2080RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2080 | 12.8384 | 15.4629 | 18.792 | 21.3163 | 23.8594
| SchreiberIce Accretion2085RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2085 | 12.7194 | 15.3359 | 18.639 | 21.1536 | 23.6779
| SchreiberIce Accretion2090RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2090 | 12.6004 | 15.2089 | 18.486 | 20.9909 | 23.4965
| SchreiberIce Accretion2095RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2095 | 12.6004 | 15.2089 | 18.486 | 20.9909 | 23.4965
| SchreiberIce Accretion2100RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2100 | 12.6004 | 15.2089 | 18.486 | 20.9909 | 23.4965
| SchreiberWind2023RCP4.5 | Schreiber | Wind | RCP4.5 | 2023 | 81.3134 | 87.4987 | 93.9812 | 100.4895 | 106.9885
| SchreiberWind2025RCP4.5 | Schreiber | Wind | RCP4.5 | 2025 | 81.4568 | 87.6808 | 94.2099 | 100.7577 | 107.2993
| SchreiberWind2030RCP4.5 | Schreiber | Wind | RCP4.5 | 2030 | 81.6002 | 87.8629 | 94.4387 | 101.0259 | 107.6101
| SchreiberWind2035RCP4.5 | Schreiber | Wind | RCP4.5 | 2035 | 81.7436 | 88.0451 | 94.6674 | 101.2941 | 107.9208
| SchreiberWind2040RCP4.5 | Schreiber | Wind | RCP4.5 | 2040 | 81.887 | 88.2272 | 94.8961 | 101.5623 | 108.2316
| SchreiberWind2045RCP4.5 | Schreiber | Wind | RCP4.5 | 2045 | 82.0304 | 88.4093 | 95.1249 | 101.8305 | 108.5424
| SchreiberWind2050RCP4.5 | Schreiber | Wind | RCP4.5 | 2050 | 82.3751 | 88.838 | 95.66 | 102.4548 | 109.2582
| SchreiberWind2055RCP4.5 | Schreiber | Wind | RCP4.5 | 2055 | 82.5764 | 89.0845 | 95.9665 | 102.8109 | 109.6633
| SchreiberWind2060RCP4.5 | Schreiber | Wind | RCP4.5 | 2060 | 82.7777 | 89.331 | 96.2729 | 103.1669 | 110.0683
| SchreiberWind2065RCP4.5 | Schreiber | Wind | RCP4.5 | 2065 | 82.979 | 89.5775 | 96.5794 | 103.523 | 110.4734
| SchreiberWind2070RCP4.5 | Schreiber | Wind | RCP4.5 | 2070 | 83.1803 | 89.8241 | 96.8858 | 103.879 | 110.8785
| SchreiberWind2075RCP4.5 | Schreiber | Wind | RCP4.5 | 2075 | 83.2804 | 89.9362 | 97.0096 | 104.0148 | 111.0267
| SchreiberWind2080RCP4.5 | Schreiber | Wind | RCP4.5 | 2080 | 83.3805 | 90.0484 | 97.1333 | 104.1506 | 111.1749
| SchreiberWind2085RCP4.5 | Schreiber | Wind | RCP4.5 | 2085 | 83.4806 | 90.1606 | 97.2571 | 104.2864 | 111.3232
| SchreiberWind2090RCP4.5 | Schreiber | Wind | RCP4.5 | 2090 | 83.5807 | 90.2728 | 97.3809 | 104.4222 | 111.4714
| SchreiberWind2095RCP4.5 | Schreiber | Wind | RCP4.5 | 2095 | 83.6808 | 90.385 | 97.5046 | 104.5579 | 111.6196
| SchreiberWind2100RCP4.5 | Schreiber | Wind | RCP4.5 | 2100 | 83.7809 | 90.4972 | 97.6284 | 104.6937 | 111.7679
| SchreiberWind2023RCP6.0 | Schreiber | Wind | RCP6.0 | 2023 | 81.3134 | 87.4987 | 93.9812 | 100.4895 | 106.9885
| SchreiberWind2025RCP6.0 | Schreiber | Wind | RCP6.0 | 2025 | 81.4568 | 87.6808 | 94.2099 | 100.7577 | 107.2993
| SchreiberWind2030RCP6.0 | Schreiber | Wind | RCP6.0 | 2030 | 81.6002 | 87.8629 | 94.4387 | 101.0259 | 107.6101
| SchreiberWind2035RCP6.0 | Schreiber | Wind | RCP6.0 | 2035 | 81.7436 | 88.0451 | 94.6674 | 101.2941 | 107.9208
| SchreiberWind2040RCP6.0 | Schreiber | Wind | RCP6.0 | 2040 | 81.887 | 88.2272 | 94.8961 | 101.5623 | 108.2316
| SchreiberWind2045RCP6.0 | Schreiber | Wind | RCP6.0 | 2045 | 82.0304 | 88.4093 | 95.1249 | 101.8305 | 108.5424
| SchreiberWind2050RCP6.0 | Schreiber | Wind | RCP6.0 | 2050 | 82.3751 | 88.838 | 95.66 | 102.4548 | 109.2582
| SchreiberWind2055RCP6.0 | Schreiber | Wind | RCP6.0 | 2055 | 82.5764 | 89.0845 | 95.9665 | 102.8109 | 109.6633
| SchreiberWind2060RCP6.0 | Schreiber | Wind | RCP6.0 | 2060 | 82.7777 | 89.331 | 96.2729 | 103.1669 | 110.0683
| SchreiberWind2065RCP6.0 | Schreiber | Wind | RCP6.0 | 2065 | 82.979 | 89.5775 | 96.5794 | 103.523 | 110.4734
| SchreiberWind2070RCP6.0 | Schreiber | Wind | RCP6.0 | 2070 | 83.1803 | 89.8241 | 96.8858 | 103.879 | 110.8785
| SchreiberWind2075RCP6.0 | Schreiber | Wind | RCP6.0 | 2075 | 83.3305 | 89.9923 | 97.0714 | 104.0827 | 111.1008
| SchreiberWind2080RCP6.0 | Schreiber | Wind | RCP6.0 | 2080 | 83.4806 | 90.1606 | 97.2571 | 104.2864 | 111.3232
| SchreiberWind2085RCP6.0 | Schreiber | Wind | RCP6.0 | 2085 | 83.6308 | 90.3289 | 97.4427 | 104.49 | 111.5455
| SchreiberWind2090RCP6.0 | Schreiber | Wind | RCP6.0 | 2090 | 83.8702 | 90.57 | 97.6817 | 104.7306 | 111.7857
| SchreiberWind2095RCP6.0 | Schreiber | Wind | RCP6.0 | 2095 | 83.9595 | 90.6429 | 97.7349 | 104.7675 | 111.8036
| SchreiberWind2100RCP6.0 | Schreiber | Wind | RCP6.0 | 2100 | 84.0488 | 90.7157 | 97.7882 | 104.8044 | 111.8215
| SchreiberWind2023RCP8.5 | Schreiber | Wind | RCP8.5 | 2023 | 81.3134 | 87.4987 | 93.9812 | 100.4895 | 106.9885
| SchreiberWind2025RCP8.5 | Schreiber | Wind | RCP8.5 | 2025 | 81.6002 | 87.8629 | 94.4387 | 101.0259 | 107.6101
| SchreiberWind2030RCP8.5 | Schreiber | Wind | RCP8.5 | 2030 | 81.887 | 88.2272 | 94.8961 | 101.5623 | 108.2316
| SchreiberWind2035RCP8.5 | Schreiber | Wind | RCP8.5 | 2035 | 82.1738 | 88.5914 | 95.3536 | 102.0988 | 108.8531
| SchreiberWind2040RCP8.5 | Schreiber | Wind | RCP8.5 | 2040 | 82.5093 | 89.0023 | 95.8643 | 102.6922 | 109.5282
| SchreiberWind2045RCP8.5 | Schreiber | Wind | RCP8.5 | 2045 | 82.8448 | 89.4132 | 96.3751 | 103.2856 | 110.2033
| SchreiberWind2050RCP8.5 | Schreiber | Wind | RCP8.5 | 2050 | 83.3805 | 90.0484 | 97.1333 | 104.1506 | 111.1749
| SchreiberWind2055RCP8.5 | Schreiber | Wind | RCP8.5 | 2055 | 83.5807 | 90.2728 | 97.3809 | 104.4222 | 111.4714
| SchreiberWind2060RCP8.5 | Schreiber | Wind | RCP8.5 | 2060 | 83.8702 | 90.57 | 97.6817 | 104.7306 | 111.7857
| SchreiberWind2065RCP8.5 | Schreiber | Wind | RCP8.5 | 2065 | 83.9595 | 90.6429 | 97.7349 | 104.7675 | 111.8036
| SchreiberWind2070RCP8.5 | Schreiber | Wind | RCP8.5 | 2070 | 84.3058 | 91.013 | 98.1329 | 105.1933 | 112.2572
| SchreiberWind2075RCP8.5 | Schreiber | Wind | RCP8.5 | 2075 | 84.5628 | 91.3102 | 98.4775 | 105.5822 | 112.693
| SchreiberWind2080RCP8.5 | Schreiber | Wind | RCP8.5 | 2080 | 84.8199 | 91.6074 | 98.8222 | 105.9711 | 113.1288
| SchreiberWind2085RCP8.5 | Schreiber | Wind | RCP8.5 | 2085 | 85.2338 | 92.1451 | 99.5131 | 106.7908 | 114.0772
| SchreiberWind2090RCP8.5 | Schreiber | Wind | RCP8.5 | 2090 | 85.6478 | 92.6827 | 100.204 | 107.6105 | 115.0255
| SchreiberWind2095RCP8.5 | Schreiber | Wind | RCP8.5 | 2095 | 85.6478 | 92.6827 | 100.204 | 107.6105 | 115.0255
| SchreiberWind2100RCP8.5 | Schreiber | Wind | RCP8.5 | 2100 | 85.6478 | 92.6827 | 100.204 | 107.6105 | 115.0255
| SeaforthIce Accretion2023RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2023 | 15.278 | 18.3513 | 22.242 | 25.208 | 28.1635
| SeaforthIce Accretion2025RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2025 | 15.352 | 18.4456 | 22.363 | 25.3531 | 28.3298
| SeaforthIce Accretion2030RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2030 | 15.426 | 18.54 | 22.484 | 25.4981 | 28.4962
| SeaforthIce Accretion2035RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2035 | 15.5 | 18.6343 | 22.605 | 25.6431 | 28.6625
| SeaforthIce Accretion2040RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2040 | 15.574 | 18.7287 | 22.726 | 25.7881 | 28.8288
| SeaforthIce Accretion2045RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2045 | 15.648 | 18.823 | 22.847 | 25.9331 | 28.9951
| SeaforthIce Accretion2050RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2050 | 15.7281 | 18.9466 | 23.0296 | 26.1527 | 29.2612
| SeaforthIce Accretion2055RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2055 | 15.7342 | 18.9758 | 23.0912 | 26.2273 | 29.361
| SeaforthIce Accretion2060RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2060 | 15.7403 | 19.005 | 23.1528 | 26.3019 | 29.4608
| SeaforthIce Accretion2065RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2065 | 15.7464 | 19.0342 | 23.2144 | 26.3765 | 29.5606
| SeaforthIce Accretion2070RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2070 | 15.7526 | 19.0634 | 23.276 | 26.451 | 29.6604
| SeaforthIce Accretion2075RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2075 | 15.7041 | 19.033 | 23.2613 | 26.4552 | 29.6743
| SeaforthIce Accretion2080RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2080 | 15.6556 | 19.0026 | 23.2467 | 26.4593 | 29.6881
| SeaforthIce Accretion2085RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2085 | 15.6071 | 18.9721 | 23.232 | 26.4635 | 29.702
| SeaforthIce Accretion2090RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2090 | 15.5587 | 18.9417 | 23.2173 | 26.4676 | 29.7158
| SeaforthIce Accretion2095RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2095 | 15.5102 | 18.9113 | 23.2027 | 26.4718 | 29.7297
| SeaforthIce Accretion2100RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2100 | 15.4617 | 18.8808 | 23.188 | 26.4759 | 29.7436
| SeaforthIce Accretion2023RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2023 | 15.278 | 18.3513 | 22.242 | 25.208 | 28.1635
| SeaforthIce Accretion2025RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2025 | 15.352 | 18.4456 | 22.363 | 25.3531 | 28.3298
| SeaforthIce Accretion2030RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2030 | 15.426 | 18.54 | 22.484 | 25.4981 | 28.4962
| SeaforthIce Accretion2035RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2035 | 15.5 | 18.6343 | 22.605 | 25.6431 | 28.6625
| SeaforthIce Accretion2040RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2040 | 15.574 | 18.7287 | 22.726 | 25.7881 | 28.8288
| SeaforthIce Accretion2045RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2045 | 15.648 | 18.823 | 22.847 | 25.9331 | 28.9951
| SeaforthIce Accretion2050RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2050 | 15.7281 | 18.9466 | 23.0296 | 26.1527 | 29.2612
| SeaforthIce Accretion2055RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2055 | 15.7342 | 18.9758 | 23.0912 | 26.2273 | 29.361
| SeaforthIce Accretion2060RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2060 | 15.7403 | 19.005 | 23.1528 | 26.3019 | 29.4608
| SeaforthIce Accretion2065RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2065 | 15.7464 | 19.0342 | 23.2144 | 26.3765 | 29.5606
| SeaforthIce Accretion2070RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2070 | 15.7526 | 19.0634 | 23.276 | 26.451 | 29.6604
| SeaforthIce Accretion2075RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2075 | 15.6798 | 19.0178 | 23.254 | 26.4573 | 29.6812
| SeaforthIce Accretion2080RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2080 | 15.6071 | 18.9721 | 23.232 | 26.4635 | 29.702
| SeaforthIce Accretion2085RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2085 | 15.5344 | 18.9265 | 23.21 | 26.4697 | 29.7228
| SeaforthIce Accretion2090RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2090 | 15.2066 | 18.6191 | 22.9167 | 26.1859 | 29.4479
| SeaforthIce Accretion2095RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2095 | 14.9514 | 18.3574 | 22.6453 | 25.8958 | 29.1522
| SeaforthIce Accretion2100RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2100 | 14.6963 | 18.0957 | 22.374 | 25.6058 | 28.8565
| SeaforthIce Accretion2023RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2023 | 15.278 | 18.3513 | 22.242 | 25.208 | 28.1635
| SeaforthIce Accretion2025RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2025 | 15.426 | 18.54 | 22.484 | 25.4981 | 28.4962
| SeaforthIce Accretion2030RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2030 | 15.574 | 18.7287 | 22.726 | 25.7881 | 28.8288
| SeaforthIce Accretion2035RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2035 | 15.7219 | 18.9174 | 22.968 | 26.0781 | 29.1614
| SeaforthIce Accretion2040RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2040 | 15.7322 | 18.9661 | 23.0707 | 26.2024 | 29.3278
| SeaforthIce Accretion2045RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2045 | 15.7424 | 19.0147 | 23.1733 | 26.3267 | 29.4941
| SeaforthIce Accretion2050RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2050 | 15.6556 | 19.0026 | 23.2467 | 26.4593 | 29.6881
| SeaforthIce Accretion2055RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2055 | 15.5587 | 18.9417 | 23.2173 | 26.4676 | 29.7158
| SeaforthIce Accretion2060RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2060 | 15.2066 | 18.6191 | 22.9167 | 26.1859 | 29.4479
| SeaforthIce Accretion2065RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2065 | 14.9514 | 18.3574 | 22.6453 | 25.8958 | 29.1522
| SeaforthIce Accretion2070RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2070 | 14.2268 | 17.5661 | 21.7727 | 24.9512 | 28.1358
| SeaforthIce Accretion2075RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2075 | 13.7573 | 17.0366 | 21.1713 | 24.2965 | 27.4151
| SeaforthIce Accretion2080RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2080 | 13.2879 | 16.507 | 20.57 | 23.6419 | 26.6944
| SeaforthIce Accretion2085RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2085 | 12.599 | 15.6945 | 19.602 | 22.548 | 25.4885
| SeaforthIce Accretion2090RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2090 | 11.9101 | 14.8819 | 18.634 | 21.4542 | 24.2827
| SeaforthIce Accretion2095RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2095 | 11.9101 | 14.8819 | 18.634 | 21.4542 | 24.2827
| SeaforthIce Accretion2100RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2100 | 11.9101 | 14.8819 | 18.634 | 21.4542 | 24.2827
| SeaforthWind2023RCP4.5 | Seaforth | Wind | RCP4.5 | 2023 | 85.2136 | 91.8691 | 98.8918 | 105.8981 | 112.9042
| SeaforthWind2025RCP4.5 | Seaforth | Wind | RCP4.5 | 2025 | 85.2588 | 91.9223 | 98.9555 | 105.9698 | 112.9862
| SeaforthWind2030RCP4.5 | Seaforth | Wind | RCP4.5 | 2030 | 85.3039 | 91.9754 | 99.0192 | 106.0414 | 113.0681
| SeaforthWind2035RCP4.5 | Seaforth | Wind | RCP4.5 | 2035 | 85.349 | 92.0286 | 99.0829 | 106.1131 | 113.15
| SeaforthWind2040RCP4.5 | Seaforth | Wind | RCP4.5 | 2040 | 85.3942 | 92.0818 | 99.1466 | 106.1847 | 113.2319
| SeaforthWind2045RCP4.5 | Seaforth | Wind | RCP4.5 | 2045 | 85.4393 | 92.1349 | 99.2103 | 106.2564 | 113.3139
| SeaforthWind2050RCP4.5 | Seaforth | Wind | RCP4.5 | 2050 | 85.4929 | 92.1936 | 99.274 | 106.3259 | 113.3869
| SeaforthWind2055RCP4.5 | Seaforth | Wind | RCP4.5 | 2055 | 85.5013 | 92.199 | 99.274 | 106.3238 | 113.3779
| SeaforthWind2060RCP4.5 | Seaforth | Wind | RCP4.5 | 2060 | 85.5098 | 92.2045 | 99.274 | 106.3217 | 113.369
| SeaforthWind2065RCP4.5 | Seaforth | Wind | RCP4.5 | 2065 | 85.5183 | 92.21 | 99.274 | 106.3197 | 113.36
| SeaforthWind2070RCP4.5 | Seaforth | Wind | RCP4.5 | 2070 | 85.5267 | 92.2155 | 99.274 | 106.3176 | 113.3511
| SeaforthWind2075RCP4.5 | Seaforth | Wind | RCP4.5 | 2075 | 85.6212 | 92.3446 | 99.4488 | 106.5308 | 113.6043
| SeaforthWind2080RCP4.5 | Seaforth | Wind | RCP4.5 | 2080 | 85.7157 | 92.4737 | 99.6235 | 106.744 | 113.8576
| SeaforthWind2085RCP4.5 | Seaforth | Wind | RCP4.5 | 2085 | 85.8102 | 92.6028 | 99.7983 | 106.9572 | 114.1108
| SeaforthWind2090RCP4.5 | Seaforth | Wind | RCP4.5 | 2090 | 85.9047 | 92.7319 | 99.9731 | 107.1704 | 114.364
| SeaforthWind2095RCP4.5 | Seaforth | Wind | RCP4.5 | 2095 | 85.9992 | 92.861 | 100.1478 | 107.3836 | 114.6173
| SeaforthWind2100RCP4.5 | Seaforth | Wind | RCP4.5 | 2100 | 86.0937 | 92.9901 | 100.3226 | 107.5968 | 114.8705
| SeaforthWind2023RCP6.0 | Seaforth | Wind | RCP6.0 | 2023 | 85.2136 | 91.8691 | 98.8918 | 105.8981 | 112.9042
| SeaforthWind2025RCP6.0 | Seaforth | Wind | RCP6.0 | 2025 | 85.2588 | 91.9223 | 98.9555 | 105.9698 | 112.9862
| SeaforthWind2030RCP6.0 | Seaforth | Wind | RCP6.0 | 2030 | 85.3039 | 91.9754 | 99.0192 | 106.0414 | 113.0681
| SeaforthWind2035RCP6.0 | Seaforth | Wind | RCP6.0 | 2035 | 85.349 | 92.0286 | 99.0829 | 106.1131 | 113.15
| SeaforthWind2040RCP6.0 | Seaforth | Wind | RCP6.0 | 2040 | 85.3942 | 92.0818 | 99.1466 | 106.1847 | 113.2319
| SeaforthWind2045RCP6.0 | Seaforth | Wind | RCP6.0 | 2045 | 85.4393 | 92.1349 | 99.2103 | 106.2564 | 113.3139
| SeaforthWind2050RCP6.0 | Seaforth | Wind | RCP6.0 | 2050 | 85.4929 | 92.1936 | 99.274 | 106.3259 | 113.3869
| SeaforthWind2055RCP6.0 | Seaforth | Wind | RCP6.0 | 2055 | 85.5013 | 92.199 | 99.274 | 106.3238 | 113.3779
| SeaforthWind2060RCP6.0 | Seaforth | Wind | RCP6.0 | 2060 | 85.5098 | 92.2045 | 99.274 | 106.3217 | 113.369
| SeaforthWind2065RCP6.0 | Seaforth | Wind | RCP6.0 | 2065 | 85.5183 | 92.21 | 99.274 | 106.3197 | 113.36
| SeaforthWind2070RCP6.0 | Seaforth | Wind | RCP6.0 | 2070 | 85.5267 | 92.2155 | 99.274 | 106.3176 | 113.3511
| SeaforthWind2075RCP6.0 | Seaforth | Wind | RCP6.0 | 2075 | 85.6685 | 92.4091 | 99.5361 | 106.6374 | 113.731
| SeaforthWind2080RCP6.0 | Seaforth | Wind | RCP6.0 | 2080 | 85.8102 | 92.6028 | 99.7983 | 106.9572 | 114.1108
| SeaforthWind2085RCP6.0 | Seaforth | Wind | RCP6.0 | 2085 | 85.9519 | 92.7965 | 100.0605 | 107.277 | 114.4907
| SeaforthWind2090RCP6.0 | Seaforth | Wind | RCP6.0 | 2090 | 86.4688 | 93.4519 | 100.8877 | 108.2505 | 115.619
| SeaforthWind2095RCP6.0 | Seaforth | Wind | RCP6.0 | 2095 | 86.844 | 93.9137 | 101.4529 | 108.9041 | 116.3676
| SeaforthWind2100RCP6.0 | Seaforth | Wind | RCP6.0 | 2100 | 87.2192 | 94.3755 | 102.018 | 109.5577 | 117.1161
| SeaforthWind2023RCP8.5 | Seaforth | Wind | RCP8.5 | 2023 | 85.2136 | 91.8691 | 98.8918 | 105.8981 | 112.9042
| SeaforthWind2025RCP8.5 | Seaforth | Wind | RCP8.5 | 2025 | 85.3039 | 91.9754 | 99.0192 | 106.0414 | 113.0681
| SeaforthWind2030RCP8.5 | Seaforth | Wind | RCP8.5 | 2030 | 85.3942 | 92.0818 | 99.1466 | 106.1847 | 113.2319
| SeaforthWind2035RCP8.5 | Seaforth | Wind | RCP8.5 | 2035 | 85.4844 | 92.1881 | 99.274 | 106.328 | 113.3958
| SeaforthWind2040RCP8.5 | Seaforth | Wind | RCP8.5 | 2040 | 85.4985 | 92.1972 | 99.274 | 106.3245 | 113.3809
| SeaforthWind2045RCP8.5 | Seaforth | Wind | RCP8.5 | 2045 | 85.5126 | 92.2063 | 99.274 | 106.321 | 113.366
| SeaforthWind2050RCP8.5 | Seaforth | Wind | RCP8.5 | 2050 | 85.7157 | 92.4737 | 99.6235 | 106.744 | 113.8576
| SeaforthWind2055RCP8.5 | Seaforth | Wind | RCP8.5 | 2055 | 85.9047 | 92.7319 | 99.9731 | 107.1704 | 114.364
| SeaforthWind2060RCP8.5 | Seaforth | Wind | RCP8.5 | 2060 | 86.4688 | 93.4519 | 100.8877 | 108.2505 | 115.619
| SeaforthWind2065RCP8.5 | Seaforth | Wind | RCP8.5 | 2065 | 86.844 | 93.9137 | 101.4529 | 108.9041 | 116.3676
| SeaforthWind2070RCP8.5 | Seaforth | Wind | RCP8.5 | 2070 | 87.4956 | 94.737 | 102.4917 | 110.124 | 117.7789
| SeaforthWind2075RCP8.5 | Seaforth | Wind | RCP8.5 | 2075 | 87.772 | 95.0985 | 102.9653 | 110.6902 | 118.4418
| SeaforthWind2080RCP8.5 | Seaforth | Wind | RCP8.5 | 2080 | 88.0484 | 95.46 | 103.439 | 111.2565 | 119.1047
| SeaforthWind2085RCP8.5 | Seaforth | Wind | RCP8.5 | 2085 | 88.2642 | 95.7471 | 103.8163 | 111.7074 | 119.6298
| SeaforthWind2090RCP8.5 | Seaforth | Wind | RCP8.5 | 2090 | 88.48 | 96.0342 | 104.1936 | 112.1583 | 120.1549
| SeaforthWind2095RCP8.5 | Seaforth | Wind | RCP8.5 | 2095 | 88.48 | 96.0342 | 104.1936 | 112.1583 | 120.1549
| SeaforthWind2100RCP8.5 | Seaforth | Wind | RCP8.5 | 2100 | 88.48 | 96.0342 | 104.1936 | 112.1583 | 120.1549
| ShelburneIce Accretion2023RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2023 | 15.4005 | 18.4791 | 22.396 | 25.3821 | 28.3576
| ShelburneIce Accretion2025RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2025 | 15.4209 | 18.5156 | 22.451 | 25.4525 | 28.4407
| ShelburneIce Accretion2030RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2030 | 15.4413 | 18.5522 | 22.506 | 25.5229 | 28.5239
| ShelburneIce Accretion2035RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2035 | 15.4617 | 18.5887 | 22.561 | 25.5934 | 28.607
| ShelburneIce Accretion2040RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2040 | 15.4821 | 18.6252 | 22.616 | 25.6638 | 28.6902
| ShelburneIce Accretion2045RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2045 | 15.5025 | 18.6617 | 22.671 | 25.7342 | 28.7734
| ShelburneIce Accretion2050RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2050 | 15.4893 | 18.6727 | 22.7128 | 25.7997 | 28.8676
| ShelburneIce Accretion2055RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2055 | 15.4556 | 18.6471 | 22.6996 | 25.7947 | 28.8787
| ShelburneIce Accretion2060RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2060 | 15.4219 | 18.6215 | 22.6864 | 25.7898 | 28.8898
| ShelburneIce Accretion2065RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2065 | 15.3882 | 18.596 | 22.6732 | 25.7848 | 28.9009
| ShelburneIce Accretion2070RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2070 | 15.3545 | 18.5704 | 22.66 | 25.7798 | 28.912
| ShelburneIce Accretion2075RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2075 | 15.3341 | 18.5735 | 22.6893 | 25.8295 | 28.9813
| ShelburneIce Accretion2080RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2080 | 15.3137 | 18.5765 | 22.7187 | 25.8793 | 29.0506
| ShelburneIce Accretion2085RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2085 | 15.2933 | 18.5795 | 22.748 | 25.929 | 29.1199
| ShelburneIce Accretion2090RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2090 | 15.2729 | 18.5826 | 22.7773 | 25.9787 | 29.1892
| ShelburneIce Accretion2095RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2095 | 15.2525 | 18.5856 | 22.8067 | 26.0284 | 29.2585
| ShelburneIce Accretion2100RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2100 | 15.2321 | 18.5887 | 22.836 | 26.0781 | 29.3278
| ShelburneIce Accretion2023RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2023 | 15.4005 | 18.4791 | 22.396 | 25.3821 | 28.3576
| ShelburneIce Accretion2025RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2025 | 15.4209 | 18.5156 | 22.451 | 25.4525 | 28.4407
| ShelburneIce Accretion2030RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2030 | 15.4413 | 18.5522 | 22.506 | 25.5229 | 28.5239
| ShelburneIce Accretion2035RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2035 | 15.4617 | 18.5887 | 22.561 | 25.5934 | 28.607
| ShelburneIce Accretion2040RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2040 | 15.4821 | 18.6252 | 22.616 | 25.6638 | 28.6902
| ShelburneIce Accretion2045RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2045 | 15.5025 | 18.6617 | 22.671 | 25.7342 | 28.7734
| ShelburneIce Accretion2050RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2050 | 15.4893 | 18.6727 | 22.7128 | 25.7997 | 28.8676
| ShelburneIce Accretion2055RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2055 | 15.4556 | 18.6471 | 22.6996 | 25.7947 | 28.8787
| ShelburneIce Accretion2060RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2060 | 15.4219 | 18.6215 | 22.6864 | 25.7898 | 28.8898
| ShelburneIce Accretion2065RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2065 | 15.3882 | 18.596 | 22.6732 | 25.7848 | 28.9009
| ShelburneIce Accretion2070RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2070 | 15.3545 | 18.5704 | 22.66 | 25.7798 | 28.912
| ShelburneIce Accretion2075RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2075 | 15.3239 | 18.575 | 22.704 | 25.8544 | 29.0159
| ShelburneIce Accretion2080RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2080 | 15.2933 | 18.5795 | 22.748 | 25.929 | 29.1199
| ShelburneIce Accretion2085RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2085 | 15.2627 | 18.5841 | 22.792 | 26.0036 | 29.2238
| ShelburneIce Accretion2090RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2090 | 15.0331 | 18.3939 | 22.6453 | 25.8875 | 29.1245
| ShelburneIce Accretion2095RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2095 | 14.834 | 18.1991 | 22.4547 | 25.697 | 28.9212
| ShelburneIce Accretion2100RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2100 | 14.635 | 18.0044 | 22.264 | 25.5064 | 28.7179
| ShelburneIce Accretion2023RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2023 | 15.4005 | 18.4791 | 22.396 | 25.3821 | 28.3576
| ShelburneIce Accretion2025RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2025 | 15.4413 | 18.5522 | 22.506 | 25.5229 | 28.5239
| ShelburneIce Accretion2030RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2030 | 15.4821 | 18.6252 | 22.616 | 25.6638 | 28.6902
| ShelburneIce Accretion2035RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2035 | 15.5229 | 18.6982 | 22.726 | 25.8047 | 28.8565
| ShelburneIce Accretion2040RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2040 | 15.4668 | 18.6556 | 22.704 | 25.7964 | 28.875
| ShelburneIce Accretion2045RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2045 | 15.4107 | 18.613 | 22.682 | 25.7881 | 28.8935
| ShelburneIce Accretion2050RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2050 | 15.3137 | 18.5765 | 22.7187 | 25.8793 | 29.0506
| ShelburneIce Accretion2055RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2055 | 15.2729 | 18.5826 | 22.7773 | 25.9787 | 29.1892
| ShelburneIce Accretion2060RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2060 | 15.0331 | 18.3939 | 22.6453 | 25.8875 | 29.1245
| ShelburneIce Accretion2065RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2065 | 14.834 | 18.1991 | 22.4547 | 25.697 | 28.9212
| ShelburneIce Accretion2070RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2070 | 14.2778 | 17.6087 | 21.8167 | 25.0174 | 28.2005
| ShelburneIce Accretion2075RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2075 | 13.9206 | 17.2131 | 21.3693 | 24.5285 | 27.683
| ShelburneIce Accretion2080RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2080 | 13.5634 | 16.8175 | 20.922 | 24.0396 | 27.1656
| ShelburneIce Accretion2085RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2085 | 12.9817 | 16.1601 | 20.174 | 23.2192 | 26.2647
| ShelburneIce Accretion2090RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2090 | 12.4 | 15.5027 | 19.426 | 22.3989 | 25.3638
| ShelburneIce Accretion2095RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2095 | 12.4 | 15.5027 | 19.426 | 22.3989 | 25.3638
| ShelburneIce Accretion2100RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2100 | 12.4 | 15.5027 | 19.426 | 22.3989 | 25.3638
| ShelburneWind2023RCP4.5 | Shelburne | Wind | RCP4.5 | 2023 | 80.5608 | 86.7841 | 93.3348 | 99.8782 | 106.4229
| ShelburneWind2025RCP4.5 | Shelburne | Wind | RCP4.5 | 2025 | 80.5689 | 86.7985 | 93.3581 | 99.908 | 106.4617
| ShelburneWind2030RCP4.5 | Shelburne | Wind | RCP4.5 | 2030 | 80.5769 | 86.8129 | 93.3813 | 99.9379 | 106.5006
| ShelburneWind2035RCP4.5 | Shelburne | Wind | RCP4.5 | 2035 | 80.5849 | 86.8273 | 93.4046 | 99.9677 | 106.5395
| ShelburneWind2040RCP4.5 | Shelburne | Wind | RCP4.5 | 2040 | 80.593 | 86.8417 | 93.4278 | 99.9976 | 106.5784
| ShelburneWind2045RCP4.5 | Shelburne | Wind | RCP4.5 | 2045 | 80.601 | 86.8561 | 93.4511 | 100.0275 | 106.6172
| ShelburneWind2050RCP4.5 | Shelburne | Wind | RCP4.5 | 2050 | 80.6636 | 86.9294 | 93.5375 | 100.125 | 106.7282
| ShelburneWind2055RCP4.5 | Shelburne | Wind | RCP4.5 | 2055 | 80.7182 | 86.9882 | 93.6008 | 100.1926 | 106.8003
| ShelburneWind2060RCP4.5 | Shelburne | Wind | RCP4.5 | 2060 | 80.7728 | 87.047 | 93.664 | 100.2603 | 106.8724
| ShelburneWind2065RCP4.5 | Shelburne | Wind | RCP4.5 | 2065 | 80.8274 | 87.1058 | 93.7273 | 100.328 | 106.9445
| ShelburneWind2070RCP4.5 | Shelburne | Wind | RCP4.5 | 2070 | 80.8821 | 87.1646 | 93.7905 | 100.3956 | 107.0166
| ShelburneWind2075RCP4.5 | Shelburne | Wind | RCP4.5 | 2075 | 80.9503 | 87.2569 | 93.9145 | 100.5482 | 107.1951
| ShelburneWind2080RCP4.5 | Shelburne | Wind | RCP4.5 | 2080 | 81.0186 | 87.3491 | 94.0385 | 100.7008 | 107.3735
| ShelburneWind2085RCP4.5 | Shelburne | Wind | RCP4.5 | 2085 | 81.0868 | 87.4414 | 94.1625 | 100.8534 | 107.552
| ShelburneWind2090RCP4.5 | Shelburne | Wind | RCP4.5 | 2090 | 81.1551 | 87.5336 | 94.2865 | 101.006 | 107.7305
| ShelburneWind2095RCP4.5 | Shelburne | Wind | RCP4.5 | 2095 | 81.2233 | 87.6259 | 94.4105 | 101.1585 | 107.9089
| ShelburneWind2100RCP4.5 | Shelburne | Wind | RCP4.5 | 2100 | 81.2916 | 87.7182 | 94.5345 | 101.3111 | 108.0874
| ShelburneWind2023RCP6.0 | Shelburne | Wind | RCP6.0 | 2023 | 80.5608 | 86.7841 | 93.3348 | 99.8782 | 106.4229
| ShelburneWind2025RCP6.0 | Shelburne | Wind | RCP6.0 | 2025 | 80.5689 | 86.7985 | 93.3581 | 99.908 | 106.4617
| ShelburneWind2030RCP6.0 | Shelburne | Wind | RCP6.0 | 2030 | 80.5769 | 86.8129 | 93.3813 | 99.9379 | 106.5006
| ShelburneWind2035RCP6.0 | Shelburne | Wind | RCP6.0 | 2035 | 80.5849 | 86.8273 | 93.4046 | 99.9677 | 106.5395
| ShelburneWind2040RCP6.0 | Shelburne | Wind | RCP6.0 | 2040 | 80.593 | 86.8417 | 93.4278 | 99.9976 | 106.5784
| ShelburneWind2045RCP6.0 | Shelburne | Wind | RCP6.0 | 2045 | 80.601 | 86.8561 | 93.4511 | 100.0275 | 106.6172
| ShelburneWind2050RCP6.0 | Shelburne | Wind | RCP6.0 | 2050 | 80.6636 | 86.9294 | 93.5375 | 100.125 | 106.7282
| ShelburneWind2055RCP6.0 | Shelburne | Wind | RCP6.0 | 2055 | 80.7182 | 86.9882 | 93.6008 | 100.1926 | 106.8003
| ShelburneWind2060RCP6.0 | Shelburne | Wind | RCP6.0 | 2060 | 80.7728 | 87.047 | 93.664 | 100.2603 | 106.8724
| ShelburneWind2065RCP6.0 | Shelburne | Wind | RCP6.0 | 2065 | 80.8274 | 87.1058 | 93.7273 | 100.328 | 106.9445
| ShelburneWind2070RCP6.0 | Shelburne | Wind | RCP6.0 | 2070 | 80.8821 | 87.1646 | 93.7905 | 100.3956 | 107.0166
| ShelburneWind2075RCP6.0 | Shelburne | Wind | RCP6.0 | 2075 | 80.9844 | 87.303 | 93.9765 | 100.6245 | 107.2843
| ShelburneWind2080RCP6.0 | Shelburne | Wind | RCP6.0 | 2080 | 81.0868 | 87.4414 | 94.1625 | 100.8534 | 107.552
| ShelburneWind2085RCP6.0 | Shelburne | Wind | RCP6.0 | 2085 | 81.1892 | 87.5798 | 94.3485 | 101.0823 | 107.8197
| ShelburneWind2090RCP6.0 | Shelburne | Wind | RCP6.0 | 2090 | 81.6744 | 88.191 | 95.1142 | 101.9845 | 108.8543
| ShelburneWind2095RCP6.0 | Shelburne | Wind | RCP6.0 | 2095 | 82.0572 | 88.6638 | 95.6939 | 102.6578 | 109.6211
| ShelburneWind2100RCP6.0 | Shelburne | Wind | RCP6.0 | 2100 | 82.4399 | 89.1366 | 96.2736 | 103.3312 | 110.388
| ShelburneWind2023RCP8.5 | Shelburne | Wind | RCP8.5 | 2023 | 80.5608 | 86.7841 | 93.3348 | 99.8782 | 106.4229
| ShelburneWind2025RCP8.5 | Shelburne | Wind | RCP8.5 | 2025 | 80.5769 | 86.8129 | 93.3813 | 99.9379 | 106.5006
| ShelburneWind2030RCP8.5 | Shelburne | Wind | RCP8.5 | 2030 | 80.593 | 86.8417 | 93.4278 | 99.9976 | 106.5784
| ShelburneWind2035RCP8.5 | Shelburne | Wind | RCP8.5 | 2035 | 80.609 | 86.8706 | 93.4743 | 100.0573 | 106.6561
| ShelburneWind2040RCP8.5 | Shelburne | Wind | RCP8.5 | 2040 | 80.7 | 86.9686 | 93.5797 | 100.1701 | 106.7763
| ShelburneWind2045RCP8.5 | Shelburne | Wind | RCP8.5 | 2045 | 80.791 | 87.0666 | 93.6851 | 100.2829 | 106.8964
| ShelburneWind2050RCP8.5 | Shelburne | Wind | RCP8.5 | 2050 | 81.0186 | 87.3491 | 94.0385 | 100.7008 | 107.3735
| ShelburneWind2055RCP8.5 | Shelburne | Wind | RCP8.5 | 2055 | 81.1551 | 87.5336 | 94.2865 | 101.006 | 107.7305
| ShelburneWind2060RCP8.5 | Shelburne | Wind | RCP8.5 | 2060 | 81.6744 | 88.191 | 95.1142 | 101.9845 | 108.8543
| ShelburneWind2065RCP8.5 | Shelburne | Wind | RCP8.5 | 2065 | 82.0572 | 88.6638 | 95.6939 | 102.6578 | 109.6211
| ShelburneWind2070RCP8.5 | Shelburne | Wind | RCP8.5 | 2070 | 82.6514 | 89.4076 | 96.6208 | 103.7359 | 110.858
| ShelburneWind2075RCP8.5 | Shelburne | Wind | RCP8.5 | 2075 | 82.8629 | 89.6786 | 96.968 | 104.1405 | 111.3281
| ShelburneWind2080RCP8.5 | Shelburne | Wind | RCP8.5 | 2080 | 83.0743 | 89.9496 | 97.3152 | 104.5452 | 111.7981
| ShelburneWind2085RCP8.5 | Shelburne | Wind | RCP8.5 | 2085 | 83.251 | 90.1658 | 97.5803 | 104.8537 | 112.1533
| ShelburneWind2090RCP8.5 | Shelburne | Wind | RCP8.5 | 2090 | 83.4277 | 90.3821 | 97.8453 | 105.1622 | 112.5084
| ShelburneWind2095RCP8.5 | Shelburne | Wind | RCP8.5 | 2095 | 83.4277 | 90.3821 | 97.8453 | 105.1622 | 112.5084
| ShelburneWind2100RCP8.5 | Shelburne | Wind | RCP8.5 | 2100 | 83.4277 | 90.3821 | 97.8453 | 105.1622 | 112.5084
| SimcoeIce Accretion2023RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
| SimcoeIce Accretion2025RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2025 | 22.9175 | 27.5192 | 33.3427 | 37.7989 | 42.2402
| SimcoeIce Accretion2030RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2030 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
| SimcoeIce Accretion2035RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2035 | 22.6651 | 27.2464 | 33.048 | 37.4787 | 41.8975
| SimcoeIce Accretion2040RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2040 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
| SimcoeIce Accretion2045RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2045 | 22.4127 | 26.9736 | 32.7533 | 37.1585 | 41.5548
| SimcoeIce Accretion2050RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2050 | 21.7945 | 26.2954 | 31.9872 | 36.3223 | 40.6466
| SimcoeIce Accretion2055RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2055 | 21.3024 | 25.7536 | 31.3684 | 35.6461 | 39.9097
| SimcoeIce Accretion2060RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2060 | 20.8103 | 25.2117 | 30.7496 | 34.9699 | 39.1729
| SimcoeIce Accretion2065RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2065 | 20.3181 | 24.6699 | 30.1308 | 34.2937 | 38.436
| SimcoeIce Accretion2070RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2070 | 19.826 | 24.1281 | 29.512 | 33.6175 | 37.6992
| SimcoeIce Accretion2075RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2075 | 19.5895 | 23.8647 | 29.2117 | 33.2909 | 37.3422
| SimcoeIce Accretion2080RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2080 | 19.3529 | 23.6013 | 28.9113 | 32.9644 | 36.9852
| SimcoeIce Accretion2085RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2085 | 19.1163 | 23.3379 | 28.611 | 32.6378 | 36.6282
| SimcoeIce Accretion2090RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2090 | 18.8797 | 23.0746 | 28.3107 | 32.3112 | 36.2712
| SimcoeIce Accretion2095RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2095 | 18.6431 | 22.8112 | 28.0103 | 31.9846 | 35.9142
| SimcoeIce Accretion2100RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2100 | 18.4065 | 22.5478 | 27.71 | 31.6581 | 35.5572
| SimcoeIce Accretion2023RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
| SimcoeIce Accretion2025RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2025 | 22.9175 | 27.5192 | 33.3427 | 37.7989 | 42.2402
| SimcoeIce Accretion2030RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2030 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
| SimcoeIce Accretion2035RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2035 | 22.6651 | 27.2464 | 33.048 | 37.4787 | 41.8975
| SimcoeIce Accretion2040RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2040 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
| SimcoeIce Accretion2045RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2045 | 22.4127 | 26.9736 | 32.7533 | 37.1585 | 41.5548
| SimcoeIce Accretion2050RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2050 | 21.7945 | 26.2954 | 31.9872 | 36.3223 | 40.6466
| SimcoeIce Accretion2055RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2055 | 21.3024 | 25.7536 | 31.3684 | 35.6461 | 39.9097
| SimcoeIce Accretion2060RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2060 | 20.8103 | 25.2117 | 30.7496 | 34.9699 | 39.1729
| SimcoeIce Accretion2065RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2065 | 20.3181 | 24.6699 | 30.1308 | 34.2937 | 38.436
| SimcoeIce Accretion2070RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2070 | 19.826 | 24.1281 | 29.512 | 33.6175 | 37.6992
| SimcoeIce Accretion2075RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2075 | 19.4712 | 23.733 | 29.0615 | 33.1276 | 37.1637
| SimcoeIce Accretion2080RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2080 | 19.1163 | 23.3379 | 28.611 | 32.6378 | 36.6282
| SimcoeIce Accretion2085RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2085 | 18.7614 | 22.9429 | 28.1605 | 32.1479 | 36.0927
| SimcoeIce Accretion2090RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2090 | 17.4365 | 21.4002 | 26.3613 | 30.1341 | 33.8722
| SimcoeIce Accretion2095RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2095 | 16.4665 | 20.2526 | 25.0127 | 28.6101 | 32.1871
| SimcoeIce Accretion2100RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2100 | 15.4965 | 19.1049 | 23.664 | 27.0861 | 30.5021
| SimcoeIce Accretion2023RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
| SimcoeIce Accretion2025RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2025 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
| SimcoeIce Accretion2030RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2030 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
| SimcoeIce Accretion2035RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2035 | 22.2866 | 26.8372 | 32.606 | 36.9985 | 41.3834
| SimcoeIce Accretion2040RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2040 | 21.4664 | 25.9342 | 31.5747 | 35.8715 | 40.1554
| SimcoeIce Accretion2045RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2045 | 20.6462 | 25.0311 | 30.5433 | 34.7445 | 38.9273
| SimcoeIce Accretion2050RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2050 | 19.3529 | 23.6013 | 28.9113 | 32.9644 | 36.9852
| SimcoeIce Accretion2055RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2055 | 18.8797 | 23.0746 | 28.3107 | 32.3112 | 36.2712
| SimcoeIce Accretion2060RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2060 | 17.4365 | 21.4002 | 26.3613 | 30.1341 | 33.8722
| SimcoeIce Accretion2065RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2065 | 16.4665 | 20.2526 | 25.0127 | 28.6101 | 32.1871
| SimcoeIce Accretion2070RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2070 | 15.0312 | 18.5876 | 23.052 | 26.4073 | 29.7595
| SimcoeIce Accretion2075RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2075 | 14.5659 | 18.0702 | 22.44 | 25.7286 | 29.017
| SimcoeIce Accretion2080RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2080 | 14.1006 | 17.5528 | 21.828 | 25.0498 | 28.2744
| SimcoeIce Accretion2085RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2085 | 13.0596 | 16.297 | 20.332 | 23.3594 | 26.3894
| SimcoeIce Accretion2090RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2090 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
| SimcoeIce Accretion2095RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2095 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
| SimcoeIce Accretion2100RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2100 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
| SimcoeWind2023RCP4.5 | Simcoe | Wind | RCP4.5 | 2023 | 87.7786 | 94.6439 | 101.8888 | 109.1075 | 116.3375
| SimcoeWind2025RCP4.5 | Simcoe | Wind | RCP4.5 | 2025 | 87.8542 | 94.7441 | 102.0218 | 109.2696 | 116.5255
| SimcoeWind2030RCP4.5 | Simcoe | Wind | RCP4.5 | 2030 | 87.9298 | 94.8443 | 102.1548 | 109.4317 | 116.7136
| SimcoeWind2035RCP4.5 | Simcoe | Wind | RCP4.5 | 2035 | 88.0054 | 94.9444 | 102.2877 | 109.5938 | 116.9016
| SimcoeWind2040RCP4.5 | Simcoe | Wind | RCP4.5 | 2040 | 88.0809 | 95.0446 | 102.4207 | 109.7559 | 117.0897
| SimcoeWind2045RCP4.5 | Simcoe | Wind | RCP4.5 | 2045 | 88.1565 | 95.1448 | 102.5537 | 109.918 | 117.2778
| SimcoeWind2050RCP4.5 | Simcoe | Wind | RCP4.5 | 2050 | 88.3106 | 95.3502 | 102.8261 | 110.2465 | 117.6639
| SimcoeWind2055RCP4.5 | Simcoe | Wind | RCP4.5 | 2055 | 88.3891 | 95.4554 | 102.9655 | 110.413 | 117.8619
| SimcoeWind2060RCP4.5 | Simcoe | Wind | RCP4.5 | 2060 | 88.4676 | 95.5606 | 103.1048 | 110.5794 | 118.06
| SimcoeWind2065RCP4.5 | Simcoe | Wind | RCP4.5 | 2065 | 88.5461 | 95.6658 | 103.2442 | 110.7458 | 118.258
| SimcoeWind2070RCP4.5 | Simcoe | Wind | RCP4.5 | 2070 | 88.6246 | 95.771 | 103.3836 | 110.9122 | 118.456
| SimcoeWind2075RCP4.5 | Simcoe | Wind | RCP4.5 | 2075 | 88.7437 | 95.9244 | 103.5806 | 111.1464 | 118.7304
| SimcoeWind2080RCP4.5 | Simcoe | Wind | RCP4.5 | 2080 | 88.8629 | 96.0779 | 103.7775 | 111.3805 | 119.0049
| SimcoeWind2085RCP4.5 | Simcoe | Wind | RCP4.5 | 2085 | 88.9821 | 96.2313 | 103.9744 | 111.6147 | 119.2793
| SimcoeWind2090RCP4.5 | Simcoe | Wind | RCP4.5 | 2090 | 89.1013 | 96.3847 | 104.1714 | 111.8488 | 119.5537
| SimcoeWind2095RCP4.5 | Simcoe | Wind | RCP4.5 | 2095 | 89.2205 | 96.5381 | 104.3683 | 112.083 | 119.8281
| SimcoeWind2100RCP4.5 | Simcoe | Wind | RCP4.5 | 2100 | 89.3397 | 96.6915 | 104.5653 | 112.3172 | 120.1025
| SimcoeWind2023RCP6.0 | Simcoe | Wind | RCP6.0 | 2023 | 87.7786 | 94.6439 | 101.8888 | 109.1075 | 116.3375
| SimcoeWind2025RCP6.0 | Simcoe | Wind | RCP6.0 | 2025 | 87.8542 | 94.7441 | 102.0218 | 109.2696 | 116.5255
| SimcoeWind2030RCP6.0 | Simcoe | Wind | RCP6.0 | 2030 | 87.9298 | 94.8443 | 102.1548 | 109.4317 | 116.7136
| SimcoeWind2035RCP6.0 | Simcoe | Wind | RCP6.0 | 2035 | 88.0054 | 94.9444 | 102.2877 | 109.5938 | 116.9016
| SimcoeWind2040RCP6.0 | Simcoe | Wind | RCP6.0 | 2040 | 88.0809 | 95.0446 | 102.4207 | 109.7559 | 117.0897
| SimcoeWind2045RCP6.0 | Simcoe | Wind | RCP6.0 | 2045 | 88.1565 | 95.1448 | 102.5537 | 109.918 | 117.2778
| SimcoeWind2050RCP6.0 | Simcoe | Wind | RCP6.0 | 2050 | 88.3106 | 95.3502 | 102.8261 | 110.2465 | 117.6639
| SimcoeWind2055RCP6.0 | Simcoe | Wind | RCP6.0 | 2055 | 88.3891 | 95.4554 | 102.9655 | 110.413 | 117.8619
| SimcoeWind2060RCP6.0 | Simcoe | Wind | RCP6.0 | 2060 | 88.4676 | 95.5606 | 103.1048 | 110.5794 | 118.06
| SimcoeWind2065RCP6.0 | Simcoe | Wind | RCP6.0 | 2065 | 88.5461 | 95.6658 | 103.2442 | 110.7458 | 118.258
| SimcoeWind2070RCP6.0 | Simcoe | Wind | RCP6.0 | 2070 | 88.6246 | 95.771 | 103.3836 | 110.9122 | 118.456
| SimcoeWind2075RCP6.0 | Simcoe | Wind | RCP6.0 | 2075 | 88.8033 | 96.0012 | 103.679 | 111.2635 | 118.8677
| SimcoeWind2080RCP6.0 | Simcoe | Wind | RCP6.0 | 2080 | 88.9821 | 96.2313 | 103.9744 | 111.6147 | 119.2793
| SimcoeWind2085RCP6.0 | Simcoe | Wind | RCP6.0 | 2085 | 89.1609 | 96.4614 | 104.2699 | 111.9659 | 119.6909
| SimcoeWind2090RCP6.0 | Simcoe | Wind | RCP6.0 | 2090 | 89.5955 | 97.0234 | 104.9861 | 112.8179 | 120.6782
| SimcoeWind2095RCP6.0 | Simcoe | Wind | RCP6.0 | 2095 | 89.8513 | 97.3553 | 105.407 | 113.3186 | 121.2539
| SimcoeWind2100RCP6.0 | Simcoe | Wind | RCP6.0 | 2100 | 90.1072 | 97.6872 | 105.8278 | 113.8193 | 121.8296
| SimcoeWind2023RCP8.5 | Simcoe | Wind | RCP8.5 | 2023 | 87.7786 | 94.6439 | 101.8888 | 109.1075 | 116.3375
| SimcoeWind2025RCP8.5 | Simcoe | Wind | RCP8.5 | 2025 | 87.9298 | 94.8443 | 102.1548 | 109.4317 | 116.7136
| SimcoeWind2030RCP8.5 | Simcoe | Wind | RCP8.5 | 2030 | 88.0809 | 95.0446 | 102.4207 | 109.7559 | 117.0897
| SimcoeWind2035RCP8.5 | Simcoe | Wind | RCP8.5 | 2035 | 88.2321 | 95.245 | 102.6867 | 110.0801 | 117.4658
| SimcoeWind2040RCP8.5 | Simcoe | Wind | RCP8.5 | 2040 | 88.3629 | 95.4204 | 102.919 | 110.3575 | 117.7959
| SimcoeWind2045RCP8.5 | Simcoe | Wind | RCP8.5 | 2045 | 88.4937 | 95.5957 | 103.1513 | 110.6349 | 118.126
| SimcoeWind2050RCP8.5 | Simcoe | Wind | RCP8.5 | 2050 | 88.8629 | 96.0779 | 103.7775 | 111.3805 | 119.0049
| SimcoeWind2055RCP8.5 | Simcoe | Wind | RCP8.5 | 2055 | 89.1013 | 96.3847 | 104.1714 | 111.8488 | 119.5537
| SimcoeWind2060RCP8.5 | Simcoe | Wind | RCP8.5 | 2060 | 89.5955 | 97.0234 | 104.9861 | 112.8179 | 120.6782
| SimcoeWind2065RCP8.5 | Simcoe | Wind | RCP8.5 | 2065 | 89.8513 | 97.3553 | 105.407 | 113.3186 | 121.2539
| SimcoeWind2070RCP8.5 | Simcoe | Wind | RCP8.5 | 2070 | 90.2554 | 97.897 | 106.1173 | 114.176 | 122.2557
| SimcoeWind2075RCP8.5 | Simcoe | Wind | RCP8.5 | 2075 | 90.4037 | 98.1068 | 106.4069 | 114.5326 | 122.6817
| SimcoeWind2080RCP8.5 | Simcoe | Wind | RCP8.5 | 2080 | 90.5519 | 98.3165 | 106.6964 | 114.8892 | 123.1077
| SimcoeWind2085RCP8.5 | Simcoe | Wind | RCP8.5 | 2085 | 90.8921 | 98.7627 | 107.2873 | 115.5917 | 123.9367
| SimcoeWind2090RCP8.5 | Simcoe | Wind | RCP8.5 | 2090 | 91.2322 | 99.2089 | 107.8781 | 116.2941 | 124.7657
| SimcoeWind2095RCP8.5 | Simcoe | Wind | RCP8.5 | 2095 | 91.2322 | 99.2089 | 107.8781 | 116.2941 | 124.7657
| SimcoeWind2100RCP8.5 | Simcoe | Wind | RCP8.5 | 2100 | 91.2322 | 99.2089 | 107.8781 | 116.2941 | 124.7657
| Sioux LookoutIce Accretion2023RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2023 | 9.245 | 11.0274 | 13.286 | 15.0132 | 16.7404
| Sioux LookoutIce Accretion2025RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2025 | 9.3053 | 11.0939 | 13.3575 | 15.0915 | 16.825
| Sioux LookoutIce Accretion2030RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2030 | 9.3656 | 11.1605 | 13.429 | 15.1699 | 16.9096
| Sioux LookoutIce Accretion2035RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2035 | 9.4259 | 11.227 | 13.5005 | 15.2482 | 16.9943
| Sioux LookoutIce Accretion2040RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2040 | 9.4862 | 11.2935 | 13.572 | 15.3266 | 17.0789
| Sioux LookoutIce Accretion2045RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2045 | 9.5465 | 11.3601 | 13.6435 | 15.4049 | 17.1635
| Sioux LookoutIce Accretion2050RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2050 | 9.6412 | 11.4633 | 13.7592 | 15.5303 | 17.2973
| Sioux LookoutIce Accretion2055RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2055 | 9.6756 | 11.5 | 13.8034 | 15.5773 | 17.3464
| Sioux LookoutIce Accretion2060RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2060 | 9.71 | 11.5367 | 13.8476 | 15.6243 | 17.3956
| Sioux LookoutIce Accretion2065RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2065 | 9.7444 | 11.5734 | 13.8918 | 15.6713 | 17.4447
| Sioux LookoutIce Accretion2070RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2070 | 9.7787 | 11.61 | 13.936 | 15.7183 | 17.4938
| Sioux LookoutIce Accretion2075RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2075 | 9.7908 | 11.6262 | 13.9598 | 15.7477 | 17.5293
| Sioux LookoutIce Accretion2080RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2080 | 9.8028 | 11.6424 | 13.9837 | 15.7771 | 17.5648
| Sioux LookoutIce Accretion2085RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2085 | 9.8149 | 11.6586 | 14.0075 | 15.8064 | 17.6003
| Sioux LookoutIce Accretion2090RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2090 | 9.827 | 11.6748 | 14.0313 | 15.8358 | 17.6358
| Sioux LookoutIce Accretion2095RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2095 | 9.839 | 11.691 | 14.0552 | 15.8652 | 17.6713
| Sioux LookoutIce Accretion2100RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2100 | 9.8511 | 11.7071 | 14.079 | 15.8946 | 17.7068
| Sioux LookoutIce Accretion2023RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2023 | 9.245 | 11.0274 | 13.286 | 15.0132 | 16.7404
| Sioux LookoutIce Accretion2025RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2025 | 9.3053 | 11.0939 | 13.3575 | 15.0915 | 16.825
| Sioux LookoutIce Accretion2030RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2030 | 9.3656 | 11.1605 | 13.429 | 15.1699 | 16.9096
| Sioux LookoutIce Accretion2035RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2035 | 9.4259 | 11.227 | 13.5005 | 15.2482 | 16.9943
| Sioux LookoutIce Accretion2040RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2040 | 9.4862 | 11.2935 | 13.572 | 15.3266 | 17.0789
| Sioux LookoutIce Accretion2045RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2045 | 9.5465 | 11.3601 | 13.6435 | 15.4049 | 17.1635
| Sioux LookoutIce Accretion2050RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2050 | 9.6412 | 11.4633 | 13.7592 | 15.5303 | 17.2973
| Sioux LookoutIce Accretion2055RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2055 | 9.6756 | 11.5 | 13.8034 | 15.5773 | 17.3464
| Sioux LookoutIce Accretion2060RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2060 | 9.71 | 11.5367 | 13.8476 | 15.6243 | 17.3956
| Sioux LookoutIce Accretion2065RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2065 | 9.7444 | 11.5734 | 13.8918 | 15.6713 | 17.4447
| Sioux LookoutIce Accretion2070RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2070 | 9.7787 | 11.61 | 13.936 | 15.7183 | 17.4938
| Sioux LookoutIce Accretion2075RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2075 | 9.7968 | 11.6343 | 13.9718 | 15.7624 | 17.5471
| Sioux LookoutIce Accretion2080RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2080 | 9.8149 | 11.6586 | 14.0075 | 15.8064 | 17.6003
| Sioux LookoutIce Accretion2085RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2085 | 9.833 | 11.6829 | 14.0432 | 15.8505 | 17.6535
| Sioux LookoutIce Accretion2090RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2090 | 9.7636 | 11.61 | 13.9663 | 15.7673 | 17.5648
| Sioux LookoutIce Accretion2095RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2095 | 9.6762 | 11.5129 | 13.8537 | 15.64 | 17.4229
| Sioux LookoutIce Accretion2100RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2100 | 9.5888 | 11.4158 | 13.741 | 15.5126 | 17.2809
| Sioux LookoutIce Accretion2023RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2023 | 9.245 | 11.0274 | 13.286 | 15.0132 | 16.7404
| Sioux LookoutIce Accretion2025RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2025 | 9.3656 | 11.1605 | 13.429 | 15.1699 | 16.9096
| Sioux LookoutIce Accretion2030RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2030 | 9.4862 | 11.2935 | 13.572 | 15.3266 | 17.0789
| Sioux LookoutIce Accretion2035RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2035 | 9.6069 | 11.4266 | 13.715 | 15.4833 | 17.2481
| Sioux LookoutIce Accretion2040RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2040 | 9.6641 | 11.4878 | 13.7887 | 15.5616 | 17.33
| Sioux LookoutIce Accretion2045RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2045 | 9.7214 | 11.5489 | 13.8623 | 15.64 | 17.4119
| Sioux LookoutIce Accretion2050RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2050 | 9.8028 | 11.6424 | 13.9837 | 15.7771 | 17.5648
| Sioux LookoutIce Accretion2055RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2055 | 9.827 | 11.6748 | 14.0313 | 15.8358 | 17.6358
| Sioux LookoutIce Accretion2060RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2060 | 9.7636 | 11.61 | 13.9663 | 15.7673 | 17.5648
| Sioux LookoutIce Accretion2065RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2065 | 9.6762 | 11.5129 | 13.8537 | 15.64 | 17.4229
| Sioux LookoutIce Accretion2070RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2070 | 9.7335 | 11.5992 | 13.9663 | 15.7771 | 17.5812
| Sioux LookoutIce Accretion2075RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2075 | 9.8782 | 11.7827 | 14.1917 | 16.0415 | 17.8815
| Sioux LookoutIce Accretion2080RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2080 | 10.023 | 11.9661 | 14.417 | 16.3059 | 18.1818
| Sioux LookoutIce Accretion2085RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2085 | 9.7516 | 11.6316 | 14.014 | 15.8432 | 17.6658
| Sioux LookoutIce Accretion2090RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2090 | 9.4802 | 11.2971 | 13.611 | 15.3804 | 17.1499
| Sioux LookoutIce Accretion2095RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2095 | 9.4802 | 11.2971 | 13.611 | 15.3804 | 17.1499
| Sioux LookoutIce Accretion2100RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2100 | 9.4802 | 11.2971 | 13.611 | 15.3804 | 17.1499
| Sioux LookoutWind2023RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2023 | 71.2304 | 76.7633 | 82.5986 | 88.4156 | 94.2372
| Sioux LookoutWind2025RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2025 | 71.2481 | 76.7671 | 82.5849 | 88.3878 | 94.1951
| Sioux LookoutWind2030RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2030 | 71.2658 | 76.7709 | 82.5713 | 88.36 | 94.1531
| Sioux LookoutWind2035RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2035 | 71.2835 | 76.7748 | 82.5576 | 88.3322 | 94.111
| Sioux LookoutWind2040RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2040 | 71.3012 | 76.7786 | 82.5439 | 88.3045 | 94.0689
| Sioux LookoutWind2045RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2045 | 71.3189 | 76.7824 | 82.5303 | 88.2767 | 94.0269
| Sioux LookoutWind2050RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2050 | 71.3961 | 76.8625 | 82.6117 | 88.3612 | 94.1138
| Sioux LookoutWind2055RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2055 | 71.4556 | 76.9387 | 82.7068 | 88.4735 | 94.2428
| Sioux LookoutWind2060RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2060 | 71.515 | 77.015 | 82.802 | 88.5858 | 94.3718
| Sioux LookoutWind2065RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2065 | 71.5745 | 77.0912 | 82.8971 | 88.6981 | 94.5008
| Sioux LookoutWind2070RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2070 | 71.634 | 77.1675 | 82.9922 | 88.8104 | 94.6298
| Sioux LookoutWind2075RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2075 | 71.7437 | 77.3022 | 83.1576 | 89.0035 | 94.851
| Sioux LookoutWind2080RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2080 | 71.8535 | 77.4369 | 83.3229 | 89.1965 | 95.0723
| Sioux LookoutWind2085RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2085 | 71.9632 | 77.5717 | 83.4883 | 89.3895 | 95.2935
| Sioux LookoutWind2090RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2090 | 72.073 | 77.7064 | 83.6537 | 89.5825 | 95.5147
| Sioux LookoutWind2095RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2095 | 72.1827 | 77.8411 | 83.819 | 89.7756 | 95.736
| Sioux LookoutWind2100RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2100 | 72.2925 | 77.9759 | 83.9844 | 89.9686 | 95.9572
| Sioux LookoutWind2023RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2023 | 71.2304 | 76.7633 | 82.5986 | 88.4156 | 94.2372
| Sioux LookoutWind2025RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2025 | 71.2481 | 76.7671 | 82.5849 | 88.3878 | 94.1951
| Sioux LookoutWind2030RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2030 | 71.2658 | 76.7709 | 82.5713 | 88.36 | 94.1531
| Sioux LookoutWind2035RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2035 | 71.2835 | 76.7748 | 82.5576 | 88.3322 | 94.111
| Sioux LookoutWind2040RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2040 | 71.3012 | 76.7786 | 82.5439 | 88.3045 | 94.0689
| Sioux LookoutWind2045RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2045 | 71.3189 | 76.7824 | 82.5303 | 88.2767 | 94.0269
| Sioux LookoutWind2050RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2050 | 71.3961 | 76.8625 | 82.6117 | 88.3612 | 94.1138
| Sioux LookoutWind2055RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2055 | 71.4556 | 76.9387 | 82.7068 | 88.4735 | 94.2428
| Sioux LookoutWind2060RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2060 | 71.515 | 77.015 | 82.802 | 88.5858 | 94.3718
| Sioux LookoutWind2065RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2065 | 71.5745 | 77.0912 | 82.8971 | 88.6981 | 94.5008
| Sioux LookoutWind2070RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2070 | 71.634 | 77.1675 | 82.9922 | 88.8104 | 94.6298
| Sioux LookoutWind2075RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2075 | 71.7986 | 77.3696 | 83.2403 | 89.1 | 94.9617
| Sioux LookoutWind2080RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2080 | 71.9632 | 77.5717 | 83.4883 | 89.3895 | 95.2935
| Sioux LookoutWind2085RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2085 | 72.1279 | 77.7738 | 83.7363 | 89.6791 | 95.6254
| Sioux LookoutWind2090RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2090 | 72.4341 | 78.164 | 84.2331 | 90.2669 | 96.3031
| Sioux LookoutWind2095RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2095 | 72.5757 | 78.3521 | 84.4819 | 90.5652 | 96.649
| Sioux LookoutWind2100RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2100 | 72.7173 | 78.5402 | 84.7306 | 90.8635 | 96.9948
| Sioux LookoutWind2023RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2023 | 71.2304 | 76.7633 | 82.5986 | 88.4156 | 94.2372
| Sioux LookoutWind2025RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2025 | 71.2658 | 76.7709 | 82.5713 | 88.36 | 94.1531
| Sioux LookoutWind2030RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2030 | 71.3012 | 76.7786 | 82.5439 | 88.3045 | 94.0689
| Sioux LookoutWind2035RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2035 | 71.3366 | 76.7862 | 82.5166 | 88.2489 | 93.9848
| Sioux LookoutWind2040RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2040 | 71.4357 | 76.9133 | 82.6751 | 88.4361 | 94.1998
| Sioux LookoutWind2045RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2045 | 71.5349 | 77.0404 | 82.8337 | 88.6232 | 94.4148
| Sioux LookoutWind2050RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2050 | 71.8535 | 77.4369 | 83.3229 | 89.1965 | 95.0723
| Sioux LookoutWind2055RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2055 | 72.073 | 77.7064 | 83.6537 | 89.5825 | 95.5147
| Sioux LookoutWind2060RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2060 | 72.4341 | 78.164 | 84.2331 | 90.2669 | 96.3031
| Sioux LookoutWind2065RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2065 | 72.5757 | 78.3521 | 84.4819 | 90.5652 | 96.649
| Sioux LookoutWind2070RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2070 | 72.8448 | 78.6749 | 84.8727 | 91.0098 | 97.1506
| Sioux LookoutWind2075RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2075 | 72.9722 | 78.8096 | 85.0149 | 91.156 | 97.3064
| Sioux LookoutWind2080RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2080 | 73.0997 | 78.9444 | 85.157 | 91.3022 | 97.4622
| Sioux LookoutWind2085RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2085 | 73.2625 | 79.135 | 85.3784 | 91.5611 | 97.7474
| Sioux LookoutWind2090RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2090 | 73.4254 | 79.3257 | 85.5998 | 91.8199 | 98.0325
| Sioux LookoutWind2095RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2095 | 73.4254 | 79.3257 | 85.5998 | 91.8199 | 98.0325
| Sioux LookoutWind2100RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2100 | 73.4254 | 79.3257 | 85.5998 | 91.8199 | 98.0325
| Smiths FallsIce Accretion2023RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2023 | 17.9473 | 21.3426 | 25.636 | 28.9393 | 32.2358
| Smiths FallsIce Accretion2025RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2025 | 17.9412 | 21.339 | 25.6403 | 28.9491 | 32.2468
| Smiths FallsIce Accretion2030RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2030 | 17.9352 | 21.3354 | 25.6447 | 28.9589 | 32.2577
| Smiths FallsIce Accretion2035RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2035 | 17.9292 | 21.3318 | 25.649 | 28.9687 | 32.2686
| Smiths FallsIce Accretion2040RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2040 | 17.9231 | 21.3282 | 25.6533 | 28.9785 | 32.2795
| Smiths FallsIce Accretion2045RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2045 | 17.9171 | 21.3246 | 25.6577 | 28.9883 | 32.2904
| Smiths FallsIce Accretion2050RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2050 | 17.9147 | 21.3426 | 25.7036 | 29.0568 | 32.3734
| Smiths FallsIce Accretion2055RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2055 | 17.9183 | 21.3642 | 25.7452 | 29.1156 | 32.4455
| Smiths FallsIce Accretion2060RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2060 | 17.9219 | 21.3858 | 25.7868 | 29.1743 | 32.5176
| Smiths FallsIce Accretion2065RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2065 | 17.9256 | 21.4074 | 25.8284 | 29.2331 | 32.5896
| Smiths FallsIce Accretion2070RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2070 | 17.9292 | 21.4289 | 25.87 | 29.2919 | 32.6617
| Smiths FallsIce Accretion2075RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2075 | 18.0106 | 21.5476 | 26.0347 | 29.4877 | 32.8965
| Smiths FallsIce Accretion2080RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2080 | 18.092 | 21.6663 | 26.1993 | 29.6836 | 33.1313
| Smiths FallsIce Accretion2085RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2085 | 18.1734 | 21.785 | 26.364 | 29.8795 | 33.3661
| Smiths FallsIce Accretion2090RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2090 | 18.2548 | 21.9037 | 26.5287 | 30.0753 | 33.6008
| Smiths FallsIce Accretion2095RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2095 | 18.3362 | 22.0224 | 26.6933 | 30.2712 | 33.8356
| Smiths FallsIce Accretion2100RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2100 | 18.4177 | 22.1411 | 26.858 | 30.4671 | 34.0704
| Smiths FallsIce Accretion2023RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2023 | 17.9473 | 21.3426 | 25.636 | 28.9393 | 32.2358
| Smiths FallsIce Accretion2025RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2025 | 17.9412 | 21.339 | 25.6403 | 28.9491 | 32.2468
| Smiths FallsIce Accretion2030RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2030 | 17.9352 | 21.3354 | 25.6447 | 28.9589 | 32.2577
| Smiths FallsIce Accretion2035RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2035 | 17.9292 | 21.3318 | 25.649 | 28.9687 | 32.2686
| Smiths FallsIce Accretion2040RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2040 | 17.9231 | 21.3282 | 25.6533 | 28.9785 | 32.2795
| Smiths FallsIce Accretion2045RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2045 | 17.9171 | 21.3246 | 25.6577 | 28.9883 | 32.2904
| Smiths FallsIce Accretion2050RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2050 | 17.9147 | 21.3426 | 25.7036 | 29.0568 | 32.3734
| Smiths FallsIce Accretion2055RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2055 | 17.9183 | 21.3642 | 25.7452 | 29.1156 | 32.4455
| Smiths FallsIce Accretion2060RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2060 | 17.9219 | 21.3858 | 25.7868 | 29.1743 | 32.5176
| Smiths FallsIce Accretion2065RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2065 | 17.9256 | 21.4074 | 25.8284 | 29.2331 | 32.5896
| Smiths FallsIce Accretion2070RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2070 | 17.9292 | 21.4289 | 25.87 | 29.2919 | 32.6617
| Smiths FallsIce Accretion2075RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2075 | 18.0513 | 21.607 | 26.117 | 29.5857 | 33.0139
| Smiths FallsIce Accretion2080RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2080 | 18.1734 | 21.785 | 26.364 | 29.8795 | 33.3661
| Smiths FallsIce Accretion2085RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2085 | 18.2955 | 21.963 | 26.611 | 30.1733 | 33.7182
| Smiths FallsIce Accretion2090RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2090 | 18.4056 | 22.1627 | 26.9273 | 30.5552 | 34.1905
| Smiths FallsIce Accretion2095RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2095 | 18.3935 | 22.1842 | 26.9967 | 30.6433 | 34.3106
| Smiths FallsIce Accretion2100RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2100 | 18.3815 | 22.2058 | 27.066 | 30.7315 | 34.4308
| Smiths FallsIce Accretion2023RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2023 | 17.9473 | 21.3426 | 25.636 | 28.9393 | 32.2358
| Smiths FallsIce Accretion2025RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2025 | 17.9352 | 21.3354 | 25.6447 | 28.9589 | 32.2577
| Smiths FallsIce Accretion2030RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2030 | 17.9231 | 21.3282 | 25.6533 | 28.9785 | 32.2795
| Smiths FallsIce Accretion2035RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2035 | 17.9111 | 21.321 | 25.662 | 28.9981 | 32.3014
| Smiths FallsIce Accretion2040RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2040 | 17.9171 | 21.357 | 25.7313 | 29.096 | 32.4215
| Smiths FallsIce Accretion2045RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2045 | 17.9231 | 21.393 | 25.8007 | 29.1939 | 32.5416
| Smiths FallsIce Accretion2050RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2050 | 18.092 | 21.6663 | 26.1993 | 29.6836 | 33.1313
| Smiths FallsIce Accretion2055RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2055 | 18.2548 | 21.9037 | 26.5287 | 30.0753 | 33.6008
| Smiths FallsIce Accretion2060RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2060 | 18.4056 | 22.1627 | 26.9273 | 30.5552 | 34.1905
| Smiths FallsIce Accretion2065RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2065 | 18.3935 | 22.1842 | 26.9967 | 30.6433 | 34.3106
| Smiths FallsIce Accretion2070RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2070 | 18.1885 | 22.0044 | 26.8493 | 30.5062 | 34.1905
| Smiths FallsIce Accretion2075RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2075 | 17.9955 | 21.803 | 26.6327 | 30.281 | 33.9503
| Smiths FallsIce Accretion2080RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2080 | 17.8025 | 21.6016 | 26.416 | 30.0557 | 33.71
| Smiths FallsIce Accretion2085RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2085 | 17.0608 | 20.7492 | 25.415 | 28.954 | 32.4979
| Smiths FallsIce Accretion2090RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2090 | 16.319 | 19.8968 | 24.414 | 27.8522 | 31.2858
| Smiths FallsIce Accretion2095RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2095 | 16.319 | 19.8968 | 24.414 | 27.8522 | 31.2858
| Smiths FallsIce Accretion2100RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2100 | 16.319 | 19.8968 | 24.414 | 27.8522 | 31.2858
| Smiths FallsWind2023RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2023 | 76.5564 | 82.5275 | 88.8272 | 95.1016 | 101.3834
| Smiths FallsWind2025RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2025 | 76.6665 | 82.6598 | 88.9871 | 95.2868 | 101.5941
| Smiths FallsWind2030RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2030 | 76.7767 | 82.7921 | 89.1469 | 95.472 | 101.8047
| Smiths FallsWind2035RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2035 | 76.8869 | 82.9244 | 89.3068 | 95.6571 | 102.0154
| Smiths FallsWind2040RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2040 | 76.9971 | 83.0567 | 89.4667 | 95.8423 | 102.2261
| Smiths FallsWind2045RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2045 | 77.1073 | 83.189 | 89.6265 | 96.0275 | 102.4368
| Smiths FallsWind2050RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2050 | 77.2022 | 83.2984 | 89.7547 | 96.1731 | 102.5993
| Smiths FallsWind2055RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2055 | 77.187 | 83.2755 | 89.723 | 96.1336 | 102.5511
| Smiths FallsWind2060RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2060 | 77.1718 | 83.2526 | 89.6914 | 96.094 | 102.503
| Smiths FallsWind2065RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2065 | 77.1566 | 83.2296 | 89.6597 | 96.0545 | 102.4548
| Smiths FallsWind2070RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2070 | 77.1414 | 83.2067 | 89.628 | 96.015 | 102.4067
| Smiths FallsWind2075RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2075 | 77.1693 | 83.2436 | 89.6779 | 96.0746 | 102.4752
| Smiths FallsWind2080RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2080 | 77.1972 | 83.2804 | 89.7277 | 96.1342 | 102.5438
| Smiths FallsWind2085RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2085 | 77.225 | 83.3172 | 89.7776 | 96.1939 | 102.6123
| Smiths FallsWind2090RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2090 | 77.2529 | 83.354 | 89.8275 | 96.2535 | 102.6809
| Smiths FallsWind2095RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2095 | 77.2808 | 83.3909 | 89.8773 | 96.3131 | 102.7494
| Smiths FallsWind2100RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2100 | 77.3086 | 83.4277 | 89.9272 | 96.3728 | 102.818
| Smiths FallsWind2023RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2023 | 76.5564 | 82.5275 | 88.8272 | 95.1016 | 101.3834
| Smiths FallsWind2025RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2025 | 76.6665 | 82.6598 | 88.9871 | 95.2868 | 101.5941
| Smiths FallsWind2030RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2030 | 76.7767 | 82.7921 | 89.1469 | 95.472 | 101.8047
| Smiths FallsWind2035RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2035 | 76.8869 | 82.9244 | 89.3068 | 95.6571 | 102.0154
| Smiths FallsWind2040RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2040 | 76.9971 | 83.0567 | 89.4667 | 95.8423 | 102.2261
| Smiths FallsWind2045RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2045 | 77.1073 | 83.189 | 89.6265 | 96.0275 | 102.4368
| Smiths FallsWind2050RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2050 | 77.2022 | 83.2984 | 89.7547 | 96.1731 | 102.5993
| Smiths FallsWind2055RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2055 | 77.187 | 83.2755 | 89.723 | 96.1336 | 102.5511
| Smiths FallsWind2060RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2060 | 77.1718 | 83.2526 | 89.6914 | 96.094 | 102.503
| Smiths FallsWind2065RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2065 | 77.1566 | 83.2296 | 89.6597 | 96.0545 | 102.4548
| Smiths FallsWind2070RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2070 | 77.1414 | 83.2067 | 89.628 | 96.015 | 102.4067
| Smiths FallsWind2075RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2075 | 77.1832 | 83.262 | 89.7028 | 96.1044 | 102.5095
| Smiths FallsWind2080RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2080 | 77.225 | 83.3172 | 89.7776 | 96.1939 | 102.6123
| Smiths FallsWind2085RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2085 | 77.2668 | 83.3725 | 89.8524 | 96.2833 | 102.7151
| Smiths FallsWind2090RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2090 | 77.2529 | 83.3431 | 89.7981 | 96.2127 | 102.624
| Smiths FallsWind2095RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2095 | 77.1972 | 83.2586 | 89.6691 | 96.0526 | 102.4301
| Smiths FallsWind2100RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2100 | 77.1414 | 83.174 | 89.54 | 95.8925 | 102.2361
| Smiths FallsWind2023RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2023 | 76.5564 | 82.5275 | 88.8272 | 95.1016 | 101.3834
| Smiths FallsWind2025RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2025 | 76.7767 | 82.7921 | 89.1469 | 95.472 | 101.8047
| Smiths FallsWind2030RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2030 | 76.9971 | 83.0567 | 89.4667 | 95.8423 | 102.2261
| Smiths FallsWind2035RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2035 | 77.2174 | 83.3213 | 89.7864 | 96.2127 | 102.6474
| Smiths FallsWind2040RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2040 | 77.1921 | 83.2831 | 89.7336 | 96.1468 | 102.5672
| Smiths FallsWind2045RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2045 | 77.1668 | 83.2449 | 89.6808 | 96.0809 | 102.4869
| Smiths FallsWind2050RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2050 | 77.1972 | 83.2804 | 89.7277 | 96.1342 | 102.5438
| Smiths FallsWind2055RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2055 | 77.2529 | 83.354 | 89.8275 | 96.2535 | 102.6809
| Smiths FallsWind2060RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2060 | 77.2529 | 83.3431 | 89.7981 | 96.2127 | 102.624
| Smiths FallsWind2065RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2065 | 77.1972 | 83.2586 | 89.6691 | 96.0526 | 102.4301
| Smiths FallsWind2070RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2070 | 77.1744 | 83.204 | 89.5664 | 95.9177 | 102.2595
| Smiths FallsWind2075RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2075 | 77.2073 | 83.234 | 89.5928 | 95.9428 | 102.2829
| Smiths FallsWind2080RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2080 | 77.2402 | 83.264 | 89.6192 | 95.9679 | 102.3063
| Smiths FallsWind2085RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2085 | 77.2668 | 83.3049 | 89.6764 | 96.0338 | 102.3866
| Smiths FallsWind2090RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2090 | 77.2934 | 83.3459 | 89.7336 | 96.0997 | 102.4668
| Smiths FallsWind2095RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2095 | 77.2934 | 83.3459 | 89.7336 | 96.0997 | 102.4668
| Smiths FallsWind2100RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2100 | 77.2934 | 83.3459 | 89.7336 | 96.0997 | 102.4668
| SmithvilleIce Accretion2023RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
| SmithvilleIce Accretion2025RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2025 | 21.9182 | 26.3121 | 31.8773 | 36.1299 | 40.3738
| SmithvilleIce Accretion2030RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2030 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
| SmithvilleIce Accretion2035RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2035 | 21.7104 | 26.0819 | 31.632 | 35.8526 | 40.0781
| SmithvilleIce Accretion2040RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2040 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
| SmithvilleIce Accretion2045RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2045 | 21.5026 | 25.8517 | 31.3867 | 35.5754 | 39.7824
| SmithvilleIce Accretion2050RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2050 | 20.9221 | 25.2001 | 30.6368 | 34.7425 | 38.8765
| SmithvilleIce Accretion2055RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2055 | 20.4456 | 24.6636 | 30.0096 | 34.0483 | 38.1185
| SmithvilleIce Accretion2060RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2060 | 19.9691 | 24.1271 | 29.3824 | 33.354 | 37.3605
| SmithvilleIce Accretion2065RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2065 | 19.4926 | 23.5906 | 28.7552 | 32.6597 | 36.6025
| SmithvilleIce Accretion2070RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2070 | 19.0161 | 23.0541 | 28.128 | 31.9654 | 35.8445
| SmithvilleIce Accretion2075RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2075 | 18.8379 | 22.8682 | 27.9307 | 31.7605 | 35.6294
| SmithvilleIce Accretion2080RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2080 | 18.6598 | 22.6822 | 27.7333 | 31.5556 | 35.4144
| SmithvilleIce Accretion2085RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2085 | 18.4817 | 22.4963 | 27.536 | 31.3507 | 35.1994
| SmithvilleIce Accretion2090RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2090 | 18.3035 | 22.3104 | 27.3387 | 31.1458 | 34.9843
| SmithvilleIce Accretion2095RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2095 | 18.1254 | 22.1245 | 27.1413 | 30.9409 | 34.7693
| SmithvilleIce Accretion2100RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2100 | 17.9473 | 21.9386 | 26.944 | 30.736 | 34.5542
| SmithvilleIce Accretion2023RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
| SmithvilleIce Accretion2025RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2025 | 21.9182 | 26.3121 | 31.8773 | 36.1299 | 40.3738
| SmithvilleIce Accretion2030RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2030 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
| SmithvilleIce Accretion2035RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2035 | 21.7104 | 26.0819 | 31.632 | 35.8526 | 40.0781
| SmithvilleIce Accretion2040RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2040 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
| SmithvilleIce Accretion2045RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2045 | 21.5026 | 25.8517 | 31.3867 | 35.5754 | 39.7824
| SmithvilleIce Accretion2050RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2050 | 20.9221 | 25.2001 | 30.6368 | 34.7425 | 38.8765
| SmithvilleIce Accretion2055RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2055 | 20.4456 | 24.6636 | 30.0096 | 34.0483 | 38.1185
| SmithvilleIce Accretion2060RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2060 | 19.9691 | 24.1271 | 29.3824 | 33.354 | 37.3605
| SmithvilleIce Accretion2065RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2065 | 19.4926 | 23.5906 | 28.7552 | 32.6597 | 36.6025
| SmithvilleIce Accretion2070RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2070 | 19.0161 | 23.0541 | 28.128 | 31.9654 | 35.8445
| SmithvilleIce Accretion2075RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2075 | 18.7489 | 22.7752 | 27.832 | 31.6581 | 35.5219
| SmithvilleIce Accretion2080RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2080 | 18.4817 | 22.4963 | 27.536 | 31.3507 | 35.1994
| SmithvilleIce Accretion2085RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2085 | 18.2145 | 22.2174 | 27.24 | 31.0434 | 34.8768
| SmithvilleIce Accretion2090RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2090 | 17.2199 | 21.1063 | 25.9733 | 29.6633 | 33.3581
| SmithvilleIce Accretion2095RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2095 | 16.4925 | 20.2741 | 25.0027 | 28.5905 | 32.1619
| SmithvilleIce Accretion2100RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2100 | 15.7651 | 19.4419 | 24.032 | 27.5178 | 30.9658
| SmithvilleIce Accretion2023RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
| SmithvilleIce Accretion2025RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2025 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
| SmithvilleIce Accretion2030RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2030 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
| SmithvilleIce Accretion2035RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2035 | 21.3987 | 25.7366 | 31.264 | 35.4368 | 39.6346
| SmithvilleIce Accretion2040RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2040 | 20.6045 | 24.8425 | 30.2187 | 34.2797 | 38.3712
| SmithvilleIce Accretion2045RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2045 | 19.8103 | 23.9483 | 29.1733 | 33.1226 | 37.1078
| SmithvilleIce Accretion2050RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2050 | 18.6598 | 22.6822 | 27.7333 | 31.5556 | 35.4144
| SmithvilleIce Accretion2055RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2055 | 18.3035 | 22.3104 | 27.3387 | 31.1458 | 34.9843
| SmithvilleIce Accretion2060RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2060 | 17.2199 | 21.1063 | 25.9733 | 29.6633 | 33.3581
| SmithvilleIce Accretion2065RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2065 | 16.4925 | 20.2741 | 25.0027 | 28.5905 | 32.1619
| SmithvilleIce Accretion2070RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2070 | 15.4014 | 19.0258 | 23.5627 | 26.9995 | 30.4013
| SmithvilleIce Accretion2075RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2075 | 15.0377 | 18.6097 | 23.0933 | 26.4812 | 29.8368
| SmithvilleIce Accretion2080RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2080 | 14.674 | 18.1936 | 22.624 | 25.9629 | 29.2723
| SmithvilleIce Accretion2085RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2085 | 13.8501 | 17.2242 | 21.456 | 24.643 | 27.8006
| SmithvilleIce Accretion2090RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2090 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
| SmithvilleIce Accretion2095RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2095 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
| SmithvilleIce Accretion2100RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2100 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
| SmithvilleWind2023RCP4.5 | Smithville | Wind | RCP4.5 | 2023 | 88.11 | 95.1229 | 102.5655 | 109.9612 | 117.3507
| SmithvilleWind2025RCP4.5 | Smithville | Wind | RCP4.5 | 2025 | 88.0809 | 95.0932 | 102.5335 | 109.927 | 117.3142
| SmithvilleWind2030RCP4.5 | Smithville | Wind | RCP4.5 | 2030 | 88.0519 | 95.0634 | 102.5015 | 109.8928 | 117.2778
| SmithvilleWind2035RCP4.5 | Smithville | Wind | RCP4.5 | 2035 | 88.0228 | 95.0337 | 102.4695 | 109.8586 | 117.2413
| SmithvilleWind2040RCP4.5 | Smithville | Wind | RCP4.5 | 2040 | 87.9937 | 95.0039 | 102.4376 | 109.8243 | 117.2048
| SmithvilleWind2045RCP4.5 | Smithville | Wind | RCP4.5 | 2045 | 87.9647 | 94.9742 | 102.4056 | 109.7901 | 117.1684
| SmithvilleWind2050RCP4.5 | Smithville | Wind | RCP4.5 | 2050 | 87.9931 | 95.0177 | 102.4685 | 109.8661 | 117.2609
| SmithvilleWind2055RCP4.5 | Smithville | Wind | RCP4.5 | 2055 | 88.0507 | 95.091 | 102.5635 | 109.9764 | 117.3898
| SmithvilleWind2060RCP4.5 | Smithville | Wind | RCP4.5 | 2060 | 88.1083 | 95.1642 | 102.6584 | 110.0866 | 117.5188
| SmithvilleWind2065RCP4.5 | Smithville | Wind | RCP4.5 | 2065 | 88.1658 | 95.2375 | 102.7534 | 110.1968 | 117.6477
| SmithvilleWind2070RCP4.5 | Smithville | Wind | RCP4.5 | 2070 | 88.2234 | 95.3108 | 102.8483 | 110.307 | 117.7767
| SmithvilleWind2075RCP4.5 | Smithville | Wind | RCP4.5 | 2075 | 88.3048 | 95.4251 | 103.0049 | 110.498 | 118.0051
| SmithvilleWind2080RCP4.5 | Smithville | Wind | RCP4.5 | 2080 | 88.3862 | 95.5393 | 103.1614 | 110.6889 | 118.2334
| SmithvilleWind2085RCP4.5 | Smithville | Wind | RCP4.5 | 2085 | 88.4676 | 95.6536 | 103.3179 | 110.8798 | 118.4618
| SmithvilleWind2090RCP4.5 | Smithville | Wind | RCP4.5 | 2090 | 88.549 | 95.7679 | 103.4745 | 111.0707 | 118.6901
| SmithvilleWind2095RCP4.5 | Smithville | Wind | RCP4.5 | 2095 | 88.6304 | 95.8822 | 103.6311 | 111.2617 | 118.9185
| SmithvilleWind2100RCP4.5 | Smithville | Wind | RCP4.5 | 2100 | 88.7118 | 95.9965 | 103.7876 | 111.4526 | 119.1469
| SmithvilleWind2023RCP6.0 | Smithville | Wind | RCP6.0 | 2023 | 88.11 | 95.1229 | 102.5655 | 109.9612 | 117.3507
| SmithvilleWind2025RCP6.0 | Smithville | Wind | RCP6.0 | 2025 | 88.0809 | 95.0932 | 102.5335 | 109.927 | 117.3142
| SmithvilleWind2030RCP6.0 | Smithville | Wind | RCP6.0 | 2030 | 88.0519 | 95.0634 | 102.5015 | 109.8928 | 117.2778
| SmithvilleWind2035RCP6.0 | Smithville | Wind | RCP6.0 | 2035 | 88.0228 | 95.0337 | 102.4695 | 109.8586 | 117.2413
| SmithvilleWind2040RCP6.0 | Smithville | Wind | RCP6.0 | 2040 | 87.9937 | 95.0039 | 102.4376 | 109.8243 | 117.2048
| SmithvilleWind2045RCP6.0 | Smithville | Wind | RCP6.0 | 2045 | 87.9647 | 94.9742 | 102.4056 | 109.7901 | 117.1684
| SmithvilleWind2050RCP6.0 | Smithville | Wind | RCP6.0 | 2050 | 87.9931 | 95.0177 | 102.4685 | 109.8661 | 117.2609
| SmithvilleWind2055RCP6.0 | Smithville | Wind | RCP6.0 | 2055 | 88.0507 | 95.091 | 102.5635 | 109.9764 | 117.3898
| SmithvilleWind2060RCP6.0 | Smithville | Wind | RCP6.0 | 2060 | 88.1083 | 95.1642 | 102.6584 | 110.0866 | 117.5188
| SmithvilleWind2065RCP6.0 | Smithville | Wind | RCP6.0 | 2065 | 88.1658 | 95.2375 | 102.7534 | 110.1968 | 117.6477
| SmithvilleWind2070RCP6.0 | Smithville | Wind | RCP6.0 | 2070 | 88.2234 | 95.3108 | 102.8483 | 110.307 | 117.7767
| SmithvilleWind2075RCP6.0 | Smithville | Wind | RCP6.0 | 2075 | 88.3455 | 95.4822 | 103.0831 | 110.5934 | 118.1192
| SmithvilleWind2080RCP6.0 | Smithville | Wind | RCP6.0 | 2080 | 88.4676 | 95.6536 | 103.3179 | 110.8798 | 118.4618
| SmithvilleWind2085RCP6.0 | Smithville | Wind | RCP6.0 | 2085 | 88.5897 | 95.825 | 103.5528 | 111.1662 | 118.8043
| SmithvilleWind2090RCP6.0 | Smithville | Wind | RCP6.0 | 2090 | 88.8978 | 96.2344 | 104.0872 | 111.8092 | 119.5614
| SmithvilleWind2095RCP6.0 | Smithville | Wind | RCP6.0 | 2095 | 89.0839 | 96.4724 | 104.3869 | 112.1659 | 119.9759
| SmithvilleWind2100RCP6.0 | Smithville | Wind | RCP6.0 | 2100 | 89.2699 | 96.7103 | 104.6865 | 112.5225 | 120.3904
| SmithvilleWind2023RCP8.5 | Smithville | Wind | RCP8.5 | 2023 | 88.11 | 95.1229 | 102.5655 | 109.9612 | 117.3507
| SmithvilleWind2025RCP8.5 | Smithville | Wind | RCP8.5 | 2025 | 88.0519 | 95.0634 | 102.5015 | 109.8928 | 117.2778
| SmithvilleWind2030RCP8.5 | Smithville | Wind | RCP8.5 | 2030 | 87.9937 | 95.0039 | 102.4376 | 109.8243 | 117.2048
| SmithvilleWind2035RCP8.5 | Smithville | Wind | RCP8.5 | 2035 | 87.9356 | 94.9444 | 102.3736 | 109.7559 | 117.1319
| SmithvilleWind2040RCP8.5 | Smithville | Wind | RCP8.5 | 2040 | 88.0315 | 95.0666 | 102.5318 | 109.9396 | 117.3468
| SmithvilleWind2045RCP8.5 | Smithville | Wind | RCP8.5 | 2045 | 88.1274 | 95.1887 | 102.6901 | 110.1233 | 117.5618
| SmithvilleWind2050RCP8.5 | Smithville | Wind | RCP8.5 | 2050 | 88.3862 | 95.5393 | 103.1614 | 110.6889 | 118.2334
| SmithvilleWind2055RCP8.5 | Smithville | Wind | RCP8.5 | 2055 | 88.549 | 95.7679 | 103.4745 | 111.0707 | 118.6901
| SmithvilleWind2060RCP8.5 | Smithville | Wind | RCP8.5 | 2060 | 88.8978 | 96.2344 | 104.0872 | 111.8092 | 119.5614
| SmithvilleWind2065RCP8.5 | Smithville | Wind | RCP8.5 | 2065 | 89.0839 | 96.4724 | 104.3869 | 112.1659 | 119.9759
| SmithvilleWind2070RCP8.5 | Smithville | Wind | RCP8.5 | 2070 | 89.331 | 96.8137 | 104.8515 | 112.7386 | 120.6514
| SmithvilleWind2075RCP8.5 | Smithville | Wind | RCP8.5 | 2075 | 89.392 | 96.917 | 105.0164 | 112.9548 | 120.9124
| SmithvilleWind2080RCP8.5 | Smithville | Wind | RCP8.5 | 2080 | 89.4531 | 97.0203 | 105.1814 | 113.1709 | 121.1733
| SmithvilleWind2085RCP8.5 | Smithville | Wind | RCP8.5 | 2085 | 89.5185 | 97.1283 | 105.338 | 113.3654 | 121.4151
| SmithvilleWind2090RCP8.5 | Smithville | Wind | RCP8.5 | 2090 | 89.5839 | 97.2363 | 105.4945 | 113.56 | 121.6569
| SmithvilleWind2095RCP8.5 | Smithville | Wind | RCP8.5 | 2095 | 89.5839 | 97.2363 | 105.4945 | 113.56 | 121.6569
| SmithvilleWind2100RCP8.5 | Smithville | Wind | RCP8.5 | 2100 | 89.5839 | 97.2363 | 105.4945 | 113.56 | 121.6569
| Smooth Rock FallsIce Accretion2023RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2023 | 11.256 | 13.4128 | 16.144 | 18.2246 | 20.3213
| Smooth Rock FallsIce Accretion2025RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2025 | 11.2542 | 13.4084 | 16.136 | 18.2156 | 20.3078
| Smooth Rock FallsIce Accretion2030RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2030 | 11.2523 | 13.4039 | 16.128 | 18.2066 | 20.2944
| Smooth Rock FallsIce Accretion2035RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2035 | 11.2504 | 13.3995 | 16.12 | 18.1975 | 20.281
| Smooth Rock FallsIce Accretion2040RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2040 | 11.2486 | 13.3951 | 16.112 | 18.1885 | 20.2675
| Smooth Rock FallsIce Accretion2045RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2045 | 11.2467 | 13.3907 | 16.104 | 18.1794 | 20.2541
| Smooth Rock FallsIce Accretion2050RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2050 | 11.3495 | 13.5164 | 16.2592 | 18.3584 | 20.4543
| Smooth Rock FallsIce Accretion2055RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2055 | 11.4542 | 13.6465 | 16.4224 | 18.5465 | 20.668
| Smooth Rock FallsIce Accretion2060RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2060 | 11.5588 | 13.7767 | 16.5856 | 18.7345 | 20.8817
| Smooth Rock FallsIce Accretion2065RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2065 | 11.6635 | 13.9068 | 16.7488 | 18.9225 | 21.0954
| Smooth Rock FallsIce Accretion2070RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2070 | 11.7681 | 14.037 | 16.912 | 19.1106 | 21.3091
| Smooth Rock FallsIce Accretion2075RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2075 | 11.8034 | 14.079 | 16.9627 | 19.1678 | 21.373
| Smooth Rock FallsIce Accretion2080RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2080 | 11.8387 | 14.1211 | 17.0133 | 19.2251 | 21.4368
| Smooth Rock FallsIce Accretion2085RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2085 | 11.8739 | 14.1631 | 17.064 | 19.2823 | 21.5006
| Smooth Rock FallsIce Accretion2090RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2090 | 11.9092 | 14.2052 | 17.1147 | 19.3396 | 21.5645
| Smooth Rock FallsIce Accretion2095RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2095 | 11.9444 | 14.2472 | 17.1653 | 19.3968 | 21.6283
| Smooth Rock FallsIce Accretion2100RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2100 | 11.9797 | 14.2893 | 17.216 | 19.4541 | 21.6922
| Smooth Rock FallsIce Accretion2023RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2023 | 11.256 | 13.4128 | 16.144 | 18.2246 | 20.3213
| Smooth Rock FallsIce Accretion2025RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2025 | 11.2542 | 13.4084 | 16.136 | 18.2156 | 20.3078
| Smooth Rock FallsIce Accretion2030RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2030 | 11.2523 | 13.4039 | 16.128 | 18.2066 | 20.2944
| Smooth Rock FallsIce Accretion2035RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2035 | 11.2504 | 13.3995 | 16.12 | 18.1975 | 20.281
| Smooth Rock FallsIce Accretion2040RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2040 | 11.2486 | 13.3951 | 16.112 | 18.1885 | 20.2675
| Smooth Rock FallsIce Accretion2045RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2045 | 11.2467 | 13.3907 | 16.104 | 18.1794 | 20.2541
| Smooth Rock FallsIce Accretion2050RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2050 | 11.3495 | 13.5164 | 16.2592 | 18.3584 | 20.4543
| Smooth Rock FallsIce Accretion2055RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2055 | 11.4542 | 13.6465 | 16.4224 | 18.5465 | 20.668
| Smooth Rock FallsIce Accretion2060RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2060 | 11.5588 | 13.7767 | 16.5856 | 18.7345 | 20.8817
| Smooth Rock FallsIce Accretion2065RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2065 | 11.6635 | 13.9068 | 16.7488 | 18.9225 | 21.0954
| Smooth Rock FallsIce Accretion2070RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2070 | 11.7681 | 14.037 | 16.912 | 19.1106 | 21.3091
| Smooth Rock FallsIce Accretion2075RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2075 | 11.821 | 14.1 | 16.988 | 19.1964 | 21.4049
| Smooth Rock FallsIce Accretion2080RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2080 | 11.8739 | 14.1631 | 17.064 | 19.2823 | 21.5006
| Smooth Rock FallsIce Accretion2085RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2085 | 11.9268 | 14.2262 | 17.14 | 19.3682 | 21.5964
| Smooth Rock FallsIce Accretion2090RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2090 | 11.9277 | 14.2583 | 17.2053 | 19.4601 | 21.7123
| Smooth Rock FallsIce Accretion2095RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2095 | 11.8758 | 14.2273 | 17.1947 | 19.4661 | 21.7325
| Smooth Rock FallsIce Accretion2100RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2100 | 11.8238 | 14.1963 | 17.184 | 19.4722 | 21.7526
| Smooth Rock FallsIce Accretion2023RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2023 | 11.256 | 13.4128 | 16.144 | 18.2246 | 20.3213
| Smooth Rock FallsIce Accretion2025RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2025 | 11.2523 | 13.4039 | 16.128 | 18.2066 | 20.2944
| Smooth Rock FallsIce Accretion2030RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2030 | 11.2486 | 13.3951 | 16.112 | 18.1885 | 20.2675
| Smooth Rock FallsIce Accretion2035RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2035 | 11.2449 | 13.3862 | 16.096 | 18.1704 | 20.2406
| Smooth Rock FallsIce Accretion2040RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2040 | 11.4193 | 13.6031 | 16.368 | 18.4838 | 20.5968
| Smooth Rock FallsIce Accretion2045RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2045 | 11.5937 | 13.8201 | 16.64 | 18.7972 | 20.953
| Smooth Rock FallsIce Accretion2050RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2050 | 11.8387 | 14.1211 | 17.0133 | 19.2251 | 21.4368
| Smooth Rock FallsIce Accretion2055RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2055 | 11.9092 | 14.2052 | 17.1147 | 19.3396 | 21.5645
| Smooth Rock FallsIce Accretion2060RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2060 | 11.9277 | 14.2583 | 17.2053 | 19.4601 | 21.7123
| Smooth Rock FallsIce Accretion2065RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2065 | 11.8758 | 14.2273 | 17.1947 | 19.4661 | 21.7325
| Smooth Rock FallsIce Accretion2070RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2070 | 11.7978 | 14.1742 | 17.1787 | 19.4722 | 21.7594
| Smooth Rock FallsIce Accretion2075RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2075 | 11.7719 | 14.1521 | 17.1733 | 19.4722 | 21.7661
| Smooth Rock FallsIce Accretion2080RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2080 | 11.7459 | 14.1299 | 17.168 | 19.4722 | 21.7728
| Smooth Rock FallsIce Accretion2085RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2085 | 11.5789 | 13.9706 | 17 | 19.3094 | 21.6115
| Smooth Rock FallsIce Accretion2090RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2090 | 11.4119 | 13.8112 | 16.832 | 19.1467 | 21.4502
| Smooth Rock FallsIce Accretion2095RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2095 | 11.4119 | 13.8112 | 16.832 | 19.1467 | 21.4502
| Smooth Rock FallsIce Accretion2100RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2100 | 11.4119 | 13.8112 | 16.832 | 19.1467 | 21.4502
| Smooth Rock FallsWind2023RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2023 | 73.0185 | 78.6278 | 84.5292 | 90.4283 | 96.3346
| Smooth Rock FallsWind2025RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2025 | 73.1152 | 78.7371 | 84.6524 | 90.5646 | 96.483
| Smooth Rock FallsWind2030RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2030 | 73.2119 | 78.8465 | 84.7756 | 90.7009 | 96.6314
| Smooth Rock FallsWind2035RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2035 | 73.3086 | 78.9559 | 84.8988 | 90.8372 | 96.7798
| Smooth Rock FallsWind2040RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2040 | 73.4053 | 79.0653 | 85.022 | 90.9735 | 96.9283
| Smooth Rock FallsWind2045RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2045 | 73.502 | 79.1746 | 85.1452 | 91.1099 | 97.0767
| Smooth Rock FallsWind2050RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2050 | 73.6292 | 79.3152 | 85.3003 | 91.2803 | 97.2615
| Smooth Rock FallsWind2055RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2055 | 73.6597 | 79.3465 | 85.3322 | 91.3145 | 97.2979
| Smooth Rock FallsWind2060RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2060 | 73.6901 | 79.3777 | 85.3642 | 91.3486 | 97.3343
| Smooth Rock FallsWind2065RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2065 | 73.7206 | 79.409 | 85.3961 | 91.3828 | 97.3707
| Smooth Rock FallsWind2070RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2070 | 73.7511 | 79.4402 | 85.428 | 91.4169 | 97.4071
| Smooth Rock FallsWind2075RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2075 | 73.7499 | 79.4142 | 85.3706 | 91.3331 | 97.2954
| Smooth Rock FallsWind2080RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2080 | 73.7487 | 79.3881 | 85.3132 | 91.2492 | 97.1836
| Smooth Rock FallsWind2085RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2085 | 73.7474 | 79.3621 | 85.2558 | 91.1653 | 97.0719
| Smooth Rock FallsWind2090RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2090 | 73.7462 | 79.3361 | 85.1984 | 91.0814 | 96.9602
| Smooth Rock FallsWind2095RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2095 | 73.745 | 79.31 | 85.141 | 90.9975 | 96.8485
| Smooth Rock FallsWind2100RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2100 | 73.7438 | 79.284 | 85.0836 | 90.9136 | 96.7368
| Smooth Rock FallsWind2023RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2023 | 73.0185 | 78.6278 | 84.5292 | 90.4283 | 96.3346
| Smooth Rock FallsWind2025RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2025 | 73.1152 | 78.7371 | 84.6524 | 90.5646 | 96.483
| Smooth Rock FallsWind2030RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2030 | 73.2119 | 78.8465 | 84.7756 | 90.7009 | 96.6314
| Smooth Rock FallsWind2035RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2035 | 73.3086 | 78.9559 | 84.8988 | 90.8372 | 96.7798
| Smooth Rock FallsWind2040RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2040 | 73.4053 | 79.0653 | 85.022 | 90.9735 | 96.9283
| Smooth Rock FallsWind2045RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2045 | 73.502 | 79.1746 | 85.1452 | 91.1099 | 97.0767
| Smooth Rock FallsWind2050RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2050 | 73.6292 | 79.3152 | 85.3003 | 91.2803 | 97.2615
| Smooth Rock FallsWind2055RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2055 | 73.6597 | 79.3465 | 85.3322 | 91.3145 | 97.2979
| Smooth Rock FallsWind2060RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2060 | 73.6901 | 79.3777 | 85.3642 | 91.3486 | 97.3343
| Smooth Rock FallsWind2065RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2065 | 73.7206 | 79.409 | 85.3961 | 91.3828 | 97.3707
| Smooth Rock FallsWind2070RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2070 | 73.7511 | 79.4402 | 85.428 | 91.4169 | 97.4071
| Smooth Rock FallsWind2075RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2075 | 73.7493 | 79.4012 | 85.3419 | 91.2911 | 97.2395
| Smooth Rock FallsWind2080RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2080 | 73.7474 | 79.3621 | 85.2558 | 91.1653 | 97.0719
| Smooth Rock FallsWind2085RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2085 | 73.7456 | 79.323 | 85.1697 | 91.0395 | 96.9043
| Smooth Rock FallsWind2090RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2090 | 73.8913 | 79.4559 | 85.2824 | 91.1383 | 96.9889
| Smooth Rock FallsWind2095RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2095 | 74.0388 | 79.6277 | 85.4812 | 91.363 | 97.2411
| Smooth Rock FallsWind2100RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2100 | 74.1863 | 79.7996 | 85.68 | 91.5877 | 97.4933
| Smooth Rock FallsWind2023RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2023 | 73.0185 | 78.6278 | 84.5292 | 90.4283 | 96.3346
| Smooth Rock FallsWind2025RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2025 | 73.2119 | 78.8465 | 84.7756 | 90.7009 | 96.6314
| Smooth Rock FallsWind2030RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2030 | 73.4053 | 79.0653 | 85.022 | 90.9735 | 96.9283
| Smooth Rock FallsWind2035RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2035 | 73.5988 | 79.284 | 85.2684 | 91.2462 | 97.2251
| Smooth Rock FallsWind2040RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2040 | 73.6495 | 79.3361 | 85.3216 | 91.3031 | 97.2858
| Smooth Rock FallsWind2045RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2045 | 73.7003 | 79.3881 | 85.3748 | 91.36 | 97.3464
| Smooth Rock FallsWind2050RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2050 | 73.7487 | 79.3881 | 85.3132 | 91.2492 | 97.1836
| Smooth Rock FallsWind2055RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2055 | 73.7462 | 79.3361 | 85.1984 | 91.0814 | 96.9602
| Smooth Rock FallsWind2060RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2060 | 73.8913 | 79.4559 | 85.2824 | 91.1383 | 96.9889
| Smooth Rock FallsWind2065RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2065 | 74.0388 | 79.6277 | 85.4812 | 91.363 | 97.2411
| Smooth Rock FallsWind2070RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2070 | 74.3337 | 79.9584 | 85.8536 | 91.7735 | 97.6944
| Smooth Rock FallsWind2075RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2075 | 74.4812 | 80.1173 | 86.0272 | 91.9592 | 97.8954
| Smooth Rock FallsWind2080RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2080 | 74.6287 | 80.2761 | 86.2008 | 92.145 | 98.0965
| Smooth Rock FallsWind2085RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2085 | 74.7919 | 80.4831 | 86.4612 | 92.4506 | 98.4461
| Smooth Rock FallsWind2090RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2090 | 74.9551 | 80.6901 | 86.7216 | 92.7562 | 98.7956
| Smooth Rock FallsWind2095RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2095 | 74.9551 | 80.6901 | 86.7216 | 92.7562 | 98.7956
| Smooth Rock FallsWind2100RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2100 | 74.9551 | 80.6901 | 86.7216 | 92.7562 | 98.7956
| South RiverIce Accretion2023RCP4.5 | South River | Ice Accretion | RCP4.5 | 2023 | 15.2321 | 18.1504 | 21.868 | 24.7108 | 27.526
| South RiverIce Accretion2025RCP4.5 | South River | Ice Accretion | RCP4.5 | 2025 | 15.3086 | 18.2509 | 22 | 24.8641 | 27.7061
| South RiverIce Accretion2030RCP4.5 | South River | Ice Accretion | RCP4.5 | 2030 | 15.3852 | 18.3513 | 22.132 | 25.0174 | 27.8863
| South RiverIce Accretion2035RCP4.5 | South River | Ice Accretion | RCP4.5 | 2035 | 15.4617 | 18.4517 | 22.264 | 25.1707 | 28.0665
| South RiverIce Accretion2040RCP4.5 | South River | Ice Accretion | RCP4.5 | 2040 | 15.5382 | 18.5522 | 22.396 | 25.3241 | 28.2467
| South RiverIce Accretion2045RCP4.5 | South River | Ice Accretion | RCP4.5 | 2045 | 15.6148 | 18.6526 | 22.528 | 25.4774 | 28.4269
| South RiverIce Accretion2050RCP4.5 | South River | Ice Accretion | RCP4.5 | 2050 | 15.7373 | 18.8261 | 22.7612 | 25.755 | 28.7512
| South RiverIce Accretion2055RCP4.5 | South River | Ice Accretion | RCP4.5 | 2055 | 15.7832 | 18.8991 | 22.8624 | 25.8793 | 28.8953
| South RiverIce Accretion2060RCP4.5 | South River | Ice Accretion | RCP4.5 | 2060 | 15.8291 | 18.9721 | 22.9636 | 26.0036 | 29.0395
| South RiverIce Accretion2065RCP4.5 | South River | Ice Accretion | RCP4.5 | 2065 | 15.875 | 19.0452 | 23.0648 | 26.1279 | 29.1836
| South RiverIce Accretion2070RCP4.5 | South River | Ice Accretion | RCP4.5 | 2070 | 15.921 | 19.1182 | 23.166 | 26.2522 | 29.3278
| South RiverIce Accretion2075RCP4.5 | South River | Ice Accretion | RCP4.5 | 2075 | 15.9235 | 19.1395 | 23.21 | 26.3143 | 29.4109
| South RiverIce Accretion2080RCP4.5 | South River | Ice Accretion | RCP4.5 | 2080 | 15.9261 | 19.1608 | 23.254 | 26.3765 | 29.4941
| South RiverIce Accretion2085RCP4.5 | South River | Ice Accretion | RCP4.5 | 2085 | 15.9286 | 19.1821 | 23.298 | 26.4386 | 29.5772
| South RiverIce Accretion2090RCP4.5 | South River | Ice Accretion | RCP4.5 | 2090 | 15.9312 | 19.2034 | 23.342 | 26.5008 | 29.6604
| South RiverIce Accretion2095RCP4.5 | South River | Ice Accretion | RCP4.5 | 2095 | 15.9337 | 19.2247 | 23.386 | 26.5629 | 29.7436
| South RiverIce Accretion2100RCP4.5 | South River | Ice Accretion | RCP4.5 | 2100 | 15.9363 | 19.246 | 23.43 | 26.6251 | 29.8267
| South RiverIce Accretion2023RCP6.0 | South River | Ice Accretion | RCP6.0 | 2023 | 15.2321 | 18.1504 | 21.868 | 24.7108 | 27.526
| South RiverIce Accretion2025RCP6.0 | South River | Ice Accretion | RCP6.0 | 2025 | 15.3086 | 18.2509 | 22 | 24.8641 | 27.7061
| South RiverIce Accretion2030RCP6.0 | South River | Ice Accretion | RCP6.0 | 2030 | 15.3852 | 18.3513 | 22.132 | 25.0174 | 27.8863
| South RiverIce Accretion2035RCP6.0 | South River | Ice Accretion | RCP6.0 | 2035 | 15.4617 | 18.4517 | 22.264 | 25.1707 | 28.0665
| South RiverIce Accretion2040RCP6.0 | South River | Ice Accretion | RCP6.0 | 2040 | 15.5382 | 18.5522 | 22.396 | 25.3241 | 28.2467
| South RiverIce Accretion2045RCP6.0 | South River | Ice Accretion | RCP6.0 | 2045 | 15.6148 | 18.6526 | 22.528 | 25.4774 | 28.4269
| South RiverIce Accretion2050RCP6.0 | South River | Ice Accretion | RCP6.0 | 2050 | 15.7373 | 18.8261 | 22.7612 | 25.755 | 28.7512
| South RiverIce Accretion2055RCP6.0 | South River | Ice Accretion | RCP6.0 | 2055 | 15.7832 | 18.8991 | 22.8624 | 25.8793 | 28.8953
| South RiverIce Accretion2060RCP6.0 | South River | Ice Accretion | RCP6.0 | 2060 | 15.8291 | 18.9721 | 22.9636 | 26.0036 | 29.0395
| South RiverIce Accretion2065RCP6.0 | South River | Ice Accretion | RCP6.0 | 2065 | 15.875 | 19.0452 | 23.0648 | 26.1279 | 29.1836
| South RiverIce Accretion2070RCP6.0 | South River | Ice Accretion | RCP6.0 | 2070 | 15.921 | 19.1182 | 23.166 | 26.2522 | 29.3278
| South RiverIce Accretion2075RCP6.0 | South River | Ice Accretion | RCP6.0 | 2075 | 15.9248 | 19.1502 | 23.232 | 26.3454 | 29.4525
| South RiverIce Accretion2080RCP6.0 | South River | Ice Accretion | RCP6.0 | 2080 | 15.9286 | 19.1821 | 23.298 | 26.4386 | 29.5772
| South RiverIce Accretion2085RCP6.0 | South River | Ice Accretion | RCP6.0 | 2085 | 15.9324 | 19.2141 | 23.364 | 26.5318 | 29.702
| South RiverIce Accretion2090RCP6.0 | South River | Ice Accretion | RCP6.0 | 2090 | 15.9618 | 19.2947 | 23.5107 | 26.7328 | 29.9468
| South RiverIce Accretion2095RCP6.0 | South River | Ice Accretion | RCP6.0 | 2095 | 15.9873 | 19.3434 | 23.5913 | 26.8405 | 30.067
| South RiverIce Accretion2100RCP6.0 | South River | Ice Accretion | RCP6.0 | 2100 | 16.0128 | 19.3921 | 23.672 | 26.9482 | 30.1871
| South RiverIce Accretion2023RCP8.5 | South River | Ice Accretion | RCP8.5 | 2023 | 15.2321 | 18.1504 | 21.868 | 24.7108 | 27.526
| South RiverIce Accretion2025RCP8.5 | South River | Ice Accretion | RCP8.5 | 2025 | 15.3852 | 18.3513 | 22.132 | 25.0174 | 27.8863
| South RiverIce Accretion2030RCP8.5 | South River | Ice Accretion | RCP8.5 | 2030 | 15.5382 | 18.5522 | 22.396 | 25.3241 | 28.2467
| South RiverIce Accretion2035RCP8.5 | South River | Ice Accretion | RCP8.5 | 2035 | 15.6913 | 18.753 | 22.66 | 25.6307 | 28.607
| South RiverIce Accretion2040RCP8.5 | South River | Ice Accretion | RCP8.5 | 2040 | 15.7679 | 18.8748 | 22.8287 | 25.8378 | 28.8473
| South RiverIce Accretion2045RCP8.5 | South River | Ice Accretion | RCP8.5 | 2045 | 15.8444 | 18.9965 | 22.9973 | 26.045 | 29.0875
| South RiverIce Accretion2050RCP8.5 | South River | Ice Accretion | RCP8.5 | 2050 | 15.9261 | 19.1608 | 23.254 | 26.3765 | 29.4941
| South RiverIce Accretion2055RCP8.5 | South River | Ice Accretion | RCP8.5 | 2055 | 15.9312 | 19.2034 | 23.342 | 26.5008 | 29.6604
| South RiverIce Accretion2060RCP8.5 | South River | Ice Accretion | RCP8.5 | 2060 | 15.9618 | 19.2947 | 23.5107 | 26.7328 | 29.9468
| South RiverIce Accretion2065RCP8.5 | South River | Ice Accretion | RCP8.5 | 2065 | 15.9873 | 19.3434 | 23.5913 | 26.8405 | 30.067
| South RiverIce Accretion2070RCP8.5 | South River | Ice Accretion | RCP8.5 | 2070 | 15.8801 | 19.2521 | 23.5253 | 26.7908 | 30.03
| South RiverIce Accretion2075RCP8.5 | South River | Ice Accretion | RCP8.5 | 2075 | 15.7475 | 19.1121 | 23.3787 | 26.6333 | 29.8729
| South RiverIce Accretion2080RCP8.5 | South River | Ice Accretion | RCP8.5 | 2080 | 15.6148 | 18.9721 | 23.232 | 26.4759 | 29.7158
| South RiverIce Accretion2085RCP8.5 | South River | Ice Accretion | RCP8.5 | 2085 | 15.2091 | 18.5248 | 22.715 | 25.9166 | 29.106
| South RiverIce Accretion2090RCP8.5 | South River | Ice Accretion | RCP8.5 | 2090 | 14.8034 | 18.0774 | 22.198 | 25.3572 | 28.4962
| South RiverIce Accretion2095RCP8.5 | South River | Ice Accretion | RCP8.5 | 2095 | 14.8034 | 18.0774 | 22.198 | 25.3572 | 28.4962
| South RiverIce Accretion2100RCP8.5 | South River | Ice Accretion | RCP8.5 | 2100 | 14.8034 | 18.0774 | 22.198 | 25.3572 | 28.4962
| South RiverWind2023RCP4.5 | South River | Wind | RCP4.5 | 2023 | 69.3273 | 74.6976 | 80.36 | 86.0109 | 91.6651
| South RiverWind2025RCP4.5 | South River | Wind | RCP4.5 | 2025 | 69.371 | 74.7559 | 80.436 | 86.1008 | 91.77
| South RiverWind2030RCP4.5 | South River | Wind | RCP4.5 | 2030 | 69.4148 | 74.8142 | 80.512 | 86.1906 | 91.8749
| South RiverWind2035RCP4.5 | South River | Wind | RCP4.5 | 2035 | 69.4585 | 74.8724 | 80.588 | 86.2805 | 91.9798
| South RiverWind2040RCP4.5 | South River | Wind | RCP4.5 | 2040 | 69.5023 | 74.9307 | 80.664 | 86.3704 | 92.0846
| South RiverWind2045RCP4.5 | South River | Wind | RCP4.5 | 2045 | 69.546 | 74.989 | 80.74 | 86.4603 | 92.1895
| South RiverWind2050RCP4.5 | South River | Wind | RCP4.5 | 2050 | 69.5842 | 75.0309 | 80.784 | 86.5091 | 92.2397
| South RiverWind2055RCP4.5 | South River | Wind | RCP4.5 | 2055 | 69.5787 | 75.0145 | 80.752 | 86.468 | 92.185
| South RiverWind2060RCP4.5 | South River | Wind | RCP4.5 | 2060 | 69.5732 | 74.9982 | 80.72 | 86.4269 | 92.1302
| South RiverWind2065RCP4.5 | South River | Wind | RCP4.5 | 2065 | 69.5677 | 74.9818 | 80.688 | 86.3858 | 92.0755
| South RiverWind2070RCP4.5 | South River | Wind | RCP4.5 | 2070 | 69.5621 | 74.9654 | 80.656 | 86.3447 | 92.0208
| South RiverWind2075RCP4.5 | South River | Wind | RCP4.5 | 2075 | 69.6347 | 75.0485 | 80.7533 | 86.4531 | 92.1424
| South RiverWind2080RCP4.5 | South River | Wind | RCP4.5 | 2080 | 69.7072 | 75.1316 | 80.8507 | 86.5616 | 92.264
| South RiverWind2085RCP4.5 | South River | Wind | RCP4.5 | 2085 | 69.7797 | 75.2147 | 80.948 | 86.67 | 92.3856
| South RiverWind2090RCP4.5 | South River | Wind | RCP4.5 | 2090 | 69.8523 | 75.2978 | 81.0453 | 86.7784 | 92.5072
| South RiverWind2095RCP4.5 | South River | Wind | RCP4.5 | 2095 | 69.9248 | 75.3808 | 81.1427 | 86.8869 | 92.6288
| South RiverWind2100RCP4.5 | South River | Wind | RCP4.5 | 2100 | 69.9973 | 75.4639 | 81.24 | 86.9953 | 92.7504
| South RiverWind2023RCP6.0 | South River | Wind | RCP6.0 | 2023 | 69.3273 | 74.6976 | 80.36 | 86.0109 | 91.6651
| South RiverWind2025RCP6.0 | South River | Wind | RCP6.0 | 2025 | 69.371 | 74.7559 | 80.436 | 86.1008 | 91.77
| South RiverWind2030RCP6.0 | South River | Wind | RCP6.0 | 2030 | 69.4148 | 74.8142 | 80.512 | 86.1906 | 91.8749
| South RiverWind2035RCP6.0 | South River | Wind | RCP6.0 | 2035 | 69.4585 | 74.8724 | 80.588 | 86.2805 | 91.9798
| South RiverWind2040RCP6.0 | South River | Wind | RCP6.0 | 2040 | 69.5023 | 74.9307 | 80.664 | 86.3704 | 92.0846
| South RiverWind2045RCP6.0 | South River | Wind | RCP6.0 | 2045 | 69.546 | 74.989 | 80.74 | 86.4603 | 92.1895
| South RiverWind2050RCP6.0 | South River | Wind | RCP6.0 | 2050 | 69.5842 | 75.0309 | 80.784 | 86.5091 | 92.2397
| South RiverWind2055RCP6.0 | South River | Wind | RCP6.0 | 2055 | 69.5787 | 75.0145 | 80.752 | 86.468 | 92.185
| South RiverWind2060RCP6.0 | South River | Wind | RCP6.0 | 2060 | 69.5732 | 74.9982 | 80.72 | 86.4269 | 92.1302
| South RiverWind2065RCP6.0 | South River | Wind | RCP6.0 | 2065 | 69.5677 | 74.9818 | 80.688 | 86.3858 | 92.0755
| South RiverWind2070RCP6.0 | South River | Wind | RCP6.0 | 2070 | 69.5621 | 74.9654 | 80.656 | 86.3447 | 92.0208
| South RiverWind2075RCP6.0 | South River | Wind | RCP6.0 | 2075 | 69.6709 | 75.0901 | 80.802 | 86.5074 | 92.2032
| South RiverWind2080RCP6.0 | South River | Wind | RCP6.0 | 2080 | 69.7797 | 75.2147 | 80.948 | 86.67 | 92.3856
| South RiverWind2085RCP6.0 | South River | Wind | RCP6.0 | 2085 | 69.8885 | 75.3393 | 81.094 | 86.8326 | 92.568
| South RiverWind2090RCP6.0 | South River | Wind | RCP6.0 | 2090 | 69.8638 | 75.2978 | 81.0293 | 86.7499 | 92.4677
| South RiverWind2095RCP6.0 | South River | Wind | RCP6.0 | 2095 | 69.7302 | 75.1316 | 80.8187 | 86.5045 | 92.185
| South RiverWind2100RCP6.0 | South River | Wind | RCP6.0 | 2100 | 69.5967 | 74.9654 | 80.608 | 86.2591 | 91.9022
| South RiverWind2023RCP8.5 | South River | Wind | RCP8.5 | 2023 | 69.3273 | 74.6976 | 80.36 | 86.0109 | 91.6651
| South RiverWind2025RCP8.5 | South River | Wind | RCP8.5 | 2025 | 69.4148 | 74.8142 | 80.512 | 86.1906 | 91.8749
| South RiverWind2030RCP8.5 | South River | Wind | RCP8.5 | 2030 | 69.5023 | 74.9307 | 80.664 | 86.3704 | 92.0846
| South RiverWind2035RCP8.5 | South River | Wind | RCP8.5 | 2035 | 69.5898 | 75.0473 | 80.816 | 86.5502 | 92.2944
| South RiverWind2040RCP8.5 | South River | Wind | RCP8.5 | 2040 | 69.5806 | 75.02 | 80.7627 | 86.4817 | 92.2032
| South RiverWind2045RCP8.5 | South River | Wind | RCP8.5 | 2045 | 69.5714 | 74.9927 | 80.7093 | 86.4132 | 92.112
| South RiverWind2050RCP8.5 | South River | Wind | RCP8.5 | 2050 | 69.7072 | 75.1316 | 80.8507 | 86.5616 | 92.264
| South RiverWind2055RCP8.5 | South River | Wind | RCP8.5 | 2055 | 69.8523 | 75.2978 | 81.0453 | 86.7784 | 92.5072
| South RiverWind2060RCP8.5 | South River | Wind | RCP8.5 | 2060 | 69.8638 | 75.2978 | 81.0293 | 86.7499 | 92.4677
| South RiverWind2065RCP8.5 | South River | Wind | RCP8.5 | 2065 | 69.7302 | 75.1316 | 80.8187 | 86.5045 | 92.185
| South RiverWind2070RCP8.5 | South River | Wind | RCP8.5 | 2070 | 69.7302 | 75.1266 | 80.808 | 86.4874 | 92.1637
| South RiverWind2075RCP8.5 | South River | Wind | RCP8.5 | 2075 | 69.8638 | 75.2878 | 81.008 | 86.7157 | 92.4251
| South RiverWind2080RCP8.5 | South River | Wind | RCP8.5 | 2080 | 69.9973 | 75.449 | 81.208 | 86.9439 | 92.6866
| South RiverWind2085RCP8.5 | South River | Wind | RCP8.5 | 2085 | 70.0284 | 75.4676 | 81.208 | 86.9311 | 92.6592
| South RiverWind2090RCP8.5 | South River | Wind | RCP8.5 | 2090 | 70.0595 | 75.4862 | 81.208 | 86.9182 | 92.6318
| South RiverWind2095RCP8.5 | South River | Wind | RCP8.5 | 2095 | 70.0595 | 75.4862 | 81.208 | 86.9182 | 92.6318
| South RiverWind2100RCP8.5 | South River | Wind | RCP8.5 | 2100 | 70.0595 | 75.4862 | 81.208 | 86.9182 | 92.6318
| SouthamptonIce Accretion2023RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2023 | 13.9865 | 16.7162 | 20.18 | 22.8486 | 25.4772
| SouthamptonIce Accretion2025RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2025 | 13.9958 | 16.7383 | 20.2167 | 22.8938 | 25.536
| SouthamptonIce Accretion2030RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2030 | 14.0051 | 16.7605 | 20.2533 | 22.939 | 25.5948
| SouthamptonIce Accretion2035RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2035 | 14.0143 | 16.7826 | 20.29 | 22.9842 | 25.6536
| SouthamptonIce Accretion2040RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2040 | 14.0236 | 16.8047 | 20.3267 | 23.0294 | 25.7124
| SouthamptonIce Accretion2045RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2045 | 14.0329 | 16.8269 | 20.3633 | 23.0746 | 25.7712
| SouthamptonIce Accretion2050RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2050 | 13.9921 | 16.8025 | 20.36 | 23.0836 | 25.7947
| SouthamptonIce Accretion2055RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2055 | 13.942 | 16.756 | 20.32 | 23.0475 | 25.7594
| SouthamptonIce Accretion2060RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2060 | 13.8919 | 16.7096 | 20.28 | 23.0113 | 25.7242
| SouthamptonIce Accretion2065RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2065 | 13.8418 | 16.6631 | 20.24 | 22.9752 | 25.6889
| SouthamptonIce Accretion2070RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2070 | 13.7917 | 16.6166 | 20.2 | 22.939 | 25.6536
| SouthamptonIce Accretion2075RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2075 | 13.7406 | 16.5806 | 20.18 | 22.9277 | 25.6536
| SouthamptonIce Accretion2080RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2080 | 13.6896 | 16.5447 | 20.16 | 22.9164 | 25.6536
| SouthamptonIce Accretion2085RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2085 | 13.6386 | 16.5087 | 20.14 | 22.9051 | 25.6536
| SouthamptonIce Accretion2090RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2090 | 13.5876 | 16.4727 | 20.12 | 22.8938 | 25.6536
| SouthamptonIce Accretion2095RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2095 | 13.5365 | 16.4368 | 20.1 | 22.8825 | 25.6536
| SouthamptonIce Accretion2100RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2100 | 13.4855 | 16.4008 | 20.08 | 22.8712 | 25.6536
| SouthamptonIce Accretion2023RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2023 | 13.9865 | 16.7162 | 20.18 | 22.8486 | 25.4772
| SouthamptonIce Accretion2025RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2025 | 13.9958 | 16.7383 | 20.2167 | 22.8938 | 25.536
| SouthamptonIce Accretion2030RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2030 | 14.0051 | 16.7605 | 20.2533 | 22.939 | 25.5948
| SouthamptonIce Accretion2035RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2035 | 14.0143 | 16.7826 | 20.29 | 22.9842 | 25.6536
| SouthamptonIce Accretion2040RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2040 | 14.0236 | 16.8047 | 20.3267 | 23.0294 | 25.7124
| SouthamptonIce Accretion2045RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2045 | 14.0329 | 16.8269 | 20.3633 | 23.0746 | 25.7712
| SouthamptonIce Accretion2050RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2050 | 13.9921 | 16.8025 | 20.36 | 23.0836 | 25.7947
| SouthamptonIce Accretion2055RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2055 | 13.942 | 16.756 | 20.32 | 23.0475 | 25.7594
| SouthamptonIce Accretion2060RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2060 | 13.8919 | 16.7096 | 20.28 | 23.0113 | 25.7242
| SouthamptonIce Accretion2065RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2065 | 13.8418 | 16.6631 | 20.24 | 22.9752 | 25.6889
| SouthamptonIce Accretion2070RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2070 | 13.7917 | 16.6166 | 20.2 | 22.939 | 25.6536
| SouthamptonIce Accretion2075RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2075 | 13.7151 | 16.5626 | 20.17 | 22.922 | 25.6536
| SouthamptonIce Accretion2080RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2080 | 13.6386 | 16.5087 | 20.14 | 22.9051 | 25.6536
| SouthamptonIce Accretion2085RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2085 | 13.562 | 16.4547 | 20.11 | 22.8881 | 25.6536
| SouthamptonIce Accretion2090RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2090 | 13.2489 | 16.1518 | 19.8067 | 22.5849 | 25.3512
| SouthamptonIce Accretion2095RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2095 | 13.0123 | 15.9028 | 19.5333 | 22.2987 | 25.0488
| SouthamptonIce Accretion2100RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2100 | 12.7757 | 15.6538 | 19.26 | 22.0124 | 24.7464
| SouthamptonIce Accretion2023RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2023 | 13.9865 | 16.7162 | 20.18 | 22.8486 | 25.4772
| SouthamptonIce Accretion2025RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2025 | 14.0051 | 16.7605 | 20.2533 | 22.939 | 25.5948
| SouthamptonIce Accretion2030RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2030 | 14.0236 | 16.8047 | 20.3267 | 23.0294 | 25.7124
| SouthamptonIce Accretion2035RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2035 | 14.0422 | 16.849 | 20.4 | 23.1198 | 25.83
| SouthamptonIce Accretion2040RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2040 | 13.9587 | 16.7715 | 20.3333 | 23.0595 | 25.7712
| SouthamptonIce Accretion2045RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2045 | 13.8752 | 16.6941 | 20.2667 | 22.9993 | 25.7124
| SouthamptonIce Accretion2050RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2050 | 13.6896 | 16.5447 | 20.16 | 22.9164 | 25.6536
| SouthamptonIce Accretion2055RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2055 | 13.5876 | 16.4727 | 20.12 | 22.8938 | 25.6536
| SouthamptonIce Accretion2060RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2060 | 13.2489 | 16.1518 | 19.8067 | 22.5849 | 25.3512
| SouthamptonIce Accretion2065RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2065 | 13.0123 | 15.9028 | 19.5333 | 22.2987 | 25.0488
| SouthamptonIce Accretion2070RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2070 | 12.4232 | 15.2609 | 18.82 | 21.5378 | 24.234
| SouthamptonIce Accretion2075RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2075 | 12.0706 | 14.8681 | 18.38 | 21.0632 | 23.7216
| SouthamptonIce Accretion2080RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2080 | 11.718 | 14.4752 | 17.94 | 20.5886 | 23.2092
| SouthamptonIce Accretion2085RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2085 | 11.1196 | 13.7863 | 17.13 | 19.6733 | 22.2012
| SouthamptonIce Accretion2090RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2090 | 10.5212 | 13.0974 | 16.32 | 18.758 | 21.1932
| SouthamptonIce Accretion2095RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2095 | 10.5212 | 13.0974 | 16.32 | 18.758 | 21.1932
| SouthamptonIce Accretion2100RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2100 | 10.5212 | 13.0974 | 16.32 | 18.758 | 21.1932
| SouthamptonWind2023RCP4.5 | Southampton | Wind | RCP4.5 | 2023 | 85.4848 | 91.9687 | 98.7624 | 105.591 | 112.4086
| SouthamptonWind2025RCP4.5 | Southampton | Wind | RCP4.5 | 2025 | 85.5631 | 92.0654 | 98.8845 | 105.7323 | 112.5722
| SouthamptonWind2030RCP4.5 | Southampton | Wind | RCP4.5 | 2030 | 85.6415 | 92.1621 | 99.0066 | 105.8735 | 112.7359
| SouthamptonWind2035RCP4.5 | Southampton | Wind | RCP4.5 | 2035 | 85.7198 | 92.2587 | 99.1287 | 106.0147 | 112.8995
| SouthamptonWind2040RCP4.5 | Southampton | Wind | RCP4.5 | 2040 | 85.7982 | 92.3554 | 99.2508 | 106.156 | 113.0631
| SouthamptonWind2045RCP4.5 | Southampton | Wind | RCP4.5 | 2045 | 85.8766 | 92.4521 | 99.3729 | 106.2972 | 113.2268
| SouthamptonWind2050RCP4.5 | Southampton | Wind | RCP4.5 | 2050 | 85.9515 | 92.5396 | 99.4752 | 106.413 | 113.3566
| SouthamptonWind2055RCP4.5 | Southampton | Wind | RCP4.5 | 2055 | 85.9481 | 92.5304 | 99.4554 | 106.3876 | 113.3227
| SouthamptonWind2060RCP4.5 | Southampton | Wind | RCP4.5 | 2060 | 85.9447 | 92.5211 | 99.4356 | 106.3622 | 113.2889
| SouthamptonWind2065RCP4.5 | Southampton | Wind | RCP4.5 | 2065 | 85.9412 | 92.5119 | 99.4158 | 106.3368 | 113.255
| SouthamptonWind2070RCP4.5 | Southampton | Wind | RCP4.5 | 2070 | 85.9378 | 92.5027 | 99.396 | 106.3113 | 113.2212
| SouthamptonWind2075RCP4.5 | Southampton | Wind | RCP4.5 | 2075 | 85.9564 | 92.5227 | 99.4175 | 106.3343 | 113.2456
| SouthamptonWind2080RCP4.5 | Southampton | Wind | RCP4.5 | 2080 | 85.9749 | 92.5426 | 99.4389 | 106.3573 | 113.2701
| SouthamptonWind2085RCP4.5 | Southampton | Wind | RCP4.5 | 2085 | 85.9934 | 92.5626 | 99.4604 | 106.3802 | 113.2945
| SouthamptonWind2090RCP4.5 | Southampton | Wind | RCP4.5 | 2090 | 86.0119 | 92.5825 | 99.4818 | 106.4032 | 113.319
| SouthamptonWind2095RCP4.5 | Southampton | Wind | RCP4.5 | 2095 | 86.0304 | 92.6025 | 99.5033 | 106.4261 | 113.3434
| SouthamptonWind2100RCP4.5 | Southampton | Wind | RCP4.5 | 2100 | 86.049 | 92.6224 | 99.5247 | 106.4491 | 113.3679
| SouthamptonWind2023RCP6.0 | Southampton | Wind | RCP6.0 | 2023 | 85.4848 | 91.9687 | 98.7624 | 105.591 | 112.4086
| SouthamptonWind2025RCP6.0 | Southampton | Wind | RCP6.0 | 2025 | 85.5631 | 92.0654 | 98.8845 | 105.7323 | 112.5722
| SouthamptonWind2030RCP6.0 | Southampton | Wind | RCP6.0 | 2030 | 85.6415 | 92.1621 | 99.0066 | 105.8735 | 112.7359
| SouthamptonWind2035RCP6.0 | Southampton | Wind | RCP6.0 | 2035 | 85.7198 | 92.2587 | 99.1287 | 106.0147 | 112.8995
| SouthamptonWind2040RCP6.0 | Southampton | Wind | RCP6.0 | 2040 | 85.7982 | 92.3554 | 99.2508 | 106.156 | 113.0631
| SouthamptonWind2045RCP6.0 | Southampton | Wind | RCP6.0 | 2045 | 85.8766 | 92.4521 | 99.3729 | 106.2972 | 113.2268
| SouthamptonWind2050RCP6.0 | Southampton | Wind | RCP6.0 | 2050 | 85.9515 | 92.5396 | 99.4752 | 106.413 | 113.3566
| SouthamptonWind2055RCP6.0 | Southampton | Wind | RCP6.0 | 2055 | 85.9481 | 92.5304 | 99.4554 | 106.3876 | 113.3227
| SouthamptonWind2060RCP6.0 | Southampton | Wind | RCP6.0 | 2060 | 85.9447 | 92.5211 | 99.4356 | 106.3622 | 113.2889
| SouthamptonWind2065RCP6.0 | Southampton | Wind | RCP6.0 | 2065 | 85.9412 | 92.5119 | 99.4158 | 106.3368 | 113.255
| SouthamptonWind2070RCP6.0 | Southampton | Wind | RCP6.0 | 2070 | 85.9378 | 92.5027 | 99.396 | 106.3113 | 113.2212
| SouthamptonWind2075RCP6.0 | Southampton | Wind | RCP6.0 | 2075 | 85.9656 | 92.5327 | 99.4282 | 106.3458 | 113.2578
| SouthamptonWind2080RCP6.0 | Southampton | Wind | RCP6.0 | 2080 | 85.9934 | 92.5626 | 99.4604 | 106.3802 | 113.2945
| SouthamptonWind2085RCP6.0 | Southampton | Wind | RCP6.0 | 2085 | 86.0212 | 92.5925 | 99.4925 | 106.4146 | 113.3312
| SouthamptonWind2090RCP6.0 | Southampton | Wind | RCP6.0 | 2090 | 86.1857 | 92.7881 | 99.726 | 106.6786 | 113.6237
| SouthamptonWind2095RCP6.0 | Southampton | Wind | RCP6.0 | 2095 | 86.3225 | 92.9539 | 99.9273 | 106.9081 | 113.8795
| SouthamptonWind2100RCP6.0 | Southampton | Wind | RCP6.0 | 2100 | 86.4593 | 93.1196 | 100.1286 | 107.1376 | 114.1353
| SouthamptonWind2023RCP8.5 | Southampton | Wind | RCP8.5 | 2023 | 85.4848 | 91.9687 | 98.7624 | 105.591 | 112.4086
| SouthamptonWind2025RCP8.5 | Southampton | Wind | RCP8.5 | 2025 | 85.6415 | 92.1621 | 99.0066 | 105.8735 | 112.7359
| SouthamptonWind2030RCP8.5 | Southampton | Wind | RCP8.5 | 2030 | 85.7982 | 92.3554 | 99.2508 | 106.156 | 113.0631
| SouthamptonWind2035RCP8.5 | Southampton | Wind | RCP8.5 | 2035 | 85.9549 | 92.5488 | 99.495 | 106.4385 | 113.3904
| SouthamptonWind2040RCP8.5 | Southampton | Wind | RCP8.5 | 2040 | 85.9492 | 92.5334 | 99.462 | 106.3961 | 113.334
| SouthamptonWind2045RCP8.5 | Southampton | Wind | RCP8.5 | 2045 | 85.9435 | 92.5181 | 99.429 | 106.3537 | 113.2776
| SouthamptonWind2050RCP8.5 | Southampton | Wind | RCP8.5 | 2050 | 85.9749 | 92.5426 | 99.4389 | 106.3573 | 113.2701
| SouthamptonWind2055RCP8.5 | Southampton | Wind | RCP8.5 | 2055 | 86.0119 | 92.5825 | 99.4818 | 106.4032 | 113.319
| SouthamptonWind2060RCP8.5 | Southampton | Wind | RCP8.5 | 2060 | 86.1857 | 92.7881 | 99.726 | 106.6786 | 113.6237
| SouthamptonWind2065RCP8.5 | Southampton | Wind | RCP8.5 | 2065 | 86.3225 | 92.9539 | 99.9273 | 106.9081 | 113.8795
| SouthamptonWind2070RCP8.5 | Southampton | Wind | RCP8.5 | 2070 | 86.5305 | 93.2055 | 100.2276 | 107.2506 | 114.267
| SouthamptonWind2075RCP8.5 | Southampton | Wind | RCP8.5 | 2075 | 86.6018 | 93.2915 | 100.3266 | 107.3636 | 114.3987
| SouthamptonWind2080RCP8.5 | Southampton | Wind | RCP8.5 | 2080 | 86.673 | 93.3774 | 100.4256 | 107.4766 | 114.5303
| SouthamptonWind2085RCP8.5 | Southampton | Wind | RCP8.5 | 2085 | 87.0021 | 93.8193 | 101.0147 | 108.1863 | 115.3598
| SouthamptonWind2090RCP8.5 | Southampton | Wind | RCP8.5 | 2090 | 87.3312 | 94.2613 | 101.6037 | 108.896 | 116.1894
| SouthamptonWind2095RCP8.5 | Southampton | Wind | RCP8.5 | 2095 | 87.3312 | 94.2613 | 101.6037 | 108.896 | 116.1894
| SouthamptonWind2100RCP8.5 | Southampton | Wind | RCP8.5 | 2100 | 87.3312 | 94.2613 | 101.6037 | 108.896 | 116.1894
| St. CatharinesIce Accretion2023RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2023 | 19.9576 | 23.9497 | 29 | 32.8683 | 36.7227
| St. CatharinesIce Accretion2025RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2025 | 19.8634 | 23.8453 | 28.8888 | 32.7427 | 36.5887
| St. CatharinesIce Accretion2030RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2030 | 19.7692 | 23.741 | 28.7777 | 32.6171 | 36.4547
| St. CatharinesIce Accretion2035RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2035 | 19.675 | 23.6367 | 28.6665 | 32.4915 | 36.3208
| St. CatharinesIce Accretion2040RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2040 | 19.5809 | 23.5324 | 28.5553 | 32.3658 | 36.1868
| St. CatharinesIce Accretion2045RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2045 | 19.4867 | 23.4281 | 28.4442 | 32.2402 | 36.0528
| St. CatharinesIce Accretion2050RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2050 | 18.9607 | 22.8376 | 27.7646 | 31.4854 | 35.2319
| St. CatharinesIce Accretion2055RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2055 | 18.5289 | 22.3514 | 27.1962 | 30.8562 | 34.5449
| St. CatharinesIce Accretion2060RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2060 | 18.097 | 21.8652 | 26.6278 | 30.227 | 33.858
| St. CatharinesIce Accretion2065RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2065 | 17.6652 | 21.379 | 26.0594 | 29.5979 | 33.171
| St. CatharinesIce Accretion2070RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2070 | 17.2333 | 20.8928 | 25.491 | 28.9687 | 32.4841
| St. CatharinesIce Accretion2075RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2075 | 17.0719 | 20.7243 | 25.3122 | 28.783 | 32.2892
| St. CatharinesIce Accretion2080RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2080 | 16.9105 | 20.5558 | 25.1333 | 28.5973 | 32.0943
| St. CatharinesIce Accretion2085RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2085 | 16.749 | 20.3873 | 24.9545 | 28.4116 | 31.8994
| St. CatharinesIce Accretion2090RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2090 | 16.5876 | 20.2188 | 24.7757 | 28.2259 | 31.7045
| St. CatharinesIce Accretion2095RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2095 | 16.4261 | 20.0503 | 24.5968 | 28.0402 | 31.5097
| St. CatharinesIce Accretion2100RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2100 | 16.2647 | 19.8818 | 24.418 | 27.8545 | 31.3148
| St. CatharinesIce Accretion2023RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2023 | 19.9576 | 23.9497 | 29 | 32.8683 | 36.7227
| St. CatharinesIce Accretion2025RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2025 | 19.8634 | 23.8453 | 28.8888 | 32.7427 | 36.5887
| St. CatharinesIce Accretion2030RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2030 | 19.7692 | 23.741 | 28.7777 | 32.6171 | 36.4547
| St. CatharinesIce Accretion2035RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2035 | 19.675 | 23.6367 | 28.6665 | 32.4915 | 36.3208
| St. CatharinesIce Accretion2040RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2040 | 19.5809 | 23.5324 | 28.5553 | 32.3658 | 36.1868
| St. CatharinesIce Accretion2045RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2045 | 19.4867 | 23.4281 | 28.4442 | 32.2402 | 36.0528
| St. CatharinesIce Accretion2050RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2050 | 18.9607 | 22.8376 | 27.7646 | 31.4854 | 35.2319
| St. CatharinesIce Accretion2055RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2055 | 18.5289 | 22.3514 | 27.1962 | 30.8562 | 34.5449
| St. CatharinesIce Accretion2060RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2060 | 18.097 | 21.8652 | 26.6278 | 30.227 | 33.858
| St. CatharinesIce Accretion2065RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2065 | 17.6652 | 21.379 | 26.0594 | 29.5979 | 33.171
| St. CatharinesIce Accretion2070RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2070 | 17.2333 | 20.8928 | 25.491 | 28.9687 | 32.4841
| St. CatharinesIce Accretion2075RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2075 | 16.9912 | 20.64 | 25.2227 | 28.6901 | 32.1917
| St. CatharinesIce Accretion2080RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2080 | 16.749 | 20.3873 | 24.9545 | 28.4116 | 31.8994
| St. CatharinesIce Accretion2085RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2085 | 16.5069 | 20.1346 | 24.6863 | 28.133 | 31.6071
| St. CatharinesIce Accretion2090RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2090 | 15.6055 | 19.1276 | 23.5383 | 26.8823 | 30.2308
| St. CatharinesIce Accretion2095RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2095 | 14.9463 | 18.3734 | 22.6587 | 25.9101 | 29.1467
| St. CatharinesIce Accretion2100RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2100 | 14.2871 | 17.6192 | 21.779 | 24.938 | 28.0627
| St. CatharinesIce Accretion2023RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2023 | 19.9576 | 23.9497 | 29 | 32.8683 | 36.7227
| St. CatharinesIce Accretion2025RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2025 | 19.7692 | 23.741 | 28.7777 | 32.6171 | 36.4547
| St. CatharinesIce Accretion2030RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2030 | 19.5809 | 23.5324 | 28.5553 | 32.3658 | 36.1868
| St. CatharinesIce Accretion2035RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2035 | 19.3925 | 23.3238 | 28.333 | 32.1146 | 35.9188
| St. CatharinesIce Accretion2040RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2040 | 18.6728 | 22.5135 | 27.3857 | 31.066 | 34.7739
| St. CatharinesIce Accretion2045RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2045 | 17.9531 | 21.7031 | 26.4383 | 30.0173 | 33.629
| St. CatharinesIce Accretion2050RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2050 | 16.9105 | 20.5558 | 25.1333 | 28.5973 | 32.0943
| St. CatharinesIce Accretion2055RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2055 | 16.5876 | 20.2188 | 24.7757 | 28.2259 | 31.7045
| St. CatharinesIce Accretion2060RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2060 | 15.6055 | 19.1276 | 23.5383 | 26.8823 | 30.2308
| St. CatharinesIce Accretion2065RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2065 | 14.9463 | 18.3734 | 22.6587 | 25.9101 | 29.1467
| St. CatharinesIce Accretion2070RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2070 | 13.9575 | 17.2421 | 21.3537 | 24.4683 | 27.5512
| St. CatharinesIce Accretion2075RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2075 | 13.6279 | 16.865 | 20.9283 | 23.9986 | 27.0396
| St. CatharinesIce Accretion2080RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2080 | 13.2983 | 16.488 | 20.503 | 23.5289 | 26.528
| St. CatharinesIce Accretion2085RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2085 | 12.5517 | 15.6094 | 19.4445 | 22.3328 | 25.1943
| St. CatharinesIce Accretion2090RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2090 | 11.805 | 14.7308 | 18.386 | 21.1366 | 23.8606
| St. CatharinesIce Accretion2095RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2095 | 11.805 | 14.7308 | 18.386 | 21.1366 | 23.8606
| St. CatharinesIce Accretion2100RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2100 | 11.805 | 14.7308 | 18.386 | 21.1366 | 23.8606
| St. CatharinesWind2023RCP4.5 | St. Catharines | Wind | RCP4.5 | 2023 | 88.9824 | 96.0647 | 103.581 | 111.05 | 118.5126
| St. CatharinesWind2025RCP4.5 | St. Catharines | Wind | RCP4.5 | 2025 | 88.953 | 96.0347 | 103.5487 | 111.0154 | 118.4758
| St. CatharinesWind2030RCP4.5 | St. Catharines | Wind | RCP4.5 | 2030 | 88.9237 | 96.0046 | 103.5164 | 110.9808 | 118.4389
| St. CatharinesWind2035RCP4.5 | St. Catharines | Wind | RCP4.5 | 2035 | 88.8943 | 95.9746 | 103.4841 | 110.9463 | 118.4021
| St. CatharinesWind2040RCP4.5 | St. Catharines | Wind | RCP4.5 | 2040 | 88.8649 | 95.9446 | 103.4518 | 110.9117 | 118.3653
| St. CatharinesWind2045RCP4.5 | St. Catharines | Wind | RCP4.5 | 2045 | 88.8356 | 95.9145 | 103.4195 | 110.8771 | 118.3285
| St. CatharinesWind2050RCP4.5 | St. Catharines | Wind | RCP4.5 | 2050 | 88.8644 | 95.9585 | 103.4831 | 110.9539 | 118.4219
| St. CatharinesWind2055RCP4.5 | St. Catharines | Wind | RCP4.5 | 2055 | 88.9225 | 96.0325 | 103.579 | 111.0652 | 118.5521
| St. CatharinesWind2060RCP4.5 | St. Catharines | Wind | RCP4.5 | 2060 | 88.9806 | 96.1065 | 103.6748 | 111.1766 | 118.6823
| St. CatharinesWind2065RCP4.5 | St. Catharines | Wind | RCP4.5 | 2065 | 89.0388 | 96.1805 | 103.7707 | 111.2879 | 118.8126
| St. CatharinesWind2070RCP4.5 | St. Catharines | Wind | RCP4.5 | 2070 | 89.0969 | 96.2544 | 103.8666 | 111.3992 | 118.9428
| St. CatharinesWind2075RCP4.5 | St. Catharines | Wind | RCP4.5 | 2075 | 89.1791 | 96.3699 | 104.0247 | 111.592 | 119.1734
| St. CatharinesWind2080RCP4.5 | St. Catharines | Wind | RCP4.5 | 2080 | 89.2613 | 96.4853 | 104.1828 | 111.7848 | 119.4041
| St. CatharinesWind2085RCP4.5 | St. Catharines | Wind | RCP4.5 | 2085 | 89.3435 | 96.6007 | 104.3409 | 111.9776 | 119.6347
| St. CatharinesWind2090RCP4.5 | St. Catharines | Wind | RCP4.5 | 2090 | 89.4257 | 96.7161 | 104.499 | 112.1705 | 119.8653
| St. CatharinesWind2095RCP4.5 | St. Catharines | Wind | RCP4.5 | 2095 | 89.5079 | 96.8315 | 104.6571 | 112.3633 | 120.0959
| St. CatharinesWind2100RCP4.5 | St. Catharines | Wind | RCP4.5 | 2100 | 89.5901 | 96.9469 | 104.8152 | 112.5561 | 120.3265
| St. CatharinesWind2023RCP6.0 | St. Catharines | Wind | RCP6.0 | 2023 | 88.9824 | 96.0647 | 103.581 | 111.05 | 118.5126
| St. CatharinesWind2025RCP6.0 | St. Catharines | Wind | RCP6.0 | 2025 | 88.953 | 96.0347 | 103.5487 | 111.0154 | 118.4758
| St. CatharinesWind2030RCP6.0 | St. Catharines | Wind | RCP6.0 | 2030 | 88.9237 | 96.0046 | 103.5164 | 110.9808 | 118.4389
| St. CatharinesWind2035RCP6.0 | St. Catharines | Wind | RCP6.0 | 2035 | 88.8943 | 95.9746 | 103.4841 | 110.9463 | 118.4021
| St. CatharinesWind2040RCP6.0 | St. Catharines | Wind | RCP6.0 | 2040 | 88.8649 | 95.9446 | 103.4518 | 110.9117 | 118.3653
| St. CatharinesWind2045RCP6.0 | St. Catharines | Wind | RCP6.0 | 2045 | 88.8356 | 95.9145 | 103.4195 | 110.8771 | 118.3285
| St. CatharinesWind2050RCP6.0 | St. Catharines | Wind | RCP6.0 | 2050 | 88.8644 | 95.9585 | 103.4831 | 110.9539 | 118.4219
| St. CatharinesWind2055RCP6.0 | St. Catharines | Wind | RCP6.0 | 2055 | 88.9225 | 96.0325 | 103.579 | 111.0652 | 118.5521
| St. CatharinesWind2060RCP6.0 | St. Catharines | Wind | RCP6.0 | 2060 | 88.9806 | 96.1065 | 103.6748 | 111.1766 | 118.6823
| St. CatharinesWind2065RCP6.0 | St. Catharines | Wind | RCP6.0 | 2065 | 89.0388 | 96.1805 | 103.7707 | 111.2879 | 118.8126
| St. CatharinesWind2070RCP6.0 | St. Catharines | Wind | RCP6.0 | 2070 | 89.0969 | 96.2544 | 103.8666 | 111.3992 | 118.9428
| St. CatharinesWind2075RCP6.0 | St. Catharines | Wind | RCP6.0 | 2075 | 89.2202 | 96.4276 | 104.1038 | 111.6884 | 119.2887
| St. CatharinesWind2080RCP6.0 | St. Catharines | Wind | RCP6.0 | 2080 | 89.3435 | 96.6007 | 104.3409 | 111.9776 | 119.6347
| St. CatharinesWind2085RCP6.0 | St. Catharines | Wind | RCP6.0 | 2085 | 89.4668 | 96.7738 | 104.5781 | 112.2669 | 119.9806
| St. CatharinesWind2090RCP6.0 | St. Catharines | Wind | RCP6.0 | 2090 | 89.778 | 97.1872 | 105.1178 | 112.9162 | 120.7452
| St. CatharinesWind2095RCP6.0 | St. Catharines | Wind | RCP6.0 | 2095 | 89.9659 | 97.4275 | 105.4204 | 113.2764 | 121.1638
| St. CatharinesWind2100RCP6.0 | St. Catharines | Wind | RCP6.0 | 2100 | 90.1538 | 97.6679 | 105.723 | 113.6366 | 121.5824
| St. CatharinesWind2023RCP8.5 | St. Catharines | Wind | RCP8.5 | 2023 | 88.9824 | 96.0647 | 103.581 | 111.05 | 118.5126
| St. CatharinesWind2025RCP8.5 | St. Catharines | Wind | RCP8.5 | 2025 | 88.9237 | 96.0046 | 103.5164 | 110.9808 | 118.4389
| St. CatharinesWind2030RCP8.5 | St. Catharines | Wind | RCP8.5 | 2030 | 88.8649 | 95.9446 | 103.4518 | 110.9117 | 118.3653
| St. CatharinesWind2035RCP8.5 | St. Catharines | Wind | RCP8.5 | 2035 | 88.8062 | 95.8845 | 103.3872 | 110.8426 | 118.2916
| St. CatharinesWind2040RCP8.5 | St. Catharines | Wind | RCP8.5 | 2040 | 88.9031 | 96.0078 | 103.547 | 111.0281 | 118.5087
| St. CatharinesWind2045RCP8.5 | St. Catharines | Wind | RCP8.5 | 2045 | 89 | 96.1311 | 103.7068 | 111.2137 | 118.7258
| St. CatharinesWind2050RCP8.5 | St. Catharines | Wind | RCP8.5 | 2050 | 89.2613 | 96.4853 | 104.1828 | 111.7848 | 119.4041
| St. CatharinesWind2055RCP8.5 | St. Catharines | Wind | RCP8.5 | 2055 | 89.4257 | 96.7161 | 104.499 | 112.1705 | 119.8653
| St. CatharinesWind2060RCP8.5 | St. Catharines | Wind | RCP8.5 | 2060 | 89.778 | 97.1872 | 105.1178 | 112.9162 | 120.7452
| St. CatharinesWind2065RCP8.5 | St. Catharines | Wind | RCP8.5 | 2065 | 89.9659 | 97.4275 | 105.4204 | 113.2764 | 121.1638
| St. CatharinesWind2070RCP8.5 | St. Catharines | Wind | RCP8.5 | 2070 | 90.2154 | 97.7722 | 105.8896 | 113.8548 | 121.8459
| St. CatharinesWind2075RCP8.5 | St. Catharines | Wind | RCP8.5 | 2075 | 90.2771 | 97.8765 | 106.0562 | 114.0731 | 122.1095
| St. CatharinesWind2080RCP8.5 | St. Catharines | Wind | RCP8.5 | 2080 | 90.3387 | 97.9809 | 106.2228 | 114.2914 | 122.3731
| St. CatharinesWind2085RCP8.5 | St. Catharines | Wind | RCP8.5 | 2085 | 90.4048 | 98.09 | 106.3809 | 114.4879 | 122.6173
| St. CatharinesWind2090RCP8.5 | St. Catharines | Wind | RCP8.5 | 2090 | 90.4709 | 98.1991 | 106.539 | 114.6843 | 122.8614
| St. CatharinesWind2095RCP8.5 | St. Catharines | Wind | RCP8.5 | 2095 | 90.4709 | 98.1991 | 106.539 | 114.6843 | 122.8614
| St. CatharinesWind2100RCP8.5 | St. Catharines | Wind | RCP8.5 | 2100 | 90.4709 | 98.1991 | 106.539 | 114.6843 | 122.8614
| St. Mary'sIce Accretion2023RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425
| St. Mary'sIce Accretion2025RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2025 | 17.1352 | 20.5563 | 24.8625 | 28.1605 | 31.4423
| St. Mary'sIce Accretion2030RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2030 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542
| St. Mary'sIce Accretion2035RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2035 | 17.17 | 20.6255 | 24.9875 | 28.3206 | 31.6418
| St. Mary'sIce Accretion2040RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2040 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415
| St. Mary'sIce Accretion2045RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2045 | 17.2048 | 20.6947 | 25.1125 | 28.4807 | 31.8412
| St. Mary'sIce Accretion2050RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2050 | 17.1526 | 20.6794 | 25.145 | 28.5438 | 31.941
| St. Mary'sIce Accretion2055RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2055 | 17.083 | 20.6296 | 25.115 | 28.5268 | 31.941
| St. Mary'sIce Accretion2060RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2060 | 17.0134 | 20.5799 | 25.085 | 28.5099 | 31.941
| St. Mary'sIce Accretion2065RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2065 | 16.9439 | 20.53 | 25.055 | 28.4929 | 31.941
| St. Mary'sIce Accretion2070RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2070 | 16.8743 | 20.4802 | 25.025 | 28.476 | 31.941
| St. Mary'sIce Accretion2075RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2075 | 16.8424 | 20.4664 | 25.0375 | 28.5042 | 31.9883
| St. Mary'sIce Accretion2080RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2080 | 16.8105 | 20.4526 | 25.05 | 28.5325 | 32.0355
| St. Mary'sIce Accretion2085RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2085 | 16.7786 | 20.4387 | 25.0625 | 28.5607 | 32.0827
| St. Mary'sIce Accretion2090RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2090 | 16.7467 | 20.4249 | 25.075 | 28.589 | 32.13
| St. Mary'sIce Accretion2095RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2095 | 16.7148 | 20.4111 | 25.0875 | 28.6172 | 32.1773
| St. Mary'sIce Accretion2100RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.3972 | 25.1 | 28.6455 | 32.2245
| St. Mary'sIce Accretion2023RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425
| St. Mary'sIce Accretion2025RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2025 | 17.1352 | 20.5563 | 24.8625 | 28.1605 | 31.4423
| St. Mary'sIce Accretion2030RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2030 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542
| St. Mary'sIce Accretion2035RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2035 | 17.17 | 20.6255 | 24.9875 | 28.3206 | 31.6418
| St. Mary'sIce Accretion2040RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2040 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415
| St. Mary'sIce Accretion2045RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2045 | 17.2048 | 20.6947 | 25.1125 | 28.4807 | 31.8412
| St. Mary'sIce Accretion2050RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2050 | 17.1526 | 20.6794 | 25.145 | 28.5438 | 31.941
| St. Mary'sIce Accretion2055RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2055 | 17.083 | 20.6296 | 25.115 | 28.5268 | 31.941
| St. Mary'sIce Accretion2060RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2060 | 17.0134 | 20.5799 | 25.085 | 28.5099 | 31.941
| St. Mary'sIce Accretion2065RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2065 | 16.9439 | 20.53 | 25.055 | 28.4929 | 31.941
| St. Mary'sIce Accretion2070RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2070 | 16.8743 | 20.4802 | 25.025 | 28.476 | 31.941
| St. Mary'sIce Accretion2075RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2075 | 16.8264 | 20.4595 | 25.0437 | 28.5184 | 32.0119
| St. Mary'sIce Accretion2080RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2080 | 16.7786 | 20.4387 | 25.0625 | 28.5607 | 32.0827
| St. Mary'sIce Accretion2085RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2085 | 16.7308 | 20.418 | 25.0813 | 28.6031 | 32.1536
| St. Mary'sIce Accretion2090RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2090 | 16.4742 | 20.1898 | 24.8833 | 28.4289 | 31.9935
| St. Mary'sIce Accretion2095RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2095 | 16.2654 | 19.9822 | 24.6667 | 28.2123 | 31.7625
| St. Mary'sIce Accretion2100RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2100 | 16.0566 | 19.7747 | 24.45 | 27.9957 | 31.5315
| St. Mary'sIce Accretion2023RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425
| St. Mary'sIce Accretion2025RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2025 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542
| St. Mary'sIce Accretion2030RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2030 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415
| St. Mary'sIce Accretion2035RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2035 | 17.2222 | 20.7293 | 25.175 | 28.5607 | 31.941
| St. Mary'sIce Accretion2040RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2040 | 17.1062 | 20.6462 | 25.125 | 28.5325 | 31.941
| St. Mary'sIce Accretion2045RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2045 | 16.9902 | 20.5633 | 25.075 | 28.5042 | 31.941
| St. Mary'sIce Accretion2050RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2050 | 16.8105 | 20.4526 | 25.05 | 28.5325 | 32.0355
| St. Mary'sIce Accretion2055RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2055 | 16.7467 | 20.4249 | 25.075 | 28.589 | 32.13
| St. Mary'sIce Accretion2060RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2060 | 16.4742 | 20.1898 | 24.8833 | 28.4289 | 31.9935
| St. Mary'sIce Accretion2065RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2065 | 16.2654 | 19.9822 | 24.6667 | 28.2123 | 31.7625
| St. Mary'sIce Accretion2070RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2070 | 15.6797 | 19.3528 | 23.975 | 27.4778 | 30.9645
| St. Mary'sIce Accretion2075RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2075 | 15.3028 | 18.9309 | 23.5 | 26.9599 | 30.3975
| St. Mary'sIce Accretion2080RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2080 | 14.9259 | 18.509 | 23.025 | 26.442 | 29.8305
| St. Mary'sIce Accretion2085RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2085 | 14.1431 | 17.5856 | 21.925 | 25.2131 | 28.476
| St. Mary'sIce Accretion2090RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2090 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215
| St. Mary'sIce Accretion2095RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2095 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215
| St. Mary'sIce Accretion2100RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2100 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215
| St. Mary'sWind2023RCP4.5 | St. Mary's | Wind | RCP4.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| St. Mary'sWind2025RCP4.5 | St. Mary's | Wind | RCP4.5 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
| St. Mary'sWind2030RCP4.5 | St. Mary's | Wind | RCP4.5 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| St. Mary'sWind2035RCP4.5 | St. Mary's | Wind | RCP4.5 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
| St. Mary'sWind2040RCP4.5 | St. Mary's | Wind | RCP4.5 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| St. Mary'sWind2045RCP4.5 | St. Mary's | Wind | RCP4.5 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
| St. Mary'sWind2050RCP4.5 | St. Mary's | Wind | RCP4.5 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
| St. Mary'sWind2055RCP4.5 | St. Mary's | Wind | RCP4.5 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
| St. Mary'sWind2060RCP4.5 | St. Mary's | Wind | RCP4.5 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
| St. Mary'sWind2065RCP4.5 | St. Mary's | Wind | RCP4.5 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
| St. Mary'sWind2070RCP4.5 | St. Mary's | Wind | RCP4.5 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
| St. Mary'sWind2075RCP4.5 | St. Mary's | Wind | RCP4.5 | 2075 | 86.3504 | 93.3577 | 100.8387 | 108.226 | 115.6228
| St. Mary'sWind2080RCP4.5 | St. Mary's | Wind | RCP4.5 | 2080 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
| St. Mary'sWind2085RCP4.5 | St. Mary's | Wind | RCP4.5 | 2085 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
| St. Mary'sWind2090RCP4.5 | St. Mary's | Wind | RCP4.5 | 2090 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
| St. Mary'sWind2095RCP4.5 | St. Mary's | Wind | RCP4.5 | 2095 | 86.7678 | 93.9167 | 101.5705 | 109.1068 | 116.6655
| St. Mary'sWind2100RCP4.5 | St. Mary's | Wind | RCP4.5 | 2100 | 86.8722 | 94.0565 | 101.7534 | 109.327 | 116.9262
| St. Mary'sWind2023RCP6.0 | St. Mary's | Wind | RCP6.0 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| St. Mary'sWind2025RCP6.0 | St. Mary's | Wind | RCP6.0 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
| St. Mary'sWind2030RCP6.0 | St. Mary's | Wind | RCP6.0 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| St. Mary'sWind2035RCP6.0 | St. Mary's | Wind | RCP6.0 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
| St. Mary'sWind2040RCP6.0 | St. Mary's | Wind | RCP6.0 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| St. Mary'sWind2045RCP6.0 | St. Mary's | Wind | RCP6.0 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
| St. Mary'sWind2050RCP6.0 | St. Mary's | Wind | RCP6.0 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
| St. Mary'sWind2055RCP6.0 | St. Mary's | Wind | RCP6.0 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
| St. Mary'sWind2060RCP6.0 | St. Mary's | Wind | RCP6.0 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
| St. Mary'sWind2065RCP6.0 | St. Mary's | Wind | RCP6.0 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
| St. Mary'sWind2070RCP6.0 | St. Mary's | Wind | RCP6.0 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
| St. Mary'sWind2075RCP6.0 | St. Mary's | Wind | RCP6.0 | 2075 | 86.4026 | 93.4276 | 100.9302 | 108.3361 | 115.7531
| St. Mary'sWind2080RCP6.0 | St. Mary's | Wind | RCP6.0 | 2080 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
| St. Mary'sWind2085RCP6.0 | St. Mary's | Wind | RCP6.0 | 2085 | 86.7157 | 93.8469 | 101.479 | 108.9967 | 116.5351
| St. Mary'sWind2090RCP6.0 | St. Mary's | Wind | RCP6.0 | 2090 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
| St. Mary'sWind2095RCP6.0 | St. Mary's | Wind | RCP6.0 | 2095 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
| St. Mary'sWind2100RCP6.0 | St. Mary's | Wind | RCP6.0 | 2100 | 87.7861 | 95.1502 | 103.0568 | 110.8265 | 118.6131
| St. Mary'sWind2023RCP8.5 | St. Mary's | Wind | RCP8.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| St. Mary'sWind2025RCP8.5 | St. Mary's | Wind | RCP8.5 | 2025 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| St. Mary'sWind2030RCP8.5 | St. Mary's | Wind | RCP8.5 | 2030 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| St. Mary'sWind2035RCP8.5 | St. Mary's | Wind | RCP8.5 | 2035 | 86.0768 | 93.0084 | 100.3912 | 107.7017 | 115.0269
| St. Mary'sWind2040RCP8.5 | St. Mary's | Wind | RCP8.5 | 2040 | 86.1332 | 93.0782 | 100.4794 | 107.8031 | 115.1386
| St. Mary'sWind2045RCP8.5 | St. Mary's | Wind | RCP8.5 | 2045 | 86.1896 | 93.1481 | 100.5676 | 107.9044 | 115.2504
| St. Mary'sWind2050RCP8.5 | St. Mary's | Wind | RCP8.5 | 2050 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
| St. Mary'sWind2055RCP8.5 | St. Mary's | Wind | RCP8.5 | 2055 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
| St. Mary'sWind2060RCP8.5 | St. Mary's | Wind | RCP8.5 | 2060 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
| St. Mary'sWind2065RCP8.5 | St. Mary's | Wind | RCP8.5 | 2065 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
| St. Mary'sWind2070RCP8.5 | St. Mary's | Wind | RCP8.5 | 2070 | 88.0541 | 95.5026 | 103.5207 | 111.3788 | 119.2611
| St. Mary'sWind2075RCP8.5 | St. Mary's | Wind | RCP8.5 | 2075 | 88.322 | 95.855 | 103.9845 | 111.9311 | 119.9091
| St. Mary'sWind2080RCP8.5 | St. Mary's | Wind | RCP8.5 | 2080 | 88.59 | 96.2074 | 104.4484 | 112.4833 | 120.5571
| St. Mary'sWind2085RCP8.5 | St. Mary's | Wind | RCP8.5 | 2085 | 88.9454 | 96.6585 | 105.0217 | 113.1649 | 121.3447
| St. Mary'sWind2090RCP8.5 | St. Mary's | Wind | RCP8.5 | 2090 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| St. Mary'sWind2095RCP8.5 | St. Mary's | Wind | RCP8.5 | 2095 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| St. Mary'sWind2100RCP8.5 | St. Mary's | Wind | RCP8.5 | 2100 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| St. ThomasIce Accretion2023RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2023 | 21.9553 | 26.3475 | 31.904 | 36.1238 | 40.3603
| St. ThomasIce Accretion2025RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2025 | 21.8254 | 26.2059 | 31.7493 | 35.9611 | 40.1856
| St. ThomasIce Accretion2030RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2030 | 21.6956 | 26.0642 | 31.5947 | 35.7984 | 40.0109
| St. ThomasIce Accretion2035RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2035 | 21.5657 | 25.9226 | 31.44 | 35.6357 | 39.8362
| St. ThomasIce Accretion2040RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2040 | 21.4358 | 25.7809 | 31.2853 | 35.473 | 39.6614
| St. ThomasIce Accretion2045RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2045 | 21.3059 | 25.6393 | 31.1307 | 35.3102 | 39.4867
| St. ThomasIce Accretion2050RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2050 | 20.7618 | 25.0408 | 30.4576 | 34.5834 | 38.6991
| St. ThomasIce Accretion2055RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2055 | 20.3477 | 24.5839 | 29.9392 | 34.0193 | 38.0863
| St. ThomasIce Accretion2060RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2060 | 19.9335 | 24.1271 | 29.4208 | 33.4552 | 37.4734
| St. ThomasIce Accretion2065RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2065 | 19.5193 | 23.6703 | 28.9024 | 32.8911 | 36.8605
| St. ThomasIce Accretion2070RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2070 | 19.1052 | 23.2134 | 28.384 | 32.327 | 36.2477
| St. ThomasIce Accretion2075RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2075 | 18.9604 | 23.0674 | 28.2347 | 32.1703 | 36.0864
| St. ThomasIce Accretion2080RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2080 | 18.8157 | 22.9213 | 28.0853 | 32.0137 | 35.9251
| St. ThomasIce Accretion2085RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2085 | 18.6709 | 22.7752 | 27.936 | 31.857 | 35.7638
| St. ThomasIce Accretion2090RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2090 | 18.5262 | 22.6291 | 27.7867 | 31.7003 | 35.6026
| St. ThomasIce Accretion2095RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2095 | 18.3815 | 22.483 | 27.6373 | 31.5436 | 35.4413
| St. ThomasIce Accretion2100RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2100 | 18.2367 | 22.337 | 27.488 | 31.3869 | 35.28
| St. ThomasIce Accretion2023RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2023 | 21.9553 | 26.3475 | 31.904 | 36.1238 | 40.3603
| St. ThomasIce Accretion2025RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2025 | 21.8254 | 26.2059 | 31.7493 | 35.9611 | 40.1856
| St. ThomasIce Accretion2030RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2030 | 21.6956 | 26.0642 | 31.5947 | 35.7984 | 40.0109
| St. ThomasIce Accretion2035RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2035 | 21.5657 | 25.9226 | 31.44 | 35.6357 | 39.8362
| St. ThomasIce Accretion2040RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2040 | 21.4358 | 25.7809 | 31.2853 | 35.473 | 39.6614
| St. ThomasIce Accretion2045RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2045 | 21.3059 | 25.6393 | 31.1307 | 35.3102 | 39.4867
| St. ThomasIce Accretion2050RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2050 | 20.7618 | 25.0408 | 30.4576 | 34.5834 | 38.6991
| St. ThomasIce Accretion2055RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2055 | 20.3477 | 24.5839 | 29.9392 | 34.0193 | 38.0863
| St. ThomasIce Accretion2060RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2060 | 19.9335 | 24.1271 | 29.4208 | 33.4552 | 37.4734
| St. ThomasIce Accretion2065RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2065 | 19.5193 | 23.6703 | 28.9024 | 32.8911 | 36.8605
| St. ThomasIce Accretion2070RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2070 | 19.1052 | 23.2134 | 28.384 | 32.327 | 36.2477
| St. ThomasIce Accretion2075RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2075 | 18.888 | 22.9943 | 28.16 | 32.092 | 36.0058
| St. ThomasIce Accretion2080RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2080 | 18.6709 | 22.7752 | 27.936 | 31.857 | 35.7638
| St. ThomasIce Accretion2085RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2085 | 18.4538 | 22.5561 | 27.712 | 31.6219 | 35.5219
| St. ThomasIce Accretion2090RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2090 | 17.7172 | 21.7526 | 26.8267 | 30.6637 | 34.487
| St. ThomasIce Accretion2095RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2095 | 17.1976 | 21.1683 | 26.1653 | 29.9405 | 33.6941
| St. ThomasIce Accretion2100RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2100 | 16.678 | 20.584 | 25.504 | 29.2173 | 32.9011
| St. ThomasIce Accretion2023RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2023 | 21.9553 | 26.3475 | 31.904 | 36.1238 | 40.3603
| St. ThomasIce Accretion2025RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2025 | 21.6956 | 26.0642 | 31.5947 | 35.7984 | 40.0109
| St. ThomasIce Accretion2030RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2030 | 21.4358 | 25.7809 | 31.2853 | 35.473 | 39.6614
| St. ThomasIce Accretion2035RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2035 | 21.176 | 25.4976 | 30.976 | 35.1475 | 39.312
| St. ThomasIce Accretion2040RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2040 | 20.4857 | 24.7362 | 30.112 | 34.2074 | 38.2906
| St. ThomasIce Accretion2045RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2045 | 19.7954 | 23.9748 | 29.248 | 33.2672 | 37.2691
| St. ThomasIce Accretion2050RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2050 | 18.8157 | 22.9213 | 28.0853 | 32.0137 | 35.9251
| St. ThomasIce Accretion2055RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2055 | 18.5262 | 22.6291 | 27.7867 | 31.7003 | 35.6026
| St. ThomasIce Accretion2060RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2060 | 17.7172 | 21.7526 | 26.8267 | 30.6637 | 34.487
| St. ThomasIce Accretion2065RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2065 | 17.1976 | 21.1683 | 26.1653 | 29.9405 | 33.6941
| St. ThomasIce Accretion2070RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2070 | 16.344 | 20.2299 | 25.12 | 28.7954 | 32.4576
| St. ThomasIce Accretion2075RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2075 | 16.01 | 19.8757 | 24.736 | 28.3735 | 32.0141
| St. ThomasIce Accretion2080RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2080 | 15.676 | 19.5216 | 24.352 | 27.9517 | 31.5706
| St. ThomasIce Accretion2085RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2085 | 14.6851 | 18.353 | 22.944 | 26.3787 | 29.8166
| St. ThomasIce Accretion2090RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2090 | 13.6943 | 17.1843 | 21.536 | 24.8058 | 28.0627
| St. ThomasIce Accretion2095RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2095 | 13.6943 | 17.1843 | 21.536 | 24.8058 | 28.0627
| St. ThomasIce Accretion2100RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2100 | 13.6943 | 17.1843 | 21.536 | 24.8058 | 28.0627
| St. ThomasWind2023RCP4.5 | St. Thomas | Wind | RCP4.5 | 2023 | 87.9269 | 94.8505 | 102.1817 | 109.4749 | 116.775
| St. ThomasWind2025RCP4.5 | St. Thomas | Wind | RCP4.5 | 2025 | 88.0373 | 94.9977 | 102.3753 | 109.7073 | 117.0475
| St. ThomasWind2030RCP4.5 | St. Thomas | Wind | RCP4.5 | 2030 | 88.1478 | 95.1448 | 102.5689 | 109.9396 | 117.32
| St. ThomasWind2035RCP4.5 | St. Thomas | Wind | RCP4.5 | 2035 | 88.2583 | 95.292 | 102.7625 | 110.172 | 117.5925
| St. ThomasWind2040RCP4.5 | St. Thomas | Wind | RCP4.5 | 2040 | 88.3687 | 95.4391 | 102.956 | 110.4043 | 117.865
| St. ThomasWind2045RCP4.5 | St. Thomas | Wind | RCP4.5 | 2045 | 88.4792 | 95.5863 | 103.1496 | 110.6367 | 118.1375
| St. ThomasWind2050RCP4.5 | St. Thomas | Wind | RCP4.5 | 2050 | 88.642 | 95.8067 | 103.4442 | 110.9944 | 118.5597
| St. ThomasWind2055RCP4.5 | St. Thomas | Wind | RCP4.5 | 2055 | 88.6943 | 95.88 | 103.5452 | 111.1197 | 118.7093
| St. ThomasWind2060RCP4.5 | St. Thomas | Wind | RCP4.5 | 2060 | 88.7467 | 95.9533 | 103.6462 | 111.2451 | 118.859
| St. ThomasWind2065RCP4.5 | St. Thomas | Wind | RCP4.5 | 2065 | 88.799 | 96.0265 | 103.7472 | 111.3705 | 119.0087
| St. ThomasWind2070RCP4.5 | St. Thomas | Wind | RCP4.5 | 2070 | 88.8513 | 96.0998 | 103.8482 | 111.4958 | 119.1584
| St. ThomasWind2075RCP4.5 | St. Thomas | Wind | RCP4.5 | 2075 | 89.0054 | 96.3002 | 104.1074 | 111.8038 | 119.5172
| St. ThomasWind2080RCP4.5 | St. Thomas | Wind | RCP4.5 | 2080 | 89.1595 | 96.5006 | 104.3667 | 112.1118 | 119.8761
| St. ThomasWind2085RCP4.5 | St. Thomas | Wind | RCP4.5 | 2085 | 89.3135 | 96.7009 | 104.6259 | 112.4198 | 120.2349
| St. ThomasWind2090RCP4.5 | St. Thomas | Wind | RCP4.5 | 2090 | 89.4676 | 96.9013 | 104.8851 | 112.7278 | 120.5938
| St. ThomasWind2095RCP4.5 | St. Thomas | Wind | RCP4.5 | 2095 | 89.6217 | 97.1017 | 105.1444 | 113.0358 | 120.9527
| St. ThomasWind2100RCP4.5 | St. Thomas | Wind | RCP4.5 | 2100 | 89.7757 | 97.3021 | 105.4036 | 113.3438 | 121.3115
| St. ThomasWind2023RCP6.0 | St. Thomas | Wind | RCP6.0 | 2023 | 87.9269 | 94.8505 | 102.1817 | 109.4749 | 116.775
| St. ThomasWind2025RCP6.0 | St. Thomas | Wind | RCP6.0 | 2025 | 88.0373 | 94.9977 | 102.3753 | 109.7073 | 117.0475
| St. ThomasWind2030RCP6.0 | St. Thomas | Wind | RCP6.0 | 2030 | 88.1478 | 95.1448 | 102.5689 | 109.9396 | 117.32
| St. ThomasWind2035RCP6.0 | St. Thomas | Wind | RCP6.0 | 2035 | 88.2583 | 95.292 | 102.7625 | 110.172 | 117.5925
| St. ThomasWind2040RCP6.0 | St. Thomas | Wind | RCP6.0 | 2040 | 88.3687 | 95.4391 | 102.956 | 110.4043 | 117.865
| St. ThomasWind2045RCP6.0 | St. Thomas | Wind | RCP6.0 | 2045 | 88.4792 | 95.5863 | 103.1496 | 110.6367 | 118.1375
| St. ThomasWind2050RCP6.0 | St. Thomas | Wind | RCP6.0 | 2050 | 88.642 | 95.8067 | 103.4442 | 110.9944 | 118.5597
| St. ThomasWind2055RCP6.0 | St. Thomas | Wind | RCP6.0 | 2055 | 88.6943 | 95.88 | 103.5452 | 111.1197 | 118.7093
| St. ThomasWind2060RCP6.0 | St. Thomas | Wind | RCP6.0 | 2060 | 88.7467 | 95.9533 | 103.6462 | 111.2451 | 118.859
| St. ThomasWind2065RCP6.0 | St. Thomas | Wind | RCP6.0 | 2065 | 88.799 | 96.0265 | 103.7472 | 111.3705 | 119.0087
| St. ThomasWind2070RCP6.0 | St. Thomas | Wind | RCP6.0 | 2070 | 88.8513 | 96.0998 | 103.8482 | 111.4958 | 119.1584
| St. ThomasWind2075RCP6.0 | St. Thomas | Wind | RCP6.0 | 2075 | 89.0824 | 96.4004 | 104.2371 | 111.9578 | 119.6967
| St. ThomasWind2080RCP6.0 | St. Thomas | Wind | RCP6.0 | 2080 | 89.3135 | 96.7009 | 104.6259 | 112.4198 | 120.2349
| St. ThomasWind2085RCP6.0 | St. Thomas | Wind | RCP6.0 | 2085 | 89.5446 | 97.0015 | 105.0148 | 112.8818 | 120.7732
| St. ThomasWind2090RCP6.0 | St. Thomas | Wind | RCP6.0 | 2090 | 90.1566 | 97.7874 | 106.013 | 114.0607 | 122.1405
| St. ThomasWind2095RCP6.0 | St. Thomas | Wind | RCP6.0 | 2095 | 90.5374 | 98.2727 | 106.6223 | 114.7775 | 122.9695
| St. ThomasWind2100RCP6.0 | St. Thomas | Wind | RCP6.0 | 2100 | 90.9182 | 98.758 | 107.2317 | 115.4944 | 123.7985
| St. ThomasWind2023RCP8.5 | St. Thomas | Wind | RCP8.5 | 2023 | 87.9269 | 94.8505 | 102.1817 | 109.4749 | 116.775
| St. ThomasWind2025RCP8.5 | St. Thomas | Wind | RCP8.5 | 2025 | 88.1478 | 95.1448 | 102.5689 | 109.9396 | 117.32
| St. ThomasWind2030RCP8.5 | St. Thomas | Wind | RCP8.5 | 2030 | 88.3687 | 95.4391 | 102.956 | 110.4043 | 117.865
| St. ThomasWind2035RCP8.5 | St. Thomas | Wind | RCP8.5 | 2035 | 88.5897 | 95.7335 | 103.3432 | 110.869 | 118.41
| St. ThomasWind2040RCP8.5 | St. Thomas | Wind | RCP8.5 | 2040 | 88.6769 | 95.8556 | 103.5115 | 111.0779 | 118.6594
| St. ThomasWind2045RCP8.5 | St. Thomas | Wind | RCP8.5 | 2045 | 88.7641 | 95.9777 | 103.6799 | 111.2869 | 118.9089
| St. ThomasWind2050RCP8.5 | St. Thomas | Wind | RCP8.5 | 2050 | 89.1595 | 96.5006 | 104.3667 | 112.1118 | 119.8761
| St. ThomasWind2055RCP8.5 | St. Thomas | Wind | RCP8.5 | 2055 | 89.4676 | 96.9013 | 104.8851 | 112.7278 | 120.5938
| St. ThomasWind2060RCP8.5 | St. Thomas | Wind | RCP8.5 | 2060 | 90.1566 | 97.7874 | 106.013 | 114.0607 | 122.1405
| St. ThomasWind2065RCP8.5 | St. Thomas | Wind | RCP8.5 | 2065 | 90.5374 | 98.2727 | 106.6223 | 114.7775 | 122.9695
| St. ThomasWind2070RCP8.5 | St. Thomas | Wind | RCP8.5 | 2070 | 91.1537 | 99.0523 | 107.6054 | 115.9375 | 124.309
| St. ThomasWind2075RCP8.5 | St. Thomas | Wind | RCP8.5 | 2075 | 91.3892 | 99.3466 | 107.9791 | 116.3806 | 124.8194
| St. ThomasWind2080RCP8.5 | St. Thomas | Wind | RCP8.5 | 2080 | 91.6246 | 99.6409 | 108.3528 | 116.8237 | 125.3299
| St. ThomasWind2085RCP8.5 | St. Thomas | Wind | RCP8.5 | 2085 | 92.0258 | 100.1716 | 109.0497 | 117.6558 | 126.3086
| St. ThomasWind2090RCP8.5 | St. Thomas | Wind | RCP8.5 | 2090 | 92.427 | 100.7024 | 109.7466 | 118.4879 | 127.2873
| St. ThomasWind2095RCP8.5 | St. Thomas | Wind | RCP8.5 | 2095 | 92.427 | 100.7024 | 109.7466 | 118.4879 | 127.2873
| St. ThomasWind2100RCP8.5 | St. Thomas | Wind | RCP8.5 | 2100 | 92.427 | 100.7024 | 109.7466 | 118.4879 | 127.2873
| StirlingIce Accretion2023RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3065 | 31.563
| StirlingIce Accretion2025RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2025 | 17.544 | 20.9091 | 25.1667 | 28.4148 | 31.6837
| StirlingIce Accretion2030RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2030 | 17.6049 | 20.9852 | 25.2583 | 28.5231 | 31.8045
| StirlingIce Accretion2035RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2035 | 17.6658 | 21.0613 | 25.35 | 28.6314 | 31.9252
| StirlingIce Accretion2040RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2040 | 17.7267 | 21.1373 | 25.4417 | 28.7397 | 32.046
| StirlingIce Accretion2045RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2045 | 17.7876 | 21.2134 | 25.5333 | 28.848 | 32.1667
| StirlingIce Accretion2050RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2050 | 17.8032 | 21.248 | 25.595 | 28.928 | 32.2623
| StirlingIce Accretion2055RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2055 | 17.758 | 21.2065 | 25.565 | 28.8997 | 32.2371
| StirlingIce Accretion2060RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2060 | 17.7128 | 21.165 | 25.535 | 28.8715 | 32.2119
| StirlingIce Accretion2065RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2065 | 17.6675 | 21.1235 | 25.505 | 28.8432 | 32.1867
| StirlingIce Accretion2070RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2070 | 17.6223 | 21.082 | 25.475 | 28.815 | 32.1615
| StirlingIce Accretion2075RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2075 | 17.6919 | 21.1927 | 25.6375 | 29.0175 | 32.403
| StirlingIce Accretion2080RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2080 | 17.7615 | 21.3033 | 25.8 | 29.2199 | 32.6445
| StirlingIce Accretion2085RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2085 | 17.8311 | 21.414 | 25.9625 | 29.4224 | 32.886
| StirlingIce Accretion2090RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2090 | 17.9006 | 21.5247 | 26.125 | 29.6248 | 33.1275
| StirlingIce Accretion2095RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2095 | 17.9702 | 21.6353 | 26.2875 | 29.8273 | 33.369
| StirlingIce Accretion2100RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2100 | 18.0398 | 21.746 | 26.45 | 30.0297 | 33.6105
| StirlingIce Accretion2023RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3065 | 31.563
| StirlingIce Accretion2025RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2025 | 17.544 | 20.9091 | 25.1667 | 28.4148 | 31.6837
| StirlingIce Accretion2030RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2030 | 17.6049 | 20.9852 | 25.2583 | 28.5231 | 31.8045
| StirlingIce Accretion2035RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2035 | 17.6658 | 21.0613 | 25.35 | 28.6314 | 31.9252
| StirlingIce Accretion2040RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2040 | 17.7267 | 21.1373 | 25.4417 | 28.7397 | 32.046
| StirlingIce Accretion2045RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2045 | 17.7876 | 21.2134 | 25.5333 | 28.848 | 32.1667
| StirlingIce Accretion2050RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2050 | 17.8032 | 21.248 | 25.595 | 28.928 | 32.2623
| StirlingIce Accretion2055RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2055 | 17.758 | 21.2065 | 25.565 | 28.8997 | 32.2371
| StirlingIce Accretion2060RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2060 | 17.7128 | 21.165 | 25.535 | 28.8715 | 32.2119
| StirlingIce Accretion2065RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2065 | 17.6675 | 21.1235 | 25.505 | 28.8432 | 32.1867
| StirlingIce Accretion2070RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2070 | 17.6223 | 21.082 | 25.475 | 28.815 | 32.1615
| StirlingIce Accretion2075RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2075 | 17.7267 | 21.248 | 25.7188 | 29.1187 | 32.5237
| StirlingIce Accretion2080RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2080 | 17.8311 | 21.414 | 25.9625 | 29.4224 | 32.886
| StirlingIce Accretion2085RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2085 | 17.9354 | 21.58 | 26.2063 | 29.7261 | 33.2482
| StirlingIce Accretion2090RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2090 | 17.7499 | 21.4486 | 26.1333 | 29.7002 | 33.264
| StirlingIce Accretion2095RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2095 | 17.4599 | 21.1512 | 25.8167 | 29.3706 | 32.9175
| StirlingIce Accretion2100RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2100 | 17.17 | 20.8537 | 25.5 | 29.041 | 32.571
| StirlingIce Accretion2023RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3065 | 31.563
| StirlingIce Accretion2025RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2025 | 17.6049 | 20.9852 | 25.2583 | 28.5231 | 31.8045
| StirlingIce Accretion2030RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2030 | 17.7267 | 21.1373 | 25.4417 | 28.7397 | 32.046
| StirlingIce Accretion2035RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2035 | 17.8485 | 21.2895 | 25.625 | 28.9562 | 32.2875
| StirlingIce Accretion2040RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2040 | 17.7731 | 21.2203 | 25.575 | 28.9092 | 32.2455
| StirlingIce Accretion2045RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2045 | 17.6977 | 21.1512 | 25.525 | 28.8621 | 32.2035
| StirlingIce Accretion2050RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2050 | 17.7615 | 21.3033 | 25.8 | 29.2199 | 32.6445
| StirlingIce Accretion2055RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2055 | 17.9006 | 21.5247 | 26.125 | 29.6248 | 33.1275
| StirlingIce Accretion2060RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2060 | 17.7499 | 21.4486 | 26.1333 | 29.7002 | 33.264
| StirlingIce Accretion2065RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2065 | 17.4599 | 21.1512 | 25.8167 | 29.3706 | 32.9175
| StirlingIce Accretion2070RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2070 | 16.8801 | 20.5287 | 25.1417 | 28.6455 | 32.151
| StirlingIce Accretion2075RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2075 | 16.5901 | 20.2036 | 24.7833 | 28.25 | 31.731
| StirlingIce Accretion2080RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2080 | 16.3002 | 19.8785 | 24.425 | 27.8545 | 31.311
| StirlingIce Accretion2085RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2085 | 15.6826 | 19.1626 | 23.5875 | 26.9222 | 30.2715
| StirlingIce Accretion2090RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2090 | 15.0651 | 18.4468 | 22.75 | 25.99 | 29.232
| StirlingIce Accretion2095RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2095 | 15.0651 | 18.4468 | 22.75 | 25.99 | 29.232
| StirlingIce Accretion2100RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2100 | 15.0651 | 18.4468 | 22.75 | 25.99 | 29.232
| StirlingWind2023RCP4.5 | Stirling | Wind | RCP4.5 | 2023 | 76.1688 | 82.0773 | 88.308 | 94.5178 | 100.7413
| StirlingWind2025RCP4.5 | Stirling | Wind | RCP4.5 | 2025 | 76.1992 | 82.1223 | 88.3696 | 94.5963 | 100.835
| StirlingWind2030RCP4.5 | Stirling | Wind | RCP4.5 | 2030 | 76.2296 | 82.1674 | 88.4312 | 94.6747 | 100.9286
| StirlingWind2035RCP4.5 | Stirling | Wind | RCP4.5 | 2035 | 76.26 | 82.2124 | 88.4928 | 94.7532 | 101.0222
| StirlingWind2040RCP4.5 | Stirling | Wind | RCP4.5 | 2040 | 76.2904 | 82.2574 | 88.5544 | 94.8317 | 101.1159
| StirlingWind2045RCP4.5 | Stirling | Wind | RCP4.5 | 2045 | 76.3208 | 82.3024 | 88.616 | 94.9101 | 101.2095
| StirlingWind2050RCP4.5 | Stirling | Wind | RCP4.5 | 2050 | 76.3269 | 82.3016 | 88.609 | 94.8982 | 101.1908
| StirlingWind2055RCP4.5 | Stirling | Wind | RCP4.5 | 2055 | 76.3026 | 82.2557 | 88.5403 | 94.8078 | 101.0784
| StirlingWind2060RCP4.5 | Stirling | Wind | RCP4.5 | 2060 | 76.2782 | 82.2099 | 88.4717 | 94.7174 | 100.9661
| StirlingWind2065RCP4.5 | Stirling | Wind | RCP4.5 | 2065 | 76.2539 | 82.1641 | 88.403 | 94.627 | 100.8537
| StirlingWind2070RCP4.5 | Stirling | Wind | RCP4.5 | 2070 | 76.2296 | 82.1183 | 88.3344 | 94.5366 | 100.7413
| StirlingWind2075RCP4.5 | Stirling | Wind | RCP4.5 | 2075 | 76.2068 | 82.0923 | 88.3036 | 94.5021 | 100.7046
| StirlingWind2080RCP4.5 | Stirling | Wind | RCP4.5 | 2080 | 76.184 | 82.0664 | 88.2728 | 94.4676 | 100.6678
| StirlingWind2085RCP4.5 | Stirling | Wind | RCP4.5 | 2085 | 76.1612 | 82.0405 | 88.242 | 94.4331 | 100.631
| StirlingWind2090RCP4.5 | Stirling | Wind | RCP4.5 | 2090 | 76.1384 | 82.0146 | 88.2112 | 94.3985 | 100.5942
| StirlingWind2095RCP4.5 | Stirling | Wind | RCP4.5 | 2095 | 76.1156 | 81.9887 | 88.1804 | 94.364 | 100.5574
| StirlingWind2100RCP4.5 | Stirling | Wind | RCP4.5 | 2100 | 76.0928 | 81.9628 | 88.1496 | 94.3295 | 100.5206
| StirlingWind2023RCP6.0 | Stirling | Wind | RCP6.0 | 2023 | 76.1688 | 82.0773 | 88.308 | 94.5178 | 100.7413
| StirlingWind2025RCP6.0 | Stirling | Wind | RCP6.0 | 2025 | 76.1992 | 82.1223 | 88.3696 | 94.5963 | 100.835
| StirlingWind2030RCP6.0 | Stirling | Wind | RCP6.0 | 2030 | 76.2296 | 82.1674 | 88.4312 | 94.6747 | 100.9286
| StirlingWind2035RCP6.0 | Stirling | Wind | RCP6.0 | 2035 | 76.26 | 82.2124 | 88.4928 | 94.7532 | 101.0222
| StirlingWind2040RCP6.0 | Stirling | Wind | RCP6.0 | 2040 | 76.2904 | 82.2574 | 88.5544 | 94.8317 | 101.1159
| StirlingWind2045RCP6.0 | Stirling | Wind | RCP6.0 | 2045 | 76.3208 | 82.3024 | 88.616 | 94.9101 | 101.2095
| StirlingWind2050RCP6.0 | Stirling | Wind | RCP6.0 | 2050 | 76.3269 | 82.3016 | 88.609 | 94.8982 | 101.1908
| StirlingWind2055RCP6.0 | Stirling | Wind | RCP6.0 | 2055 | 76.3026 | 82.2557 | 88.5403 | 94.8078 | 101.0784
| StirlingWind2060RCP6.0 | Stirling | Wind | RCP6.0 | 2060 | 76.2782 | 82.2099 | 88.4717 | 94.7174 | 100.9661
| StirlingWind2065RCP6.0 | Stirling | Wind | RCP6.0 | 2065 | 76.2539 | 82.1641 | 88.403 | 94.627 | 100.8537
| StirlingWind2070RCP6.0 | Stirling | Wind | RCP6.0 | 2070 | 76.2296 | 82.1183 | 88.3344 | 94.5366 | 100.7413
| StirlingWind2075RCP6.0 | Stirling | Wind | RCP6.0 | 2075 | 76.1954 | 82.0794 | 88.2882 | 94.4849 | 100.6862
| StirlingWind2080RCP6.0 | Stirling | Wind | RCP6.0 | 2080 | 76.1612 | 82.0405 | 88.242 | 94.4331 | 100.631
| StirlingWind2085RCP6.0 | Stirling | Wind | RCP6.0 | 2085 | 76.127 | 82.0016 | 88.1958 | 94.3813 | 100.5758
| StirlingWind2090RCP6.0 | Stirling | Wind | RCP6.0 | 2090 | 76.0802 | 81.9382 | 88.1085 | 94.273 | 100.4471
| StirlingWind2095RCP6.0 | Stirling | Wind | RCP6.0 | 2095 | 76.0675 | 81.9137 | 88.0675 | 94.2165 | 100.3735
| StirlingWind2100RCP6.0 | Stirling | Wind | RCP6.0 | 2100 | 76.0548 | 81.8891 | 88.0264 | 94.16 | 100.2999
| StirlingWind2023RCP8.5 | Stirling | Wind | RCP8.5 | 2023 | 76.1688 | 82.0773 | 88.308 | 94.5178 | 100.7413
| StirlingWind2025RCP8.5 | Stirling | Wind | RCP8.5 | 2025 | 76.2296 | 82.1674 | 88.4312 | 94.6747 | 100.9286
| StirlingWind2030RCP8.5 | Stirling | Wind | RCP8.5 | 2030 | 76.2904 | 82.2574 | 88.5544 | 94.8317 | 101.1159
| StirlingWind2035RCP8.5 | Stirling | Wind | RCP8.5 | 2035 | 76.3512 | 82.3474 | 88.6776 | 94.9886 | 101.3031
| StirlingWind2040RCP8.5 | Stirling | Wind | RCP8.5 | 2040 | 76.3107 | 82.271 | 88.5632 | 94.838 | 101.1159
| StirlingWind2045RCP8.5 | Stirling | Wind | RCP8.5 | 2045 | 76.2701 | 82.1946 | 88.4488 | 94.6873 | 100.9286
| StirlingWind2050RCP8.5 | Stirling | Wind | RCP8.5 | 2050 | 76.184 | 82.0664 | 88.2728 | 94.4676 | 100.6678
| StirlingWind2055RCP8.5 | Stirling | Wind | RCP8.5 | 2055 | 76.1384 | 82.0146 | 88.2112 | 94.3985 | 100.5942
| StirlingWind2060RCP8.5 | Stirling | Wind | RCP8.5 | 2060 | 76.0802 | 81.9382 | 88.1085 | 94.273 | 100.4471
| StirlingWind2065RCP8.5 | Stirling | Wind | RCP8.5 | 2065 | 76.0675 | 81.9137 | 88.0675 | 94.2165 | 100.3735
| StirlingWind2070RCP8.5 | Stirling | Wind | RCP8.5 | 2070 | 76.0219 | 81.8455 | 87.9707 | 94.0941 | 100.223
| StirlingWind2075RCP8.5 | Stirling | Wind | RCP8.5 | 2075 | 75.989 | 81.8018 | 87.9149 | 94.0282 | 100.1461
| StirlingWind2080RCP8.5 | Stirling | Wind | RCP8.5 | 2080 | 75.9561 | 81.7582 | 87.8592 | 93.9623 | 100.0692
| StirlingWind2085RCP8.5 | Stirling | Wind | RCP8.5 | 2085 | 75.9143 | 81.7295 | 87.846 | 93.967 | 100.0842
| StirlingWind2090RCP8.5 | Stirling | Wind | RCP8.5 | 2090 | 75.8725 | 81.7009 | 87.8328 | 93.9717 | 100.0993
| StirlingWind2095RCP8.5 | Stirling | Wind | RCP8.5 | 2095 | 75.8725 | 81.7009 | 87.8328 | 93.9717 | 100.0993
| StirlingWind2100RCP8.5 | Stirling | Wind | RCP8.5 | 2100 | 75.8725 | 81.7009 | 87.8328 | 93.9717 | 100.0993
| StratfordIce Accretion2023RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425
| StratfordIce Accretion2025RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2025 | 17.1352 | 20.5563 | 24.8625 | 28.1605 | 31.4423
| StratfordIce Accretion2030RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2030 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542
| StratfordIce Accretion2035RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2035 | 17.17 | 20.6255 | 24.9875 | 28.3206 | 31.6418
| StratfordIce Accretion2040RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2040 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415
| StratfordIce Accretion2045RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2045 | 17.2048 | 20.6947 | 25.1125 | 28.4807 | 31.8412
| StratfordIce Accretion2050RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2050 | 17.1526 | 20.6794 | 25.145 | 28.5438 | 31.941
| StratfordIce Accretion2055RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2055 | 17.083 | 20.6296 | 25.115 | 28.5268 | 31.941
| StratfordIce Accretion2060RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2060 | 17.0134 | 20.5799 | 25.085 | 28.5099 | 31.941
| StratfordIce Accretion2065RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2065 | 16.9439 | 20.53 | 25.055 | 28.4929 | 31.941
| StratfordIce Accretion2070RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2070 | 16.8743 | 20.4802 | 25.025 | 28.476 | 31.941
| StratfordIce Accretion2075RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2075 | 16.8424 | 20.4664 | 25.0375 | 28.5042 | 31.9883
| StratfordIce Accretion2080RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2080 | 16.8105 | 20.4526 | 25.05 | 28.5325 | 32.0355
| StratfordIce Accretion2085RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2085 | 16.7786 | 20.4387 | 25.0625 | 28.5607 | 32.0827
| StratfordIce Accretion2090RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2090 | 16.7467 | 20.4249 | 25.075 | 28.589 | 32.13
| StratfordIce Accretion2095RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2095 | 16.7148 | 20.4111 | 25.0875 | 28.6172 | 32.1773
| StratfordIce Accretion2100RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.3972 | 25.1 | 28.6455 | 32.2245
| StratfordIce Accretion2023RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425
| StratfordIce Accretion2025RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2025 | 17.1352 | 20.5563 | 24.8625 | 28.1605 | 31.4423
| StratfordIce Accretion2030RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2030 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542
| StratfordIce Accretion2035RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2035 | 17.17 | 20.6255 | 24.9875 | 28.3206 | 31.6418
| StratfordIce Accretion2040RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2040 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415
| StratfordIce Accretion2045RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2045 | 17.2048 | 20.6947 | 25.1125 | 28.4807 | 31.8412
| StratfordIce Accretion2050RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2050 | 17.1526 | 20.6794 | 25.145 | 28.5438 | 31.941
| StratfordIce Accretion2055RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2055 | 17.083 | 20.6296 | 25.115 | 28.5268 | 31.941
| StratfordIce Accretion2060RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2060 | 17.0134 | 20.5799 | 25.085 | 28.5099 | 31.941
| StratfordIce Accretion2065RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2065 | 16.9439 | 20.53 | 25.055 | 28.4929 | 31.941
| StratfordIce Accretion2070RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2070 | 16.8743 | 20.4802 | 25.025 | 28.476 | 31.941
| StratfordIce Accretion2075RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2075 | 16.8264 | 20.4595 | 25.0437 | 28.5184 | 32.0119
| StratfordIce Accretion2080RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2080 | 16.7786 | 20.4387 | 25.0625 | 28.5607 | 32.0827
| StratfordIce Accretion2085RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2085 | 16.7308 | 20.418 | 25.0813 | 28.6031 | 32.1536
| StratfordIce Accretion2090RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2090 | 16.4742 | 20.1898 | 24.8833 | 28.4289 | 31.9935
| StratfordIce Accretion2095RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2095 | 16.2654 | 19.9822 | 24.6667 | 28.2123 | 31.7625
| StratfordIce Accretion2100RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2100 | 16.0566 | 19.7747 | 24.45 | 27.9957 | 31.5315
| StratfordIce Accretion2023RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425
| StratfordIce Accretion2025RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2025 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542
| StratfordIce Accretion2030RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2030 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415
| StratfordIce Accretion2035RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2035 | 17.2222 | 20.7293 | 25.175 | 28.5607 | 31.941
| StratfordIce Accretion2040RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2040 | 17.1062 | 20.6462 | 25.125 | 28.5325 | 31.941
| StratfordIce Accretion2045RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2045 | 16.9902 | 20.5633 | 25.075 | 28.5042 | 31.941
| StratfordIce Accretion2050RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2050 | 16.8105 | 20.4526 | 25.05 | 28.5325 | 32.0355
| StratfordIce Accretion2055RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2055 | 16.7467 | 20.4249 | 25.075 | 28.589 | 32.13
| StratfordIce Accretion2060RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2060 | 16.4742 | 20.1898 | 24.8833 | 28.4289 | 31.9935
| StratfordIce Accretion2065RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2065 | 16.2654 | 19.9822 | 24.6667 | 28.2123 | 31.7625
| StratfordIce Accretion2070RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2070 | 15.6797 | 19.3528 | 23.975 | 27.4778 | 30.9645
| StratfordIce Accretion2075RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2075 | 15.3028 | 18.9309 | 23.5 | 26.9599 | 30.3975
| StratfordIce Accretion2080RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2080 | 14.9259 | 18.509 | 23.025 | 26.442 | 29.8305
| StratfordIce Accretion2085RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2085 | 14.1431 | 17.5856 | 21.925 | 25.2131 | 28.476
| StratfordIce Accretion2090RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2090 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215
| StratfordIce Accretion2095RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2095 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215
| StratfordIce Accretion2100RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2100 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215
| StratfordWind2023RCP4.5 | Stratford | Wind | RCP4.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| StratfordWind2025RCP4.5 | Stratford | Wind | RCP4.5 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
| StratfordWind2030RCP4.5 | Stratford | Wind | RCP4.5 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| StratfordWind2035RCP4.5 | Stratford | Wind | RCP4.5 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
| StratfordWind2040RCP4.5 | Stratford | Wind | RCP4.5 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| StratfordWind2045RCP4.5 | Stratford | Wind | RCP4.5 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
| StratfordWind2050RCP4.5 | Stratford | Wind | RCP4.5 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
| StratfordWind2055RCP4.5 | Stratford | Wind | RCP4.5 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
| StratfordWind2060RCP4.5 | Stratford | Wind | RCP4.5 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
| StratfordWind2065RCP4.5 | Stratford | Wind | RCP4.5 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
| StratfordWind2070RCP4.5 | Stratford | Wind | RCP4.5 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
| StratfordWind2075RCP4.5 | Stratford | Wind | RCP4.5 | 2075 | 86.3504 | 93.3577 | 100.8387 | 108.226 | 115.6228
| StratfordWind2080RCP4.5 | Stratford | Wind | RCP4.5 | 2080 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
| StratfordWind2085RCP4.5 | Stratford | Wind | RCP4.5 | 2085 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
| StratfordWind2090RCP4.5 | Stratford | Wind | RCP4.5 | 2090 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
| StratfordWind2095RCP4.5 | Stratford | Wind | RCP4.5 | 2095 | 86.7678 | 93.9167 | 101.5705 | 109.1068 | 116.6655
| StratfordWind2100RCP4.5 | Stratford | Wind | RCP4.5 | 2100 | 86.8722 | 94.0565 | 101.7534 | 109.327 | 116.9262
| StratfordWind2023RCP6.0 | Stratford | Wind | RCP6.0 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| StratfordWind2025RCP6.0 | Stratford | Wind | RCP6.0 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
| StratfordWind2030RCP6.0 | Stratford | Wind | RCP6.0 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| StratfordWind2035RCP6.0 | Stratford | Wind | RCP6.0 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
| StratfordWind2040RCP6.0 | Stratford | Wind | RCP6.0 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| StratfordWind2045RCP6.0 | Stratford | Wind | RCP6.0 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
| StratfordWind2050RCP6.0 | Stratford | Wind | RCP6.0 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
| StratfordWind2055RCP6.0 | Stratford | Wind | RCP6.0 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
| StratfordWind2060RCP6.0 | Stratford | Wind | RCP6.0 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
| StratfordWind2065RCP6.0 | Stratford | Wind | RCP6.0 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
| StratfordWind2070RCP6.0 | Stratford | Wind | RCP6.0 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
| StratfordWind2075RCP6.0 | Stratford | Wind | RCP6.0 | 2075 | 86.4026 | 93.4276 | 100.9302 | 108.3361 | 115.7531
| StratfordWind2080RCP6.0 | Stratford | Wind | RCP6.0 | 2080 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
| StratfordWind2085RCP6.0 | Stratford | Wind | RCP6.0 | 2085 | 86.7157 | 93.8469 | 101.479 | 108.9967 | 116.5351
| StratfordWind2090RCP6.0 | Stratford | Wind | RCP6.0 | 2090 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
| StratfordWind2095RCP6.0 | Stratford | Wind | RCP6.0 | 2095 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
| StratfordWind2100RCP6.0 | Stratford | Wind | RCP6.0 | 2100 | 87.7861 | 95.1502 | 103.0568 | 110.8265 | 118.6131
| StratfordWind2023RCP8.5 | Stratford | Wind | RCP8.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| StratfordWind2025RCP8.5 | Stratford | Wind | RCP8.5 | 2025 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| StratfordWind2030RCP8.5 | Stratford | Wind | RCP8.5 | 2030 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| StratfordWind2035RCP8.5 | Stratford | Wind | RCP8.5 | 2035 | 86.0768 | 93.0084 | 100.3912 | 107.7017 | 115.0269
| StratfordWind2040RCP8.5 | Stratford | Wind | RCP8.5 | 2040 | 86.1332 | 93.0782 | 100.4794 | 107.8031 | 115.1386
| StratfordWind2045RCP8.5 | Stratford | Wind | RCP8.5 | 2045 | 86.1896 | 93.1481 | 100.5676 | 107.9044 | 115.2504
| StratfordWind2050RCP8.5 | Stratford | Wind | RCP8.5 | 2050 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
| StratfordWind2055RCP8.5 | Stratford | Wind | RCP8.5 | 2055 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
| StratfordWind2060RCP8.5 | Stratford | Wind | RCP8.5 | 2060 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
| StratfordWind2065RCP8.5 | Stratford | Wind | RCP8.5 | 2065 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
| StratfordWind2070RCP8.5 | Stratford | Wind | RCP8.5 | 2070 | 88.0541 | 95.5026 | 103.5207 | 111.3788 | 119.2611
| StratfordWind2075RCP8.5 | Stratford | Wind | RCP8.5 | 2075 | 88.322 | 95.855 | 103.9845 | 111.9311 | 119.9091
| StratfordWind2080RCP8.5 | Stratford | Wind | RCP8.5 | 2080 | 88.59 | 96.2074 | 104.4484 | 112.4833 | 120.5571
| StratfordWind2085RCP8.5 | Stratford | Wind | RCP8.5 | 2085 | 88.9454 | 96.6585 | 105.0217 | 113.1649 | 121.3447
| StratfordWind2090RCP8.5 | Stratford | Wind | RCP8.5 | 2090 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| StratfordWind2095RCP8.5 | Stratford | Wind | RCP8.5 | 2095 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| StratfordWind2100RCP8.5 | Stratford | Wind | RCP8.5 | 2100 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| StrathroyIce Accretion2023RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2023 | 16.7525 | 20.1067 | 24.35 | 27.572 | 30.807
| StrathroyIce Accretion2025RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2025 | 16.6858 | 20.041 | 24.2833 | 27.5061 | 30.7387
| StrathroyIce Accretion2030RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2030 | 16.6191 | 19.9753 | 24.2167 | 27.4402 | 30.6705
| StrathroyIce Accretion2035RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2035 | 16.5524 | 19.9096 | 24.15 | 27.3742 | 30.6022
| StrathroyIce Accretion2040RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2040 | 16.4858 | 19.8439 | 24.0833 | 27.3083 | 30.534
| StrathroyIce Accretion2045RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2045 | 16.4191 | 19.7782 | 24.0167 | 27.2424 | 30.4657
| StrathroyIce Accretion2050RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2050 | 16.0462 | 19.3722 | 23.56 | 26.7527 | 29.9376
| StrathroyIce Accretion2055RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2055 | 15.74 | 19.0319 | 23.17 | 26.329 | 29.4777
| StrathroyIce Accretion2060RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2060 | 15.4339 | 18.6916 | 22.78 | 25.9052 | 29.0178
| StrathroyIce Accretion2065RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2065 | 15.1277 | 18.3513 | 22.39 | 25.4815 | 28.5579
| StrathroyIce Accretion2070RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2070 | 14.8215 | 18.011 | 22 | 25.0577 | 28.098
| StrathroyIce Accretion2075RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2075 | 14.6824 | 17.8657 | 21.85 | 24.8977 | 27.93
| StrathroyIce Accretion2080RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2080 | 14.5432 | 17.7205 | 21.7 | 24.7376 | 27.762
| StrathroyIce Accretion2085RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2085 | 14.404 | 17.5753 | 21.55 | 24.5775 | 27.594
| StrathroyIce Accretion2090RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2090 | 14.2648 | 17.43 | 21.4 | 24.4174 | 27.426
| StrathroyIce Accretion2095RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2095 | 14.1257 | 17.2848 | 21.25 | 24.2573 | 27.258
| StrathroyIce Accretion2100RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2100 | 13.9865 | 17.1395 | 21.1 | 24.0972 | 27.09
| StrathroyIce Accretion2023RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2023 | 16.7525 | 20.1067 | 24.35 | 27.572 | 30.807
| StrathroyIce Accretion2025RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2025 | 16.6858 | 20.041 | 24.2833 | 27.5061 | 30.7387
| StrathroyIce Accretion2030RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2030 | 16.6191 | 19.9753 | 24.2167 | 27.4402 | 30.6705
| StrathroyIce Accretion2035RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2035 | 16.5524 | 19.9096 | 24.15 | 27.3742 | 30.6022
| StrathroyIce Accretion2040RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2040 | 16.4858 | 19.8439 | 24.0833 | 27.3083 | 30.534
| StrathroyIce Accretion2045RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2045 | 16.4191 | 19.7782 | 24.0167 | 27.2424 | 30.4657
| StrathroyIce Accretion2050RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2050 | 16.0462 | 19.3722 | 23.56 | 26.7527 | 29.9376
| StrathroyIce Accretion2055RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2055 | 15.74 | 19.0319 | 23.17 | 26.329 | 29.4777
| StrathroyIce Accretion2060RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2060 | 15.4339 | 18.6916 | 22.78 | 25.9052 | 29.0178
| StrathroyIce Accretion2065RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2065 | 15.1277 | 18.3513 | 22.39 | 25.4815 | 28.5579
| StrathroyIce Accretion2070RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2070 | 14.8215 | 18.011 | 22 | 25.0577 | 28.098
| StrathroyIce Accretion2075RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2075 | 14.6128 | 17.7931 | 21.775 | 24.8176 | 27.846
| StrathroyIce Accretion2080RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2080 | 14.404 | 17.5753 | 21.55 | 24.5775 | 27.594
| StrathroyIce Accretion2085RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2085 | 14.1953 | 17.3574 | 21.325 | 24.3374 | 27.342
| StrathroyIce Accretion2090RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2090 | 13.5632 | 16.6623 | 20.55 | 23.4852 | 26.418
| StrathroyIce Accretion2095RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2095 | 13.1399 | 16.185 | 20 | 22.8731 | 25.746
| StrathroyIce Accretion2100RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2100 | 12.7166 | 15.7078 | 19.45 | 22.261 | 25.074
| StrathroyIce Accretion2023RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2023 | 16.7525 | 20.1067 | 24.35 | 27.572 | 30.807
| StrathroyIce Accretion2025RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2025 | 16.6191 | 19.9753 | 24.2167 | 27.4402 | 30.6705
| StrathroyIce Accretion2030RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2030 | 16.4858 | 19.8439 | 24.0833 | 27.3083 | 30.534
| StrathroyIce Accretion2035RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2035 | 16.3524 | 19.7125 | 23.95 | 27.1765 | 30.3975
| StrathroyIce Accretion2040RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2040 | 15.8421 | 19.1453 | 23.3 | 26.4702 | 29.631
| StrathroyIce Accretion2045RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2045 | 15.3318 | 18.5782 | 22.65 | 25.764 | 28.8645
| StrathroyIce Accretion2050RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2050 | 14.5432 | 17.7205 | 21.7 | 24.7376 | 27.762
| StrathroyIce Accretion2055RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2055 | 14.2648 | 17.43 | 21.4 | 24.4174 | 27.426
| StrathroyIce Accretion2060RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2060 | 13.5632 | 16.6623 | 20.55 | 23.4852 | 26.418
| StrathroyIce Accretion2065RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2065 | 13.1399 | 16.185 | 20 | 22.8731 | 25.746
| StrathroyIce Accretion2070RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2070 | 12.3861 | 15.3481 | 19.0417 | 21.8278 | 24.6015
| StrathroyIce Accretion2075RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2075 | 12.0555 | 14.9884 | 18.6333 | 21.3947 | 24.129
| StrathroyIce Accretion2080RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2080 | 11.725 | 14.6288 | 18.225 | 20.9615 | 23.6565
| StrathroyIce Accretion2085RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2085 | 10.9248 | 13.6743 | 17.0875 | 19.662 | 22.2233
| StrathroyIce Accretion2090RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2090 | 10.1246 | 12.7197 | 15.95 | 18.3625 | 20.79
| StrathroyIce Accretion2095RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2095 | 10.1246 | 12.7197 | 15.95 | 18.3625 | 20.79
| StrathroyIce Accretion2100RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2100 | 10.1246 | 12.7197 | 15.95 | 18.3625 | 20.79
| StrathroyWind2023RCP4.5 | Strathroy | Wind | RCP4.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
| StrathroyWind2025RCP4.5 | Strathroy | Wind | RCP4.5 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
| StrathroyWind2030RCP4.5 | Strathroy | Wind | RCP4.5 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
| StrathroyWind2035RCP4.5 | Strathroy | Wind | RCP4.5 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
| StrathroyWind2040RCP4.5 | Strathroy | Wind | RCP4.5 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
| StrathroyWind2045RCP4.5 | Strathroy | Wind | RCP4.5 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
| StrathroyWind2050RCP4.5 | Strathroy | Wind | RCP4.5 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
| StrathroyWind2055RCP4.5 | Strathroy | Wind | RCP4.5 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
| StrathroyWind2060RCP4.5 | Strathroy | Wind | RCP4.5 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
| StrathroyWind2065RCP4.5 | Strathroy | Wind | RCP4.5 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
| StrathroyWind2070RCP4.5 | Strathroy | Wind | RCP4.5 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
| StrathroyWind2075RCP4.5 | Strathroy | Wind | RCP4.5 | 2075 | 85.7411 | 92.542 | 99.746 | 106.9048 | 114.0736
| StrathroyWind2080RCP4.5 | Strathroy | Wind | RCP4.5 | 2080 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
| StrathroyWind2085RCP4.5 | Strathroy | Wind | RCP4.5 | 2085 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
| StrathroyWind2090RCP4.5 | Strathroy | Wind | RCP4.5 | 2090 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
| StrathroyWind2095RCP4.5 | Strathroy | Wind | RCP4.5 | 2095 | 86.3278 | 93.3015 | 100.7326 | 108.0792 | 115.444
| StrathroyWind2100RCP4.5 | Strathroy | Wind | RCP4.5 | 2100 | 86.4745 | 93.4914 | 100.9792 | 108.3728 | 115.7866
| StrathroyWind2023RCP6.0 | Strathroy | Wind | RCP6.0 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
| StrathroyWind2025RCP6.0 | Strathroy | Wind | RCP6.0 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
| StrathroyWind2030RCP6.0 | Strathroy | Wind | RCP6.0 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
| StrathroyWind2035RCP6.0 | Strathroy | Wind | RCP6.0 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
| StrathroyWind2040RCP6.0 | Strathroy | Wind | RCP6.0 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
| StrathroyWind2045RCP6.0 | Strathroy | Wind | RCP6.0 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
| StrathroyWind2050RCP6.0 | Strathroy | Wind | RCP6.0 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
| StrathroyWind2055RCP6.0 | Strathroy | Wind | RCP6.0 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
| StrathroyWind2060RCP6.0 | Strathroy | Wind | RCP6.0 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
| StrathroyWind2065RCP6.0 | Strathroy | Wind | RCP6.0 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
| StrathroyWind2070RCP6.0 | Strathroy | Wind | RCP6.0 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
| StrathroyWind2075RCP6.0 | Strathroy | Wind | RCP6.0 | 2075 | 85.8144 | 92.637 | 99.8693 | 107.0516 | 114.2449
| StrathroyWind2080RCP6.0 | Strathroy | Wind | RCP6.0 | 2080 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
| StrathroyWind2085RCP6.0 | Strathroy | Wind | RCP6.0 | 2085 | 86.2545 | 93.2066 | 100.6093 | 107.9324 | 115.2727
| StrathroyWind2090RCP6.0 | Strathroy | Wind | RCP6.0 | 2090 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
| StrathroyWind2095RCP6.0 | Strathroy | Wind | RCP6.0 | 2095 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
| StrathroyWind2100RCP6.0 | Strathroy | Wind | RCP6.0 | 2100 | 87.5746 | 94.8494 | 102.6452 | 110.3127 | 117.9987
| StrathroyWind2023RCP8.5 | Strathroy | Wind | RCP8.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
| StrathroyWind2025RCP8.5 | Strathroy | Wind | RCP8.5 | 2025 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
| StrathroyWind2030RCP8.5 | Strathroy | Wind | RCP8.5 | 2030 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
| StrathroyWind2035RCP8.5 | Strathroy | Wind | RCP8.5 | 2035 | 85.586 | 92.3248 | 99.4504 | 106.5378 | 113.6304
| StrathroyWind2040RCP8.5 | Strathroy | Wind | RCP8.5 | 2040 | 85.5888 | 92.3339 | 99.4667 | 106.5622 | 113.6639
| StrathroyWind2045RCP8.5 | Strathroy | Wind | RCP8.5 | 2045 | 85.5916 | 92.343 | 99.4831 | 106.5867 | 113.6974
| StrathroyWind2050RCP8.5 | Strathroy | Wind | RCP8.5 | 2050 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
| StrathroyWind2055RCP8.5 | Strathroy | Wind | RCP8.5 | 2055 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
| StrathroyWind2060RCP8.5 | Strathroy | Wind | RCP8.5 | 2060 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
| StrathroyWind2065RCP8.5 | Strathroy | Wind | RCP8.5 | 2065 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
| StrathroyWind2070RCP8.5 | Strathroy | Wind | RCP8.5 | 2070 | 87.882 | 95.2383 | 103.1385 | 110.8929 | 118.669
| StrathroyWind2075RCP8.5 | Strathroy | Wind | RCP8.5 | 2075 | 88.1895 | 95.6271 | 103.6317 | 111.4732 | 119.3393
| StrathroyWind2080RCP8.5 | Strathroy | Wind | RCP8.5 | 2080 | 88.4969 | 96.016 | 104.125 | 112.0534 | 120.0096
| StrathroyWind2085RCP8.5 | Strathroy | Wind | RCP8.5 | 2085 | 88.8396 | 96.4489 | 104.664 | 112.6826 | 120.7358
| StrathroyWind2090RCP8.5 | Strathroy | Wind | RCP8.5 | 2090 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
| StrathroyWind2095RCP8.5 | Strathroy | Wind | RCP8.5 | 2095 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
| StrathroyWind2100RCP8.5 | Strathroy | Wind | RCP8.5 | 2100 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
| Sturgeon FallsIce Accretion2023RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2023 | 16.4046 | 19.6054 | 23.667 | 26.7437 | 29.8494
| Sturgeon FallsIce Accretion2025RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2025 | 16.5086 | 19.7359 | 23.8357 | 26.943 | 30.0716
| Sturgeon FallsIce Accretion2030RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2030 | 16.6126 | 19.8663 | 24.0043 | 27.1422 | 30.2938
| Sturgeon FallsIce Accretion2035RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2035 | 16.7167 | 19.9968 | 24.173 | 27.3415 | 30.5159
| Sturgeon FallsIce Accretion2040RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2040 | 16.8207 | 20.1272 | 24.3417 | 27.5407 | 30.7381
| Sturgeon FallsIce Accretion2045RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2045 | 16.9247 | 20.2577 | 24.5103 | 27.74 | 30.9603
| Sturgeon FallsIce Accretion2050RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2050 | 17.16 | 20.5752 | 24.932 | 28.2407 | 31.5418
| Sturgeon FallsIce Accretion2055RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2055 | 17.2912 | 20.7623 | 25.185 | 28.5422 | 31.9012
| Sturgeon FallsIce Accretion2060RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2060 | 17.4225 | 20.9494 | 25.438 | 28.8437 | 32.2605
| Sturgeon FallsIce Accretion2065RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2065 | 17.5537 | 21.1364 | 25.691 | 29.1452 | 32.6199
| Sturgeon FallsIce Accretion2070RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2070 | 17.6849 | 21.3235 | 25.944 | 29.4467 | 32.9792
| Sturgeon FallsIce Accretion2075RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2075 | 17.6209 | 21.2599 | 25.8827 | 29.386 | 32.9164
| Sturgeon FallsIce Accretion2080RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2080 | 17.5569 | 21.1963 | 25.8213 | 29.3254 | 32.8537
| Sturgeon FallsIce Accretion2085RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2085 | 17.4929 | 21.1326 | 25.76 | 29.2647 | 32.7909
| Sturgeon FallsIce Accretion2090RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2090 | 17.4289 | 21.069 | 25.6987 | 29.2041 | 32.7281
| Sturgeon FallsIce Accretion2095RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2095 | 17.3648 | 21.0054 | 25.6373 | 29.1435 | 32.6653
| Sturgeon FallsIce Accretion2100RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2100 | 17.3008 | 20.9417 | 25.576 | 29.0828 | 32.6025
| Sturgeon FallsIce Accretion2023RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2023 | 16.4046 | 19.6054 | 23.667 | 26.7437 | 29.8494
| Sturgeon FallsIce Accretion2025RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2025 | 16.5086 | 19.7359 | 23.8357 | 26.943 | 30.0716
| Sturgeon FallsIce Accretion2030RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2030 | 16.6126 | 19.8663 | 24.0043 | 27.1422 | 30.2938
| Sturgeon FallsIce Accretion2035RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2035 | 16.7167 | 19.9968 | 24.173 | 27.3415 | 30.5159
| Sturgeon FallsIce Accretion2040RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2040 | 16.8207 | 20.1272 | 24.3417 | 27.5407 | 30.7381
| Sturgeon FallsIce Accretion2045RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2045 | 16.9247 | 20.2577 | 24.5103 | 27.74 | 30.9603
| Sturgeon FallsIce Accretion2050RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2050 | 17.16 | 20.5752 | 24.932 | 28.2407 | 31.5418
| Sturgeon FallsIce Accretion2055RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2055 | 17.2912 | 20.7623 | 25.185 | 28.5422 | 31.9012
| Sturgeon FallsIce Accretion2060RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2060 | 17.4225 | 20.9494 | 25.438 | 28.8437 | 32.2605
| Sturgeon FallsIce Accretion2065RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2065 | 17.5537 | 21.1364 | 25.691 | 29.1452 | 32.6199
| Sturgeon FallsIce Accretion2070RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2070 | 17.6849 | 21.3235 | 25.944 | 29.4467 | 32.9792
| Sturgeon FallsIce Accretion2075RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2075 | 17.5889 | 21.2281 | 25.852 | 29.3557 | 32.8851
| Sturgeon FallsIce Accretion2080RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2080 | 17.4929 | 21.1326 | 25.76 | 29.2647 | 32.7909
| Sturgeon FallsIce Accretion2085RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2085 | 17.3968 | 21.0372 | 25.668 | 29.1738 | 32.6967
| Sturgeon FallsIce Accretion2090RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2090 | 17.2795 | 20.9354 | 25.5837 | 29.1088 | 32.6411
| Sturgeon FallsIce Accretion2095RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2095 | 17.2581 | 20.929 | 25.5913 | 29.1348 | 32.6798
| Sturgeon FallsIce Accretion2100RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2100 | 17.2368 | 20.9226 | 25.599 | 29.1608 | 32.7184
| Sturgeon FallsIce Accretion2023RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2023 | 16.4046 | 19.6054 | 23.667 | 26.7437 | 29.8494
| Sturgeon FallsIce Accretion2025RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2025 | 16.6126 | 19.8663 | 24.0043 | 27.1422 | 30.2938
| Sturgeon FallsIce Accretion2030RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2030 | 16.8207 | 20.1272 | 24.3417 | 27.5407 | 30.7381
| Sturgeon FallsIce Accretion2035RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2035 | 17.0287 | 20.3881 | 24.679 | 27.9392 | 31.1825
| Sturgeon FallsIce Accretion2040RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2040 | 17.2475 | 20.6999 | 25.1007 | 28.4417 | 31.7814
| Sturgeon FallsIce Accretion2045RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2045 | 17.4662 | 21.0117 | 25.5223 | 28.9442 | 32.3803
| Sturgeon FallsIce Accretion2050RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2050 | 17.5569 | 21.1963 | 25.8213 | 29.3254 | 32.8537
| Sturgeon FallsIce Accretion2055RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2055 | 17.4289 | 21.069 | 25.6987 | 29.2041 | 32.7281
| Sturgeon FallsIce Accretion2060RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2060 | 17.2795 | 20.9354 | 25.5837 | 29.1088 | 32.6411
| Sturgeon FallsIce Accretion2065RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2065 | 17.2581 | 20.929 | 25.5913 | 29.1348 | 32.6798
| Sturgeon FallsIce Accretion2070RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2070 | 16.7993 | 20.4072 | 24.9703 | 28.4504 | 31.9263
| Sturgeon FallsIce Accretion2075RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2075 | 16.3619 | 19.8918 | 24.3417 | 27.74 | 31.1342
| Sturgeon FallsIce Accretion2080RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2080 | 15.9244 | 19.3763 | 23.713 | 27.0296 | 30.3421
| Sturgeon FallsIce Accretion2085RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2085 | 15.6764 | 19.1186 | 23.46 | 26.7567 | 30.0667
| Sturgeon FallsIce Accretion2090RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2090 | 15.4283 | 18.8609 | 23.207 | 26.4838 | 29.7914
| Sturgeon FallsIce Accretion2095RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2095 | 15.4283 | 18.8609 | 23.207 | 26.4838 | 29.7914
| Sturgeon FallsIce Accretion2100RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2100 | 15.4283 | 18.8609 | 23.207 | 26.4838 | 29.7914
| Sturgeon FallsWind2023RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2023 | 76.6095 | 82.4947 | 88.6864 | 94.885 | 101.0824
| Sturgeon FallsWind2025RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2025 | 76.6349 | 82.522 | 88.7143 | 94.9148 | 101.1125
| Sturgeon FallsWind2030RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2030 | 76.6602 | 82.5493 | 88.7421 | 94.9447 | 101.1426
| Sturgeon FallsWind2035RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2035 | 76.6855 | 82.5766 | 88.77 | 94.9745 | 101.1727
| Sturgeon FallsWind2040RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2040 | 76.7109 | 82.6038 | 88.7979 | 95.0043 | 101.2028
| Sturgeon FallsWind2045RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2045 | 76.7362 | 82.6311 | 88.8257 | 95.0341 | 101.2329
| Sturgeon FallsWind2050RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2050 | 76.7007 | 82.5749 | 88.7427 | 94.9302 | 101.1065
| Sturgeon FallsWind2055RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2055 | 76.6399 | 82.4914 | 88.6318 | 94.7965 | 100.95
| Sturgeon FallsWind2060RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2060 | 76.5791 | 82.408 | 88.521 | 94.6628 | 100.7935
| Sturgeon FallsWind2065RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2065 | 76.5184 | 82.3245 | 88.4101 | 94.5291 | 100.637
| Sturgeon FallsWind2070RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2070 | 76.4576 | 82.241 | 88.2992 | 94.3954 | 100.4805
| Sturgeon FallsWind2075RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2075 | 76.5222 | 82.3242 | 88.4048 | 94.5194 | 100.6243
| Sturgeon FallsWind2080RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2080 | 76.5867 | 82.4074 | 88.5104 | 94.6434 | 100.7681
| Sturgeon FallsWind2085RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2085 | 76.6513 | 82.4906 | 88.616 | 94.7673 | 100.9119
| Sturgeon FallsWind2090RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2090 | 76.7159 | 82.5738 | 88.7216 | 94.8913 | 101.0557
| Sturgeon FallsWind2095RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2095 | 76.7805 | 82.657 | 88.8272 | 95.0153 | 101.1995
| Sturgeon FallsWind2100RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2100 | 76.8451 | 82.7402 | 88.9328 | 95.1393 | 101.3433
| Sturgeon FallsWind2023RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2023 | 76.6095 | 82.4947 | 88.6864 | 94.885 | 101.0824
| Sturgeon FallsWind2025RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2025 | 76.6349 | 82.522 | 88.7143 | 94.9148 | 101.1125
| Sturgeon FallsWind2030RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2030 | 76.6602 | 82.5493 | 88.7421 | 94.9447 | 101.1426
| Sturgeon FallsWind2035RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2035 | 76.6855 | 82.5766 | 88.77 | 94.9745 | 101.1727
| Sturgeon FallsWind2040RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2040 | 76.7109 | 82.6038 | 88.7979 | 95.0043 | 101.2028
| Sturgeon FallsWind2045RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2045 | 76.7362 | 82.6311 | 88.8257 | 95.0341 | 101.2329
| Sturgeon FallsWind2050RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2050 | 76.7007 | 82.5749 | 88.7427 | 94.9302 | 101.1065
| Sturgeon FallsWind2055RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2055 | 76.6399 | 82.4914 | 88.6318 | 94.7965 | 100.95
| Sturgeon FallsWind2060RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2060 | 76.5791 | 82.408 | 88.521 | 94.6628 | 100.7935
| Sturgeon FallsWind2065RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2065 | 76.5184 | 82.3245 | 88.4101 | 94.5291 | 100.637
| Sturgeon FallsWind2070RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2070 | 76.4576 | 82.241 | 88.2992 | 94.3954 | 100.4805
| Sturgeon FallsWind2075RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2075 | 76.5545 | 82.3658 | 88.4576 | 94.5814 | 100.6962
| Sturgeon FallsWind2080RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2080 | 76.6513 | 82.4906 | 88.616 | 94.7673 | 100.9119
| Sturgeon FallsWind2085RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2085 | 76.7482 | 82.6154 | 88.7744 | 94.9533 | 101.1276
| Sturgeon FallsWind2090RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2090 | 76.8426 | 82.7348 | 88.924 | 95.1267 | 101.3265
| Sturgeon FallsWind2095RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2095 | 76.84 | 82.7293 | 88.9152 | 95.1142 | 101.3098
| Sturgeon FallsWind2100RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2100 | 76.8375 | 82.7239 | 88.9064 | 95.1016 | 101.2931
| Sturgeon FallsWind2023RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2023 | 76.6095 | 82.4947 | 88.6864 | 94.885 | 101.0824
| Sturgeon FallsWind2025RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2025 | 76.6602 | 82.5493 | 88.7421 | 94.9447 | 101.1426
| Sturgeon FallsWind2030RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2030 | 76.7109 | 82.6038 | 88.7979 | 95.0043 | 101.2028
| Sturgeon FallsWind2035RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2035 | 76.7615 | 82.6584 | 88.8536 | 95.0639 | 101.263
| Sturgeon FallsWind2040RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2040 | 76.6602 | 82.5193 | 88.6688 | 94.8411 | 101.0022
| Sturgeon FallsWind2045RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2045 | 76.5589 | 82.3801 | 88.484 | 94.6182 | 100.7413
| Sturgeon FallsWind2050RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2050 | 76.5867 | 82.4074 | 88.5104 | 94.6434 | 100.7681
| Sturgeon FallsWind2055RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2055 | 76.7159 | 82.5738 | 88.7216 | 94.8913 | 101.0557
| Sturgeon FallsWind2060RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2060 | 76.8426 | 82.7348 | 88.924 | 95.1267 | 101.3265
| Sturgeon FallsWind2065RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2065 | 76.84 | 82.7293 | 88.9152 | 95.1142 | 101.3098
| Sturgeon FallsWind2070RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2070 | 77.1288 | 83.0949 | 89.3787 | 95.654 | 101.9318
| Sturgeon FallsWind2075RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2075 | 77.4201 | 83.4659 | 89.8509 | 96.2064 | 102.5705
| Sturgeon FallsWind2080RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2080 | 77.7113 | 83.8369 | 90.3232 | 96.7588 | 103.2092
| Sturgeon FallsWind2085RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2085 | 77.9811 | 84.1274 | 90.6312 | 97.0931 | 103.5603
| Sturgeon FallsWind2090RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2090 | 78.2508 | 84.418 | 90.9392 | 97.4274 | 103.9115
| Sturgeon FallsWind2095RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2095 | 78.2508 | 84.418 | 90.9392 | 97.4274 | 103.9115
| Sturgeon FallsWind2100RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2100 | 78.2508 | 84.418 | 90.9392 | 97.4274 | 103.9115
| SudburyIce Accretion2023RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2023 | 16.0587 | 19.1913 | 23.166 | 26.2024 | 29.2446
| SudburyIce Accretion2025RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2025 | 16.1353 | 19.2826 | 23.2797 | 26.3309 | 29.3878
| SudburyIce Accretion2030RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2030 | 16.2118 | 19.3739 | 23.3933 | 26.4593 | 29.531
| SudburyIce Accretion2035RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2035 | 16.2884 | 19.4652 | 23.507 | 26.5878 | 29.6743
| SudburyIce Accretion2040RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2040 | 16.3649 | 19.5565 | 23.6207 | 26.7162 | 29.8175
| SudburyIce Accretion2045RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2045 | 16.4415 | 19.6478 | 23.7343 | 26.8447 | 29.9607
| SudburyIce Accretion2050RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2050 | 16.5945 | 19.845 | 23.9888 | 27.1421 | 30.298
| SudburyIce Accretion2055RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2055 | 16.6711 | 19.9509 | 24.1296 | 27.3112 | 30.492
| SudburyIce Accretion2060RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2060 | 16.7476 | 20.0568 | 24.2704 | 27.4802 | 30.686
| SudburyIce Accretion2065RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2065 | 16.8242 | 20.1627 | 24.4112 | 27.6493 | 30.8801
| SudburyIce Accretion2070RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2070 | 16.9007 | 20.2686 | 24.552 | 27.8183 | 31.0741
| SudburyIce Accretion2075RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2075 | 16.814 | 20.1773 | 24.4493 | 27.7106 | 30.9586
| SudburyIce Accretion2080RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2080 | 16.7272 | 20.086 | 24.3467 | 27.6029 | 30.8431
| SudburyIce Accretion2085RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2085 | 16.6405 | 19.9947 | 24.244 | 27.4952 | 30.7276
| SudburyIce Accretion2090RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2090 | 16.5537 | 19.9034 | 24.1413 | 27.3874 | 30.6121
| SudburyIce Accretion2095RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2095 | 16.467 | 19.8121 | 24.0387 | 27.2797 | 30.4966
| SudburyIce Accretion2100RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2100 | 16.3802 | 19.7208 | 23.936 | 27.172 | 30.3811
| SudburyIce Accretion2023RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2023 | 16.0587 | 19.1913 | 23.166 | 26.2024 | 29.2446
| SudburyIce Accretion2025RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2025 | 16.1353 | 19.2826 | 23.2797 | 26.3309 | 29.3878
| SudburyIce Accretion2030RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2030 | 16.2118 | 19.3739 | 23.3933 | 26.4593 | 29.531
| SudburyIce Accretion2035RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2035 | 16.2884 | 19.4652 | 23.507 | 26.5878 | 29.6743
| SudburyIce Accretion2040RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2040 | 16.3649 | 19.5565 | 23.6207 | 26.7162 | 29.8175
| SudburyIce Accretion2045RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2045 | 16.4415 | 19.6478 | 23.7343 | 26.8447 | 29.9607
| SudburyIce Accretion2050RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2050 | 16.5945 | 19.845 | 23.9888 | 27.1421 | 30.298
| SudburyIce Accretion2055RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2055 | 16.6711 | 19.9509 | 24.1296 | 27.3112 | 30.492
| SudburyIce Accretion2060RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2060 | 16.7476 | 20.0568 | 24.2704 | 27.4802 | 30.686
| SudburyIce Accretion2065RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2065 | 16.8242 | 20.1627 | 24.4112 | 27.6493 | 30.8801
| SudburyIce Accretion2070RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2070 | 16.9007 | 20.2686 | 24.552 | 27.8183 | 31.0741
| SudburyIce Accretion2075RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2075 | 16.7706 | 20.1317 | 24.398 | 27.6567 | 30.9009
| SudburyIce Accretion2080RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2080 | 16.6405 | 19.9947 | 24.244 | 27.4952 | 30.7276
| SudburyIce Accretion2085RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2085 | 16.5103 | 19.8577 | 24.09 | 27.3336 | 30.5544
| SudburyIce Accretion2090RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2090 | 16.3853 | 19.7512 | 24.0093 | 27.2631 | 30.5012
| SudburyIce Accretion2095RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2095 | 16.3904 | 19.7817 | 24.0827 | 27.3543 | 30.6214
| SudburyIce Accretion2100RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2100 | 16.3955 | 19.8121 | 24.156 | 27.4454 | 30.7415
| SudburyIce Accretion2023RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2023 | 16.0587 | 19.1913 | 23.166 | 26.2024 | 29.2446
| SudburyIce Accretion2025RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2025 | 16.2118 | 19.3739 | 23.3933 | 26.4593 | 29.531
| SudburyIce Accretion2030RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2030 | 16.3649 | 19.5565 | 23.6207 | 26.7162 | 29.8175
| SudburyIce Accretion2035RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2035 | 16.518 | 19.7391 | 23.848 | 26.9731 | 30.1039
| SudburyIce Accretion2040RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2040 | 16.6456 | 19.9156 | 24.0827 | 27.2548 | 30.4273
| SudburyIce Accretion2045RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2045 | 16.7731 | 20.0921 | 24.3173 | 27.5366 | 30.7507
| SudburyIce Accretion2050RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2050 | 16.7272 | 20.086 | 24.3467 | 27.6029 | 30.8431
| SudburyIce Accretion2055RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2055 | 16.5537 | 19.9034 | 24.1413 | 27.3874 | 30.6121
| SudburyIce Accretion2060RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2060 | 16.3853 | 19.7512 | 24.0093 | 27.2631 | 30.5012
| SudburyIce Accretion2065RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2065 | 16.3904 | 19.7817 | 24.0827 | 27.3543 | 30.6214
| SudburyIce Accretion2070RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2070 | 16.0996 | 19.4895 | 23.782 | 27.0394 | 30.298
| SudburyIce Accretion2075RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2075 | 15.8036 | 19.1669 | 23.408 | 26.6333 | 29.8544
| SudburyIce Accretion2080RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2080 | 15.5076 | 18.8443 | 23.034 | 26.2273 | 29.4109
| SudburyIce Accretion2085RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2085 | 15.4464 | 18.8169 | 23.067 | 26.2895 | 29.5079
| SudburyIce Accretion2090RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2090 | 15.3852 | 18.7895 | 23.1 | 26.3516 | 29.605
| SudburyIce Accretion2095RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2095 | 15.3852 | 18.7895 | 23.1 | 26.3516 | 29.605
| SudburyIce Accretion2100RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2100 | 15.3852 | 18.7895 | 23.1 | 26.3516 | 29.605
| SudburyWind2023RCP4.5 | Sudbury | Wind | RCP4.5 | 2023 | 80.0521 | 86.2274 | 92.7268 | 99.2275 | 105.7295
| SudburyWind2025RCP4.5 | Sudbury | Wind | RCP4.5 | 2025 | 80.1593 | 86.35 | 92.8663 | 99.3817 | 105.8991
| SudburyWind2030RCP4.5 | Sudbury | Wind | RCP4.5 | 2030 | 80.2666 | 86.4726 | 93.0059 | 99.536 | 106.0686
| SudburyWind2035RCP4.5 | Sudbury | Wind | RCP4.5 | 2035 | 80.3738 | 86.5953 | 93.1454 | 99.6902 | 106.2382
| SudburyWind2040RCP4.5 | Sudbury | Wind | RCP4.5 | 2040 | 80.4811 | 86.7179 | 93.2849 | 99.8444 | 106.4078
| SudburyWind2045RCP4.5 | Sudbury | Wind | RCP4.5 | 2045 | 80.5883 | 86.8405 | 93.4245 | 99.9986 | 106.5773
| SudburyWind2050RCP4.5 | Sudbury | Wind | RCP4.5 | 2050 | 80.7384 | 87.0008 | 93.5953 | 100.1785 | 106.7678
| SudburyWind2055RCP4.5 | Sudbury | Wind | RCP4.5 | 2055 | 80.7813 | 87.0385 | 93.6266 | 100.204 | 106.7888
| SudburyWind2060RCP4.5 | Sudbury | Wind | RCP4.5 | 2060 | 80.8242 | 87.0761 | 93.6578 | 100.2296 | 106.8098
| SudburyWind2065RCP4.5 | Sudbury | Wind | RCP4.5 | 2065 | 80.8671 | 87.1138 | 93.6891 | 100.2552 | 106.8308
| SudburyWind2070RCP4.5 | Sudbury | Wind | RCP4.5 | 2070 | 80.91 | 87.1514 | 93.7204 | 100.2808 | 106.8517
| SudburyWind2075RCP4.5 | Sudbury | Wind | RCP4.5 | 2075 | 80.9948 | 87.2598 | 93.8584 | 100.4465 | 107.0423
| SudburyWind2080RCP4.5 | Sudbury | Wind | RCP4.5 | 2080 | 81.0795 | 87.3682 | 93.9964 | 100.6122 | 107.2328
| SudburyWind2085RCP4.5 | Sudbury | Wind | RCP4.5 | 2085 | 81.1642 | 87.4765 | 94.1344 | 100.778 | 107.4233
| SudburyWind2090RCP4.5 | Sudbury | Wind | RCP4.5 | 2090 | 81.249 | 87.5849 | 94.2724 | 100.9437 | 107.6139
| SudburyWind2095RCP4.5 | Sudbury | Wind | RCP4.5 | 2095 | 81.3337 | 87.6933 | 94.4104 | 101.1094 | 107.8044
| SudburyWind2100RCP4.5 | Sudbury | Wind | RCP4.5 | 2100 | 81.4184 | 87.8017 | 94.5484 | 101.2751 | 107.9949
| SudburyWind2023RCP6.0 | Sudbury | Wind | RCP6.0 | 2023 | 80.0521 | 86.2274 | 92.7268 | 99.2275 | 105.7295
| SudburyWind2025RCP6.0 | Sudbury | Wind | RCP6.0 | 2025 | 80.1593 | 86.35 | 92.8663 | 99.3817 | 105.8991
| SudburyWind2030RCP6.0 | Sudbury | Wind | RCP6.0 | 2030 | 80.2666 | 86.4726 | 93.0059 | 99.536 | 106.0686
| SudburyWind2035RCP6.0 | Sudbury | Wind | RCP6.0 | 2035 | 80.3738 | 86.5953 | 93.1454 | 99.6902 | 106.2382
| SudburyWind2040RCP6.0 | Sudbury | Wind | RCP6.0 | 2040 | 80.4811 | 86.7179 | 93.2849 | 99.8444 | 106.4078
| SudburyWind2045RCP6.0 | Sudbury | Wind | RCP6.0 | 2045 | 80.5883 | 86.8405 | 93.4245 | 99.9986 | 106.5773
| SudburyWind2050RCP6.0 | Sudbury | Wind | RCP6.0 | 2050 | 80.7384 | 87.0008 | 93.5953 | 100.1785 | 106.7678
| SudburyWind2055RCP6.0 | Sudbury | Wind | RCP6.0 | 2055 | 80.7813 | 87.0385 | 93.6266 | 100.204 | 106.7888
| SudburyWind2060RCP6.0 | Sudbury | Wind | RCP6.0 | 2060 | 80.8242 | 87.0761 | 93.6578 | 100.2296 | 106.8098
| SudburyWind2065RCP6.0 | Sudbury | Wind | RCP6.0 | 2065 | 80.8671 | 87.1138 | 93.6891 | 100.2552 | 106.8308
| SudburyWind2070RCP6.0 | Sudbury | Wind | RCP6.0 | 2070 | 80.91 | 87.1514 | 93.7204 | 100.2808 | 106.8517
| SudburyWind2075RCP6.0 | Sudbury | Wind | RCP6.0 | 2075 | 81.0371 | 87.314 | 93.9274 | 100.5294 | 107.1375
| SudburyWind2080RCP6.0 | Sudbury | Wind | RCP6.0 | 2080 | 81.1642 | 87.4765 | 94.1344 | 100.778 | 107.4233
| SudburyWind2085RCP6.0 | Sudbury | Wind | RCP6.0 | 2085 | 81.2913 | 87.6391 | 94.3414 | 101.0265 | 107.7091
| SudburyWind2090RCP6.0 | Sudbury | Wind | RCP6.0 | 2090 | 81.7309 | 88.201 | 95.0544 | 101.869 | 108.6836
| SudburyWind2095RCP6.0 | Sudbury | Wind | RCP6.0 | 2095 | 82.0434 | 88.6002 | 95.5604 | 102.4629 | 109.3724
| SudburyWind2100RCP6.0 | Sudbury | Wind | RCP6.0 | 2100 | 82.3558 | 88.9995 | 96.0664 | 103.0568 | 110.0611
| SudburyWind2023RCP8.5 | Sudbury | Wind | RCP8.5 | 2023 | 80.0521 | 86.2274 | 92.7268 | 99.2275 | 105.7295
| SudburyWind2025RCP8.5 | Sudbury | Wind | RCP8.5 | 2025 | 80.2666 | 86.4726 | 93.0059 | 99.536 | 106.0686
| SudburyWind2030RCP8.5 | Sudbury | Wind | RCP8.5 | 2030 | 80.4811 | 86.7179 | 93.2849 | 99.8444 | 106.4078
| SudburyWind2035RCP8.5 | Sudbury | Wind | RCP8.5 | 2035 | 80.6955 | 86.9632 | 93.564 | 100.1529 | 106.7469
| SudburyWind2040RCP8.5 | Sudbury | Wind | RCP8.5 | 2040 | 80.767 | 87.0259 | 93.6161 | 100.1955 | 106.7818
| SudburyWind2045RCP8.5 | Sudbury | Wind | RCP8.5 | 2045 | 80.8385 | 87.0887 | 93.6683 | 100.2382 | 106.8168
| SudburyWind2050RCP8.5 | Sudbury | Wind | RCP8.5 | 2050 | 81.0795 | 87.3682 | 93.9964 | 100.6122 | 107.2328
| SudburyWind2055RCP8.5 | Sudbury | Wind | RCP8.5 | 2055 | 81.249 | 87.5849 | 94.2724 | 100.9437 | 107.6139
| SudburyWind2060RCP8.5 | Sudbury | Wind | RCP8.5 | 2060 | 81.7309 | 88.201 | 95.0544 | 101.869 | 108.6836
| SudburyWind2065RCP8.5 | Sudbury | Wind | RCP8.5 | 2065 | 82.0434 | 88.6002 | 95.5604 | 102.4629 | 109.3724
| SudburyWind2070RCP8.5 | Sudbury | Wind | RCP8.5 | 2070 | 82.5783 | 89.2762 | 96.4129 | 103.4604 | 110.519
| SudburyWind2075RCP8.5 | Sudbury | Wind | RCP8.5 | 2075 | 82.8007 | 89.5528 | 96.7595 | 103.864 | 110.977
| SudburyWind2080RCP8.5 | Sudbury | Wind | RCP8.5 | 2080 | 83.0231 | 89.8294 | 97.106 | 104.2676 | 111.435
| SudburyWind2085RCP8.5 | Sudbury | Wind | RCP8.5 | 2085 | 83.2535 | 90.1118 | 97.4464 | 104.6614 | 111.8912
| SudburyWind2090RCP8.5 | Sudbury | Wind | RCP8.5 | 2090 | 83.4839 | 90.3941 | 97.7868 | 105.0552 | 112.3475
| SudburyWind2095RCP8.5 | Sudbury | Wind | RCP8.5 | 2095 | 83.4839 | 90.3941 | 97.7868 | 105.0552 | 112.3475
| SudburyWind2100RCP8.5 | Sudbury | Wind | RCP8.5 | 2100 | 83.4839 | 90.3941 | 97.7868 | 105.0552 | 112.3475
| SundridgeIce Accretion2023RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2023 | 15.2321 | 18.1504 | 21.868 | 24.7108 | 27.526
| SundridgeIce Accretion2025RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2025 | 15.3086 | 18.2509 | 22 | 24.8641 | 27.7061
| SundridgeIce Accretion2030RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2030 | 15.3852 | 18.3513 | 22.132 | 25.0174 | 27.8863
| SundridgeIce Accretion2035RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2035 | 15.4617 | 18.4517 | 22.264 | 25.1707 | 28.0665
| SundridgeIce Accretion2040RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2040 | 15.5382 | 18.5522 | 22.396 | 25.3241 | 28.2467
| SundridgeIce Accretion2045RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2045 | 15.6148 | 18.6526 | 22.528 | 25.4774 | 28.4269
| SundridgeIce Accretion2050RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2050 | 15.7373 | 18.8261 | 22.7612 | 25.755 | 28.7512
| SundridgeIce Accretion2055RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2055 | 15.7832 | 18.8991 | 22.8624 | 25.8793 | 28.8953
| SundridgeIce Accretion2060RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2060 | 15.8291 | 18.9721 | 22.9636 | 26.0036 | 29.0395
| SundridgeIce Accretion2065RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2065 | 15.875 | 19.0452 | 23.0648 | 26.1279 | 29.1836
| SundridgeIce Accretion2070RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2070 | 15.921 | 19.1182 | 23.166 | 26.2522 | 29.3278
| SundridgeIce Accretion2075RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2075 | 15.9235 | 19.1395 | 23.21 | 26.3143 | 29.4109
| SundridgeIce Accretion2080RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2080 | 15.9261 | 19.1608 | 23.254 | 26.3765 | 29.4941
| SundridgeIce Accretion2085RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2085 | 15.9286 | 19.1821 | 23.298 | 26.4386 | 29.5772
| SundridgeIce Accretion2090RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2090 | 15.9312 | 19.2034 | 23.342 | 26.5008 | 29.6604
| SundridgeIce Accretion2095RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2095 | 15.9337 | 19.2247 | 23.386 | 26.5629 | 29.7436
| SundridgeIce Accretion2100RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2100 | 15.9363 | 19.246 | 23.43 | 26.6251 | 29.8267
| SundridgeIce Accretion2023RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2023 | 15.2321 | 18.1504 | 21.868 | 24.7108 | 27.526
| SundridgeIce Accretion2025RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2025 | 15.3086 | 18.2509 | 22 | 24.8641 | 27.7061
| SundridgeIce Accretion2030RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2030 | 15.3852 | 18.3513 | 22.132 | 25.0174 | 27.8863
| SundridgeIce Accretion2035RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2035 | 15.4617 | 18.4517 | 22.264 | 25.1707 | 28.0665
| SundridgeIce Accretion2040RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2040 | 15.5382 | 18.5522 | 22.396 | 25.3241 | 28.2467
| SundridgeIce Accretion2045RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2045 | 15.6148 | 18.6526 | 22.528 | 25.4774 | 28.4269
| SundridgeIce Accretion2050RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2050 | 15.7373 | 18.8261 | 22.7612 | 25.755 | 28.7512
| SundridgeIce Accretion2055RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2055 | 15.7832 | 18.8991 | 22.8624 | 25.8793 | 28.8953
| SundridgeIce Accretion2060RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2060 | 15.8291 | 18.9721 | 22.9636 | 26.0036 | 29.0395
| SundridgeIce Accretion2065RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2065 | 15.875 | 19.0452 | 23.0648 | 26.1279 | 29.1836
| SundridgeIce Accretion2070RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2070 | 15.921 | 19.1182 | 23.166 | 26.2522 | 29.3278
| SundridgeIce Accretion2075RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2075 | 15.9248 | 19.1502 | 23.232 | 26.3454 | 29.4525
| SundridgeIce Accretion2080RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2080 | 15.9286 | 19.1821 | 23.298 | 26.4386 | 29.5772
| SundridgeIce Accretion2085RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2085 | 15.9324 | 19.2141 | 23.364 | 26.5318 | 29.702
| SundridgeIce Accretion2090RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2090 | 15.9618 | 19.2947 | 23.5107 | 26.7328 | 29.9468
| SundridgeIce Accretion2095RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2095 | 15.9873 | 19.3434 | 23.5913 | 26.8405 | 30.067
| SundridgeIce Accretion2100RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2100 | 16.0128 | 19.3921 | 23.672 | 26.9482 | 30.1871
| SundridgeIce Accretion2023RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2023 | 15.2321 | 18.1504 | 21.868 | 24.7108 | 27.526
| SundridgeIce Accretion2025RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2025 | 15.3852 | 18.3513 | 22.132 | 25.0174 | 27.8863
| SundridgeIce Accretion2030RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2030 | 15.5382 | 18.5522 | 22.396 | 25.3241 | 28.2467
| SundridgeIce Accretion2035RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2035 | 15.6913 | 18.753 | 22.66 | 25.6307 | 28.607
| SundridgeIce Accretion2040RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2040 | 15.7679 | 18.8748 | 22.8287 | 25.8378 | 28.8473
| SundridgeIce Accretion2045RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2045 | 15.8444 | 18.9965 | 22.9973 | 26.045 | 29.0875
| SundridgeIce Accretion2050RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2050 | 15.9261 | 19.1608 | 23.254 | 26.3765 | 29.4941
| SundridgeIce Accretion2055RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2055 | 15.9312 | 19.2034 | 23.342 | 26.5008 | 29.6604
| SundridgeIce Accretion2060RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2060 | 15.9618 | 19.2947 | 23.5107 | 26.7328 | 29.9468
| SundridgeIce Accretion2065RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2065 | 15.9873 | 19.3434 | 23.5913 | 26.8405 | 30.067
| SundridgeIce Accretion2070RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2070 | 15.8801 | 19.2521 | 23.5253 | 26.7908 | 30.03
| SundridgeIce Accretion2075RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2075 | 15.7475 | 19.1121 | 23.3787 | 26.6333 | 29.8729
| SundridgeIce Accretion2080RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2080 | 15.6148 | 18.9721 | 23.232 | 26.4759 | 29.7158
| SundridgeIce Accretion2085RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2085 | 15.2091 | 18.5248 | 22.715 | 25.9166 | 29.106
| SundridgeIce Accretion2090RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2090 | 14.8034 | 18.0774 | 22.198 | 25.3572 | 28.4962
| SundridgeIce Accretion2095RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2095 | 14.8034 | 18.0774 | 22.198 | 25.3572 | 28.4962
| SundridgeIce Accretion2100RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2100 | 14.8034 | 18.0774 | 22.198 | 25.3572 | 28.4962
| SundridgeWind2023RCP4.5 | Sundridge | Wind | RCP4.5 | 2023 | 69.3273 | 74.6976 | 80.36 | 86.0109 | 91.6651
| SundridgeWind2025RCP4.5 | Sundridge | Wind | RCP4.5 | 2025 | 69.371 | 74.7559 | 80.436 | 86.1008 | 91.77
| SundridgeWind2030RCP4.5 | Sundridge | Wind | RCP4.5 | 2030 | 69.4148 | 74.8142 | 80.512 | 86.1906 | 91.8749
| SundridgeWind2035RCP4.5 | Sundridge | Wind | RCP4.5 | 2035 | 69.4585 | 74.8724 | 80.588 | 86.2805 | 91.9798
| SundridgeWind2040RCP4.5 | Sundridge | Wind | RCP4.5 | 2040 | 69.5023 | 74.9307 | 80.664 | 86.3704 | 92.0846
| SundridgeWind2045RCP4.5 | Sundridge | Wind | RCP4.5 | 2045 | 69.546 | 74.989 | 80.74 | 86.4603 | 92.1895
| SundridgeWind2050RCP4.5 | Sundridge | Wind | RCP4.5 | 2050 | 69.5842 | 75.0309 | 80.784 | 86.5091 | 92.2397
| SundridgeWind2055RCP4.5 | Sundridge | Wind | RCP4.5 | 2055 | 69.5787 | 75.0145 | 80.752 | 86.468 | 92.185
| SundridgeWind2060RCP4.5 | Sundridge | Wind | RCP4.5 | 2060 | 69.5732 | 74.9982 | 80.72 | 86.4269 | 92.1302
| SundridgeWind2065RCP4.5 | Sundridge | Wind | RCP4.5 | 2065 | 69.5677 | 74.9818 | 80.688 | 86.3858 | 92.0755
| SundridgeWind2070RCP4.5 | Sundridge | Wind | RCP4.5 | 2070 | 69.5621 | 74.9654 | 80.656 | 86.3447 | 92.0208
| SundridgeWind2075RCP4.5 | Sundridge | Wind | RCP4.5 | 2075 | 69.6347 | 75.0485 | 80.7533 | 86.4531 | 92.1424
| SundridgeWind2080RCP4.5 | Sundridge | Wind | RCP4.5 | 2080 | 69.7072 | 75.1316 | 80.8507 | 86.5616 | 92.264
| SundridgeWind2085RCP4.5 | Sundridge | Wind | RCP4.5 | 2085 | 69.7797 | 75.2147 | 80.948 | 86.67 | 92.3856
| SundridgeWind2090RCP4.5 | Sundridge | Wind | RCP4.5 | 2090 | 69.8523 | 75.2978 | 81.0453 | 86.7784 | 92.5072
| SundridgeWind2095RCP4.5 | Sundridge | Wind | RCP4.5 | 2095 | 69.9248 | 75.3808 | 81.1427 | 86.8869 | 92.6288
| SundridgeWind2100RCP4.5 | Sundridge | Wind | RCP4.5 | 2100 | 69.9973 | 75.4639 | 81.24 | 86.9953 | 92.7504
| SundridgeWind2023RCP6.0 | Sundridge | Wind | RCP6.0 | 2023 | 69.3273 | 74.6976 | 80.36 | 86.0109 | 91.6651
| SundridgeWind2025RCP6.0 | Sundridge | Wind | RCP6.0 | 2025 | 69.371 | 74.7559 | 80.436 | 86.1008 | 91.77
| SundridgeWind2030RCP6.0 | Sundridge | Wind | RCP6.0 | 2030 | 69.4148 | 74.8142 | 80.512 | 86.1906 | 91.8749
| SundridgeWind2035RCP6.0 | Sundridge | Wind | RCP6.0 | 2035 | 69.4585 | 74.8724 | 80.588 | 86.2805 | 91.9798
| SundridgeWind2040RCP6.0 | Sundridge | Wind | RCP6.0 | 2040 | 69.5023 | 74.9307 | 80.664 | 86.3704 | 92.0846
| SundridgeWind2045RCP6.0 | Sundridge | Wind | RCP6.0 | 2045 | 69.546 | 74.989 | 80.74 | 86.4603 | 92.1895
| SundridgeWind2050RCP6.0 | Sundridge | Wind | RCP6.0 | 2050 | 69.5842 | 75.0309 | 80.784 | 86.5091 | 92.2397
| SundridgeWind2055RCP6.0 | Sundridge | Wind | RCP6.0 | 2055 | 69.5787 | 75.0145 | 80.752 | 86.468 | 92.185
| SundridgeWind2060RCP6.0 | Sundridge | Wind | RCP6.0 | 2060 | 69.5732 | 74.9982 | 80.72 | 86.4269 | 92.1302
| SundridgeWind2065RCP6.0 | Sundridge | Wind | RCP6.0 | 2065 | 69.5677 | 74.9818 | 80.688 | 86.3858 | 92.0755
| SundridgeWind2070RCP6.0 | Sundridge | Wind | RCP6.0 | 2070 | 69.5621 | 74.9654 | 80.656 | 86.3447 | 92.0208
| SundridgeWind2075RCP6.0 | Sundridge | Wind | RCP6.0 | 2075 | 69.6709 | 75.0901 | 80.802 | 86.5074 | 92.2032
| SundridgeWind2080RCP6.0 | Sundridge | Wind | RCP6.0 | 2080 | 69.7797 | 75.2147 | 80.948 | 86.67 | 92.3856
| SundridgeWind2085RCP6.0 | Sundridge | Wind | RCP6.0 | 2085 | 69.8885 | 75.3393 | 81.094 | 86.8326 | 92.568
| SundridgeWind2090RCP6.0 | Sundridge | Wind | RCP6.0 | 2090 | 69.8638 | 75.2978 | 81.0293 | 86.7499 | 92.4677
| SundridgeWind2095RCP6.0 | Sundridge | Wind | RCP6.0 | 2095 | 69.7302 | 75.1316 | 80.8187 | 86.5045 | 92.185
| SundridgeWind2100RCP6.0 | Sundridge | Wind | RCP6.0 | 2100 | 69.5967 | 74.9654 | 80.608 | 86.2591 | 91.9022
| SundridgeWind2023RCP8.5 | Sundridge | Wind | RCP8.5 | 2023 | 69.3273 | 74.6976 | 80.36 | 86.0109 | 91.6651
| SundridgeWind2025RCP8.5 | Sundridge | Wind | RCP8.5 | 2025 | 69.4148 | 74.8142 | 80.512 | 86.1906 | 91.8749
| SundridgeWind2030RCP8.5 | Sundridge | Wind | RCP8.5 | 2030 | 69.5023 | 74.9307 | 80.664 | 86.3704 | 92.0846
| SundridgeWind2035RCP8.5 | Sundridge | Wind | RCP8.5 | 2035 | 69.5898 | 75.0473 | 80.816 | 86.5502 | 92.2944
| SundridgeWind2040RCP8.5 | Sundridge | Wind | RCP8.5 | 2040 | 69.5806 | 75.02 | 80.7627 | 86.4817 | 92.2032
| SundridgeWind2045RCP8.5 | Sundridge | Wind | RCP8.5 | 2045 | 69.5714 | 74.9927 | 80.7093 | 86.4132 | 92.112
| SundridgeWind2050RCP8.5 | Sundridge | Wind | RCP8.5 | 2050 | 69.7072 | 75.1316 | 80.8507 | 86.5616 | 92.264
| SundridgeWind2055RCP8.5 | Sundridge | Wind | RCP8.5 | 2055 | 69.8523 | 75.2978 | 81.0453 | 86.7784 | 92.5072
| SundridgeWind2060RCP8.5 | Sundridge | Wind | RCP8.5 | 2060 | 69.8638 | 75.2978 | 81.0293 | 86.7499 | 92.4677
| SundridgeWind2065RCP8.5 | Sundridge | Wind | RCP8.5 | 2065 | 69.7302 | 75.1316 | 80.8187 | 86.5045 | 92.185
| SundridgeWind2070RCP8.5 | Sundridge | Wind | RCP8.5 | 2070 | 69.7302 | 75.1266 | 80.808 | 86.4874 | 92.1637
| SundridgeWind2075RCP8.5 | Sundridge | Wind | RCP8.5 | 2075 | 69.8638 | 75.2878 | 81.008 | 86.7157 | 92.4251
| SundridgeWind2080RCP8.5 | Sundridge | Wind | RCP8.5 | 2080 | 69.9973 | 75.449 | 81.208 | 86.9439 | 92.6866
| SundridgeWind2085RCP8.5 | Sundridge | Wind | RCP8.5 | 2085 | 70.0284 | 75.4676 | 81.208 | 86.9311 | 92.6592
| SundridgeWind2090RCP8.5 | Sundridge | Wind | RCP8.5 | 2090 | 70.0595 | 75.4862 | 81.208 | 86.9182 | 92.6318
| SundridgeWind2095RCP8.5 | Sundridge | Wind | RCP8.5 | 2095 | 70.0595 | 75.4862 | 81.208 | 86.9182 | 92.6318
| SundridgeWind2100RCP8.5 | Sundridge | Wind | RCP8.5 | 2100 | 70.0595 | 75.4862 | 81.208 | 86.9182 | 92.6318
| TavistockIce Accretion2023RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2023 | 18.3933 | 22.0514 | 26.676 | 30.2049 | 33.7478
| TavistockIce Accretion2025RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2025 | 18.3557 | 22.0178 | 26.6445 | 30.1795 | 33.7195
| TavistockIce Accretion2030RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2030 | 18.3181 | 21.9842 | 26.613 | 30.154 | 33.6911
| TavistockIce Accretion2035RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2035 | 18.2806 | 21.9506 | 26.5815 | 30.1286 | 33.6628
| TavistockIce Accretion2040RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2040 | 18.243 | 21.917 | 26.55 | 30.1032 | 33.6344
| TavistockIce Accretion2045RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2045 | 18.2054 | 21.8834 | 26.5185 | 30.0778 | 33.6061
| TavistockIce Accretion2050RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2050 | 18.0514 | 21.7377 | 26.3844 | 29.9486 | 33.4825
| TavistockIce Accretion2055RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2055 | 17.9349 | 21.6257 | 26.2818 | 29.8449 | 33.3872
| TavistockIce Accretion2060RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2060 | 17.8184 | 21.5136 | 26.1792 | 29.7411 | 33.292
| TavistockIce Accretion2065RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2065 | 17.7019 | 21.4016 | 26.0766 | 29.6374 | 33.1967
| TavistockIce Accretion2070RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2070 | 17.5854 | 21.2895 | 25.974 | 29.5337 | 33.1015
| TavistockIce Accretion2075RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2075 | 17.5353 | 21.2522 | 25.956 | 29.5286 | 33.1071
| TavistockIce Accretion2080RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2080 | 17.4852 | 21.2148 | 25.938 | 29.5235 | 33.1128
| TavistockIce Accretion2085RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2085 | 17.4351 | 21.1775 | 25.92 | 29.5184 | 33.1185
| TavistockIce Accretion2090RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2090 | 17.385 | 21.1401 | 25.902 | 29.5133 | 33.1241
| TavistockIce Accretion2095RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2095 | 17.3349 | 21.1028 | 25.884 | 29.5083 | 33.1298
| TavistockIce Accretion2100RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2100 | 17.2848 | 21.0654 | 25.866 | 29.5032 | 33.1355
| TavistockIce Accretion2023RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2023 | 18.3933 | 22.0514 | 26.676 | 30.2049 | 33.7478
| TavistockIce Accretion2025RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2025 | 18.3557 | 22.0178 | 26.6445 | 30.1795 | 33.7195
| TavistockIce Accretion2030RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2030 | 18.3181 | 21.9842 | 26.613 | 30.154 | 33.6911
| TavistockIce Accretion2035RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2035 | 18.2806 | 21.9506 | 26.5815 | 30.1286 | 33.6628
| TavistockIce Accretion2040RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2040 | 18.243 | 21.917 | 26.55 | 30.1032 | 33.6344
| TavistockIce Accretion2045RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2045 | 18.2054 | 21.8834 | 26.5185 | 30.0778 | 33.6061
| TavistockIce Accretion2050RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2050 | 18.0514 | 21.7377 | 26.3844 | 29.9486 | 33.4825
| TavistockIce Accretion2055RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2055 | 17.9349 | 21.6257 | 26.2818 | 29.8449 | 33.3872
| TavistockIce Accretion2060RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2060 | 17.8184 | 21.5136 | 26.1792 | 29.7411 | 33.292
| TavistockIce Accretion2065RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2065 | 17.7019 | 21.4016 | 26.0766 | 29.6374 | 33.1967
| TavistockIce Accretion2070RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2070 | 17.5854 | 21.2895 | 25.974 | 29.5337 | 33.1015
| TavistockIce Accretion2075RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2075 | 17.5103 | 21.2335 | 25.947 | 29.5261 | 33.11
| TavistockIce Accretion2080RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2080 | 17.4351 | 21.1775 | 25.92 | 29.5184 | 33.1185
| TavistockIce Accretion2085RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2085 | 17.36 | 21.1214 | 25.893 | 29.5108 | 33.127
| TavistockIce Accretion2090RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2090 | 16.8965 | 20.6471 | 25.389 | 28.9947 | 32.5798
| TavistockIce Accretion2095RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2095 | 16.5083 | 20.2288 | 24.912 | 28.4862 | 32.0242
| TavistockIce Accretion2100RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2100 | 16.12 | 19.8104 | 24.435 | 27.9777 | 31.4685
| TavistockIce Accretion2023RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2023 | 18.3933 | 22.0514 | 26.676 | 30.2049 | 33.7478
| TavistockIce Accretion2025RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2025 | 18.3181 | 21.9842 | 26.613 | 30.154 | 33.6911
| TavistockIce Accretion2030RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2030 | 18.243 | 21.917 | 26.55 | 30.1032 | 33.6344
| TavistockIce Accretion2035RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2035 | 18.1678 | 21.8498 | 26.487 | 30.0523 | 33.5777
| TavistockIce Accretion2040RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2040 | 17.9737 | 21.663 | 26.316 | 29.8795 | 33.419
| TavistockIce Accretion2045RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2045 | 17.7796 | 21.4763 | 26.145 | 29.7066 | 33.2602
| TavistockIce Accretion2050RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2050 | 17.4852 | 21.2148 | 25.938 | 29.5235 | 33.1128
| TavistockIce Accretion2055RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2055 | 17.385 | 21.1401 | 25.902 | 29.5133 | 33.1241
| TavistockIce Accretion2060RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2060 | 16.8965 | 20.6471 | 25.389 | 28.9947 | 32.5798
| TavistockIce Accretion2065RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2065 | 16.5083 | 20.2288 | 24.912 | 28.4862 | 32.0242
| TavistockIce Accretion2070RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2070 | 15.7818 | 19.4444 | 24.039 | 27.5505 | 31.0149
| TavistockIce Accretion2075RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2075 | 15.4436 | 19.0784 | 23.643 | 27.1234 | 30.5613
| TavistockIce Accretion2080RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2080 | 15.1054 | 18.7124 | 23.247 | 26.6962 | 30.1077
| TavistockIce Accretion2085RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2085 | 14.2694 | 17.7487 | 22.113 | 25.4148 | 28.7129
| TavistockIce Accretion2090RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2090 | 13.4333 | 16.7851 | 20.979 | 24.1334 | 27.3181
| TavistockIce Accretion2095RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2095 | 13.4333 | 16.7851 | 20.979 | 24.1334 | 27.3181
| TavistockIce Accretion2100RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2100 | 13.4333 | 16.7851 | 20.979 | 24.1334 | 27.3181
| TavistockWind2023RCP4.5 | Tavistock | Wind | RCP4.5 | 2023 | 85.3829 | 92.1152 | 99.2446 | 106.3385 | 113.4405
| TavistockWind2025RCP4.5 | Tavistock | Wind | RCP4.5 | 2025 | 85.4618 | 92.22 | 99.3802 | 106.5011 | 113.6304
| TavistockWind2030RCP4.5 | Tavistock | Wind | RCP4.5 | 2030 | 85.5408 | 92.3248 | 99.5157 | 106.6636 | 113.8203
| TavistockWind2035RCP4.5 | Tavistock | Wind | RCP4.5 | 2035 | 85.6198 | 92.4296 | 99.6513 | 106.8261 | 114.0103
| TavistockWind2040RCP4.5 | Tavistock | Wind | RCP4.5 | 2040 | 85.6988 | 92.5344 | 99.7869 | 106.9887 | 114.2002
| TavistockWind2045RCP4.5 | Tavistock | Wind | RCP4.5 | 2045 | 85.7778 | 92.6393 | 99.9224 | 107.1512 | 114.3901
| TavistockWind2050RCP4.5 | Tavistock | Wind | RCP4.5 | 2050 | 85.9244 | 92.8261 | 100.1619 | 107.4333 | 114.7163
| TavistockWind2055RCP4.5 | Tavistock | Wind | RCP4.5 | 2055 | 85.9921 | 92.9081 | 100.2658 | 107.5528 | 114.8526
| TavistockWind2060RCP4.5 | Tavistock | Wind | RCP4.5 | 2060 | 86.0598 | 92.9901 | 100.3696 | 107.6723 | 114.9889
| TavistockWind2065RCP4.5 | Tavistock | Wind | RCP4.5 | 2065 | 86.1275 | 93.0722 | 100.4735 | 107.7919 | 115.1252
| TavistockWind2070RCP4.5 | Tavistock | Wind | RCP4.5 | 2070 | 86.1952 | 93.1542 | 100.5774 | 107.9114 | 115.2615
| TavistockWind2075RCP4.5 | Tavistock | Wind | RCP4.5 | 2075 | 86.2799 | 93.2712 | 100.7358 | 108.1054 | 115.4924
| TavistockWind2080RCP4.5 | Tavistock | Wind | RCP4.5 | 2080 | 86.3645 | 93.3881 | 100.8943 | 108.2994 | 115.7233
| TavistockWind2085RCP4.5 | Tavistock | Wind | RCP4.5 | 2085 | 86.4491 | 93.5051 | 101.0527 | 108.4934 | 115.9542
| TavistockWind2090RCP4.5 | Tavistock | Wind | RCP4.5 | 2090 | 86.5337 | 93.622 | 101.2111 | 108.6874 | 116.1851
| TavistockWind2095RCP4.5 | Tavistock | Wind | RCP4.5 | 2095 | 86.6183 | 93.739 | 101.3696 | 108.8814 | 116.416
| TavistockWind2100RCP4.5 | Tavistock | Wind | RCP4.5 | 2100 | 86.703 | 93.856 | 101.528 | 109.0754 | 116.6469
| TavistockWind2023RCP6.0 | Tavistock | Wind | RCP6.0 | 2023 | 85.3829 | 92.1152 | 99.2446 | 106.3385 | 113.4405
| TavistockWind2025RCP6.0 | Tavistock | Wind | RCP6.0 | 2025 | 85.4618 | 92.22 | 99.3802 | 106.5011 | 113.6304
| TavistockWind2030RCP6.0 | Tavistock | Wind | RCP6.0 | 2030 | 85.5408 | 92.3248 | 99.5157 | 106.6636 | 113.8203
| TavistockWind2035RCP6.0 | Tavistock | Wind | RCP6.0 | 2035 | 85.6198 | 92.4296 | 99.6513 | 106.8261 | 114.0103
| TavistockWind2040RCP6.0 | Tavistock | Wind | RCP6.0 | 2040 | 85.6988 | 92.5344 | 99.7869 | 106.9887 | 114.2002
| TavistockWind2045RCP6.0 | Tavistock | Wind | RCP6.0 | 2045 | 85.7778 | 92.6393 | 99.9224 | 107.1512 | 114.3901
| TavistockWind2050RCP6.0 | Tavistock | Wind | RCP6.0 | 2050 | 85.9244 | 92.8261 | 100.1619 | 107.4333 | 114.7163
| TavistockWind2055RCP6.0 | Tavistock | Wind | RCP6.0 | 2055 | 85.9921 | 92.9081 | 100.2658 | 107.5528 | 114.8526
| TavistockWind2060RCP6.0 | Tavistock | Wind | RCP6.0 | 2060 | 86.0598 | 92.9901 | 100.3696 | 107.6723 | 114.9889
| TavistockWind2065RCP6.0 | Tavistock | Wind | RCP6.0 | 2065 | 86.1275 | 93.0722 | 100.4735 | 107.7919 | 115.1252
| TavistockWind2070RCP6.0 | Tavistock | Wind | RCP6.0 | 2070 | 86.1952 | 93.1542 | 100.5774 | 107.9114 | 115.2615
| TavistockWind2075RCP6.0 | Tavistock | Wind | RCP6.0 | 2075 | 86.3222 | 93.3296 | 100.815 | 108.2024 | 115.6079
| TavistockWind2080RCP6.0 | Tavistock | Wind | RCP6.0 | 2080 | 86.4491 | 93.5051 | 101.0527 | 108.4934 | 115.9542
| TavistockWind2085RCP6.0 | Tavistock | Wind | RCP6.0 | 2085 | 86.576 | 93.6805 | 101.2904 | 108.7844 | 116.3005
| TavistockWind2090RCP6.0 | Tavistock | Wind | RCP6.0 | 2090 | 87.0499 | 94.3026 | 102.0964 | 109.7465 | 117.4252
| TavistockWind2095RCP6.0 | Tavistock | Wind | RCP6.0 | 2095 | 87.3969 | 94.7491 | 102.6648 | 110.4176 | 118.2035
| TavistockWind2100RCP6.0 | Tavistock | Wind | RCP6.0 | 2100 | 87.7438 | 95.1957 | 103.2332 | 111.0887 | 118.9818
| TavistockWind2023RCP8.5 | Tavistock | Wind | RCP8.5 | 2023 | 85.3829 | 92.1152 | 99.2446 | 106.3385 | 113.4405
| TavistockWind2025RCP8.5 | Tavistock | Wind | RCP8.5 | 2025 | 85.5408 | 92.3248 | 99.5157 | 106.6636 | 113.8203
| TavistockWind2030RCP8.5 | Tavistock | Wind | RCP8.5 | 2030 | 85.6988 | 92.5344 | 99.7869 | 106.9887 | 114.2002
| TavistockWind2035RCP8.5 | Tavistock | Wind | RCP8.5 | 2035 | 85.8567 | 92.7441 | 100.058 | 107.3137 | 114.58
| TavistockWind2040RCP8.5 | Tavistock | Wind | RCP8.5 | 2040 | 85.9696 | 92.8808 | 100.2311 | 107.513 | 114.8072
| TavistockWind2045RCP8.5 | Tavistock | Wind | RCP8.5 | 2045 | 86.0824 | 93.0175 | 100.4043 | 107.7122 | 115.0344
| TavistockWind2050RCP8.5 | Tavistock | Wind | RCP8.5 | 2050 | 86.3645 | 93.3881 | 100.8943 | 108.2994 | 115.7233
| TavistockWind2055RCP8.5 | Tavistock | Wind | RCP8.5 | 2055 | 86.5337 | 93.622 | 101.2111 | 108.6874 | 116.1851
| TavistockWind2060RCP8.5 | Tavistock | Wind | RCP8.5 | 2060 | 87.0499 | 94.3026 | 102.0964 | 109.7465 | 117.4252
| TavistockWind2065RCP8.5 | Tavistock | Wind | RCP8.5 | 2065 | 87.3969 | 94.7491 | 102.6648 | 110.4176 | 118.2035
| TavistockWind2070RCP8.5 | Tavistock | Wind | RCP8.5 | 2070 | 87.9638 | 95.4904 | 103.6219 | 111.5571 | 119.533
| TavistockWind2075RCP8.5 | Tavistock | Wind | RCP8.5 | 2075 | 88.1838 | 95.7851 | 104.0107 | 112.0254 | 120.0841
| TavistockWind2080RCP8.5 | Tavistock | Wind | RCP8.5 | 2080 | 88.4038 | 96.0798 | 104.3994 | 112.4938 | 120.6353
| TavistockWind2085RCP8.5 | Tavistock | Wind | RCP8.5 | 2085 | 88.8354 | 96.6449 | 105.1393 | 113.3799 | 121.6687
| TavistockWind2090RCP8.5 | Tavistock | Wind | RCP8.5 | 2090 | 89.267 | 97.2099 | 105.8792 | 114.2659 | 122.7021
| TavistockWind2095RCP8.5 | Tavistock | Wind | RCP8.5 | 2095 | 89.267 | 97.2099 | 105.8792 | 114.2659 | 122.7021
| TavistockWind2100RCP8.5 | Tavistock | Wind | RCP8.5 | 2100 | 89.267 | 97.2099 | 105.8792 | 114.2659 | 122.7021
| TemagamiIce Accretion2023RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2023 | 15.3726 | 18.3886 | 22.218 | 25.1538 | 28.0741
| TemagamiIce Accretion2025RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2025 | 15.3556 | 18.3683 | 22.1935 | 25.1222 | 28.0388
| TemagamiIce Accretion2030RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2030 | 15.3385 | 18.348 | 22.169 | 25.0905 | 28.0035
| TemagamiIce Accretion2035RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2035 | 15.3215 | 18.3276 | 22.1445 | 25.0589 | 27.9682
| TemagamiIce Accretion2040RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2040 | 15.3044 | 18.3073 | 22.12 | 25.0272 | 27.9329
| TemagamiIce Accretion2045RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2045 | 15.2874 | 18.287 | 22.0955 | 24.9956 | 27.8977
| TemagamiIce Accretion2050RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2050 | 15.2937 | 18.2945 | 22.1046 | 25.0067 | 27.91
| TemagamiIce Accretion2055RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2055 | 15.3171 | 18.3224 | 22.1382 | 25.0494 | 27.9576
| TemagamiIce Accretion2060RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2060 | 15.3405 | 18.3503 | 22.1718 | 25.0921 | 28.0053
| TemagamiIce Accretion2065RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2065 | 15.3639 | 18.3782 | 22.2054 | 25.1348 | 28.0529
| TemagamiIce Accretion2070RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2070 | 15.3872 | 18.4061 | 22.239 | 25.1775 | 28.1005
| TemagamiIce Accretion2075RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2075 | 15.3848 | 18.4032 | 22.2355 | 25.1736 | 28.0961
| TemagamiIce Accretion2080RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2080 | 15.3824 | 18.4003 | 22.232 | 25.1696 | 28.0917
| TemagamiIce Accretion2085RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2085 | 15.3799 | 18.3974 | 22.2285 | 25.1657 | 28.0873
| TemagamiIce Accretion2090RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2090 | 15.3775 | 18.3945 | 22.225 | 25.1617 | 28.0829
| TemagamiIce Accretion2095RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2095 | 15.3751 | 18.3916 | 22.2215 | 25.1578 | 28.0785
| TemagamiIce Accretion2100RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2100 | 15.3726 | 18.3886 | 22.218 | 25.1538 | 28.0741
| TemagamiIce Accretion2023RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2023 | 15.3726 | 18.3886 | 22.218 | 25.1538 | 28.0741
| TemagamiIce Accretion2025RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2025 | 15.3556 | 18.3683 | 22.1935 | 25.1222 | 28.0388
| TemagamiIce Accretion2030RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2030 | 15.3385 | 18.348 | 22.169 | 25.0905 | 28.0035
| TemagamiIce Accretion2035RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2035 | 15.3215 | 18.3276 | 22.1445 | 25.0589 | 27.9682
| TemagamiIce Accretion2040RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2040 | 15.3044 | 18.3073 | 22.12 | 25.0272 | 27.9329
| TemagamiIce Accretion2045RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2045 | 15.2874 | 18.287 | 22.0955 | 24.9956 | 27.8977
| TemagamiIce Accretion2050RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2050 | 15.2937 | 18.2945 | 22.1046 | 25.0067 | 27.91
| TemagamiIce Accretion2055RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2055 | 15.3171 | 18.3224 | 22.1382 | 25.0494 | 27.9576
| TemagamiIce Accretion2060RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2060 | 15.3405 | 18.3503 | 22.1718 | 25.0921 | 28.0053
| TemagamiIce Accretion2065RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2065 | 15.3639 | 18.3782 | 22.2054 | 25.1348 | 28.0529
| TemagamiIce Accretion2070RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2070 | 15.3872 | 18.4061 | 22.239 | 25.1775 | 28.1005
| TemagamiIce Accretion2075RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2075 | 15.3836 | 18.4017 | 22.2337 | 25.1716 | 28.0939
| TemagamiIce Accretion2080RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2080 | 15.3799 | 18.3974 | 22.2285 | 25.1657 | 28.0873
| TemagamiIce Accretion2085RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2085 | 15.3763 | 18.393 | 22.2233 | 25.1597 | 28.0807
| TemagamiIce Accretion2090RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2090 | 15.436 | 18.4874 | 22.358 | 25.3199 | 28.2769
| TemagamiIce Accretion2095RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2095 | 15.4993 | 18.5862 | 22.498 | 25.486 | 28.4798
| TemagamiIce Accretion2100RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2100 | 15.5626 | 18.685 | 22.638 | 25.6521 | 28.6826
| TemagamiIce Accretion2023RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2023 | 15.3726 | 18.3886 | 22.218 | 25.1538 | 28.0741
| TemagamiIce Accretion2025RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2025 | 15.3385 | 18.348 | 22.169 | 25.0905 | 28.0035
| TemagamiIce Accretion2030RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2030 | 15.3044 | 18.3073 | 22.12 | 25.0272 | 27.9329
| TemagamiIce Accretion2035RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2035 | 15.2703 | 18.2666 | 22.071 | 24.964 | 27.8624
| TemagamiIce Accretion2040RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2040 | 15.3093 | 18.3131 | 22.127 | 25.0351 | 27.9418
| TemagamiIce Accretion2045RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2045 | 15.3483 | 18.3596 | 22.183 | 25.1063 | 28.0211
| TemagamiIce Accretion2050RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2050 | 15.3824 | 18.4003 | 22.232 | 25.1696 | 28.0917
| TemagamiIce Accretion2055RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2055 | 15.3775 | 18.3945 | 22.225 | 25.1617 | 28.0829
| TemagamiIce Accretion2060RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2060 | 15.436 | 18.4874 | 22.358 | 25.3199 | 28.2769
| TemagamiIce Accretion2065RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2065 | 15.4993 | 18.5862 | 22.498 | 25.486 | 28.4798
| TemagamiIce Accretion2070RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2070 | 15.3726 | 18.47 | 22.4 | 25.3911 | 28.3916
| TemagamiIce Accretion2075RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2075 | 15.1827 | 18.255 | 22.162 | 25.1301 | 28.1005
| TemagamiIce Accretion2080RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2080 | 14.9927 | 18.04 | 21.924 | 24.869 | 27.8095
| TemagamiIce Accretion2085RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2085 | 14.832 | 17.8919 | 21.7665 | 24.7267 | 27.6639
| TemagamiIce Accretion2090RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2090 | 14.6712 | 17.7437 | 21.609 | 24.5843 | 27.5184
| TemagamiIce Accretion2095RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2095 | 14.6712 | 17.7437 | 21.609 | 24.5843 | 27.5184
| TemagamiIce Accretion2100RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2100 | 14.6712 | 17.7437 | 21.609 | 24.5843 | 27.5184
| TemagamiWind2023RCP4.5 | Temagami | Wind | RCP4.5 | 2023 | 75.0929 | 80.7725 | 86.7129 | 92.6804 | 98.6543
| TemagamiWind2025RCP4.5 | Temagami | Wind | RCP4.5 | 2025 | 75.0228 | 80.6727 | 86.5781 | 92.5175 | 98.4609
| TemagamiWind2030RCP4.5 | Temagami | Wind | RCP4.5 | 2030 | 74.9527 | 80.5729 | 86.4432 | 92.3546 | 98.2675
| TemagamiWind2035RCP4.5 | Temagami | Wind | RCP4.5 | 2035 | 74.8826 | 80.4731 | 86.3084 | 92.1917 | 98.0741
| TemagamiWind2040RCP4.5 | Temagami | Wind | RCP4.5 | 2040 | 74.8125 | 80.3733 | 86.1735 | 92.0288 | 97.8807
| TemagamiWind2045RCP4.5 | Temagami | Wind | RCP4.5 | 2045 | 74.7423 | 80.2735 | 86.0387 | 91.8659 | 97.6873
| TemagamiWind2050RCP4.5 | Temagami | Wind | RCP4.5 | 2050 | 74.6677 | 80.1575 | 85.8725 | 91.6601 | 97.4384
| TemagamiWind2055RCP4.5 | Temagami | Wind | RCP4.5 | 2055 | 74.6632 | 80.1414 | 85.8412 | 91.6173 | 97.3829
| TemagamiWind2060RCP4.5 | Temagami | Wind | RCP4.5 | 2060 | 74.6587 | 80.1252 | 85.8098 | 91.5745 | 97.3273
| TemagamiWind2065RCP4.5 | Temagami | Wind | RCP4.5 | 2065 | 74.6542 | 80.109 | 85.7785 | 91.5317 | 97.2718
| TemagamiWind2070RCP4.5 | Temagami | Wind | RCP4.5 | 2070 | 74.6497 | 80.0928 | 85.7472 | 91.4889 | 97.2162
| TemagamiWind2075RCP4.5 | Temagami | Wind | RCP4.5 | 2075 | 74.7774 | 80.2479 | 85.9343 | 91.703 | 97.4592
| TemagamiWind2080RCP4.5 | Temagami | Wind | RCP4.5 | 2080 | 74.9051 | 80.403 | 86.1213 | 91.9171 | 97.7022
| TemagamiWind2085RCP4.5 | Temagami | Wind | RCP4.5 | 2085 | 75.0328 | 80.558 | 86.3084 | 92.1312 | 97.9452
| TemagamiWind2090RCP4.5 | Temagami | Wind | RCP4.5 | 2090 | 75.1605 | 80.7131 | 86.4954 | 92.3453 | 98.1882
| TemagamiWind2095RCP4.5 | Temagami | Wind | RCP4.5 | 2095 | 75.2882 | 80.8682 | 86.6825 | 92.5594 | 98.4312
| TemagamiWind2100RCP4.5 | Temagami | Wind | RCP4.5 | 2100 | 75.416 | 81.0233 | 86.8695 | 92.7735 | 98.6742
| TemagamiWind2023RCP6.0 | Temagami | Wind | RCP6.0 | 2023 | 75.0929 | 80.7725 | 86.7129 | 92.6804 | 98.6543
| TemagamiWind2025RCP6.0 | Temagami | Wind | RCP6.0 | 2025 | 75.0228 | 80.6727 | 86.5781 | 92.5175 | 98.4609
| TemagamiWind2030RCP6.0 | Temagami | Wind | RCP6.0 | 2030 | 74.9527 | 80.5729 | 86.4432 | 92.3546 | 98.2675
| TemagamiWind2035RCP6.0 | Temagami | Wind | RCP6.0 | 2035 | 74.8826 | 80.4731 | 86.3084 | 92.1917 | 98.0741
| TemagamiWind2040RCP6.0 | Temagami | Wind | RCP6.0 | 2040 | 74.8125 | 80.3733 | 86.1735 | 92.0288 | 97.8807
| TemagamiWind2045RCP6.0 | Temagami | Wind | RCP6.0 | 2045 | 74.7423 | 80.2735 | 86.0387 | 91.8659 | 97.6873
| TemagamiWind2050RCP6.0 | Temagami | Wind | RCP6.0 | 2050 | 74.6677 | 80.1575 | 85.8725 | 91.6601 | 97.4384
| TemagamiWind2055RCP6.0 | Temagami | Wind | RCP6.0 | 2055 | 74.6632 | 80.1414 | 85.8412 | 91.6173 | 97.3829
| TemagamiWind2060RCP6.0 | Temagami | Wind | RCP6.0 | 2060 | 74.6587 | 80.1252 | 85.8098 | 91.5745 | 97.3273
| TemagamiWind2065RCP6.0 | Temagami | Wind | RCP6.0 | 2065 | 74.6542 | 80.109 | 85.7785 | 91.5317 | 97.2718
| TemagamiWind2070RCP6.0 | Temagami | Wind | RCP6.0 | 2070 | 74.6497 | 80.0928 | 85.7472 | 91.4889 | 97.2162
| TemagamiWind2075RCP6.0 | Temagami | Wind | RCP6.0 | 2075 | 74.8413 | 80.3254 | 86.0278 | 91.81 | 97.5807
| TemagamiWind2080RCP6.0 | Temagami | Wind | RCP6.0 | 2080 | 75.0328 | 80.558 | 86.3084 | 92.1312 | 97.9452
| TemagamiWind2085RCP6.0 | Temagami | Wind | RCP6.0 | 2085 | 75.2244 | 80.7907 | 86.5889 | 92.4523 | 98.3097
| TemagamiWind2090RCP6.0 | Temagami | Wind | RCP6.0 | 2090 | 75.6664 | 81.3442 | 87.2784 | 93.2545 | 99.2296
| TemagamiWind2095RCP6.0 | Temagami | Wind | RCP6.0 | 2095 | 75.9168 | 81.6652 | 87.6873 | 93.7354 | 99.785
| TemagamiWind2100RCP6.0 | Temagami | Wind | RCP6.0 | 2100 | 76.1672 | 81.9861 | 88.0962 | 94.2164 | 100.3404
| TemagamiWind2023RCP8.5 | Temagami | Wind | RCP8.5 | 2023 | 75.0929 | 80.7725 | 86.7129 | 92.6804 | 98.6543
| TemagamiWind2025RCP8.5 | Temagami | Wind | RCP8.5 | 2025 | 74.9527 | 80.5729 | 86.4432 | 92.3546 | 98.2675
| TemagamiWind2030RCP8.5 | Temagami | Wind | RCP8.5 | 2030 | 74.8125 | 80.3733 | 86.1735 | 92.0288 | 97.8807
| TemagamiWind2035RCP8.5 | Temagami | Wind | RCP8.5 | 2035 | 74.6722 | 80.1737 | 85.9038 | 91.703 | 97.4939
| TemagamiWind2040RCP8.5 | Temagami | Wind | RCP8.5 | 2040 | 74.6647 | 80.1467 | 85.8516 | 91.6316 | 97.4014
| TemagamiWind2045RCP8.5 | Temagami | Wind | RCP8.5 | 2045 | 74.6572 | 80.1198 | 85.7994 | 91.5602 | 97.3088
| TemagamiWind2050RCP8.5 | Temagami | Wind | RCP8.5 | 2050 | 74.9051 | 80.403 | 86.1213 | 91.9171 | 97.7022
| TemagamiWind2055RCP8.5 | Temagami | Wind | RCP8.5 | 2055 | 75.1605 | 80.7131 | 86.4954 | 92.3453 | 98.1882
| TemagamiWind2060RCP8.5 | Temagami | Wind | RCP8.5 | 2060 | 75.6664 | 81.3442 | 87.2784 | 93.2545 | 99.2296
| TemagamiWind2065RCP8.5 | Temagami | Wind | RCP8.5 | 2065 | 75.9168 | 81.6652 | 87.6873 | 93.7354 | 99.785
| TemagamiWind2070RCP8.5 | Temagami | Wind | RCP8.5 | 2070 | 76.3074 | 82.1425 | 88.2731 | 94.415 | 100.5553
| TemagamiWind2075RCP8.5 | Temagami | Wind | RCP8.5 | 2075 | 76.4476 | 82.299 | 88.45 | 94.6136 | 100.7702
| TemagamiWind2080RCP8.5 | Temagami | Wind | RCP8.5 | 2080 | 76.5879 | 82.4554 | 88.6269 | 94.8122 | 100.9851
| TemagamiWind2085RCP8.5 | Temagami | Wind | RCP8.5 | 2085 | 76.5503 | 82.3987 | 88.5399 | 94.7005 | 100.8512
| TemagamiWind2090RCP8.5 | Temagami | Wind | RCP8.5 | 2090 | 76.5127 | 82.3421 | 88.4529 | 94.5887 | 100.7173
| TemagamiWind2095RCP8.5 | Temagami | Wind | RCP8.5 | 2095 | 76.5127 | 82.3421 | 88.4529 | 94.5887 | 100.7173
| TemagamiWind2100RCP8.5 | Temagami | Wind | RCP8.5 | 2100 | 76.5127 | 82.3421 | 88.4529 | 94.5887 | 100.7173
| ThamesfordIce Accretion2023RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2023 | 20.5414 | 24.6261 | 29.76 | 33.6966 | 37.611
| ThamesfordIce Accretion2025RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2025 | 20.5623 | 24.6676 | 29.835 | 33.7926 | 37.7307
| ThamesfordIce Accretion2030RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2030 | 20.5831 | 24.7091 | 29.91 | 33.8887 | 37.8504
| ThamesfordIce Accretion2035RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2035 | 20.604 | 24.7506 | 29.985 | 33.9847 | 37.9701
| ThamesfordIce Accretion2040RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2040 | 20.6249 | 24.7921 | 30.06 | 34.0808 | 38.0898
| ThamesfordIce Accretion2045RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2045 | 20.6458 | 24.8336 | 30.135 | 34.1768 | 38.2095
| ThamesfordIce Accretion2050RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2050 | 20.5831 | 24.8153 | 30.174 | 34.2526 | 38.3292
| ThamesfordIce Accretion2055RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2055 | 20.4996 | 24.7556 | 30.138 | 34.2322 | 38.3292
| ThamesfordIce Accretion2060RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2060 | 20.4161 | 24.6958 | 30.102 | 34.2119 | 38.3292
| ThamesfordIce Accretion2065RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2065 | 20.3326 | 24.6361 | 30.066 | 34.1915 | 38.3292
| ThamesfordIce Accretion2070RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2070 | 20.2491 | 24.5763 | 30.03 | 34.1712 | 38.3292
| ThamesfordIce Accretion2075RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2075 | 20.2109 | 24.5597 | 30.045 | 34.2051 | 38.3859
| ThamesfordIce Accretion2080RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2080 | 20.1726 | 24.5431 | 30.06 | 34.239 | 38.4426
| ThamesfordIce Accretion2085RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2085 | 20.1343 | 24.5265 | 30.075 | 34.2729 | 38.4993
| ThamesfordIce Accretion2090RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2090 | 20.096 | 24.5099 | 30.09 | 34.3068 | 38.556
| ThamesfordIce Accretion2095RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2095 | 20.0578 | 24.4933 | 30.105 | 34.3407 | 38.6127
| ThamesfordIce Accretion2100RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2100 | 20.0195 | 24.4767 | 30.12 | 34.3746 | 38.6694
| ThamesfordIce Accretion2023RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2023 | 20.5414 | 24.6261 | 29.76 | 33.6966 | 37.611
| ThamesfordIce Accretion2025RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2025 | 20.5623 | 24.6676 | 29.835 | 33.7926 | 37.7307
| ThamesfordIce Accretion2030RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2030 | 20.5831 | 24.7091 | 29.91 | 33.8887 | 37.8504
| ThamesfordIce Accretion2035RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2035 | 20.604 | 24.7506 | 29.985 | 33.9847 | 37.9701
| ThamesfordIce Accretion2040RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2040 | 20.6249 | 24.7921 | 30.06 | 34.0808 | 38.0898
| ThamesfordIce Accretion2045RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2045 | 20.6458 | 24.8336 | 30.135 | 34.1768 | 38.2095
| ThamesfordIce Accretion2050RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2050 | 20.5831 | 24.8153 | 30.174 | 34.2526 | 38.3292
| ThamesfordIce Accretion2055RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2055 | 20.4996 | 24.7556 | 30.138 | 34.2322 | 38.3292
| ThamesfordIce Accretion2060RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2060 | 20.4161 | 24.6958 | 30.102 | 34.2119 | 38.3292
| ThamesfordIce Accretion2065RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2065 | 20.3326 | 24.6361 | 30.066 | 34.1915 | 38.3292
| ThamesfordIce Accretion2070RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2070 | 20.2491 | 24.5763 | 30.03 | 34.1712 | 38.3292
| ThamesfordIce Accretion2075RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2075 | 20.1917 | 24.5514 | 30.0525 | 34.222 | 38.4142
| ThamesfordIce Accretion2080RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2080 | 20.1343 | 24.5265 | 30.075 | 34.2729 | 38.4993
| ThamesfordIce Accretion2085RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2085 | 20.0769 | 24.5016 | 30.0975 | 34.3238 | 38.5844
| ThamesfordIce Accretion2090RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2090 | 19.769 | 24.2277 | 29.86 | 34.1147 | 38.3922
| ThamesfordIce Accretion2095RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2095 | 19.5185 | 23.9787 | 29.6 | 33.8548 | 38.115
| ThamesfordIce Accretion2100RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2100 | 19.268 | 23.7297 | 29.34 | 33.5949 | 37.8378
| ThamesfordIce Accretion2023RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2023 | 20.5414 | 24.6261 | 29.76 | 33.6966 | 37.611
| ThamesfordIce Accretion2025RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2025 | 20.5831 | 24.7091 | 29.91 | 33.8887 | 37.8504
| ThamesfordIce Accretion2030RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2030 | 20.6249 | 24.7921 | 30.06 | 34.0808 | 38.0898
| ThamesfordIce Accretion2035RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2035 | 20.6666 | 24.8751 | 30.21 | 34.2729 | 38.3292
| ThamesfordIce Accretion2040RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2040 | 20.5275 | 24.7755 | 30.15 | 34.239 | 38.3292
| ThamesfordIce Accretion2045RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2045 | 20.3883 | 24.6759 | 30.09 | 34.2051 | 38.3292
| ThamesfordIce Accretion2050RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2050 | 20.1726 | 24.5431 | 30.06 | 34.239 | 38.4426
| ThamesfordIce Accretion2055RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2055 | 20.096 | 24.5099 | 30.09 | 34.3068 | 38.556
| ThamesfordIce Accretion2060RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2060 | 19.769 | 24.2277 | 29.86 | 34.1147 | 38.3922
| ThamesfordIce Accretion2065RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2065 | 19.5185 | 23.9787 | 29.6 | 33.8548 | 38.115
| ThamesfordIce Accretion2070RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2070 | 18.8157 | 23.2234 | 28.77 | 32.9734 | 37.1574
| ThamesfordIce Accretion2075RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2075 | 18.3634 | 22.7171 | 28.2 | 32.3519 | 36.477
| ThamesfordIce Accretion2080RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2080 | 17.9111 | 22.2108 | 27.63 | 31.7304 | 35.7966
| ThamesfordIce Accretion2085RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2085 | 16.9717 | 21.1028 | 26.31 | 30.2557 | 34.1712
| ThamesfordIce Accretion2090RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2090 | 16.0323 | 19.9947 | 24.99 | 28.7811 | 32.5458
| ThamesfordIce Accretion2095RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2095 | 16.0323 | 19.9947 | 24.99 | 28.7811 | 32.5458
| ThamesfordIce Accretion2100RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2100 | 16.0323 | 19.9947 | 24.99 | 28.7811 | 32.5458
| ThamesfordWind2023RCP4.5 | Thamesford | Wind | RCP4.5 | 2023 | 88.1536 | 95.1229 | 102.5049 | 109.8423 | 117.1895
| ThamesfordWind2025RCP4.5 | Thamesford | Wind | RCP4.5 | 2025 | 88.2466 | 95.245 | 102.6648 | 110.0351 | 117.4159
| ThamesfordWind2030RCP4.5 | Thamesford | Wind | RCP4.5 | 2030 | 88.3397 | 95.3671 | 102.8247 | 110.2278 | 117.6424
| ThamesfordWind2035RCP4.5 | Thamesford | Wind | RCP4.5 | 2035 | 88.4327 | 95.4892 | 102.9846 | 110.4205 | 117.8688
| ThamesfordWind2040RCP4.5 | Thamesford | Wind | RCP4.5 | 2040 | 88.5257 | 95.6113 | 103.1446 | 110.6132 | 118.0953
| ThamesfordWind2045RCP4.5 | Thamesford | Wind | RCP4.5 | 2045 | 88.6187 | 95.7335 | 103.3045 | 110.806 | 118.3217
| ThamesfordWind2050RCP4.5 | Thamesford | Wind | RCP4.5 | 2050 | 88.7467 | 95.8988 | 103.5189 | 111.0614 | 118.6172
| ThamesfordWind2055RCP4.5 | Thamesford | Wind | RCP4.5 | 2055 | 88.7815 | 95.942 | 103.5735 | 111.1241 | 118.6863
| ThamesfordWind2060RCP4.5 | Thamesford | Wind | RCP4.5 | 2060 | 88.8164 | 95.9852 | 103.628 | 111.1867 | 118.7554
| ThamesfordWind2065RCP4.5 | Thamesford | Wind | RCP4.5 | 2065 | 88.8513 | 96.0284 | 103.6826 | 111.2494 | 118.8245
| ThamesfordWind2070RCP4.5 | Thamesford | Wind | RCP4.5 | 2070 | 88.8862 | 96.0716 | 103.7371 | 111.3121 | 118.8936
| ThamesfordWind2075RCP4.5 | Thamesford | Wind | RCP4.5 | 2075 | 88.9938 | 96.2156 | 103.9256 | 111.539 | 119.1622
| ThamesfordWind2080RCP4.5 | Thamesford | Wind | RCP4.5 | 2080 | 89.1013 | 96.3597 | 104.1142 | 111.766 | 119.4309
| ThamesfordWind2085RCP4.5 | Thamesford | Wind | RCP4.5 | 2085 | 89.2089 | 96.5037 | 104.3027 | 111.9929 | 119.6995
| ThamesfordWind2090RCP4.5 | Thamesford | Wind | RCP4.5 | 2090 | 89.3164 | 96.6477 | 104.4912 | 112.2199 | 119.9682
| ThamesfordWind2095RCP4.5 | Thamesford | Wind | RCP4.5 | 2095 | 89.424 | 96.7917 | 104.6798 | 112.4468 | 120.2369
| ThamesfordWind2100RCP4.5 | Thamesford | Wind | RCP4.5 | 2100 | 89.5316 | 96.9358 | 104.8683 | 112.6738 | 120.5055
| ThamesfordWind2023RCP6.0 | Thamesford | Wind | RCP6.0 | 2023 | 88.1536 | 95.1229 | 102.5049 | 109.8423 | 117.1895
| ThamesfordWind2025RCP6.0 | Thamesford | Wind | RCP6.0 | 2025 | 88.2466 | 95.245 | 102.6648 | 110.0351 | 117.4159
| ThamesfordWind2030RCP6.0 | Thamesford | Wind | RCP6.0 | 2030 | 88.3397 | 95.3671 | 102.8247 | 110.2278 | 117.6424
| ThamesfordWind2035RCP6.0 | Thamesford | Wind | RCP6.0 | 2035 | 88.4327 | 95.4892 | 102.9846 | 110.4205 | 117.8688
| ThamesfordWind2040RCP6.0 | Thamesford | Wind | RCP6.0 | 2040 | 88.5257 | 95.6113 | 103.1446 | 110.6132 | 118.0953
| ThamesfordWind2045RCP6.0 | Thamesford | Wind | RCP6.0 | 2045 | 88.6187 | 95.7335 | 103.3045 | 110.806 | 118.3217
| ThamesfordWind2050RCP6.0 | Thamesford | Wind | RCP6.0 | 2050 | 88.7467 | 95.8988 | 103.5189 | 111.0614 | 118.6172
| ThamesfordWind2055RCP6.0 | Thamesford | Wind | RCP6.0 | 2055 | 88.7815 | 95.942 | 103.5735 | 111.1241 | 118.6863
| ThamesfordWind2060RCP6.0 | Thamesford | Wind | RCP6.0 | 2060 | 88.8164 | 95.9852 | 103.628 | 111.1867 | 118.7554
| ThamesfordWind2065RCP6.0 | Thamesford | Wind | RCP6.0 | 2065 | 88.8513 | 96.0284 | 103.6826 | 111.2494 | 118.8245
| ThamesfordWind2070RCP6.0 | Thamesford | Wind | RCP6.0 | 2070 | 88.8862 | 96.0716 | 103.7371 | 111.3121 | 118.8936
| ThamesfordWind2075RCP6.0 | Thamesford | Wind | RCP6.0 | 2075 | 89.0475 | 96.2876 | 104.0199 | 111.6525 | 119.2966
| ThamesfordWind2080RCP6.0 | Thamesford | Wind | RCP6.0 | 2080 | 89.2089 | 96.5037 | 104.3027 | 111.9929 | 119.6995
| ThamesfordWind2085RCP6.0 | Thamesford | Wind | RCP6.0 | 2085 | 89.3702 | 96.7197 | 104.5855 | 112.3334 | 120.1025
| ThamesfordWind2090RCP6.0 | Thamesford | Wind | RCP6.0 | 2090 | 89.8455 | 97.3115 | 105.3161 | 113.1889 | 121.0851
| ThamesfordWind2095RCP6.0 | Thamesford | Wind | RCP6.0 | 2095 | 90.1595 | 97.6872 | 105.7638 | 113.704 | 121.6646
| ThamesfordWind2100RCP6.0 | Thamesford | Wind | RCP6.0 | 2100 | 90.4734 | 98.0629 | 106.2116 | 114.2192 | 122.2441
| ThamesfordWind2023RCP8.5 | Thamesford | Wind | RCP8.5 | 2023 | 88.1536 | 95.1229 | 102.5049 | 109.8423 | 117.1895
| ThamesfordWind2025RCP8.5 | Thamesford | Wind | RCP8.5 | 2025 | 88.3397 | 95.3671 | 102.8247 | 110.2278 | 117.6424
| ThamesfordWind2030RCP8.5 | Thamesford | Wind | RCP8.5 | 2030 | 88.5257 | 95.6113 | 103.1446 | 110.6132 | 118.0953
| ThamesfordWind2035RCP8.5 | Thamesford | Wind | RCP8.5 | 2035 | 88.7118 | 95.8556 | 103.4644 | 110.9987 | 118.5481
| ThamesfordWind2040RCP8.5 | Thamesford | Wind | RCP8.5 | 2040 | 88.7699 | 95.9276 | 103.5553 | 111.1032 | 118.6633
| ThamesfordWind2045RCP8.5 | Thamesford | Wind | RCP8.5 | 2045 | 88.828 | 95.9996 | 103.6462 | 111.2076 | 118.7784
| ThamesfordWind2050RCP8.5 | Thamesford | Wind | RCP8.5 | 2050 | 89.1013 | 96.3597 | 104.1142 | 111.766 | 119.4309
| ThamesfordWind2055RCP8.5 | Thamesford | Wind | RCP8.5 | 2055 | 89.3164 | 96.6477 | 104.4912 | 112.2199 | 119.9682
| ThamesfordWind2060RCP8.5 | Thamesford | Wind | RCP8.5 | 2060 | 89.8455 | 97.3115 | 105.3161 | 113.1889 | 121.0851
| ThamesfordWind2065RCP8.5 | Thamesford | Wind | RCP8.5 | 2065 | 90.1595 | 97.6872 | 105.7638 | 113.704 | 121.6646
| ThamesfordWind2070RCP8.5 | Thamesford | Wind | RCP8.5 | 2070 | 90.7496 | 98.4261 | 106.6897 | 114.7884 | 122.9119
| ThamesfordWind2075RCP8.5 | Thamesford | Wind | RCP8.5 | 2075 | 91.0258 | 98.7893 | 107.1677 | 115.3575 | 123.5798
| ThamesfordWind2080RCP8.5 | Thamesford | Wind | RCP8.5 | 2080 | 91.302 | 99.1525 | 107.6458 | 115.9267 | 124.2476
| ThamesfordWind2085RCP8.5 | Thamesford | Wind | RCP8.5 | 2085 | 91.6682 | 99.6175 | 108.2366 | 116.6291 | 125.0593
| ThamesfordWind2090RCP8.5 | Thamesford | Wind | RCP8.5 | 2090 | 92.0345 | 100.0824 | 108.8275 | 117.3316 | 125.871
| ThamesfordWind2095RCP8.5 | Thamesford | Wind | RCP8.5 | 2095 | 92.0345 | 100.0824 | 108.8275 | 117.3316 | 125.871
| ThamesfordWind2100RCP8.5 | Thamesford | Wind | RCP8.5 | 2100 | 92.0345 | 100.0824 | 108.8275 | 117.3316 | 125.871
| ThedfordIce Accretion2023RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2023 | 15.0637 | 18.0591 | 21.824 | 24.7108 | 27.5814
| ThedfordIce Accretion2025RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2025 | 15.079 | 18.0896 | 21.879 | 24.7813 | 27.6692
| ThedfordIce Accretion2030RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2030 | 15.0943 | 18.12 | 21.934 | 24.8517 | 27.757
| ThedfordIce Accretion2035RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2035 | 15.1096 | 18.1504 | 21.989 | 24.9221 | 27.8447
| ThedfordIce Accretion2040RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2040 | 15.1249 | 18.1809 | 22.044 | 24.9926 | 27.9325
| ThedfordIce Accretion2045RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2045 | 15.1402 | 18.2113 | 22.099 | 25.063 | 28.0203
| ThedfordIce Accretion2050RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2050 | 15.0943 | 18.1979 | 22.1276 | 25.1185 | 28.1081
| ThedfordIce Accretion2055RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2055 | 15.0331 | 18.1541 | 22.1012 | 25.1036 | 28.1081
| ThedfordIce Accretion2060RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2060 | 14.9718 | 18.1103 | 22.0748 | 25.0887 | 28.1081
| ThedfordIce Accretion2065RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2065 | 14.9106 | 18.0664 | 22.0484 | 25.0738 | 28.1081
| ThedfordIce Accretion2070RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2070 | 14.8494 | 18.0226 | 22.022 | 25.0589 | 28.1081
| ThedfordIce Accretion2075RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2075 | 14.8213 | 18.0104 | 22.033 | 25.0837 | 28.1497
| ThedfordIce Accretion2080RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2080 | 14.7932 | 17.9983 | 22.044 | 25.1086 | 28.1912
| ThedfordIce Accretion2085RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2085 | 14.7652 | 17.9861 | 22.055 | 25.1335 | 28.2328
| ThedfordIce Accretion2090RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2090 | 14.7371 | 17.9739 | 22.066 | 25.1583 | 28.2744
| ThedfordIce Accretion2095RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2095 | 14.709 | 17.9618 | 22.077 | 25.1832 | 28.316
| ThedfordIce Accretion2100RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2100 | 14.681 | 17.9496 | 22.088 | 25.208 | 28.3576
| ThedfordIce Accretion2023RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2023 | 15.0637 | 18.0591 | 21.824 | 24.7108 | 27.5814
| ThedfordIce Accretion2025RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2025 | 15.079 | 18.0896 | 21.879 | 24.7813 | 27.6692
| ThedfordIce Accretion2030RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2030 | 15.0943 | 18.12 | 21.934 | 24.8517 | 27.757
| ThedfordIce Accretion2035RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2035 | 15.1096 | 18.1504 | 21.989 | 24.9221 | 27.8447
| ThedfordIce Accretion2040RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2040 | 15.1249 | 18.1809 | 22.044 | 24.9926 | 27.9325
| ThedfordIce Accretion2045RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2045 | 15.1402 | 18.2113 | 22.099 | 25.063 | 28.0203
| ThedfordIce Accretion2050RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2050 | 15.0943 | 18.1979 | 22.1276 | 25.1185 | 28.1081
| ThedfordIce Accretion2055RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2055 | 15.0331 | 18.1541 | 22.1012 | 25.1036 | 28.1081
| ThedfordIce Accretion2060RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2060 | 14.9718 | 18.1103 | 22.0748 | 25.0887 | 28.1081
| ThedfordIce Accretion2065RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2065 | 14.9106 | 18.0664 | 22.0484 | 25.0738 | 28.1081
| ThedfordIce Accretion2070RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2070 | 14.8494 | 18.0226 | 22.022 | 25.0589 | 28.1081
| ThedfordIce Accretion2075RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2075 | 14.8073 | 18.0044 | 22.0385 | 25.0962 | 28.1704
| ThedfordIce Accretion2080RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2080 | 14.7652 | 17.9861 | 22.055 | 25.1335 | 28.2328
| ThedfordIce Accretion2085RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2085 | 14.7231 | 17.9678 | 22.0715 | 25.1707 | 28.2952
| ThedfordIce Accretion2090RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2090 | 14.4973 | 17.767 | 21.8973 | 25.0174 | 28.1543
| ThedfordIce Accretion2095RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2095 | 14.3136 | 17.5844 | 21.7067 | 24.8269 | 27.951
| ThedfordIce Accretion2100RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2100 | 14.1299 | 17.4018 | 21.516 | 24.6363 | 27.7477
| ThedfordIce Accretion2023RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2023 | 15.0637 | 18.0591 | 21.824 | 24.7108 | 27.5814
| ThedfordIce Accretion2025RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2025 | 15.0943 | 18.12 | 21.934 | 24.8517 | 27.757
| ThedfordIce Accretion2030RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2030 | 15.1249 | 18.1809 | 22.044 | 24.9926 | 27.9325
| ThedfordIce Accretion2035RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2035 | 15.1555 | 18.2417 | 22.154 | 25.1335 | 28.1081
| ThedfordIce Accretion2040RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2040 | 15.0535 | 18.1687 | 22.11 | 25.1086 | 28.1081
| ThedfordIce Accretion2045RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2045 | 14.9514 | 18.0957 | 22.066 | 25.0837 | 28.1081
| ThedfordIce Accretion2050RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2050 | 14.7932 | 17.9983 | 22.044 | 25.1086 | 28.1912
| ThedfordIce Accretion2055RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2055 | 14.7371 | 17.9739 | 22.066 | 25.1583 | 28.2744
| ThedfordIce Accretion2060RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2060 | 14.4973 | 17.767 | 21.8973 | 25.0174 | 28.1543
| ThedfordIce Accretion2065RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2065 | 14.3136 | 17.5844 | 21.7067 | 24.8269 | 27.951
| ThedfordIce Accretion2070RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2070 | 13.7982 | 17.0305 | 21.098 | 24.1805 | 27.2488
| ThedfordIce Accretion2075RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2075 | 13.4665 | 16.6592 | 20.68 | 23.7247 | 26.7498
| ThedfordIce Accretion2080RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2080 | 13.1348 | 16.2879 | 20.262 | 23.269 | 26.2508
| ThedfordIce Accretion2085RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2085 | 12.4459 | 15.4753 | 19.294 | 22.1875 | 25.0589
| ThedfordIce Accretion2090RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2090 | 11.757 | 14.6628 | 18.326 | 21.1061 | 23.8669
| ThedfordIce Accretion2095RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2095 | 11.757 | 14.6628 | 18.326 | 21.1061 | 23.8669
| ThedfordIce Accretion2100RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2100 | 11.757 | 14.6628 | 18.326 | 21.1061 | 23.8669
| ThedfordWind2023RCP4.5 | Thedford | Wind | RCP4.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| ThedfordWind2025RCP4.5 | Thedford | Wind | RCP4.5 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
| ThedfordWind2030RCP4.5 | Thedford | Wind | RCP4.5 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| ThedfordWind2035RCP4.5 | Thedford | Wind | RCP4.5 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
| ThedfordWind2040RCP4.5 | Thedford | Wind | RCP4.5 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| ThedfordWind2045RCP4.5 | Thedford | Wind | RCP4.5 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
| ThedfordWind2050RCP4.5 | Thedford | Wind | RCP4.5 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
| ThedfordWind2055RCP4.5 | Thedford | Wind | RCP4.5 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
| ThedfordWind2060RCP4.5 | Thedford | Wind | RCP4.5 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
| ThedfordWind2065RCP4.5 | Thedford | Wind | RCP4.5 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
| ThedfordWind2070RCP4.5 | Thedford | Wind | RCP4.5 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
| ThedfordWind2075RCP4.5 | Thedford | Wind | RCP4.5 | 2075 | 86.3504 | 93.3577 | 100.8387 | 108.226 | 115.6228
| ThedfordWind2080RCP4.5 | Thedford | Wind | RCP4.5 | 2080 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
| ThedfordWind2085RCP4.5 | Thedford | Wind | RCP4.5 | 2085 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
| ThedfordWind2090RCP4.5 | Thedford | Wind | RCP4.5 | 2090 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
| ThedfordWind2095RCP4.5 | Thedford | Wind | RCP4.5 | 2095 | 86.7678 | 93.9167 | 101.5705 | 109.1068 | 116.6655
| ThedfordWind2100RCP4.5 | Thedford | Wind | RCP4.5 | 2100 | 86.8722 | 94.0565 | 101.7534 | 109.327 | 116.9262
| ThedfordWind2023RCP6.0 | Thedford | Wind | RCP6.0 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| ThedfordWind2025RCP6.0 | Thedford | Wind | RCP6.0 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
| ThedfordWind2030RCP6.0 | Thedford | Wind | RCP6.0 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| ThedfordWind2035RCP6.0 | Thedford | Wind | RCP6.0 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
| ThedfordWind2040RCP6.0 | Thedford | Wind | RCP6.0 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| ThedfordWind2045RCP6.0 | Thedford | Wind | RCP6.0 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
| ThedfordWind2050RCP6.0 | Thedford | Wind | RCP6.0 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
| ThedfordWind2055RCP6.0 | Thedford | Wind | RCP6.0 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
| ThedfordWind2060RCP6.0 | Thedford | Wind | RCP6.0 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
| ThedfordWind2065RCP6.0 | Thedford | Wind | RCP6.0 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
| ThedfordWind2070RCP6.0 | Thedford | Wind | RCP6.0 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
| ThedfordWind2075RCP6.0 | Thedford | Wind | RCP6.0 | 2075 | 86.4026 | 93.4276 | 100.9302 | 108.3361 | 115.7531
| ThedfordWind2080RCP6.0 | Thedford | Wind | RCP6.0 | 2080 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
| ThedfordWind2085RCP6.0 | Thedford | Wind | RCP6.0 | 2085 | 86.7157 | 93.8469 | 101.479 | 108.9967 | 116.5351
| ThedfordWind2090RCP6.0 | Thedford | Wind | RCP6.0 | 2090 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
| ThedfordWind2095RCP6.0 | Thedford | Wind | RCP6.0 | 2095 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
| ThedfordWind2100RCP6.0 | Thedford | Wind | RCP6.0 | 2100 | 87.7861 | 95.1502 | 103.0568 | 110.8265 | 118.6131
| ThedfordWind2023RCP8.5 | Thedford | Wind | RCP8.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
| ThedfordWind2025RCP8.5 | Thedford | Wind | RCP8.5 | 2025 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
| ThedfordWind2030RCP8.5 | Thedford | Wind | RCP8.5 | 2030 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
| ThedfordWind2035RCP8.5 | Thedford | Wind | RCP8.5 | 2035 | 86.0768 | 93.0084 | 100.3912 | 107.7017 | 115.0269
| ThedfordWind2040RCP8.5 | Thedford | Wind | RCP8.5 | 2040 | 86.1332 | 93.0782 | 100.4794 | 107.8031 | 115.1386
| ThedfordWind2045RCP8.5 | Thedford | Wind | RCP8.5 | 2045 | 86.1896 | 93.1481 | 100.5676 | 107.9044 | 115.2504
| ThedfordWind2050RCP8.5 | Thedford | Wind | RCP8.5 | 2050 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
| ThedfordWind2055RCP8.5 | Thedford | Wind | RCP8.5 | 2055 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
| ThedfordWind2060RCP8.5 | Thedford | Wind | RCP8.5 | 2060 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
| ThedfordWind2065RCP8.5 | Thedford | Wind | RCP8.5 | 2065 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
| ThedfordWind2070RCP8.5 | Thedford | Wind | RCP8.5 | 2070 | 88.0541 | 95.5026 | 103.5207 | 111.3788 | 119.2611
| ThedfordWind2075RCP8.5 | Thedford | Wind | RCP8.5 | 2075 | 88.322 | 95.855 | 103.9845 | 111.9311 | 119.9091
| ThedfordWind2080RCP8.5 | Thedford | Wind | RCP8.5 | 2080 | 88.59 | 96.2074 | 104.4484 | 112.4833 | 120.5571
| ThedfordWind2085RCP8.5 | Thedford | Wind | RCP8.5 | 2085 | 88.9454 | 96.6585 | 105.0217 | 113.1649 | 121.3447
| ThedfordWind2090RCP8.5 | Thedford | Wind | RCP8.5 | 2090 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| ThedfordWind2095RCP8.5 | Thedford | Wind | RCP8.5 | 2095 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| ThedfordWind2100RCP8.5 | Thedford | Wind | RCP8.5 | 2100 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
| Thunder BayIce Accretion2023RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2023 | 11.7013 | 14.0104 | 16.928 | 19.1467 | 21.3696
| Thunder BayIce Accretion2025RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2025 | 11.6531 | 13.9551 | 16.8667 | 19.0804 | 21.2957
| Thunder BayIce Accretion2030RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2030 | 11.6049 | 13.8997 | 16.8053 | 19.0141 | 21.2218
| Thunder BayIce Accretion2035RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2035 | 11.5566 | 13.8444 | 16.744 | 18.9478 | 21.1478
| Thunder BayIce Accretion2040RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2040 | 11.5084 | 13.7891 | 16.6827 | 18.8815 | 21.0739
| Thunder BayIce Accretion2045RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2045 | 11.4601 | 13.7337 | 16.6213 | 18.8153 | 21
| Thunder BayIce Accretion2050RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2050 | 11.3762 | 13.6439 | 16.5248 | 18.7128 | 20.8938
| Thunder BayIce Accretion2055RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2055 | 11.3406 | 13.6093 | 16.4896 | 18.6766 | 20.8616
| Thunder BayIce Accretion2060RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2060 | 11.305 | 13.5748 | 16.4544 | 18.6405 | 20.8293
| Thunder BayIce Accretion2065RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2065 | 11.2694 | 13.5403 | 16.4192 | 18.6043 | 20.7971
| Thunder BayIce Accretion2070RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2070 | 11.2337 | 13.5058 | 16.384 | 18.5682 | 20.7648
| Thunder BayIce Accretion2075RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2075 | 11.2504 | 13.5323 | 16.4213 | 18.6134 | 20.8186
| Thunder BayIce Accretion2080RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2080 | 11.2671 | 13.5589 | 16.4587 | 18.6586 | 20.8723
| Thunder BayIce Accretion2085RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2085 | 11.2838 | 13.5854 | 16.496 | 18.7038 | 20.9261
| Thunder BayIce Accretion2090RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2090 | 11.3005 | 13.612 | 16.5333 | 18.749 | 20.9798
| Thunder BayIce Accretion2095RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2095 | 11.3172 | 13.6386 | 16.5707 | 18.7942 | 21.0336
| Thunder BayIce Accretion2100RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2100 | 11.3339 | 13.6651 | 16.608 | 18.8394 | 21.0874
| Thunder BayIce Accretion2023RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2023 | 11.7013 | 14.0104 | 16.928 | 19.1467 | 21.3696
| Thunder BayIce Accretion2025RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2025 | 11.6531 | 13.9551 | 16.8667 | 19.0804 | 21.2957
| Thunder BayIce Accretion2030RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2030 | 11.6049 | 13.8997 | 16.8053 | 19.0141 | 21.2218
| Thunder BayIce Accretion2035RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2035 | 11.5566 | 13.8444 | 16.744 | 18.9478 | 21.1478
| Thunder BayIce Accretion2040RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2040 | 11.5084 | 13.7891 | 16.6827 | 18.8815 | 21.0739
| Thunder BayIce Accretion2045RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2045 | 11.4601 | 13.7337 | 16.6213 | 18.8153 | 21
| Thunder BayIce Accretion2050RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2050 | 11.3762 | 13.6439 | 16.5248 | 18.7128 | 20.8938
| Thunder BayIce Accretion2055RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2055 | 11.3406 | 13.6093 | 16.4896 | 18.6766 | 20.8616
| Thunder BayIce Accretion2060RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2060 | 11.305 | 13.5748 | 16.4544 | 18.6405 | 20.8293
| Thunder BayIce Accretion2065RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2065 | 11.2694 | 13.5403 | 16.4192 | 18.6043 | 20.7971
| Thunder BayIce Accretion2070RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2070 | 11.2337 | 13.5058 | 16.384 | 18.5682 | 20.7648
| Thunder BayIce Accretion2075RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2075 | 11.2588 | 13.5456 | 16.44 | 18.636 | 20.8454
| Thunder BayIce Accretion2080RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2080 | 11.2838 | 13.5854 | 16.496 | 18.7038 | 20.9261
| Thunder BayIce Accretion2085RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2085 | 11.3089 | 13.6253 | 16.552 | 18.7716 | 21.0067
| Thunder BayIce Accretion2090RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2090 | 11.3005 | 13.6341 | 16.576 | 18.8092 | 21.0538
| Thunder BayIce Accretion2095RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2095 | 11.2671 | 13.6031 | 16.544 | 18.7791 | 21.0202
| Thunder BayIce Accretion2100RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2100 | 11.2337 | 13.5722 | 16.512 | 18.749 | 20.9866
| Thunder BayIce Accretion2023RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2023 | 11.7013 | 14.0104 | 16.928 | 19.1467 | 21.3696
| Thunder BayIce Accretion2025RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2025 | 11.6049 | 13.8997 | 16.8053 | 19.0141 | 21.2218
| Thunder BayIce Accretion2030RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2030 | 11.5084 | 13.7891 | 16.6827 | 18.8815 | 21.0739
| Thunder BayIce Accretion2035RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2035 | 11.4119 | 13.6784 | 16.56 | 18.749 | 20.9261
| Thunder BayIce Accretion2040RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2040 | 11.3525 | 13.6209 | 16.5013 | 18.6887 | 20.8723
| Thunder BayIce Accretion2045RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2045 | 11.2931 | 13.5633 | 16.4427 | 18.6284 | 20.8186
| Thunder BayIce Accretion2050RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2050 | 11.2671 | 13.5589 | 16.4587 | 18.6586 | 20.8723
| Thunder BayIce Accretion2055RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2055 | 11.3005 | 13.612 | 16.5333 | 18.749 | 20.9798
| Thunder BayIce Accretion2060RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2060 | 11.3005 | 13.6341 | 16.576 | 18.8092 | 21.0538
| Thunder BayIce Accretion2065RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2065 | 11.2671 | 13.6031 | 16.544 | 18.7791 | 21.0202
| Thunder BayIce Accretion2070RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2070 | 11.141 | 13.4659 | 16.3947 | 18.6224 | 20.8522
| Thunder BayIce Accretion2075RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2075 | 11.0482 | 13.3597 | 16.2773 | 18.4958 | 20.7178
| Thunder BayIce Accretion2080RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2080 | 10.9554 | 13.2534 | 16.16 | 18.3693 | 20.5834
| Thunder BayIce Accretion2085RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2085 | 10.6492 | 12.8949 | 15.736 | 17.8902 | 20.039
| Thunder BayIce Accretion2090RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2090 | 10.3431 | 12.5363 | 15.312 | 17.411 | 19.4947
| Thunder BayIce Accretion2095RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2095 | 10.3431 | 12.5363 | 15.312 | 17.411 | 19.4947
| Thunder BayIce Accretion2100RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2100 | 10.3431 | 12.5363 | 15.312 | 17.411 | 19.4947
| Thunder BayWind2023RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2023 | 81.2566 | 87.4987 | 94.0564 | 100.6202 | 107.1814
| Thunder BayWind2025RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2025 | 81.3175 | 87.5672 | 94.1363 | 100.7108 | 107.2814
| Thunder BayWind2030RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2030 | 81.3784 | 87.6356 | 94.2162 | 100.8013 | 107.3815
| Thunder BayWind2035RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2035 | 81.4393 | 87.7041 | 94.2961 | 100.8918 | 107.4815
| Thunder BayWind2040RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2040 | 81.5001 | 87.7726 | 94.376 | 100.9823 | 107.5815
| Thunder BayWind2045RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2045 | 81.561 | 87.8411 | 94.4559 | 101.0728 | 107.6815
| Thunder BayWind2050RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2050 | 81.7566 | 88.0739 | 94.7351 | 101.3927 | 108.043
| Thunder BayWind2055RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2055 | 81.8914 | 88.2383 | 94.9344 | 101.622 | 108.3045
| Thunder BayWind2060RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2060 | 82.0261 | 88.4026 | 95.1336 | 101.8513 | 108.5659
| Thunder BayWind2065RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2065 | 82.1608 | 88.567 | 95.3329 | 102.0807 | 108.8274
| Thunder BayWind2070RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2070 | 82.2956 | 88.7313 | 95.5322 | 102.31 | 109.0889
| Thunder BayWind2075RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2075 | 82.3835 | 88.8333 | 95.6481 | 102.4391 | 109.2318
| Thunder BayWind2080RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2080 | 82.4714 | 88.9353 | 95.7641 | 102.5681 | 109.3746
| Thunder BayWind2085RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2085 | 82.5594 | 89.0373 | 95.88 | 102.6972 | 109.5175
| Thunder BayWind2090RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2090 | 82.6473 | 89.1393 | 95.9959 | 102.8263 | 109.6604
| Thunder BayWind2095RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2095 | 82.7352 | 89.2413 | 96.1119 | 102.9554 | 109.8033
| Thunder BayWind2100RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2100 | 82.8232 | 89.3432 | 96.2278 | 103.0844 | 109.9462
| Thunder BayWind2023RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2023 | 81.2566 | 87.4987 | 94.0564 | 100.6202 | 107.1814
| Thunder BayWind2025RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2025 | 81.3175 | 87.5672 | 94.1363 | 100.7108 | 107.2814
| Thunder BayWind2030RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2030 | 81.3784 | 87.6356 | 94.2162 | 100.8013 | 107.3815
| Thunder BayWind2035RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2035 | 81.4393 | 87.7041 | 94.2961 | 100.8918 | 107.4815
| Thunder BayWind2040RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2040 | 81.5001 | 87.7726 | 94.376 | 100.9823 | 107.5815
| Thunder BayWind2045RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2045 | 81.561 | 87.8411 | 94.4559 | 101.0728 | 107.6815
| Thunder BayWind2050RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2050 | 81.7566 | 88.0739 | 94.7351 | 101.3927 | 108.043
| Thunder BayWind2055RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2055 | 81.8914 | 88.2383 | 94.9344 | 101.622 | 108.3045
| Thunder BayWind2060RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2060 | 82.0261 | 88.4026 | 95.1336 | 101.8513 | 108.5659
| Thunder BayWind2065RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2065 | 82.1608 | 88.567 | 95.3329 | 102.0807 | 108.8274
| Thunder BayWind2070RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2070 | 82.2956 | 88.7313 | 95.5322 | 102.31 | 109.0889
| Thunder BayWind2075RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2075 | 82.4275 | 88.8843 | 95.7061 | 102.5036 | 109.3032
| Thunder BayWind2080RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2080 | 82.5594 | 89.0373 | 95.88 | 102.6972 | 109.5175
| Thunder BayWind2085RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2085 | 82.6913 | 89.1903 | 96.0539 | 102.8908 | 109.7318
| Thunder BayWind2090RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2090 | 83.0423 | 89.6084 | 96.5537 | 103.4599 | 110.3712
| Thunder BayWind2095RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2095 | 83.2615 | 89.8736 | 96.8795 | 103.8354 | 110.7963
| Thunder BayWind2100RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2100 | 83.4806 | 90.1388 | 97.2054 | 104.2109 | 111.2214
| Thunder BayWind2023RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2023 | 81.2566 | 87.4987 | 94.0564 | 100.6202 | 107.1814
| Thunder BayWind2025RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2025 | 81.3784 | 87.6356 | 94.2162 | 100.8013 | 107.3815
| Thunder BayWind2030RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2030 | 81.5001 | 87.7726 | 94.376 | 100.9823 | 107.5815
| Thunder BayWind2035RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2035 | 81.6219 | 87.9096 | 94.5358 | 101.1634 | 107.7815
| Thunder BayWind2040RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2040 | 81.8464 | 88.1835 | 94.8679 | 101.5456 | 108.2173
| Thunder BayWind2045RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2045 | 82.071 | 88.4574 | 95.2001 | 101.9278 | 108.6531
| Thunder BayWind2050RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2050 | 82.4714 | 88.9353 | 95.7641 | 102.5681 | 109.3746
| Thunder BayWind2055RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2055 | 82.6473 | 89.1393 | 95.9959 | 102.8263 | 109.6604
| Thunder BayWind2060RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2060 | 83.0423 | 89.6084 | 96.5537 | 103.4599 | 110.3712
| Thunder BayWind2065RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2065 | 83.2615 | 89.8736 | 96.8795 | 103.8354 | 110.7963
| Thunder BayWind2070RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2070 | 83.6132 | 90.2874 | 97.3683 | 104.392 | 111.4178
| Thunder BayWind2075RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2075 | 83.7458 | 90.436 | 97.5313 | 104.573 | 111.6143
| Thunder BayWind2080RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2080 | 83.8783 | 90.5846 | 97.6942 | 104.7541 | 111.8107
| Thunder BayWind2085RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2085 | 84.1218 | 90.8687 | 98.0373 | 105.1413 | 112.2501
| Thunder BayWind2090RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2090 | 84.3653 | 91.1528 | 98.3804 | 105.5285 | 112.6895
| Thunder BayWind2095RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2095 | 84.3653 | 91.1528 | 98.3804 | 105.5285 | 112.6895
| Thunder BayWind2100RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2100 | 84.3653 | 91.1528 | 98.3804 | 105.5285 | 112.6895
| TillsonburgIce Accretion2023RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
| TillsonburgIce Accretion2025RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2025 | 22.9175 | 27.5192 | 33.3427 | 37.7989 | 42.2402
| TillsonburgIce Accretion2030RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2030 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
| TillsonburgIce Accretion2035RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2035 | 22.6651 | 27.2464 | 33.048 | 37.4787 | 41.8975
| TillsonburgIce Accretion2040RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2040 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
| TillsonburgIce Accretion2045RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2045 | 22.4127 | 26.9736 | 32.7533 | 37.1585 | 41.5548
| TillsonburgIce Accretion2050RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2050 | 21.7945 | 26.2954 | 31.9872 | 36.3223 | 40.6466
| TillsonburgIce Accretion2055RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2055 | 21.3024 | 25.7536 | 31.3684 | 35.6461 | 39.9097
| TillsonburgIce Accretion2060RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2060 | 20.8103 | 25.2117 | 30.7496 | 34.9699 | 39.1729
| TillsonburgIce Accretion2065RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2065 | 20.3181 | 24.6699 | 30.1308 | 34.2937 | 38.436
| TillsonburgIce Accretion2070RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2070 | 19.826 | 24.1281 | 29.512 | 33.6175 | 37.6992
| TillsonburgIce Accretion2075RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2075 | 19.5895 | 23.8647 | 29.2117 | 33.2909 | 37.3422
| TillsonburgIce Accretion2080RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2080 | 19.3529 | 23.6013 | 28.9113 | 32.9644 | 36.9852
| TillsonburgIce Accretion2085RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2085 | 19.1163 | 23.3379 | 28.611 | 32.6378 | 36.6282
| TillsonburgIce Accretion2090RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2090 | 18.8797 | 23.0746 | 28.3107 | 32.3112 | 36.2712
| TillsonburgIce Accretion2095RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2095 | 18.6431 | 22.8112 | 28.0103 | 31.9846 | 35.9142
| TillsonburgIce Accretion2100RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2100 | 18.4065 | 22.5478 | 27.71 | 31.6581 | 35.5572
| TillsonburgIce Accretion2023RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
| TillsonburgIce Accretion2025RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2025 | 22.9175 | 27.5192 | 33.3427 | 37.7989 | 42.2402
| TillsonburgIce Accretion2030RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2030 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
| TillsonburgIce Accretion2035RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2035 | 22.6651 | 27.2464 | 33.048 | 37.4787 | 41.8975
| TillsonburgIce Accretion2040RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2040 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
| TillsonburgIce Accretion2045RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2045 | 22.4127 | 26.9736 | 32.7533 | 37.1585 | 41.5548
| TillsonburgIce Accretion2050RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2050 | 21.7945 | 26.2954 | 31.9872 | 36.3223 | 40.6466
| TillsonburgIce Accretion2055RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2055 | 21.3024 | 25.7536 | 31.3684 | 35.6461 | 39.9097
| TillsonburgIce Accretion2060RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2060 | 20.8103 | 25.2117 | 30.7496 | 34.9699 | 39.1729
| TillsonburgIce Accretion2065RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2065 | 20.3181 | 24.6699 | 30.1308 | 34.2937 | 38.436
| TillsonburgIce Accretion2070RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2070 | 19.826 | 24.1281 | 29.512 | 33.6175 | 37.6992
| TillsonburgIce Accretion2075RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2075 | 19.4712 | 23.733 | 29.0615 | 33.1276 | 37.1637
| TillsonburgIce Accretion2080RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2080 | 19.1163 | 23.3379 | 28.611 | 32.6378 | 36.6282
| TillsonburgIce Accretion2085RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2085 | 18.7614 | 22.9429 | 28.1605 | 32.1479 | 36.0927
| TillsonburgIce Accretion2090RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2090 | 17.4365 | 21.4002 | 26.3613 | 30.1341 | 33.8722
| TillsonburgIce Accretion2095RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2095 | 16.4665 | 20.2526 | 25.0127 | 28.6101 | 32.1871
| TillsonburgIce Accretion2100RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2100 | 15.4965 | 19.1049 | 23.664 | 27.0861 | 30.5021
| TillsonburgIce Accretion2023RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
| TillsonburgIce Accretion2025RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2025 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
| TillsonburgIce Accretion2030RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2030 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
| TillsonburgIce Accretion2035RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2035 | 22.2866 | 26.8372 | 32.606 | 36.9985 | 41.3834
| TillsonburgIce Accretion2040RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2040 | 21.4664 | 25.9342 | 31.5747 | 35.8715 | 40.1554
| TillsonburgIce Accretion2045RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2045 | 20.6462 | 25.0311 | 30.5433 | 34.7445 | 38.9273
| TillsonburgIce Accretion2050RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2050 | 19.3529 | 23.6013 | 28.9113 | 32.9644 | 36.9852
| TillsonburgIce Accretion2055RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2055 | 18.8797 | 23.0746 | 28.3107 | 32.3112 | 36.2712
| TillsonburgIce Accretion2060RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2060 | 17.4365 | 21.4002 | 26.3613 | 30.1341 | 33.8722
| TillsonburgIce Accretion2065RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2065 | 16.4665 | 20.2526 | 25.0127 | 28.6101 | 32.1871
| TillsonburgIce Accretion2070RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2070 | 15.0312 | 18.5876 | 23.052 | 26.4073 | 29.7595
| TillsonburgIce Accretion2075RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2075 | 14.5659 | 18.0702 | 22.44 | 25.7286 | 29.017
| TillsonburgIce Accretion2080RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2080 | 14.1006 | 17.5528 | 21.828 | 25.0498 | 28.2744
| TillsonburgIce Accretion2085RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2085 | 13.0596 | 16.297 | 20.332 | 23.3594 | 26.3894
| TillsonburgIce Accretion2090RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2090 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
| TillsonburgIce Accretion2095RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2095 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
| TillsonburgIce Accretion2100RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2100 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
| TillsonburgWind2023RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2023 | 87.7786 | 94.6439 | 101.8888 | 109.1075 | 116.3375
| TillsonburgWind2025RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2025 | 87.8542 | 94.7441 | 102.0218 | 109.2696 | 116.5255
| TillsonburgWind2030RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2030 | 87.9298 | 94.8443 | 102.1548 | 109.4317 | 116.7136
| TillsonburgWind2035RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2035 | 88.0054 | 94.9444 | 102.2877 | 109.5938 | 116.9016
| TillsonburgWind2040RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2040 | 88.0809 | 95.0446 | 102.4207 | 109.7559 | 117.0897
| TillsonburgWind2045RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2045 | 88.1565 | 95.1448 | 102.5537 | 109.918 | 117.2778
| TillsonburgWind2050RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2050 | 88.3106 | 95.3502 | 102.8261 | 110.2465 | 117.6639
| TillsonburgWind2055RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2055 | 88.3891 | 95.4554 | 102.9655 | 110.413 | 117.8619
| TillsonburgWind2060RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2060 | 88.4676 | 95.5606 | 103.1048 | 110.5794 | 118.06
| TillsonburgWind2065RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2065 | 88.5461 | 95.6658 | 103.2442 | 110.7458 | 118.258
| TillsonburgWind2070RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2070 | 88.6246 | 95.771 | 103.3836 | 110.9122 | 118.456
| TillsonburgWind2075RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2075 | 88.7437 | 95.9244 | 103.5806 | 111.1464 | 118.7304
| TillsonburgWind2080RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2080 | 88.8629 | 96.0779 | 103.7775 | 111.3805 | 119.0049
| TillsonburgWind2085RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2085 | 88.9821 | 96.2313 | 103.9744 | 111.6147 | 119.2793
| TillsonburgWind2090RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2090 | 89.1013 | 96.3847 | 104.1714 | 111.8488 | 119.5537
| TillsonburgWind2095RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2095 | 89.2205 | 96.5381 | 104.3683 | 112.083 | 119.8281
| TillsonburgWind2100RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2100 | 89.3397 | 96.6915 | 104.5653 | 112.3172 | 120.1025
| TillsonburgWind2023RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2023 | 87.7786 | 94.6439 | 101.8888 | 109.1075 | 116.3375
| TillsonburgWind2025RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2025 | 87.8542 | 94.7441 | 102.0218 | 109.2696 | 116.5255
| TillsonburgWind2030RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2030 | 87.9298 | 94.8443 | 102.1548 | 109.4317 | 116.7136
| TillsonburgWind2035RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2035 | 88.0054 | 94.9444 | 102.2877 | 109.5938 | 116.9016
| TillsonburgWind2040RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2040 | 88.0809 | 95.0446 | 102.4207 | 109.7559 | 117.0897
| TillsonburgWind2045RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2045 | 88.1565 | 95.1448 | 102.5537 | 109.918 | 117.2778
| TillsonburgWind2050RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2050 | 88.3106 | 95.3502 | 102.8261 | 110.2465 | 117.6639
| TillsonburgWind2055RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2055 | 88.3891 | 95.4554 | 102.9655 | 110.413 | 117.8619
| TillsonburgWind2060RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2060 | 88.4676 | 95.5606 | 103.1048 | 110.5794 | 118.06
| TillsonburgWind2065RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2065 | 88.5461 | 95.6658 | 103.2442 | 110.7458 | 118.258
| TillsonburgWind2070RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2070 | 88.6246 | 95.771 | 103.3836 | 110.9122 | 118.456
| TillsonburgWind2075RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2075 | 88.8033 | 96.0012 | 103.679 | 111.2635 | 118.8677
| TillsonburgWind2080RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2080 | 88.9821 | 96.2313 | 103.9744 | 111.6147 | 119.2793
| TillsonburgWind2085RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2085 | 89.1609 | 96.4614 | 104.2699 | 111.9659 | 119.6909
| TillsonburgWind2090RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2090 | 89.5955 | 97.0234 | 104.9861 | 112.8179 | 120.6782
| TillsonburgWind2095RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2095 | 89.8513 | 97.3553 | 105.407 | 113.3186 | 121.2539
| TillsonburgWind2100RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2100 | 90.1072 | 97.6872 | 105.8278 | 113.8193 | 121.8296
| TillsonburgWind2023RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2023 | 87.7786 | 94.6439 | 101.8888 | 109.1075 | 116.3375
| TillsonburgWind2025RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2025 | 87.9298 | 94.8443 | 102.1548 | 109.4317 | 116.7136
| TillsonburgWind2030RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2030 | 88.0809 | 95.0446 | 102.4207 | 109.7559 | 117.0897
| TillsonburgWind2035RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2035 | 88.2321 | 95.245 | 102.6867 | 110.0801 | 117.4658
| TillsonburgWind2040RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2040 | 88.3629 | 95.4204 | 102.919 | 110.3575 | 117.7959
| TillsonburgWind2045RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2045 | 88.4937 | 95.5957 | 103.1513 | 110.6349 | 118.126
| TillsonburgWind2050RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2050 | 88.8629 | 96.0779 | 103.7775 | 111.3805 | 119.0049
| TillsonburgWind2055RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2055 | 89.1013 | 96.3847 | 104.1714 | 111.8488 | 119.5537
| TillsonburgWind2060RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2060 | 89.5955 | 97.0234 | 104.9861 | 112.8179 | 120.6782
| TillsonburgWind2065RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2065 | 89.8513 | 97.3553 | 105.407 | 113.3186 | 121.2539
| TillsonburgWind2070RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2070 | 90.2554 | 97.897 | 106.1173 | 114.176 | 122.2557
| TillsonburgWind2075RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2075 | 90.4037 | 98.1068 | 106.4069 | 114.5326 | 122.6817
| TillsonburgWind2080RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2080 | 90.5519 | 98.3165 | 106.6964 | 114.8892 | 123.1077
| TillsonburgWind2085RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2085 | 90.8921 | 98.7627 | 107.2873 | 115.5917 | 123.9367
| TillsonburgWind2090RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2090 | 91.2322 | 99.2089 | 107.8781 | 116.2941 | 124.7657
| TillsonburgWind2095RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2095 | 91.2322 | 99.2089 | 107.8781 | 116.2941 | 124.7657
| TillsonburgWind2100RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2100 | 91.2322 | 99.2089 | 107.8781 | 116.2941 | 124.7657
| TimminsIce Accretion2023RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2023 | 13.2211 | 15.7069 | 18.867 | 21.2982 | 23.7006
| TimminsIce Accretion2025RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2025 | 13.2057 | 15.6885 | 18.8448 | 21.2696 | 23.6727
| TimminsIce Accretion2030RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2030 | 13.1902 | 15.6701 | 18.8227 | 21.241 | 23.6447
| TimminsIce Accretion2035RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2035 | 13.1748 | 15.6517 | 18.8005 | 21.2124 | 23.6168
| TimminsIce Accretion2040RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2040 | 13.1594 | 15.6333 | 18.7783 | 21.1837 | 23.5889
| TimminsIce Accretion2045RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2045 | 13.144 | 15.6149 | 18.7562 | 21.1551 | 23.561
| TimminsIce Accretion2050RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2050 | 13.2343 | 15.7353 | 18.9126 | 21.3369 | 23.7724
| TimminsIce Accretion2055RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2055 | 13.3401 | 15.8741 | 19.0912 | 21.5473 | 24.0118
| TimminsIce Accretion2060RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2060 | 13.4458 | 16.0129 | 19.2698 | 21.7577 | 24.2512
| TimminsIce Accretion2065RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2065 | 13.5516 | 16.1516 | 19.4484 | 21.9681 | 24.4906
| TimminsIce Accretion2070RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2070 | 13.6574 | 16.2904 | 19.627 | 22.1785 | 24.73
| TimminsIce Accretion2075RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2075 | 13.686 | 16.3272 | 19.6713 | 22.2322 | 24.7899
| TimminsIce Accretion2080RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2080 | 13.7147 | 16.364 | 19.7157 | 22.2859 | 24.8497
| TimminsIce Accretion2085RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2085 | 13.7433 | 16.4008 | 19.76 | 22.3395 | 24.9096
| TimminsIce Accretion2090RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2090 | 13.772 | 16.4376 | 19.8043 | 22.3932 | 24.9694
| TimminsIce Accretion2095RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2095 | 13.8006 | 16.4744 | 19.8487 | 22.4469 | 25.0293
| TimminsIce Accretion2100RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2100 | 13.8292 | 16.5112 | 19.893 | 22.5006 | 25.0891
| TimminsIce Accretion2023RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2023 | 13.2211 | 15.7069 | 18.867 | 21.2982 | 23.7006
| TimminsIce Accretion2025RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2025 | 13.2057 | 15.6885 | 18.8448 | 21.2696 | 23.6727
| TimminsIce Accretion2030RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2030 | 13.1902 | 15.6701 | 18.8227 | 21.241 | 23.6447
| TimminsIce Accretion2035RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2035 | 13.1748 | 15.6517 | 18.8005 | 21.2124 | 23.6168
| TimminsIce Accretion2040RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2040 | 13.1594 | 15.6333 | 18.7783 | 21.1837 | 23.5889
| TimminsIce Accretion2045RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2045 | 13.144 | 15.6149 | 18.7562 | 21.1551 | 23.561
| TimminsIce Accretion2050RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2050 | 13.2343 | 15.7353 | 18.9126 | 21.3369 | 23.7724
| TimminsIce Accretion2055RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2055 | 13.3401 | 15.8741 | 19.0912 | 21.5473 | 24.0118
| TimminsIce Accretion2060RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2060 | 13.4458 | 16.0129 | 19.2698 | 21.7577 | 24.2512
| TimminsIce Accretion2065RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2065 | 13.5516 | 16.1516 | 19.4484 | 21.9681 | 24.4906
| TimminsIce Accretion2070RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2070 | 13.6574 | 16.2904 | 19.627 | 22.1785 | 24.73
| TimminsIce Accretion2075RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2075 | 13.7003 | 16.3456 | 19.6935 | 22.259 | 24.8198
| TimminsIce Accretion2080RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2080 | 13.7433 | 16.4008 | 19.76 | 22.3395 | 24.9096
| TimminsIce Accretion2085RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2085 | 13.7863 | 16.456 | 19.8265 | 22.42 | 24.9993
| TimminsIce Accretion2090RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2090 | 13.7499 | 16.4323 | 19.817 | 22.4218 | 25.0093
| TimminsIce Accretion2095RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2095 | 13.6706 | 16.3535 | 19.741 | 22.3431 | 24.9295
| TimminsIce Accretion2100RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2100 | 13.5913 | 16.2746 | 19.665 | 22.2644 | 24.8497
| TimminsIce Accretion2023RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2023 | 13.2211 | 15.7069 | 18.867 | 21.2982 | 23.7006
| TimminsIce Accretion2025RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2025 | 13.1902 | 15.6701 | 18.8227 | 21.241 | 23.6447
| TimminsIce Accretion2030RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2030 | 13.1594 | 15.6333 | 18.7783 | 21.1837 | 23.5889
| TimminsIce Accretion2035RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2035 | 13.1285 | 15.5965 | 18.734 | 21.1265 | 23.533
| TimminsIce Accretion2040RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2040 | 13.3048 | 15.8278 | 19.0317 | 21.4772 | 23.932
| TimminsIce Accretion2045RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2045 | 13.4811 | 16.0591 | 19.3293 | 21.8278 | 24.331
| TimminsIce Accretion2050RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2050 | 13.7147 | 16.364 | 19.7157 | 22.2859 | 24.8497
| TimminsIce Accretion2055RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2055 | 13.772 | 16.4376 | 19.8043 | 22.3932 | 24.9694
| TimminsIce Accretion2060RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2060 | 13.7499 | 16.4323 | 19.817 | 22.4218 | 25.0093
| TimminsIce Accretion2065RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2065 | 13.6706 | 16.3535 | 19.741 | 22.3431 | 24.9295
| TimminsIce Accretion2070RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2070 | 13.534 | 16.2116 | 19.6017 | 22.1928 | 24.7779
| TimminsIce Accretion2075RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2075 | 13.4767 | 16.1485 | 19.5383 | 22.1213 | 24.7061
| TimminsIce Accretion2080RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2080 | 13.4194 | 16.0854 | 19.475 | 22.0497 | 24.6343
| TimminsIce Accretion2085RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2085 | 13.3731 | 16.0854 | 19.5225 | 22.1356 | 24.754
| TimminsIce Accretion2090RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2090 | 13.3268 | 16.0854 | 19.57 | 22.2214 | 24.8737
| TimminsIce Accretion2095RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2095 | 13.3268 | 16.0854 | 19.57 | 22.2214 | 24.8737
| TimminsIce Accretion2100RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2100 | 13.3268 | 16.0854 | 19.57 | 22.2214 | 24.8737
| TimminsWind2023RCP4.5 | Timmins | Wind | RCP4.5 | 2023 | 74.1446 | 79.9195 | 86.003 | 92.0687 | 98.15
| TimminsWind2025RCP4.5 | Timmins | Wind | RCP4.5 | 2025 | 74.1471 | 79.9103 | 85.9803 | 92.0353 | 98.1032
| TimminsWind2030RCP4.5 | Timmins | Wind | RCP4.5 | 2030 | 74.1495 | 79.9011 | 85.9577 | 92.002 | 98.0563
| TimminsWind2035RCP4.5 | Timmins | Wind | RCP4.5 | 2035 | 74.152 | 79.8919 | 85.935 | 91.9686 | 98.0095
| TimminsWind2040RCP4.5 | Timmins | Wind | RCP4.5 | 2040 | 74.1544 | 79.8827 | 85.9123 | 91.9353 | 97.9627
| TimminsWind2045RCP4.5 | Timmins | Wind | RCP4.5 | 2045 | 74.1569 | 79.8734 | 85.8897 | 91.9019 | 97.9158
| TimminsWind2050RCP4.5 | Timmins | Wind | RCP4.5 | 2050 | 74.1784 | 79.8895 | 85.901 | 91.9086 | 97.9174
| TimminsWind2055RCP4.5 | Timmins | Wind | RCP4.5 | 2055 | 74.1975 | 79.9148 | 85.935 | 91.9486 | 97.9659
| TimminsWind2060RCP4.5 | Timmins | Wind | RCP4.5 | 2060 | 74.2166 | 79.9401 | 85.969 | 91.9886 | 98.0143
| TimminsWind2065RCP4.5 | Timmins | Wind | RCP4.5 | 2065 | 74.2357 | 79.9654 | 86.003 | 92.0287 | 98.0628
| TimminsWind2070RCP4.5 | Timmins | Wind | RCP4.5 | 2070 | 74.2547 | 79.9907 | 86.037 | 92.0687 | 98.1112
| TimminsWind2075RCP4.5 | Timmins | Wind | RCP4.5 | 2075 | 74.3024 | 80.0355 | 86.0767 | 92.1051 | 98.1435
| TimminsWind2080RCP4.5 | Timmins | Wind | RCP4.5 | 2080 | 74.3502 | 80.0803 | 86.1163 | 92.1414 | 98.1758
| TimminsWind2085RCP4.5 | Timmins | Wind | RCP4.5 | 2085 | 74.3979 | 80.1251 | 86.156 | 92.1778 | 98.2081
| TimminsWind2090RCP4.5 | Timmins | Wind | RCP4.5 | 2090 | 74.4456 | 80.1699 | 86.1957 | 92.2142 | 98.2404
| TimminsWind2095RCP4.5 | Timmins | Wind | RCP4.5 | 2095 | 74.4933 | 80.2147 | 86.2353 | 92.2506 | 98.2727
| TimminsWind2100RCP4.5 | Timmins | Wind | RCP4.5 | 2100 | 74.541 | 80.2595 | 86.275 | 92.287 | 98.305
| TimminsWind2023RCP6.0 | Timmins | Wind | RCP6.0 | 2023 | 74.1446 | 79.9195 | 86.003 | 92.0687 | 98.15
| TimminsWind2025RCP6.0 | Timmins | Wind | RCP6.0 | 2025 | 74.1471 | 79.9103 | 85.9803 | 92.0353 | 98.1032
| TimminsWind2030RCP6.0 | Timmins | Wind | RCP6.0 | 2030 | 74.1495 | 79.9011 | 85.9577 | 92.002 | 98.0563
| TimminsWind2035RCP6.0 | Timmins | Wind | RCP6.0 | 2035 | 74.152 | 79.8919 | 85.935 | 91.9686 | 98.0095
| TimminsWind2040RCP6.0 | Timmins | Wind | RCP6.0 | 2040 | 74.1544 | 79.8827 | 85.9123 | 91.9353 | 97.9627
| TimminsWind2045RCP6.0 | Timmins | Wind | RCP6.0 | 2045 | 74.1569 | 79.8734 | 85.8897 | 91.9019 | 97.9158
| TimminsWind2050RCP6.0 | Timmins | Wind | RCP6.0 | 2050 | 74.1784 | 79.8895 | 85.901 | 91.9086 | 97.9174
| TimminsWind2055RCP6.0 | Timmins | Wind | RCP6.0 | 2055 | 74.1975 | 79.9148 | 85.935 | 91.9486 | 97.9659
| TimminsWind2060RCP6.0 | Timmins | Wind | RCP6.0 | 2060 | 74.2166 | 79.9401 | 85.969 | 91.9886 | 98.0143
| TimminsWind2065RCP6.0 | Timmins | Wind | RCP6.0 | 2065 | 74.2357 | 79.9654 | 86.003 | 92.0287 | 98.0628
| TimminsWind2070RCP6.0 | Timmins | Wind | RCP6.0 | 2070 | 74.2547 | 79.9907 | 86.037 | 92.0687 | 98.1112
| TimminsWind2075RCP6.0 | Timmins | Wind | RCP6.0 | 2075 | 74.3263 | 80.0579 | 86.0965 | 92.1233 | 98.1597
| TimminsWind2080RCP6.0 | Timmins | Wind | RCP6.0 | 2080 | 74.3979 | 80.1251 | 86.156 | 92.1778 | 98.2081
| TimminsWind2085RCP6.0 | Timmins | Wind | RCP6.0 | 2085 | 74.4694 | 80.1923 | 86.2155 | 92.2324 | 98.2566
| TimminsWind2090RCP6.0 | Timmins | Wind | RCP6.0 | 2090 | 74.6755 | 80.4018 | 86.4252 | 92.4507 | 98.4762
| TimminsWind2095RCP6.0 | Timmins | Wind | RCP6.0 | 2095 | 74.8101 | 80.544 | 86.5753 | 92.6144 | 98.6474
| TimminsWind2100RCP6.0 | Timmins | Wind | RCP6.0 | 2100 | 74.9447 | 80.6863 | 86.7255 | 92.7781 | 98.8186
| TimminsWind2023RCP8.5 | Timmins | Wind | RCP8.5 | 2023 | 74.1446 | 79.9195 | 86.003 | 92.0687 | 98.15
| TimminsWind2025RCP8.5 | Timmins | Wind | RCP8.5 | 2025 | 74.1495 | 79.9011 | 85.9577 | 92.002 | 98.0563
| TimminsWind2030RCP8.5 | Timmins | Wind | RCP8.5 | 2030 | 74.1544 | 79.8827 | 85.9123 | 91.9353 | 97.9627
| TimminsWind2035RCP8.5 | Timmins | Wind | RCP8.5 | 2035 | 74.1593 | 79.8642 | 85.867 | 91.8686 | 97.869
| TimminsWind2040RCP8.5 | Timmins | Wind | RCP8.5 | 2040 | 74.1911 | 79.9064 | 85.9237 | 91.9353 | 97.9497
| TimminsWind2045RCP8.5 | Timmins | Wind | RCP8.5 | 2045 | 74.2229 | 79.9485 | 85.9803 | 92.002 | 98.0305
| TimminsWind2050RCP8.5 | Timmins | Wind | RCP8.5 | 2050 | 74.3502 | 80.0803 | 86.1163 | 92.1414 | 98.1758
| TimminsWind2055RCP8.5 | Timmins | Wind | RCP8.5 | 2055 | 74.4456 | 80.1699 | 86.1957 | 92.2142 | 98.2404
| TimminsWind2060RCP8.5 | Timmins | Wind | RCP8.5 | 2060 | 74.6755 | 80.4018 | 86.4252 | 92.4507 | 98.4762
| TimminsWind2065RCP8.5 | Timmins | Wind | RCP8.5 | 2065 | 74.8101 | 80.544 | 86.5753 | 92.6144 | 98.6474
| TimminsWind2070RCP8.5 | Timmins | Wind | RCP8.5 | 2070 | 75.1282 | 80.884 | 86.938 | 93.0024 | 99.0576
| TimminsWind2075RCP8.5 | Timmins | Wind | RCP8.5 | 2075 | 75.3116 | 81.0816 | 87.1505 | 93.2268 | 99.2967
| TimminsWind2080RCP8.5 | Timmins | Wind | RCP8.5 | 2080 | 75.4951 | 81.2792 | 87.363 | 93.4511 | 99.5357
| TimminsWind2085RCP8.5 | Timmins | Wind | RCP8.5 | 2085 | 75.5612 | 81.3622 | 87.4607 | 93.5603 | 99.6616
| TimminsWind2090RCP8.5 | Timmins | Wind | RCP8.5 | 2090 | 75.6272 | 81.4452 | 87.5585 | 93.6694 | 99.7876
| TimminsWind2095RCP8.5 | Timmins | Wind | RCP8.5 | 2095 | 75.6272 | 81.4452 | 87.5585 | 93.6694 | 99.7876
| TimminsWind2100RCP8.5 | Timmins | Wind | RCP8.5 | 2100 | 75.6272 | 81.4452 | 87.5585 | 93.6694 | 99.7876
| Timmins (Porcupine)Ice Accretion2023RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2023 | 13.1682 | 15.6596 | 18.829 | 21.2553 | 23.6767
| Timmins (Porcupine)Ice Accretion2025RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2025 | 13.2189 | 15.7227 | 18.9082 | 21.3448 | 23.7764
| Timmins (Porcupine)Ice Accretion2030RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2030 | 13.2696 | 15.7858 | 18.9873 | 21.4342 | 23.8762
| Timmins (Porcupine)Ice Accretion2035RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2035 | 13.3202 | 15.8488 | 19.0665 | 21.5237 | 23.9759
| Timmins (Porcupine)Ice Accretion2040RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2040 | 13.3709 | 15.9119 | 19.1457 | 21.6131 | 24.0757
| Timmins (Porcupine)Ice Accretion2045RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2045 | 13.4216 | 15.975 | 19.2248 | 21.7026 | 24.1754
| Timmins (Porcupine)Ice Accretion2050RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2050 | 13.5516 | 16.1422 | 19.437 | 21.9509 | 24.4571
| Timmins (Porcupine)Ice Accretion2055RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2055 | 13.6309 | 16.2463 | 19.57 | 22.1098 | 24.639
| Timmins (Porcupine)Ice Accretion2060RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2060 | 13.7103 | 16.3503 | 19.703 | 22.2687 | 24.821
| Timmins (Porcupine)Ice Accretion2065RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2065 | 13.7896 | 16.4544 | 19.836 | 22.4276 | 25.0029
| Timmins (Porcupine)Ice Accretion2070RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2070 | 13.8689 | 16.5585 | 19.969 | 22.5864 | 25.1849
| Timmins (Porcupine)Ice Accretion2075RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2075 | 13.8513 | 16.5427 | 19.9532 | 22.5721 | 25.1689
| Timmins (Porcupine)Ice Accretion2080RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2080 | 13.8337 | 16.527 | 19.9373 | 22.5578 | 25.153
| Timmins (Porcupine)Ice Accretion2085RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2085 | 13.816 | 16.5112 | 19.9215 | 22.5435 | 25.137
| Timmins (Porcupine)Ice Accretion2090RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2090 | 13.7984 | 16.4954 | 19.9057 | 22.5292 | 25.121
| Timmins (Porcupine)Ice Accretion2095RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2095 | 13.7808 | 16.4796 | 19.8898 | 22.5149 | 25.1051
| Timmins (Porcupine)Ice Accretion2100RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2100 | 13.7631 | 16.4639 | 19.874 | 22.5006 | 25.0891
| Timmins (Porcupine)Ice Accretion2023RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2023 | 13.1682 | 15.6596 | 18.829 | 21.2553 | 23.6767
| Timmins (Porcupine)Ice Accretion2025RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2025 | 13.2189 | 15.7227 | 18.9082 | 21.3448 | 23.7764
| Timmins (Porcupine)Ice Accretion2030RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2030 | 13.2696 | 15.7858 | 18.9873 | 21.4342 | 23.8762
| Timmins (Porcupine)Ice Accretion2035RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2035 | 13.3202 | 15.8488 | 19.0665 | 21.5237 | 23.9759
| Timmins (Porcupine)Ice Accretion2040RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2040 | 13.3709 | 15.9119 | 19.1457 | 21.6131 | 24.0757
| Timmins (Porcupine)Ice Accretion2045RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2045 | 13.4216 | 15.975 | 19.2248 | 21.7026 | 24.1754
| Timmins (Porcupine)Ice Accretion2050RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2050 | 13.5516 | 16.1422 | 19.437 | 21.9509 | 24.4571
| Timmins (Porcupine)Ice Accretion2055RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2055 | 13.6309 | 16.2463 | 19.57 | 22.1098 | 24.639
| Timmins (Porcupine)Ice Accretion2060RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2060 | 13.7103 | 16.3503 | 19.703 | 22.2687 | 24.821
| Timmins (Porcupine)Ice Accretion2065RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2065 | 13.7896 | 16.4544 | 19.836 | 22.4276 | 25.0029
| Timmins (Porcupine)Ice Accretion2070RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2070 | 13.8689 | 16.5585 | 19.969 | 22.5864 | 25.1849
| Timmins (Porcupine)Ice Accretion2075RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2075 | 13.8425 | 16.5348 | 19.9452 | 22.565 | 25.1609
| Timmins (Porcupine)Ice Accretion2080RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2080 | 13.816 | 16.5112 | 19.9215 | 22.5435 | 25.137
| Timmins (Porcupine)Ice Accretion2085RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2085 | 13.7896 | 16.4875 | 19.8978 | 22.522 | 25.1131
| Timmins (Porcupine)Ice Accretion2090RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2090 | 13.6442 | 16.3325 | 19.7347 | 22.3431 | 24.9295
| Timmins (Porcupine)Ice Accretion2095RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2095 | 13.5252 | 16.201 | 19.5953 | 22.1857 | 24.7699
| Timmins (Porcupine)Ice Accretion2100RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2100 | 13.4062 | 16.0696 | 19.456 | 22.0282 | 24.6103
| Timmins (Porcupine)Ice Accretion2023RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2023 | 13.1682 | 15.6596 | 18.829 | 21.2553 | 23.6767
| Timmins (Porcupine)Ice Accretion2025RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2025 | 13.2696 | 15.7858 | 18.9873 | 21.4342 | 23.8762
| Timmins (Porcupine)Ice Accretion2030RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2030 | 13.3709 | 15.9119 | 19.1457 | 21.6131 | 24.0757
| Timmins (Porcupine)Ice Accretion2035RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2035 | 13.4723 | 16.0381 | 19.304 | 21.792 | 24.2752
| Timmins (Porcupine)Ice Accretion2040RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2040 | 13.6045 | 16.2116 | 19.5257 | 22.0568 | 24.5784
| Timmins (Porcupine)Ice Accretion2045RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2045 | 13.7367 | 16.385 | 19.7473 | 22.3216 | 24.8816
| Timmins (Porcupine)Ice Accretion2050RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2050 | 13.8337 | 16.527 | 19.9373 | 22.5578 | 25.153
| Timmins (Porcupine)Ice Accretion2055RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2055 | 13.7984 | 16.4954 | 19.9057 | 22.5292 | 25.121
| Timmins (Porcupine)Ice Accretion2060RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2060 | 13.6442 | 16.3325 | 19.7347 | 22.3431 | 24.9295
| Timmins (Porcupine)Ice Accretion2065RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2065 | 13.5252 | 16.201 | 19.5953 | 22.1857 | 24.7699
| Timmins (Porcupine)Ice Accretion2070RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2070 | 13.3268 | 15.9908 | 19.3737 | 21.9495 | 24.5225
| Timmins (Porcupine)Ice Accretion2075RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2075 | 13.2475 | 15.9119 | 19.2913 | 21.8708 | 24.4348
| Timmins (Porcupine)Ice Accretion2080RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2080 | 13.1682 | 15.8331 | 19.209 | 21.792 | 24.347
| Timmins (Porcupine)Ice Accretion2085RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2085 | 13.0228 | 15.699 | 19.076 | 21.6632 | 24.2273
| Timmins (Porcupine)Ice Accretion2090RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2090 | 12.8773 | 15.565 | 18.943 | 21.5344 | 24.1076
| Timmins (Porcupine)Ice Accretion2095RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2095 | 12.8773 | 15.565 | 18.943 | 21.5344 | 24.1076
| Timmins (Porcupine)Ice Accretion2100RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2100 | 12.8773 | 15.565 | 18.943 | 21.5344 | 24.1076
| Timmins (Porcupine)Wind2023RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2023 | 74.1667 | 79.9195 | 85.986 | 92.0414 | 98.1016
| Timmins (Porcupine)Wind2025RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2025 | 74.1581 | 79.8932 | 85.935 | 91.9717 | 98.0111
| Timmins (Porcupine)Wind2030RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2030 | 74.1495 | 79.8668 | 85.884 | 91.9019 | 97.9207
| Timmins (Porcupine)Wind2035RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2035 | 74.141 | 79.8405 | 85.833 | 91.8322 | 97.8302
| Timmins (Porcupine)Wind2040RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2040 | 74.1324 | 79.8141 | 85.782 | 91.7625 | 97.7398
| Timmins (Porcupine)Wind2045RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2045 | 74.1239 | 79.7878 | 85.731 | 91.6928 | 97.6494
| Timmins (Porcupine)Wind2050RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2050 | 74.1476 | 79.8089 | 85.7446 | 91.7031 | 97.6539
| Timmins (Porcupine)Wind2055RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2055 | 74.1799 | 79.8563 | 85.8092 | 91.7831 | 97.7488
| Timmins (Porcupine)Wind2060RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2060 | 74.2122 | 79.9037 | 85.8738 | 91.8631 | 97.8438
| Timmins (Porcupine)Wind2065RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2065 | 74.2445 | 79.9512 | 85.9384 | 91.9432 | 97.9388
| Timmins (Porcupine)Wind2070RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2070 | 74.2768 | 79.9986 | 86.003 | 92.0232 | 98.0337
| Timmins (Porcupine)Wind2075RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2075 | 74.3061 | 80.017 | 86.0115 | 92.0217 | 98.024
| Timmins (Porcupine)Wind2080RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2080 | 74.3355 | 80.0355 | 86.02 | 92.0202 | 98.0143
| Timmins (Porcupine)Wind2085RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2085 | 74.3648 | 80.0539 | 86.0285 | 92.0187 | 98.0047
| Timmins (Porcupine)Wind2090RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2090 | 74.3942 | 80.0724 | 86.037 | 92.0171 | 97.995
| Timmins (Porcupine)Wind2095RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2095 | 74.4236 | 80.0908 | 86.0455 | 92.0156 | 97.9853
| Timmins (Porcupine)Wind2100RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2100 | 74.4529 | 80.1093 | 86.054 | 92.0141 | 97.9756
| Timmins (Porcupine)Wind2023RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2023 | 74.1667 | 79.9195 | 85.986 | 92.0414 | 98.1016
| Timmins (Porcupine)Wind2025RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2025 | 74.1581 | 79.8932 | 85.935 | 91.9717 | 98.0111
| Timmins (Porcupine)Wind2030RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2030 | 74.1495 | 79.8668 | 85.884 | 91.9019 | 97.9207
| Timmins (Porcupine)Wind2035RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2035 | 74.141 | 79.8405 | 85.833 | 91.8322 | 97.8302
| Timmins (Porcupine)Wind2040RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2040 | 74.1324 | 79.8141 | 85.782 | 91.7625 | 97.7398
| Timmins (Porcupine)Wind2045RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2045 | 74.1239 | 79.7878 | 85.731 | 91.6928 | 97.6494
| Timmins (Porcupine)Wind2050RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2050 | 74.1476 | 79.8089 | 85.7446 | 91.7031 | 97.6539
| Timmins (Porcupine)Wind2055RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2055 | 74.1799 | 79.8563 | 85.8092 | 91.7831 | 97.7488
| Timmins (Porcupine)Wind2060RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2060 | 74.2122 | 79.9037 | 85.8738 | 91.8631 | 97.8438
| Timmins (Porcupine)Wind2065RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2065 | 74.2445 | 79.9512 | 85.9384 | 91.9432 | 97.9388
| Timmins (Porcupine)Wind2070RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2070 | 74.2768 | 79.9986 | 86.003 | 92.0232 | 98.0337
| Timmins (Porcupine)Wind2075RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2075 | 74.3208 | 80.0263 | 86.0157 | 92.0209 | 98.0192
| Timmins (Porcupine)Wind2080RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2080 | 74.3648 | 80.0539 | 86.0285 | 92.0187 | 98.0047
| Timmins (Porcupine)Wind2085RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2085 | 74.4089 | 80.0816 | 86.0413 | 92.0164 | 97.9901
| Timmins (Porcupine)Wind2090RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2090 | 74.7073 | 80.4281 | 86.4478 | 92.4719 | 98.4989
| Timmins (Porcupine)Wind2095RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2095 | 74.9618 | 80.7469 | 86.8417 | 92.9297 | 99.0221
| Timmins (Porcupine)Wind2100RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2100 | 75.2162 | 81.0658 | 87.2355 | 93.3875 | 99.5454
| Timmins (Porcupine)Wind2023RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2023 | 74.1667 | 79.9195 | 85.986 | 92.0414 | 98.1016
| Timmins (Porcupine)Wind2025RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2025 | 74.1495 | 79.8668 | 85.884 | 91.9019 | 97.9207
| Timmins (Porcupine)Wind2030RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2030 | 74.1324 | 79.8141 | 85.782 | 91.7625 | 97.7398
| Timmins (Porcupine)Wind2035RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2035 | 74.1153 | 79.7614 | 85.68 | 91.623 | 97.5589
| Timmins (Porcupine)Wind2040RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2040 | 74.1691 | 79.8405 | 85.7877 | 91.7564 | 97.7172
| Timmins (Porcupine)Wind2045RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2045 | 74.2229 | 79.9195 | 85.8953 | 91.8898 | 97.8755
| Timmins (Porcupine)Wind2050RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2050 | 74.3355 | 80.0355 | 86.02 | 92.0202 | 98.0143
| Timmins (Porcupine)Wind2055RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2055 | 74.3942 | 80.0724 | 86.037 | 92.0171 | 97.995
| Timmins (Porcupine)Wind2060RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2060 | 74.7073 | 80.4281 | 86.4478 | 92.4719 | 98.4989
| Timmins (Porcupine)Wind2065RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2065 | 74.9618 | 80.7469 | 86.8417 | 92.9297 | 99.0221
| Timmins (Porcupine)Wind2070RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2070 | 75.3997 | 81.2555 | 87.4338 | 93.5936 | 99.7618
| Timmins (Porcupine)Wind2075RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2075 | 75.5832 | 81.4452 | 87.6322 | 93.7998 | 99.9782
| Timmins (Porcupine)Wind2080RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2080 | 75.7667 | 81.6349 | 87.8305 | 94.0059 | 100.1946
| Timmins (Porcupine)Wind2085RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2085 | 75.8988 | 81.8247 | 88.0813 | 94.3152 | 100.558
| Timmins (Porcupine)Wind2090RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2090 | 76.0309 | 82.0144 | 88.332 | 94.6244 | 100.9214
| Timmins (Porcupine)Wind2095RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2095 | 76.0309 | 82.0144 | 88.332 | 94.6244 | 100.9214
| Timmins (Porcupine)Wind2100RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2100 | 76.0309 | 82.0144 | 88.332 | 94.6244 | 100.9214
| Toronto (LBP Int'l Airport)Ice Accretion2023RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| Toronto (LBP Int'l Airport)Ice Accretion2025RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
| Toronto (LBP Int'l Airport)Ice Accretion2030RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| Toronto (LBP Int'l Airport)Ice Accretion2035RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
| Toronto (LBP Int'l Airport)Ice Accretion2040RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| Toronto (LBP Int'l Airport)Ice Accretion2045RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
| Toronto (LBP Int'l Airport)Ice Accretion2050RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
| Toronto (LBP Int'l Airport)Ice Accretion2055RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
| Toronto (LBP Int'l Airport)Ice Accretion2060RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
| Toronto (LBP Int'l Airport)Ice Accretion2065RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
| Toronto (LBP Int'l Airport)Ice Accretion2070RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
| Toronto (LBP Int'l Airport)Ice Accretion2075RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2075 | 15.5377 | 18.8894 | 23.1125 | 26.329 | 29.5313
| Toronto (LBP Int'l Airport)Ice Accretion2080RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2080 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
| Toronto (LBP Int'l Airport)Ice Accretion2085RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2085 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
| Toronto (LBP Int'l Airport)Ice Accretion2090RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2090 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
| Toronto (LBP Int'l Airport)Ice Accretion2095RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2095 | 15.3405 | 18.7511 | 23.0625 | 26.329 | 29.5942
| Toronto (LBP Int'l Airport)Ice Accretion2100RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2100 | 15.2912 | 18.7165 | 23.05 | 26.329 | 29.61
| Toronto (LBP Int'l Airport)Ice Accretion2023RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| Toronto (LBP Int'l Airport)Ice Accretion2025RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
| Toronto (LBP Int'l Airport)Ice Accretion2030RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| Toronto (LBP Int'l Airport)Ice Accretion2035RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
| Toronto (LBP Int'l Airport)Ice Accretion2040RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| Toronto (LBP Int'l Airport)Ice Accretion2045RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
| Toronto (LBP Int'l Airport)Ice Accretion2050RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
| Toronto (LBP Int'l Airport)Ice Accretion2055RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
| Toronto (LBP Int'l Airport)Ice Accretion2060RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
| Toronto (LBP Int'l Airport)Ice Accretion2065RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
| Toronto (LBP Int'l Airport)Ice Accretion2070RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
| Toronto (LBP Int'l Airport)Ice Accretion2075RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2075 | 15.513 | 18.8721 | 23.1062 | 26.329 | 29.5391
| Toronto (LBP Int'l Airport)Ice Accretion2080RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2080 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
| Toronto (LBP Int'l Airport)Ice Accretion2085RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2085 | 15.3652 | 18.7684 | 23.0688 | 26.329 | 29.5864
| Toronto (LBP Int'l Airport)Ice Accretion2090RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2090 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
| Toronto (LBP Int'l Airport)Ice Accretion2095RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2095 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
| Toronto (LBP Int'l Airport)Ice Accretion2100RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2100 | 14.2127 | 17.596 | 21.825 | 25.0577 | 28.2555
| Toronto (LBP Int'l Airport)Ice Accretion2023RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
| Toronto (LBP Int'l Airport)Ice Accretion2025RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2025 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
| Toronto (LBP Int'l Airport)Ice Accretion2030RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2030 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
| Toronto (LBP Int'l Airport)Ice Accretion2035RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2035 | 16.6133 | 20.0652 | 24.425 | 27.7415 | 31.059
| Toronto (LBP Int'l Airport)Ice Accretion2040RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2040 | 16.2712 | 19.6848 | 23.9917 | 27.2707 | 30.5445
| Toronto (LBP Int'l Airport)Ice Accretion2045RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2045 | 15.9291 | 19.3044 | 23.5583 | 26.7998 | 30.03
| Toronto (LBP Int'l Airport)Ice Accretion2050RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2050 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
| Toronto (LBP Int'l Airport)Ice Accretion2055RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2055 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
| Toronto (LBP Int'l Airport)Ice Accretion2060RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2060 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
| Toronto (LBP Int'l Airport)Ice Accretion2065RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2065 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
| Toronto (LBP Int'l Airport)Ice Accretion2070RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2070 | 13.8125 | 17.1464 | 21.325 | 24.5022 | 27.657
| Toronto (LBP Int'l Airport)Ice Accretion2075RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2075 | 13.4124 | 16.6968 | 20.825 | 23.9466 | 27.0585
| Toronto (LBP Int'l Airport)Ice Accretion2080RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2080 | 13.0123 | 16.2473 | 20.325 | 23.391 | 26.46
| Toronto (LBP Int'l Airport)Ice Accretion2085RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2085 | 12.1338 | 15.1994 | 19.0625 | 21.9785 | 24.885
| Toronto (LBP Int'l Airport)Ice Accretion2090RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2090 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| Toronto (LBP Int'l Airport)Ice Accretion2095RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2095 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| Toronto (LBP Int'l Airport)Ice Accretion2100RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2100 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
| Toronto (LBP Int'l Airport)Wind2023RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2023 | 85.9036 | 92.5764 | 99.6138 | 106.6397 | 113.6613
| Toronto (LBP Int'l Airport)Wind2025RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2025 | 85.935 | 92.6224 | 99.6798 | 106.7227 | 113.761
| Toronto (LBP Int'l Airport)Wind2030RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2030 | 85.9663 | 92.6685 | 99.7458 | 106.8057 | 113.8607
| Toronto (LBP Int'l Airport)Wind2035RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2035 | 85.9977 | 92.7145 | 99.8118 | 106.8887 | 113.9604
| Toronto (LBP Int'l Airport)Wind2040RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2040 | 86.029 | 92.7605 | 99.8778 | 106.9716 | 114.0601
| Toronto (LBP Int'l Airport)Wind2045RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2045 | 86.0604 | 92.8066 | 99.9438 | 107.0546 | 114.1598
| Toronto (LBP Int'l Airport)Wind2050RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2050 | 86.1601 | 92.9355 | 100.1108 | 107.2541 | 114.3926
| Toronto (LBP Int'l Airport)Wind2055RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2055 | 86.2285 | 93.0183 | 100.2118 | 107.3706 | 114.5258
| Toronto (LBP Int'l Airport)Wind2060RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2060 | 86.2969 | 93.1012 | 100.3127 | 107.4872 | 114.659
| Toronto (LBP Int'l Airport)Wind2065RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2065 | 86.3653 | 93.184 | 100.4137 | 107.6037 | 114.7922
| Toronto (LBP Int'l Airport)Wind2070RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2070 | 86.4336 | 93.2669 | 100.5147 | 107.7202 | 114.9253
| Toronto (LBP Int'l Airport)Wind2075RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2075 | 86.5277 | 93.3989 | 100.6946 | 107.9391 | 115.1849
| Toronto (LBP Int'l Airport)Wind2080RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2080 | 86.6217 | 93.5308 | 100.8744 | 108.1581 | 115.4445
| Toronto (LBP Int'l Airport)Wind2085RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2085 | 86.7157 | 93.6628 | 101.0542 | 108.377 | 115.7041
| Toronto (LBP Int'l Airport)Wind2090RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2090 | 86.8098 | 93.7948 | 101.2341 | 108.5959 | 115.9636
| Toronto (LBP Int'l Airport)Wind2095RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2095 | 86.9038 | 93.9267 | 101.4139 | 108.8148 | 116.2232
| Toronto (LBP Int'l Airport)Wind2100RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2100 | 86.9978 | 94.0587 | 101.5938 | 109.0337 | 116.4828
| Toronto (LBP Int'l Airport)Wind2023RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2023 | 85.9036 | 92.5764 | 99.6138 | 106.6397 | 113.6613
| Toronto (LBP Int'l Airport)Wind2025RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2025 | 85.935 | 92.6224 | 99.6798 | 106.7227 | 113.761
| Toronto (LBP Int'l Airport)Wind2030RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2030 | 85.9663 | 92.6685 | 99.7458 | 106.8057 | 113.8607
| Toronto (LBP Int'l Airport)Wind2035RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2035 | 85.9977 | 92.7145 | 99.8118 | 106.8887 | 113.9604
| Toronto (LBP Int'l Airport)Wind2040RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2040 | 86.029 | 92.7605 | 99.8778 | 106.9716 | 114.0601
| Toronto (LBP Int'l Airport)Wind2045RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2045 | 86.0604 | 92.8066 | 99.9438 | 107.0546 | 114.1598
| Toronto (LBP Int'l Airport)Wind2050RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2050 | 86.1601 | 92.9355 | 100.1108 | 107.2541 | 114.3926
| Toronto (LBP Int'l Airport)Wind2055RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2055 | 86.2285 | 93.0183 | 100.2118 | 107.3706 | 114.5258
| Toronto (LBP Int'l Airport)Wind2060RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2060 | 86.2969 | 93.1012 | 100.3127 | 107.4872 | 114.659
| Toronto (LBP Int'l Airport)Wind2065RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2065 | 86.3653 | 93.184 | 100.4137 | 107.6037 | 114.7922
| Toronto (LBP Int'l Airport)Wind2070RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2070 | 86.4336 | 93.2669 | 100.5147 | 107.7202 | 114.9253
| Toronto (LBP Int'l Airport)Wind2075RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2075 | 86.5747 | 93.4649 | 100.7845 | 108.0486 | 115.3147
| Toronto (LBP Int'l Airport)Wind2080RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2080 | 86.7157 | 93.6628 | 101.0542 | 108.377 | 115.7041
| Toronto (LBP Int'l Airport)Wind2085RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2085 | 86.8568 | 93.8608 | 101.324 | 108.7054 | 116.0934
| Toronto (LBP Int'l Airport)Wind2090RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2090 | 87.2942 | 94.4393 | 102.0789 | 109.6093 | 117.1524
| Toronto (LBP Int'l Airport)Wind2095RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2095 | 87.5905 | 94.8198 | 102.564 | 110.1849 | 117.8221
| Toronto (LBP Int'l Airport)Wind2100RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2100 | 87.8869 | 95.2004 | 103.0491 | 110.7604 | 118.4917
| Toronto (LBP Int'l Airport)Wind2023RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2023 | 85.9036 | 92.5764 | 99.6138 | 106.6397 | 113.6613
| Toronto (LBP Int'l Airport)Wind2025RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2025 | 85.9663 | 92.6685 | 99.7458 | 106.8057 | 113.8607
| Toronto (LBP Int'l Airport)Wind2030RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2030 | 86.029 | 92.7605 | 99.8778 | 106.9716 | 114.0601
| Toronto (LBP Int'l Airport)Wind2035RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2035 | 86.0917 | 92.8526 | 100.0098 | 107.1376 | 114.2595
| Toronto (LBP Int'l Airport)Wind2040RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2040 | 86.2057 | 92.9907 | 100.1781 | 107.3318 | 114.4814
| Toronto (LBP Int'l Airport)Wind2045RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2045 | 86.3197 | 93.1288 | 100.3464 | 107.526 | 114.7034
| Toronto (LBP Int'l Airport)Wind2050RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2050 | 86.6217 | 93.5308 | 100.8744 | 108.1581 | 115.4445
| Toronto (LBP Int'l Airport)Wind2055RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2055 | 86.8098 | 93.7948 | 101.2341 | 108.5959 | 115.9636
| Toronto (LBP Int'l Airport)Wind2060RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2060 | 87.2942 | 94.4393 | 102.0789 | 109.6093 | 117.1524
| Toronto (LBP Int'l Airport)Wind2065RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2065 | 87.5905 | 94.8198 | 102.564 | 110.1849 | 117.8221
| Toronto (LBP Int'l Airport)Wind2070RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2070 | 88.055 | 95.4428 | 103.3857 | 111.1735 | 118.9845
| Toronto (LBP Int'l Airport)Wind2075RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2075 | 88.2231 | 95.6853 | 103.7223 | 111.5867 | 119.4774
| Toronto (LBP Int'l Airport)Wind2080RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2080 | 88.3912 | 95.9277 | 104.0589 | 111.9998 | 119.9702
| Toronto (LBP Int'l Airport)Wind2085RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2085 | 88.6605 | 96.2776 | 104.5093 | 112.54 | 120.6022
| Toronto (LBP Int'l Airport)Wind2090RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2090 | 88.9298 | 96.6275 | 104.9598 | 113.0803 | 121.2342
| Toronto (LBP Int'l Airport)Wind2095RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2095 | 88.9298 | 96.6275 | 104.9598 | 113.0803 | 121.2342
| Toronto (LBP Int'l Airport)Wind2100RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2100 | 88.9298 | 96.6275 | 104.9598 | 113.0803 | 121.2342
| Toronto (city hall)Ice Accretion2023RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| Toronto (city hall)Ice Accretion2025RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| Toronto (city hall)Ice Accretion2030RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| Toronto (city hall)Ice Accretion2035RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| Toronto (city hall)Ice Accretion2040RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| Toronto (city hall)Ice Accretion2045RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| Toronto (city hall)Ice Accretion2050RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| Toronto (city hall)Ice Accretion2055RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| Toronto (city hall)Ice Accretion2060RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| Toronto (city hall)Ice Accretion2065RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| Toronto (city hall)Ice Accretion2070RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| Toronto (city hall)Ice Accretion2075RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
| Toronto (city hall)Ice Accretion2080RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| Toronto (city hall)Ice Accretion2085RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| Toronto (city hall)Ice Accretion2090RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| Toronto (city hall)Ice Accretion2095RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
| Toronto (city hall)Ice Accretion2100RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
| Toronto (city hall)Ice Accretion2023RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| Toronto (city hall)Ice Accretion2025RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| Toronto (city hall)Ice Accretion2030RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| Toronto (city hall)Ice Accretion2035RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| Toronto (city hall)Ice Accretion2040RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| Toronto (city hall)Ice Accretion2045RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| Toronto (city hall)Ice Accretion2050RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| Toronto (city hall)Ice Accretion2055RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| Toronto (city hall)Ice Accretion2060RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| Toronto (city hall)Ice Accretion2065RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| Toronto (city hall)Ice Accretion2070RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| Toronto (city hall)Ice Accretion2075RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
| Toronto (city hall)Ice Accretion2080RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| Toronto (city hall)Ice Accretion2085RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
| Toronto (city hall)Ice Accretion2090RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| Toronto (city hall)Ice Accretion2095RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| Toronto (city hall)Ice Accretion2100RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
| Toronto (city hall)Ice Accretion2023RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| Toronto (city hall)Ice Accretion2025RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| Toronto (city hall)Ice Accretion2030RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| Toronto (city hall)Ice Accretion2035RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
| Toronto (city hall)Ice Accretion2040RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
| Toronto (city hall)Ice Accretion2045RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
| Toronto (city hall)Ice Accretion2050RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| Toronto (city hall)Ice Accretion2055RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| Toronto (city hall)Ice Accretion2060RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| Toronto (city hall)Ice Accretion2065RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| Toronto (city hall)Ice Accretion2070RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
| Toronto (city hall)Ice Accretion2075RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
| Toronto (city hall)Ice Accretion2080RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
| Toronto (city hall)Ice Accretion2085RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
| Toronto (city hall)Ice Accretion2090RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| Toronto (city hall)Ice Accretion2095RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| Toronto (city hall)Ice Accretion2100RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| Toronto (city hall)Wind2023RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2023 | 85.6899 | 92.2541 | 99.1584 | 106.0677 | 112.9729
| Toronto (city hall)Wind2025RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2025 | 85.7056 | 92.2879 | 99.2129 | 106.1401 | 113.0631
| Toronto (city hall)Wind2030RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2030 | 85.7213 | 92.3217 | 99.2673 | 106.2125 | 113.1534
| Toronto (city hall)Wind2035RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2035 | 85.7369 | 92.3554 | 99.3217 | 106.2849 | 113.2437
| Toronto (city hall)Wind2040RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2040 | 85.7526 | 92.3892 | 99.3762 | 106.3573 | 113.334
| Toronto (city hall)Wind2045RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2045 | 85.7683 | 92.4229 | 99.4306 | 106.4296 | 113.4243
| Toronto (city hall)Wind2050RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2050 | 85.8677 | 92.5617 | 99.6178 | 106.6567 | 113.6952
| Toronto (city hall)Wind2055RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2055 | 85.9515 | 92.6666 | 99.7504 | 106.8113 | 113.8757
| Toronto (city hall)Wind2060RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2060 | 86.0353 | 92.7716 | 99.8831 | 106.966 | 114.0563
| Toronto (city hall)Wind2065RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2065 | 86.1191 | 92.8765 | 100.0157 | 107.1207 | 114.2369
| Toronto (city hall)Wind2070RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2070 | 86.2028 | 92.9815 | 100.1484 | 107.2753 | 114.4175
| Toronto (city hall)Wind2075RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2075 | 86.3482 | 93.1687 | 100.3877 | 107.5596 | 114.7466
| Toronto (city hall)Wind2080RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2080 | 86.4935 | 93.3559 | 100.6269 | 107.8438 | 115.0758
| Toronto (city hall)Wind2085RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2085 | 86.6388 | 93.5431 | 100.8662 | 108.128 | 115.405
| Toronto (city hall)Wind2090RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2090 | 86.7841 | 93.7303 | 101.1054 | 108.4123 | 115.7342
| Toronto (city hall)Wind2095RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2095 | 86.9295 | 93.9175 | 101.3447 | 108.6965 | 116.0633
| Toronto (city hall)Wind2100RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2100 | 87.0748 | 94.1047 | 101.5839 | 108.9808 | 116.3925
| Toronto (city hall)Wind2023RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2023 | 85.6899 | 92.2541 | 99.1584 | 106.0677 | 112.9729
| Toronto (city hall)Wind2025RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2025 | 85.7056 | 92.2879 | 99.2129 | 106.1401 | 113.0631
| Toronto (city hall)Wind2030RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2030 | 85.7213 | 92.3217 | 99.2673 | 106.2125 | 113.1534
| Toronto (city hall)Wind2035RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2035 | 85.7369 | 92.3554 | 99.3217 | 106.2849 | 113.2437
| Toronto (city hall)Wind2040RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2040 | 85.7526 | 92.3892 | 99.3762 | 106.3573 | 113.334
| Toronto (city hall)Wind2045RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2045 | 85.7683 | 92.4229 | 99.4306 | 106.4296 | 113.4243
| Toronto (city hall)Wind2050RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2050 | 85.8677 | 92.5617 | 99.6178 | 106.6567 | 113.6952
| Toronto (city hall)Wind2055RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2055 | 85.9515 | 92.6666 | 99.7504 | 106.8113 | 113.8757
| Toronto (city hall)Wind2060RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2060 | 86.0353 | 92.7716 | 99.8831 | 106.966 | 114.0563
| Toronto (city hall)Wind2065RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2065 | 86.1191 | 92.8765 | 100.0157 | 107.1207 | 114.2369
| Toronto (city hall)Wind2070RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2070 | 86.2028 | 92.9815 | 100.1484 | 107.2753 | 114.4175
| Toronto (city hall)Wind2075RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2075 | 86.4208 | 93.2623 | 100.5073 | 107.7017 | 114.9112
| Toronto (city hall)Wind2080RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2080 | 86.6388 | 93.5431 | 100.8662 | 108.128 | 115.405
| Toronto (city hall)Wind2085RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2085 | 86.8568 | 93.8239 | 101.225 | 108.5544 | 115.8988
| Toronto (city hall)Wind2090RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2090 | 87.525 | 94.6572 | 102.267 | 109.7753 | 117.3029
| Toronto (city hall)Wind2095RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2095 | 87.9752 | 95.2096 | 102.9501 | 110.5697 | 118.2133
| Toronto (city hall)Wind2100RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2100 | 88.4254 | 95.762 | 103.6332 | 111.3642 | 119.1237
| Toronto (city hall)Wind2023RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2023 | 85.6899 | 92.2541 | 99.1584 | 106.0677 | 112.9729
| Toronto (city hall)Wind2025RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2025 | 85.7213 | 92.3217 | 99.2673 | 106.2125 | 113.1534
| Toronto (city hall)Wind2030RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2030 | 85.7526 | 92.3892 | 99.3762 | 106.3573 | 113.334
| Toronto (city hall)Wind2035RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2035 | 85.784 | 92.4567 | 99.4851 | 106.502 | 113.5146
| Toronto (city hall)Wind2040RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2040 | 85.9236 | 92.6316 | 99.7062 | 106.7598 | 113.8155
| Toronto (city hall)Wind2045RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2045 | 86.0632 | 92.8066 | 99.9273 | 107.0175 | 114.1165
| Toronto (city hall)Wind2050RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2050 | 86.4935 | 93.3559 | 100.6269 | 107.8438 | 115.0758
| Toronto (city hall)Wind2055RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2055 | 86.7841 | 93.7303 | 101.1054 | 108.4123 | 115.7342
| Toronto (city hall)Wind2060RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2060 | 87.525 | 94.6572 | 102.267 | 109.7753 | 117.3029
| Toronto (city hall)Wind2065RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2065 | 87.9752 | 95.2096 | 102.9501 | 110.5697 | 118.2133
| Toronto (city hall)Wind2070RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2070 | 88.5594 | 95.9431 | 103.8741 | 111.6608 | 119.4698
| Toronto (city hall)Wind2075RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2075 | 88.6933 | 96.1241 | 104.115 | 111.9574 | 119.8159
| Toronto (city hall)Wind2080RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2080 | 88.8272 | 96.3052 | 104.3559 | 112.254 | 120.162
| Toronto (city hall)Wind2085RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2085 | 89.1136 | 96.7103 | 104.9103 | 112.932 | 120.969
| Toronto (city hall)Wind2090RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2090 | 89.4 | 97.1154 | 105.4647 | 113.6099 | 121.7759
| Toronto (city hall)Wind2095RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2095 | 89.4 | 97.1154 | 105.4647 | 113.6099 | 121.7759
| Toronto (city hall)Wind2100RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2100 | 89.4 | 97.1154 | 105.4647 | 113.6099 | 121.7759
| TrentonIce Accretion2023RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| TrentonIce Accretion2025RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
| TrentonIce Accretion2030RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| TrentonIce Accretion2035RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
| TrentonIce Accretion2040RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| TrentonIce Accretion2045RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
| TrentonIce Accretion2050RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
| TrentonIce Accretion2055RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
| TrentonIce Accretion2060RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
| TrentonIce Accretion2065RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
| TrentonIce Accretion2070RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
| TrentonIce Accretion2075RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2075 | 16.8859 | 20.3972 | 24.8292 | 28.2123 | 31.5682
| TrentonIce Accretion2080RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2080 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
| TrentonIce Accretion2085RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2085 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
| TrentonIce Accretion2090RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2090 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
| TrentonIce Accretion2095RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2095 | 16.7235 | 20.3142 | 24.8458 | 28.2877 | 31.7152
| TrentonIce Accretion2100RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.2935 | 24.85 | 28.3065 | 31.752
| TrentonIce Accretion2023RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| TrentonIce Accretion2025RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
| TrentonIce Accretion2030RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| TrentonIce Accretion2035RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
| TrentonIce Accretion2040RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| TrentonIce Accretion2045RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
| TrentonIce Accretion2050RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
| TrentonIce Accretion2055RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
| TrentonIce Accretion2060RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
| TrentonIce Accretion2065RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
| TrentonIce Accretion2070RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
| TrentonIce Accretion2075RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2075 | 16.8656 | 20.3869 | 24.8313 | 28.2217 | 31.5866
| TrentonIce Accretion2080RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2080 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
| TrentonIce Accretion2085RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2085 | 16.7438 | 20.3246 | 24.8438 | 28.2782 | 31.6969
| TrentonIce Accretion2090RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2090 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
| TrentonIce Accretion2095RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2095 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
| TrentonIce Accretion2100RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2100 | 15.6565 | 19.173 | 23.6 | 26.9505 | 30.2715
| TrentonIce Accretion2023RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
| TrentonIce Accretion2025RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2025 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
| TrentonIce Accretion2030RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2030 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
| TrentonIce Accretion2035RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2035 | 17.6745 | 21.2272 | 25.725 | 29.154 | 32.571
| TrentonIce Accretion2040RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2040 | 17.4251 | 20.9575 | 25.425 | 28.8338 | 32.2245
| TrentonIce Accretion2045RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2045 | 17.1758 | 20.6877 | 25.125 | 28.5137 | 31.878
| TrentonIce Accretion2050RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2050 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
| TrentonIce Accretion2055RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2055 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
| TrentonIce Accretion2060RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2060 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
| TrentonIce Accretion2065RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2065 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
| TrentonIce Accretion2070RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2070 | 15.2216 | 18.6888 | 23.05 | 26.3478 | 29.631
| TrentonIce Accretion2075RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2075 | 14.7867 | 18.2047 | 22.5 | 25.7452 | 28.9905
| TrentonIce Accretion2080RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2080 | 14.3518 | 17.7205 | 21.95 | 25.1425 | 28.35
| TrentonIce Accretion2085RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2085 | 13.6908 | 16.9424 | 21.025 | 24.0972 | 27.1845
| TrentonIce Accretion2090RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2090 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| TrentonIce Accretion2095RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2095 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| TrentonIce Accretion2100RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2100 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
| TrentonWind2023RCP4.5 | Trenton | Wind | RCP4.5 | 2023 | 87.735 | 94.5124 | 101.6363 | 108.7616 | 115.8884
| TrentonWind2025RCP4.5 | Trenton | Wind | RCP4.5 | 2025 | 87.7016 | 94.4764 | 101.6009 | 108.7238 | 115.85
| TrentonWind2030RCP4.5 | Trenton | Wind | RCP4.5 | 2030 | 87.6681 | 94.4404 | 101.5656 | 108.686 | 115.8116
| TrentonWind2035RCP4.5 | Trenton | Wind | RCP4.5 | 2035 | 87.6347 | 94.4043 | 101.5302 | 108.6482 | 115.7733
| TrentonWind2040RCP4.5 | Trenton | Wind | RCP4.5 | 2040 | 87.6013 | 94.3683 | 101.4949 | 108.6103 | 115.7349
| TrentonWind2045RCP4.5 | Trenton | Wind | RCP4.5 | 2045 | 87.5678 | 94.3323 | 101.4595 | 108.5725 | 115.6965
| TrentonWind2050RCP4.5 | Trenton | Wind | RCP4.5 | 2050 | 87.6582 | 94.4616 | 101.6403 | 108.7941 | 115.9621
| TrentonWind2055RCP4.5 | Trenton | Wind | RCP4.5 | 2055 | 87.7821 | 94.627 | 101.8565 | 109.0534 | 116.2661
| TrentonWind2060RCP4.5 | Trenton | Wind | RCP4.5 | 2060 | 87.9059 | 94.7923 | 102.0726 | 109.3128 | 116.57
| TrentonWind2065RCP4.5 | Trenton | Wind | RCP4.5 | 2065 | 88.0298 | 94.9576 | 102.2888 | 109.5722 | 116.874
| TrentonWind2070RCP4.5 | Trenton | Wind | RCP4.5 | 2070 | 88.1536 | 95.1229 | 102.5049 | 109.8315 | 117.178
| TrentonWind2075RCP4.5 | Trenton | Wind | RCP4.5 | 2075 | 88.2161 | 95.209 | 102.6194 | 109.9702 | 117.3411
| TrentonWind2080RCP4.5 | Trenton | Wind | RCP4.5 | 2080 | 88.2786 | 95.2951 | 102.7338 | 110.1089 | 117.5042
| TrentonWind2085RCP4.5 | Trenton | Wind | RCP4.5 | 2085 | 88.3411 | 95.3812 | 102.8483 | 110.2476 | 117.6673
| TrentonWind2090RCP4.5 | Trenton | Wind | RCP4.5 | 2090 | 88.4036 | 95.4673 | 102.9628 | 110.3863 | 117.8304
| TrentonWind2095RCP4.5 | Trenton | Wind | RCP4.5 | 2095 | 88.4661 | 95.5534 | 103.0772 | 110.525 | 117.9936
| TrentonWind2100RCP4.5 | Trenton | Wind | RCP4.5 | 2100 | 88.5286 | 95.6395 | 103.1917 | 110.6637 | 118.1567
| TrentonWind2023RCP6.0 | Trenton | Wind | RCP6.0 | 2023 | 87.735 | 94.5124 | 101.6363 | 108.7616 | 115.8884
| TrentonWind2025RCP6.0 | Trenton | Wind | RCP6.0 | 2025 | 87.7016 | 94.4764 | 101.6009 | 108.7238 | 115.85
| TrentonWind2030RCP6.0 | Trenton | Wind | RCP6.0 | 2030 | 87.6681 | 94.4404 | 101.5656 | 108.686 | 115.8116
| TrentonWind2035RCP6.0 | Trenton | Wind | RCP6.0 | 2035 | 87.6347 | 94.4043 | 101.5302 | 108.6482 | 115.7733
| TrentonWind2040RCP6.0 | Trenton | Wind | RCP6.0 | 2040 | 87.6013 | 94.3683 | 101.4949 | 108.6103 | 115.7349
| TrentonWind2045RCP6.0 | Trenton | Wind | RCP6.0 | 2045 | 87.5678 | 94.3323 | 101.4595 | 108.5725 | 115.6965
| TrentonWind2050RCP6.0 | Trenton | Wind | RCP6.0 | 2050 | 87.6582 | 94.4616 | 101.6403 | 108.7941 | 115.9621
| TrentonWind2055RCP6.0 | Trenton | Wind | RCP6.0 | 2055 | 87.7821 | 94.627 | 101.8565 | 109.0534 | 116.2661
| TrentonWind2060RCP6.0 | Trenton | Wind | RCP6.0 | 2060 | 87.9059 | 94.7923 | 102.0726 | 109.3128 | 116.57
| TrentonWind2065RCP6.0 | Trenton | Wind | RCP6.0 | 2065 | 88.0298 | 94.9576 | 102.2888 | 109.5722 | 116.874
| TrentonWind2070RCP6.0 | Trenton | Wind | RCP6.0 | 2070 | 88.1536 | 95.1229 | 102.5049 | 109.8315 | 117.178
| TrentonWind2075RCP6.0 | Trenton | Wind | RCP6.0 | 2075 | 88.2474 | 95.2521 | 102.6766 | 110.0396 | 117.4227
| TrentonWind2080RCP6.0 | Trenton | Wind | RCP6.0 | 2080 | 88.3411 | 95.3812 | 102.8483 | 110.2476 | 117.6673
| TrentonWind2085RCP6.0 | Trenton | Wind | RCP6.0 | 2085 | 88.4349 | 95.5104 | 103.02 | 110.4556 | 117.912
| TrentonWind2090RCP6.0 | Trenton | Wind | RCP6.0 | 2090 | 88.828 | 96.0027 | 103.6361 | 111.1824 | 118.7439
| TrentonWind2095RCP6.0 | Trenton | Wind | RCP6.0 | 2095 | 89.1275 | 96.3659 | 104.0805 | 111.7012 | 119.3311
| TrentonWind2100RCP6.0 | Trenton | Wind | RCP6.0 | 2100 | 89.4269 | 96.7291 | 104.5249 | 112.2199 | 119.9183
| TrentonWind2023RCP8.5 | Trenton | Wind | RCP8.5 | 2023 | 87.735 | 94.5124 | 101.6363 | 108.7616 | 115.8884
| TrentonWind2025RCP8.5 | Trenton | Wind | RCP8.5 | 2025 | 87.6681 | 94.4404 | 101.5656 | 108.686 | 115.8116
| TrentonWind2030RCP8.5 | Trenton | Wind | RCP8.5 | 2030 | 87.6013 | 94.3683 | 101.4949 | 108.6103 | 115.7349
| TrentonWind2035RCP8.5 | Trenton | Wind | RCP8.5 | 2035 | 87.5344 | 94.2963 | 101.4242 | 108.5347 | 115.6581
| TrentonWind2040RCP8.5 | Trenton | Wind | RCP8.5 | 2040 | 87.7408 | 94.5719 | 101.7844 | 108.967 | 116.1647
| TrentonWind2045RCP8.5 | Trenton | Wind | RCP8.5 | 2045 | 87.9472 | 94.8474 | 102.1447 | 109.3993 | 116.6714
| TrentonWind2050RCP8.5 | Trenton | Wind | RCP8.5 | 2050 | 88.2786 | 95.2951 | 102.7338 | 110.1089 | 117.5042
| TrentonWind2055RCP8.5 | Trenton | Wind | RCP8.5 | 2055 | 88.4036 | 95.4673 | 102.9628 | 110.3863 | 117.8304
| TrentonWind2060RCP8.5 | Trenton | Wind | RCP8.5 | 2060 | 88.828 | 96.0027 | 103.6361 | 111.1824 | 118.7439
| TrentonWind2065RCP8.5 | Trenton | Wind | RCP8.5 | 2065 | 89.1275 | 96.3659 | 104.0805 | 111.7012 | 119.3311
| TrentonWind2070RCP8.5 | Trenton | Wind | RCP8.5 | 2070 | 89.3455 | 96.6383 | 104.4205 | 112.1046 | 119.7955
| TrentonWind2075RCP8.5 | Trenton | Wind | RCP8.5 | 2075 | 89.2641 | 96.5475 | 104.3162 | 111.9893 | 119.6727
| TrentonWind2080RCP8.5 | Trenton | Wind | RCP8.5 | 2080 | 89.1827 | 96.4567 | 104.2118 | 111.8741 | 119.5499
| TrentonWind2085RCP8.5 | Trenton | Wind | RCP8.5 | 2085 | 89.3964 | 96.7808 | 104.6764 | 112.4522 | 120.2465
| TrentonWind2090RCP8.5 | Trenton | Wind | RCP8.5 | 2090 | 89.61 | 97.1048 | 105.141 | 113.0304 | 120.9431
| TrentonWind2095RCP8.5 | Trenton | Wind | RCP8.5 | 2095 | 89.61 | 97.1048 | 105.141 | 113.0304 | 120.9431
| TrentonWind2100RCP8.5 | Trenton | Wind | RCP8.5 | 2100 | 89.61 | 97.1048 | 105.141 | 113.0304 | 120.9431
| Trout CreekIce Accretion2023RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2023 | 15.5536 | 18.5704 | 22.396 | 25.3075 | 28.2467
| Trout CreekIce Accretion2025RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2025 | 15.6275 | 18.6617 | 22.5097 | 25.4401 | 28.3899
| Trout CreekIce Accretion2030RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2030 | 15.7015 | 18.753 | 22.6233 | 25.5727 | 28.5331
| Trout CreekIce Accretion2035RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2035 | 15.7755 | 18.8443 | 22.737 | 25.7052 | 28.6763
| Trout CreekIce Accretion2040RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2040 | 15.8495 | 18.9356 | 22.8507 | 25.8378 | 28.8196
| Trout CreekIce Accretion2045RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2045 | 15.9235 | 19.0269 | 22.9643 | 25.9704 | 28.9628
| Trout CreekIce Accretion2050RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2050 | 16.0679 | 19.2168 | 23.2144 | 26.2671 | 29.3
| Trout CreekIce Accretion2055RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2055 | 16.1383 | 19.3154 | 23.3508 | 26.4312 | 29.4941
| Trout CreekIce Accretion2060RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2060 | 16.2088 | 19.414 | 23.4872 | 26.5952 | 29.6881
| Trout CreekIce Accretion2065RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2065 | 16.2792 | 19.5126 | 23.6236 | 26.7593 | 29.8822
| Trout CreekIce Accretion2070RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2070 | 16.3496 | 19.6112 | 23.76 | 26.9234 | 30.0762
| Trout CreekIce Accretion2075RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2075 | 16.3394 | 19.6173 | 23.7857 | 26.9607 | 30.1316
| Trout CreekIce Accretion2080RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2080 | 16.3292 | 19.6234 | 23.8113 | 26.998 | 30.1871
| Trout CreekIce Accretion2085RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2085 | 16.319 | 19.6295 | 23.837 | 27.0352 | 30.2425
| Trout CreekIce Accretion2090RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2090 | 16.3088 | 19.6356 | 23.8627 | 27.0725 | 30.298
| Trout CreekIce Accretion2095RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2095 | 16.2986 | 19.6417 | 23.8883 | 27.1098 | 30.3534
| Trout CreekIce Accretion2100RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2100 | 16.2884 | 19.6478 | 23.914 | 27.1471 | 30.4088
| Trout CreekIce Accretion2023RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2023 | 15.5536 | 18.5704 | 22.396 | 25.3075 | 28.2467
| Trout CreekIce Accretion2025RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2025 | 15.6275 | 18.6617 | 22.5097 | 25.4401 | 28.3899
| Trout CreekIce Accretion2030RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2030 | 15.7015 | 18.753 | 22.6233 | 25.5727 | 28.5331
| Trout CreekIce Accretion2035RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2035 | 15.7755 | 18.8443 | 22.737 | 25.7052 | 28.6763
| Trout CreekIce Accretion2040RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2040 | 15.8495 | 18.9356 | 22.8507 | 25.8378 | 28.8196
| Trout CreekIce Accretion2045RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2045 | 15.9235 | 19.0269 | 22.9643 | 25.9704 | 28.9628
| Trout CreekIce Accretion2050RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2050 | 16.0679 | 19.2168 | 23.2144 | 26.2671 | 29.3
| Trout CreekIce Accretion2055RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2055 | 16.1383 | 19.3154 | 23.3508 | 26.4312 | 29.4941
| Trout CreekIce Accretion2060RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2060 | 16.2088 | 19.414 | 23.4872 | 26.5952 | 29.6881
| Trout CreekIce Accretion2065RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2065 | 16.2792 | 19.5126 | 23.6236 | 26.7593 | 29.8822
| Trout CreekIce Accretion2070RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2070 | 16.3496 | 19.6112 | 23.76 | 26.9234 | 30.0762
| Trout CreekIce Accretion2075RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2075 | 16.3343 | 19.6204 | 23.7985 | 26.9793 | 30.1594
| Trout CreekIce Accretion2080RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2080 | 16.319 | 19.6295 | 23.837 | 27.0352 | 30.2425
| Trout CreekIce Accretion2085RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2085 | 16.3037 | 19.6386 | 23.8755 | 27.0912 | 30.3257
| Trout CreekIce Accretion2090RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2090 | 16.2373 | 19.6052 | 23.8773 | 27.114 | 30.3811
| Trout CreekIce Accretion2095RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2095 | 16.1863 | 19.5625 | 23.8407 | 27.0808 | 30.3534
| Trout CreekIce Accretion2100RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2100 | 16.1353 | 19.5199 | 23.804 | 27.0477 | 30.3257
| Trout CreekIce Accretion2023RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2023 | 15.5536 | 18.5704 | 22.396 | 25.3075 | 28.2467
| Trout CreekIce Accretion2025RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2025 | 15.7015 | 18.753 | 22.6233 | 25.5727 | 28.5331
| Trout CreekIce Accretion2030RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2030 | 15.8495 | 18.9356 | 22.8507 | 25.8378 | 28.8196
| Trout CreekIce Accretion2035RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2035 | 15.9975 | 19.1182 | 23.078 | 26.103 | 29.106
| Trout CreekIce Accretion2040RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2040 | 16.1149 | 19.2826 | 23.3053 | 26.3765 | 29.4294
| Trout CreekIce Accretion2045RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2045 | 16.2322 | 19.4469 | 23.5327 | 26.6499 | 29.7528
| Trout CreekIce Accretion2050RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2050 | 16.3292 | 19.6234 | 23.8113 | 26.998 | 30.1871
| Trout CreekIce Accretion2055RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2055 | 16.3088 | 19.6356 | 23.8627 | 27.0725 | 30.298
| Trout CreekIce Accretion2060RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2060 | 16.2373 | 19.6052 | 23.8773 | 27.114 | 30.3811
| Trout CreekIce Accretion2065RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2065 | 16.1863 | 19.5625 | 23.8407 | 27.0808 | 30.3534
| Trout CreekIce Accretion2070RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2070 | 15.8852 | 19.2217 | 23.4447 | 26.6582 | 29.8822
| Trout CreekIce Accretion2075RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2075 | 15.6352 | 18.9234 | 23.0853 | 26.2687 | 29.4386
| Trout CreekIce Accretion2080RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2080 | 15.3852 | 18.6252 | 22.726 | 25.8793 | 28.9951
| Trout CreekIce Accretion2085RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2085 | 15.1402 | 18.3696 | 22.451 | 25.5809 | 28.6902
| Trout CreekIce Accretion2090RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2090 | 14.8953 | 18.1139 | 22.176 | 25.2826 | 28.3853
| Trout CreekIce Accretion2095RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2095 | 14.8953 | 18.1139 | 22.176 | 25.2826 | 28.3853
| Trout CreekIce Accretion2100RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2100 | 14.8953 | 18.1139 | 22.176 | 25.2826 | 28.3853
| Trout CreekWind2023RCP4.5 | Trout Creek | Wind | RCP4.5 | 2023 | 69.6036 | 74.9803 | 80.64 | 86.3019 | 91.957
| Trout CreekWind2025RCP4.5 | Trout Creek | Wind | RCP4.5 | 2025 | 69.6773 | 75.0733 | 80.7573 | 86.4389 | 92.115
| Trout CreekWind2030RCP4.5 | Trout Creek | Wind | RCP4.5 | 2030 | 69.751 | 75.1663 | 80.8747 | 86.5758 | 92.2731
| Trout CreekWind2035RCP4.5 | Trout Creek | Wind | RCP4.5 | 2035 | 69.8246 | 75.2593 | 80.992 | 86.7128 | 92.4312
| Trout CreekWind2040RCP4.5 | Trout Creek | Wind | RCP4.5 | 2040 | 69.8983 | 75.3523 | 81.1093 | 86.8498 | 92.5893
| Trout CreekWind2045RCP4.5 | Trout Creek | Wind | RCP4.5 | 2045 | 69.972 | 75.4453 | 81.2267 | 86.9867 | 92.7474
| Trout CreekWind2050RCP4.5 | Trout Creek | Wind | RCP4.5 | 2050 | 69.9904 | 75.4609 | 81.2368 | 86.9936 | 92.7504
| Trout CreekWind2055RCP4.5 | Trout Creek | Wind | RCP4.5 | 2055 | 69.9352 | 75.3836 | 81.1296 | 86.8635 | 92.5954
| Trout CreekWind2060RCP4.5 | Trout Creek | Wind | RCP4.5 | 2060 | 69.8799 | 75.3062 | 81.0224 | 86.7333 | 92.4403
| Trout CreekWind2065RCP4.5 | Trout Creek | Wind | RCP4.5 | 2065 | 69.8246 | 75.2288 | 80.9152 | 86.6032 | 92.2853
| Trout CreekWind2070RCP4.5 | Trout Creek | Wind | RCP4.5 | 2070 | 69.7694 | 75.1514 | 80.808 | 86.4731 | 92.1302
| Trout CreekWind2075RCP4.5 | Trout Creek | Wind | RCP4.5 | 2075 | 69.8603 | 75.268 | 80.956 | 86.6457 | 92.3309
| Trout CreekWind2080RCP4.5 | Trout Creek | Wind | RCP4.5 | 2080 | 69.9513 | 75.3846 | 81.104 | 86.8184 | 92.5315
| Trout CreekWind2085RCP4.5 | Trout Creek | Wind | RCP4.5 | 2085 | 70.0422 | 75.5011 | 81.252 | 86.991 | 92.7322
| Trout CreekWind2090RCP4.5 | Trout Creek | Wind | RCP4.5 | 2090 | 70.1332 | 75.6177 | 81.4 | 87.1636 | 92.9328
| Trout CreekWind2095RCP4.5 | Trout Creek | Wind | RCP4.5 | 2095 | 70.2241 | 75.7342 | 81.548 | 87.3363 | 93.1334
| Trout CreekWind2100RCP4.5 | Trout Creek | Wind | RCP4.5 | 2100 | 70.3151 | 75.8508 | 81.696 | 87.5089 | 93.3341
| Trout CreekWind2023RCP6.0 | Trout Creek | Wind | RCP6.0 | 2023 | 69.6036 | 74.9803 | 80.64 | 86.3019 | 91.957
| Trout CreekWind2025RCP6.0 | Trout Creek | Wind | RCP6.0 | 2025 | 69.6773 | 75.0733 | 80.7573 | 86.4389 | 92.115
| Trout CreekWind2030RCP6.0 | Trout Creek | Wind | RCP6.0 | 2030 | 69.751 | 75.1663 | 80.8747 | 86.5758 | 92.2731
| Trout CreekWind2035RCP6.0 | Trout Creek | Wind | RCP6.0 | 2035 | 69.8246 | 75.2593 | 80.992 | 86.7128 | 92.4312
| Trout CreekWind2040RCP6.0 | Trout Creek | Wind | RCP6.0 | 2040 | 69.8983 | 75.3523 | 81.1093 | 86.8498 | 92.5893
| Trout CreekWind2045RCP6.0 | Trout Creek | Wind | RCP6.0 | 2045 | 69.972 | 75.4453 | 81.2267 | 86.9867 | 92.7474
| Trout CreekWind2050RCP6.0 | Trout Creek | Wind | RCP6.0 | 2050 | 69.9904 | 75.4609 | 81.2368 | 86.9936 | 92.7504
| Trout CreekWind2055RCP6.0 | Trout Creek | Wind | RCP6.0 | 2055 | 69.9352 | 75.3836 | 81.1296 | 86.8635 | 92.5954
| Trout CreekWind2060RCP6.0 | Trout Creek | Wind | RCP6.0 | 2060 | 69.8799 | 75.3062 | 81.0224 | 86.7333 | 92.4403
| Trout CreekWind2065RCP6.0 | Trout Creek | Wind | RCP6.0 | 2065 | 69.8246 | 75.2288 | 80.9152 | 86.6032 | 92.2853
| Trout CreekWind2070RCP6.0 | Trout Creek | Wind | RCP6.0 | 2070 | 69.7694 | 75.1514 | 80.808 | 86.4731 | 92.1302
| Trout CreekWind2075RCP6.0 | Trout Creek | Wind | RCP6.0 | 2075 | 69.9058 | 75.3263 | 81.03 | 86.7321 | 92.4312
| Trout CreekWind2080RCP6.0 | Trout Creek | Wind | RCP6.0 | 2080 | 70.0422 | 75.5011 | 81.252 | 86.991 | 92.7322
| Trout CreekWind2085RCP6.0 | Trout Creek | Wind | RCP6.0 | 2085 | 70.1787 | 75.676 | 81.474 | 87.2499 | 93.0331
| Trout CreekWind2090RCP6.0 | Trout Creek | Wind | RCP6.0 | 2090 | 70.1792 | 75.6698 | 81.464 | 87.235 | 93.0149
| Trout CreekWind2095RCP6.0 | Trout Creek | Wind | RCP6.0 | 2095 | 70.0434 | 75.4887 | 81.232 | 86.961 | 92.6957
| Trout CreekWind2100RCP6.0 | Trout Creek | Wind | RCP6.0 | 2100 | 69.9075 | 75.3077 | 81 | 86.6871 | 92.3765
| Trout CreekWind2023RCP8.5 | Trout Creek | Wind | RCP8.5 | 2023 | 69.6036 | 74.9803 | 80.64 | 86.3019 | 91.957
| Trout CreekWind2025RCP8.5 | Trout Creek | Wind | RCP8.5 | 2025 | 69.751 | 75.1663 | 80.8747 | 86.5758 | 92.2731
| Trout CreekWind2030RCP8.5 | Trout Creek | Wind | RCP8.5 | 2030 | 69.8983 | 75.3523 | 81.1093 | 86.8498 | 92.5893
| Trout CreekWind2035RCP8.5 | Trout Creek | Wind | RCP8.5 | 2035 | 70.0457 | 75.5383 | 81.344 | 87.1237 | 92.9054
| Trout CreekWind2040RCP8.5 | Trout Creek | Wind | RCP8.5 | 2040 | 69.9536 | 75.4094 | 81.1653 | 86.9068 | 92.647
| Trout CreekWind2045RCP8.5 | Trout Creek | Wind | RCP8.5 | 2045 | 69.8615 | 75.2804 | 80.9867 | 86.69 | 92.3886
| Trout CreekWind2050RCP8.5 | Trout Creek | Wind | RCP8.5 | 2050 | 69.9513 | 75.3846 | 81.104 | 86.8184 | 92.5315
| Trout CreekWind2055RCP8.5 | Trout Creek | Wind | RCP8.5 | 2055 | 70.1332 | 75.6177 | 81.4 | 87.1636 | 92.9328
| Trout CreekWind2060RCP8.5 | Trout Creek | Wind | RCP8.5 | 2060 | 70.1792 | 75.6698 | 81.464 | 87.235 | 93.0149
| Trout CreekWind2065RCP8.5 | Trout Creek | Wind | RCP8.5 | 2065 | 70.0434 | 75.4887 | 81.232 | 86.961 | 92.6957
| Trout CreekWind2070RCP8.5 | Trout Creek | Wind | RCP8.5 | 2070 | 70.1263 | 75.5656 | 81.3013 | 87.0267 | 92.7565
| Trout CreekWind2075RCP8.5 | Trout Creek | Wind | RCP8.5 | 2075 | 70.345 | 75.8235 | 81.6027 | 87.3662 | 93.1365
| Trout CreekWind2080RCP8.5 | Trout Creek | Wind | RCP8.5 | 2080 | 70.5638 | 76.0814 | 81.904 | 87.7058 | 93.5165
| Trout CreekWind2085RCP8.5 | Trout Creek | Wind | RCP8.5 | 2085 | 70.6018 | 76.0814 | 81.856 | 87.6202 | 93.3888
| Trout CreekWind2090RCP8.5 | Trout Creek | Wind | RCP8.5 | 2090 | 70.6398 | 76.0814 | 81.808 | 87.5346 | 93.2611
| Trout CreekWind2095RCP8.5 | Trout Creek | Wind | RCP8.5 | 2095 | 70.6398 | 76.0814 | 81.808 | 87.5346 | 93.2611
| Trout CreekWind2100RCP8.5 | Trout Creek | Wind | RCP8.5 | 2100 | 70.6398 | 76.0814 | 81.808 | 87.5346 | 93.2611
| UxbridgeIce Accretion2023RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
| UxbridgeIce Accretion2025RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
| UxbridgeIce Accretion2030RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
| UxbridgeIce Accretion2035RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
| UxbridgeIce Accretion2040RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
| UxbridgeIce Accretion2045RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
| UxbridgeIce Accretion2050RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
| UxbridgeIce Accretion2055RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
| UxbridgeIce Accretion2060RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
| UxbridgeIce Accretion2065RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
| UxbridgeIce Accretion2070RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
| UxbridgeIce Accretion2075RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2075 | 17.2744 | 20.8814 | 25.4167 | 28.8762 | 32.34
| UxbridgeIce Accretion2080RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2080 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
| UxbridgeIce Accretion2085RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2085 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
| UxbridgeIce Accretion2090RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2090 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
| UxbridgeIce Accretion2095RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2095 | 17.2048 | 20.9091 | 25.5833 | 29.121 | 32.676
| UxbridgeIce Accretion2100RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2100 | 17.1874 | 20.916 | 25.625 | 29.1822 | 32.76
| UxbridgeIce Accretion2023RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
| UxbridgeIce Accretion2025RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
| UxbridgeIce Accretion2030RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
| UxbridgeIce Accretion2035RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
| UxbridgeIce Accretion2040RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
| UxbridgeIce Accretion2045RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
| UxbridgeIce Accretion2050RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
| UxbridgeIce Accretion2055RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
| UxbridgeIce Accretion2060RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
| UxbridgeIce Accretion2065RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
| UxbridgeIce Accretion2070RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
| UxbridgeIce Accretion2075RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2075 | 17.2657 | 20.8849 | 25.4375 | 28.9068 | 32.382
| UxbridgeIce Accretion2080RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2080 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
| UxbridgeIce Accretion2085RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2085 | 17.2135 | 20.9056 | 25.5625 | 29.0904 | 32.634
| UxbridgeIce Accretion2090RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2090 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
| UxbridgeIce Accretion2095RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2095 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
| UxbridgeIce Accretion2100RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2100 | 16.2654 | 19.8992 | 24.5 | 27.9957 | 31.4685
| UxbridgeIce Accretion2023RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
| UxbridgeIce Accretion2025RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2025 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
| UxbridgeIce Accretion2030RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2030 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
| UxbridgeIce Accretion2035RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2035 | 17.6919 | 21.2272 | 25.725 | 29.154 | 32.6025
| UxbridgeIce Accretion2040RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2040 | 17.5585 | 21.1097 | 25.6083 | 29.041 | 32.487
| UxbridgeIce Accretion2045RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2045 | 17.4251 | 20.9921 | 25.4917 | 28.928 | 32.3715
| UxbridgeIce Accretion2050RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2050 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
| UxbridgeIce Accretion2055RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2055 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
| UxbridgeIce Accretion2060RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2060 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
| UxbridgeIce Accretion2065RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2065 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
| UxbridgeIce Accretion2070RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2070 | 15.9987 | 19.6226 | 24.2083 | 27.685 | 31.143
| UxbridgeIce Accretion2075RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2075 | 15.7319 | 19.3459 | 23.9167 | 27.3742 | 30.8175
| UxbridgeIce Accretion2080RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2080 | 15.4652 | 19.0693 | 23.625 | 27.0635 | 30.492
| UxbridgeIce Accretion2085RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2085 | 14.8911 | 18.426 | 22.8875 | 26.2584 | 29.6258
| UxbridgeIce Accretion2090RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2090 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
| UxbridgeIce Accretion2095RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2095 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
| UxbridgeIce Accretion2100RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2100 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
| UxbridgeWind2023RCP4.5 | Uxbridge | Wind | RCP4.5 | 2023 | 76.488 | 82.3883 | 88.5896 | 94.7909 | 101.0022
| UxbridgeWind2025RCP4.5 | Uxbridge | Wind | RCP4.5 | 2025 | 76.5222 | 82.4333 | 88.6497 | 94.8646 | 101.0874
| UxbridgeWind2030RCP4.5 | Uxbridge | Wind | RCP4.5 | 2030 | 76.5564 | 82.4784 | 88.7099 | 94.9384 | 101.1727
| UxbridgeWind2035RCP4.5 | Uxbridge | Wind | RCP4.5 | 2035 | 76.5905 | 82.5234 | 88.77 | 95.0121 | 101.258
| UxbridgeWind2040RCP4.5 | Uxbridge | Wind | RCP4.5 | 2040 | 76.6247 | 82.5684 | 88.8301 | 95.0859 | 101.3433
| UxbridgeWind2045RCP4.5 | Uxbridge | Wind | RCP4.5 | 2045 | 76.6589 | 82.6134 | 88.8903 | 95.1597 | 101.4285
| UxbridgeWind2050RCP4.5 | Uxbridge | Wind | RCP4.5 | 2050 | 76.7615 | 82.7386 | 89.0437 | 95.337 | 101.6302
| UxbridgeWind2055RCP4.5 | Uxbridge | Wind | RCP4.5 | 2055 | 76.8299 | 82.8188 | 89.137 | 95.4406 | 101.7466
| UxbridgeWind2060RCP4.5 | Uxbridge | Wind | RCP4.5 | 2060 | 76.8983 | 82.899 | 89.2302 | 95.5442 | 101.8629
| UxbridgeWind2065RCP4.5 | Uxbridge | Wind | RCP4.5 | 2065 | 76.9667 | 82.9792 | 89.3235 | 95.6477 | 101.9793
| UxbridgeWind2070RCP4.5 | Uxbridge | Wind | RCP4.5 | 2070 | 77.0351 | 83.0594 | 89.4168 | 95.7513 | 102.0957
| UxbridgeWind2075RCP4.5 | Uxbridge | Wind | RCP4.5 | 2075 | 77.1098 | 83.1522 | 89.5312 | 95.8863 | 102.2495
| UxbridgeWind2080RCP4.5 | Uxbridge | Wind | RCP4.5 | 2080 | 77.1845 | 83.2449 | 89.6456 | 96.0212 | 102.4033
| UxbridgeWind2085RCP4.5 | Uxbridge | Wind | RCP4.5 | 2085 | 77.2592 | 83.3377 | 89.76 | 96.1562 | 102.5571
| UxbridgeWind2090RCP4.5 | Uxbridge | Wind | RCP4.5 | 2090 | 77.3339 | 83.4304 | 89.8744 | 96.2912 | 102.711
| UxbridgeWind2095RCP4.5 | Uxbridge | Wind | RCP4.5 | 2095 | 77.4087 | 83.5232 | 89.9888 | 96.4261 | 102.8648
| UxbridgeWind2100RCP4.5 | Uxbridge | Wind | RCP4.5 | 2100 | 77.4834 | 83.6159 | 90.1032 | 96.5611 | 103.0186
| UxbridgeWind2023RCP6.0 | Uxbridge | Wind | RCP6.0 | 2023 | 76.488 | 82.3883 | 88.5896 | 94.7909 | 101.0022
| UxbridgeWind2025RCP6.0 | Uxbridge | Wind | RCP6.0 | 2025 | 76.5222 | 82.4333 | 88.6497 | 94.8646 | 101.0874
| UxbridgeWind2030RCP6.0 | Uxbridge | Wind | RCP6.0 | 2030 | 76.5564 | 82.4784 | 88.7099 | 94.9384 | 101.1727
| UxbridgeWind2035RCP6.0 | Uxbridge | Wind | RCP6.0 | 2035 | 76.5905 | 82.5234 | 88.77 | 95.0121 | 101.258
| UxbridgeWind2040RCP6.0 | Uxbridge | Wind | RCP6.0 | 2040 | 76.6247 | 82.5684 | 88.8301 | 95.0859 | 101.3433
| UxbridgeWind2045RCP6.0 | Uxbridge | Wind | RCP6.0 | 2045 | 76.6589 | 82.6134 | 88.8903 | 95.1597 | 101.4285
| UxbridgeWind2050RCP6.0 | Uxbridge | Wind | RCP6.0 | 2050 | 76.7615 | 82.7386 | 89.0437 | 95.337 | 101.6302
| UxbridgeWind2055RCP6.0 | Uxbridge | Wind | RCP6.0 | 2055 | 76.8299 | 82.8188 | 89.137 | 95.4406 | 101.7466
| UxbridgeWind2060RCP6.0 | Uxbridge | Wind | RCP6.0 | 2060 | 76.8983 | 82.899 | 89.2302 | 95.5442 | 101.8629
| UxbridgeWind2065RCP6.0 | Uxbridge | Wind | RCP6.0 | 2065 | 76.9667 | 82.9792 | 89.3235 | 95.6477 | 101.9793
| UxbridgeWind2070RCP6.0 | Uxbridge | Wind | RCP6.0 | 2070 | 77.0351 | 83.0594 | 89.4168 | 95.7513 | 102.0957
| UxbridgeWind2075RCP6.0 | Uxbridge | Wind | RCP6.0 | 2075 | 77.1471 | 83.1985 | 89.5884 | 95.9537 | 102.3264
| UxbridgeWind2080RCP6.0 | Uxbridge | Wind | RCP6.0 | 2080 | 77.2592 | 83.3377 | 89.76 | 96.1562 | 102.5571
| UxbridgeWind2085RCP6.0 | Uxbridge | Wind | RCP6.0 | 2085 | 77.3713 | 83.4768 | 89.9316 | 96.3586 | 102.7879
| UxbridgeWind2090RCP6.0 | Uxbridge | Wind | RCP6.0 | 2090 | 77.7291 | 83.8969 | 90.4317 | 96.9252 | 103.4232
| UxbridgeWind2095RCP6.0 | Uxbridge | Wind | RCP6.0 | 2095 | 77.9748 | 84.1779 | 90.7603 | 97.2893 | 103.8279
| UxbridgeWind2100RCP6.0 | Uxbridge | Wind | RCP6.0 | 2100 | 78.2205 | 84.4589 | 91.0888 | 97.6533 | 104.2325
| UxbridgeWind2023RCP8.5 | Uxbridge | Wind | RCP8.5 | 2023 | 76.488 | 82.3883 | 88.5896 | 94.7909 | 101.0022
| UxbridgeWind2025RCP8.5 | Uxbridge | Wind | RCP8.5 | 2025 | 76.5564 | 82.4784 | 88.7099 | 94.9384 | 101.1727
| UxbridgeWind2030RCP8.5 | Uxbridge | Wind | RCP8.5 | 2030 | 76.6247 | 82.5684 | 88.8301 | 95.0859 | 101.3433
| UxbridgeWind2035RCP8.5 | Uxbridge | Wind | RCP8.5 | 2035 | 76.6931 | 82.6584 | 88.9504 | 95.2334 | 101.5138
| UxbridgeWind2040RCP8.5 | Uxbridge | Wind | RCP8.5 | 2040 | 76.8071 | 82.7921 | 89.1059 | 95.4061 | 101.7078
| UxbridgeWind2045RCP8.5 | Uxbridge | Wind | RCP8.5 | 2045 | 76.9211 | 82.9257 | 89.2613 | 95.5787 | 101.9017
| UxbridgeWind2050RCP8.5 | Uxbridge | Wind | RCP8.5 | 2050 | 77.1845 | 83.2449 | 89.6456 | 96.0212 | 102.4033
| UxbridgeWind2055RCP8.5 | Uxbridge | Wind | RCP8.5 | 2055 | 77.3339 | 83.4304 | 89.8744 | 96.2912 | 102.711
| UxbridgeWind2060RCP8.5 | Uxbridge | Wind | RCP8.5 | 2060 | 77.7291 | 83.8969 | 90.4317 | 96.9252 | 103.4232
| UxbridgeWind2065RCP8.5 | Uxbridge | Wind | RCP8.5 | 2065 | 77.9748 | 84.1779 | 90.7603 | 97.2893 | 103.8279
| UxbridgeWind2070RCP8.5 | Uxbridge | Wind | RCP8.5 | 2070 | 78.3066 | 84.5707 | 91.2267 | 97.8165 | 104.4231
| UxbridgeWind2075RCP8.5 | Uxbridge | Wind | RCP8.5 | 2075 | 78.3927 | 84.6826 | 91.3645 | 97.9798 | 104.6137
| UxbridgeWind2080RCP8.5 | Uxbridge | Wind | RCP8.5 | 2080 | 78.4788 | 84.7944 | 91.5024 | 98.143 | 104.8043
| UxbridgeWind2085RCP8.5 | Uxbridge | Wind | RCP8.5 | 2085 | 78.6802 | 85.0768 | 91.8984 | 98.6279 | 105.3811
| UxbridgeWind2090RCP8.5 | Uxbridge | Wind | RCP8.5 | 2090 | 78.8815 | 85.3591 | 92.2944 | 99.1128 | 105.958
| UxbridgeWind2095RCP8.5 | Uxbridge | Wind | RCP8.5 | 2095 | 78.8815 | 85.3591 | 92.2944 | 99.1128 | 105.958
| UxbridgeWind2100RCP8.5 | Uxbridge | Wind | RCP8.5 | 2100 | 78.8815 | 85.3591 | 92.2944 | 99.1128 | 105.958
| Vaughan (Woodbridge)Ice Accretion2023RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
| Vaughan (Woodbridge)Ice Accretion2025RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2025 | 17.4222 | 20.9229 | 25.3542 | 28.7444 | 32.1247
| Vaughan (Woodbridge)Ice Accretion2030RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2030 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
| Vaughan (Woodbridge)Ice Accretion2035RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2035 | 17.5092 | 21.0612 | 25.5625 | 28.9986 | 32.4292
| Vaughan (Woodbridge)Ice Accretion2040RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2040 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
| Vaughan (Woodbridge)Ice Accretion2045RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2045 | 17.5962 | 21.1996 | 25.7708 | 29.2529 | 32.7338
| Vaughan (Woodbridge)Ice Accretion2050RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2050 | 17.5214 | 21.1484 | 25.745 | 29.2444 | 32.7411
| Vaughan (Woodbridge)Ice Accretion2055RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2055 | 17.4031 | 21.0281 | 25.615 | 29.1088 | 32.5962
| Vaughan (Woodbridge)Ice Accretion2060RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2060 | 17.2848 | 20.9077 | 25.485 | 28.9732 | 32.4513
| Vaughan (Woodbridge)Ice Accretion2065RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2065 | 17.1665 | 20.7873 | 25.355 | 28.8376 | 32.3064
| Vaughan (Woodbridge)Ice Accretion2070RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2070 | 17.0482 | 20.667 | 25.225 | 28.702 | 32.1615
| Vaughan (Woodbridge)Ice Accretion2075RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2075 | 17.0105 | 20.6497 | 25.2333 | 28.7255 | 32.2035
| Vaughan (Woodbridge)Ice Accretion2080RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2080 | 16.9728 | 20.6324 | 25.2417 | 28.7491 | 32.2455
| Vaughan (Woodbridge)Ice Accretion2085RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2085 | 16.9352 | 20.6151 | 25.25 | 28.7726 | 32.2875
| Vaughan (Woodbridge)Ice Accretion2090RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2090 | 16.8975 | 20.5978 | 25.2583 | 28.7962 | 32.3295
| Vaughan (Woodbridge)Ice Accretion2095RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2095 | 16.8598 | 20.5805 | 25.2667 | 28.8197 | 32.3715
| Vaughan (Woodbridge)Ice Accretion2100RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2100 | 16.8221 | 20.5633 | 25.275 | 28.8432 | 32.4135
| Vaughan (Woodbridge)Ice Accretion2023RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
| Vaughan (Woodbridge)Ice Accretion2025RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2025 | 17.4222 | 20.9229 | 25.3542 | 28.7444 | 32.1247
| Vaughan (Woodbridge)Ice Accretion2030RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2030 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
| Vaughan (Woodbridge)Ice Accretion2035RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2035 | 17.5092 | 21.0612 | 25.5625 | 28.9986 | 32.4292
| Vaughan (Woodbridge)Ice Accretion2040RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2040 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
| Vaughan (Woodbridge)Ice Accretion2045RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2045 | 17.5962 | 21.1996 | 25.7708 | 29.2529 | 32.7338
| Vaughan (Woodbridge)Ice Accretion2050RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2050 | 17.5214 | 21.1484 | 25.745 | 29.2444 | 32.7411
| Vaughan (Woodbridge)Ice Accretion2055RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2055 | 17.4031 | 21.0281 | 25.615 | 29.1088 | 32.5962
| Vaughan (Woodbridge)Ice Accretion2060RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2060 | 17.2848 | 20.9077 | 25.485 | 28.9732 | 32.4513
| Vaughan (Woodbridge)Ice Accretion2065RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2065 | 17.1665 | 20.7873 | 25.355 | 28.8376 | 32.3064
| Vaughan (Woodbridge)Ice Accretion2070RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2070 | 17.0482 | 20.667 | 25.225 | 28.702 | 32.1615
| Vaughan (Woodbridge)Ice Accretion2075RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2075 | 16.9917 | 20.6411 | 25.2375 | 28.7373 | 32.2245
| Vaughan (Woodbridge)Ice Accretion2080RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2080 | 16.9352 | 20.6151 | 25.25 | 28.7726 | 32.2875
| Vaughan (Woodbridge)Ice Accretion2085RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2085 | 16.8786 | 20.5892 | 25.2625 | 28.8079 | 32.3505
| Vaughan (Woodbridge)Ice Accretion2090RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2090 | 16.5147 | 20.2382 | 24.925 | 28.4854 | 32.0355
| Vaughan (Woodbridge)Ice Accretion2095RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2095 | 16.2074 | 19.9131 | 24.575 | 28.1276 | 31.6575
| Vaughan (Woodbridge)Ice Accretion2100RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2100 | 15.9001 | 19.588 | 24.225 | 27.7697 | 31.2795
| Vaughan (Woodbridge)Ice Accretion2023RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
| Vaughan (Woodbridge)Ice Accretion2025RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2025 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
| Vaughan (Woodbridge)Ice Accretion2030RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2030 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
| Vaughan (Woodbridge)Ice Accretion2035RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2035 | 17.6397 | 21.2687 | 25.875 | 29.38 | 32.886
| Vaughan (Woodbridge)Ice Accretion2040RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2040 | 17.4425 | 21.0682 | 25.6583 | 29.154 | 32.6445
| Vaughan (Woodbridge)Ice Accretion2045RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2045 | 17.2454 | 20.8676 | 25.4417 | 28.928 | 32.403
| Vaughan (Woodbridge)Ice Accretion2050RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2050 | 16.9728 | 20.6324 | 25.2417 | 28.7491 | 32.2455
| Vaughan (Woodbridge)Ice Accretion2055RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2055 | 16.8975 | 20.5978 | 25.2583 | 28.7962 | 32.3295
| Vaughan (Woodbridge)Ice Accretion2060RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2060 | 16.5147 | 20.2382 | 24.925 | 28.4854 | 32.0355
| Vaughan (Woodbridge)Ice Accretion2065RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2065 | 16.2074 | 19.9131 | 24.575 | 28.1276 | 31.6575
| Vaughan (Woodbridge)Ice Accretion2070RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2070 | 15.5116 | 19.173 | 23.775 | 27.2801 | 30.765
| Vaughan (Woodbridge)Ice Accretion2075RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2075 | 15.1231 | 18.758 | 23.325 | 26.7904 | 30.2505
| Vaughan (Woodbridge)Ice Accretion2080RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2080 | 14.7345 | 18.343 | 22.875 | 26.3007 | 29.736
| Vaughan (Woodbridge)Ice Accretion2085RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2085 | 13.9691 | 17.4404 | 21.8 | 25.1001 | 28.3972
| Vaughan (Woodbridge)Ice Accretion2090RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2090 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
| Vaughan (Woodbridge)Ice Accretion2095RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2095 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
| Vaughan (Woodbridge)Ice Accretion2100RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2100 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
| Vaughan (Woodbridge)Wind2023RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2023 | 83.201 | 89.6103 | 96.3552 | 103.1001 | 109.8449
| Vaughan (Woodbridge)Wind2025RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2025 | 83.2273 | 89.6475 | 96.4064 | 103.1634 | 109.9215
| Vaughan (Woodbridge)Wind2030RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2030 | 83.2535 | 89.6847 | 96.4576 | 103.2268 | 109.9981
| Vaughan (Woodbridge)Wind2035RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2035 | 83.2798 | 89.7219 | 96.5088 | 103.2901 | 110.0748
| Vaughan (Woodbridge)Wind2040RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2040 | 83.306 | 89.7591 | 96.56 | 103.3534 | 110.1514
| Vaughan (Woodbridge)Wind2045RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2045 | 83.3323 | 89.7963 | 96.6112 | 103.4168 | 110.228
| Vaughan (Woodbridge)Wind2050RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2050 | 83.4132 | 89.8853 | 96.7104 | 103.5253 | 110.3462
| Vaughan (Woodbridge)Wind2055RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2055 | 83.4679 | 89.9371 | 96.7584 | 103.5705 | 110.3878
| Vaughan (Woodbridge)Wind2060RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2060 | 83.5227 | 89.9889 | 96.8064 | 103.6157 | 110.4293
| Vaughan (Woodbridge)Wind2065RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2065 | 83.5774 | 90.0407 | 96.8544 | 103.6609 | 110.4709
| Vaughan (Woodbridge)Wind2070RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2070 | 83.6321 | 90.0924 | 96.9024 | 103.7061 | 110.5125
| Vaughan (Woodbridge)Wind2075RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2075 | 83.7122 | 90.2026 | 97.0496 | 103.8842 | 110.7223
| Vaughan (Woodbridge)Wind2080RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2080 | 83.7923 | 90.3127 | 97.1968 | 104.0622 | 110.932
| Vaughan (Woodbridge)Wind2085RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2085 | 83.8725 | 90.4228 | 97.344 | 104.2403 | 111.1418
| Vaughan (Woodbridge)Wind2090RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2090 | 83.9526 | 90.5329 | 97.4912 | 104.4183 | 111.3516
| Vaughan (Woodbridge)Wind2095RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2095 | 84.0327 | 90.643 | 97.6384 | 104.5964 | 111.5613
| Vaughan (Woodbridge)Wind2100RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2100 | 84.1129 | 90.7531 | 97.7856 | 104.7744 | 111.7711
| Vaughan (Woodbridge)Wind2023RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2023 | 83.201 | 89.6103 | 96.3552 | 103.1001 | 109.8449
| Vaughan (Woodbridge)Wind2025RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2025 | 83.2273 | 89.6475 | 96.4064 | 103.1634 | 109.9215
| Vaughan (Woodbridge)Wind2030RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2030 | 83.2535 | 89.6847 | 96.4576 | 103.2268 | 109.9981
| Vaughan (Woodbridge)Wind2035RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2035 | 83.2798 | 89.7219 | 96.5088 | 103.2901 | 110.0748
| Vaughan (Woodbridge)Wind2040RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2040 | 83.306 | 89.7591 | 96.56 | 103.3534 | 110.1514
| Vaughan (Woodbridge)Wind2045RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2045 | 83.3323 | 89.7963 | 96.6112 | 103.4168 | 110.228
| Vaughan (Woodbridge)Wind2050RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2050 | 83.4132 | 89.8853 | 96.7104 | 103.5253 | 110.3462
| Vaughan (Woodbridge)Wind2055RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2055 | 83.4679 | 89.9371 | 96.7584 | 103.5705 | 110.3878
| Vaughan (Woodbridge)Wind2060RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2060 | 83.5227 | 89.9889 | 96.8064 | 103.6157 | 110.4293
| Vaughan (Woodbridge)Wind2065RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2065 | 83.5774 | 90.0407 | 96.8544 | 103.6609 | 110.4709
| Vaughan (Woodbridge)Wind2070RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2070 | 83.6321 | 90.0924 | 96.9024 | 103.7061 | 110.5125
| Vaughan (Woodbridge)Wind2075RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2075 | 83.7523 | 90.2576 | 97.1232 | 103.9732 | 110.8272
| Vaughan (Woodbridge)Wind2080RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2080 | 83.8725 | 90.4228 | 97.344 | 104.2403 | 111.1418
| Vaughan (Woodbridge)Wind2085RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2085 | 83.9927 | 90.588 | 97.5648 | 104.5073 | 111.4564
| Vaughan (Woodbridge)Wind2090RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2090 | 84.3919 | 91.0983 | 98.2112 | 105.2709 | 112.3402
| Vaughan (Woodbridge)Wind2095RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2095 | 84.671 | 91.4436 | 98.6368 | 105.7674 | 112.9092
| Vaughan (Woodbridge)Wind2100RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2100 | 84.9501 | 91.7888 | 99.0624 | 106.2638 | 113.4783
| Vaughan (Woodbridge)Wind2023RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2023 | 83.201 | 89.6103 | 96.3552 | 103.1001 | 109.8449
| Vaughan (Woodbridge)Wind2025RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2025 | 83.2535 | 89.6847 | 96.4576 | 103.2268 | 109.9981
| Vaughan (Woodbridge)Wind2030RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2030 | 83.306 | 89.7591 | 96.56 | 103.3534 | 110.1514
| Vaughan (Woodbridge)Wind2035RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2035 | 83.3585 | 89.8335 | 96.6624 | 103.4801 | 110.3046
| Vaughan (Woodbridge)Wind2040RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2040 | 83.4497 | 89.9198 | 96.7424 | 103.5555 | 110.3739
| Vaughan (Woodbridge)Wind2045RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2045 | 83.5409 | 90.0061 | 96.8224 | 103.6308 | 110.4432
| Vaughan (Woodbridge)Wind2050RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2050 | 83.7923 | 90.3127 | 97.1968 | 104.0622 | 110.932
| Vaughan (Woodbridge)Wind2055RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2055 | 83.9526 | 90.5329 | 97.4912 | 104.4183 | 111.3516
| Vaughan (Woodbridge)Wind2060RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2060 | 84.3919 | 91.0983 | 98.2112 | 105.2709 | 112.3402
| Vaughan (Woodbridge)Wind2065RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2065 | 84.671 | 91.4436 | 98.6368 | 105.7674 | 112.9092
| Vaughan (Woodbridge)Wind2070RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2070 | 85.1629 | 92.0745 | 99.44 | 106.7192 | 114.0109
| Vaughan (Woodbridge)Wind2075RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2075 | 85.3756 | 92.3602 | 99.8176 | 107.1746 | 114.5436
| Vaughan (Woodbridge)Wind2080RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2080 | 85.5884 | 92.6459 | 100.1952 | 107.63 | 115.0762
| Vaughan (Woodbridge)Wind2085RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2085 | 85.6961 | 92.7887 | 100.3872 | 107.856 | 115.3443
| Vaughan (Woodbridge)Wind2090RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2090 | 85.8039 | 92.9316 | 100.5792 | 108.082 | 115.6124
| Vaughan (Woodbridge)Wind2095RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2095 | 85.8039 | 92.9316 | 100.5792 | 108.082 | 115.6124
| Vaughan (Woodbridge)Wind2100RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2100 | 85.8039 | 92.9316 | 100.5792 | 108.082 | 115.6124
| VittoriaIce Accretion2023RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
| VittoriaIce Accretion2025RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2025 | 22.9175 | 27.5192 | 33.3427 | 37.7989 | 42.2402
| VittoriaIce Accretion2030RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2030 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
| VittoriaIce Accretion2035RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2035 | 22.6651 | 27.2464 | 33.048 | 37.4787 | 41.8975
| VittoriaIce Accretion2040RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2040 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
| VittoriaIce Accretion2045RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2045 | 22.4127 | 26.9736 | 32.7533 | 37.1585 | 41.5548
| VittoriaIce Accretion2050RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2050 | 21.7945 | 26.2954 | 31.9872 | 36.3223 | 40.6466
| VittoriaIce Accretion2055RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2055 | 21.3024 | 25.7536 | 31.3684 | 35.6461 | 39.9097
| VittoriaIce Accretion2060RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2060 | 20.8103 | 25.2117 | 30.7496 | 34.9699 | 39.1729
| VittoriaIce Accretion2065RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2065 | 20.3181 | 24.6699 | 30.1308 | 34.2937 | 38.436
| VittoriaIce Accretion2070RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2070 | 19.826 | 24.1281 | 29.512 | 33.6175 | 37.6992
| VittoriaIce Accretion2075RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2075 | 19.5895 | 23.8647 | 29.2117 | 33.2909 | 37.3422
| VittoriaIce Accretion2080RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2080 | 19.3529 | 23.6013 | 28.9113 | 32.9644 | 36.9852
| VittoriaIce Accretion2085RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2085 | 19.1163 | 23.3379 | 28.611 | 32.6378 | 36.6282
| VittoriaIce Accretion2090RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2090 | 18.8797 | 23.0746 | 28.3107 | 32.3112 | 36.2712
| VittoriaIce Accretion2095RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2095 | 18.6431 | 22.8112 | 28.0103 | 31.9846 | 35.9142
| VittoriaIce Accretion2100RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2100 | 18.4065 | 22.5478 | 27.71 | 31.6581 | 35.5572
| VittoriaIce Accretion2023RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
| VittoriaIce Accretion2025RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2025 | 22.9175 | 27.5192 | 33.3427 | 37.7989 | 42.2402
| VittoriaIce Accretion2030RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2030 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
| VittoriaIce Accretion2035RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2035 | 22.6651 | 27.2464 | 33.048 | 37.4787 | 41.8975
| VittoriaIce Accretion2040RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2040 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
| VittoriaIce Accretion2045RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2045 | 22.4127 | 26.9736 | 32.7533 | 37.1585 | 41.5548
| VittoriaIce Accretion2050RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2050 | 21.7945 | 26.2954 | 31.9872 | 36.3223 | 40.6466
| VittoriaIce Accretion2055RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2055 | 21.3024 | 25.7536 | 31.3684 | 35.6461 | 39.9097
| VittoriaIce Accretion2060RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2060 | 20.8103 | 25.2117 | 30.7496 | 34.9699 | 39.1729
| VittoriaIce Accretion2065RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2065 | 20.3181 | 24.6699 | 30.1308 | 34.2937 | 38.436
| VittoriaIce Accretion2070RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2070 | 19.826 | 24.1281 | 29.512 | 33.6175 | 37.6992
| VittoriaIce Accretion2075RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2075 | 19.4712 | 23.733 | 29.0615 | 33.1276 | 37.1637
| VittoriaIce Accretion2080RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2080 | 19.1163 | 23.3379 | 28.611 | 32.6378 | 36.6282
| VittoriaIce Accretion2085RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2085 | 18.7614 | 22.9429 | 28.1605 | 32.1479 | 36.0927
| VittoriaIce Accretion2090RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2090 | 17.4365 | 21.4002 | 26.3613 | 30.1341 | 33.8722
| VittoriaIce Accretion2095RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2095 | 16.4665 | 20.2526 | 25.0127 | 28.6101 | 32.1871
| VittoriaIce Accretion2100RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2100 | 15.4965 | 19.1049 | 23.664 | 27.0861 | 30.5021
| VittoriaIce Accretion2023RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
| VittoriaIce Accretion2025RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2025 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
| VittoriaIce Accretion2030RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2030 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
| VittoriaIce Accretion2035RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2035 | 22.2866 | 26.8372 | 32.606 | 36.9985 | 41.3834
| VittoriaIce Accretion2040RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2040 | 21.4664 | 25.9342 | 31.5747 | 35.8715 | 40.1554
| VittoriaIce Accretion2045RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2045 | 20.6462 | 25.0311 | 30.5433 | 34.7445 | 38.9273
| VittoriaIce Accretion2050RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2050 | 19.3529 | 23.6013 | 28.9113 | 32.9644 | 36.9852
| VittoriaIce Accretion2055RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2055 | 18.8797 | 23.0746 | 28.3107 | 32.3112 | 36.2712
| VittoriaIce Accretion2060RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2060 | 17.4365 | 21.4002 | 26.3613 | 30.1341 | 33.8722
| VittoriaIce Accretion2065RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2065 | 16.4665 | 20.2526 | 25.0127 | 28.6101 | 32.1871
| VittoriaIce Accretion2070RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2070 | 15.0312 | 18.5876 | 23.052 | 26.4073 | 29.7595
| VittoriaIce Accretion2075RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2075 | 14.5659 | 18.0702 | 22.44 | 25.7286 | 29.017
| VittoriaIce Accretion2080RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2080 | 14.1006 | 17.5528 | 21.828 | 25.0498 | 28.2744
| VittoriaIce Accretion2085RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2085 | 13.0596 | 16.297 | 20.332 | 23.3594 | 26.3894
| VittoriaIce Accretion2090RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2090 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
| VittoriaIce Accretion2095RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2095 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
| VittoriaIce Accretion2100RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2100 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
| VittoriaWind2023RCP4.5 | Vittoria | Wind | RCP4.5 | 2023 | 88.6477 | 95.5809 | 102.8976 | 110.1877 | 117.4893
| VittoriaWind2025RCP4.5 | Vittoria | Wind | RCP4.5 | 2025 | 88.724 | 95.6821 | 103.0319 | 110.3515 | 117.6792
| VittoriaWind2030RCP4.5 | Vittoria | Wind | RCP4.5 | 2030 | 88.8004 | 95.7833 | 103.1662 | 110.5152 | 117.8692
| VittoriaWind2035RCP4.5 | Vittoria | Wind | RCP4.5 | 2035 | 88.8767 | 95.8845 | 103.3005 | 110.6789 | 118.0591
| VittoriaWind2040RCP4.5 | Vittoria | Wind | RCP4.5 | 2040 | 88.953 | 95.9857 | 103.4348 | 110.8426 | 118.249
| VittoriaWind2045RCP4.5 | Vittoria | Wind | RCP4.5 | 2045 | 89.0294 | 96.0869 | 103.5691 | 111.0063 | 118.4389
| VittoriaWind2050RCP4.5 | Vittoria | Wind | RCP4.5 | 2050 | 89.185 | 96.2943 | 103.8442 | 111.3381 | 118.8289
| VittoriaWind2055RCP4.5 | Vittoria | Wind | RCP4.5 | 2055 | 89.2642 | 96.4005 | 103.9849 | 111.5062 | 119.0289
| VittoriaWind2060RCP4.5 | Vittoria | Wind | RCP4.5 | 2060 | 89.3435 | 96.5068 | 104.1257 | 111.6742 | 119.2289
| VittoriaWind2065RCP4.5 | Vittoria | Wind | RCP4.5 | 2065 | 89.4228 | 96.613 | 104.2664 | 111.8423 | 119.4289
| VittoriaWind2070RCP4.5 | Vittoria | Wind | RCP4.5 | 2070 | 89.502 | 96.7193 | 104.4072 | 112.0104 | 119.6289
| VittoriaWind2075RCP4.5 | Vittoria | Wind | RCP4.5 | 2075 | 89.6224 | 96.8742 | 104.6061 | 112.2469 | 119.906
| VittoriaWind2080RCP4.5 | Vittoria | Wind | RCP4.5 | 2080 | 89.7428 | 97.0291 | 104.805 | 112.4833 | 120.1831
| VittoriaWind2085RCP4.5 | Vittoria | Wind | RCP4.5 | 2085 | 89.8631 | 97.1841 | 105.0039 | 112.7198 | 120.4603
| VittoriaWind2090RCP4.5 | Vittoria | Wind | RCP4.5 | 2090 | 89.9835 | 97.339 | 105.2028 | 112.9563 | 120.7374
| VittoriaWind2095RCP4.5 | Vittoria | Wind | RCP4.5 | 2095 | 90.1039 | 97.4939 | 105.4017 | 113.1927 | 121.0145
| VittoriaWind2100RCP4.5 | Vittoria | Wind | RCP4.5 | 2100 | 90.2242 | 97.6489 | 105.6006 | 113.4292 | 121.2917
| VittoriaWind2023RCP6.0 | Vittoria | Wind | RCP6.0 | 2023 | 88.6477 | 95.5809 | 102.8976 | 110.1877 | 117.4893
| VittoriaWind2025RCP6.0 | Vittoria | Wind | RCP6.0 | 2025 | 88.724 | 95.6821 | 103.0319 | 110.3515 | 117.6792
| VittoriaWind2030RCP6.0 | Vittoria | Wind | RCP6.0 | 2030 | 88.8004 | 95.7833 | 103.1662 | 110.5152 | 117.8692
| VittoriaWind2035RCP6.0 | Vittoria | Wind | RCP6.0 | 2035 | 88.8767 | 95.8845 | 103.3005 | 110.6789 | 118.0591
| VittoriaWind2040RCP6.0 | Vittoria | Wind | RCP6.0 | 2040 | 88.953 | 95.9857 | 103.4348 | 110.8426 | 118.249
| VittoriaWind2045RCP6.0 | Vittoria | Wind | RCP6.0 | 2045 | 89.0294 | 96.0869 | 103.5691 | 111.0063 | 118.4389
| VittoriaWind2050RCP6.0 | Vittoria | Wind | RCP6.0 | 2050 | 89.185 | 96.2943 | 103.8442 | 111.3381 | 118.8289
| VittoriaWind2055RCP6.0 | Vittoria | Wind | RCP6.0 | 2055 | 89.2642 | 96.4005 | 103.9849 | 111.5062 | 119.0289
| VittoriaWind2060RCP6.0 | Vittoria | Wind | RCP6.0 | 2060 | 89.3435 | 96.5068 | 104.1257 | 111.6742 | 119.2289
| VittoriaWind2065RCP6.0 | Vittoria | Wind | RCP6.0 | 2065 | 89.4228 | 96.613 | 104.2664 | 111.8423 | 119.4289
| VittoriaWind2070RCP6.0 | Vittoria | Wind | RCP6.0 | 2070 | 89.502 | 96.7193 | 104.4072 | 112.0104 | 119.6289
| VittoriaWind2075RCP6.0 | Vittoria | Wind | RCP6.0 | 2075 | 89.6826 | 96.9517 | 104.7056 | 112.3651 | 120.0446
| VittoriaWind2080RCP6.0 | Vittoria | Wind | RCP6.0 | 2080 | 89.8631 | 97.1841 | 105.0039 | 112.7198 | 120.4603
| VittoriaWind2085RCP6.0 | Vittoria | Wind | RCP6.0 | 2085 | 90.0437 | 97.4165 | 105.3022 | 113.0745 | 120.876
| VittoriaWind2090RCP6.0 | Vittoria | Wind | RCP6.0 | 2090 | 90.4826 | 97.9841 | 106.0256 | 113.9349 | 121.8731
| VittoriaWind2095RCP6.0 | Vittoria | Wind | RCP6.0 | 2095 | 90.741 | 98.3192 | 106.4506 | 114.4406 | 122.4545
| VittoriaWind2100RCP6.0 | Vittoria | Wind | RCP6.0 | 2100 | 90.9993 | 98.6544 | 106.8756 | 114.9462 | 123.0359
| VittoriaWind2023RCP8.5 | Vittoria | Wind | RCP8.5 | 2023 | 88.6477 | 95.5809 | 102.8976 | 110.1877 | 117.4893
| VittoriaWind2025RCP8.5 | Vittoria | Wind | RCP8.5 | 2025 | 88.8004 | 95.7833 | 103.1662 | 110.5152 | 117.8692
| VittoriaWind2030RCP8.5 | Vittoria | Wind | RCP8.5 | 2030 | 88.953 | 95.9857 | 103.4348 | 110.8426 | 118.249
| VittoriaWind2035RCP8.5 | Vittoria | Wind | RCP8.5 | 2035 | 89.1057 | 96.188 | 103.7034 | 111.17 | 118.6289
| VittoriaWind2040RCP8.5 | Vittoria | Wind | RCP8.5 | 2040 | 89.2378 | 96.3651 | 103.938 | 111.4501 | 118.9622
| VittoriaWind2045RCP8.5 | Vittoria | Wind | RCP8.5 | 2045 | 89.3699 | 96.5422 | 104.1726 | 111.7303 | 119.2955
| VittoriaWind2050RCP8.5 | Vittoria | Wind | RCP8.5 | 2050 | 89.7428 | 97.0291 | 104.805 | 112.4833 | 120.1831
| VittoriaWind2055RCP8.5 | Vittoria | Wind | RCP8.5 | 2055 | 89.9835 | 97.339 | 105.2028 | 112.9563 | 120.7374
| VittoriaWind2060RCP8.5 | Vittoria | Wind | RCP8.5 | 2060 | 90.4826 | 97.9841 | 106.0256 | 113.9349 | 121.8731
| VittoriaWind2065RCP8.5 | Vittoria | Wind | RCP8.5 | 2065 | 90.741 | 98.3192 | 106.4506 | 114.4406 | 122.4545
| VittoriaWind2070RCP8.5 | Vittoria | Wind | RCP8.5 | 2070 | 91.149 | 98.8663 | 107.168 | 115.3064 | 123.4661
| VittoriaWind2075RCP8.5 | Vittoria | Wind | RCP8.5 | 2075 | 91.2988 | 99.0781 | 107.4604 | 115.6666 | 123.8963
| VittoriaWind2080RCP8.5 | Vittoria | Wind | RCP8.5 | 2080 | 91.4485 | 99.29 | 107.7528 | 116.0267 | 124.3266
| VittoriaWind2085RCP8.5 | Vittoria | Wind | RCP8.5 | 2085 | 91.792 | 99.7405 | 108.3495 | 116.7361 | 125.1638
| VittoriaWind2090RCP8.5 | Vittoria | Wind | RCP8.5 | 2090 | 92.1355 | 100.1911 | 108.9462 | 117.4456 | 126.001
| VittoriaWind2095RCP8.5 | Vittoria | Wind | RCP8.5 | 2095 | 92.1355 | 100.1911 | 108.9462 | 117.4456 | 126.001
| VittoriaWind2100RCP8.5 | Vittoria | Wind | RCP8.5 | 2100 | 92.1355 | 100.1911 | 108.9462 | 117.4456 | 126.001
| WalkertonIce Accretion2023RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2023 | 15.9885 | 19.1664 | 23.207 | 26.2759 | 29.3567
| WalkertonIce Accretion2025RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2025 | 15.9938 | 19.1886 | 23.2415 | 26.3235 | 29.4195
| WalkertonIce Accretion2030RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2030 | 15.9991 | 19.2109 | 23.276 | 26.3712 | 29.4823
| WalkertonIce Accretion2035RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2035 | 16.0045 | 19.2332 | 23.3105 | 26.4188 | 29.5451
| WalkertonIce Accretion2040RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2040 | 16.0098 | 19.2554 | 23.345 | 26.4665 | 29.6079
| WalkertonIce Accretion2045RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2045 | 16.0151 | 19.2777 | 23.3795 | 26.5141 | 29.6707
| WalkertonIce Accretion2050RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2050 | 16.0141 | 19.3114 | 23.4554 | 26.6242 | 29.8146
| WalkertonIce Accretion2055RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2055 | 16.0077 | 19.3229 | 23.4968 | 26.6865 | 29.8958
| WalkertonIce Accretion2060RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2060 | 16.0013 | 19.3344 | 23.5382 | 26.7489 | 29.9769
| WalkertonIce Accretion2065RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2065 | 15.9949 | 19.3458 | 23.5796 | 26.8113 | 30.0581
| WalkertonIce Accretion2070RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2070 | 15.9885 | 19.3573 | 23.621 | 26.8737 | 30.1392
| WalkertonIce Accretion2075RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2075 | 15.9191 | 19.3 | 23.5827 | 26.8433 | 30.1199
| WalkertonIce Accretion2080RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2080 | 15.8498 | 19.2427 | 23.5443 | 26.813 | 30.1006
| WalkertonIce Accretion2085RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2085 | 15.7804 | 19.1854 | 23.506 | 26.7827 | 30.0812
| WalkertonIce Accretion2090RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2090 | 15.711 | 19.1282 | 23.4677 | 26.7524 | 30.0619
| WalkertonIce Accretion2095RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2095 | 15.6417 | 19.0709 | 23.4293 | 26.7221 | 30.0426
| WalkertonIce Accretion2100RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2100 | 15.5723 | 19.0136 | 23.391 | 26.6917 | 30.0233
| WalkertonIce Accretion2023RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2023 | 15.9885 | 19.1664 | 23.207 | 26.2759 | 29.3567
| WalkertonIce Accretion2025RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2025 | 15.9938 | 19.1886 | 23.2415 | 26.3235 | 29.4195
| WalkertonIce Accretion2030RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2030 | 15.9991 | 19.2109 | 23.276 | 26.3712 | 29.4823
| WalkertonIce Accretion2035RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2035 | 16.0045 | 19.2332 | 23.3105 | 26.4188 | 29.5451
| WalkertonIce Accretion2040RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2040 | 16.0098 | 19.2554 | 23.345 | 26.4665 | 29.6079
| WalkertonIce Accretion2045RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2045 | 16.0151 | 19.2777 | 23.3795 | 26.5141 | 29.6707
| WalkertonIce Accretion2050RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2050 | 16.0141 | 19.3114 | 23.4554 | 26.6242 | 29.8146
| WalkertonIce Accretion2055RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2055 | 16.0077 | 19.3229 | 23.4968 | 26.6865 | 29.8958
| WalkertonIce Accretion2060RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2060 | 16.0013 | 19.3344 | 23.5382 | 26.7489 | 29.9769
| WalkertonIce Accretion2065RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2065 | 15.9949 | 19.3458 | 23.5796 | 26.8113 | 30.0581
| WalkertonIce Accretion2070RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2070 | 15.9885 | 19.3573 | 23.621 | 26.8737 | 30.1392
| WalkertonIce Accretion2075RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2075 | 15.8844 | 19.2714 | 23.5635 | 26.8282 | 30.1102
| WalkertonIce Accretion2080RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2080 | 15.7804 | 19.1854 | 23.506 | 26.7827 | 30.0812
| WalkertonIce Accretion2085RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2085 | 15.6764 | 19.0995 | 23.4485 | 26.7372 | 30.0523
| WalkertonIce Accretion2090RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2090 | 15.3056 | 18.7337 | 23.0767 | 26.3625 | 29.6659
| WalkertonIce Accretion2095RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2095 | 15.0389 | 18.4537 | 22.7623 | 26.0333 | 29.3084
| WalkertonIce Accretion2100RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2100 | 14.7721 | 18.1737 | 22.448 | 25.7041 | 28.951
| WalkertonIce Accretion2023RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2023 | 15.9885 | 19.1664 | 23.207 | 26.2759 | 29.3567
| WalkertonIce Accretion2025RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2025 | 15.9991 | 19.2109 | 23.276 | 26.3712 | 29.4823
| WalkertonIce Accretion2030RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2030 | 16.0098 | 19.2554 | 23.345 | 26.4665 | 29.6079
| WalkertonIce Accretion2035RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2035 | 16.0205 | 19.3 | 23.414 | 26.5618 | 29.7335
| WalkertonIce Accretion2040RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2040 | 16.0098 | 19.3191 | 23.483 | 26.6657 | 29.8687
| WalkertonIce Accretion2045RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2045 | 15.9991 | 19.3382 | 23.552 | 26.7697 | 30.004
| WalkertonIce Accretion2050RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2050 | 15.8498 | 19.2427 | 23.5443 | 26.813 | 30.1006
| WalkertonIce Accretion2055RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2055 | 15.711 | 19.1282 | 23.4677 | 26.7524 | 30.0619
| WalkertonIce Accretion2060RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2060 | 15.3056 | 18.7337 | 23.0767 | 26.3625 | 29.6659
| WalkertonIce Accretion2065RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2065 | 15.0389 | 18.4537 | 22.7623 | 26.0333 | 29.3084
| WalkertonIce Accretion2070RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2070 | 14.3347 | 17.6773 | 21.8883 | 25.089 | 28.2845
| WalkertonIce Accretion2075RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2075 | 13.8972 | 17.181 | 21.3287 | 24.4739 | 27.6179
| WalkertonIce Accretion2080RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2080 | 13.4598 | 16.6847 | 20.769 | 23.8588 | 26.9514
| WalkertonIce Accretion2085RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2085 | 13.0196 | 16.1979 | 20.217 | 23.261 | 26.3138
| WalkertonIce Accretion2090RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2090 | 12.5795 | 15.7111 | 19.665 | 22.6633 | 25.6763
| WalkertonIce Accretion2095RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2095 | 12.5795 | 15.7111 | 19.665 | 22.6633 | 25.6763
| WalkertonIce Accretion2100RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2100 | 12.5795 | 15.7111 | 19.665 | 22.6633 | 25.6763
| WalkertonWind2023RCP4.5 | Walkerton | Wind | RCP4.5 | 2023 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2506
| WalkertonWind2025RCP4.5 | Walkerton | Wind | RCP4.5 | 2025 | 85.4139 | 92.1425 | 99.2626 | 106.3385 | 113.42
| WalkertonWind2030RCP4.5 | Walkerton | Wind | RCP4.5 | 2030 | 85.4957 | 92.2428 | 99.3883 | 106.4853 | 113.5894
| WalkertonWind2035RCP4.5 | Walkerton | Wind | RCP4.5 | 2035 | 85.5775 | 92.343 | 99.5141 | 106.6321 | 113.7589
| WalkertonWind2040RCP4.5 | Walkerton | Wind | RCP4.5 | 2040 | 85.6593 | 92.4433 | 99.6399 | 106.7789 | 113.9283
| WalkertonWind2045RCP4.5 | Walkerton | Wind | RCP4.5 | 2045 | 85.7411 | 92.5436 | 99.7656 | 106.9257 | 114.0978
| WalkertonWind2050RCP4.5 | Walkerton | Wind | RCP4.5 | 2050 | 85.8364 | 92.6566 | 99.9012 | 107.0809 | 114.2739
| WalkertonWind2055RCP4.5 | Walkerton | Wind | RCP4.5 | 2055 | 85.85 | 92.6693 | 99.911 | 107.0893 | 114.2806
| WalkertonWind2060RCP4.5 | Walkerton | Wind | RCP4.5 | 2060 | 85.8635 | 92.6821 | 99.9208 | 107.0977 | 114.2873
| WalkertonWind2065RCP4.5 | Walkerton | Wind | RCP4.5 | 2065 | 85.8771 | 92.6948 | 99.9306 | 107.1061 | 114.294
| WalkertonWind2070RCP4.5 | Walkerton | Wind | RCP4.5 | 2070 | 85.8906 | 92.7076 | 99.9404 | 107.1145 | 114.3007
| WalkertonWind2075RCP4.5 | Walkerton | Wind | RCP4.5 | 2075 | 85.9738 | 92.8155 | 100.0792 | 107.2805 | 114.4925
| WalkertonWind2080RCP4.5 | Walkerton | Wind | RCP4.5 | 2080 | 86.057 | 92.9233 | 100.2181 | 107.4465 | 114.6843
| WalkertonWind2085RCP4.5 | Walkerton | Wind | RCP4.5 | 2085 | 86.1402 | 93.0312 | 100.3569 | 107.6126 | 114.8761
| WalkertonWind2090RCP4.5 | Walkerton | Wind | RCP4.5 | 2090 | 86.2234 | 93.139 | 100.4957 | 107.7786 | 115.0679
| WalkertonWind2095RCP4.5 | Walkerton | Wind | RCP4.5 | 2095 | 86.3067 | 93.2469 | 100.6346 | 107.9446 | 115.2597
| WalkertonWind2100RCP4.5 | Walkerton | Wind | RCP4.5 | 2100 | 86.3899 | 93.3547 | 100.7734 | 108.1107 | 115.4514
| WalkertonWind2023RCP6.0 | Walkerton | Wind | RCP6.0 | 2023 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2506
| WalkertonWind2025RCP6.0 | Walkerton | Wind | RCP6.0 | 2025 | 85.4139 | 92.1425 | 99.2626 | 106.3385 | 113.42
| WalkertonWind2030RCP6.0 | Walkerton | Wind | RCP6.0 | 2030 | 85.4957 | 92.2428 | 99.3883 | 106.4853 | 113.5894
| WalkertonWind2035RCP6.0 | Walkerton | Wind | RCP6.0 | 2035 | 85.5775 | 92.343 | 99.5141 | 106.6321 | 113.7589
| WalkertonWind2040RCP6.0 | Walkerton | Wind | RCP6.0 | 2040 | 85.6593 | 92.4433 | 99.6399 | 106.7789 | 113.9283
| WalkertonWind2045RCP6.0 | Walkerton | Wind | RCP6.0 | 2045 | 85.7411 | 92.5436 | 99.7656 | 106.9257 | 114.0978
| WalkertonWind2050RCP6.0 | Walkerton | Wind | RCP6.0 | 2050 | 85.8364 | 92.6566 | 99.9012 | 107.0809 | 114.2739
| WalkertonWind2055RCP6.0 | Walkerton | Wind | RCP6.0 | 2055 | 85.85 | 92.6693 | 99.911 | 107.0893 | 114.2806
| WalkertonWind2060RCP6.0 | Walkerton | Wind | RCP6.0 | 2060 | 85.8635 | 92.6821 | 99.9208 | 107.0977 | 114.2873
| WalkertonWind2065RCP6.0 | Walkerton | Wind | RCP6.0 | 2065 | 85.8771 | 92.6948 | 99.9306 | 107.1061 | 114.294
| WalkertonWind2070RCP6.0 | Walkerton | Wind | RCP6.0 | 2070 | 85.8906 | 92.7076 | 99.9404 | 107.1145 | 114.3007
| WalkertonWind2075RCP6.0 | Walkerton | Wind | RCP6.0 | 2075 | 86.0154 | 92.8694 | 100.1487 | 107.3635 | 114.5884
| WalkertonWind2080RCP6.0 | Walkerton | Wind | RCP6.0 | 2080 | 86.1402 | 93.0312 | 100.3569 | 107.6126 | 114.8761
| WalkertonWind2085RCP6.0 | Walkerton | Wind | RCP6.0 | 2085 | 86.265 | 93.1929 | 100.5652 | 107.8616 | 115.1638
| WalkertonWind2090RCP6.0 | Walkerton | Wind | RCP6.0 | 2090 | 86.8017 | 93.8712 | 101.4169 | 108.8657 | 116.3229
| WalkertonWind2095RCP6.0 | Walkerton | Wind | RCP6.0 | 2095 | 87.2135 | 94.3876 | 102.0605 | 109.6206 | 117.1943
| WalkertonWind2100RCP6.0 | Walkerton | Wind | RCP6.0 | 2100 | 87.6253 | 94.9041 | 102.704 | 110.3756 | 118.0657
| WalkertonWind2023RCP8.5 | Walkerton | Wind | RCP8.5 | 2023 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2506
| WalkertonWind2025RCP8.5 | Walkerton | Wind | RCP8.5 | 2025 | 85.4957 | 92.2428 | 99.3883 | 106.4853 | 113.5894
| WalkertonWind2030RCP8.5 | Walkerton | Wind | RCP8.5 | 2030 | 85.6593 | 92.4433 | 99.6399 | 106.7789 | 113.9283
| WalkertonWind2035RCP8.5 | Walkerton | Wind | RCP8.5 | 2035 | 85.8229 | 92.6438 | 99.8914 | 107.0725 | 114.2672
| WalkertonWind2040RCP8.5 | Walkerton | Wind | RCP8.5 | 2040 | 85.8455 | 92.6651 | 99.9077 | 107.0865 | 114.2784
| WalkertonWind2045RCP8.5 | Walkerton | Wind | RCP8.5 | 2045 | 85.868 | 92.6863 | 99.9241 | 107.1005 | 114.2896
| WalkertonWind2050RCP8.5 | Walkerton | Wind | RCP8.5 | 2050 | 86.057 | 92.9233 | 100.2181 | 107.4465 | 114.6843
| WalkertonWind2055RCP8.5 | Walkerton | Wind | RCP8.5 | 2055 | 86.2234 | 93.139 | 100.4957 | 107.7786 | 115.0679
| WalkertonWind2060RCP8.5 | Walkerton | Wind | RCP8.5 | 2060 | 86.8017 | 93.8712 | 101.4169 | 108.8657 | 116.3229
| WalkertonWind2065RCP8.5 | Walkerton | Wind | RCP8.5 | 2065 | 87.2135 | 94.3876 | 102.0605 | 109.6206 | 117.1943
| WalkertonWind2070RCP8.5 | Walkerton | Wind | RCP8.5 | 2070 | 87.8397 | 95.1653 | 103.0241 | 110.7461 | 118.4865
| WalkertonWind2075RCP8.5 | Walkerton | Wind | RCP8.5 | 2075 | 88.0541 | 95.4266 | 103.3443 | 111.1166 | 118.9073
| WalkertonWind2080RCP8.5 | Walkerton | Wind | RCP8.5 | 2080 | 88.2685 | 95.6879 | 103.6644 | 111.4872 | 119.3281
| WalkertonWind2085RCP8.5 | Walkerton | Wind | RCP8.5 | 2085 | 88.2896 | 95.697 | 103.6644 | 111.4714 | 119.3058
| WalkertonWind2090RCP8.5 | Walkerton | Wind | RCP8.5 | 2090 | 88.3108 | 95.7061 | 103.6644 | 111.4557 | 119.2834
| WalkertonWind2095RCP8.5 | Walkerton | Wind | RCP8.5 | 2095 | 88.3108 | 95.7061 | 103.6644 | 111.4557 | 119.2834
| WalkertonWind2100RCP8.5 | Walkerton | Wind | RCP8.5 | 2100 | 88.3108 | 95.7061 | 103.6644 | 111.4557 | 119.2834
| WallaceburgIce Accretion2023RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2023 | 15.4123 | 18.46 | 22.333 | 25.2623 | 28.2265
| WallaceburgIce Accretion2025RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2025 | 15.3376 | 18.3869 | 22.2563 | 25.1843 | 28.1444
| WallaceburgIce Accretion2030RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2030 | 15.2629 | 18.3137 | 22.1797 | 25.1063 | 28.0623
| WallaceburgIce Accretion2035RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2035 | 15.1882 | 18.2405 | 22.103 | 25.0284 | 27.9802
| WallaceburgIce Accretion2040RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2040 | 15.1135 | 18.1673 | 22.0263 | 24.9504 | 27.8981
| WallaceburgIce Accretion2045RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2045 | 15.0389 | 18.0941 | 21.9497 | 24.8724 | 27.816
| WallaceburgIce Accretion2050RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2050 | 14.6921 | 17.7193 | 21.5326 | 24.4306 | 27.3339
| WallaceburgIce Accretion2055RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2055 | 14.42 | 17.4177 | 21.1922 | 24.0667 | 26.934
| WallaceburgIce Accretion2060RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2060 | 14.1479 | 17.1161 | 20.8518 | 23.7029 | 26.5341
| WallaceburgIce Accretion2065RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2065 | 13.8759 | 16.8145 | 20.5114 | 23.339 | 26.1342
| WallaceburgIce Accretion2070RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2070 | 13.6038 | 16.5129 | 20.171 | 22.9752 | 25.7342
| WallaceburgIce Accretion2075RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2075 | 13.2837 | 16.147 | 19.7493 | 22.503 | 25.2174
| WallaceburgIce Accretion2080RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2080 | 12.9636 | 15.7811 | 19.3277 | 22.0309 | 24.7006
| WallaceburgIce Accretion2085RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2085 | 12.6435 | 15.4152 | 18.906 | 21.5587 | 24.1838
| WallaceburgIce Accretion2090RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2090 | 12.3234 | 15.0493 | 18.4843 | 21.0866 | 23.667
| WallaceburgIce Accretion2095RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2095 | 12.0033 | 14.6834 | 18.0627 | 20.6144 | 23.1502
| WallaceburgIce Accretion2100RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2100 | 11.6833 | 14.3175 | 17.641 | 20.1423 | 22.6334
| WallaceburgIce Accretion2023RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2023 | 15.4123 | 18.46 | 22.333 | 25.2623 | 28.2265
| WallaceburgIce Accretion2025RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2025 | 15.3376 | 18.3869 | 22.2563 | 25.1843 | 28.1444
| WallaceburgIce Accretion2030RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2030 | 15.2629 | 18.3137 | 22.1797 | 25.1063 | 28.0623
| WallaceburgIce Accretion2035RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2035 | 15.1882 | 18.2405 | 22.103 | 25.0284 | 27.9802
| WallaceburgIce Accretion2040RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2040 | 15.1135 | 18.1673 | 22.0263 | 24.9504 | 27.8981
| WallaceburgIce Accretion2045RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2045 | 15.0389 | 18.0941 | 21.9497 | 24.8724 | 27.816
| WallaceburgIce Accretion2050RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2050 | 14.6921 | 17.7193 | 21.5326 | 24.4306 | 27.3339
| WallaceburgIce Accretion2055RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2055 | 14.42 | 17.4177 | 21.1922 | 24.0667 | 26.934
| WallaceburgIce Accretion2060RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2060 | 14.1479 | 17.1161 | 20.8518 | 23.7029 | 26.5341
| WallaceburgIce Accretion2065RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2065 | 13.8759 | 16.8145 | 20.5114 | 23.339 | 26.1342
| WallaceburgIce Accretion2070RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2070 | 13.6038 | 16.5129 | 20.171 | 22.9752 | 25.7342
| WallaceburgIce Accretion2075RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2075 | 13.1237 | 15.964 | 19.5385 | 22.2669 | 24.959
| WallaceburgIce Accretion2080RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2080 | 12.6435 | 15.4152 | 18.906 | 21.5587 | 24.1838
| WallaceburgIce Accretion2085RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2085 | 12.1634 | 14.8663 | 18.2735 | 20.8505 | 23.4086
| WallaceburgIce Accretion2090RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2090 | 11.2031 | 13.7639 | 16.9893 | 19.4145 | 21.8316
| WallaceburgIce Accretion2095RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2095 | 10.723 | 13.2103 | 16.3377 | 18.6868 | 21.0298
| WallaceburgIce Accretion2100RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2100 | 10.2429 | 12.6567 | 15.686 | 17.9591 | 20.228
| WallaceburgIce Accretion2023RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2023 | 15.4123 | 18.46 | 22.333 | 25.2623 | 28.2265
| WallaceburgIce Accretion2025RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2025 | 15.2629 | 18.3137 | 22.1797 | 25.1063 | 28.0623
| WallaceburgIce Accretion2030RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2030 | 15.1135 | 18.1673 | 22.0263 | 24.9504 | 27.8981
| WallaceburgIce Accretion2035RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2035 | 14.9642 | 18.021 | 21.873 | 24.7945 | 27.7339
| WallaceburgIce Accretion2040RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2040 | 14.5107 | 17.5183 | 21.3057 | 24.188 | 27.0673
| WallaceburgIce Accretion2045RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2045 | 14.0573 | 17.0156 | 20.7383 | 23.5816 | 26.4008
| WallaceburgIce Accretion2050RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2050 | 12.9636 | 15.7811 | 19.3277 | 22.0309 | 24.7006
| WallaceburgIce Accretion2055RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2055 | 12.3234 | 15.0493 | 18.4843 | 21.0866 | 23.667
| WallaceburgIce Accretion2060RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2060 | 11.2031 | 13.7639 | 16.9893 | 19.4145 | 21.8316
| WallaceburgIce Accretion2065RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2065 | 10.723 | 13.2103 | 16.3377 | 18.6868 | 21.0298
| WallaceburgIce Accretion2070RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2070 | 9.7521 | 12.084 | 15.0037 | 17.1967 | 19.378
| WallaceburgIce Accretion2075RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2075 | 9.2612 | 11.5113 | 14.3213 | 16.4343 | 18.5279
| WallaceburgIce Accretion2080RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2080 | 8.7704 | 10.9386 | 13.639 | 15.672 | 17.6778
| WallaceburgIce Accretion2085RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2085 | 8.1463 | 10.2036 | 12.765 | 14.6843 | 16.591
| WallaceburgIce Accretion2090RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2090 | 7.5221 | 9.4686 | 11.891 | 13.6967 | 15.5043
| WallaceburgIce Accretion2095RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2095 | 7.5221 | 9.4686 | 11.891 | 13.6967 | 15.5043
| WallaceburgIce Accretion2100RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2100 | 7.5221 | 9.4686 | 11.891 | 13.6967 | 15.5043
| WallaceburgWind2023RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2023 | 85.1205 | 91.7051 | 98.637 | 105.573 | 112.502
| WallaceburgWind2025RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2025 | 85.1614 | 91.7643 | 98.7203 | 105.6744 | 112.6249
| WallaceburgWind2030RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2030 | 85.2023 | 91.8235 | 98.8036 | 105.7758 | 112.7478
| WallaceburgWind2035RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2035 | 85.2432 | 91.8828 | 98.8869 | 105.8771 | 112.8707
| WallaceburgWind2040RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2040 | 85.2841 | 91.942 | 98.9702 | 105.9785 | 112.9936
| WallaceburgWind2045RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2045 | 85.325 | 92.0013 | 99.0535 | 106.0799 | 113.1165
| WallaceburgWind2050RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2050 | 85.3507 | 92.0332 | 99.0956 | 106.1288 | 113.1724
| WallaceburgWind2055RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2055 | 85.3355 | 92.0058 | 99.0545 | 106.0764 | 113.1053
| WallaceburgWind2060RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2060 | 85.3202 | 91.9785 | 99.0133 | 106.0239 | 113.0383
| WallaceburgWind2065RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2065 | 85.305 | 91.9511 | 98.9722 | 105.9715 | 112.9713
| WallaceburgWind2070RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2070 | 85.2898 | 91.9238 | 98.931 | 105.9191 | 112.9042
| WallaceburgWind2075RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2075 | 85.4618 | 92.1456 | 99.2136 | 106.2546 | 113.2934
| WallaceburgWind2080RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2080 | 85.6339 | 92.3674 | 99.4961 | 106.5902 | 113.6825
| WallaceburgWind2085RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2085 | 85.806 | 92.5891 | 99.7787 | 106.9257 | 114.0717
| WallaceburgWind2090RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2090 | 85.978 | 92.8109 | 100.0613 | 107.2613 | 114.4609
| WallaceburgWind2095RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2095 | 86.1501 | 93.0327 | 100.3438 | 107.5968 | 114.85
| WallaceburgWind2100RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2100 | 86.3222 | 93.2544 | 100.6264 | 107.9324 | 115.2392
| WallaceburgWind2023RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2023 | 85.1205 | 91.7051 | 98.637 | 105.573 | 112.502
| WallaceburgWind2025RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2025 | 85.1614 | 91.7643 | 98.7203 | 105.6744 | 112.6249
| WallaceburgWind2030RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2030 | 85.2023 | 91.8235 | 98.8036 | 105.7758 | 112.7478
| WallaceburgWind2035RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2035 | 85.2432 | 91.8828 | 98.8869 | 105.8771 | 112.8707
| WallaceburgWind2040RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2040 | 85.2841 | 91.942 | 98.9702 | 105.9785 | 112.9936
| WallaceburgWind2045RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2045 | 85.325 | 92.0013 | 99.0535 | 106.0799 | 113.1165
| WallaceburgWind2050RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2050 | 85.3507 | 92.0332 | 99.0956 | 106.1288 | 113.1724
| WallaceburgWind2055RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2055 | 85.3355 | 92.0058 | 99.0545 | 106.0764 | 113.1053
| WallaceburgWind2060RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2060 | 85.3202 | 91.9785 | 99.0133 | 106.0239 | 113.0383
| WallaceburgWind2065RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2065 | 85.305 | 91.9511 | 98.9722 | 105.9715 | 112.9713
| WallaceburgWind2070RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2070 | 85.2898 | 91.9238 | 98.931 | 105.9191 | 112.9042
| WallaceburgWind2075RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2075 | 85.5479 | 92.2565 | 99.3548 | 106.4224 | 113.488
| WallaceburgWind2080RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2080 | 85.806 | 92.5891 | 99.7787 | 106.9257 | 114.0717
| WallaceburgWind2085RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2085 | 86.0641 | 92.9218 | 100.2026 | 107.4291 | 114.6554
| WallaceburgWind2090RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2090 | 86.6663 | 93.6615 | 101.1131 | 108.4847 | 115.8611
| WallaceburgWind2095RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2095 | 87.0104 | 94.0686 | 101.5999 | 109.0369 | 116.483
| WallaceburgWind2100RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2100 | 87.3545 | 94.4757 | 102.0866 | 109.5892 | 117.1049
| WallaceburgWind2023RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2023 | 85.1205 | 91.7051 | 98.637 | 105.573 | 112.502
| WallaceburgWind2025RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2025 | 85.2023 | 91.8235 | 98.8036 | 105.7758 | 112.7478
| WallaceburgWind2030RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2030 | 85.2841 | 91.942 | 98.9702 | 105.9785 | 112.9936
| WallaceburgWind2035RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2035 | 85.3659 | 92.0605 | 99.1368 | 106.1812 | 113.2394
| WallaceburgWind2040RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2040 | 85.3406 | 92.0149 | 99.0682 | 106.0939 | 113.1277
| WallaceburgWind2045RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2045 | 85.3152 | 91.9694 | 98.9996 | 106.0065 | 113.016
| WallaceburgWind2050RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2050 | 85.6339 | 92.3674 | 99.4961 | 106.5902 | 113.6825
| WallaceburgWind2055RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2055 | 85.978 | 92.8109 | 100.0613 | 107.2613 | 114.4609
| WallaceburgWind2060RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2060 | 86.6663 | 93.6615 | 101.1131 | 108.4847 | 115.8611
| WallaceburgWind2065RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2065 | 87.0104 | 94.0686 | 101.5999 | 109.0369 | 116.483
| WallaceburgWind2070RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2070 | 87.5971 | 94.7826 | 102.4655 | 110.0331 | 117.6151
| WallaceburgWind2075RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2075 | 87.8397 | 95.0894 | 102.8445 | 110.477 | 118.1253
| WallaceburgWind2080RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2080 | 88.0823 | 95.3962 | 103.2234 | 110.9209 | 118.6355
| WallaceburgWind2085RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2085 | 88.5646 | 96.0205 | 104.0319 | 111.8804 | 119.7471
| WallaceburgWind2090RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2090 | 89.047 | 96.6449 | 104.8404 | 112.8398 | 120.8587
| WallaceburgWind2095RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2095 | 89.047 | 96.6449 | 104.8404 | 112.8398 | 120.8587
| WallaceburgWind2100RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2100 | 89.047 | 96.6449 | 104.8404 | 112.8398 | 120.8587
| WaterlooIce Accretion2023RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
| WaterlooIce Accretion2025RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2025 | 17.3208 | 20.7984 | 25.1958 | 28.5655 | 31.92
| WaterlooIce Accretion2030RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2030 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
| WaterlooIce Accretion2035RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2035 | 17.3788 | 20.8953 | 25.3375 | 28.7444 | 32.13
| WaterlooIce Accretion2040RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2040 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
| WaterlooIce Accretion2045RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2045 | 17.4367 | 20.9921 | 25.4792 | 28.9233 | 32.34
| WaterlooIce Accretion2050RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2050 | 17.4101 | 20.9907 | 25.51 | 28.9788 | 32.4198
| WaterlooIce Accretion2055RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2055 | 17.3544 | 20.9409 | 25.47 | 28.9449 | 32.3946
| WaterlooIce Accretion2060RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2060 | 17.2987 | 20.8911 | 25.43 | 28.911 | 32.3694
| WaterlooIce Accretion2065RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2065 | 17.2431 | 20.8413 | 25.39 | 28.8771 | 32.3442
| WaterlooIce Accretion2070RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2070 | 17.1874 | 20.7915 | 25.35 | 28.8432 | 32.319
| WaterlooIce Accretion2075RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2075 | 17.1555 | 20.7846 | 25.3708 | 28.8809 | 32.3768
| WaterlooIce Accretion2080RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2080 | 17.1236 | 20.7777 | 25.3917 | 28.9186 | 32.4345
| WaterlooIce Accretion2085RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2085 | 17.0917 | 20.7707 | 25.4125 | 28.9562 | 32.4922
| WaterlooIce Accretion2090RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2090 | 17.0598 | 20.7638 | 25.4333 | 28.9939 | 32.55
| WaterlooIce Accretion2095RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2095 | 17.0279 | 20.7569 | 25.4542 | 29.0316 | 32.6077
| WaterlooIce Accretion2100RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2100 | 16.996 | 20.75 | 25.475 | 29.0692 | 32.6655
| WaterlooIce Accretion2023RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
| WaterlooIce Accretion2025RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2025 | 17.3208 | 20.7984 | 25.1958 | 28.5655 | 31.92
| WaterlooIce Accretion2030RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2030 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
| WaterlooIce Accretion2035RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2035 | 17.3788 | 20.8953 | 25.3375 | 28.7444 | 32.13
| WaterlooIce Accretion2040RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2040 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
| WaterlooIce Accretion2045RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2045 | 17.4367 | 20.9921 | 25.4792 | 28.9233 | 32.34
| WaterlooIce Accretion2050RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2050 | 17.4101 | 20.9907 | 25.51 | 28.9788 | 32.4198
| WaterlooIce Accretion2055RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2055 | 17.3544 | 20.9409 | 25.47 | 28.9449 | 32.3946
| WaterlooIce Accretion2060RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2060 | 17.2987 | 20.8911 | 25.43 | 28.911 | 32.3694
| WaterlooIce Accretion2065RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2065 | 17.2431 | 20.8413 | 25.39 | 28.8771 | 32.3442
| WaterlooIce Accretion2070RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2070 | 17.1874 | 20.7915 | 25.35 | 28.8432 | 32.319
| WaterlooIce Accretion2075RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2075 | 17.1396 | 20.7811 | 25.3813 | 28.8997 | 32.4056
| WaterlooIce Accretion2080RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2080 | 17.0917 | 20.7707 | 25.4125 | 28.9562 | 32.4922
| WaterlooIce Accretion2085RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2085 | 17.0439 | 20.7604 | 25.4437 | 29.0127 | 32.5789
| WaterlooIce Accretion2090RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2090 | 16.6887 | 20.4249 | 25.1333 | 28.7114 | 32.298
| WaterlooIce Accretion2095RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2095 | 16.3814 | 20.0998 | 24.7917 | 28.3536 | 31.9305
| WaterlooIce Accretion2100RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2100 | 16.074 | 19.7747 | 24.45 | 27.9957 | 31.563
| WaterlooIce Accretion2023RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
| WaterlooIce Accretion2025RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2025 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
| WaterlooIce Accretion2030RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2030 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
| WaterlooIce Accretion2035RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2035 | 17.4657 | 21.0405 | 25.55 | 29.0127 | 32.445
| WaterlooIce Accretion2040RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2040 | 17.373 | 20.9575 | 25.4833 | 28.9562 | 32.403
| WaterlooIce Accretion2045RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2045 | 17.2802 | 20.8745 | 25.4167 | 28.8997 | 32.361
| WaterlooIce Accretion2050RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2050 | 17.1236 | 20.7777 | 25.3917 | 28.9186 | 32.4345
| WaterlooIce Accretion2055RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2055 | 17.0598 | 20.7638 | 25.4333 | 28.9939 | 32.55
| WaterlooIce Accretion2060RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2060 | 16.6887 | 20.4249 | 25.1333 | 28.7114 | 32.298
| WaterlooIce Accretion2065RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2065 | 16.3814 | 20.0998 | 24.7917 | 28.3536 | 31.9305
| WaterlooIce Accretion2070RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2070 | 15.6507 | 19.3182 | 23.95 | 27.4684 | 30.9855
| WaterlooIce Accretion2075RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2075 | 15.2274 | 18.8617 | 23.45 | 26.9411 | 30.408
| WaterlooIce Accretion2080RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2080 | 14.8041 | 18.4052 | 22.95 | 26.4137 | 29.8305
| WaterlooIce Accretion2085RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2085 | 13.9778 | 17.43 | 21.7875 | 25.086 | 28.3657
| WaterlooIce Accretion2090RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2090 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
| WaterlooIce Accretion2095RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2095 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
| WaterlooIce Accretion2100RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2100 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
| WaterlooWind2023RCP4.5 | Waterloo | Wind | RCP4.5 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
| WaterlooWind2025RCP4.5 | Waterloo | Wind | RCP4.5 | 2025 | 81.5488 | 87.8469 | 94.481 | 101.1097 | 107.7494
| WaterlooWind2030RCP4.5 | Waterloo | Wind | RCP4.5 | 2030 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
| WaterlooWind2035RCP4.5 | Waterloo | Wind | RCP4.5 | 2035 | 81.6625 | 88.0013 | 94.6909 | 101.3645 | 108.0494
| WaterlooWind2040RCP4.5 | Waterloo | Wind | RCP4.5 | 2040 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
| WaterlooWind2045RCP4.5 | Waterloo | Wind | RCP4.5 | 2045 | 81.7761 | 88.1558 | 94.9008 | 101.6193 | 108.3495
| WaterlooWind2050RCP4.5 | Waterloo | Wind | RCP4.5 | 2050 | 81.8962 | 88.3099 | 95.096 | 101.8513 | 108.6174
| WaterlooWind2055RCP4.5 | Waterloo | Wind | RCP4.5 | 2055 | 81.9595 | 88.3869 | 95.1863 | 101.9559 | 108.7353
| WaterlooWind2060RCP4.5 | Waterloo | Wind | RCP4.5 | 2060 | 82.0229 | 88.4638 | 95.2765 | 102.0605 | 108.8531
| WaterlooWind2065RCP4.5 | Waterloo | Wind | RCP4.5 | 2065 | 82.0862 | 88.5407 | 95.3668 | 102.1651 | 108.971
| WaterlooWind2070RCP4.5 | Waterloo | Wind | RCP4.5 | 2070 | 82.1495 | 88.6177 | 95.457 | 102.2697 | 109.0889
| WaterlooWind2075RCP4.5 | Waterloo | Wind | RCP4.5 | 2075 | 82.2185 | 88.7167 | 95.598 | 102.4424 | 109.2961
| WaterlooWind2080RCP4.5 | Waterloo | Wind | RCP4.5 | 2080 | 82.2875 | 88.8158 | 95.739 | 102.6151 | 109.5032
| WaterlooWind2085RCP4.5 | Waterloo | Wind | RCP4.5 | 2085 | 82.3564 | 88.9149 | 95.88 | 102.7877 | 109.7104
| WaterlooWind2090RCP4.5 | Waterloo | Wind | RCP4.5 | 2090 | 82.4254 | 89.014 | 96.021 | 102.9604 | 109.9176
| WaterlooWind2095RCP4.5 | Waterloo | Wind | RCP4.5 | 2095 | 82.4944 | 89.113 | 96.162 | 103.1331 | 110.1248
| WaterlooWind2100RCP4.5 | Waterloo | Wind | RCP4.5 | 2100 | 82.5634 | 89.2121 | 96.303 | 103.3057 | 110.3319
| WaterlooWind2023RCP6.0 | Waterloo | Wind | RCP6.0 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
| WaterlooWind2025RCP6.0 | Waterloo | Wind | RCP6.0 | 2025 | 81.5488 | 87.8469 | 94.481 | 101.1097 | 107.7494
| WaterlooWind2030RCP6.0 | Waterloo | Wind | RCP6.0 | 2030 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
| WaterlooWind2035RCP6.0 | Waterloo | Wind | RCP6.0 | 2035 | 81.6625 | 88.0013 | 94.6909 | 101.3645 | 108.0494
| WaterlooWind2040RCP6.0 | Waterloo | Wind | RCP6.0 | 2040 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
| WaterlooWind2045RCP6.0 | Waterloo | Wind | RCP6.0 | 2045 | 81.7761 | 88.1558 | 94.9008 | 101.6193 | 108.3495
| WaterlooWind2050RCP6.0 | Waterloo | Wind | RCP6.0 | 2050 | 81.8962 | 88.3099 | 95.096 | 101.8513 | 108.6174
| WaterlooWind2055RCP6.0 | Waterloo | Wind | RCP6.0 | 2055 | 81.9595 | 88.3869 | 95.1863 | 101.9559 | 108.7353
| WaterlooWind2060RCP6.0 | Waterloo | Wind | RCP6.0 | 2060 | 82.0229 | 88.4638 | 95.2765 | 102.0605 | 108.8531
| WaterlooWind2065RCP6.0 | Waterloo | Wind | RCP6.0 | 2065 | 82.0862 | 88.5407 | 95.3668 | 102.1651 | 108.971
| WaterlooWind2070RCP6.0 | Waterloo | Wind | RCP6.0 | 2070 | 82.1495 | 88.6177 | 95.457 | 102.2697 | 109.0889
| WaterlooWind2075RCP6.0 | Waterloo | Wind | RCP6.0 | 2075 | 82.253 | 88.7663 | 95.6685 | 102.5287 | 109.3996
| WaterlooWind2080RCP6.0 | Waterloo | Wind | RCP6.0 | 2080 | 82.3564 | 88.9149 | 95.88 | 102.7877 | 109.7104
| WaterlooWind2085RCP6.0 | Waterloo | Wind | RCP6.0 | 2085 | 82.4599 | 89.0635 | 96.0915 | 103.0467 | 110.0212
| WaterlooWind2090RCP6.0 | Waterloo | Wind | RCP6.0 | 2090 | 82.8421 | 89.5618 | 96.7385 | 103.8187 | 110.9213
| WaterlooWind2095RCP6.0 | Waterloo | Wind | RCP6.0 | 2095 | 83.1208 | 89.9115 | 97.1741 | 104.3316 | 111.5107
| WaterlooWind2100RCP6.0 | Waterloo | Wind | RCP6.0 | 2100 | 83.3995 | 90.2612 | 97.6096 | 104.8446 | 112.1001
| WaterlooWind2023RCP8.5 | Waterloo | Wind | RCP8.5 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
| WaterlooWind2025RCP8.5 | Waterloo | Wind | RCP8.5 | 2025 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
| WaterlooWind2030RCP8.5 | Waterloo | Wind | RCP8.5 | 2030 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
| WaterlooWind2035RCP8.5 | Waterloo | Wind | RCP8.5 | 2035 | 81.8329 | 88.233 | 95.0058 | 101.7467 | 108.4995
| WaterlooWind2040RCP8.5 | Waterloo | Wind | RCP8.5 | 2040 | 81.9384 | 88.3612 | 95.1562 | 101.9211 | 108.696
| WaterlooWind2045RCP8.5 | Waterloo | Wind | RCP8.5 | 2045 | 82.044 | 88.4894 | 95.3066 | 102.0954 | 108.8924
| WaterlooWind2050RCP8.5 | Waterloo | Wind | RCP8.5 | 2050 | 82.2875 | 88.8158 | 95.739 | 102.6151 | 109.5032
| WaterlooWind2055RCP8.5 | Waterloo | Wind | RCP8.5 | 2055 | 82.4254 | 89.014 | 96.021 | 102.9604 | 109.9176
| WaterlooWind2060RCP8.5 | Waterloo | Wind | RCP8.5 | 2060 | 82.8421 | 89.5618 | 96.7385 | 103.8187 | 110.9213
| WaterlooWind2065RCP8.5 | Waterloo | Wind | RCP8.5 | 2065 | 83.1208 | 89.9115 | 97.1741 | 104.3316 | 111.5107
| WaterlooWind2070RCP8.5 | Waterloo | Wind | RCP8.5 | 2070 | 83.6457 | 90.5933 | 98.0451 | 105.371 | 112.718
| WaterlooWind2075RCP8.5 | Waterloo | Wind | RCP8.5 | 2075 | 83.8919 | 90.9255 | 98.4807 | 105.8973 | 113.336
| WaterlooWind2080RCP8.5 | Waterloo | Wind | RCP8.5 | 2080 | 84.1381 | 91.2577 | 98.9162 | 106.4237 | 113.9539
| WaterlooWind2085RCP8.5 | Waterloo | Wind | RCP8.5 | 2085 | 84.3775 | 91.5768 | 99.3392 | 106.9266 | 114.5433
| WaterlooWind2090RCP8.5 | Waterloo | Wind | RCP8.5 | 2090 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
| WaterlooWind2095RCP8.5 | Waterloo | Wind | RCP8.5 | 2095 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
| WaterlooWind2100RCP8.5 | Waterloo | Wind | RCP8.5 | 2100 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
| WatfordIce Accretion2023RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2023 | 14.7422 | 17.6939 | 21.428 | 24.2634 | 27.1102
| WatfordIce Accretion2025RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2025 | 14.6835 | 17.6361 | 21.3693 | 24.2054 | 27.0501
| WatfordIce Accretion2030RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2030 | 14.6248 | 17.5783 | 21.3107 | 24.1473 | 26.99
| WatfordIce Accretion2035RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2035 | 14.5661 | 17.5205 | 21.252 | 24.0893 | 26.93
| WatfordIce Accretion2040RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2040 | 14.5075 | 17.4626 | 21.1933 | 24.0313 | 26.8699
| WatfordIce Accretion2045RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2045 | 14.4488 | 17.4048 | 21.1347 | 23.9733 | 26.8099
| WatfordIce Accretion2050RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2050 | 14.1207 | 17.0475 | 20.7328 | 23.5424 | 26.3451
| WatfordIce Accretion2055RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2055 | 13.8512 | 16.7481 | 20.3896 | 23.1695 | 25.9404
| WatfordIce Accretion2060RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2060 | 13.5818 | 16.4486 | 20.0464 | 22.7966 | 25.5357
| WatfordIce Accretion2065RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2065 | 13.3124 | 16.1491 | 19.7032 | 22.4237 | 25.131
| WatfordIce Accretion2070RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2070 | 13.0429 | 15.8497 | 19.36 | 22.0508 | 24.7262
| WatfordIce Accretion2075RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2075 | 12.9205 | 15.7219 | 19.228 | 21.9099 | 24.5784
| WatfordIce Accretion2080RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2080 | 12.798 | 15.594 | 19.096 | 21.7691 | 24.4306
| WatfordIce Accretion2085RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2085 | 12.6755 | 15.4662 | 18.964 | 21.6282 | 24.2827
| WatfordIce Accretion2090RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2090 | 12.5531 | 15.3384 | 18.832 | 21.4873 | 24.1349
| WatfordIce Accretion2095RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2095 | 12.4306 | 15.2106 | 18.7 | 21.3465 | 23.987
| WatfordIce Accretion2100RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2100 | 12.3081 | 15.0828 | 18.568 | 21.2056 | 23.8392
| WatfordIce Accretion2023RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2023 | 14.7422 | 17.6939 | 21.428 | 24.2634 | 27.1102
| WatfordIce Accretion2025RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2025 | 14.6835 | 17.6361 | 21.3693 | 24.2054 | 27.0501
| WatfordIce Accretion2030RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2030 | 14.6248 | 17.5783 | 21.3107 | 24.1473 | 26.99
| WatfordIce Accretion2035RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2035 | 14.5661 | 17.5205 | 21.252 | 24.0893 | 26.93
| WatfordIce Accretion2040RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2040 | 14.5075 | 17.4626 | 21.1933 | 24.0313 | 26.8699
| WatfordIce Accretion2045RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2045 | 14.4488 | 17.4048 | 21.1347 | 23.9733 | 26.8099
| WatfordIce Accretion2050RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2050 | 14.1207 | 17.0475 | 20.7328 | 23.5424 | 26.3451
| WatfordIce Accretion2055RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2055 | 13.8512 | 16.7481 | 20.3896 | 23.1695 | 25.9404
| WatfordIce Accretion2060RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2060 | 13.5818 | 16.4486 | 20.0464 | 22.7966 | 25.5357
| WatfordIce Accretion2065RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2065 | 13.3124 | 16.1491 | 19.7032 | 22.4237 | 25.131
| WatfordIce Accretion2070RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2070 | 13.0429 | 15.8497 | 19.36 | 22.0508 | 24.7262
| WatfordIce Accretion2075RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2075 | 12.8592 | 15.6579 | 19.162 | 21.8395 | 24.5045
| WatfordIce Accretion2080RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2080 | 12.6755 | 15.4662 | 18.964 | 21.6282 | 24.2827
| WatfordIce Accretion2085RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2085 | 12.4918 | 15.2745 | 18.766 | 21.4169 | 24.061
| WatfordIce Accretion2090RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2090 | 11.9356 | 14.6628 | 18.084 | 20.6669 | 23.2478
| WatfordIce Accretion2095RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2095 | 11.5631 | 14.2428 | 17.6 | 20.1283 | 22.6565
| WatfordIce Accretion2100RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2100 | 11.1906 | 13.8228 | 17.116 | 19.5897 | 22.0651
| WatfordIce Accretion2023RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2023 | 14.7422 | 17.6939 | 21.428 | 24.2634 | 27.1102
| WatfordIce Accretion2025RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2025 | 14.6248 | 17.5783 | 21.3107 | 24.1473 | 26.99
| WatfordIce Accretion2030RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2030 | 14.5075 | 17.4626 | 21.1933 | 24.0313 | 26.8699
| WatfordIce Accretion2035RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2035 | 14.3901 | 17.347 | 21.076 | 23.9153 | 26.7498
| WatfordIce Accretion2040RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2040 | 13.941 | 16.8479 | 20.504 | 23.2938 | 26.0753
| WatfordIce Accretion2045RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2045 | 13.492 | 16.3488 | 19.932 | 22.6723 | 25.4008
| WatfordIce Accretion2050RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2050 | 12.798 | 15.594 | 19.096 | 21.7691 | 24.4306
| WatfordIce Accretion2055RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2055 | 12.5531 | 15.3384 | 18.832 | 21.4873 | 24.1349
| WatfordIce Accretion2060RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2060 | 11.9356 | 14.6628 | 18.084 | 20.6669 | 23.2478
| WatfordIce Accretion2065RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2065 | 11.5631 | 14.2428 | 17.6 | 20.1283 | 22.6565
| WatfordIce Accretion2070RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2070 | 10.8997 | 13.5063 | 16.7567 | 19.2085 | 21.6493
| WatfordIce Accretion2075RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2075 | 10.6089 | 13.1898 | 16.3973 | 18.8273 | 21.2335
| WatfordIce Accretion2080RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2080 | 10.318 | 12.8733 | 16.038 | 18.4461 | 20.8177
| WatfordIce Accretion2085RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2085 | 9.6138 | 12.0333 | 15.037 | 17.3026 | 19.5565
| WatfordIce Accretion2090RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2090 | 8.9096 | 11.1934 | 14.036 | 16.159 | 18.2952
| WatfordIce Accretion2095RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2095 | 8.9096 | 11.1934 | 14.036 | 16.159 | 18.2952
| WatfordIce Accretion2100RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2100 | 8.9096 | 11.1934 | 14.036 | 16.159 | 18.2952
| WatfordWind2023RCP4.5 | Watford | Wind | RCP4.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
| WatfordWind2025RCP4.5 | Watford | Wind | RCP4.5 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
| WatfordWind2030RCP4.5 | Watford | Wind | RCP4.5 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
| WatfordWind2035RCP4.5 | Watford | Wind | RCP4.5 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
| WatfordWind2040RCP4.5 | Watford | Wind | RCP4.5 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
| WatfordWind2045RCP4.5 | Watford | Wind | RCP4.5 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
| WatfordWind2050RCP4.5 | Watford | Wind | RCP4.5 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
| WatfordWind2055RCP4.5 | Watford | Wind | RCP4.5 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
| WatfordWind2060RCP4.5 | Watford | Wind | RCP4.5 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
| WatfordWind2065RCP4.5 | Watford | Wind | RCP4.5 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
| WatfordWind2070RCP4.5 | Watford | Wind | RCP4.5 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
| WatfordWind2075RCP4.5 | Watford | Wind | RCP4.5 | 2075 | 85.7411 | 92.542 | 99.746 | 106.9048 | 114.0736
| WatfordWind2080RCP4.5 | Watford | Wind | RCP4.5 | 2080 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
| WatfordWind2085RCP4.5 | Watford | Wind | RCP4.5 | 2085 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
| WatfordWind2090RCP4.5 | Watford | Wind | RCP4.5 | 2090 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
| WatfordWind2095RCP4.5 | Watford | Wind | RCP4.5 | 2095 | 86.3278 | 93.3015 | 100.7326 | 108.0792 | 115.444
| WatfordWind2100RCP4.5 | Watford | Wind | RCP4.5 | 2100 | 86.4745 | 93.4914 | 100.9792 | 108.3728 | 115.7866
| WatfordWind2023RCP6.0 | Watford | Wind | RCP6.0 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
| WatfordWind2025RCP6.0 | Watford | Wind | RCP6.0 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
| WatfordWind2030RCP6.0 | Watford | Wind | RCP6.0 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
| WatfordWind2035RCP6.0 | Watford | Wind | RCP6.0 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
| WatfordWind2040RCP6.0 | Watford | Wind | RCP6.0 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
| WatfordWind2045RCP6.0 | Watford | Wind | RCP6.0 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
| WatfordWind2050RCP6.0 | Watford | Wind | RCP6.0 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
| WatfordWind2055RCP6.0 | Watford | Wind | RCP6.0 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
| WatfordWind2060RCP6.0 | Watford | Wind | RCP6.0 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
| WatfordWind2065RCP6.0 | Watford | Wind | RCP6.0 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
| WatfordWind2070RCP6.0 | Watford | Wind | RCP6.0 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
| WatfordWind2075RCP6.0 | Watford | Wind | RCP6.0 | 2075 | 85.8144 | 92.637 | 99.8693 | 107.0516 | 114.2449
| WatfordWind2080RCP6.0 | Watford | Wind | RCP6.0 | 2080 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
| WatfordWind2085RCP6.0 | Watford | Wind | RCP6.0 | 2085 | 86.2545 | 93.2066 | 100.6093 | 107.9324 | 115.2727
| WatfordWind2090RCP6.0 | Watford | Wind | RCP6.0 | 2090 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
| WatfordWind2095RCP6.0 | Watford | Wind | RCP6.0 | 2095 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
| WatfordWind2100RCP6.0 | Watford | Wind | RCP6.0 | 2100 | 87.5746 | 94.8494 | 102.6452 | 110.3127 | 117.9987
| WatfordWind2023RCP8.5 | Watford | Wind | RCP8.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
| WatfordWind2025RCP8.5 | Watford | Wind | RCP8.5 | 2025 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
| WatfordWind2030RCP8.5 | Watford | Wind | RCP8.5 | 2030 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
| WatfordWind2035RCP8.5 | Watford | Wind | RCP8.5 | 2035 | 85.586 | 92.3248 | 99.4504 | 106.5378 | 113.6304
| WatfordWind2040RCP8.5 | Watford | Wind | RCP8.5 | 2040 | 85.5888 | 92.3339 | 99.4667 | 106.5622 | 113.6639
| WatfordWind2045RCP8.5 | Watford | Wind | RCP8.5 | 2045 | 85.5916 | 92.343 | 99.4831 | 106.5867 | 113.6974
| WatfordWind2050RCP8.5 | Watford | Wind | RCP8.5 | 2050 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
| WatfordWind2055RCP8.5 | Watford | Wind | RCP8.5 | 2055 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
| WatfordWind2060RCP8.5 | Watford | Wind | RCP8.5 | 2060 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
| WatfordWind2065RCP8.5 | Watford | Wind | RCP8.5 | 2065 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
| WatfordWind2070RCP8.5 | Watford | Wind | RCP8.5 | 2070 | 87.882 | 95.2383 | 103.1385 | 110.8929 | 118.669
| WatfordWind2075RCP8.5 | Watford | Wind | RCP8.5 | 2075 | 88.1895 | 95.6271 | 103.6317 | 111.4732 | 119.3393
| WatfordWind2080RCP8.5 | Watford | Wind | RCP8.5 | 2080 | 88.4969 | 96.016 | 104.125 | 112.0534 | 120.0096
| WatfordWind2085RCP8.5 | Watford | Wind | RCP8.5 | 2085 | 88.8396 | 96.4489 | 104.664 | 112.6826 | 120.7358
| WatfordWind2090RCP8.5 | Watford | Wind | RCP8.5 | 2090 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
| WatfordWind2095RCP8.5 | Watford | Wind | RCP8.5 | 2095 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
| WatfordWind2100RCP8.5 | Watford | Wind | RCP8.5 | 2100 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
| WawaIce Accretion2023RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2023 | 12.9761 | 15.4778 | 18.666 | 21.0926 | 23.5192
| WawaIce Accretion2025RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2025 | 12.9741 | 15.4729 | 18.654 | 21.0756 | 23.5003
| WawaIce Accretion2030RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2030 | 12.972 | 15.4679 | 18.642 | 21.0587 | 23.4814
| WawaIce Accretion2035RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2035 | 12.9699 | 15.4629 | 18.63 | 21.0417 | 23.4625
| WawaIce Accretion2040RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2040 | 12.9678 | 15.4579 | 18.618 | 21.0248 | 23.4436
| WawaIce Accretion2045RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2045 | 12.9657 | 15.4529 | 18.606 | 21.0078 | 23.4247
| WawaIce Accretion2050RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2050 | 13.0162 | 15.5137 | 18.6768 | 21.0885 | 23.5146
| WawaIce Accretion2055RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2055 | 13.0688 | 15.5794 | 18.7596 | 21.1861 | 23.6235
| WawaIce Accretion2060RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2060 | 13.1214 | 15.6452 | 18.8424 | 21.2838 | 23.7324
| WawaIce Accretion2065RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2065 | 13.174 | 15.7109 | 18.9252 | 21.3814 | 23.8412
| WawaIce Accretion2070RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2070 | 13.2266 | 15.7766 | 19.008 | 21.479 | 23.9501
| WawaIce Accretion2075RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2075 | 13.2392 | 15.7991 | 19.041 | 21.5231 | 24.003
| WawaIce Accretion2080RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2080 | 13.2517 | 15.8215 | 19.074 | 21.5672 | 24.0559
| WawaIce Accretion2085RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2085 | 13.2642 | 15.8439 | 19.107 | 21.6112 | 24.1088
| WawaIce Accretion2090RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2090 | 13.2767 | 15.8663 | 19.14 | 21.6553 | 24.1618
| WawaIce Accretion2095RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2095 | 13.2893 | 15.8887 | 19.173 | 21.6994 | 24.2147
| WawaIce Accretion2100RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2100 | 13.3018 | 15.9111 | 19.206 | 21.7435 | 24.2676
| WawaIce Accretion2023RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2023 | 12.9761 | 15.4778 | 18.666 | 21.0926 | 23.5192
| WawaIce Accretion2025RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2025 | 12.9741 | 15.4729 | 18.654 | 21.0756 | 23.5003
| WawaIce Accretion2030RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2030 | 12.972 | 15.4679 | 18.642 | 21.0587 | 23.4814
| WawaIce Accretion2035RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2035 | 12.9699 | 15.4629 | 18.63 | 21.0417 | 23.4625
| WawaIce Accretion2040RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2040 | 12.9678 | 15.4579 | 18.618 | 21.0248 | 23.4436
| WawaIce Accretion2045RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2045 | 12.9657 | 15.4529 | 18.606 | 21.0078 | 23.4247
| WawaIce Accretion2050RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2050 | 13.0162 | 15.5137 | 18.6768 | 21.0885 | 23.5146
| WawaIce Accretion2055RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2055 | 13.0688 | 15.5794 | 18.7596 | 21.1861 | 23.6235
| WawaIce Accretion2060RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2060 | 13.1214 | 15.6452 | 18.8424 | 21.2838 | 23.7324
| WawaIce Accretion2065RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2065 | 13.174 | 15.7109 | 18.9252 | 21.3814 | 23.8412
| WawaIce Accretion2070RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2070 | 13.2266 | 15.7766 | 19.008 | 21.479 | 23.9501
| WawaIce Accretion2075RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2075 | 13.2454 | 15.8103 | 19.0575 | 21.5451 | 24.0295
| WawaIce Accretion2080RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2080 | 13.2642 | 15.8439 | 19.107 | 21.6112 | 24.1088
| WawaIce Accretion2085RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2085 | 13.283 | 15.8775 | 19.1565 | 21.6774 | 24.1882
| WawaIce Accretion2090RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2090 | 13.1557 | 15.7468 | 19.026 | 21.5401 | 24.0484
| WawaIce Accretion2095RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2095 | 13.0095 | 15.5824 | 18.846 | 21.3367 | 23.8291
| WawaIce Accretion2100RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2100 | 12.8634 | 15.4181 | 18.666 | 21.1333 | 23.6099
| WawaIce Accretion2023RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2023 | 12.9761 | 15.4778 | 18.666 | 21.0926 | 23.5192
| WawaIce Accretion2025RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2025 | 12.972 | 15.4679 | 18.642 | 21.0587 | 23.4814
| WawaIce Accretion2030RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2030 | 12.9678 | 15.4579 | 18.618 | 21.0248 | 23.4436
| WawaIce Accretion2035RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2035 | 12.9636 | 15.448 | 18.594 | 20.9909 | 23.4058
| WawaIce Accretion2040RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2040 | 13.0513 | 15.5575 | 18.732 | 21.1536 | 23.5872
| WawaIce Accretion2045RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2045 | 13.139 | 15.6671 | 18.87 | 21.3163 | 23.7686
| WawaIce Accretion2050RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2050 | 13.2517 | 15.8215 | 19.074 | 21.5672 | 24.0559
| WawaIce Accretion2055RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2055 | 13.2767 | 15.8663 | 19.14 | 21.6553 | 24.1618
| WawaIce Accretion2060RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2060 | 13.1557 | 15.7468 | 19.026 | 21.5401 | 24.0484
| WawaIce Accretion2065RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2065 | 13.0095 | 15.5824 | 18.846 | 21.3367 | 23.8291
| WawaIce Accretion2070RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2070 | 12.9594 | 15.5426 | 18.822 | 21.3231 | 23.8216
| WawaIce Accretion2075RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2075 | 13.0555 | 15.6671 | 18.978 | 21.5129 | 24.0332
| WawaIce Accretion2080RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2080 | 13.1515 | 15.7916 | 19.134 | 21.7028 | 24.2449
| WawaIce Accretion2085RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2085 | 13.0638 | 15.7169 | 19.062 | 21.6316 | 24.1769
| WawaIce Accretion2090RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2090 | 12.9761 | 15.6422 | 18.99 | 21.5604 | 24.1088
| WawaIce Accretion2095RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2095 | 12.9761 | 15.6422 | 18.99 | 21.5604 | 24.1088
| WawaIce Accretion2100RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2100 | 12.9761 | 15.6422 | 18.99 | 21.5604 | 24.1088
| WawaWind2023RCP4.5 | Wawa | Wind | RCP4.5 | 2023 | 82.3118 | 88.7138 | 95.4758 | 102.2094 | 108.9496
| WawaWind2025RCP4.5 | Wawa | Wind | RCP4.5 | 2025 | 82.3957 | 88.8143 | 95.5949 | 102.3469 | 109.1032
| WawaWind2030RCP4.5 | Wawa | Wind | RCP4.5 | 2030 | 82.4796 | 88.9149 | 95.7139 | 102.4843 | 109.2568
| WawaWind2035RCP4.5 | Wawa | Wind | RCP4.5 | 2035 | 82.5634 | 89.0154 | 95.833 | 102.6218 | 109.4104
| WawaWind2040RCP4.5 | Wawa | Wind | RCP4.5 | 2040 | 82.6473 | 89.1159 | 95.9521 | 102.7592 | 109.564
| WawaWind2045RCP4.5 | Wawa | Wind | RCP4.5 | 2045 | 82.7312 | 89.2165 | 96.0711 | 102.8967 | 109.7176
| WawaWind2050RCP4.5 | Wawa | Wind | RCP4.5 | 2050 | 82.7907 | 89.2681 | 96.1094 | 102.9275 | 109.7383
| WawaWind2055RCP4.5 | Wawa | Wind | RCP4.5 | 2055 | 82.7663 | 89.2191 | 96.0285 | 102.8209 | 109.6054
| WawaWind2060RCP4.5 | Wawa | Wind | RCP4.5 | 2060 | 82.742 | 89.1701 | 95.9477 | 102.7143 | 109.4725
| WawaWind2065RCP4.5 | Wawa | Wind | RCP4.5 | 2065 | 82.7176 | 89.1212 | 95.8668 | 102.6077 | 109.3396
| WawaWind2070RCP4.5 | Wawa | Wind | RCP4.5 | 2070 | 82.6933 | 89.0722 | 95.786 | 102.5011 | 109.2068
| WawaWind2075RCP4.5 | Wawa | Wind | RCP4.5 | 2075 | 82.7325 | 89.113 | 95.8283 | 102.5463 | 109.255
| WawaWind2080RCP4.5 | Wawa | Wind | RCP4.5 | 2080 | 82.7718 | 89.1538 | 95.8706 | 102.5916 | 109.3032
| WawaWind2085RCP4.5 | Wawa | Wind | RCP4.5 | 2085 | 82.811 | 89.1946 | 95.9129 | 102.6369 | 109.3514
| WawaWind2090RCP4.5 | Wawa | Wind | RCP4.5 | 2090 | 82.8502 | 89.2354 | 95.9552 | 102.6821 | 109.3996
| WawaWind2095RCP4.5 | Wawa | Wind | RCP4.5 | 2095 | 82.8894 | 89.2762 | 95.9975 | 102.7274 | 109.4479
| WawaWind2100RCP4.5 | Wawa | Wind | RCP4.5 | 2100 | 82.9287 | 89.317 | 96.0398 | 102.7726 | 109.4961
| WawaWind2023RCP6.0 | Wawa | Wind | RCP6.0 | 2023 | 82.3118 | 88.7138 | 95.4758 | 102.2094 | 108.9496
| WawaWind2025RCP6.0 | Wawa | Wind | RCP6.0 | 2025 | 82.3957 | 88.8143 | 95.5949 | 102.3469 | 109.1032
| WawaWind2030RCP6.0 | Wawa | Wind | RCP6.0 | 2030 | 82.4796 | 88.9149 | 95.7139 | 102.4843 | 109.2568
| WawaWind2035RCP6.0 | Wawa | Wind | RCP6.0 | 2035 | 82.5634 | 89.0154 | 95.833 | 102.6218 | 109.4104
| WawaWind2040RCP6.0 | Wawa | Wind | RCP6.0 | 2040 | 82.6473 | 89.1159 | 95.9521 | 102.7592 | 109.564
| WawaWind2045RCP6.0 | Wawa | Wind | RCP6.0 | 2045 | 82.7312 | 89.2165 | 96.0711 | 102.8967 | 109.7176
| WawaWind2050RCP6.0 | Wawa | Wind | RCP6.0 | 2050 | 82.7907 | 89.2681 | 96.1094 | 102.9275 | 109.7383
| WawaWind2055RCP6.0 | Wawa | Wind | RCP6.0 | 2055 | 82.7663 | 89.2191 | 96.0285 | 102.8209 | 109.6054
| WawaWind2060RCP6.0 | Wawa | Wind | RCP6.0 | 2060 | 82.742 | 89.1701 | 95.9477 | 102.7143 | 109.4725
| WawaWind2065RCP6.0 | Wawa | Wind | RCP6.0 | 2065 | 82.7176 | 89.1212 | 95.8668 | 102.6077 | 109.3396
| WawaWind2070RCP6.0 | Wawa | Wind | RCP6.0 | 2070 | 82.6933 | 89.0722 | 95.786 | 102.5011 | 109.2068
| WawaWind2075RCP6.0 | Wawa | Wind | RCP6.0 | 2075 | 82.7521 | 89.1334 | 95.8494 | 102.569 | 109.2791
| WawaWind2080RCP6.0 | Wawa | Wind | RCP6.0 | 2080 | 82.811 | 89.1946 | 95.9129 | 102.6369 | 109.3514
| WawaWind2085RCP6.0 | Wawa | Wind | RCP6.0 | 2085 | 82.8698 | 89.2558 | 95.9763 | 102.7048 | 109.4238
| WawaWind2090RCP6.0 | Wawa | Wind | RCP6.0 | 2090 | 83.1722 | 89.5968 | 96.3563 | 103.1213 | 109.8819
| WawaWind2095RCP6.0 | Wawa | Wind | RCP6.0 | 2095 | 83.4157 | 89.8765 | 96.6727 | 103.47 | 110.2676
| WawaWind2100RCP6.0 | Wawa | Wind | RCP6.0 | 2100 | 83.6592 | 90.1562 | 96.9892 | 103.8187 | 110.6534
| WawaWind2023RCP8.5 | Wawa | Wind | RCP8.5 | 2023 | 82.3118 | 88.7138 | 95.4758 | 102.2094 | 108.9496
| WawaWind2025RCP8.5 | Wawa | Wind | RCP8.5 | 2025 | 82.4796 | 88.9149 | 95.7139 | 102.4843 | 109.2568
| WawaWind2030RCP8.5 | Wawa | Wind | RCP8.5 | 2030 | 82.6473 | 89.1159 | 95.9521 | 102.7592 | 109.564
| WawaWind2035RCP8.5 | Wawa | Wind | RCP8.5 | 2035 | 82.815 | 89.317 | 96.1902 | 103.0342 | 109.8711
| WawaWind2040RCP8.5 | Wawa | Wind | RCP8.5 | 2040 | 82.7745 | 89.2354 | 96.0555 | 102.8565 | 109.6497
| WawaWind2045RCP8.5 | Wawa | Wind | RCP8.5 | 2045 | 82.7339 | 89.1538 | 95.9207 | 102.6788 | 109.4282
| WawaWind2050RCP8.5 | Wawa | Wind | RCP8.5 | 2050 | 82.7718 | 89.1538 | 95.8706 | 102.5916 | 109.3032
| WawaWind2055RCP8.5 | Wawa | Wind | RCP8.5 | 2055 | 82.8502 | 89.2354 | 95.9552 | 102.6821 | 109.3996
| WawaWind2060RCP8.5 | Wawa | Wind | RCP8.5 | 2060 | 83.1722 | 89.5968 | 96.3563 | 103.1213 | 109.8819
| WawaWind2065RCP8.5 | Wawa | Wind | RCP8.5 | 2065 | 83.4157 | 89.8765 | 96.6727 | 103.47 | 110.2676
| WawaWind2070RCP8.5 | Wawa | Wind | RCP8.5 | 2070 | 83.7539 | 90.2466 | 97.0738 | 103.8991 | 110.7249
| WawaWind2075RCP8.5 | Wawa | Wind | RCP8.5 | 2075 | 83.8486 | 90.3369 | 97.1584 | 103.9796 | 110.7963
| WawaWind2080RCP8.5 | Wawa | Wind | RCP8.5 | 2080 | 83.9433 | 90.4272 | 97.243 | 104.0601 | 110.8677
| WawaWind2085RCP8.5 | Wawa | Wind | RCP8.5 | 2085 | 84.1746 | 90.6939 | 97.5532 | 104.4071 | 111.2589
| WawaWind2090RCP8.5 | Wawa | Wind | RCP8.5 | 2090 | 84.4059 | 90.9605 | 97.8634 | 104.7541 | 111.65
| WawaWind2095RCP8.5 | Wawa | Wind | RCP8.5 | 2095 | 84.4059 | 90.9605 | 97.8634 | 104.7541 | 111.65
| WawaWind2100RCP8.5 | Wawa | Wind | RCP8.5 | 2100 | 84.4059 | 90.9605 | 97.8634 | 104.7541 | 111.65
| WellandIce Accretion2023RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
| WellandIce Accretion2025RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2025 | 21.9182 | 26.3121 | 31.8773 | 36.1299 | 40.3738
| WellandIce Accretion2030RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2030 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
| WellandIce Accretion2035RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2035 | 21.7104 | 26.0819 | 31.632 | 35.8526 | 40.0781
| WellandIce Accretion2040RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2040 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
| WellandIce Accretion2045RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2045 | 21.5026 | 25.8517 | 31.3867 | 35.5754 | 39.7824
| WellandIce Accretion2050RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2050 | 20.9221 | 25.2001 | 30.6368 | 34.7425 | 38.8765
| WellandIce Accretion2055RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2055 | 20.4456 | 24.6636 | 30.0096 | 34.0483 | 38.1185
| WellandIce Accretion2060RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2060 | 19.9691 | 24.1271 | 29.3824 | 33.354 | 37.3605
| WellandIce Accretion2065RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2065 | 19.4926 | 23.5906 | 28.7552 | 32.6597 | 36.6025
| WellandIce Accretion2070RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2070 | 19.0161 | 23.0541 | 28.128 | 31.9654 | 35.8445
| WellandIce Accretion2075RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2075 | 18.8379 | 22.8682 | 27.9307 | 31.7605 | 35.6294
| WellandIce Accretion2080RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2080 | 18.6598 | 22.6822 | 27.7333 | 31.5556 | 35.4144
| WellandIce Accretion2085RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2085 | 18.4817 | 22.4963 | 27.536 | 31.3507 | 35.1994
| WellandIce Accretion2090RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2090 | 18.3035 | 22.3104 | 27.3387 | 31.1458 | 34.9843
| WellandIce Accretion2095RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2095 | 18.1254 | 22.1245 | 27.1413 | 30.9409 | 34.7693
| WellandIce Accretion2100RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2100 | 17.9473 | 21.9386 | 26.944 | 30.736 | 34.5542
| WellandIce Accretion2023RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
| WellandIce Accretion2025RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2025 | 21.9182 | 26.3121 | 31.8773 | 36.1299 | 40.3738
| WellandIce Accretion2030RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2030 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
| WellandIce Accretion2035RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2035 | 21.7104 | 26.0819 | 31.632 | 35.8526 | 40.0781
| WellandIce Accretion2040RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2040 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
| WellandIce Accretion2045RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2045 | 21.5026 | 25.8517 | 31.3867 | 35.5754 | 39.7824
| WellandIce Accretion2050RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2050 | 20.9221 | 25.2001 | 30.6368 | 34.7425 | 38.8765
| WellandIce Accretion2055RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2055 | 20.4456 | 24.6636 | 30.0096 | 34.0483 | 38.1185
| WellandIce Accretion2060RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2060 | 19.9691 | 24.1271 | 29.3824 | 33.354 | 37.3605
| WellandIce Accretion2065RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2065 | 19.4926 | 23.5906 | 28.7552 | 32.6597 | 36.6025
| WellandIce Accretion2070RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2070 | 19.0161 | 23.0541 | 28.128 | 31.9654 | 35.8445
| WellandIce Accretion2075RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2075 | 18.7489 | 22.7752 | 27.832 | 31.6581 | 35.5219
| WellandIce Accretion2080RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2080 | 18.4817 | 22.4963 | 27.536 | 31.3507 | 35.1994
| WellandIce Accretion2085RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2085 | 18.2145 | 22.2174 | 27.24 | 31.0434 | 34.8768
| WellandIce Accretion2090RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2090 | 17.2199 | 21.1063 | 25.9733 | 29.6633 | 33.3581
| WellandIce Accretion2095RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2095 | 16.4925 | 20.2741 | 25.0027 | 28.5905 | 32.1619
| WellandIce Accretion2100RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2100 | 15.7651 | 19.4419 | 24.032 | 27.5178 | 30.9658
| WellandIce Accretion2023RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
| WellandIce Accretion2025RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2025 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
| WellandIce Accretion2030RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2030 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
| WellandIce Accretion2035RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2035 | 21.3987 | 25.7366 | 31.264 | 35.4368 | 39.6346
| WellandIce Accretion2040RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2040 | 20.6045 | 24.8425 | 30.2187 | 34.2797 | 38.3712
| WellandIce Accretion2045RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2045 | 19.8103 | 23.9483 | 29.1733 | 33.1226 | 37.1078
| WellandIce Accretion2050RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2050 | 18.6598 | 22.6822 | 27.7333 | 31.5556 | 35.4144
| WellandIce Accretion2055RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2055 | 18.3035 | 22.3104 | 27.3387 | 31.1458 | 34.9843
| WellandIce Accretion2060RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2060 | 17.2199 | 21.1063 | 25.9733 | 29.6633 | 33.3581
| WellandIce Accretion2065RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2065 | 16.4925 | 20.2741 | 25.0027 | 28.5905 | 32.1619
| WellandIce Accretion2070RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2070 | 15.4014 | 19.0258 | 23.5627 | 26.9995 | 30.4013
| WellandIce Accretion2075RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2075 | 15.0377 | 18.6097 | 23.0933 | 26.4812 | 29.8368
| WellandIce Accretion2080RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2080 | 14.674 | 18.1936 | 22.624 | 25.9629 | 29.2723
| WellandIce Accretion2085RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2085 | 13.8501 | 17.2242 | 21.456 | 24.643 | 27.8006
| WellandIce Accretion2090RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2090 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
| WellandIce Accretion2095RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2095 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
| WellandIce Accretion2100RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2100 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
| WellandWind2023RCP4.5 | Welland | Wind | RCP4.5 | 2023 | 88.11 | 95.1229 | 102.5655 | 109.9612 | 117.3507
| WellandWind2025RCP4.5 | Welland | Wind | RCP4.5 | 2025 | 88.0809 | 95.0932 | 102.5335 | 109.927 | 117.3142
| WellandWind2030RCP4.5 | Welland | Wind | RCP4.5 | 2030 | 88.0519 | 95.0634 | 102.5015 | 109.8928 | 117.2778
| WellandWind2035RCP4.5 | Welland | Wind | RCP4.5 | 2035 | 88.0228 | 95.0337 | 102.4695 | 109.8586 | 117.2413
| WellandWind2040RCP4.5 | Welland | Wind | RCP4.5 | 2040 | 87.9937 | 95.0039 | 102.4376 | 109.8243 | 117.2048
| WellandWind2045RCP4.5 | Welland | Wind | RCP4.5 | 2045 | 87.9647 | 94.9742 | 102.4056 | 109.7901 | 117.1684
| WellandWind2050RCP4.5 | Welland | Wind | RCP4.5 | 2050 | 87.9931 | 95.0177 | 102.4685 | 109.8661 | 117.2609
| WellandWind2055RCP4.5 | Welland | Wind | RCP4.5 | 2055 | 88.0507 | 95.091 | 102.5635 | 109.9764 | 117.3898
| WellandWind2060RCP4.5 | Welland | Wind | RCP4.5 | 2060 | 88.1083 | 95.1642 | 102.6584 | 110.0866 | 117.5188
| WellandWind2065RCP4.5 | Welland | Wind | RCP4.5 | 2065 | 88.1658 | 95.2375 | 102.7534 | 110.1968 | 117.6477
| WellandWind2070RCP4.5 | Welland | Wind | RCP4.5 | 2070 | 88.2234 | 95.3108 | 102.8483 | 110.307 | 117.7767
| WellandWind2075RCP4.5 | Welland | Wind | RCP4.5 | 2075 | 88.3048 | 95.4251 | 103.0049 | 110.498 | 118.0051
| WellandWind2080RCP4.5 | Welland | Wind | RCP4.5 | 2080 | 88.3862 | 95.5393 | 103.1614 | 110.6889 | 118.2334
| WellandWind2085RCP4.5 | Welland | Wind | RCP4.5 | 2085 | 88.4676 | 95.6536 | 103.3179 | 110.8798 | 118.4618
| WellandWind2090RCP4.5 | Welland | Wind | RCP4.5 | 2090 | 88.549 | 95.7679 | 103.4745 | 111.0707 | 118.6901
| WellandWind2095RCP4.5 | Welland | Wind | RCP4.5 | 2095 | 88.6304 | 95.8822 | 103.6311 | 111.2617 | 118.9185
| WellandWind2100RCP4.5 | Welland | Wind | RCP4.5 | 2100 | 88.7118 | 95.9965 | 103.7876 | 111.4526 | 119.1469
| WellandWind2023RCP6.0 | Welland | Wind | RCP6.0 | 2023 | 88.11 | 95.1229 | 102.5655 | 109.9612 | 117.3507
| WellandWind2025RCP6.0 | Welland | Wind | RCP6.0 | 2025 | 88.0809 | 95.0932 | 102.5335 | 109.927 | 117.3142
| WellandWind2030RCP6.0 | Welland | Wind | RCP6.0 | 2030 | 88.0519 | 95.0634 | 102.5015 | 109.8928 | 117.2778
| WellandWind2035RCP6.0 | Welland | Wind | RCP6.0 | 2035 | 88.0228 | 95.0337 | 102.4695 | 109.8586 | 117.2413
| WellandWind2040RCP6.0 | Welland | Wind | RCP6.0 | 2040 | 87.9937 | 95.0039 | 102.4376 | 109.8243 | 117.2048
| WellandWind2045RCP6.0 | Welland | Wind | RCP6.0 | 2045 | 87.9647 | 94.9742 | 102.4056 | 109.7901 | 117.1684
| WellandWind2050RCP6.0 | Welland | Wind | RCP6.0 | 2050 | 87.9931 | 95.0177 | 102.4685 | 109.8661 | 117.2609
| WellandWind2055RCP6.0 | Welland | Wind | RCP6.0 | 2055 | 88.0507 | 95.091 | 102.5635 | 109.9764 | 117.3898
| WellandWind2060RCP6.0 | Welland | Wind | RCP6.0 | 2060 | 88.1083 | 95.1642 | 102.6584 | 110.0866 | 117.5188
| WellandWind2065RCP6.0 | Welland | Wind | RCP6.0 | 2065 | 88.1658 | 95.2375 | 102.7534 | 110.1968 | 117.6477
| WellandWind2070RCP6.0 | Welland | Wind | RCP6.0 | 2070 | 88.2234 | 95.3108 | 102.8483 | 110.307 | 117.7767
| WellandWind2075RCP6.0 | Welland | Wind | RCP6.0 | 2075 | 88.3455 | 95.4822 | 103.0831 | 110.5934 | 118.1192
| WellandWind2080RCP6.0 | Welland | Wind | RCP6.0 | 2080 | 88.4676 | 95.6536 | 103.3179 | 110.8798 | 118.4618
| WellandWind2085RCP6.0 | Welland | Wind | RCP6.0 | 2085 | 88.5897 | 95.825 | 103.5528 | 111.1662 | 118.8043
| WellandWind2090RCP6.0 | Welland | Wind | RCP6.0 | 2090 | 88.8978 | 96.2344 | 104.0872 | 111.8092 | 119.5614
| WellandWind2095RCP6.0 | Welland | Wind | RCP6.0 | 2095 | 89.0839 | 96.4724 | 104.3869 | 112.1659 | 119.9759
| WellandWind2100RCP6.0 | Welland | Wind | RCP6.0 | 2100 | 89.2699 | 96.7103 | 104.6865 | 112.5225 | 120.3904
| WellandWind2023RCP8.5 | Welland | Wind | RCP8.5 | 2023 | 88.11 | 95.1229 | 102.5655 | 109.9612 | 117.3507
| WellandWind2025RCP8.5 | Welland | Wind | RCP8.5 | 2025 | 88.0519 | 95.0634 | 102.5015 | 109.8928 | 117.2778
| WellandWind2030RCP8.5 | Welland | Wind | RCP8.5 | 2030 | 87.9937 | 95.0039 | 102.4376 | 109.8243 | 117.2048
| WellandWind2035RCP8.5 | Welland | Wind | RCP8.5 | 2035 | 87.9356 | 94.9444 | 102.3736 | 109.7559 | 117.1319
| WellandWind2040RCP8.5 | Welland | Wind | RCP8.5 | 2040 | 88.0315 | 95.0666 | 102.5318 | 109.9396 | 117.3468
| WellandWind2045RCP8.5 | Welland | Wind | RCP8.5 | 2045 | 88.1274 | 95.1887 | 102.6901 | 110.1233 | 117.5618
| WellandWind2050RCP8.5 | Welland | Wind | RCP8.5 | 2050 | 88.3862 | 95.5393 | 103.1614 | 110.6889 | 118.2334
| WellandWind2055RCP8.5 | Welland | Wind | RCP8.5 | 2055 | 88.549 | 95.7679 | 103.4745 | 111.0707 | 118.6901
| WellandWind2060RCP8.5 | Welland | Wind | RCP8.5 | 2060 | 88.8978 | 96.2344 | 104.0872 | 111.8092 | 119.5614
| WellandWind2065RCP8.5 | Welland | Wind | RCP8.5 | 2065 | 89.0839 | 96.4724 | 104.3869 | 112.1659 | 119.9759
| WellandWind2070RCP8.5 | Welland | Wind | RCP8.5 | 2070 | 89.331 | 96.8137 | 104.8515 | 112.7386 | 120.6514
| WellandWind2075RCP8.5 | Welland | Wind | RCP8.5 | 2075 | 89.392 | 96.917 | 105.0164 | 112.9548 | 120.9124
| WellandWind2080RCP8.5 | Welland | Wind | RCP8.5 | 2080 | 89.4531 | 97.0203 | 105.1814 | 113.1709 | 121.1733
| WellandWind2085RCP8.5 | Welland | Wind | RCP8.5 | 2085 | 89.5185 | 97.1283 | 105.338 | 113.3654 | 121.4151
| WellandWind2090RCP8.5 | Welland | Wind | RCP8.5 | 2090 | 89.5839 | 97.2363 | 105.4945 | 113.56 | 121.6569
| WellandWind2095RCP8.5 | Welland | Wind | RCP8.5 | 2095 | 89.5839 | 97.2363 | 105.4945 | 113.56 | 121.6569
| WellandWind2100RCP8.5 | Welland | Wind | RCP8.5 | 2100 | 89.5839 | 97.2363 | 105.4945 | 113.56 | 121.6569
| West LorneIce Accretion2023RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2023 | 20.5414 | 24.6261 | 29.79 | 33.7305 | 37.6866
| West LorneIce Accretion2025RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2025 | 20.4126 | 24.4974 | 29.66 | 33.5949 | 37.5417
| West LorneIce Accretion2030RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2030 | 20.2839 | 24.3688 | 29.53 | 33.4593 | 37.3968
| West LorneIce Accretion2035RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2035 | 20.1552 | 24.2401 | 29.4 | 33.3237 | 37.2519
| West LorneIce Accretion2040RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2040 | 20.0265 | 24.1115 | 29.27 | 33.1881 | 37.107
| West LorneIce Accretion2045RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2045 | 19.8977 | 23.9828 | 29.14 | 33.0525 | 36.9621
| West LorneIce Accretion2050RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2050 | 19.2972 | 23.3263 | 28.404 | 32.2525 | 36.0914
| West LorneIce Accretion2055RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2055 | 18.8254 | 22.7984 | 27.798 | 31.588 | 35.3657
| West LorneIce Accretion2060RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2060 | 18.3536 | 22.2706 | 27.192 | 30.9236 | 34.6399
| West LorneIce Accretion2065RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2065 | 17.8819 | 21.7427 | 26.586 | 30.2591 | 33.9142
| West LorneIce Accretion2070RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2070 | 17.4101 | 21.2148 | 25.98 | 29.5947 | 33.1884
| West LorneIce Accretion2075RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2075 | 16.9543 | 20.6877 | 25.365 | 28.911 | 32.4324
| West LorneIce Accretion2080RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2080 | 16.4985 | 20.1607 | 24.75 | 28.2274 | 31.6764
| West LorneIce Accretion2085RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2085 | 16.0427 | 19.6336 | 24.135 | 27.5437 | 30.9204
| West LorneIce Accretion2090RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2090 | 15.587 | 19.1066 | 23.52 | 26.8601 | 30.1644
| West LorneIce Accretion2095RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2095 | 15.1312 | 18.5795 | 22.905 | 26.1764 | 29.4084
| West LorneIce Accretion2100RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2100 | 14.6754 | 18.0525 | 22.29 | 25.4928 | 28.6524
| West LorneIce Accretion2023RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2023 | 20.5414 | 24.6261 | 29.79 | 33.7305 | 37.6866
| West LorneIce Accretion2025RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2025 | 20.4126 | 24.4974 | 29.66 | 33.5949 | 37.5417
| West LorneIce Accretion2030RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2030 | 20.2839 | 24.3688 | 29.53 | 33.4593 | 37.3968
| West LorneIce Accretion2035RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2035 | 20.1552 | 24.2401 | 29.4 | 33.3237 | 37.2519
| West LorneIce Accretion2040RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2040 | 20.0265 | 24.1115 | 29.27 | 33.1881 | 37.107
| West LorneIce Accretion2045RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2045 | 19.8977 | 23.9828 | 29.14 | 33.0525 | 36.9621
| West LorneIce Accretion2050RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2050 | 19.2972 | 23.3263 | 28.404 | 32.2525 | 36.0914
| West LorneIce Accretion2055RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2055 | 18.8254 | 22.7984 | 27.798 | 31.588 | 35.3657
| West LorneIce Accretion2060RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2060 | 18.3536 | 22.2706 | 27.192 | 30.9236 | 34.6399
| West LorneIce Accretion2065RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2065 | 17.8819 | 21.7427 | 26.586 | 30.2591 | 33.9142
| West LorneIce Accretion2070RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2070 | 17.4101 | 21.2148 | 25.98 | 29.5947 | 33.1884
| West LorneIce Accretion2075RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2075 | 16.7264 | 20.4242 | 25.0575 | 28.5692 | 32.0544
| West LorneIce Accretion2080RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2080 | 16.0427 | 19.6336 | 24.135 | 27.5437 | 30.9204
| West LorneIce Accretion2085RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2085 | 15.3591 | 18.8431 | 23.2125 | 26.5183 | 29.7864
| West LorneIce Accretion2090RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2090 | 13.6316 | 16.8075 | 20.78 | 23.7865 | 26.7498
| West LorneIce Accretion2095RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2095 | 12.5879 | 15.5625 | 19.27 | 22.0802 | 24.8472
| West LorneIce Accretion2100RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2100 | 11.5441 | 14.3175 | 17.76 | 20.3739 | 22.9446
| West LorneIce Accretion2023RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2023 | 20.5414 | 24.6261 | 29.79 | 33.7305 | 37.6866
| West LorneIce Accretion2025RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2025 | 20.2839 | 24.3688 | 29.53 | 33.4593 | 37.3968
| West LorneIce Accretion2030RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2030 | 20.0265 | 24.1115 | 29.27 | 33.1881 | 37.107
| West LorneIce Accretion2035RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2035 | 19.769 | 23.8542 | 29.01 | 32.9169 | 36.8172
| West LorneIce Accretion2040RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2040 | 18.9827 | 22.9744 | 28 | 31.8095 | 35.6076
| West LorneIce Accretion2045RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2045 | 18.1964 | 22.0946 | 26.99 | 30.7021 | 34.398
| West LorneIce Accretion2050RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2050 | 16.4985 | 20.1607 | 24.75 | 28.2274 | 31.6764
| West LorneIce Accretion2055RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2055 | 15.587 | 19.1066 | 23.52 | 26.8601 | 30.1644
| West LorneIce Accretion2060RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2060 | 13.6316 | 16.8075 | 20.78 | 23.7865 | 26.7498
| West LorneIce Accretion2065RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2065 | 12.5879 | 15.5625 | 19.27 | 22.0802 | 24.8472
| West LorneIce Accretion2070RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2070 | 10.9665 | 13.6286 | 16.93 | 19.4247 | 21.8862
| West LorneIce Accretion2075RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2075 | 10.389 | 12.9397 | 16.1 | 18.4755 | 20.8278
| West LorneIce Accretion2080RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2080 | 9.8114 | 12.2508 | 15.27 | 17.5263 | 19.7694
| West LorneIce Accretion2085RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2085 | 9.0182 | 11.2921 | 14.115 | 16.2211 | 18.3141
| West LorneIce Accretion2090RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2090 | 8.2249 | 10.3335 | 12.96 | 14.916 | 16.8588
| West LorneIce Accretion2095RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2095 | 8.2249 | 10.3335 | 12.96 | 14.916 | 16.8588
| West LorneIce Accretion2100RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2100 | 8.2249 | 10.3335 | 12.96 | 14.916 | 16.8588
| West LorneWind2023RCP4.5 | West Lorne | Wind | RCP4.5 | 2023 | 85.8694 | 92.5119 | 99.5148 | 106.5126 | 113.5146
| West LorneWind2025RCP4.5 | West Lorne | Wind | RCP4.5 | 2025 | 85.9592 | 92.6332 | 99.6765 | 106.7086 | 113.7441
| West LorneWind2030RCP4.5 | West Lorne | Wind | RCP4.5 | 2030 | 86.049 | 92.7544 | 99.8382 | 106.9046 | 113.9736
| West LorneWind2035RCP4.5 | West Lorne | Wind | RCP4.5 | 2035 | 86.1387 | 92.8756 | 99.9999 | 107.1005 | 114.203
| West LorneWind2040RCP4.5 | West Lorne | Wind | RCP4.5 | 2040 | 86.2285 | 92.9968 | 100.1616 | 107.2965 | 114.4325
| West LorneWind2045RCP4.5 | West Lorne | Wind | RCP4.5 | 2045 | 86.3182 | 93.1181 | 100.3233 | 107.4925 | 114.662
| West LorneWind2050RCP4.5 | West Lorne | Wind | RCP4.5 | 2050 | 86.5174 | 93.3848 | 100.6751 | 107.9172 | 115.1601
| West LorneWind2055RCP4.5 | West Lorne | Wind | RCP4.5 | 2055 | 86.6268 | 93.5302 | 100.8652 | 108.1461 | 115.4287
| West LorneWind2060RCP4.5 | West Lorne | Wind | RCP4.5 | 2060 | 86.7363 | 93.6757 | 101.0552 | 108.3749 | 115.6973
| West LorneWind2065RCP4.5 | West Lorne | Wind | RCP4.5 | 2065 | 86.8457 | 93.8212 | 101.2453 | 108.6037 | 115.9659
| West LorneWind2070RCP4.5 | West Lorne | Wind | RCP4.5 | 2070 | 86.9551 | 93.9666 | 101.4354 | 108.8325 | 116.2345
| West LorneWind2075RCP4.5 | West Lorne | Wind | RCP4.5 | 2075 | 87.1403 | 94.2076 | 101.7456 | 109.1997 | 116.6634
| West LorneWind2080RCP4.5 | West Lorne | Wind | RCP4.5 | 2080 | 87.3255 | 94.4485 | 102.0558 | 109.5669 | 117.0922
| West LorneWind2085RCP4.5 | West Lorne | Wind | RCP4.5 | 2085 | 87.5107 | 94.6894 | 102.366 | 109.9342 | 117.5211
| West LorneWind2090RCP4.5 | West Lorne | Wind | RCP4.5 | 2090 | 87.696 | 94.9303 | 102.6762 | 110.3014 | 117.95
| West LorneWind2095RCP4.5 | West Lorne | Wind | RCP4.5 | 2095 | 87.8812 | 95.1712 | 102.9864 | 110.6686 | 118.3789
| West LorneWind2100RCP4.5 | West Lorne | Wind | RCP4.5 | 2100 | 88.0664 | 95.4121 | 103.2966 | 111.0358 | 118.8077
| West LorneWind2023RCP6.0 | West Lorne | Wind | RCP6.0 | 2023 | 85.8694 | 92.5119 | 99.5148 | 106.5126 | 113.5146
| West LorneWind2025RCP6.0 | West Lorne | Wind | RCP6.0 | 2025 | 85.9592 | 92.6332 | 99.6765 | 106.7086 | 113.7441
| West LorneWind2030RCP6.0 | West Lorne | Wind | RCP6.0 | 2030 | 86.049 | 92.7544 | 99.8382 | 106.9046 | 113.9736
| West LorneWind2035RCP6.0 | West Lorne | Wind | RCP6.0 | 2035 | 86.1387 | 92.8756 | 99.9999 | 107.1005 | 114.203
| West LorneWind2040RCP6.0 | West Lorne | Wind | RCP6.0 | 2040 | 86.2285 | 92.9968 | 100.1616 | 107.2965 | 114.4325
| West LorneWind2045RCP6.0 | West Lorne | Wind | RCP6.0 | 2045 | 86.3182 | 93.1181 | 100.3233 | 107.4925 | 114.662
| West LorneWind2050RCP6.0 | West Lorne | Wind | RCP6.0 | 2050 | 86.5174 | 93.3848 | 100.6751 | 107.9172 | 115.1601
| West LorneWind2055RCP6.0 | West Lorne | Wind | RCP6.0 | 2055 | 86.6268 | 93.5302 | 100.8652 | 108.1461 | 115.4287
| West LorneWind2060RCP6.0 | West Lorne | Wind | RCP6.0 | 2060 | 86.7363 | 93.6757 | 101.0552 | 108.3749 | 115.6973
| West LorneWind2065RCP6.0 | West Lorne | Wind | RCP6.0 | 2065 | 86.8457 | 93.8212 | 101.2453 | 108.6037 | 115.9659
| West LorneWind2070RCP6.0 | West Lorne | Wind | RCP6.0 | 2070 | 86.9551 | 93.9666 | 101.4354 | 108.8325 | 116.2345
| West LorneWind2075RCP6.0 | West Lorne | Wind | RCP6.0 | 2075 | 87.2329 | 94.328 | 101.9007 | 109.3833 | 116.8778
| West LorneWind2080RCP6.0 | West Lorne | Wind | RCP6.0 | 2080 | 87.5107 | 94.6894 | 102.366 | 109.9342 | 117.5211
| West LorneWind2085RCP6.0 | West Lorne | Wind | RCP6.0 | 2085 | 87.7886 | 95.0508 | 102.8313 | 110.485 | 118.1644
| West LorneWind2090RCP6.0 | West Lorne | Wind | RCP6.0 | 2090 | 88.4596 | 95.9062 | 103.917 | 111.7632 | 119.6466
| West LorneWind2095RCP6.0 | West Lorne | Wind | RCP6.0 | 2095 | 88.8529 | 96.4004 | 104.5374 | 112.4906 | 120.4856
| West LorneWind2100RCP6.0 | West Lorne | Wind | RCP6.0 | 2100 | 89.2461 | 96.8945 | 105.1578 | 113.218 | 121.3245
| West LorneWind2023RCP8.5 | West Lorne | Wind | RCP8.5 | 2023 | 85.8694 | 92.5119 | 99.5148 | 106.5126 | 113.5146
| West LorneWind2025RCP8.5 | West Lorne | Wind | RCP8.5 | 2025 | 86.049 | 92.7544 | 99.8382 | 106.9046 | 113.9736
| West LorneWind2030RCP8.5 | West Lorne | Wind | RCP8.5 | 2030 | 86.2285 | 92.9968 | 100.1616 | 107.2965 | 114.4325
| West LorneWind2035RCP8.5 | West Lorne | Wind | RCP8.5 | 2035 | 86.408 | 93.2393 | 100.485 | 107.6884 | 114.8915
| West LorneWind2040RCP8.5 | West Lorne | Wind | RCP8.5 | 2040 | 86.5904 | 93.4817 | 100.8018 | 108.0698 | 115.3392
| West LorneWind2045RCP8.5 | West Lorne | Wind | RCP8.5 | 2045 | 86.7727 | 93.7242 | 101.1186 | 108.4511 | 115.7868
| West LorneWind2050RCP8.5 | West Lorne | Wind | RCP8.5 | 2050 | 87.3255 | 94.4485 | 102.0558 | 109.5669 | 117.0922
| West LorneWind2055RCP8.5 | West Lorne | Wind | RCP8.5 | 2055 | 87.696 | 94.9303 | 102.6762 | 110.3014 | 117.95
| West LorneWind2060RCP8.5 | West Lorne | Wind | RCP8.5 | 2060 | 88.4596 | 95.9062 | 103.917 | 111.7632 | 119.6466
| West LorneWind2065RCP8.5 | West Lorne | Wind | RCP8.5 | 2065 | 88.8529 | 96.4004 | 104.5374 | 112.4906 | 120.4856
| West LorneWind2070RCP8.5 | West Lorne | Wind | RCP8.5 | 2070 | 89.4285 | 97.1216 | 105.4383 | 113.5464 | 121.6969
| West LorneWind2075RCP8.5 | West Lorne | Wind | RCP8.5 | 2075 | 89.6108 | 97.3487 | 105.7188 | 113.8748 | 122.0694
| West LorneWind2080RCP8.5 | West Lorne | Wind | RCP8.5 | 2080 | 89.7932 | 97.5758 | 105.9993 | 114.2031 | 122.4418
| West LorneWind2085RCP8.5 | West Lorne | Wind | RCP8.5 | 2085 | 90.2976 | 98.2111 | 106.8012 | 115.1459 | 123.5309
| West LorneWind2090RCP8.5 | West Lorne | Wind | RCP8.5 | 2090 | 90.8019 | 98.8464 | 107.6031 | 116.0887 | 124.62
| West LorneWind2095RCP8.5 | West Lorne | Wind | RCP8.5 | 2095 | 90.8019 | 98.8464 | 107.6031 | 116.0887 | 124.62
| West LorneWind2100RCP8.5 | West Lorne | Wind | RCP8.5 | 2100 | 90.8019 | 98.8464 | 107.6031 | 116.0887 | 124.62
| WhitbyIce Accretion2023RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| WhitbyIce Accretion2025RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| WhitbyIce Accretion2030RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| WhitbyIce Accretion2035RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| WhitbyIce Accretion2040RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| WhitbyIce Accretion2045RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| WhitbyIce Accretion2050RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| WhitbyIce Accretion2055RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| WhitbyIce Accretion2060RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| WhitbyIce Accretion2065RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| WhitbyIce Accretion2070RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| WhitbyIce Accretion2075RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
| WhitbyIce Accretion2080RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| WhitbyIce Accretion2085RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| WhitbyIce Accretion2090RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| WhitbyIce Accretion2095RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
| WhitbyIce Accretion2100RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
| WhitbyIce Accretion2023RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| WhitbyIce Accretion2025RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| WhitbyIce Accretion2030RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| WhitbyIce Accretion2035RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| WhitbyIce Accretion2040RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| WhitbyIce Accretion2045RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| WhitbyIce Accretion2050RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| WhitbyIce Accretion2055RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| WhitbyIce Accretion2060RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| WhitbyIce Accretion2065RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| WhitbyIce Accretion2070RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| WhitbyIce Accretion2075RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
| WhitbyIce Accretion2080RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| WhitbyIce Accretion2085RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
| WhitbyIce Accretion2090RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| WhitbyIce Accretion2095RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| WhitbyIce Accretion2100RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
| WhitbyIce Accretion2023RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| WhitbyIce Accretion2025RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| WhitbyIce Accretion2030RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| WhitbyIce Accretion2035RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
| WhitbyIce Accretion2040RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
| WhitbyIce Accretion2045RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
| WhitbyIce Accretion2050RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| WhitbyIce Accretion2055RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| WhitbyIce Accretion2060RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| WhitbyIce Accretion2065RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| WhitbyIce Accretion2070RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
| WhitbyIce Accretion2075RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
| WhitbyIce Accretion2080RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
| WhitbyIce Accretion2085RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
| WhitbyIce Accretion2090RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| WhitbyIce Accretion2095RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| WhitbyIce Accretion2100RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| WhitbyWind2023RCP4.5 | Whitby | Wind | RCP4.5 | 2023 | 85.6899 | 92.2541 | 99.1584 | 106.0677 | 112.9729
| WhitbyWind2025RCP4.5 | Whitby | Wind | RCP4.5 | 2025 | 85.7056 | 92.2879 | 99.2129 | 106.1401 | 113.0631
| WhitbyWind2030RCP4.5 | Whitby | Wind | RCP4.5 | 2030 | 85.7213 | 92.3217 | 99.2673 | 106.2125 | 113.1534
| WhitbyWind2035RCP4.5 | Whitby | Wind | RCP4.5 | 2035 | 85.7369 | 92.3554 | 99.3217 | 106.2849 | 113.2437
| WhitbyWind2040RCP4.5 | Whitby | Wind | RCP4.5 | 2040 | 85.7526 | 92.3892 | 99.3762 | 106.3573 | 113.334
| WhitbyWind2045RCP4.5 | Whitby | Wind | RCP4.5 | 2045 | 85.7683 | 92.4229 | 99.4306 | 106.4296 | 113.4243
| WhitbyWind2050RCP4.5 | Whitby | Wind | RCP4.5 | 2050 | 85.8677 | 92.5617 | 99.6178 | 106.6567 | 113.6952
| WhitbyWind2055RCP4.5 | Whitby | Wind | RCP4.5 | 2055 | 85.9515 | 92.6666 | 99.7504 | 106.8113 | 113.8757
| WhitbyWind2060RCP4.5 | Whitby | Wind | RCP4.5 | 2060 | 86.0353 | 92.7716 | 99.8831 | 106.966 | 114.0563
| WhitbyWind2065RCP4.5 | Whitby | Wind | RCP4.5 | 2065 | 86.1191 | 92.8765 | 100.0157 | 107.1207 | 114.2369
| WhitbyWind2070RCP4.5 | Whitby | Wind | RCP4.5 | 2070 | 86.2028 | 92.9815 | 100.1484 | 107.2753 | 114.4175
| WhitbyWind2075RCP4.5 | Whitby | Wind | RCP4.5 | 2075 | 86.3482 | 93.1687 | 100.3877 | 107.5596 | 114.7466
| WhitbyWind2080RCP4.5 | Whitby | Wind | RCP4.5 | 2080 | 86.4935 | 93.3559 | 100.6269 | 107.8438 | 115.0758
| WhitbyWind2085RCP4.5 | Whitby | Wind | RCP4.5 | 2085 | 86.6388 | 93.5431 | 100.8662 | 108.128 | 115.405
| WhitbyWind2090RCP4.5 | Whitby | Wind | RCP4.5 | 2090 | 86.7841 | 93.7303 | 101.1054 | 108.4123 | 115.7342
| WhitbyWind2095RCP4.5 | Whitby | Wind | RCP4.5 | 2095 | 86.9295 | 93.9175 | 101.3447 | 108.6965 | 116.0633
| WhitbyWind2100RCP4.5 | Whitby | Wind | RCP4.5 | 2100 | 87.0748 | 94.1047 | 101.5839 | 108.9808 | 116.3925
| WhitbyWind2023RCP6.0 | Whitby | Wind | RCP6.0 | 2023 | 85.6899 | 92.2541 | 99.1584 | 106.0677 | 112.9729
| WhitbyWind2025RCP6.0 | Whitby | Wind | RCP6.0 | 2025 | 85.7056 | 92.2879 | 99.2129 | 106.1401 | 113.0631
| WhitbyWind2030RCP6.0 | Whitby | Wind | RCP6.0 | 2030 | 85.7213 | 92.3217 | 99.2673 | 106.2125 | 113.1534
| WhitbyWind2035RCP6.0 | Whitby | Wind | RCP6.0 | 2035 | 85.7369 | 92.3554 | 99.3217 | 106.2849 | 113.2437
| WhitbyWind2040RCP6.0 | Whitby | Wind | RCP6.0 | 2040 | 85.7526 | 92.3892 | 99.3762 | 106.3573 | 113.334
| WhitbyWind2045RCP6.0 | Whitby | Wind | RCP6.0 | 2045 | 85.7683 | 92.4229 | 99.4306 | 106.4296 | 113.4243
| WhitbyWind2050RCP6.0 | Whitby | Wind | RCP6.0 | 2050 | 85.8677 | 92.5617 | 99.6178 | 106.6567 | 113.6952
| WhitbyWind2055RCP6.0 | Whitby | Wind | RCP6.0 | 2055 | 85.9515 | 92.6666 | 99.7504 | 106.8113 | 113.8757
| WhitbyWind2060RCP6.0 | Whitby | Wind | RCP6.0 | 2060 | 86.0353 | 92.7716 | 99.8831 | 106.966 | 114.0563
| WhitbyWind2065RCP6.0 | Whitby | Wind | RCP6.0 | 2065 | 86.1191 | 92.8765 | 100.0157 | 107.1207 | 114.2369
| WhitbyWind2070RCP6.0 | Whitby | Wind | RCP6.0 | 2070 | 86.2028 | 92.9815 | 100.1484 | 107.2753 | 114.4175
| WhitbyWind2075RCP6.0 | Whitby | Wind | RCP6.0 | 2075 | 86.4208 | 93.2623 | 100.5073 | 107.7017 | 114.9112
| WhitbyWind2080RCP6.0 | Whitby | Wind | RCP6.0 | 2080 | 86.6388 | 93.5431 | 100.8662 | 108.128 | 115.405
| WhitbyWind2085RCP6.0 | Whitby | Wind | RCP6.0 | 2085 | 86.8568 | 93.8239 | 101.225 | 108.5544 | 115.8988
| WhitbyWind2090RCP6.0 | Whitby | Wind | RCP6.0 | 2090 | 87.525 | 94.6572 | 102.267 | 109.7753 | 117.3029
| WhitbyWind2095RCP6.0 | Whitby | Wind | RCP6.0 | 2095 | 87.9752 | 95.2096 | 102.9501 | 110.5697 | 118.2133
| WhitbyWind2100RCP6.0 | Whitby | Wind | RCP6.0 | 2100 | 88.4254 | 95.762 | 103.6332 | 111.3642 | 119.1237
| WhitbyWind2023RCP8.5 | Whitby | Wind | RCP8.5 | 2023 | 85.6899 | 92.2541 | 99.1584 | 106.0677 | 112.9729
| WhitbyWind2025RCP8.5 | Whitby | Wind | RCP8.5 | 2025 | 85.7213 | 92.3217 | 99.2673 | 106.2125 | 113.1534
| WhitbyWind2030RCP8.5 | Whitby | Wind | RCP8.5 | 2030 | 85.7526 | 92.3892 | 99.3762 | 106.3573 | 113.334
| WhitbyWind2035RCP8.5 | Whitby | Wind | RCP8.5 | 2035 | 85.784 | 92.4567 | 99.4851 | 106.502 | 113.5146
| WhitbyWind2040RCP8.5 | Whitby | Wind | RCP8.5 | 2040 | 85.9236 | 92.6316 | 99.7062 | 106.7598 | 113.8155
| WhitbyWind2045RCP8.5 | Whitby | Wind | RCP8.5 | 2045 | 86.0632 | 92.8066 | 99.9273 | 107.0175 | 114.1165
| WhitbyWind2050RCP8.5 | Whitby | Wind | RCP8.5 | 2050 | 86.4935 | 93.3559 | 100.6269 | 107.8438 | 115.0758
| WhitbyWind2055RCP8.5 | Whitby | Wind | RCP8.5 | 2055 | 86.7841 | 93.7303 | 101.1054 | 108.4123 | 115.7342
| WhitbyWind2060RCP8.5 | Whitby | Wind | RCP8.5 | 2060 | 87.525 | 94.6572 | 102.267 | 109.7753 | 117.3029
| WhitbyWind2065RCP8.5 | Whitby | Wind | RCP8.5 | 2065 | 87.9752 | 95.2096 | 102.9501 | 110.5697 | 118.2133
| WhitbyWind2070RCP8.5 | Whitby | Wind | RCP8.5 | 2070 | 88.5594 | 95.9431 | 103.8741 | 111.6608 | 119.4698
| WhitbyWind2075RCP8.5 | Whitby | Wind | RCP8.5 | 2075 | 88.6933 | 96.1241 | 104.115 | 111.9574 | 119.8159
| WhitbyWind2080RCP8.5 | Whitby | Wind | RCP8.5 | 2080 | 88.8272 | 96.3052 | 104.3559 | 112.254 | 120.162
| WhitbyWind2085RCP8.5 | Whitby | Wind | RCP8.5 | 2085 | 89.1136 | 96.7103 | 104.9103 | 112.932 | 120.969
| WhitbyWind2090RCP8.5 | Whitby | Wind | RCP8.5 | 2090 | 89.4 | 97.1154 | 105.4647 | 113.6099 | 121.7759
| WhitbyWind2095RCP8.5 | Whitby | Wind | RCP8.5 | 2095 | 89.4 | 97.1154 | 105.4647 | 113.6099 | 121.7759
| WhitbyWind2100RCP8.5 | Whitby | Wind | RCP8.5 | 2100 | 89.4 | 97.1154 | 105.4647 | 113.6099 | 121.7759
| Whitby (Brooklin)Ice Accretion2023RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| Whitby (Brooklin)Ice Accretion2025RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| Whitby (Brooklin)Ice Accretion2030RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| Whitby (Brooklin)Ice Accretion2035RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| Whitby (Brooklin)Ice Accretion2040RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| Whitby (Brooklin)Ice Accretion2045RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| Whitby (Brooklin)Ice Accretion2050RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| Whitby (Brooklin)Ice Accretion2055RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| Whitby (Brooklin)Ice Accretion2060RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| Whitby (Brooklin)Ice Accretion2065RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| Whitby (Brooklin)Ice Accretion2070RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| Whitby (Brooklin)Ice Accretion2075RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
| Whitby (Brooklin)Ice Accretion2080RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| Whitby (Brooklin)Ice Accretion2085RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| Whitby (Brooklin)Ice Accretion2090RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| Whitby (Brooklin)Ice Accretion2095RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
| Whitby (Brooklin)Ice Accretion2100RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
| Whitby (Brooklin)Ice Accretion2023RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| Whitby (Brooklin)Ice Accretion2025RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
| Whitby (Brooklin)Ice Accretion2030RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| Whitby (Brooklin)Ice Accretion2035RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
| Whitby (Brooklin)Ice Accretion2040RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| Whitby (Brooklin)Ice Accretion2045RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
| Whitby (Brooklin)Ice Accretion2050RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
| Whitby (Brooklin)Ice Accretion2055RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
| Whitby (Brooklin)Ice Accretion2060RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
| Whitby (Brooklin)Ice Accretion2065RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
| Whitby (Brooklin)Ice Accretion2070RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
| Whitby (Brooklin)Ice Accretion2075RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
| Whitby (Brooklin)Ice Accretion2080RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
| Whitby (Brooklin)Ice Accretion2085RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
| Whitby (Brooklin)Ice Accretion2090RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| Whitby (Brooklin)Ice Accretion2095RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| Whitby (Brooklin)Ice Accretion2100RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
| Whitby (Brooklin)Ice Accretion2023RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
| Whitby (Brooklin)Ice Accretion2025RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
| Whitby (Brooklin)Ice Accretion2030RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
| Whitby (Brooklin)Ice Accretion2035RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
| Whitby (Brooklin)Ice Accretion2040RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
| Whitby (Brooklin)Ice Accretion2045RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
| Whitby (Brooklin)Ice Accretion2050RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
| Whitby (Brooklin)Ice Accretion2055RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
| Whitby (Brooklin)Ice Accretion2060RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
| Whitby (Brooklin)Ice Accretion2065RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
| Whitby (Brooklin)Ice Accretion2070RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
| Whitby (Brooklin)Ice Accretion2075RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
| Whitby (Brooklin)Ice Accretion2080RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
| Whitby (Brooklin)Ice Accretion2085RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
| Whitby (Brooklin)Ice Accretion2090RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| Whitby (Brooklin)Ice Accretion2095RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| Whitby (Brooklin)Ice Accretion2100RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
| Whitby (Brooklin)Wind2023RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2023 | 82.2277 | 88.5267 | 95.152 | 101.7821 | 108.4083
| Whitby (Brooklin)Wind2025RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2025 | 82.2427 | 88.5591 | 95.2043 | 101.8516 | 108.4949
| Whitby (Brooklin)Wind2030RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2030 | 82.2578 | 88.5915 | 95.2565 | 101.9211 | 108.5816
| Whitby (Brooklin)Wind2035RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2035 | 82.2728 | 88.6239 | 95.3088 | 101.9905 | 108.6682
| Whitby (Brooklin)Wind2040RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2040 | 82.2879 | 88.6563 | 95.361 | 102.06 | 108.7549
| Whitby (Brooklin)Wind2045RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2045 | 82.3029 | 88.6887 | 95.4132 | 102.1294 | 108.8415
| Whitby (Brooklin)Wind2050RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2050 | 82.3983 | 88.8218 | 95.5928 | 102.3473 | 109.1014
| Whitby (Brooklin)Wind2055RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2055 | 82.4787 | 88.9225 | 95.7201 | 102.4957 | 109.2747
| Whitby (Brooklin)Wind2060RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2060 | 82.5591 | 89.0232 | 95.8474 | 102.6441 | 109.448
| Whitby (Brooklin)Wind2065RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2065 | 82.6395 | 89.1239 | 95.9747 | 102.7925 | 109.6213
| Whitby (Brooklin)Wind2070RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2070 | 82.7199 | 89.2247 | 96.102 | 102.941 | 109.7945
| Whitby (Brooklin)Wind2075RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2075 | 82.8593 | 89.4043 | 96.3316 | 103.2137 | 110.1104
| Whitby (Brooklin)Wind2080RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2080 | 82.9988 | 89.584 | 96.5612 | 103.4865 | 110.4263
| Whitby (Brooklin)Wind2085RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2085 | 83.1382 | 89.7636 | 96.7908 | 103.7592 | 110.7422
| Whitby (Brooklin)Wind2090RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2090 | 83.2777 | 89.9432 | 97.0203 | 104.032 | 111.058
| Whitby (Brooklin)Wind2095RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2095 | 83.4172 | 90.1229 | 97.2499 | 104.3048 | 111.3739
| Whitby (Brooklin)Wind2100RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2100 | 83.5566 | 90.3025 | 97.4795 | 104.5775 | 111.6898
| Whitby (Brooklin)Wind2023RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2023 | 82.2277 | 88.5267 | 95.152 | 101.7821 | 108.4083
| Whitby (Brooklin)Wind2025RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2025 | 82.2427 | 88.5591 | 95.2043 | 101.8516 | 108.4949
| Whitby (Brooklin)Wind2030RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2030 | 82.2578 | 88.5915 | 95.2565 | 101.9211 | 108.5816
| Whitby (Brooklin)Wind2035RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2035 | 82.2728 | 88.6239 | 95.3088 | 101.9905 | 108.6682
| Whitby (Brooklin)Wind2040RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2040 | 82.2879 | 88.6563 | 95.361 | 102.06 | 108.7549
| Whitby (Brooklin)Wind2045RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2045 | 82.3029 | 88.6887 | 95.4132 | 102.1294 | 108.8415
| Whitby (Brooklin)Wind2050RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2050 | 82.3983 | 88.8218 | 95.5928 | 102.3473 | 109.1014
| Whitby (Brooklin)Wind2055RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2055 | 82.4787 | 88.9225 | 95.7201 | 102.4957 | 109.2747
| Whitby (Brooklin)Wind2060RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2060 | 82.5591 | 89.0232 | 95.8474 | 102.6441 | 109.448
| Whitby (Brooklin)Wind2065RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2065 | 82.6395 | 89.1239 | 95.9747 | 102.7925 | 109.6213
| Whitby (Brooklin)Wind2070RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2070 | 82.7199 | 89.2247 | 96.102 | 102.941 | 109.7945
| Whitby (Brooklin)Wind2075RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2075 | 82.9291 | 89.4941 | 96.4464 | 103.3501 | 110.2684
| Whitby (Brooklin)Wind2080RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2080 | 83.1382 | 89.7636 | 96.7908 | 103.7592 | 110.7422
| Whitby (Brooklin)Wind2085RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2085 | 83.3474 | 90.0331 | 97.1351 | 104.1684 | 111.216
| Whitby (Brooklin)Wind2090RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2090 | 83.9886 | 90.8326 | 98.135 | 105.3399 | 112.5634
| Whitby (Brooklin)Wind2095RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2095 | 84.4207 | 91.3627 | 98.7905 | 106.1023 | 113.437
| Whitby (Brooklin)Wind2100RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2100 | 84.8527 | 91.8928 | 99.446 | 106.8646 | 114.3107
| Whitby (Brooklin)Wind2023RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2023 | 82.2277 | 88.5267 | 95.152 | 101.7821 | 108.4083
| Whitby (Brooklin)Wind2025RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2025 | 82.2578 | 88.5915 | 95.2565 | 101.9211 | 108.5816
| Whitby (Brooklin)Wind2030RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2030 | 82.2879 | 88.6563 | 95.361 | 102.06 | 108.7549
| Whitby (Brooklin)Wind2035RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2035 | 82.3179 | 88.7211 | 95.4655 | 102.1989 | 108.9281
| Whitby (Brooklin)Wind2040RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2040 | 82.4519 | 88.8889 | 95.6777 | 102.4463 | 109.2169
| Whitby (Brooklin)Wind2045RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2045 | 82.5859 | 89.0568 | 95.8898 | 102.6936 | 109.5057
| Whitby (Brooklin)Wind2050RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2050 | 82.9988 | 89.584 | 96.5612 | 103.4865 | 110.4263
| Whitby (Brooklin)Wind2055RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2055 | 83.2777 | 89.9432 | 97.0203 | 104.032 | 111.058
| Whitby (Brooklin)Wind2060RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2060 | 83.9886 | 90.8326 | 98.135 | 105.3399 | 112.5634
| Whitby (Brooklin)Wind2065RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2065 | 84.4207 | 91.3627 | 98.7905 | 106.1023 | 113.437
| Whitby (Brooklin)Wind2070RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2070 | 84.9812 | 92.0666 | 99.6772 | 107.1493 | 114.6428
| Whitby (Brooklin)Wind2075RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2075 | 85.1097 | 92.2403 | 99.9083 | 107.4339 | 114.9749
| Whitby (Brooklin)Wind2080RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2080 | 85.2382 | 92.4141 | 100.1395 | 107.7185 | 115.307
| Whitby (Brooklin)Wind2085RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2085 | 85.513 | 92.8028 | 100.6715 | 108.3691 | 116.0814
| Whitby (Brooklin)Wind2090RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2090 | 85.7878 | 93.1916 | 101.2035 | 109.0196 | 116.8557
| Whitby (Brooklin)Wind2095RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2095 | 85.7878 | 93.1916 | 101.2035 | 109.0196 | 116.8557
| Whitby (Brooklin)Wind2100RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2100 | 85.7878 | 93.1916 | 101.2035 | 109.0196 | 116.8557
| White RiverIce Accretion2023RCP4.5 | White River | Ice Accretion | RCP4.5 | 2023 | 10.6569 | 12.6741 | 15.225 | 17.1873 | 19.1457
| White RiverIce Accretion2025RCP4.5 | White River | Ice Accretion | RCP4.5 | 2025 | 10.7039 | 12.7301 | 15.2925 | 17.2608 | 19.2276
| White RiverIce Accretion2030RCP4.5 | White River | Ice Accretion | RCP4.5 | 2030 | 10.7508 | 12.7861 | 15.36 | 17.3342 | 19.3095
| White RiverIce Accretion2035RCP4.5 | White River | Ice Accretion | RCP4.5 | 2035 | 10.7978 | 12.8422 | 15.4275 | 17.4077 | 19.3914
| White RiverIce Accretion2040RCP4.5 | White River | Ice Accretion | RCP4.5 | 2040 | 10.8448 | 12.8982 | 15.495 | 17.4811 | 19.4733
| White RiverIce Accretion2045RCP4.5 | White River | Ice Accretion | RCP4.5 | 2045 | 10.8917 | 12.9542 | 15.5625 | 17.5545 | 19.5552
| White RiverIce Accretion2050RCP4.5 | White River | Ice Accretion | RCP4.5 | 2050 | 10.9825 | 13.065 | 15.699 | 17.7127 | 19.7316
| White RiverIce Accretion2055RCP4.5 | White River | Ice Accretion | RCP4.5 | 2055 | 11.0264 | 13.1198 | 15.768 | 17.7975 | 19.8261
| White RiverIce Accretion2060RCP4.5 | White River | Ice Accretion | RCP4.5 | 2060 | 11.0702 | 13.1746 | 15.837 | 17.8822 | 19.9206
| White RiverIce Accretion2065RCP4.5 | White River | Ice Accretion | RCP4.5 | 2065 | 11.1141 | 13.2294 | 15.906 | 17.967 | 20.0151
| White RiverIce Accretion2070RCP4.5 | White River | Ice Accretion | RCP4.5 | 2070 | 11.1579 | 13.2841 | 15.975 | 18.0517 | 20.1096
| White RiverIce Accretion2075RCP4.5 | White River | Ice Accretion | RCP4.5 | 2075 | 11.177 | 13.3111 | 16.015 | 18.0969 | 20.1632
| White RiverIce Accretion2080RCP4.5 | White River | Ice Accretion | RCP4.5 | 2080 | 11.1962 | 13.3381 | 16.055 | 18.1421 | 20.2167
| White RiverIce Accretion2085RCP4.5 | White River | Ice Accretion | RCP4.5 | 2085 | 11.2153 | 13.3651 | 16.095 | 18.1873 | 20.2702
| White RiverIce Accretion2090RCP4.5 | White River | Ice Accretion | RCP4.5 | 2090 | 11.2344 | 13.392 | 16.135 | 18.2325 | 20.3238
| White RiverIce Accretion2095RCP4.5 | White River | Ice Accretion | RCP4.5 | 2095 | 11.2536 | 13.419 | 16.175 | 18.2777 | 20.3773
| White RiverIce Accretion2100RCP4.5 | White River | Ice Accretion | RCP4.5 | 2100 | 11.2727 | 13.446 | 16.215 | 18.3229 | 20.4309
| White RiverIce Accretion2023RCP6.0 | White River | Ice Accretion | RCP6.0 | 2023 | 10.6569 | 12.6741 | 15.225 | 17.1873 | 19.1457
| White RiverIce Accretion2025RCP6.0 | White River | Ice Accretion | RCP6.0 | 2025 | 10.7039 | 12.7301 | 15.2925 | 17.2608 | 19.2276
| White RiverIce Accretion2030RCP6.0 | White River | Ice Accretion | RCP6.0 | 2030 | 10.7508 | 12.7861 | 15.36 | 17.3342 | 19.3095
| White RiverIce Accretion2035RCP6.0 | White River | Ice Accretion | RCP6.0 | 2035 | 10.7978 | 12.8422 | 15.4275 | 17.4077 | 19.3914
| White RiverIce Accretion2040RCP6.0 | White River | Ice Accretion | RCP6.0 | 2040 | 10.8448 | 12.8982 | 15.495 | 17.4811 | 19.4733
| White RiverIce Accretion2045RCP6.0 | White River | Ice Accretion | RCP6.0 | 2045 | 10.8917 | 12.9542 | 15.5625 | 17.5545 | 19.5552
| White RiverIce Accretion2050RCP6.0 | White River | Ice Accretion | RCP6.0 | 2050 | 10.9825 | 13.065 | 15.699 | 17.7127 | 19.7316
| White RiverIce Accretion2055RCP6.0 | White River | Ice Accretion | RCP6.0 | 2055 | 11.0264 | 13.1198 | 15.768 | 17.7975 | 19.8261
| White RiverIce Accretion2060RCP6.0 | White River | Ice Accretion | RCP6.0 | 2060 | 11.0702 | 13.1746 | 15.837 | 17.8822 | 19.9206
| White RiverIce Accretion2065RCP6.0 | White River | Ice Accretion | RCP6.0 | 2065 | 11.1141 | 13.2294 | 15.906 | 17.967 | 20.0151
| White RiverIce Accretion2070RCP6.0 | White River | Ice Accretion | RCP6.0 | 2070 | 11.1579 | 13.2841 | 15.975 | 18.0517 | 20.1096
| White RiverIce Accretion2075RCP6.0 | White River | Ice Accretion | RCP6.0 | 2075 | 11.1866 | 13.3246 | 16.035 | 18.1195 | 20.1899
| White RiverIce Accretion2080RCP6.0 | White River | Ice Accretion | RCP6.0 | 2080 | 11.2153 | 13.3651 | 16.095 | 18.1873 | 20.2702
| White RiverIce Accretion2085RCP6.0 | White River | Ice Accretion | RCP6.0 | 2085 | 11.244 | 13.4055 | 16.155 | 18.2552 | 20.3506
| White RiverIce Accretion2090RCP6.0 | White River | Ice Accretion | RCP6.0 | 2090 | 11.1718 | 13.3339 | 16.085 | 18.1817 | 20.2797
| White RiverIce Accretion2095RCP6.0 | White River | Ice Accretion | RCP6.0 | 2095 | 11.0709 | 13.2219 | 15.955 | 18.0404 | 20.1285
| White RiverIce Accretion2100RCP6.0 | White River | Ice Accretion | RCP6.0 | 2100 | 10.97 | 13.1098 | 15.825 | 17.8992 | 19.9773
| White RiverIce Accretion2023RCP8.5 | White River | Ice Accretion | RCP8.5 | 2023 | 10.6569 | 12.6741 | 15.225 | 17.1873 | 19.1457
| White RiverIce Accretion2025RCP8.5 | White River | Ice Accretion | RCP8.5 | 2025 | 10.7508 | 12.7861 | 15.36 | 17.3342 | 19.3095
| White RiverIce Accretion2030RCP8.5 | White River | Ice Accretion | RCP8.5 | 2030 | 10.8448 | 12.8982 | 15.495 | 17.4811 | 19.4733
| White RiverIce Accretion2035RCP8.5 | White River | Ice Accretion | RCP8.5 | 2035 | 10.9387 | 13.0102 | 15.63 | 17.628 | 19.6371
| White RiverIce Accretion2040RCP8.5 | White River | Ice Accretion | RCP8.5 | 2040 | 11.0118 | 13.1015 | 15.745 | 17.7692 | 19.7946
| White RiverIce Accretion2045RCP8.5 | White River | Ice Accretion | RCP8.5 | 2045 | 11.0848 | 13.1928 | 15.86 | 17.9105 | 19.9521
| White RiverIce Accretion2050RCP8.5 | White River | Ice Accretion | RCP8.5 | 2050 | 11.1962 | 13.3381 | 16.055 | 18.1421 | 20.2167
| White RiverIce Accretion2055RCP8.5 | White River | Ice Accretion | RCP8.5 | 2055 | 11.2344 | 13.392 | 16.135 | 18.2325 | 20.3238
| White RiverIce Accretion2060RCP8.5 | White River | Ice Accretion | RCP8.5 | 2060 | 11.1718 | 13.3339 | 16.085 | 18.1817 | 20.2797
| White RiverIce Accretion2065RCP8.5 | White River | Ice Accretion | RCP8.5 | 2065 | 11.0709 | 13.2219 | 15.955 | 18.0404 | 20.1285
| White RiverIce Accretion2070RCP8.5 | White River | Ice Accretion | RCP8.5 | 2070 | 10.9874 | 13.1472 | 15.885 | 17.9726 | 20.0655
| White RiverIce Accretion2075RCP8.5 | White River | Ice Accretion | RCP8.5 | 2075 | 11.0048 | 13.1845 | 15.945 | 18.0461 | 20.1537
| White RiverIce Accretion2080RCP8.5 | White River | Ice Accretion | RCP8.5 | 2080 | 11.0222 | 13.2219 | 16.005 | 18.1195 | 20.2419
| White RiverIce Accretion2085RCP8.5 | White River | Ice Accretion | RCP8.5 | 2085 | 10.9074 | 13.0849 | 15.8475 | 17.95 | 20.0529
| White RiverIce Accretion2090RCP8.5 | White River | Ice Accretion | RCP8.5 | 2090 | 10.7926 | 12.948 | 15.69 | 17.7805 | 19.8639
| White RiverIce Accretion2095RCP8.5 | White River | Ice Accretion | RCP8.5 | 2095 | 10.7926 | 12.948 | 15.69 | 17.7805 | 19.8639
| White RiverIce Accretion2100RCP8.5 | White River | Ice Accretion | RCP8.5 | 2100 | 10.7926 | 12.948 | 15.69 | 17.7805 | 19.8639
| White RiverWind2023RCP4.5 | White River | Wind | RCP4.5 | 2023 | 72.2926 | 77.7998 | 83.581 | 89.3784 | 95.1783
| White RiverWind2025RCP4.5 | White River | Wind | RCP4.5 | 2025 | 72.3308 | 77.8435 | 83.6308 | 89.4332 | 95.2382
| White RiverWind2030RCP4.5 | White River | Wind | RCP4.5 | 2030 | 72.369 | 77.8873 | 83.6806 | 89.4879 | 95.2981
| White RiverWind2035RCP4.5 | White River | Wind | RCP4.5 | 2035 | 72.4072 | 77.931 | 83.7304 | 89.5427 | 95.358
| White RiverWind2040RCP4.5 | White River | Wind | RCP4.5 | 2040 | 72.4455 | 77.9748 | 83.7802 | 89.5974 | 95.418
| White RiverWind2045RCP4.5 | White River | Wind | RCP4.5 | 2045 | 72.4837 | 78.0185 | 83.83 | 89.6522 | 95.4779
| White RiverWind2050RCP4.5 | White River | Wind | RCP4.5 | 2050 | 72.5491 | 78.0854 | 83.8997 | 89.7247 | 95.5511
| White RiverWind2055RCP4.5 | White River | Wind | RCP4.5 | 2055 | 72.5764 | 78.1086 | 83.9196 | 89.7425 | 95.5643
| White RiverWind2060RCP4.5 | White River | Wind | RCP4.5 | 2060 | 72.6036 | 78.1317 | 83.9396 | 89.7603 | 95.5776
| White RiverWind2065RCP4.5 | White River | Wind | RCP4.5 | 2065 | 72.6308 | 78.1549 | 83.9595 | 89.778 | 95.5908
| White RiverWind2070RCP4.5 | White River | Wind | RCP4.5 | 2070 | 72.6581 | 78.178 | 83.9794 | 89.7958 | 95.604
| White RiverWind2075RCP4.5 | White River | Wind | RCP4.5 | 2075 | 72.7106 | 78.2334 | 84.0375 | 89.8565 | 95.6687
| White RiverWind2080RCP4.5 | White River | Wind | RCP4.5 | 2080 | 72.7632 | 78.2887 | 84.0956 | 89.9172 | 95.7334
| White RiverWind2085RCP4.5 | White River | Wind | RCP4.5 | 2085 | 72.8157 | 78.344 | 84.1537 | 89.9779 | 95.798
| White RiverWind2090RCP4.5 | White River | Wind | RCP4.5 | 2090 | 72.8683 | 78.3993 | 84.2118 | 90.0385 | 95.8627
| White RiverWind2095RCP4.5 | White River | Wind | RCP4.5 | 2095 | 72.9209 | 78.4546 | 84.2699 | 90.0992 | 95.9273
| White RiverWind2100RCP4.5 | White River | Wind | RCP4.5 | 2100 | 72.9734 | 78.5099 | 84.328 | 90.1599 | 95.992
| White RiverWind2023RCP6.0 | White River | Wind | RCP6.0 | 2023 | 72.2926 | 77.7998 | 83.581 | 89.3784 | 95.1783
| White RiverWind2025RCP6.0 | White River | Wind | RCP6.0 | 2025 | 72.3308 | 77.8435 | 83.6308 | 89.4332 | 95.2382
| White RiverWind2030RCP6.0 | White River | Wind | RCP6.0 | 2030 | 72.369 | 77.8873 | 83.6806 | 89.4879 | 95.2981
| White RiverWind2035RCP6.0 | White River | Wind | RCP6.0 | 2035 | 72.4072 | 77.931 | 83.7304 | 89.5427 | 95.358
| White RiverWind2040RCP6.0 | White River | Wind | RCP6.0 | 2040 | 72.4455 | 77.9748 | 83.7802 | 89.5974 | 95.418
| White RiverWind2045RCP6.0 | White River | Wind | RCP6.0 | 2045 | 72.4837 | 78.0185 | 83.83 | 89.6522 | 95.4779
| White RiverWind2050RCP6.0 | White River | Wind | RCP6.0 | 2050 | 72.5491 | 78.0854 | 83.8997 | 89.7247 | 95.5511
| White RiverWind2055RCP6.0 | White River | Wind | RCP6.0 | 2055 | 72.5764 | 78.1086 | 83.9196 | 89.7425 | 95.5643
| White RiverWind2060RCP6.0 | White River | Wind | RCP6.0 | 2060 | 72.6036 | 78.1317 | 83.9396 | 89.7603 | 95.5776
| White RiverWind2065RCP6.0 | White River | Wind | RCP6.0 | 2065 | 72.6308 | 78.1549 | 83.9595 | 89.778 | 95.5908
| White RiverWind2070RCP6.0 | White River | Wind | RCP6.0 | 2070 | 72.6581 | 78.178 | 83.9794 | 89.7958 | 95.604
| White RiverWind2075RCP6.0 | White River | Wind | RCP6.0 | 2075 | 72.7369 | 78.261 | 84.0666 | 89.8868 | 95.701
| White RiverWind2080RCP6.0 | White River | Wind | RCP6.0 | 2080 | 72.8157 | 78.344 | 84.1537 | 89.9779 | 95.798
| White RiverWind2085RCP6.0 | White River | Wind | RCP6.0 | 2085 | 72.8946 | 78.427 | 84.2408 | 90.0689 | 95.895
| White RiverWind2090RCP6.0 | White River | Wind | RCP6.0 | 2090 | 73.2266 | 78.8136 | 84.6904 | 90.5744 | 96.4588
| White RiverWind2095RCP6.0 | White River | Wind | RCP6.0 | 2095 | 73.4799 | 79.1172 | 85.0529 | 90.9888 | 96.9256
| White RiverWind2100RCP6.0 | White River | Wind | RCP6.0 | 2100 | 73.7331 | 79.4208 | 85.4153 | 91.4033 | 97.3924
| White RiverWind2023RCP8.5 | White River | Wind | RCP8.5 | 2023 | 72.2926 | 77.7998 | 83.581 | 89.3784 | 95.1783
| White RiverWind2025RCP8.5 | White River | Wind | RCP8.5 | 2025 | 72.369 | 77.8873 | 83.6806 | 89.4879 | 95.2981
| White RiverWind2030RCP8.5 | White River | Wind | RCP8.5 | 2030 | 72.4455 | 77.9748 | 83.7802 | 89.5974 | 95.418
| White RiverWind2035RCP8.5 | White River | Wind | RCP8.5 | 2035 | 72.5219 | 78.0622 | 83.8798 | 89.707 | 95.5378
| White RiverWind2040RCP8.5 | White River | Wind | RCP8.5 | 2040 | 72.5673 | 78.1008 | 83.913 | 89.7366 | 95.5599
| White RiverWind2045RCP8.5 | White River | Wind | RCP8.5 | 2045 | 72.6127 | 78.1394 | 83.9462 | 89.7662 | 95.582
| White RiverWind2050RCP8.5 | White River | Wind | RCP8.5 | 2050 | 72.7632 | 78.2887 | 84.0956 | 89.9172 | 95.7334
| White RiverWind2055RCP8.5 | White River | Wind | RCP8.5 | 2055 | 72.8683 | 78.3993 | 84.2118 | 90.0385 | 95.8627
| White RiverWind2060RCP8.5 | White River | Wind | RCP8.5 | 2060 | 73.2266 | 78.8136 | 84.6904 | 90.5744 | 96.4588
| White RiverWind2065RCP8.5 | White River | Wind | RCP8.5 | 2065 | 73.4799 | 79.1172 | 85.0529 | 90.9888 | 96.9256
| White RiverWind2070RCP8.5 | White River | Wind | RCP8.5 | 2070 | 73.9338 | 79.6498 | 85.6754 | 91.6904 | 97.7078
| White RiverWind2075RCP8.5 | White River | Wind | RCP8.5 | 2075 | 74.1345 | 79.8788 | 85.9354 | 91.9776 | 98.0232
| White RiverWind2080RCP8.5 | White River | Wind | RCP8.5 | 2080 | 74.3351 | 80.1078 | 86.1955 | 92.2647 | 98.3386
| White RiverWind2085RCP8.5 | White River | Wind | RCP8.5 | 2085 | 74.6075 | 80.4551 | 86.6312 | 92.7754 | 98.9252
| White RiverWind2090RCP8.5 | White River | Wind | RCP8.5 | 2090 | 74.8798 | 80.8025 | 87.067 | 93.286 | 99.5119
| White RiverWind2095RCP8.5 | White River | Wind | RCP8.5 | 2095 | 74.8798 | 80.8025 | 87.067 | 93.286 | 99.5119
| White RiverWind2100RCP8.5 | White River | Wind | RCP8.5 | 2100 | 74.8798 | 80.8025 | 87.067 | 93.286 | 99.5119
| WiartonIce Accretion2023RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2023 | 13.9865 | 16.7162 | 20.18 | 22.8486 | 25.4772
| WiartonIce Accretion2025RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2025 | 13.9958 | 16.7383 | 20.2167 | 22.8938 | 25.536
| WiartonIce Accretion2030RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2030 | 14.0051 | 16.7605 | 20.2533 | 22.939 | 25.5948
| WiartonIce Accretion2035RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2035 | 14.0143 | 16.7826 | 20.29 | 22.9842 | 25.6536
| WiartonIce Accretion2040RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2040 | 14.0236 | 16.8047 | 20.3267 | 23.0294 | 25.7124
| WiartonIce Accretion2045RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2045 | 14.0329 | 16.8269 | 20.3633 | 23.0746 | 25.7712
| WiartonIce Accretion2050RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2050 | 13.9921 | 16.8025 | 20.36 | 23.0836 | 25.7947
| WiartonIce Accretion2055RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2055 | 13.942 | 16.756 | 20.32 | 23.0475 | 25.7594
| WiartonIce Accretion2060RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2060 | 13.8919 | 16.7096 | 20.28 | 23.0113 | 25.7242
| WiartonIce Accretion2065RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2065 | 13.8418 | 16.6631 | 20.24 | 22.9752 | 25.6889
| WiartonIce Accretion2070RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2070 | 13.7917 | 16.6166 | 20.2 | 22.939 | 25.6536
| WiartonIce Accretion2075RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2075 | 13.7406 | 16.5806 | 20.18 | 22.9277 | 25.6536
| WiartonIce Accretion2080RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2080 | 13.6896 | 16.5447 | 20.16 | 22.9164 | 25.6536
| WiartonIce Accretion2085RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2085 | 13.6386 | 16.5087 | 20.14 | 22.9051 | 25.6536
| WiartonIce Accretion2090RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2090 | 13.5876 | 16.4727 | 20.12 | 22.8938 | 25.6536
| WiartonIce Accretion2095RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2095 | 13.5365 | 16.4368 | 20.1 | 22.8825 | 25.6536
| WiartonIce Accretion2100RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2100 | 13.4855 | 16.4008 | 20.08 | 22.8712 | 25.6536
| WiartonIce Accretion2023RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2023 | 13.9865 | 16.7162 | 20.18 | 22.8486 | 25.4772
| WiartonIce Accretion2025RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2025 | 13.9958 | 16.7383 | 20.2167 | 22.8938 | 25.536
| WiartonIce Accretion2030RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2030 | 14.0051 | 16.7605 | 20.2533 | 22.939 | 25.5948
| WiartonIce Accretion2035RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2035 | 14.0143 | 16.7826 | 20.29 | 22.9842 | 25.6536
| WiartonIce Accretion2040RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2040 | 14.0236 | 16.8047 | 20.3267 | 23.0294 | 25.7124
| WiartonIce Accretion2045RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2045 | 14.0329 | 16.8269 | 20.3633 | 23.0746 | 25.7712
| WiartonIce Accretion2050RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2050 | 13.9921 | 16.8025 | 20.36 | 23.0836 | 25.7947
| WiartonIce Accretion2055RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2055 | 13.942 | 16.756 | 20.32 | 23.0475 | 25.7594
| WiartonIce Accretion2060RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2060 | 13.8919 | 16.7096 | 20.28 | 23.0113 | 25.7242
| WiartonIce Accretion2065RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2065 | 13.8418 | 16.6631 | 20.24 | 22.9752 | 25.6889
| WiartonIce Accretion2070RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2070 | 13.7917 | 16.6166 | 20.2 | 22.939 | 25.6536
| WiartonIce Accretion2075RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2075 | 13.7151 | 16.5626 | 20.17 | 22.922 | 25.6536
| WiartonIce Accretion2080RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2080 | 13.6386 | 16.5087 | 20.14 | 22.9051 | 25.6536
| WiartonIce Accretion2085RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2085 | 13.562 | 16.4547 | 20.11 | 22.8881 | 25.6536
| WiartonIce Accretion2090RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2090 | 13.2489 | 16.1518 | 19.8067 | 22.5849 | 25.3512
| WiartonIce Accretion2095RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2095 | 13.0123 | 15.9028 | 19.5333 | 22.2987 | 25.0488
| WiartonIce Accretion2100RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2100 | 12.7757 | 15.6538 | 19.26 | 22.0124 | 24.7464
| WiartonIce Accretion2023RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2023 | 13.9865 | 16.7162 | 20.18 | 22.8486 | 25.4772
| WiartonIce Accretion2025RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2025 | 14.0051 | 16.7605 | 20.2533 | 22.939 | 25.5948
| WiartonIce Accretion2030RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2030 | 14.0236 | 16.8047 | 20.3267 | 23.0294 | 25.7124
| WiartonIce Accretion2035RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2035 | 14.0422 | 16.849 | 20.4 | 23.1198 | 25.83
| WiartonIce Accretion2040RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2040 | 13.9587 | 16.7715 | 20.3333 | 23.0595 | 25.7712
| WiartonIce Accretion2045RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2045 | 13.8752 | 16.6941 | 20.2667 | 22.9993 | 25.7124
| WiartonIce Accretion2050RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2050 | 13.6896 | 16.5447 | 20.16 | 22.9164 | 25.6536
| WiartonIce Accretion2055RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2055 | 13.5876 | 16.4727 | 20.12 | 22.8938 | 25.6536
| WiartonIce Accretion2060RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2060 | 13.2489 | 16.1518 | 19.8067 | 22.5849 | 25.3512
| WiartonIce Accretion2065RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2065 | 13.0123 | 15.9028 | 19.5333 | 22.2987 | 25.0488
| WiartonIce Accretion2070RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2070 | 12.4232 | 15.2609 | 18.82 | 21.5378 | 24.234
| WiartonIce Accretion2075RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2075 | 12.0706 | 14.8681 | 18.38 | 21.0632 | 23.7216
| WiartonIce Accretion2080RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2080 | 11.718 | 14.4752 | 17.94 | 20.5886 | 23.2092
| WiartonIce Accretion2085RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2085 | 11.1196 | 13.7863 | 17.13 | 19.6733 | 22.2012
| WiartonIce Accretion2090RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2090 | 10.5212 | 13.0974 | 16.32 | 18.758 | 21.1932
| WiartonIce Accretion2095RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2095 | 10.5212 | 13.0974 | 16.32 | 18.758 | 21.1932
| WiartonIce Accretion2100RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2100 | 10.5212 | 13.0974 | 16.32 | 18.758 | 21.1932
| WiartonWind2023RCP4.5 | Wiarton | Wind | RCP4.5 | 2023 | 82.8943 | 89.1818 | 95.7696 | 102.3913 | 109.0022
| WiartonWind2025RCP4.5 | Wiarton | Wind | RCP4.5 | 2025 | 82.9703 | 89.2755 | 95.888 | 102.5283 | 109.1609
| WiartonWind2030RCP4.5 | Wiarton | Wind | RCP4.5 | 2030 | 83.0463 | 89.3693 | 96.0064 | 102.6652 | 109.3196
| WiartonWind2035RCP4.5 | Wiarton | Wind | RCP4.5 | 2035 | 83.1223 | 89.463 | 96.1248 | 102.8022 | 109.4783
| WiartonWind2040RCP4.5 | Wiarton | Wind | RCP4.5 | 2040 | 83.1983 | 89.5568 | 96.2432 | 102.9391 | 109.637
| WiartonWind2045RCP4.5 | Wiarton | Wind | RCP4.5 | 2045 | 83.2742 | 89.6505 | 96.3616 | 103.0761 | 109.7957
| WiartonWind2050RCP4.5 | Wiarton | Wind | RCP4.5 | 2050 | 83.3469 | 89.7353 | 96.4608 | 103.1884 | 109.9215
| WiartonWind2055RCP4.5 | Wiarton | Wind | RCP4.5 | 2055 | 83.3436 | 89.7264 | 96.4416 | 103.1638 | 109.8887
| WiartonWind2060RCP4.5 | Wiarton | Wind | RCP4.5 | 2060 | 83.3403 | 89.7175 | 96.4224 | 103.1391 | 109.8559
| WiartonWind2065RCP4.5 | Wiarton | Wind | RCP4.5 | 2065 | 83.337 | 89.7085 | 96.4032 | 103.1144 | 109.823
| WiartonWind2070RCP4.5 | Wiarton | Wind | RCP4.5 | 2070 | 83.3337 | 89.6996 | 96.384 | 103.0898 | 109.7902
| WiartonWind2075RCP4.5 | Wiarton | Wind | RCP4.5 | 2075 | 83.3516 | 89.719 | 96.4048 | 103.112 | 109.8139
| WiartonWind2080RCP4.5 | Wiarton | Wind | RCP4.5 | 2080 | 83.3696 | 89.7383 | 96.4256 | 103.1343 | 109.8376
| WiartonWind2085RCP4.5 | Wiarton | Wind | RCP4.5 | 2085 | 83.3875 | 89.7576 | 96.4464 | 103.1566 | 109.8613
| WiartonWind2090RCP4.5 | Wiarton | Wind | RCP4.5 | 2090 | 83.4055 | 89.777 | 96.4672 | 103.1788 | 109.8851
| WiartonWind2095RCP4.5 | Wiarton | Wind | RCP4.5 | 2095 | 83.4235 | 89.7963 | 96.488 | 103.2011 | 109.9088
| WiartonWind2100RCP4.5 | Wiarton | Wind | RCP4.5 | 2100 | 83.4414 | 89.8157 | 96.5088 | 103.2233 | 109.9325
| WiartonWind2023RCP6.0 | Wiarton | Wind | RCP6.0 | 2023 | 82.8943 | 89.1818 | 95.7696 | 102.3913 | 109.0022
| WiartonWind2025RCP6.0 | Wiarton | Wind | RCP6.0 | 2025 | 82.9703 | 89.2755 | 95.888 | 102.5283 | 109.1609
| WiartonWind2030RCP6.0 | Wiarton | Wind | RCP6.0 | 2030 | 83.0463 | 89.3693 | 96.0064 | 102.6652 | 109.3196
| WiartonWind2035RCP6.0 | Wiarton | Wind | RCP6.0 | 2035 | 83.1223 | 89.463 | 96.1248 | 102.8022 | 109.4783
| WiartonWind2040RCP6.0 | Wiarton | Wind | RCP6.0 | 2040 | 83.1983 | 89.5568 | 96.2432 | 102.9391 | 109.637
| WiartonWind2045RCP6.0 | Wiarton | Wind | RCP6.0 | 2045 | 83.2742 | 89.6505 | 96.3616 | 103.0761 | 109.7957
| WiartonWind2050RCP6.0 | Wiarton | Wind | RCP6.0 | 2050 | 83.3469 | 89.7353 | 96.4608 | 103.1884 | 109.9215
| WiartonWind2055RCP6.0 | Wiarton | Wind | RCP6.0 | 2055 | 83.3436 | 89.7264 | 96.4416 | 103.1638 | 109.8887
| WiartonWind2060RCP6.0 | Wiarton | Wind | RCP6.0 | 2060 | 83.3403 | 89.7175 | 96.4224 | 103.1391 | 109.8559
| WiartonWind2065RCP6.0 | Wiarton | Wind | RCP6.0 | 2065 | 83.337 | 89.7085 | 96.4032 | 103.1144 | 109.823
| WiartonWind2070RCP6.0 | Wiarton | Wind | RCP6.0 | 2070 | 83.3337 | 89.6996 | 96.384 | 103.0898 | 109.7902
| WiartonWind2075RCP6.0 | Wiarton | Wind | RCP6.0 | 2075 | 83.3606 | 89.7286 | 96.4152 | 103.1232 | 109.8258
| WiartonWind2080RCP6.0 | Wiarton | Wind | RCP6.0 | 2080 | 83.3875 | 89.7576 | 96.4464 | 103.1566 | 109.8613
| WiartonWind2085RCP6.0 | Wiarton | Wind | RCP6.0 | 2085 | 83.4145 | 89.7867 | 96.4776 | 103.1899 | 109.8969
| WiartonWind2090RCP6.0 | Wiarton | Wind | RCP6.0 | 2090 | 83.574 | 89.9764 | 96.704 | 103.4459 | 110.1805
| WiartonWind2095RCP6.0 | Wiarton | Wind | RCP6.0 | 2095 | 83.7067 | 90.1371 | 96.8992 | 103.6684 | 110.4286
| WiartonWind2100RCP6.0 | Wiarton | Wind | RCP6.0 | 2100 | 83.8393 | 90.2978 | 97.0944 | 103.891 | 110.6767
| WiartonWind2023RCP8.5 | Wiarton | Wind | RCP8.5 | 2023 | 82.8943 | 89.1818 | 95.7696 | 102.3913 | 109.0022
| WiartonWind2025RCP8.5 | Wiarton | Wind | RCP8.5 | 2025 | 83.0463 | 89.3693 | 96.0064 | 102.6652 | 109.3196
| WiartonWind2030RCP8.5 | Wiarton | Wind | RCP8.5 | 2030 | 83.1983 | 89.5568 | 96.2432 | 102.9391 | 109.637
| WiartonWind2035RCP8.5 | Wiarton | Wind | RCP8.5 | 2035 | 83.3502 | 89.7443 | 96.48 | 103.2131 | 109.9544
| WiartonWind2040RCP8.5 | Wiarton | Wind | RCP8.5 | 2040 | 83.3447 | 89.7294 | 96.448 | 103.172 | 109.8996
| WiartonWind2045RCP8.5 | Wiarton | Wind | RCP8.5 | 2045 | 83.3392 | 89.7145 | 96.416 | 103.1309 | 109.8449
| WiartonWind2050RCP8.5 | Wiarton | Wind | RCP8.5 | 2050 | 83.3696 | 89.7383 | 96.4256 | 103.1343 | 109.8376
| WiartonWind2055RCP8.5 | Wiarton | Wind | RCP8.5 | 2055 | 83.4055 | 89.777 | 96.4672 | 103.1788 | 109.8851
| WiartonWind2060RCP8.5 | Wiarton | Wind | RCP8.5 | 2060 | 83.574 | 89.9764 | 96.704 | 103.4459 | 110.1805
| WiartonWind2065RCP8.5 | Wiarton | Wind | RCP8.5 | 2065 | 83.7067 | 90.1371 | 96.8992 | 103.6684 | 110.4286
| WiartonWind2070RCP8.5 | Wiarton | Wind | RCP8.5 | 2070 | 83.9084 | 90.3811 | 97.1904 | 104.0006 | 110.8044
| WiartonWind2075RCP8.5 | Wiarton | Wind | RCP8.5 | 2075 | 83.9775 | 90.4644 | 97.2864 | 104.1101 | 110.932
| WiartonWind2080RCP8.5 | Wiarton | Wind | RCP8.5 | 2080 | 84.0465 | 90.5478 | 97.3824 | 104.2197 | 111.0597
| WiartonWind2085RCP8.5 | Wiarton | Wind | RCP8.5 | 2085 | 84.3657 | 90.9763 | 97.9536 | 104.9079 | 111.8641
| WiartonWind2090RCP8.5 | Wiarton | Wind | RCP8.5 | 2090 | 84.6848 | 91.4049 | 98.5248 | 105.5962 | 112.6685
| WiartonWind2095RCP8.5 | Wiarton | Wind | RCP8.5 | 2095 | 84.6848 | 91.4049 | 98.5248 | 105.5962 | 112.6685
| WiartonWind2100RCP8.5 | Wiarton | Wind | RCP8.5 | 2100 | 84.6848 | 91.4049 | 98.5248 | 105.5962 | 112.6685
| WindsorIce Accretion2023RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2023 | 17.1352 | 20.5218 | 24.825 | 28.0805 | 31.374
| WindsorIce Accretion2025RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2025 | 17.0975 | 20.4941 | 24.8042 | 28.0711 | 31.3635
| WindsorIce Accretion2030RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2030 | 17.0598 | 20.4664 | 24.7833 | 28.0617 | 31.353
| WindsorIce Accretion2035RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2035 | 17.0221 | 20.4387 | 24.7625 | 28.0522 | 31.3425
| WindsorIce Accretion2040RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2040 | 16.9844 | 20.4111 | 24.7417 | 28.0428 | 31.332
| WindsorIce Accretion2045RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2045 | 16.9468 | 20.3834 | 24.7208 | 28.0334 | 31.3215
| WindsorIce Accretion2050RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2050 | 16.5437 | 19.949 | 24.24 | 27.5155 | 30.7629
| WindsorIce Accretion2055RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2055 | 16.1784 | 19.5423 | 23.78 | 27.007 | 30.2148
| WindsorIce Accretion2060RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2060 | 15.8131 | 19.1357 | 23.32 | 26.4985 | 29.6667
| WindsorIce Accretion2065RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2065 | 15.4478 | 18.729 | 22.86 | 25.99 | 29.1186
| WindsorIce Accretion2070RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2070 | 15.0825 | 18.3223 | 22.4 | 25.4815 | 28.5705
| WindsorIce Accretion2075RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2075 | 14.7374 | 17.928 | 21.9375 | 24.9683 | 28.0088
| WindsorIce Accretion2080RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2080 | 14.3924 | 17.5338 | 21.475 | 24.4551 | 27.447
| WindsorIce Accretion2085RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2085 | 14.0474 | 17.1395 | 21.0125 | 23.9419 | 26.8853
| WindsorIce Accretion2090RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2090 | 13.7024 | 16.7452 | 20.55 | 23.4287 | 26.3235
| WindsorIce Accretion2095RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2095 | 13.3573 | 16.351 | 20.0875 | 22.9155 | 25.7618
| WindsorIce Accretion2100RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2100 | 13.0123 | 15.9567 | 19.625 | 22.4022 | 25.2
| WindsorIce Accretion2023RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2023 | 17.1352 | 20.5218 | 24.825 | 28.0805 | 31.374
| WindsorIce Accretion2025RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2025 | 17.0975 | 20.4941 | 24.8042 | 28.0711 | 31.3635
| WindsorIce Accretion2030RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2030 | 17.0598 | 20.4664 | 24.7833 | 28.0617 | 31.353
| WindsorIce Accretion2035RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2035 | 17.0221 | 20.4387 | 24.7625 | 28.0522 | 31.3425
| WindsorIce Accretion2040RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2040 | 16.9844 | 20.4111 | 24.7417 | 28.0428 | 31.332
| WindsorIce Accretion2045RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2045 | 16.9468 | 20.3834 | 24.7208 | 28.0334 | 31.3215
| WindsorIce Accretion2050RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2050 | 16.5437 | 19.949 | 24.24 | 27.5155 | 30.7629
| WindsorIce Accretion2055RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2055 | 16.1784 | 19.5423 | 23.78 | 27.007 | 30.2148
| WindsorIce Accretion2060RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2060 | 15.8131 | 19.1357 | 23.32 | 26.4985 | 29.6667
| WindsorIce Accretion2065RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2065 | 15.4478 | 18.729 | 22.86 | 25.99 | 29.1186
| WindsorIce Accretion2070RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2070 | 15.0825 | 18.3223 | 22.4 | 25.4815 | 28.5705
| WindsorIce Accretion2075RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2075 | 14.5649 | 17.7309 | 21.7063 | 24.7117 | 27.7279
| WindsorIce Accretion2080RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2080 | 14.0474 | 17.1395 | 21.0125 | 23.9419 | 26.8853
| WindsorIce Accretion2085RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2085 | 13.5299 | 16.5481 | 20.3188 | 23.1721 | 26.0426
| WindsorIce Accretion2090RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2090 | 12.1773 | 14.9607 | 18.4333 | 21.0557 | 23.6985
| WindsorIce Accretion2095RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2095 | 11.3423 | 13.9648 | 17.2417 | 19.7091 | 22.197
| WindsorIce Accretion2100RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2100 | 10.5073 | 12.9688 | 16.05 | 18.3625 | 20.6955
| WindsorIce Accretion2023RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2023 | 17.1352 | 20.5218 | 24.825 | 28.0805 | 31.374
| WindsorIce Accretion2025RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2025 | 17.0598 | 20.4664 | 24.7833 | 28.0617 | 31.353
| WindsorIce Accretion2030RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2030 | 16.9844 | 20.4111 | 24.7417 | 28.0428 | 31.332
| WindsorIce Accretion2035RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2035 | 16.9091 | 20.3558 | 24.7 | 28.024 | 31.311
| WindsorIce Accretion2040RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2040 | 16.3002 | 19.6779 | 23.9333 | 27.1765 | 30.3975
| WindsorIce Accretion2045RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2045 | 15.6913 | 19.0001 | 23.1667 | 26.329 | 29.484
| WindsorIce Accretion2050RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2050 | 14.3924 | 17.5338 | 21.475 | 24.4551 | 27.447
| WindsorIce Accretion2055RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2055 | 13.7024 | 16.7452 | 20.55 | 23.4287 | 26.3235
| WindsorIce Accretion2060RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2060 | 12.1773 | 14.9607 | 18.4333 | 21.0557 | 23.6985
| WindsorIce Accretion2065RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2065 | 11.3423 | 13.9648 | 17.2417 | 19.7091 | 22.197
| WindsorIce Accretion2070RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2070 | 9.9506 | 12.3117 | 15.2583 | 17.4679 | 19.698
| WindsorIce Accretion2075RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2075 | 9.3939 | 11.6546 | 14.4667 | 16.5733 | 18.7005
| WindsorIce Accretion2080RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2080 | 8.8372 | 10.9975 | 13.675 | 15.6787 | 17.703
| WindsorIce Accretion2085RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2085 | 7.9413 | 9.9185 | 12.3625 | 14.1956 | 16.0335
| WindsorIce Accretion2090RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2090 | 7.0454 | 8.8395 | 11.05 | 12.7125 | 14.364
| WindsorIce Accretion2095RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2095 | 7.0454 | 8.8395 | 11.05 | 12.7125 | 14.364
| WindsorIce Accretion2100RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2100 | 7.0454 | 8.8395 | 11.05 | 12.7125 | 14.364
| WindsorWind2023RCP4.5 | Windsor | Wind | RCP4.5 | 2023 | 84.0928 | 90.5618 | 97.3686 | 104.174 | 110.9781
| WindsorWind2025RCP4.5 | Windsor | Wind | RCP4.5 | 2025 | 84.1096 | 90.5829 | 97.3961 | 104.2069 | 111.0168
| WindsorWind2030RCP4.5 | Windsor | Wind | RCP4.5 | 2030 | 84.1263 | 90.6039 | 97.4236 | 104.2398 | 111.0555
| WindsorWind2035RCP4.5 | Windsor | Wind | RCP4.5 | 2035 | 84.1431 | 90.625 | 97.4511 | 104.2726 | 111.0942
| WindsorWind2040RCP4.5 | Windsor | Wind | RCP4.5 | 2040 | 84.1598 | 90.646 | 97.4785 | 104.3055 | 111.1329
| WindsorWind2045RCP4.5 | Windsor | Wind | RCP4.5 | 2045 | 84.1766 | 90.6671 | 97.506 | 104.3384 | 111.1716
| WindsorWind2050RCP4.5 | Windsor | Wind | RCP4.5 | 2050 | 84.133 | 90.6033 | 97.4171 | 104.2301 | 111.0422
| WindsorWind2055RCP4.5 | Windsor | Wind | RCP4.5 | 2055 | 84.0727 | 90.5185 | 97.3007 | 104.0889 | 110.8741
| WindsorWind2060RCP4.5 | Windsor | Wind | RCP4.5 | 2060 | 84.0124 | 90.4337 | 97.1843 | 103.9478 | 110.7061
| WindsorWind2065RCP4.5 | Windsor | Wind | RCP4.5 | 2065 | 83.9521 | 90.3489 | 97.0679 | 103.8066 | 110.538
| WindsorWind2070RCP4.5 | Windsor | Wind | RCP4.5 | 2070 | 83.8918 | 90.2641 | 96.9515 | 103.6655 | 110.3699
| WindsorWind2075RCP4.5 | Windsor | Wind | RCP4.5 | 2075 | 84.0928 | 90.5333 | 97.3056 | 104.091 | 110.8675
| WindsorWind2080RCP4.5 | Windsor | Wind | RCP4.5 | 2080 | 84.2938 | 90.8024 | 97.6596 | 104.5165 | 111.3651
| WindsorWind2085RCP4.5 | Windsor | Wind | RCP4.5 | 2085 | 84.4949 | 91.0715 | 98.0137 | 104.9421 | 111.8627
| WindsorWind2090RCP4.5 | Windsor | Wind | RCP4.5 | 2090 | 84.6959 | 91.3406 | 98.3677 | 105.3676 | 112.3603
| WindsorWind2095RCP4.5 | Windsor | Wind | RCP4.5 | 2095 | 84.8969 | 91.6098 | 98.7218 | 105.7931 | 112.8579
| WindsorWind2100RCP4.5 | Windsor | Wind | RCP4.5 | 2100 | 85.0979 | 91.8789 | 99.0758 | 106.2187 | 113.3556
| WindsorWind2023RCP6.0 | Windsor | Wind | RCP6.0 | 2023 | 84.0928 | 90.5618 | 97.3686 | 104.174 | 110.9781
| WindsorWind2025RCP6.0 | Windsor | Wind | RCP6.0 | 2025 | 84.1096 | 90.5829 | 97.3961 | 104.2069 | 111.0168
| WindsorWind2030RCP6.0 | Windsor | Wind | RCP6.0 | 2030 | 84.1263 | 90.6039 | 97.4236 | 104.2398 | 111.0555
| WindsorWind2035RCP6.0 | Windsor | Wind | RCP6.0 | 2035 | 84.1431 | 90.625 | 97.4511 | 104.2726 | 111.0942
| WindsorWind2040RCP6.0 | Windsor | Wind | RCP6.0 | 2040 | 84.1598 | 90.646 | 97.4785 | 104.3055 | 111.1329
| WindsorWind2045RCP6.0 | Windsor | Wind | RCP6.0 | 2045 | 84.1766 | 90.6671 | 97.506 | 104.3384 | 111.1716
| WindsorWind2050RCP6.0 | Windsor | Wind | RCP6.0 | 2050 | 84.133 | 90.6033 | 97.4171 | 104.2301 | 111.0422
| WindsorWind2055RCP6.0 | Windsor | Wind | RCP6.0 | 2055 | 84.0727 | 90.5185 | 97.3007 | 104.0889 | 110.8741
| WindsorWind2060RCP6.0 | Windsor | Wind | RCP6.0 | 2060 | 84.0124 | 90.4337 | 97.1843 | 103.9478 | 110.7061
| WindsorWind2065RCP6.0 | Windsor | Wind | RCP6.0 | 2065 | 83.9521 | 90.3489 | 97.0679 | 103.8066 | 110.538
| WindsorWind2070RCP6.0 | Windsor | Wind | RCP6.0 | 2070 | 83.8918 | 90.2641 | 96.9515 | 103.6655 | 110.3699
| WindsorWind2075RCP6.0 | Windsor | Wind | RCP6.0 | 2075 | 84.1933 | 90.6678 | 97.4826 | 104.3038 | 111.1163
| WindsorWind2080RCP6.0 | Windsor | Wind | RCP6.0 | 2080 | 84.4949 | 91.0715 | 98.0137 | 104.9421 | 111.8627
| WindsorWind2085RCP6.0 | Windsor | Wind | RCP6.0 | 2085 | 84.7964 | 91.4752 | 98.5447 | 105.5804 | 112.6091
| WindsorWind2090RCP6.0 | Windsor | Wind | RCP6.0 | 2090 | 85.4748 | 92.3299 | 99.6125 | 106.8276 | 114.0448
| WindsorWind2095RCP6.0 | Windsor | Wind | RCP6.0 | 2095 | 85.8517 | 92.781 | 100.1493 | 107.4365 | 114.7341
| WindsorWind2100RCP6.0 | Windsor | Wind | RCP6.0 | 2100 | 86.2287 | 93.232 | 100.686 | 108.0454 | 115.4234
| WindsorWind2023RCP8.5 | Windsor | Wind | RCP8.5 | 2023 | 84.0928 | 90.5618 | 97.3686 | 104.174 | 110.9781
| WindsorWind2025RCP8.5 | Windsor | Wind | RCP8.5 | 2025 | 84.1263 | 90.6039 | 97.4236 | 104.2398 | 111.0555
| WindsorWind2030RCP8.5 | Windsor | Wind | RCP8.5 | 2030 | 84.1598 | 90.646 | 97.4785 | 104.3055 | 111.1329
| WindsorWind2035RCP8.5 | Windsor | Wind | RCP8.5 | 2035 | 84.1933 | 90.6881 | 97.5335 | 104.3712 | 111.2103
| WindsorWind2040RCP8.5 | Windsor | Wind | RCP8.5 | 2040 | 84.0928 | 90.5468 | 97.3395 | 104.136 | 110.9302
| WindsorWind2045RCP8.5 | Windsor | Wind | RCP8.5 | 2045 | 83.9923 | 90.4055 | 97.1455 | 103.9007 | 110.65
| WindsorWind2050RCP8.5 | Windsor | Wind | RCP8.5 | 2050 | 84.2938 | 90.8024 | 97.6596 | 104.5165 | 111.3651
| WindsorWind2055RCP8.5 | Windsor | Wind | RCP8.5 | 2055 | 84.6959 | 91.3406 | 98.3677 | 105.3676 | 112.3603
| WindsorWind2060RCP8.5 | Windsor | Wind | RCP8.5 | 2060 | 85.4748 | 92.3299 | 99.6125 | 106.8276 | 114.0448
| WindsorWind2065RCP8.5 | Windsor | Wind | RCP8.5 | 2065 | 85.8517 | 92.781 | 100.1493 | 107.4365 | 114.7341
| WindsorWind2070RCP8.5 | Windsor | Wind | RCP8.5 | 2070 | 86.4939 | 93.5508 | 101.074 | 108.4917 | 115.9247
| WindsorWind2075RCP8.5 | Windsor | Wind | RCP8.5 | 2075 | 86.7591 | 93.8695 | 101.462 | 108.938 | 116.426
| WindsorWind2080RCP8.5 | Windsor | Wind | RCP8.5 | 2080 | 87.0243 | 94.1883 | 101.85 | 109.3843 | 116.9273
| WindsorWind2085RCP8.5 | Windsor | Wind | RCP8.5 | 2085 | 87.351 | 94.5762 | 102.3108 | 109.9136 | 117.5244
| WindsorWind2090RCP8.5 | Windsor | Wind | RCP8.5 | 2090 | 87.6777 | 94.9641 | 102.7715 | 110.4429 | 118.1216
| WindsorWind2095RCP8.5 | Windsor | Wind | RCP8.5 | 2095 | 87.6777 | 94.9641 | 102.7715 | 110.4429 | 118.1216
| WindsorWind2100RCP8.5 | Windsor | Wind | RCP8.5 | 2100 | 87.6777 | 94.9641 | 102.7715 | 110.4429 | 118.1216
| WinghamIce Accretion2023RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2023 | 15.9725 | 19.1854 | 23.253 | 26.3539 | 29.4437
| WinghamIce Accretion2025RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2025 | 16.0498 | 19.2841 | 23.3795 | 26.5055 | 29.6176
| WinghamIce Accretion2030RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2030 | 16.1272 | 19.3827 | 23.506 | 26.6571 | 29.7914
| WinghamIce Accretion2035RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2035 | 16.2045 | 19.4813 | 23.6325 | 26.8087 | 29.9653
| WinghamIce Accretion2040RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2040 | 16.2819 | 19.58 | 23.759 | 26.9603 | 30.1392
| WinghamIce Accretion2045RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2045 | 16.3592 | 19.6786 | 23.8855 | 27.1119 | 30.3131
| WinghamIce Accretion2050RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2050 | 16.443 | 19.8078 | 24.0764 | 27.3415 | 30.5913
| WinghamIce Accretion2055RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2055 | 16.4494 | 19.8383 | 24.1408 | 27.4194 | 30.6956
| WinghamIce Accretion2060RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2060 | 16.4558 | 19.8689 | 24.2052 | 27.4974 | 30.7999
| WinghamIce Accretion2065RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2065 | 16.4622 | 19.8994 | 24.2696 | 27.5754 | 30.9043
| WinghamIce Accretion2070RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2070 | 16.4686 | 19.93 | 24.334 | 27.6534 | 31.0086
| WinghamIce Accretion2075RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2075 | 16.4179 | 19.8981 | 24.3187 | 27.6577 | 31.0231
| WinghamIce Accretion2080RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2080 | 16.3672 | 19.8663 | 24.3033 | 27.662 | 31.0376
| WinghamIce Accretion2085RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2085 | 16.3165 | 19.8345 | 24.288 | 27.6664 | 31.0521
| WinghamIce Accretion2090RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2090 | 16.2659 | 19.8027 | 24.2727 | 27.6707 | 31.0666
| WinghamIce Accretion2095RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2095 | 16.2152 | 19.7709 | 24.2573 | 27.675 | 31.0811
| WinghamIce Accretion2100RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2100 | 16.1645 | 19.7391 | 24.242 | 27.6793 | 31.0955
| WinghamIce Accretion2023RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2023 | 15.9725 | 19.1854 | 23.253 | 26.3539 | 29.4437
| WinghamIce Accretion2025RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2025 | 16.0498 | 19.2841 | 23.3795 | 26.5055 | 29.6176
| WinghamIce Accretion2030RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2030 | 16.1272 | 19.3827 | 23.506 | 26.6571 | 29.7914
| WinghamIce Accretion2035RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2035 | 16.2045 | 19.4813 | 23.6325 | 26.8087 | 29.9653
| WinghamIce Accretion2040RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2040 | 16.2819 | 19.58 | 23.759 | 26.9603 | 30.1392
| WinghamIce Accretion2045RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2045 | 16.3592 | 19.6786 | 23.8855 | 27.1119 | 30.3131
| WinghamIce Accretion2050RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2050 | 16.443 | 19.8078 | 24.0764 | 27.3415 | 30.5913
| WinghamIce Accretion2055RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2055 | 16.4494 | 19.8383 | 24.1408 | 27.4194 | 30.6956
| WinghamIce Accretion2060RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2060 | 16.4558 | 19.8689 | 24.2052 | 27.4974 | 30.7999
| WinghamIce Accretion2065RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2065 | 16.4622 | 19.8994 | 24.2696 | 27.5754 | 30.9043
| WinghamIce Accretion2070RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2070 | 16.4686 | 19.93 | 24.334 | 27.6534 | 31.0086
| WinghamIce Accretion2075RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2075 | 16.3926 | 19.8822 | 24.311 | 27.6599 | 31.0303
| WinghamIce Accretion2080RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2080 | 16.3165 | 19.8345 | 24.288 | 27.6664 | 31.0521
| WinghamIce Accretion2085RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2085 | 16.2405 | 19.7868 | 24.265 | 27.6729 | 31.0738
| WinghamIce Accretion2090RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2090 | 15.8978 | 19.4654 | 23.9583 | 27.3761 | 30.7864
| WinghamIce Accretion2095RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2095 | 15.631 | 19.1918 | 23.6747 | 27.0729 | 30.4773
| WinghamIce Accretion2100RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2100 | 15.3643 | 18.9182 | 23.391 | 26.7697 | 30.1682
| WinghamIce Accretion2023RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2023 | 15.9725 | 19.1854 | 23.253 | 26.3539 | 29.4437
| WinghamIce Accretion2025RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2025 | 16.1272 | 19.3827 | 23.506 | 26.6571 | 29.7914
| WinghamIce Accretion2030RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2030 | 16.2819 | 19.58 | 23.759 | 26.9603 | 30.1392
| WinghamIce Accretion2035RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2035 | 16.4366 | 19.7772 | 24.012 | 27.2635 | 30.487
| WinghamIce Accretion2040RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2040 | 16.4473 | 19.8281 | 24.1193 | 27.3935 | 30.6608
| WinghamIce Accretion2045RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2045 | 16.4579 | 19.8791 | 24.2267 | 27.5234 | 30.8347
| WinghamIce Accretion2050RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2050 | 16.3672 | 19.8663 | 24.3033 | 27.662 | 31.0376
| WinghamIce Accretion2055RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2055 | 16.2659 | 19.8027 | 24.2727 | 27.6707 | 31.0666
| WinghamIce Accretion2060RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2060 | 15.8978 | 19.4654 | 23.9583 | 27.3761 | 30.7864
| WinghamIce Accretion2065RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2065 | 15.631 | 19.1918 | 23.6747 | 27.0729 | 30.4773
| WinghamIce Accretion2070RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2070 | 14.8735 | 18.3646 | 22.7623 | 26.0853 | 29.4147
| WinghamIce Accretion2075RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2075 | 14.3827 | 17.811 | 22.1337 | 25.4009 | 28.6612
| WinghamIce Accretion2080RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2080 | 13.8919 | 17.2574 | 21.505 | 24.7165 | 27.9077
| WinghamIce Accretion2085RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2085 | 13.1717 | 16.4079 | 20.493 | 23.5729 | 26.6471
| WinghamIce Accretion2090RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2090 | 12.4515 | 15.5583 | 19.481 | 22.4294 | 25.3865
| WinghamIce Accretion2095RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2095 | 12.4515 | 15.5583 | 19.481 | 22.4294 | 25.3865
| WinghamIce Accretion2100RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2100 | 12.4515 | 15.5583 | 19.481 | 22.4294 | 25.3865
| WinghamWind2023RCP4.5 | Wingham | Wind | RCP4.5 | 2023 | 85.2136 | 91.8691 | 98.8918 | 105.8981 | 112.9042
| WinghamWind2025RCP4.5 | Wingham | Wind | RCP4.5 | 2025 | 85.2588 | 91.9223 | 98.9555 | 105.9698 | 112.9862
| WinghamWind2030RCP4.5 | Wingham | Wind | RCP4.5 | 2030 | 85.3039 | 91.9754 | 99.0192 | 106.0414 | 113.0681
| WinghamWind2035RCP4.5 | Wingham | Wind | RCP4.5 | 2035 | 85.349 | 92.0286 | 99.0829 | 106.1131 | 113.15
| WinghamWind2040RCP4.5 | Wingham | Wind | RCP4.5 | 2040 | 85.3942 | 92.0818 | 99.1466 | 106.1847 | 113.2319
| WinghamWind2045RCP4.5 | Wingham | Wind | RCP4.5 | 2045 | 85.4393 | 92.1349 | 99.2103 | 106.2564 | 113.3139
| WinghamWind2050RCP4.5 | Wingham | Wind | RCP4.5 | 2050 | 85.4929 | 92.1936 | 99.274 | 106.3259 | 113.3869
| WinghamWind2055RCP4.5 | Wingham | Wind | RCP4.5 | 2055 | 85.5013 | 92.199 | 99.274 | 106.3238 | 113.3779
| WinghamWind2060RCP4.5 | Wingham | Wind | RCP4.5 | 2060 | 85.5098 | 92.2045 | 99.274 | 106.3217 | 113.369
| WinghamWind2065RCP4.5 | Wingham | Wind | RCP4.5 | 2065 | 85.5183 | 92.21 | 99.274 | 106.3197 | 113.36
| WinghamWind2070RCP4.5 | Wingham | Wind | RCP4.5 | 2070 | 85.5267 | 92.2155 | 99.274 | 106.3176 | 113.3511
| WinghamWind2075RCP4.5 | Wingham | Wind | RCP4.5 | 2075 | 85.6212 | 92.3446 | 99.4488 | 106.5308 | 113.6043
| WinghamWind2080RCP4.5 | Wingham | Wind | RCP4.5 | 2080 | 85.7157 | 92.4737 | 99.6235 | 106.744 | 113.8576
| WinghamWind2085RCP4.5 | Wingham | Wind | RCP4.5 | 2085 | 85.8102 | 92.6028 | 99.7983 | 106.9572 | 114.1108
| WinghamWind2090RCP4.5 | Wingham | Wind | RCP4.5 | 2090 | 85.9047 | 92.7319 | 99.9731 | 107.1704 | 114.364
| WinghamWind2095RCP4.5 | Wingham | Wind | RCP4.5 | 2095 | 85.9992 | 92.861 | 100.1478 | 107.3836 | 114.6173
| WinghamWind2100RCP4.5 | Wingham | Wind | RCP4.5 | 2100 | 86.0937 | 92.9901 | 100.3226 | 107.5968 | 114.8705
| WinghamWind2023RCP6.0 | Wingham | Wind | RCP6.0 | 2023 | 85.2136 | 91.8691 | 98.8918 | 105.8981 | 112.9042
| WinghamWind2025RCP6.0 | Wingham | Wind | RCP6.0 | 2025 | 85.2588 | 91.9223 | 98.9555 | 105.9698 | 112.9862
| WinghamWind2030RCP6.0 | Wingham | Wind | RCP6.0 | 2030 | 85.3039 | 91.9754 | 99.0192 | 106.0414 | 113.0681
| WinghamWind2035RCP6.0 | Wingham | Wind | RCP6.0 | 2035 | 85.349 | 92.0286 | 99.0829 | 106.1131 | 113.15
| WinghamWind2040RCP6.0 | Wingham | Wind | RCP6.0 | 2040 | 85.3942 | 92.0818 | 99.1466 | 106.1847 | 113.2319
| WinghamWind2045RCP6.0 | Wingham | Wind | RCP6.0 | 2045 | 85.4393 | 92.1349 | 99.2103 | 106.2564 | 113.3139
| WinghamWind2050RCP6.0 | Wingham | Wind | RCP6.0 | 2050 | 85.4929 | 92.1936 | 99.274 | 106.3259 | 113.3869
| WinghamWind2055RCP6.0 | Wingham | Wind | RCP6.0 | 2055 | 85.5013 | 92.199 | 99.274 | 106.3238 | 113.3779
| WinghamWind2060RCP6.0 | Wingham | Wind | RCP6.0 | 2060 | 85.5098 | 92.2045 | 99.274 | 106.3217 | 113.369
| WinghamWind2065RCP6.0 | Wingham | Wind | RCP6.0 | 2065 | 85.5183 | 92.21 | 99.274 | 106.3197 | 113.36
| WinghamWind2070RCP6.0 | Wingham | Wind | RCP6.0 | 2070 | 85.5267 | 92.2155 | 99.274 | 106.3176 | 113.3511
| WinghamWind2075RCP6.0 | Wingham | Wind | RCP6.0 | 2075 | 85.6685 | 92.4091 | 99.5361 | 106.6374 | 113.731
| WinghamWind2080RCP6.0 | Wingham | Wind | RCP6.0 | 2080 | 85.8102 | 92.6028 | 99.7983 | 106.9572 | 114.1108
| WinghamWind2085RCP6.0 | Wingham | Wind | RCP6.0 | 2085 | 85.9519 | 92.7965 | 100.0605 | 107.277 | 114.4907
| WinghamWind2090RCP6.0 | Wingham | Wind | RCP6.0 | 2090 | 86.4688 | 93.4519 | 100.8877 | 108.2505 | 115.619
| WinghamWind2095RCP6.0 | Wingham | Wind | RCP6.0 | 2095 | 86.844 | 93.9137 | 101.4529 | 108.9041 | 116.3676
| WinghamWind2100RCP6.0 | Wingham | Wind | RCP6.0 | 2100 | 87.2192 | 94.3755 | 102.018 | 109.5577 | 117.1161
| WinghamWind2023RCP8.5 | Wingham | Wind | RCP8.5 | 2023 | 85.2136 | 91.8691 | 98.8918 | 105.8981 | 112.9042
| WinghamWind2025RCP8.5 | Wingham | Wind | RCP8.5 | 2025 | 85.3039 | 91.9754 | 99.0192 | 106.0414 | 113.0681
| WinghamWind2030RCP8.5 | Wingham | Wind | RCP8.5 | 2030 | 85.3942 | 92.0818 | 99.1466 | 106.1847 | 113.2319
| WinghamWind2035RCP8.5 | Wingham | Wind | RCP8.5 | 2035 | 85.4844 | 92.1881 | 99.274 | 106.328 | 113.3958
| WinghamWind2040RCP8.5 | Wingham | Wind | RCP8.5 | 2040 | 85.4985 | 92.1972 | 99.274 | 106.3245 | 113.3809
| WinghamWind2045RCP8.5 | Wingham | Wind | RCP8.5 | 2045 | 85.5126 | 92.2063 | 99.274 | 106.321 | 113.366
| WinghamWind2050RCP8.5 | Wingham | Wind | RCP8.5 | 2050 | 85.7157 | 92.4737 | 99.6235 | 106.744 | 113.8576
| WinghamWind2055RCP8.5 | Wingham | Wind | RCP8.5 | 2055 | 85.9047 | 92.7319 | 99.9731 | 107.1704 | 114.364
| WinghamWind2060RCP8.5 | Wingham | Wind | RCP8.5 | 2060 | 86.4688 | 93.4519 | 100.8877 | 108.2505 | 115.619
| WinghamWind2065RCP8.5 | Wingham | Wind | RCP8.5 | 2065 | 86.844 | 93.9137 | 101.4529 | 108.9041 | 116.3676
| WinghamWind2070RCP8.5 | Wingham | Wind | RCP8.5 | 2070 | 87.4956 | 94.737 | 102.4917 | 110.124 | 117.7789
| WinghamWind2075RCP8.5 | Wingham | Wind | RCP8.5 | 2075 | 87.772 | 95.0985 | 102.9653 | 110.6902 | 118.4418
| WinghamWind2080RCP8.5 | Wingham | Wind | RCP8.5 | 2080 | 88.0484 | 95.46 | 103.439 | 111.2565 | 119.1047
| WinghamWind2085RCP8.5 | Wingham | Wind | RCP8.5 | 2085 | 88.2642 | 95.7471 | 103.8163 | 111.7074 | 119.6298
| WinghamWind2090RCP8.5 | Wingham | Wind | RCP8.5 | 2090 | 88.48 | 96.0342 | 104.1936 | 112.1583 | 120.1549
| WinghamWind2095RCP8.5 | Wingham | Wind | RCP8.5 | 2095 | 88.48 | 96.0342 | 104.1936 | 112.1583 | 120.1549
| WinghamWind2100RCP8.5 | Wingham | Wind | RCP8.5 | 2100 | 88.48 | 96.0342 | 104.1936 | 112.1583 | 120.1549
| WoodstockIce Accretion2023RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
| WoodstockIce Accretion2025RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2025 | 20.3952 | 24.4642 | 29.605 | 33.5328 | 37.4661
| WoodstockIce Accretion2030RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2030 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
| WoodstockIce Accretion2035RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2035 | 20.3117 | 24.3895 | 29.535 | 33.4763 | 37.4031
| WoodstockIce Accretion2040RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2040 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
| WoodstockIce Accretion2045RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2045 | 20.2282 | 24.3148 | 29.465 | 33.4198 | 37.3401
| WoodstockIce Accretion2050RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2050 | 20.0571 | 24.153 | 29.316 | 33.2762 | 37.2028
| WoodstockIce Accretion2055RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2055 | 19.9276 | 24.0285 | 29.202 | 33.161 | 37.0969
| WoodstockIce Accretion2060RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2060 | 19.7982 | 23.904 | 29.088 | 33.0457 | 36.9911
| WoodstockIce Accretion2065RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2065 | 19.6688 | 23.7795 | 28.974 | 32.9305 | 36.8852
| WoodstockIce Accretion2070RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2070 | 19.5394 | 23.655 | 28.86 | 32.8152 | 36.7794
| WoodstockIce Accretion2075RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2075 | 19.4837 | 23.6135 | 28.84 | 32.8095 | 36.7857
| WoodstockIce Accretion2080RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2080 | 19.428 | 23.572 | 28.82 | 32.8039 | 36.792
| WoodstockIce Accretion2085RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2085 | 19.3724 | 23.5305 | 28.8 | 32.7982 | 36.7983
| WoodstockIce Accretion2090RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2090 | 19.3167 | 23.489 | 28.78 | 32.7926 | 36.8046
| WoodstockIce Accretion2095RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2095 | 19.261 | 23.4475 | 28.76 | 32.7869 | 36.8109
| WoodstockIce Accretion2100RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2100 | 19.2054 | 23.406 | 28.74 | 32.7813 | 36.8172
| WoodstockIce Accretion2023RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
| WoodstockIce Accretion2025RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2025 | 20.3952 | 24.4642 | 29.605 | 33.5328 | 37.4661
| WoodstockIce Accretion2030RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2030 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
| WoodstockIce Accretion2035RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2035 | 20.3117 | 24.3895 | 29.535 | 33.4763 | 37.4031
| WoodstockIce Accretion2040RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2040 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
| WoodstockIce Accretion2045RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2045 | 20.2282 | 24.3148 | 29.465 | 33.4198 | 37.3401
| WoodstockIce Accretion2050RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2050 | 20.0571 | 24.153 | 29.316 | 33.2762 | 37.2028
| WoodstockIce Accretion2055RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2055 | 19.9276 | 24.0285 | 29.202 | 33.161 | 37.0969
| WoodstockIce Accretion2060RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2060 | 19.7982 | 23.904 | 29.088 | 33.0457 | 36.9911
| WoodstockIce Accretion2065RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2065 | 19.6688 | 23.7795 | 28.974 | 32.9305 | 36.8852
| WoodstockIce Accretion2070RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2070 | 19.5394 | 23.655 | 28.86 | 32.8152 | 36.7794
| WoodstockIce Accretion2075RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2075 | 19.4559 | 23.5927 | 28.83 | 32.8067 | 36.7888
| WoodstockIce Accretion2080RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2080 | 19.3724 | 23.5305 | 28.8 | 32.7982 | 36.7983
| WoodstockIce Accretion2085RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2085 | 19.2889 | 23.4682 | 28.77 | 32.7898 | 36.8077
| WoodstockIce Accretion2090RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2090 | 18.7739 | 22.9412 | 28.21 | 32.2163 | 36.1998
| WoodstockIce Accretion2095RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2095 | 18.3425 | 22.4764 | 27.68 | 31.6513 | 35.5824
| WoodstockIce Accretion2100RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2100 | 17.9111 | 22.0116 | 27.15 | 31.0863 | 34.965
| WoodstockIce Accretion2023RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
| WoodstockIce Accretion2025RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2025 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
| WoodstockIce Accretion2030RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2030 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
| WoodstockIce Accretion2035RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2035 | 20.1865 | 24.2775 | 29.43 | 33.3915 | 37.3086
| WoodstockIce Accretion2040RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2040 | 19.9708 | 24.07 | 29.24 | 33.1994 | 37.1322
| WoodstockIce Accretion2045RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2045 | 19.7551 | 23.8625 | 29.05 | 33.0073 | 36.9558
| WoodstockIce Accretion2050RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2050 | 19.428 | 23.572 | 28.82 | 32.8039 | 36.792
| WoodstockIce Accretion2055RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2055 | 19.3167 | 23.489 | 28.78 | 32.7926 | 36.8046
| WoodstockIce Accretion2060RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2060 | 18.7739 | 22.9412 | 28.21 | 32.2163 | 36.1998
| WoodstockIce Accretion2065RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2065 | 18.3425 | 22.4764 | 27.68 | 31.6513 | 35.5824
| WoodstockIce Accretion2070RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2070 | 17.5353 | 21.6049 | 26.71 | 30.6117 | 34.461
| WoodstockIce Accretion2075RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2075 | 17.1596 | 21.1982 | 26.27 | 30.1371 | 33.957
| WoodstockIce Accretion2080RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2080 | 16.7838 | 20.7915 | 25.83 | 29.6625 | 33.453
| WoodstockIce Accretion2085RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2085 | 15.8549 | 19.7208 | 24.57 | 28.2387 | 31.9032
| WoodstockIce Accretion2090RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2090 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
| WoodstockIce Accretion2095RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2095 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
| WoodstockIce Accretion2100RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2100 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
| WoodstockWind2023RCP4.5 | Woodstock | Wind | RCP4.5 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
| WoodstockWind2025RCP4.5 | Woodstock | Wind | RCP4.5 | 2025 | 87.206 | 94.102 | 101.4083 | 108.6746 | 115.9494
| WoodstockWind2030RCP4.5 | Woodstock | Wind | RCP4.5 | 2030 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
| WoodstockWind2035RCP4.5 | Woodstock | Wind | RCP4.5 | 2035 | 87.3672 | 94.316 | 101.685 | 109.0063 | 116.337
| WoodstockWind2040RCP4.5 | Woodstock | Wind | RCP4.5 | 2040 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
| WoodstockWind2045RCP4.5 | Woodstock | Wind | RCP4.5 | 2045 | 87.5283 | 94.5299 | 101.9617 | 109.338 | 116.7246
| WoodstockWind2050RCP4.5 | Woodstock | Wind | RCP4.5 | 2050 | 87.678 | 94.7205 | 102.206 | 109.6258 | 117.0575
| WoodstockWind2055RCP4.5 | Woodstock | Wind | RCP4.5 | 2055 | 87.7471 | 94.8042 | 102.312 | 109.7478 | 117.1966
| WoodstockWind2060RCP4.5 | Woodstock | Wind | RCP4.5 | 2060 | 87.8162 | 94.8879 | 102.418 | 109.8697 | 117.3356
| WoodstockWind2065RCP4.5 | Woodstock | Wind | RCP4.5 | 2065 | 87.8852 | 94.9716 | 102.524 | 109.9917 | 117.4747
| WoodstockWind2070RCP4.5 | Woodstock | Wind | RCP4.5 | 2070 | 87.9543 | 95.0553 | 102.63 | 110.1137 | 117.6138
| WoodstockWind2075RCP4.5 | Woodstock | Wind | RCP4.5 | 2075 | 88.0407 | 95.1746 | 102.7917 | 110.3117 | 117.8494
| WoodstockWind2080RCP4.5 | Woodstock | Wind | RCP4.5 | 2080 | 88.127 | 95.294 | 102.9533 | 110.5096 | 118.085
| WoodstockWind2085RCP4.5 | Woodstock | Wind | RCP4.5 | 2085 | 88.2134 | 95.4134 | 103.115 | 110.7075 | 118.3206
| WoodstockWind2090RCP4.5 | Woodstock | Wind | RCP4.5 | 2090 | 88.2997 | 95.5327 | 103.2767 | 110.9055 | 118.5562
| WoodstockWind2095RCP4.5 | Woodstock | Wind | RCP4.5 | 2095 | 88.3861 | 95.6521 | 103.4383 | 111.1034 | 118.7918
| WoodstockWind2100RCP4.5 | Woodstock | Wind | RCP4.5 | 2100 | 88.4724 | 95.7714 | 103.6 | 111.3014 | 119.0274
| WoodstockWind2023RCP6.0 | Woodstock | Wind | RCP6.0 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
| WoodstockWind2025RCP6.0 | Woodstock | Wind | RCP6.0 | 2025 | 87.206 | 94.102 | 101.4083 | 108.6746 | 115.9494
| WoodstockWind2030RCP6.0 | Woodstock | Wind | RCP6.0 | 2030 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
| WoodstockWind2035RCP6.0 | Woodstock | Wind | RCP6.0 | 2035 | 87.3672 | 94.316 | 101.685 | 109.0063 | 116.337
| WoodstockWind2040RCP6.0 | Woodstock | Wind | RCP6.0 | 2040 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
| WoodstockWind2045RCP6.0 | Woodstock | Wind | RCP6.0 | 2045 | 87.5283 | 94.5299 | 101.9617 | 109.338 | 116.7246
| WoodstockWind2050RCP6.0 | Woodstock | Wind | RCP6.0 | 2050 | 87.678 | 94.7205 | 102.206 | 109.6258 | 117.0575
| WoodstockWind2055RCP6.0 | Woodstock | Wind | RCP6.0 | 2055 | 87.7471 | 94.8042 | 102.312 | 109.7478 | 117.1966
| WoodstockWind2060RCP6.0 | Woodstock | Wind | RCP6.0 | 2060 | 87.8162 | 94.8879 | 102.418 | 109.8697 | 117.3356
| WoodstockWind2065RCP6.0 | Woodstock | Wind | RCP6.0 | 2065 | 87.8852 | 94.9716 | 102.524 | 109.9917 | 117.4747
| WoodstockWind2070RCP6.0 | Woodstock | Wind | RCP6.0 | 2070 | 87.9543 | 95.0553 | 102.63 | 110.1137 | 117.6138
| WoodstockWind2075RCP6.0 | Woodstock | Wind | RCP6.0 | 2075 | 88.0838 | 95.2343 | 102.8725 | 110.4106 | 117.9672
| WoodstockWind2080RCP6.0 | Woodstock | Wind | RCP6.0 | 2080 | 88.2134 | 95.4134 | 103.115 | 110.7075 | 118.3206
| WoodstockWind2085RCP6.0 | Woodstock | Wind | RCP6.0 | 2085 | 88.3429 | 95.5924 | 103.3575 | 111.0045 | 118.674
| WoodstockWind2090RCP6.0 | Woodstock | Wind | RCP6.0 | 2090 | 88.8264 | 96.2271 | 104.18 | 111.9862 | 119.8216
| WoodstockWind2095RCP6.0 | Woodstock | Wind | RCP6.0 | 2095 | 89.1805 | 96.6828 | 104.76 | 112.671 | 120.6158
| WoodstockWind2100RCP6.0 | Woodstock | Wind | RCP6.0 | 2100 | 89.5345 | 97.1385 | 105.34 | 113.3558 | 121.41
| WoodstockWind2023RCP8.5 | Woodstock | Wind | RCP8.5 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
| WoodstockWind2025RCP8.5 | Woodstock | Wind | RCP8.5 | 2025 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
| WoodstockWind2030RCP8.5 | Woodstock | Wind | RCP8.5 | 2030 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
| WoodstockWind2035RCP8.5 | Woodstock | Wind | RCP8.5 | 2035 | 87.6089 | 94.6368 | 102.1 | 109.5038 | 116.9184
| WoodstockWind2040RCP8.5 | Woodstock | Wind | RCP8.5 | 2040 | 87.7241 | 94.7763 | 102.2767 | 109.7071 | 117.1502
| WoodstockWind2045RCP8.5 | Woodstock | Wind | RCP8.5 | 2045 | 87.8392 | 94.9158 | 102.4533 | 109.9104 | 117.382
| WoodstockWind2050RCP8.5 | Woodstock | Wind | RCP8.5 | 2050 | 88.127 | 95.294 | 102.9533 | 110.5096 | 118.085
| WoodstockWind2055RCP8.5 | Woodstock | Wind | RCP8.5 | 2055 | 88.2997 | 95.5327 | 103.2767 | 110.9055 | 118.5562
| WoodstockWind2060RCP8.5 | Woodstock | Wind | RCP8.5 | 2060 | 88.8264 | 96.2271 | 104.18 | 111.9862 | 119.8216
| WoodstockWind2065RCP8.5 | Woodstock | Wind | RCP8.5 | 2065 | 89.1805 | 96.6828 | 104.76 | 112.671 | 120.6158
| WoodstockWind2070RCP8.5 | Woodstock | Wind | RCP8.5 | 2070 | 89.759 | 97.4392 | 105.7367 | 113.8337 | 121.9724
| WoodstockWind2075RCP8.5 | Woodstock | Wind | RCP8.5 | 2075 | 89.9835 | 97.7399 | 106.1333 | 114.3117 | 122.5348
| WoodstockWind2080RCP8.5 | Woodstock | Wind | RCP8.5 | 2080 | 90.208 | 98.0406 | 106.53 | 114.7896 | 123.0972
| WoodstockWind2085RCP8.5 | Woodstock | Wind | RCP8.5 | 2085 | 90.6484 | 98.6172 | 107.285 | 115.6937 | 124.1517
| WoodstockWind2090RCP8.5 | Woodstock | Wind | RCP8.5 | 2090 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
| WoodstockWind2095RCP8.5 | Woodstock | Wind | RCP8.5 | 2095 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
| WoodstockWind2100RCP8.5 | Woodstock | Wind | RCP8.5 | 2100 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
| WyomingIce Accretion2023RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2023 | 15.4123 | 18.4982 | 22.402 | 25.3662 | 28.3424
| WyomingIce Accretion2025RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2025 | 15.3509 | 18.4378 | 22.3407 | 25.3056 | 28.2797
| WyomingIce Accretion2030RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2030 | 15.2896 | 18.3773 | 22.2793 | 25.245 | 28.2169
| WyomingIce Accretion2035RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2035 | 15.2282 | 18.3169 | 22.218 | 25.1843 | 28.1541
| WyomingIce Accretion2040RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2040 | 15.1669 | 18.2564 | 22.1567 | 25.1237 | 28.0913
| WyomingIce Accretion2045RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2045 | 15.1055 | 18.196 | 22.0953 | 25.063 | 28.0285
| WyomingIce Accretion2050RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2050 | 14.7625 | 17.8224 | 21.6752 | 24.6125 | 27.5426
| WyomingIce Accretion2055RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2055 | 14.4808 | 17.5093 | 21.3164 | 24.2227 | 27.1195
| WyomingIce Accretion2060RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2060 | 14.1992 | 17.1963 | 20.9576 | 23.8328 | 26.6964
| WyomingIce Accretion2065RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2065 | 13.9175 | 16.8832 | 20.5988 | 23.443 | 26.2733
| WyomingIce Accretion2070RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2070 | 13.6358 | 16.5701 | 20.24 | 23.0531 | 25.8502
| WyomingIce Accretion2075RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2075 | 13.5078 | 16.4365 | 20.102 | 22.9059 | 25.6956
| WyomingIce Accretion2080RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2080 | 13.3797 | 16.3029 | 19.964 | 22.7586 | 25.541
| WyomingIce Accretion2085RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2085 | 13.2517 | 16.1692 | 19.826 | 22.6113 | 25.3865
| WyomingIce Accretion2090RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2090 | 13.1237 | 16.0356 | 19.688 | 22.464 | 25.2319
| WyomingIce Accretion2095RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2095 | 12.9956 | 15.902 | 19.55 | 22.3167 | 25.0774
| WyomingIce Accretion2100RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2100 | 12.8676 | 15.7683 | 19.412 | 22.1695 | 24.9228
| WyomingIce Accretion2023RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2023 | 15.4123 | 18.4982 | 22.402 | 25.3662 | 28.3424
| WyomingIce Accretion2025RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2025 | 15.3509 | 18.4378 | 22.3407 | 25.3056 | 28.2797
| WyomingIce Accretion2030RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2030 | 15.2896 | 18.3773 | 22.2793 | 25.245 | 28.2169
| WyomingIce Accretion2035RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2035 | 15.2282 | 18.3169 | 22.218 | 25.1843 | 28.1541
| WyomingIce Accretion2040RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2040 | 15.1669 | 18.2564 | 22.1567 | 25.1237 | 28.0913
| WyomingIce Accretion2045RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2045 | 15.1055 | 18.196 | 22.0953 | 25.063 | 28.0285
| WyomingIce Accretion2050RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2050 | 14.7625 | 17.8224 | 21.6752 | 24.6125 | 27.5426
| WyomingIce Accretion2055RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2055 | 14.4808 | 17.5093 | 21.3164 | 24.2227 | 27.1195
| WyomingIce Accretion2060RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2060 | 14.1992 | 17.1963 | 20.9576 | 23.8328 | 26.6964
| WyomingIce Accretion2065RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2065 | 13.9175 | 16.8832 | 20.5988 | 23.443 | 26.2733
| WyomingIce Accretion2070RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2070 | 13.6358 | 16.5701 | 20.24 | 23.0531 | 25.8502
| WyomingIce Accretion2075RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2075 | 13.4437 | 16.3697 | 20.033 | 22.8322 | 25.6183
| WyomingIce Accretion2080RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2080 | 13.2517 | 16.1692 | 19.826 | 22.6113 | 25.3865
| WyomingIce Accretion2085RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2085 | 13.0596 | 15.9688 | 19.619 | 22.3904 | 25.1546
| WyomingIce Accretion2090RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2090 | 12.4781 | 15.3293 | 18.906 | 21.6064 | 24.3046
| WyomingIce Accretion2095RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2095 | 12.0887 | 14.8902 | 18.4 | 21.0432 | 23.6863
| WyomingIce Accretion2100RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2100 | 11.6993 | 14.4511 | 17.894 | 20.4801 | 23.0681
| WyomingIce Accretion2023RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2023 | 15.4123 | 18.4982 | 22.402 | 25.3662 | 28.3424
| WyomingIce Accretion2025RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2025 | 15.2896 | 18.3773 | 22.2793 | 25.245 | 28.2169
| WyomingIce Accretion2030RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2030 | 15.1669 | 18.2564 | 22.1567 | 25.1237 | 28.0913
| WyomingIce Accretion2035RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2035 | 15.0442 | 18.1355 | 22.034 | 25.0024 | 27.9657
| WyomingIce Accretion2040RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2040 | 14.5747 | 17.6137 | 21.436 | 24.3526 | 27.2605
| WyomingIce Accretion2045RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2045 | 14.1053 | 17.0919 | 20.838 | 23.7029 | 26.5553
| WyomingIce Accretion2050RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2050 | 13.3797 | 16.3029 | 19.964 | 22.7586 | 25.541
| WyomingIce Accretion2055RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2055 | 13.1237 | 16.0356 | 19.688 | 22.464 | 25.2319
| WyomingIce Accretion2060RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2060 | 12.4781 | 15.3293 | 18.906 | 21.6064 | 24.3046
| WyomingIce Accretion2065RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2065 | 12.0887 | 14.8902 | 18.4 | 21.0432 | 23.6863
| WyomingIce Accretion2070RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2070 | 11.3952 | 14.1202 | 17.5183 | 20.0816 | 22.6334
| WyomingIce Accretion2075RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2075 | 11.0911 | 13.7893 | 17.1427 | 19.6831 | 22.1987
| WyomingIce Accretion2080RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2080 | 10.787 | 13.4585 | 16.767 | 19.2846 | 21.764
| WyomingIce Accretion2085RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2085 | 10.0508 | 12.5803 | 15.7205 | 18.089 | 20.4454
| WyomingIce Accretion2090RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2090 | 9.3146 | 11.7022 | 14.674 | 16.8935 | 19.1268
| WyomingIce Accretion2095RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2095 | 9.3146 | 11.7022 | 14.674 | 16.8935 | 19.1268
| WyomingIce Accretion2100RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2100 | 9.3146 | 11.7022 | 14.674 | 16.8935 | 19.1268
| WyomingWind2023RCP4.5 | Wyoming | Wind | RCP4.5 | 2023 | 84.3776 | 90.9227 | 97.8245 | 104.7137 | 111.6084
| WyomingWind2025RCP4.5 | Wyoming | Wind | RCP4.5 | 2025 | 84.4334 | 90.9993 | 97.9263 | 104.8365 | 111.7521
| WyomingWind2030RCP4.5 | Wyoming | Wind | RCP4.5 | 2030 | 84.4893 | 91.076 | 98.0282 | 104.9594 | 111.8959
| WyomingWind2035RCP4.5 | Wyoming | Wind | RCP4.5 | 2035 | 84.5451 | 91.1527 | 98.13 | 105.0822 | 112.0397
| WyomingWind2040RCP4.5 | Wyoming | Wind | RCP4.5 | 2040 | 84.601 | 91.2294 | 98.2319 | 105.205 | 112.1834
| WyomingWind2045RCP4.5 | Wyoming | Wind | RCP4.5 | 2045 | 84.6568 | 91.3061 | 98.3337 | 105.3278 | 112.3272
| WyomingWind2050RCP4.5 | Wyoming | Wind | RCP4.5 | 2050 | 84.7143 | 91.3881 | 98.4453 | 105.4652 | 112.4908
| WyomingWind2055RCP4.5 | Wyoming | Wind | RCP4.5 | 2055 | 84.716 | 91.3936 | 98.455 | 105.4797 | 112.5107
| WyomingWind2060RCP4.5 | Wyoming | Wind | RCP4.5 | 2060 | 84.7177 | 91.399 | 98.4647 | 105.4942 | 112.5306
| WyomingWind2065RCP4.5 | Wyoming | Wind | RCP4.5 | 2065 | 84.7193 | 91.4044 | 98.4744 | 105.5088 | 112.5505
| WyomingWind2070RCP4.5 | Wyoming | Wind | RCP4.5 | 2070 | 84.721 | 91.4098 | 98.4841 | 105.5233 | 112.5704
| WyomingWind2075RCP4.5 | Wyoming | Wind | RCP4.5 | 2075 | 84.8662 | 91.5977 | 98.7282 | 105.8139 | 112.9096
| WyomingWind2080RCP4.5 | Wyoming | Wind | RCP4.5 | 2080 | 85.0114 | 91.7857 | 98.9723 | 106.1045 | 113.2487
| WyomingWind2085RCP4.5 | Wyoming | Wind | RCP4.5 | 2085 | 85.1566 | 91.9736 | 99.2165 | 106.3951 | 113.5878
| WyomingWind2090RCP4.5 | Wyoming | Wind | RCP4.5 | 2090 | 85.3017 | 92.1615 | 99.4606 | 106.6857 | 113.9269
| WyomingWind2095RCP4.5 | Wyoming | Wind | RCP4.5 | 2095 | 85.4469 | 92.3495 | 99.7047 | 106.9764 | 114.266
| WyomingWind2100RCP4.5 | Wyoming | Wind | RCP4.5 | 2100 | 85.5921 | 92.5374 | 99.9488 | 107.267 | 114.6051
| WyomingWind2023RCP6.0 | Wyoming | Wind | RCP6.0 | 2023 | 84.3776 | 90.9227 | 97.8245 | 104.7137 | 111.6084
| WyomingWind2025RCP6.0 | Wyoming | Wind | RCP6.0 | 2025 | 84.4334 | 90.9993 | 97.9263 | 104.8365 | 111.7521
| WyomingWind2030RCP6.0 | Wyoming | Wind | RCP6.0 | 2030 | 84.4893 | 91.076 | 98.0282 | 104.9594 | 111.8959
| WyomingWind2035RCP6.0 | Wyoming | Wind | RCP6.0 | 2035 | 84.5451 | 91.1527 | 98.13 | 105.0822 | 112.0397
| WyomingWind2040RCP6.0 | Wyoming | Wind | RCP6.0 | 2040 | 84.601 | 91.2294 | 98.2319 | 105.205 | 112.1834
| WyomingWind2045RCP6.0 | Wyoming | Wind | RCP6.0 | 2045 | 84.6568 | 91.3061 | 98.3337 | 105.3278 | 112.3272
| WyomingWind2050RCP6.0 | Wyoming | Wind | RCP6.0 | 2050 | 84.7143 | 91.3881 | 98.4453 | 105.4652 | 112.4908
| WyomingWind2055RCP6.0 | Wyoming | Wind | RCP6.0 | 2055 | 84.716 | 91.3936 | 98.455 | 105.4797 | 112.5107
| WyomingWind2060RCP6.0 | Wyoming | Wind | RCP6.0 | 2060 | 84.7177 | 91.399 | 98.4647 | 105.4942 | 112.5306
| WyomingWind2065RCP6.0 | Wyoming | Wind | RCP6.0 | 2065 | 84.7193 | 91.4044 | 98.4744 | 105.5088 | 112.5505
| WyomingWind2070RCP6.0 | Wyoming | Wind | RCP6.0 | 2070 | 84.721 | 91.4098 | 98.4841 | 105.5233 | 112.5704
| WyomingWind2075RCP6.0 | Wyoming | Wind | RCP6.0 | 2075 | 84.9388 | 91.6917 | 98.8503 | 105.9592 | 113.0791
| WyomingWind2080RCP6.0 | Wyoming | Wind | RCP6.0 | 2080 | 85.1566 | 91.9736 | 99.2165 | 106.3951 | 113.5878
| WyomingWind2085RCP6.0 | Wyoming | Wind | RCP6.0 | 2085 | 85.3743 | 92.2555 | 99.5826 | 106.831 | 114.0964
| WyomingWind2090RCP6.0 | Wyoming | Wind | RCP6.0 | 2090 | 85.955 | 92.9855 | 100.4985 | 107.907 | 115.3349
| WyomingWind2095RCP6.0 | Wyoming | Wind | RCP6.0 | 2095 | 86.318 | 93.4335 | 101.0481 | 108.547 | 116.0648
| WyomingWind2100RCP6.0 | Wyoming | Wind | RCP6.0 | 2100 | 86.6809 | 93.8815 | 101.5978 | 109.1871 | 116.7946
| WyomingWind2023RCP8.5 | Wyoming | Wind | RCP8.5 | 2023 | 84.3776 | 90.9227 | 97.8245 | 104.7137 | 111.6084
| WyomingWind2025RCP8.5 | Wyoming | Wind | RCP8.5 | 2025 | 84.4893 | 91.076 | 98.0282 | 104.9594 | 111.8959
| WyomingWind2030RCP8.5 | Wyoming | Wind | RCP8.5 | 2030 | 84.601 | 91.2294 | 98.2319 | 105.205 | 112.1834
| WyomingWind2035RCP8.5 | Wyoming | Wind | RCP8.5 | 2035 | 84.7126 | 91.3827 | 98.4356 | 105.4506 | 112.4709
| WyomingWind2040RCP8.5 | Wyoming | Wind | RCP8.5 | 2040 | 84.7154 | 91.3918 | 98.4518 | 105.4749 | 112.5041
| WyomingWind2045RCP8.5 | Wyoming | Wind | RCP8.5 | 2045 | 84.7182 | 91.4008 | 98.4679 | 105.4991 | 112.5373
| WyomingWind2050RCP8.5 | Wyoming | Wind | RCP8.5 | 2050 | 85.0114 | 91.7857 | 98.9723 | 106.1045 | 113.2487
| WyomingWind2055RCP8.5 | Wyoming | Wind | RCP8.5 | 2055 | 85.3017 | 92.1615 | 99.4606 | 106.6857 | 113.9269
| WyomingWind2060RCP8.5 | Wyoming | Wind | RCP8.5 | 2060 | 85.955 | 92.9855 | 100.4985 | 107.907 | 115.3349
| WyomingWind2065RCP8.5 | Wyoming | Wind | RCP8.5 | 2065 | 86.318 | 93.4335 | 101.0481 | 108.547 | 116.0648
| WyomingWind2070RCP8.5 | Wyoming | Wind | RCP8.5 | 2070 | 86.9853 | 94.2664 | 102.086 | 109.7614 | 117.4581
| WyomingWind2075RCP8.5 | Wyoming | Wind | RCP8.5 | 2075 | 87.2896 | 94.6513 | 102.5743 | 110.3357 | 118.1216
| WyomingWind2080RCP8.5 | Wyoming | Wind | RCP8.5 | 2080 | 87.5939 | 95.0362 | 103.0625 | 110.91 | 118.785
| WyomingWind2085RCP8.5 | Wyoming | Wind | RCP8.5 | 2085 | 87.9331 | 95.4647 | 103.596 | 111.5327 | 119.5038
| WyomingWind2090RCP8.5 | Wyoming | Wind | RCP8.5 | 2090 | 88.2723 | 95.8932 | 104.1295 | 112.1555 | 120.2226
| WyomingWind2095RCP8.5 | Wyoming | Wind | RCP8.5 | 2095 | 88.2723 | 95.8932 | 104.1295 | 112.1555 | 120.2226
| WyomingWind2100RCP8.5 | Wyoming | Wind | RCP8.5 | 2100 | 88.2723 | 95.8932 | 104.1295 | 112.1555 | 120.2226
TBD
Climate inputs developed through the use of ECCC and CSA data. Use of this climate data is optional and links to to tab '3. Climate Severity Calculator'.

## Int VA Calcs
DRAFT - Example Data Illustrative
Risk Heatmap
|  | Location | Thedford
[7 empty] | Annual Event Probability Forecast | [19 empty] | Total Annual Probability Across Perils
|  | Asset Class | Sub Class | Climate Peril | Severity Threshold | 2023 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2055 | 2060 | 2065 | 2070 | 2075 | 2080 | 2085 | 2090 | 2095 | 2100 |  | Asset Class | Sub Class | 2023 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2055 | 2060 | 2065 | 2070 | 2075 | 2080 | 2085 | 2090 | 2095 | 2100 | Unique Asset List | Class List | Sub Class List
ThedfordPoleClass 5 | ThedfordWind80 | Pole | Class 5 | Wind | 80 | 0.11607 | 0.1166 | 0.11712 | 0.11765 | 0.11782 | 0.11798 | 0.11876 | 0.11937 | 0.12087 | 0.12176 | 0.12344 | 0.12423 | 0.12502 | 0.12606 | 0.1271 | 0.1271 | 0.1271 | ThedfordPoleClass 5 | Pole | Class 5 | 11.61% | 11.66% | 11.71% | 11.77% | 11.78% | 11.8% | 11.88% | 11.94% | 12.09% | 12.18% | 12.34% | 12.42% | 12.5% | 12.61% | 12.71% | 12.71% | 12.71% | Pole-Class 5 | Pole | Class 5
ThedfordPoleClass 4 | ThedfordWind85 | Pole | Class 4 | Wind | 85 | 0.10145 | 0.10194 | 0.10243 | 0.10292 | 0.10308 | 0.10323 | 0.10395 | 0.10452 | 0.10592 | 0.10675 | 0.10831 | 0.10905 | 0.10978 | 0.11075 | 0.11173 | 0.11173 | 0.11173 | ThedfordPoleClass 4 | Pole | Class 4 | 10.15% | 10.19% | 10.24% | 10.29% | 10.31% | 10.32% | 10.4% | 10.45% | 10.59% | 10.67% | 10.83% | 10.9% | 10.98% | 11.08% | 11.17% | 11.17% | 11.17% | Pole-Class 4 | Pole | Class 4
ThedfordPoleClass 3 | ThedfordWind100 | Pole | Class 3 | Wind | 100 | 0.018976 | 0.019562 | 0.020204 | 0.020995 | 0.021223 | 0.021452 | 0.02265 | 0.023636 | 0.02589 | 0.027176 | 0.029906 | 0.031338 | 0.032797 | 0.034672 | 0.036595 | 0.036595 | 0.036595 | ThedfordPoleClass 3 | Pole | Class 3 | 1.898% | 1.956% | 2.02% | 2.1% | 2.122% | 2.145% | 2.265% | 2.364% | 2.589% | 2.718% | 2.991% | 3.134% | 3.28% | 3.467% | 3.659% | 3.659% | 3.659% | Pole-Class 3 | Pole | Class 3
ThedfordPoleClass 2 | ThedfordWind110 | Pole | Class 2 | Wind | 110 | 0.0071709 | 0.0074565 | 0.007748 | 0.0080455 | 0.0081254 | 0.0082059 | 0.0086518 | 0.0090244 | 0.0098446 | 0.010298 | 0.011293 | 0.011835 | 0.012389 | 0.013092 | 0.013814 | 0.013814 | 0.013814 | ThedfordPoleClass 2 | Pole | Class 2 | 0.7171% | 0.7457% | 0.7748% | 0.8045% | 0.8125% | 0.8206% | 0.8652% | 0.9024% | 0.9845% | 1.03% | 1.129% | 1.183% | 1.239% | 1.309% | 1.381% | 1.381% | 1.381% | Pole-Class 2 | Pole | Class 2

## Revenue Requirement Calculation
GLOBAL ASSUMPTIONS |  |  | Baseline Customer Revenue Requirement Multiplier |  |  |  | Scenario Customer Revenue Requirement Multiplier
|  |  | Asset Lifetime | 40 |  | Customer PV of Revenue Requirement for a $1 Investment | Asset Lifetime | 40 |  | Customer PV of Revenue Requirement for a $1 Investment
Asset Capital Cost | 1 |  | Depreciation | 2.5% |  | 2.2599 | Depreciation | 2.5% |  | 2.2599
|  |  |  | Opening Book Value | Nominal Revenue Requirement by Year | Present Value of Revenue Requirement in Year 1 Constant Dollars |  | Opening Book Value | Nominal Revenue Requirement by Year | Present Value of Revenue Requirement in Year 1 Constant Dollars
|  |  | Year |  |  |  | Year
Per IESO Guide for NWAs |  |  | 1 | 1 | 0.125 | 0.125 | 1 | 1 | 0.125 | 0.125
IESO_NWA_Guide_Regional_Planning |  |  | 2 | 0.975 | 0.10855 | 0.10642 | 2 | 0.975 | 0.10855 | 0.10642
Inflation Rate | 2% |  | 3 | 0.95 | 0.10651 | 0.10237 | 3 | 0.95 | 0.10651 | 0.10237
Social Discount Rate | 4% |  | 4 | 0.925 | 0.10475 | 0.098708 | 4 | 0.925 | 0.10475 | 0.098708
Pre-tax WACC | 7% |  | 5 | 0.9 | 0.103 | 0.095156 | 5 | 0.9 | 0.103 | 0.095156
|  |  | 6 | 0.875 | 0.10125 | 0.091705 | 6 | 0.875 | 0.10125 | 0.091705
|  |  | 7 | 0.85 | 0.0995 | 0.088353 | 7 | 0.85 | 0.0995 | 0.088353
OEB Cost of Capital Parameters |  |  | 8 | 0.825 | 0.09775 | 0.085097 | 8 | 0.825 | 0.09775 | 0.085097
|  |  | 9 | 0.8 | 0.096 | 0.081935 | 9 | 0.8 | 0.096 | 0.081935
Other Assumptions |  |  | 10 | 0.775 | 0.09425 | 0.078864 | 10 | 0.775 | 0.09425 | 0.078864
Tax Rate | 26.5% | 15% federal and 11.5% provincial | 11 | 0.75 | 0.0925 | 0.075882 | 11 | 0.75 | 0.0925 | 0.075882
Base OM&A Costs | 1.5% |  | 12 | 0.725 | 0.09075 | 0.072987 | 12 | 0.725 | 0.09075 | 0.072987
Scenario OM&A Costs | 1.5% |  | 13 | 0.7 | 0.089 | 0.070176 | 13 | 0.7 | 0.089 | 0.070176
|  |  | 14 | 0.675 | 0.08725 | 0.067447 | 14 | 0.675 | 0.08725 | 0.067447
Federal Tax Rate |  |  | 15 | 0.65 | 0.0855 | 0.064798 | 15 | 0.65 | 0.0855 | 0.064798
Provincial Tax Rate |  |  | 16 | 0.625 | 0.08375 | 0.062227 | 16 | 0.625 | 0.08375 | 0.062227
|  |  | 17 | 0.6 | 0.082 | 0.059733 | 17 | 0.6 | 0.082 | 0.059733
|  |  | 18 | 0.575 | 0.08025 | 0.057312 | 18 | 0.575 | 0.08025 | 0.057312
|  |  | 19 | 0.55 | 0.0785 | 0.054963 | 19 | 0.55 | 0.0785 | 0.054963
|  |  | 20 | 0.525 | 0.07675 | 0.052684 | 20 | 0.525 | 0.07675 | 0.052684
|  |  | 21 | 0.5 | 0.075 | 0.050473 | 21 | 0.5 | 0.075 | 0.050473
|  |  | 22 | 0.475 | 0.07325 | 0.048329 | 22 | 0.475 | 0.07325 | 0.048329
|  |  | 23 | 0.45 | 0.0715 | 0.046249 | 23 | 0.45 | 0.0715 | 0.046249
|  |  | 24 | 0.425 | 0.06975 | 0.044232 | 24 | 0.425 | 0.06975 | 0.044232
|  |  | 25 | 0.4 | 0.068 | 0.042277 | 25 | 0.4 | 0.068 | 0.042277
|  |  | 26 | 0.375 | 0.06625 | 0.040381 | 26 | 0.375 | 0.06625 | 0.040381
|  |  | 27 | 0.35 | 0.0645 | 0.038544 | 27 | 0.35 | 0.0645 | 0.038544
|  |  | 28 | 0.325 | 0.06275 | 0.036763 | 28 | 0.325 | 0.06275 | 0.036763
|  |  | 29 | 0.3 | 0.061 | 0.035037 | 29 | 0.3 | 0.061 | 0.035037
|  |  | 30 | 0.275 | 0.05925 | 0.033364 | 30 | 0.275 | 0.05925 | 0.033364
|  |  | 31 | 0.25 | 0.0575 | 0.031744 | 31 | 0.25 | 0.0575 | 0.031744
|  |  | 32 | 0.225 | 0.05575 | 0.030174 | 32 | 0.225 | 0.05575 | 0.030174
|  |  | 33 | 0.2 | 0.054 | 0.028654 | 33 | 0.2 | 0.054 | 0.028654
|  |  | 34 | 0.175 | 0.05225 | 0.027182 | 34 | 0.175 | 0.05225 | 0.027182
|  |  | 35 | 0.15 | 0.0505 | 0.025756 | 35 | 0.15 | 0.0505 | 0.025756
|  |  | 36 | 0.125 | 0.04875 | 0.024376 | 36 | 0.125 | 0.04875 | 0.024376
|  |  | 37 | 0.1 | 0.047 | 0.02304 | 37 | 0.1 | 0.047 | 0.02304
|  |  | 38 | 0.075 | 0.04525 | 0.021748 | 38 | 0.075 | 0.04525 | 0.021748
|  |  | 39 | 0.05 | 0.0435 | 0.020497 | 39 | 0.05 | 0.0435 | 0.020497
|  |  | 40 | 0.025 | 0.04175 | 0.019286 | 40 | 0.025 | 0.04175 | 0.019286
|  |  | 41 | 0 | 0 | 0 | 41 | 0 | 0 | 0
|  |  | 42 | 0 | 0 | 0 | 42 | 0 | 0 | 0
|  |  | 43 | 0 | 0 | 0 | 43 | 0 | 0 | 0
|  |  | 44 | 0 | 0 | 0 | 44 | 0 | 0 | 0
|  |  | 45 | 0 | 0 | 0 | 45 | 0 | 0 | 0
|  |  | 46 | 0 | 0 | 0 | 46 | 0 | 0 | 0
|  |  | 47 | 0 | 0 | 0 | 47 | 0 | 0 | 0
|  |  | 48 | 0 | 0 | 0 | 48 | 0 | 0 | 0
|  |  | 49 | 0 | 0 | 0 | 49 | 0 | 0 | 0
|  |  | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0
|  |  | 51 | 0 | 0 | 0 | 51 | 0 | 0 | 0
|  |  | 52 | 0 | 0 | 0 | 52 | 0 | 0 | 0
|  |  | 53 | 0 | 0 | 0 | 53 | 0 | 0 | 0
|  |  | 54 | 0 | 0 | 0 | 54 | 0 | 0 | 0
|  |  | 55 | 0 | 0 | 0 | 55 | 0 | 0 | 0
|  |  | 56 | 0 | 0 | 0 | 56 | 0 | 0 | 0
|  |  | 57 | 0 | 0 | 0 | 57 | 0 | 0 | 0
|  |  | 58 | 0 | 0 | 0 | 58 | 0 | 0 | 0
|  |  | 59 | 0 | 0 | 0 | 59 | 0 | 0 | 0
|  |  | 60 | 0 | 0 | 0 | 60 | 0 | 0 | 0
|  |  | 61 | 0 | 0 | 0 | 61 | 0 | 0 | 0
|  |  | 62 | 0 | 0 | 0 | 62 | 0 | 0 | 0
|  |  | 63 | 0 | 0 | 0 | 63 | 0 | 0 | 0
|  |  | 64 | 0 | 0 | 0 | 64 | 0 | 0 | 0
|  |  | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0
|  |  | 66 | 0 | 0 | 0 | 66 | 0 | 0 | 0
|  |  | 67 | 0 | 0 | 0 | 67 | 0 | 0 | 0
|  |  | 68 | 0 | 0 | 0 | 68 | 0 | 0 | 0
|  |  | 69 | 0 | 0 | 0 | 69 | 0 | 0 | 0
|  |  | 70 | 0 | 0 | 0 | 70 | 0 | 0 | 0
|  |  | 71 | 0 | 0 | 0 | 71 | 0 | 0 | 0
|  |  | 72 | 0 | 0 | 0 | 72 | 0 | 0 | 0
|  |  | 73 | 0 | 0 | 0 | 73 | 0 | 0 | 0
|  |  | 74 | 0 | 0 | 0 | 74 | 0 | 0 | 0
|  |  | 75 | 0 | 0 | 0 | 75 | 0 | 0 | 0
|  |  | 76 | 0 | 0 | 0 | 76 | 0 | 0 | 0
|  |  | 77 | 0 | 0 | 0 | 77 | 0 | 0 | 0
|  |  | 78 | 0 | 0 | 0 | 78 | 0 | 0 | 0
|  |  | 79 | 0 | 0 | 0 | 79 | 0 | 0 | 0
|  |  | 80 | 0 | 0 | 0 | 80 | 0 | 0 | 0
|  |  | 81 | 0 | 0 | 0 | 81 | 0 | 0 | 0
|  |  | 82 | 0 | 0 | 0 | 82 | 0 | 0 | 0
|  |  | 83 | 0 | 0 | 0 | 83 | 0 | 0 | 0
|  |  | 84 | 0 | 0 | 0 | 84 | 0 | 0 | 0
|  |  | 85 | 0 | 0 | 0 | 85 | 0 | 0 | 0
|  |  | 86 | 0 | 0 | 0 | 86 | 0 | 0 | 0
|  |  | 87 | 0 | 0 | 0 | 87 | 0 | 0 | 0
|  |  | 88 | 0 | 0 | 0 | 88 | 0 | 0 | 0
|  |  | 89 | 0 | 0 | 0 | 89 | 0 | 0 | 0
|  |  | 90 | 0 | 0 | 0 | 90 | 0 | 0 | 0
|  |  | 91 | 0 | 0 | 0 | 91 | 0 | 0 | 0
|  |  | 92 | 0 | 0 | 0 | 92 | 0 | 0 | 0
|  |  | 93 | 0 | 0 | 0 | 93 | 0 | 0 | 0
|  |  | 94 | 0 | 0 | 0 | 94 | 0 | 0 | 0
|  |  | 95 | 0 | 0 | 0 | 95 | 0 | 0 | 0
|  |  | 96 | 0 | 0 | 0 | 96 | 0 | 0 | 0
|  |  | 97 | 0 | 0 | 0 | 97 | 0 | 0 | 0
|  |  | 98 | 0 | 0 | 0 | 98 | 0 | 0 | 0
|  |  | 99 | 0 | 0 | 0 | 99 | 0 | 0 | 0
|  |  | 100 | 0 | 0 | 0 | 100 | 0 | 0 | 0
|  |  | 101 |  |  |  | 101
Note on K111: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is included only to ensure that the indexing for the nominal payment (which captures the depreciation in each yar) works properly.
Note on P111: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is included only to ensure that the indexing for the nominal payment (which captures the depreciation in each yar) works properly.
Calculates the baseline and scenario utility cost to PV customer cost multiplier. This value is applied to utility investment spending to estimate the PV of lifetime customer rate impacts from the investment. The multiplier considers OM&A changes from the investment as well as tax, WACC, and project lifetime. This multiplier aligns the VASH BCA methodology with the DST to allow for consistent evaluation of customer benefits from resiliency investments.

## Int BCA Costs
Early Retirement Cost Adjustment
Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101
Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 4 | -1093804.6829 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | -60709.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
For early retirement projects, the BCA cost is adjusted to account for what would have occurred in the absence of the resiliency investment. The assumption is that the LDC would have replaced the existing assets with standard assets after the RUL period is over. This tab calculates the credit that should be applied to the full upfront cost of the replacement assets (in customer revenue requirement) to account for the avoided future investment at the end of the RUL period.

## Int BCA Ann Fail Prob
Asset Class Annual Probability of Failure Uncalibrated | [79 empty] | Asset Class Annual Probability of Failure Calibrated | [79 empty] | Total Existing Asset Class Annual Probability of Failure Calibrated | [79 empty] | Total Replacement Asset Class Annual Probability of Failure Calibrated | [79 empty] | Total Standard Asset Class Annual Probability of Failure Calibrated
Asset Class | Asset Sub-Class | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | Asset Class | Asset Sub-Class | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | Asset Class | Asset Sub-Class | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | Asset Class | Asset Sub-Class | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | Asset Class | Asset Sub-Class | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100
Pole | Class 5 | 0.11607 | 0.11633 | 0.1166 | 0.1167 | 0.11681 | 0.11691 | 0.11702 | 0.11712 | 0.11723 | 0.11733 | 0.11744 | 0.11755 | 0.11765 | 0.11768 | 0.11772 | 0.11775 | 0.11778 | 0.11782 | 0.11785 | 0.11788 | 0.11792 | 0.11795 | 0.11798 | 0.11814 | 0.11829 | 0.11845 | 0.1186 | 0.11876 | 0.11888 | 0.119 | 0.11912 | 0.11925 | 0.11937 | 0.11967 | 0.11997 | 0.12027 | 0.12057 | 0.12087 | 0.12105 | 0.12123 | 0.12141 | 0.12159 | 0.12176 | 0.1221 | 0.12244 | 0.12277 | 0.12311 | 0.12344 | 0.1236 | 0.12376 | 0.12391 | 0.12407 | 0.12423 | 0.12439 | 0.12454 | 0.1247 | 0.12486 | 0.12502 | 0.12522 | 0.12543 | 0.12564 | 0.12585 | 0.12606 | 0.12627 | 0.12648 | 0.12668 | 0.12689 | 0.1271 | 0.1271 | 0.1271 | 0.1271 | 0.1271 | 0.1271 | 0.1271 | 0.1271 | 0.1271 | 0.1271 | 0.1271 | Pole | Class 5 | 0.025049 | 0.025106 | 0.025163 | 0.025185 | 0.025208 | 0.025231 | 0.025254 | 0.025276 | 0.025299 | 0.025322 | 0.025345 | 0.025368 | 0.02539 | 0.025398 | 0.025405 | 0.025412 | 0.025419 | 0.025426 | 0.025433 | 0.02544 | 0.025447 | 0.025455 | 0.025462 | 0.025495 | 0.025529 | 0.025562 | 0.025596 | 0.025629 | 0.025655 | 0.025682 | 0.025708 | 0.025735 | 0.025761 | 0.025826 | 0.025891 | 0.025956 | 0.026021 | 0.026085 | 0.026124 | 0.026162 | 0.026201 | 0.02624 | 0.026278 | 0.026351 | 0.026423 | 0.026495 | 0.026568 | 0.02664 | 0.026674 | 0.026708 | 0.026742 | 0.026776 | 0.02681 | 0.026844 | 0.026878 | 0.026912 | 0.026946 | 0.02698 | 0.027025 | 0.02707 | 0.027115 | 0.02716 | 0.027205 | 0.02725 | 0.027295 | 0.02734 | 0.027385 | 0.02743 | 0.02743 | 0.02743 | 0.02743 | 0.02743 | 0.02743 | 0.02743 | 0.02743 | 0.02743 | 0.02743 | 0.02743 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 4 | 0.10145 | 0.1017 | 0.10194 | 0.10204 | 0.10214 | 0.10224 | 0.10233 | 0.10243 | 0.10253 | 0.10263 | 0.10273 | 0.10282 | 0.10292 | 0.10295 | 0.10298 | 0.10301 | 0.10304 | 0.10308 | 0.10311 | 0.10314 | 0.10317 | 0.1032 | 0.10323 | 0.10337 | 0.10352 | 0.10366 | 0.10381 | 0.10395 | 0.10406 | 0.10418 | 0.10429 | 0.10441 | 0.10452 | 0.1048 | 0.10508 | 0.10536 | 0.10564 | 0.10592 | 0.10608 | 0.10625 | 0.10642 | 0.10658 | 0.10675 | 0.10706 | 0.10738 | 0.10769 | 0.108 | 0.10831 | 0.10846 | 0.10861 | 0.10875 | 0.1089 | 0.10905 | 0.10919 | 0.10934 | 0.10949 | 0.10963 | 0.10978 | 0.10997 | 0.11017 | 0.11036 | 0.11056 | 0.11075 | 0.11095 | 0.11114 | 0.11134 | 0.11153 | 0.11173 | 0.11173 | 0.11173 | 0.11173 | 0.11173 | 0.11173 | 0.11173 | 0.11173 | 0.11173 | 0.11173 | 0.11173 | Pole | Class 4 | 0.021894 | 0.021947 | 0.022 | 0.022021 | 0.022042 | 0.022063 | 0.022085 | 0.022106 | 0.022127 | 0.022148 | 0.022169 | 0.022191 | 0.022212 | 0.022218 | 0.022225 | 0.022232 | 0.022238 | 0.022245 | 0.022251 | 0.022258 | 0.022265 | 0.022271 | 0.022278 | 0.022309 | 0.02234 | 0.022371 | 0.022402 | 0.022434 | 0.022458 | 0.022483 | 0.022507 | 0.022532 | 0.022556 | 0.022617 | 0.022677 | 0.022737 | 0.022798 | 0.022858 | 0.022894 | 0.02293 | 0.022966 | 0.023002 | 0.023038 | 0.023105 | 0.023173 | 0.02324 | 0.023308 | 0.023375 | 0.023407 | 0.023439 | 0.02347 | 0.023502 | 0.023533 | 0.023565 | 0.023597 | 0.023628 | 0.02366 | 0.023692 | 0.023734 | 0.023776 | 0.023818 | 0.02386 | 0.023902 | 0.023944 | 0.023986 | 0.024028 | 0.02407 | 0.024112 | 0.024112 | 0.024112 | 0.024112 | 0.024112 | 0.024112 | 0.024112 | 0.024112 | 0.024112 | 0.024112 | 0.024112 | Pole | Class 4 | 2.1894 | 2.1947 | 2.2 | 2.2021 | 2.2042 | 2.2063 | 2.2085 | 2.2106 | 2.2127 | 2.2148 | 2.2169 | 2.2191 | 2.2212 | 2.2218 | 2.2225 | 2.2232 | 2.2238 | 2.2245 | 2.2251 | 2.2258 | 2.2265 | 2.2271 | 2.2278 | 2.2309 | 2.234 | 2.2371 | 2.2402 | 2.2434 | 2.2458 | 2.2483 | 2.2507 | 2.2532 | 2.2556 | 2.2617 | 2.2677 | 2.2737 | 2.2798 | 2.2858 | 2.2894 | 2.293 | 2.2966 | 2.3002 | 2.3038 | 2.3105 | 2.3173 | 2.324 | 2.3308 | 2.3375 | 2.3407 | 2.3439 | 2.347 | 2.3502 | 2.3533 | 2.3565 | 2.3597 | 2.3628 | 2.366 | 2.3692 | 2.3734 | 2.3776 | 2.3818 | 2.386 | 2.3902 | 2.3944 | 2.3986 | 2.4028 | 2.407 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 3 | 0.018976 | 0.019269 | 0.019562 | 0.01969 | 0.019819 | 0.019947 | 0.020075 | 0.020204 | 0.020362 | 0.02052 | 0.020679 | 0.020837 | 0.020995 | 0.021041 | 0.021086 | 0.021132 | 0.021177 | 0.021223 | 0.021269 | 0.021315 | 0.021361 | 0.021406 | 0.021452 | 0.021692 | 0.021931 | 0.022171 | 0.02241 | 0.02265 | 0.022847 | 0.023044 | 0.023242 | 0.023439 | 0.023636 | 0.024087 | 0.024538 | 0.024988 | 0.025439 | 0.02589 | 0.026147 | 0.026404 | 0.026662 | 0.026919 | 0.027176 | 0.027722 | 0.028268 | 0.028814 | 0.02936 | 0.029906 | 0.030193 | 0.030479 | 0.030765 | 0.031052 | 0.031338 | 0.03163 | 0.031922 | 0.032213 | 0.032505 | 0.032797 | 0.033172 | 0.033547 | 0.033922 | 0.034297 | 0.034672 | 0.035056 | 0.035441 | 0.035826 | 0.03621 | 0.036595 | 0.036595 | 0.036595 | 0.036595 | 0.036595 | 0.036595 | 0.036595 | 0.036595 | 0.036595 | 0.036595 | 0.036595 | Pole | Class 3 | 0.0040952 | 0.0041585 | 0.0042217 | 0.0042494 | 0.0042771 | 0.0043048 | 0.0043325 | 0.0043602 | 0.0043943 | 0.0044285 | 0.0044626 | 0.0044968 | 0.0045309 | 0.0045408 | 0.0045506 | 0.0045605 | 0.0045703 | 0.0045801 | 0.00459 | 0.0045999 | 0.0046098 | 0.0046197 | 0.0046296 | 0.0046813 | 0.004733 | 0.0047847 | 0.0048364 | 0.0048881 | 0.0049306 | 0.0049732 | 0.0050158 | 0.0050584 | 0.005101 | 0.0051982 | 0.0052955 | 0.0053928 | 0.00549 | 0.0055873 | 0.0056428 | 0.0056983 | 0.0057539 | 0.0058094 | 0.0058649 | 0.0059827 | 0.0061006 | 0.0062184 | 0.0063362 | 0.0064541 | 0.0065159 | 0.0065777 | 0.0066395 | 0.0067013 | 0.0067631 | 0.0068261 | 0.006889 | 0.006952 | 0.007015 | 0.0070779 | 0.0071588 | 0.0072398 | 0.0073207 | 0.0074016 | 0.0074825 | 0.0075655 | 0.0076485 | 0.0077316 | 0.0078146 | 0.0078976 | 0.0078976 | 0.0078976 | 0.0078976 | 0.0078976 | 0.0078976 | 0.0078976 | 0.0078976 | 0.0078976 | 0.0078976 | 0.0078976 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0.40952 | 0.41585 | 0.42217 | 0.42494 | 0.42771 | 0.43048 | 0.43325 | 0.43602 | 0.43943 | 0.44285 | 0.44626 | 0.44968 | 0.45309 | 0.45408 | 0.45506 | 0.45605 | 0.45703 | 0.45801 | 0.459 | 0.45999 | 0.46098 | 0.46197 | 0.46296 | 0.46813 | 0.4733 | 0.47847 | 0.48364 | 0.48881 | 0.49306 | 0.49732 | 0.50158 | 0.50584 | 0.5101 | 0.51982 | 0.52955 | 0.53928 | 0.549 | 0.55873 | 0.56428 | 0.56983 | 0.57539 | 0.58094 | 0.58649 | 0.59827 | 0.61006 | 0.62184 | 0.63362 | 0.64541 | 0.65159 | 0.65777 | 0.66395 | 0.67013 | 0.67631 | 0.68261 | 0.6889 | 0.6952 | 0.7015 | 0.70779 | 0.71588 | 0.72398 | 0.73207 | 0.74016 | 0.74825 | 0.75655 | 0.76485 | 0.77316 | 0.78146 | 0.78976 | 0.78976 | 0.78976 | 0.78976 | 0.78976 | 0.78976 | 0.78976 | 0.78976 | 0.78976 | 0.78976 | 0.78976
Pole | Class 2 | 0.0071709 | 0.0073137 | 0.0074565 | 0.0075148 | 0.0075731 | 0.0076314 | 0.0076897 | 0.007748 | 0.0078075 | 0.007867 | 0.0079265 | 0.007986 | 0.0080455 | 0.0080615 | 0.0080774 | 0.0080934 | 0.0081094 | 0.0081254 | 0.0081415 | 0.0081576 | 0.0081737 | 0.0081898 | 0.0082059 | 0.0082951 | 0.0083843 | 0.0084735 | 0.0085627 | 0.0086518 | 0.0087264 | 0.0088009 | 0.0088754 | 0.0089499 | 0.0090244 | 0.0091885 | 0.0093525 | 0.0095165 | 0.0096806 | 0.0098446 | 0.0099353 | 0.010026 | 0.010117 | 0.010208 | 0.010298 | 0.010497 | 0.010696 | 0.010895 | 0.011094 | 0.011293 | 0.011402 | 0.01151 | 0.011618 | 0.011726 | 0.011835 | 0.011945 | 0.012056 | 0.012167 | 0.012278 | 0.012389 | 0.01253 | 0.01267 | 0.012811 | 0.012951 | 0.013092 | 0.013236 | 0.013381 | 0.013525 | 0.01367 | 0.013814 | 0.013814 | 0.013814 | 0.013814 | 0.013814 | 0.013814 | 0.013814 | 0.013814 | 0.013814 | 0.013814 | 0.013814 | Pole | Class 2 | 0.0015476 | 0.0015784 | 0.0016092 | 0.0016218 | 0.0016344 | 0.0016469 | 0.0016595 | 0.0016721 | 0.0016849 | 0.0016978 | 0.0017106 | 0.0017235 | 0.0017363 | 0.0017397 | 0.0017432 | 0.0017466 | 0.0017501 | 0.0017535 | 0.001757 | 0.0017605 | 0.001764 | 0.0017674 | 0.0017709 | 0.0017902 | 0.0018094 | 0.0018287 | 0.0018479 | 0.0018672 | 0.0018832 | 0.0018993 | 0.0019154 | 0.0019315 | 0.0019476 | 0.001983 | 0.0020184 | 0.0020538 | 0.0020892 | 0.0021246 | 0.0021441 | 0.0021637 | 0.0021833 | 0.0022029 | 0.0022225 | 0.0022654 | 0.0023084 | 0.0023513 | 0.0023943 | 0.0024372 | 0.0024606 | 0.0024839 | 0.0025073 | 0.0025307 | 0.002554 | 0.002578 | 0.0026019 | 0.0026258 | 0.0026498 | 0.0026737 | 0.002704 | 0.0027343 | 0.0027647 | 0.002795 | 0.0028253 | 0.0028565 | 0.0028877 | 0.0029189 | 0.0029501 | 0.0029813 | 0.0029813 | 0.0029813 | 0.0029813 | 0.0029813 | 0.0029813 | 0.0029813 | 0.0029813 | 0.0029813 | 0.0029813 | 0.0029813 | Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 0.15476 | 0.15784 | 0.16092 | 0.16218 | 0.16344 | 0.16469 | 0.16595 | 0.16721 | 0.16849 | 0.16978 | 0.17106 | 0.17235 | 0.17363 | 0.17397 | 0.17432 | 0.17466 | 0.17501 | 0.17535 | 0.1757 | 0.17605 | 0.1764 | 0.17674 | 0.17709 | 0.17902 | 0.18094 | 0.18287 | 0.18479 | 0.18672 | 0.18832 | 0.18993 | 0.19154 | 0.19315 | 0.19476 | 0.1983 | 0.20184 | 0.20538 | 0.20892 | 0.21246 | 0.21441 | 0.21637 | 0.21833 | 0.22029 | 0.22225 | 0.22654 | 0.23084 | 0.23513 | 0.23943 | 0.24372 | 0.24606 | 0.24839 | 0.25073 | 0.25307 | 0.2554 | 0.2578 | 0.26019 | 0.26258 | 0.26498 | 0.26737 | 0.2704 | 0.27343 | 0.27647 | 0.2795 | 0.28253 | 0.28565 | 0.28877 | 0.29189 | 0.29501 | 0.29813 | 0.29813 | 0.29813 | 0.29813 | 0.29813 | 0.29813 | 0.29813 | 0.29813 | 0.29813 | 0.29813 | 0.29813 | Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Climate data given in 5-year increments in linearly interpolated to provide annual probability of failures at the asset sub-class level. These failure probabilities are calibrated using the calibration multiplier derived on the Calibration tab and then scaled to the asset counts by sub-class for the existing, standard, and replacement cases. These are used to scale VOLL benefits calibrated to annual expected outage counts.

## Int BCA Ann Fail Costs
Asset Class Annual Failure Repair and Replace Cost
Asset Class | Asset Sub-Class | Unit Basis | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100
Pole | Class 5 | pole | 2240.2922 | 2245.098 | 2250 | 2255 | 2260.1 | 2265.302 | 2270.608 | 2276.0202 | 2281.5406 | 2287.1714 | 2292.9148 | 2298.7731 | 2304.7486 | 2310.8436 | 2317.0604 | 2323.4017 | 2329.8697 | 2336.4671 | 2343.1964 | 2350.0604 | 2357.0616 | 2364.2028 | 2371.4868 | 2378.9166 | 2386.4949 | 2394.2248 | 2402.1093 | 2410.1515 | 2418.3545 | 2426.7216 | 2435.2561 | 2443.9612 | 2452.8404 | 2461.8972 | 2471.1351 | 2480.5579 | 2490.169 | 2499.9724 | 2509.9718 | 2520.1713 | 2530.5747 | 2541.1862 | 2552.0099 | 2563.0501 | 2574.3111 | 2585.7973 | 2597.5133 | 2609.4636 | 2621.6528 | 2634.0859 | 2646.7676 | 2659.7029 | 2672.897 | 2686.3549 | 2700.082 | 2714.0837 | 2728.3654 | 2742.9327 | 2757.7913 | 2772.9471 | 2788.4061 | 2804.1742 | 2820.2577 | 2836.6629 | 2853.3961 | 2870.464 | 2887.8733 | 2905.6308 | 2923.7434 | 2942.2183 | 2961.0626 | 2980.2839 | 2999.8896 | 3019.8873 | 3040.2851 | 3061.0908 | 3082.3126 | 3103.9589
Pole | Class 4 | pole | 2440.2922 | 2445.098 | 2450 | 2455 | 2460.1 | 2465.302 | 2470.608 | 2476.0202 | 2481.5406 | 2487.1714 | 2492.9148 | 2498.7731 | 2504.7486 | 2510.8436 | 2517.0604 | 2523.4017 | 2529.8697 | 2536.4671 | 2543.1964 | 2550.0604 | 2557.0616 | 2564.2028 | 2571.4868 | 2578.9166 | 2586.4949 | 2594.2248 | 2602.1093 | 2610.1515 | 2618.3545 | 2626.7216 | 2635.2561 | 2643.9612 | 2652.8404 | 2661.8972 | 2671.1351 | 2680.5579 | 2690.169 | 2699.9724 | 2709.9718 | 2720.1713 | 2730.5747 | 2741.1862 | 2752.0099 | 2763.0501 | 2774.3111 | 2785.7973 | 2797.5133 | 2809.4636 | 2821.6528 | 2834.0859 | 2846.7676 | 2859.7029 | 2872.897 | 2886.3549 | 2900.082 | 2914.0837 | 2928.3654 | 2942.9327 | 2957.7913 | 2972.9471 | 2988.4061 | 3004.1742 | 3020.2577 | 3036.6629 | 3053.3961 | 3070.464 | 3087.8733 | 3105.6308 | 3123.7434 | 3142.2183 | 3161.0626 | 3180.2839 | 3199.8896 | 3219.8873 | 3240.2851 | 3261.0908 | 3282.3126 | 3303.9589
Pole | Class 3 | pole | 2660.2922 | 2665.098 | 2670 | 2675 | 2680.1 | 2685.302 | 2690.608 | 2696.0202 | 2701.5406 | 2707.1714 | 2712.9148 | 2718.7731 | 2724.7486 | 2730.8436 | 2737.0604 | 2743.4017 | 2749.8697 | 2756.4671 | 2763.1964 | 2770.0604 | 2777.0616 | 2784.2028 | 2791.4868 | 2798.9166 | 2806.4949 | 2814.2248 | 2822.1093 | 2830.1515 | 2838.3545 | 2846.7216 | 2855.2561 | 2863.9612 | 2872.8404 | 2881.8972 | 2891.1351 | 2900.5579 | 2910.169 | 2919.9724 | 2929.9718 | 2940.1713 | 2950.5747 | 2961.1862 | 2972.0099 | 2983.0501 | 2994.3111 | 3005.7973 | 3017.5133 | 3029.4636 | 3041.6528 | 3054.0859 | 3066.7676 | 3079.7029 | 3092.897 | 3106.3549 | 3120.082 | 3134.0837 | 3148.3654 | 3162.9327 | 3177.7913 | 3192.9471 | 3208.4061 | 3224.1742 | 3240.2577 | 3256.6629 | 3273.3961 | 3290.464 | 3307.8733 | 3325.6308 | 3343.7434 | 3362.2183 | 3381.0626 | 3400.2839 | 3419.8896 | 3439.8873 | 3460.2851 | 3481.0908 | 3502.3126 | 3523.9589
Pole | Class 2 | pole | 2902.2922 | 2907.098 | 2912 | 2917 | 2922.1 | 2927.302 | 2932.608 | 2938.0202 | 2943.5406 | 2949.1714 | 2954.9148 | 2960.7731 | 2966.7486 | 2972.8436 | 2979.0604 | 2985.4017 | 2991.8697 | 2998.4671 | 3005.1964 | 3012.0604 | 3019.0616 | 3026.2028 | 3033.4868 | 3040.9166 | 3048.4949 | 3056.2248 | 3064.1093 | 3072.1515 | 3080.3545 | 3088.7216 | 3097.2561 | 3105.9612 | 3114.8404 | 3123.8972 | 3133.1351 | 3142.5579 | 3152.169 | 3161.9724 | 3171.9718 | 3182.1713 | 3192.5747 | 3203.1862 | 3214.0099 | 3225.0501 | 3236.3111 | 3247.7973 | 3259.5133 | 3271.4636 | 3283.6528 | 3296.0859 | 3308.7676 | 3321.7029 | 3334.897 | 3348.3549 | 3362.082 | 3376.0837 | 3390.3654 | 3404.9327 | 3419.7913 | 3434.9471 | 3450.4061 | 3466.1742 | 3482.2577 | 3498.6629 | 3515.3961 | 3532.464 | 3549.8733 | 3567.6308 | 3585.7434 | 3604.2183 | 3623.0626 | 3642.2839 | 3661.8896 | 3681.8873 | 3702.2851 | 3723.0908 | 3744.3126 | 3765.9589
Expected annual avoided asset damages cost are the weighted repair and replacement costs from tab '6. Generic BCA Inputs'. This tab calculates the per unit weighted value for a single failure.

## Int BCA Ann PWFC
Asset Class Annual Probability Weighted Failure Repair and Replace Cost | [78 empty] | Baseline Asset Class Annual Probability Weighted Failure Repair and Replace Cost | [78 empty] | Replacement Asset Class Annual Probability Weighted Failure Repair and Replace Cost
Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101
Pole | Class 5 | 3908.8427 | 263.1611 | 263.9949 | 264.8417 | 265.7017 | 266.5753 | 267.4627 | 268.3643 | 269.2804 | 270.2111 | 271.1569 | 271.9502 | 272.7583 | 273.5815 | 274.42 | 275.2741 | 276.1443 | 277.0308 | 277.9339 | 278.854 | 279.7914 | 281.0371 | 282.3027 | 283.5886 | 284.8953 | 286.2231 | 287.4928 | 288.784 | 290.0972 | 291.4329 | 292.7914 | 294.6128 | 296.4614 | 298.3377 | 300.2425 | 302.1762 | 303.833 | 305.5176 | 307.2306 | 308.9726 | 310.7442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 4 | 3713.7118 | 250.5065 | 251.2682 | 252.0413 | 252.826 | 253.6227 | 254.4317 | 255.2531 | 256.0872 | 256.9342 | 257.7944 | 258.4987 | 259.216 | 259.9465 | 260.6904 | 261.448 | 262.2197 | 263.0056 | 263.8062 | 264.6216 | 265.4522 | 266.5913 | 267.7479 | 268.9224 | 270.1151 | 271.3266 | 272.4769 | 273.6462 | 274.8348 | 276.0432 | 277.2718 | 278.9634 | 280.6791 | 282.4194 | 284.1849 | 285.9761 | 287.4858 | 289.0201 | 290.5794 | 292.1644 | 293.7756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 3 | 831.6133 | 52.6717 | 53.1161 | 53.5639 | 54.0151 | 54.4698 | 55.0088 | 55.5519 | 56.099 | 56.6504 | 57.2061 | 57.4586 | 57.7142 | 57.973 | 58.235 | 58.5004 | 58.7699 | 59.0429 | 59.3195 | 59.5997 | 59.8837 | 60.7134 | 61.55 | 62.3935 | 63.2443 | 64.1023 | 64.8482 | 65.6011 | 66.3612 | 67.1286 | 67.9036 | 69.4164 | 70.9419 | 72.4803 | 74.0319 | 75.5972 | 76.61 | 77.6332 | 78.6671 | 79.7119 | 80.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 187938.5335 | 11903.4269 | 12003.8619 | 12105.0526 | 12207.0171 | 12309.774 | 12431.5932 | 12554.3193 | 12677.9745 | 12802.5813 | 12928.1631 | 12985.219 | 13042.9815 | 13101.4659 | 13160.6879 | 13220.6636 | 13281.5757 | 13343.2756 | 13405.7805 | 13469.1078 | 13533.2756 | 13720.7913 | 13909.8478 | 14100.4841 | 14292.7401 | 14486.6568 | 14655.2175 | 14825.3642 | 14997.1361 | 15170.5733 | 15345.7169 | 15687.6066 | 16032.3455 | 16380.0095 | 16730.6763 | 17084.4254 | 17313.3032 | 17544.5373 | 17778.1866 | 18014.3116 | 18252.9741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 2 | 346.0887 | 21.9207 | 22.1294 | 22.3395 | 22.551 | 22.7639 | 22.9818 | 23.2012 | 23.4221 | 23.6447 | 23.8689 | 23.9654 | 24.0632 | 24.1621 | 24.2623 | 24.3637 | 24.4668 | 24.5712 | 24.6769 | 24.784 | 24.8924 | 25.2246 | 25.5594 | 25.8968 | 26.2369 | 26.5798 | 26.8803 | 27.1835 | 27.4894 | 27.7981 | 28.1097 | 28.7038 | 29.3026 | 29.9062 | 30.5148 | 31.1283 | 31.5146 | 31.9047 | 32.2987 | 32.6967 | 33.0988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 78213.5205 | 4953.9182 | 5001.0848 | 5048.5617 | 5096.3565 | 5144.477 | 5193.714 | 5243.2956 | 5293.2304 | 5343.527 | 5394.1941 | 5416.0154 | 5438.1032 | 5460.4634 | 5483.1018 | 5506.0246 | 5529.3145 | 5552.9015 | 5576.792 | 5600.9927 | 5625.5101 | 5700.5832 | 5776.2374 | 5852.4873 | 5929.348 | 6006.8349 | 6074.749 | 6143.2657 | 6212.3998 | 6282.1666 | 6352.5818 | 6486.8546 | 6622.1818 | 6758.5913 | 6896.1116 | 7034.7722 | 7122.0654 | 7210.222 | 7299.2632 | 7389.2111 | 7480.0881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Caclulates the probability weighted annual expected failure costs for repair/replacement of assets from climate peril projections. Scales to baseline scenario assets (existing for pre-RUL and standard for post-RUL) and replacement scenario asset counts by sub-class from tab '7. Project Characteristics'. Avoided repair and replace benefits are adjusted to represent avoided PV revenue requirement to align with BCA costs and the DST perspective.

## Int BCA Ann PWVOLL
Baseline Scenario Asset Class Annual Probability Weighted VOLL (Per Event Method) - with Dual | [78 empty] | Replacement Scenario Asset Class Annual Probability Weighted VOLL (Per Event Method) | [78 empty] | Replacement Scenario Asset Class Annual Probability Weighted VOLL Criticality Reduction (Per Event Method)
Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101
Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 3 | 117175.2787 | 7632.3302 | 7682.0817 | 7731.8332 | 7781.5847 | 7831.3362 | 7892.675 | 7954.0139 | 8015.3528 | 8076.6916 | 8138.0305 | 8155.7027 | 8173.3749 | 8191.0471 | 8208.7193 | 8226.3915 | 8244.1669 | 8261.9423 | 8279.7176 | 8297.493 | 8315.2684 | 8408.1051 | 8500.9419 | 8593.7787 | 8686.6154 | 8779.4522 | 8855.9378 | 8932.4235 | 9008.9091 | 9085.3947 | 9161.8803 | 9336.5652 | 9511.2501 | 9685.9349 | 9860.6198 | 10035.3047 | 10135.0389 | 10234.7731 | 10334.5073 | 10434.2415 | 10533.9758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 44823.2216 | 2912.8715 | 2935.4729 | 2958.0743 | 2980.6756 | 3003.277 | 3026.3345 | 3049.392 | 3072.4496 | 3095.5071 | 3118.5646 | 3124.7607 | 3130.9567 | 3137.1527 | 3143.3488 | 3149.5448 | 3155.7846 | 3162.0245 | 3168.2644 | 3174.5042 | 3180.7441 | 3215.3164 | 3249.8887 | 3284.461 | 3319.0334 | 3353.6057 | 3382.4903 | 3411.375 | 3440.2596 | 3469.1443 | 3498.0289 | 3561.61 | 3625.1911 | 3688.7722 | 3752.3533 | 3815.9343 | 3851.1068 | 3886.2793 | 3921.4518 | 3956.6243 | 3991.7968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 11150.2786 | 724.6094 | 730.2318 | 735.8541 | 741.4765 | 747.0988 | 752.8346 | 758.5704 | 764.3063 | 770.0421 | 775.7779 | 777.3192 | 778.8606 | 780.4019 | 781.9432 | 783.4846 | 785.0368 | 786.589 | 788.1413 | 789.6935 | 791.2457 | 799.846 | 808.4462 | 817.0465 | 825.6467 | 834.247 | 841.4324 | 848.6178 | 855.8031 | 862.9885 | 870.1739 | 885.9904 | 901.8069 | 917.6234 | 933.4399 | 949.2564 | 958.006 | 966.7555 | 975.5051 | 984.2546 | 993.0042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Calculates the expected value of last load (VOLL) to customers from resulting modeled and calibrated frequency of outages in the baseline and replacement scenarios. Annual outage event projections are taken from 'Int BCA Ann Fail Prob' for each scenario and includes dual baseline for the baseline scenario. The replacement scenario VOLL is calculated from remaining outage projections after hardening investments. The criticality VOLL is calculated from the remaining replacement scenario frequency and the updated per outage VOLL from '7. Project Characteristics'.

## Int BCA Ann CMI
Baseline Scenario Asset Class Annual CMI (Per Event Method) | [78 empty] | Scenario Asset Class Annual Probability Weighted CMI (Per Event Method)
Asset Class | Asset Sub-Class | Lifetime Total CMI Reduction | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | Asset Class | Asset Sub-Class | Lifetime Total CMI Reduction | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101
Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 3 | 247307.6519 | 5405.2247 | 5440.4587 | 5475.6928 | 5510.9269 | 5546.1609 | 5589.6012 | 5633.0414 | 5676.4817 | 5719.9219 | 5763.3622 | 5775.8776 | 5788.3931 | 5800.9086 | 5813.4241 | 5825.9396 | 5838.5281 | 5851.1166 | 5863.7052 | 5876.2937 | 5888.8822 | 5954.6293 | 6020.3764 | 6086.1235 | 6151.8706 | 6217.6177 | 6271.7849 | 6325.9521 | 6380.1193 | 6434.2865 | 6488.4537 | 6612.1658 | 6735.8778 | 6859.5898 | 6983.3018 | 7107.0139 | 7177.6457 | 7248.2776 | 7318.9095 | 7389.5414 | 7460.1732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 66821.995 | 1459.5982 | 1470.9235 | 1482.2487 | 1493.5739 | 1504.8991 | 1516.4529 | 1528.0067 | 1539.5605 | 1551.1143 | 1562.6681 | 1565.7728 | 1568.8776 | 1571.9823 | 1575.0871 | 1578.1918 | 1581.3185 | 1584.4452 | 1587.5719 | 1590.6986 | 1593.8253 | 1611.149 | 1628.4727 | 1645.7964 | 1663.1201 | 1680.4438 | 1694.9175 | 1709.3912 | 1723.8649 | 1738.3385 | 1752.8122 | 1784.6718 | 1816.5314 | 1848.3909 | 1880.2505 | 1912.1101 | 1929.7345 | 1947.359 | 1964.9834 | 1982.6078 | 2000.2323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Calculates the expected annual CMI from outages caused by climate perils modeled in the VASH Toolkit for the baseline and replacement scenarios. Modeled outage frequency from 'Int BCA Ann Fail Prob' are scaled to the number of customers and duration from '7. Project Characteristics'.