## Appendix 2-BB 2025-2031
[10 empty] | File Number: |  | EB-2025-0252
Exhibit:
Tab:
Schedule:
Page:
Date:
Appendix 2-BB
Service Life Comparison
2025-2031 Service Life
|  | Asset Details |  |  | Useful Life |  |  | USoA Account Number | USoA Account Description | Alectra Rates (2025 - 2031) |  | Outside Range of Min, Max TUL?
Parent* | # | Category¦ Component ¦ Type |  |  | MIN UL | TUL | MAX UL |  |  | Years | Rate | Below Min TUL | Above Max TUL
OH | 1 | Fully Dressed Wood Poles | Overall |  | 35 | 45 | 75 | 1830 | Poles, Towers and Fixtures (Wood) | 45 | 2.222% | No | No
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
| 2 | Fully Dressed Concrete Poles | Overall |  | 50 | 60 | 80 | 1830 | Poles, Towers and Fixtures (Concrete) | 60 | 1.667% | No | No
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
| 3 | Fully Dressed Steel Poles | Overall |  | 60 | 60 | 80
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
|  | Composite Poles | Overall |  | 60 | 60 | 80 | 1830 | Poles, Towers and Fixtures (Composite) | 70 | 1.429% | No | No
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
| 4 | OH Line Switch |  |  | 30 | 45 | 55 | 1835 | Overhead Conductors and Devices (Switches & Capacitors) | 35 | 2.857% | No | No
| 5 | OH Line Switch Motor |  |  | 15 | 25 | 25
| 6 | OH Line Switch RTU |  |  | 15 | 20 | 20
| 7 | OH Integral Switches |  |  | 35 | 45 | 60
| 8 | OH Conductors |  |  | 50 | 60 | 75
[8 empty] | 1835 | Overhead Conductors and Devices (Primary) | 50 | 2% | No | No
[8 empty] | 1855 | Services (Secondary/Services O/H) | 50 | 2% | No | No
| 9 | OH Transformers & Voltage Regulators |  |  | 30 | 40 | 60 | 1850 | Line Transformers (OH Transformers) | 45 | 2.222% | No | No
| 10 | OH Shunt Capacitor Banks |  |  | 25 | 30 | 40
| 11 | Reclosers |  |  | 25 | 40 | 55
TS & MS | 12 | Power Transformers | Overall |  | 30 | 45 | 60 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV (Power Transformers) | 45 | 2.222% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (Power Transformers) | 45 | 2.222% | No | No
|  |  | Bushing |  | 10 | 20 | 30
|  |  | Tap Changer |  | 20 | 30 | 60 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV (Tap Changer) | 45 | 2.222% | No | No
|  |  | Tap Changer |  | 20 | 30 | 60 | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (Tap Changer) | 45 | 2.222% | No | No
| 13 | Station Service Transformer |  |  | 30 | 45 | 55
| 14 | Station Grounding Transformer |  |  | 30 | 40 | 40
| 15 | Station DC System | Overall |  | 10 | 20 | 30 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV (DC Systems/Battery) | 15 | 6.667% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (DC Systems/Battery) | 15 | 6.667% | No | No
[8 empty] | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV (Capacitor Banks) | 30 | 3.333% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (Capacitor Banks) | 30 | 3.333% | No | No
|  |  | Battery Bank |  | 10 | 15 | 15
|  |  | Charger |  | 20 | 20 | 30
| 16 | Station Metal Clad Switchgear | Overall |  | 30 | 40 | 60 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV (Switchgear) | 40 | 2.5% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (Switchgear) | 40 | 2.5% | No | No
|  |  | Removable Breaker |  | 25 | 40 | 60
| 17 | Station Independent Breakers |  |  | 35 | 45 | 65
| 18 | Station Switch |  |  | 30 | 50 | 60
| 19 | Electromechanical Relays |  |  | 25 | 35 | 50 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV (Relays - SS/Electromechanical) | 30 | 3.333% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (Relays - SS/Electromechanical) | 30 | 3.333% | No | No
| 20 | Solid State Relays |  |  | 10 | 30 | 45
| 21 | Digital & Numeric Relays |  |  | 15 | 20 | 20 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV (Relays - Microprocessor) | 15 | 6.667% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (Relays - Microprocessor) | 15 | 6.667% | No | No
| 22 | Rigid Busbars |  |  | 30 | 55 | 60
| 23 | Steel Structure |  |  | 35 | 50 | 90 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV (Support Steel Structure and Grounding System) | 50 | 2% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (Support Steel Structure and Grounding System) | 50 | 2% | No | No
UG | 24 | Primary Paper Insulated Lead Covered (PILC) Cables |  |  | 60 | 65 | 75 | 1845 | Underground conductors and Devices (Primary - PILC) | 70 | 1.429% | No | No
| 25 | Primary Ethylene-Propylene Rubber (EPR) Cables |  |  | 20 | 25 | 25
| 26 | Primary Non-Tree Retardant (TR) Cross Linked Polyethylene (XLPE) Cables Direct Buried |  |  | 20 | 25 | 30 | 1845 | Underground conductors and Devices (Primary - XLPE Non-TR) | 40 | 2.5% | No | Yes | Supported by the Alliance depreciation rate study
| 27 | Primary Non-TR XLPE Cables in Duct |  |  | 20 | 25 | 30 | 1845 | Underground conductors and Devices (Primary - XLPE-TR) | 45 | 2.222% | No | Yes | Supported by the Alliance depreciation rate study
[8 empty] | 1845 | Underground conductors and Devices (Cable Injections) | 20 | 5% | No | No
| 30 | Secondary PILC Cables |  |  | 70 | 75 | 80
| 31 | Secondary Cables Direct Buried |  |  | 25 | 35 | 40 | 1845 | Underground conductors and Devices (Secondary - Direct Buried) | 30 | 3.333% | No | No
| 32 | Secondary Cables in Duct |  |  | 35 | 40 | 60 | 1845 | Underground conductors and Devices (Secondary - In Duct/Services) | 40 | 2.5% | No | No
| 33 | Network Tranformers | Overall |  | 20 | 35 | 50
|  |  | Protector |  | 20 | 35 | 40
| 34 | Pad-Mounted Transformers |  |  | 25 | 40 | 45 | 1850 | Line Transformers (UG Transformers - Padmount) | 30 | 3.333% | No | No
| 35 | Submersible/Vault Transformers |  |  | 25 | 35 | 45 | 1850 | Line Transformers (UG Transformers - Vault) | 40 | 2.5% | No | No
| 36 | UG Foundation |  |  | 35 | 55 | 70
| 37 | UG Vaults | Overall |  | 40 | 60 | 80
|  |  | Roof |  | 20 | 30 | 45
| 38 | UG Vault Switches |  |  | 20 | 35 | 50
| 39 | Pad-Mounted Switchgear |  |  | 20 | 30 | 45 | 1845 | Underground conductors and Devices (Air Insulated) | 35 | 2.857% | No | No
[8 empty] | 1845 | Underground conductors and Devices (Solid Dielectric) | 45 | 2.222% | No | No
[8 empty] | 1845 | Underground conductors and Devices (Oil/SF6) | 30 | 3.333% | No | No
| 40 | Ducts |  |  | 30 | 50 | 85
| 41 | Concrete Encased Duct Banks |  |  | 35 | 55 | 80 | 1840 | Underground Conduit (Concrete) | 60 | 1.667% | No | No
| 42 | Cable Chambers |  |  | 50 | 60 | 80
S | 43 | Remote SCADA |  |  | 15 | 20 | 30 | 1980 | System Supervisory Equipment (Communication Devices) | 15 | 6.667% | No | No
Table F-2 from Kinetrics Report1
|  | Asset Details |  |  | Useful Life Range |  |  | USoA Account Number | USoA Account Description | Alectra Rates (2025 - 2031) |  | Outside Range of Min, Max TUL?
| # | Category¦ Component ¦ Type | [7 empty] | Years | Rate | Below Min Range | Above Max Range
| 1 | Office Equipment |  |  | 5 | 15 |  | 1915 | Office Furniture and Equipment | 15 | 6.667% | No | No
| 2 | Vehicles | Trucks & Buckets |  | 5 | 15 |  | 1930 | Transportation Equipment (Single/Double Bucket Trucks) | 15 | 6.667% | No | No
|  |  | Trailers |  | 5 | 20 |  | 1930 | Transportation Equipment (Trailers) | 15 | 6.667% | No | No
|  |  | Vans |  | 5 | 10 |  | 1930 | Transportation Equipment (Automobiles/Light Trucks) | 7 | 14.29% | No | No
| 3 | Administrative Buildings |  |  | 50 | 75 |  | 1908 | Buildings and Fixtures (Non-distribution) | 60 | 1.667% | No | No
| 4 | Leasehold Improvements |  |  | Lease dependent
| 5 | Station Buildings | Station Buildings |  | 50 | 75 |  | 1808 | Buildings and Fixtures (MS/TS) | 60 | 1.667% | No | No
|  |  | Parking |  | 25 | 30 |  | 1808 | Buildings and Fixtures (MS/TS Improvements) | 25 | 4% | No | No
|  |  | Fence |  | 25 | 60
|  |  | Roof |  | 20 | 30 |  | 1908 | Buildings and Fixtures (Non-distribution Improvements) | 25 | 4% | No | No
| 6 | Computer Equipment | Hardware |  | 3 | 5 |  | 1920 | Computer Equipment - Hardware (Desktop/Laptop) | 4 | 25% | No | No
[8 empty] | 1920 | Computer Equipment - Hardware (Enterprise) | 5 | 20% | No | No
[8 empty] | 1920 | Computer Equipment - Hardware (Network, Etc.) | 5 | 20% | No | No
[8 empty] | 1920 | Computer Equipment - Hardware (Printers) | 6 | 16.67% | No | Yes | Supported by the Alliance depreciation rate study
|  |  | Software |  | 2 | 5 |  | 1611 | Computer Software (Minor) | 4 | 25% | No | No
[8 empty] | 1611 | Computer Software (Networks etc.) | 5 | 20% | No | No
[8 empty] | 1611 | Computer Software (Enterprise Systems) | 10 | 10% | No | Yes | Supported by the Alliance depreciation rate study
[8 empty] | 1611 | Computer Software (Enterprise Systems) | 15 | 6.667% | No | Yes | Supported by the Alliance depreciation rate study
| 7 | Equipment | Power Operated |  | 5 | 10
|  |  | Stores |  | 5 | 10 |  | 1935 | Stores Equipment | 10 | 10% | No | No
|  |  | Tools, Shop, Garage Equipment |  | 5 | 10
[8 empty] | 1940 | Tools, Shop and Garage Equipment | 10 | 10% | No | No
|  |  | Measurement & Testing Equipment |  | 5 | 10 |  | 1945 | Measurement and Testing Equipment | 10 | 10% | No | No
| 8 | Communication | Towers |  | 60 | 70
|  |  | Wireless |  | 2 | 10 |  | 1920 | Computer Equipment - Hardware (Switches & Routers) | 6 | 16.67% | No | No
[8 empty] | 1955 | Communication Equipment | 10 | 10% | No | No
| 9 | Residential Energy Meters |  |  | 25 | 35
| 10 | Industrial/Commercial Energy Meters |  |  | 25 | 35 |  | 1860 | Meters (AMI 1.0 Polyphase) | 25 | 4% | No | No
[8 empty] | 1860 | Meters (Primary Metering Units) | 35 | 2.857% | No | No
| 11 | Wholesale Energy Meters |  |  | 15 | 30 |  | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (Wholesale Meters) | 25 | 4% | No | No
| 12 | Current & Potential Transformer (CT & PT) |  |  | 35 | 50 |  | 1860 | Meters (Auxilliary Equipment)) | 40 | 2.5% | No | No
| 13 | Smart Meters |  |  | 5 | 15 |  | 1860 | Meters (Single Phase) | 15 | 6.667% | No | No
[8 empty] | 1860 | Meters (Suite) | 15 | 6.667% | No | No
[8 empty] | 1860 | Meters (Polyphase) | 15 | 6.667% | No | No
[8 empty] | 1860 | Meters (Compliance Testing) | 5 | 20% | No | No
| 14 | Repeaters - Smart Metering |  |  | 10 | 15
| 15 | Data Collectors - Smart Metering |  |  | 15 | 20
* TS & MS = Transformer and Municipal Stations UG = Underground Systems S = Monitoring and Control Systems
Note 1: | Tables F-1 and F-2 above are to be used as a reference in order to complete columns J, K, L and N.
See pages 17-19 of Kinetrics Report

## Appendix 2-BB 2019-2024
File Number:
Exhibit:
Tab:
Schedule:
Page:
Date:
Appendix 2-BB
Service Life Comparison
2019-2024 Service Life
|  | Asset Details |  |  | Useful Life |  |  | USoA Account Number | USoA Account Description | Alectra Rates (2019 - 2024) |  | Outside Range of Min, Max TUL?
Parent* | # | Category¦ Component ¦ Type |  |  | MIN UL | TUL | MAX UL |  |  | Years | Rate | Below Min TUL | Above Max TUL
OH | 1 | Fully Dressed Wood Poles | Overall |  | 35 | 45 | 75 | 1830 | Poles, Towers and Fixtures (Wood) | 44 | 2.273% | No | No
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
| 2 | Fully Dressed Concrete Poles | Overall |  | 50 | 60 | 80 | 1830 | Poles, Towers and Fixtures (Concrete) | 51 | 1.961% | No | No
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
| 3 | Fully Dressed Steel Poles | Overall |  | 60 | 60 | 80
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
|  | Composite Poles | Overall |  | 60 | 60 | 80
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
| 4 | OH Line Switch |  |  | 30 | 45 | 55 | 1835 | Overhead Conductors and Devices (Switches & Capacitors) | 38 | 2.632% | No | No
| 5 | OH Line Switch Motor |  |  | 15 | 25 | 25
| 6 | OH Line Switch RTU |  |  | 15 | 20 | 20
| 7 | OH Integral Switches |  |  | 35 | 45 | 60
| 8 | OH Conductors |  |  | 50 | 60 | 75
[8 empty] | 1835 | Overhead Conductors and Devices (Primary) | 45 | 2.222% | Yes | No
[8 empty] | 1855 | Services (Secondary/Services O/H) | 48 | 2.083% | Yes | No
| 9 | OH Transformers & Voltage Regulators |  |  | 30 | 40 | 60 | 1850 | Line Transformers (OH Transformers) | 41 | 2.439% | No | No
| 10 | OH Shunt Capacitor Banks |  |  | 25 | 30 | 40
| 11 | Reclosers |  |  | 25 | 40 | 55
TS & MS | 12 | Power Transformers | Overall |  | 30 | 45 | 60 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV (Transformers) | 40 | 2.5% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (Transformers) | 40 | 2.5% | No | No
|  |  | Bushing |  | 10 | 20 | 30
|  |  | Tap Changer |  | 20 | 30 | 60 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV (Tap Changer) | 25 | 4% | No | No
|  |  | Tap Changer |  | 20 | 30 | 60 | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (Tap Changer) | 25 | 4% | No | No
| 13 | Station Service Transformer |  |  | 30 | 45 | 55
| 14 | Station Grounding Transformer |  |  | 30 | 40 | 40
| 15 | Station DC System | Overall |  | 10 | 20 | 30 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV (Capacitor Banks) | 30 | 3.333% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (Capacitor Banks) | 30 | 3.333% | No | No
|  |  | Battery Bank |  | 10 | 15 | 15
|  |  | Charger |  | 20 | 20 | 30
| 16 | Station Metal Clad Switchgear | Overall |  | 30 | 40 | 60
|  |  | Removable Breaker |  | 25 | 40 | 60
| 17 | Station Independent Breakers |  |  | 35 | 45 | 65
| 18 | Station Switch |  |  | 30 | 50 | 60
| 19 | Electromechanical Relays |  |  | 25 | 35 | 50 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV (Switchgear & Relays/Protection & Control System) | 27 | 3.704% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (Switchgear & Relays/Protection & Control System) | 36 | 2.778% | No | No
| 20 | Solid State Relays |  |  | 10 | 30 | 45
| 21 | Digital & Numeric Relays |  |  | 15 | 20 | 20
| 22 | Rigid Busbars |  |  | 30 | 55 | 60
| 23 | Steel Structure |  |  | 35 | 50 | 90 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV (Support Steel Structure and Grounding System) | 40 | 2.5% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (Support Steel Structure and Grounding System) | 40 | 2.5% | No | No
UG | 24 | Primary Paper Insulated Lead Covered (PILC) Cables |  |  | 60 | 65 | 75 | 1845 | Underground conductors and Devices (Primary - PILC) | 70 | 1.429% | No | No
| 25 | Primary Ethylene-Propylene Rubber (EPR) Cables |  |  | 20 | 25 | 25
| 26 | Primary Non-Tree Retardant (TR) Cross Linked Polyethylene (XLPE) Cables Direct Buried |  |  | 20 | 25 | 30 | 1845 | Underground conductors and Devices (Primary - XLPE NonTR) | 45 | 2.222% | No | Yes
| 27 | Primary Non-TR XLPE Cables in Duct |  |  | 20 | 25 | 30 | 1845 | Underground conductors and Devices (Primary - XLPE-TR) | 38 | 2.632% | No | Yes
[8 empty] | 1845 | Underground conductors and Devices (Cable Injections) | 24 | 4.167% | No | No
| 30 | Secondary PILC Cables |  |  | 70 | 75 | 80
| 31 | Secondary Cables Direct Buried |  |  | 25 | 35 | 40 | 1845 | Underground conductors and Devices (Secondary - Direct Buried) | 31 | 3.226% | No | No
| 32 | Secondary Cables in Duct |  |  | 35 | 40 | 60 | 1845 | Underground conductors and Devices (Secondary - In Duct/Services) | 37 | 2.703% | No | No
| 33 | Network Tranformers | Overall |  | 20 | 35 | 50
|  |  | Protector |  | 20 | 35 | 40
| 34 | Pad-Mounted Transformers |  |  | 25 | 40 | 45 | 1850 | Line Transformers (UG Transformers) | 32 | 3.125% | No | No
| 35 | Submersible/Vault Transformers |  |  | 25 | 35 | 45
| 36 | UG Foundation |  |  | 35 | 55 | 70
| 37 | UG Vaults | Overall |  | 40 | 60 | 80
|  |  | Roof |  | 20 | 30 | 45
| 38 | UG Vault Switches |  |  | 20 | 35 | 50
| 39 | Pad-Mounted Switchgear |  |  | 20 | 30 | 45 | 1845 | Underground conductors and Devices (Air Insulated) | 39 | 2.564% | No | No
[8 empty] | 1845 | Underground conductors and Devices (Solid Dielectric/SF6/Oil) | 42 | 2.381% | No | No
| 40 | Ducts |  |  | 30 | 50 | 85
| 41 | Concrete Encased Duct Banks |  |  | 35 | 55 | 80 | 1840 | Underground Conduit (Concrete) | 52 | 1.923% | No | No
| 42 | Cable Chambers |  |  | 50 | 60 | 80
S | 43 | Remote SCADA |  |  | 15 | 20 | 30 | 1980 | System Supervisory Equipment (Communication Devices/Fault Indicators) | 15 | 6.667% | No | No
Table F-2 from Kinetrics Report1
|  | Asset Details |  |  | Useful Life Range |  |  | USoA Account Number | USoA Account Description | Alectra Rates (2019 - 2024) |  | Outside Range of Min, Max TUL?
| # | Category¦ Component ¦ Type | [7 empty] | Years | Rate | Below Min Range | Above Max Range
| 1 | Office Equipment |  |  | 5 | 15 |  | 1915 | Office Furniture and Equipment | 10 | 10% | No | No
| 2 | Vehicles | Trucks & Buckets |  | 5 | 15 |  | 1930 | Transportation Equipment (Single/Double Bucket Trucks) | 11 | 9.091% | No | No
|  |  | Trailers |  | 5 | 20 |  | 1930 | Transportation Equipment (Trailers) | 14 | 7.143% | No | No
|  |  | Vans |  | 5 | 10 |  | 1930 | Transportation Equipment (Automobiles) | 7 | 14.29% | No | No
[8 empty] | 1930 | Transportation Equipment (Light Trucks) | 8 | 12.5% | No | No
| 3 | Administrative Buildings |  |  | 50 | 75 |  | 1908 | Buildings and Fixtures (Non-distribution) | 60 | 1.667% | No | No
| 4 | Leasehold Improvements |  |  | Lease dependent
| 5 | Station Buildings | Station Buildings |  | 50 | 75 |  | 1808 | Buildings and Fixtures (MS/TS) | 60 | 1.667% | No | No
|  |  | Parking |  | 25 | 30 |  | 1808 | Buildings and Fixtures (TS Improvements) | 25 | 4% | No | No
|  |  | Fence |  | 25 | 60 |  | 1908 | Buildings and Fixtures (Non-distribution Improvements) | 27 | 3.704% | No | No
|  |  | Roof |  | 20 | 30 |  | 1808 | Buildings and Fixtures (MS Improvements) | 21 | 4.762% | No | No
| 6 | Computer Equipment | Hardware |  | 3 | 5 |  | 1920 | Computer Equipment - Hardware (Desktop/Laptop) | 4 | 25% | No | No
[8 empty] | 1920 | Computer Equipment - Hardware (Enterprise) | 5 | 20% | No | No
[8 empty] | 1920 | Computer Equipment - Hardware (Network, Etc.) | 5 | 20% | No | No
|  |  | Software |  | 2 | 5 |  | 1611 | Computer Software (Minor) | 4 | 25% | No | No
[8 empty] | 1611 | Computer Software (Networks etc.) | 5 | 20% | No | No
[8 empty] | 1611 | Computer Software (Enterprise Systems) | 10 | 10% | No | Yes
| 7 | Equipment | Power Operated |  | 5 | 10
|  |  | Stores |  | 5 | 10 |  | 1935 | Stores Equipment | 10 | 10% | No | No
|  |  | Tools, Shop, Garage Equipment |  | 5 | 10
[8 empty] | 1940 | Tools, Shop and Garage Equipment | 10 | 10% | No | No
|  |  | Measurement & Testing Equipment |  | 5 | 10 |  | 1945 | Measurement and Testing Equipment | 10 | 10% | No | No
| 8 | Communication | Towers |  | 60 | 70
|  |  | Wireless |  | 2 | 10 |  | 1920 | Computer Equipment - Hardware (Switches & Routers) | 6 | 16.67% | No | No
[8 empty] | 1955 | Communication Equipment | 8 | 12.5% | No | No
[8 empty] | 1955 | Communication Equipment - AMI2.0 | 10 | 10% | No | No
| 9 | Residential Energy Meters |  |  | 25 | 35
| 10 | Industrial/Commercial Energy Meters |  |  | 25 | 35 |  | 1860 | Meters (Polyphase) | 25 | 4% | No | No
[8 empty] | 1860 | Meters (Primary Metering Units) | 35 | 2.857% | No | No
| 11 | Wholesale Energy Meters |  |  | 15 | 30 |  | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (Wholesale Meters) | 25 | 4% | No | No
| 12 | Current & Potential Transformer (CT & PT) |  |  | 35 | 50
| 13 | Smart Meters |  |  | 5 | 15 |  | 1860 | Meters (Single Phase - AMI 1.0 Residential) | 15 | 6.667% | No | No
[8 empty] | 1860 | Meters (Single Phase- AMI 1.0 Commercial) | 14 | 7.143% | No | No
[8 empty] | 1860 | Meters (Suite) | 15 | 6.667% | No | No
[8 empty] | 1860 | Meters (Interval) | 16 | 6.25% | No | Yes
| 14 | Repeaters - Smart Metering |  |  | 10 | 15
| 15 | Data Collectors - Smart Metering |  |  | 15 | 20
* TS & MS = Transformer and Municipal Stations UG = Underground Systems S = Monitoring and Control Systems
Note 1: | Tables F-1 and F-2 above are to be used as a reference in order to complete columns J, K, L and N.
See pages 17-19 of Kinetrics Report

## Appendix 2-BB Legacies
Appendix 2-BB
Service Life Comparison
Legacy Service Life
[10 empty] | 2017 - 2018 | [15 empty] | 2019-2021
|  | Asset Details |  |  | Useful Life |  |  | USoA Account Number | USoA Account Description | Enersource Legacy Rates |  | Outside Range of Min, Max TUL? |  | Powerstream Legacy Rates |  | Outside Range of Min, Max TUL? |  | Brampton Legacy Rates |  | Outside Range of Min, Max TUL? |  | Horizon Legacy Rates |  | Outside Range of Min, Max TUL? |  | Guelph Legacy Rates |  | Outside Range of Min, Max TUL?
Parent* | # | Category¦ Component ¦ Type |  |  | MIN UL | TUL | MAX UL |  |  | Years | Rate | Below Min TUL | Above Max TUL | Years | Rate | Below Min TUL | Above Max TUL | Years | Rate | Below Min TUL | Above Max TUL | Years | Rate | Below Min TUL | Above Max TUL | Years | Rate | Below Min TUL | Above Max TUL
OH | 1 | Fully Dressed Wood Poles | Overall |  | 35 | 45 | 75 | 1830 | Poles, Towers and Fixtures (Wood) | 45 | 2.222% | No | No | 45 | 2.222% | No | No | 45 | 2.222% | No | No | 40 | 2.5% | No | No | 50 | 2% | No | No
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
| 2 | Fully Dressed Concrete Poles | Overall |  | 50 | 60 | 80 | 1830 | Poles, Towers and Fixtures (Concrete) | 55 | 1.818% | No | No | 45 | 2.222% | Yes | No | 50 | 2% | No | No | 50 | 2% | No | No | 40 | 2.5% | Yes | No
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
| 3 | Fully Dressed Steel Poles | Overall |  | 60 | 60 | 80
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
|  | Composite Poles | Overall |  | 60 | 60 | 80 | 1830 | Poles, Towers and Fixtures (Concrete) | [16 empty] | 70 | 1.429% | No | No
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
| 4 | OH Line Switch |  |  | 30 | 45 | 55 | 1835 | Overhead Conductors and Devices (Switches) | 40 | 2.5% | No | No | 40 | 2.5% | No | No | 30 | 3.333% | No | No | 40 | 2.5% | No | No | 50 | 2% | No | No
| 5 | OH Line Switch Motor |  |  | 15 | 25 | 25
| 6 | OH Line Switch RTU |  |  | 15 | 20 | 20
| 7 | OH Integral Switches |  |  | 35 | 45 | 60
| 8 | OH Conductors |  |  | 50 | 60 | 75 | 1835 | Overhead Conductors and Devices (Primary) | 45 | 2.222% | Yes | No
[8 empty] | 1835 | Overhead Conductors and Devices (Primary) | 55 | 1.818% | No | No | 40 | 2.5% | Yes | No | 50 | 2% | No | No | 50 | 2% | No | No | 60 | 1.667% | No | No
[8 empty] | 1855 | Services (Secondary OH) | 45 | 2.222% | Yes | No
[8 empty] | 1855 | Services (Secondary OH) | 55 | 1.818% | No | No | 40 | 2.5% | Yes | No | 50 | 2% | No | No | 50 | 2% | No | No | 60 | 1.667% | No | No
| 9 | OH Transformers & Voltage Regulators |  |  | 30 | 40 | 60 | 1850 | Line Transformers (OH) | 45 | 2.222% | No | No | 40 | 2.5% | No | No | 40 | 2.5% | No | No | 40 | 2.5% | No | No | 40 | 2.5% | No | No
| 10 | OH Shunt Capacitor Banks |  |  | 25 | 30 | 40 | 1835 | Overhead Conductors and Devices | [12 empty] | 30 | 3.333% | No | No | 30 | 3.333% | No | No
| 11 | Reclosers |  |  | 25 | 40 | 55 | 1835 | Overhead Conductors and Devices (Scadamate/Reclosures) | 25 | 4% | No | No
TS & MS | 12 | Power Transformers | Overall |  | 30 | 45 | 60 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV |  |  |  |  | 40 | 2.5% | No | No | 40 | 2.5% | No | No |  |  |  |  | 40 | 2.5% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV | 40 | 2.5% | No | No | 40 | 2.5% | No | No | 40 | 2.5% | No | No | 40 | 2.5% | No | No | 45 | 2.222% | No | No
|  |  | Bushing |  | 10 | 20 | 30
|  |  | Tap Changer |  | 20 | 30 | 60 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV |  |  |  |  | 25 | 4% | No | No | 25 | 4% | No | No |  |  |  |  | 30 | 3.333% | No | No
|  |  | Tap Changer |  | 20 | 30 | 60 | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV | [16 empty] | 40 | 2.5% | No | No
| 13 | Station Service Transformer |  |  | 30 | 45 | 55
| 14 | Station Grounding Transformer |  |  | 30 | 40 | 40
| 15 | Station DC System | Overall |  | 10 | 20 | 30
[8 empty] | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV (Capacitor Bank) |  |  |  |  | 30 | 3.333% | No | No
|  |  | Battery Bank |  | 10 | 15 | 15
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV | [8 empty] | 10 | 10% | No | No
|  |  | Charger |  | 20 | 20 | 30
| 16 | Station Metal Clad Switchgear | Overall |  | 30 | 40 | 60 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV (P&C) |  |  |  |  | 20 | 5% | Yes | No | 20 | 5% | Yes | No |  |  |  |  | 40 | 2.5% | No | No
[8 empty] | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV (Switchgear & Relays) |  |  |  |  | 30 | 3.333% | No | No | 20 | 5% | Yes | No |  |  |  |  | 50 | 2% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (P&C) | 40 | 2.5% | No | No | 20 | 5% | Yes | No | 20 | 5% | Yes | No | 40 | 2.5% | No | No | 40 | 2.5% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (Bus Work & Cubicles) | [8 empty] | 40 | 2.5% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (Switchgear) | 40 | 2.5% | No | No | 30 | 3.333% | No | No | 30 | 3.333% | No | No | 40 | 2.5% | No | No | 50 | 2% | No | No
|  |  | Removable Breaker |  | 25 | 40 | 60 | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV (Breakers & Reclosures) | [8 empty] | 40 | 2.5% | No | No | 40 | 2.5% | No | No | 40 | 2.5% | No | No
| 17 | Station Independent Breakers |  |  | 35 | 45 | 65
| 18 | Station Switch |  |  | 30 | 50 | 60
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV | [16 empty] | 45 | 2.222% | No | No
| 19 | Electromechanical Relays |  |  | 25 | 35 | 50
| 20 | Solid State Relays |  |  | 10 | 30 | 45
| 21 | Digital & Numeric Relays |  |  | 15 | 20 | 20 | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV | [16 empty] | 15 | 6.667% | No | No
| 22 | Rigid Busbars |  |  | 30 | 55 | 60
| 23 | Steel Structure |  |  | 35 | 50 | 90 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV | [16 empty] | 40 | 2.5% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV |  |  |  |  | 40 | 2.5% | No | No | [8 empty] | 50 | 2% | No | No
UG | 24 | Primary Paper Insulated Lead Covered (PILC) Cables |  |  | 60 | 65 | 75 | 1845 | Underground conductors and Devices (Primary)
| 25 | Primary Ethylene-Propylene Rubber (EPR) Cables |  |  | 20 | 25 | 25
| 26 | Primary Non-Tree Retardant (TR) Cross Linked Polyethylene (XLPE) Cables Direct Buried |  |  | 20 | 25 | 30 | 1845 | Underground conductors and Devices (Primary - XLPE Non-TR) | 40 | 2.5% | No | Yes | 45 | 2.222% | No | Yes | 35 | 2.857% | No | Yes | 40 | 2.5% | No | Yes | 40 | 2.5% | No | Yes
| 27 | Primary Non-TR XLPE Cables in Duct |  |  | 20 | 25 | 30 | 1845 | Underground conductors and Devices (Primary - XLPE TR) | 40 | 2.5% | No | Yes | 45 | 2.222% | No | Yes | 35 | 2.857% | No | Yes | 40 | 2.5% | No | Yes | 40 | 2.5% | No | Yes
[8 empty] | 1845 | Underground conductors and Devices (Cable Injections) |  |  |  |  | 20 | 5% | No | No | 35 | 2.857% | No | Yes
| 30 | Secondary PILC Cables |  |  | 70 | 75 | 80 | 1845 | Underground conductors and Devices | [8 empty] | 35 | 2.857% | Yes | No | 70 | 1.429% | No | No
| 31 | Secondary Cables Direct Buried |  |  | 25 | 35 | 40 | 1845 | Underground conductors and Devices | 40 | 2.5% | No | No | 25 | 4% | No | No | 50 | 2% | No | Yes | 25 | 4% | No | No | 40 | 2.5% | No | No
[8 empty] | 1845 | Underground conductors and Devices (Services/Accessories)
| 32 | Secondary Cables in Duct |  |  | 35 | 40 | 60 | 1845 | Underground conductors and Devices (Secondary) | 40 | 2.5% | No | No | 25 | 4% | Yes | No | 50 | 2% | No | No | 40 | 2.5% | No | No | 40 | 2.5% | No | No
[8 empty] | 1845 | Underground conductors and Devices (Services/Accessories) | 20 | 5% | Yes | No | [8 empty] | 50 | 2% | No | No
| 33 | Network Tranformers | Overall |  | 20 | 35 | 50
|  |  | Protector |  | 20 | 35 | 40
| 34 | Pad-Mounted Transformers |  |  | 25 | 40 | 45 | 1850 | Line Transformers (UG) | 35 | 2.857% | No | No | 30 | 3.333% | No | No | 40 | 2.5% | No | No | 30 | 3.333% | No | No | 40 | 2.5% | No | No
| 35 | Submersible/Vault Transformers |  |  | 25 | 35 | 45
| 36 | UG Foundation |  |  | 35 | 55 | 70
| 37 | UG Vaults | Overall |  | 40 | 60 | 80
|  |  | Roof |  | 20 | 30 | 45
| 38 | UG Vault Switches |  |  | 20 | 35 | 50
| 39 | Pad-Mounted Switchgear |  |  | 20 | 30 | 45 | 1845 | Underground conductors and Devices (Air Insulated) | 25 | 4% | No | No | 45 | 2.222% | No | No | 20 | 5% | No | No | 25 | 4% | No | No | 30 | 3.333% | No | No
[8 empty] | 1845 | Underground conductors and Devices (Solid Dielectric, SF6, Oil) | 35 | 2.857% | No | No | 45 | 2.222% | No | No | 35 | 2.857% | No | No | 25 | 4% | No | No | 30 | 3.333% | No | No
| 40 | Ducts |  |  | 30 | 50 | 85
| 41 | Concrete Encased Duct Banks |  |  | 35 | 55 | 80 | 1840 | Underground Conduit (Primary) | 50 | 2% | No | No | 60 | 1.667% | No | No | 50 | 2% | No | No | 40 | 2.5% | No | No | 55 | 1.818% | No | No
[8 empty] | 1840 | Underground Conduit (Concrete Encased) | [8 empty] | 75 | 1.333% | No | No
| 42 | Cable Chambers |  |  | 50 | 60 | 80
S | 43 | Remote SCADA |  |  | 15 | 20 | 30 | 1980 | System Supervisory Equipment (Scada/P&DC Sys) | 15 | 6.667% | No | No | 15 | 6.667% | No | No | 15 | 6.667% | No | No | 15 | 6.667% | No | No | 15 | 6.667% | No | No
[8 empty] | 1980 | System Supervisory Equipment (Other) | 10 | 10% | Yes | No | 15 | 6.667% | No | No | 7 | 14.29% | Yes | No | 15 | 6.667% | No | No | 10 | 10% | Yes | No
[8 empty] | 1980 | System Supervisory Equipment (Display Wall) |  |  |  |  | 10 | 10% | Yes | No
Table F-2 from Kinetrics Report1
|  | Asset Details |  |  | Useful Life Range |  |  | USoA Account Number | USoA Account Description | Enersource Legacy Rates |  | Outside Range of Min, Max TUL? |  | Powerstream Legacy Rates |  | Outside Range of Min, Max TUL? |  | Brampton Legacy Rates |  | Outside Range of Min, Max TUL? |  | Horizon Legacy Rates |  | Outside Range of Min, Max TUL? |  | Guelph Legacy Rates |  | Outside Range of Min, Max TUL?
| # | Category¦ Component ¦ Type | [7 empty] | Years | Rate | Below Min TUL | Above Max TUL | Years | Rate | Below Min TUL | Above Max TUL | Years | Rate | Below Min TUL | Above Max TUL | Years | Rate | Below Min TUL | Above Max TUL | Years | Rate | Below Min Range | Above Max Range
| 1 | Office Equipment |  |  | 5 | 15 |  | 1915 | Office Furniture and Equipment | 10 | 10% | No | No | 10 | 10% | No | No | 10 | 10% | No | No | 10 | 10% | No | No | 10 | 10% | No | No
| 2 | Vehicles | Trucks & Buckets |  | 5 | 15 |  | 1930 | Transportation Equipment | 8 | 12.5% | No | No | 7 | 14.29% | No | No | 10 | 10% | No | No | 15 | 6.667% | No | No | 10 | 10% | No | No
[8 empty] | 1930 | Transportation Equipment | 12 | 8.333% | No | No | 12 | 8.333% | No | No |  |  |  |  | 15 | 6.667% | No | No
|  |  | Trailers |  | 5 | 20 |  | 1930 | Transportation Equipment | 15 | 6.667% | No | No | 22 | 4.545% | No | Yes | 10 | 10% | No | No | 15 | 6.667% | No | No | 10 | 10% | No | No
[8 empty] | 1930 | Transportation Equipment |  |  |  |  | 12 | 8.333% | No | No
[8 empty] | 1930 | Transportation Equipment |  |  |  |  | 7 | 14.29% | No | No
|  |  | Vans |  | 5 | 10 |  | 1930 | Transportation Equipment | 4 | 25% | Yes | No | 7 | 14.29% | No | No | 7 | 14.29% | No | No | 5 | 20% | No | No | 5 | 20% | No | No
[8 empty] | 1930 | Transportation Equipment | 5 | 20% | No | No |  |  |  |  | 10 | 10% | No | No | 8 | 12.5% | No | No | 5 | 20% | No | No
| 3 | Administrative Buildings |  |  | 50 | 75 |  | 1908 | Buildings and Fixtures | 60 | 1.667% | No | No | 60 | 1.667% | No | No | 60 | 1.667% | No | No |  |  |  |  | 60 | 1.667% | No | No
| 4 | Leasehold Improvements |  |  | Lease dependent
[8 empty] | 1908 | Buildings and Fixtures (improvements) | 20 | 5% |  |  | 10-30 | 3%-10% |  |  | 25 | 4% |  |  | 30 | 3.333%
| 5 | Station Buildings | Station Buildings |  | 50 | 75 |  | 1808 | Buildings and Fixtures (MS & TS) | 60 | 1.667% | No | No | 60 | 1.667% | No | No | 60 | 1.667% | No | No | 60 | 1.667% | No | No | 60 | 1.667% | No | No
|  |  | Parking |  | 25 | 30
|  |  | Fence |  | 25 | 60 |  | 1808 | Buildings and Fixtures | [16 empty] | 30 | 3.333% | No | No
|  |  | Roof |  | 20 | 30 |  | 1908 | Buildings and Fixtures (improvements .) | 20 | 5% | No | No | [12 empty] | 20 | 5% | No | No
| 6 | Computer Equipment | Hardware |  | 3 | 5 |  | 1920 | Computer Equipment - Hardware (Desktop/Laptop) | 3 | 33.33% | No | No | 4 | 25% | No | No | 5 | 20% | No | No | 3 | 33.33% | No | No | 5 | 20% | No | No
[8 empty] | 1920 | Computer Equipment - Hardware (Enterprise) | 10 | 10% | No | Yes | 5 | 20% | No | No | 5 | 20% | No | No |  |  |  |  | 5 | 20% | No | No
[8 empty] | 1920 | Computer Equipment - Hardware (Network) | 5 | 20% | No | No | [8 empty] | 5 | 20% | No | No
[8 empty] | 1920 | Computer Equipment - Hardware (Server Leased) | [12 empty] | 3 | 33.33% | No | No
[8 empty] | 1920 | Computer Equipment - Hardware (Switches/Routers) |  |  |  |  | 6 | 16.67% | No | Yes
|  |  | Software |  | 2 | 5 |  | 1611 | Computer Software | 5 | 20% | No | No | 4 | 25% | No | No | 5 | 20% | No | No | 3 | 33.33% | No | No | 5 | 20% | No | No
[8 empty] | 1611 | Computer Software (Network) | 5 | 20% | No | No |  |  |  |  | 5 | 20% | No | No | 5 | 20% | No | No | 5 | 20% | No | No
[8 empty] | 1611 | Computer Software (Enterprise) | 10 | 10% | No | Yes | 10 | 10% | No | Yes
| 7 | Equipment | Power Operated |  | 5 | 10
|  |  | Stores |  | 5 | 10 |  | 1935 | Stores Equipment |  |  |  |  | 10 | 10% | No | No | 10 | 10% | No | No | 10 | 10% | No | No
|  |  | Tools, Shop, Garage Equipment |  | 5 | 10 |  | 1940 | Tools, Shop and Garage Equipment | 10 | 10% | No | No | 10 | 10% | No | No | 10 | 10% | No | No | 10 | 10% | No | No | 10 | 10% | No | No
|  |  | Measurement & Testing Equipment |  | 5 | 10 |  | 1945 | Measurement and Testing Equipment | [12 empty] | 10 | 10% | No | No
| 8 | Communication | Towers |  | 60 | 70
|  |  | Wireless |  | 2 | 10 |  | 1955 | Communication Equipment |  |  |  |  | 6 | 16.67% | No | No | 10 | 10% | No | No | 10 | 10% | No | No
[8 empty] | 1955 | Communication Equipment (Misc) |  |  |  |  | 3 | 33.33% | No | No | 10 | 10% | No | No
| 9 | Residential Energy Meters |  |  | 25 | 35
| 10 | Industrial/Commercial Energy Meters |  |  | 25 | 35 |  | 1860 | Meters (Primary Metering Units) | 35 | 2.857% | No | No
[8 empty] | 1860 | Meters (Polyphase) | 25 | 4% | No | No | 25 | 4% | No | No | 25 | 4% | No | No | 25 | 4% | No | No | 30 | 3.333% | No | No
| 11 | Wholesale Energy Meters |  |  | 15 | 30
| 12 | Current & Potential Transformer (CT & PT) |  |  | 35 | 50
| 13 | Smart Meters |  |  | 5 | 15 |  | 1860 | Meters (Residential) | 15 | 6.667% | No | No | 15 | 6.667% | No | No | 15 | 6.667% | No | No | 15 | 6.667% | No | No | 15 | 6.667% | No | No
[8 empty] | 1860 | Meters (Suite) | 15 | 6.667% | No | No
[8 empty] | 1860 | Meters (Interval) | 15 | 6.667% | No | No | 15 | 6.667% | No | No
[8 empty] | 1860 | Meters (Interval) | 25 | 4% | No | Yes
[8 empty] | 1860 | Meters (Commercial) | 15 | 6.667% | No | No |  |  |  |  | 10 | 10% | No | No | 15 | 6.667% | No | No
| 14 | Repeaters - Smart Metering |  |  | 10 | 15
| 15 | Data Collectors - Smart Metering |  |  | 15 | 20 |  | 1860 | Meters | [8 empty] | 5 | 20% | Yes | No
* TS & MS = Transformer and Municipal Stations UG = Underground Systems S = Monitoring and Control Systems
Note 1: | Tables F-1 and F-2 above are to be used as a reference in order to complete columns J, K, L and N.
See pages 17-19 of Kinetrics Report