## 2026-FULL
Dry Core Transformer Losses Effective Jan 1, 2026
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 7.5704 | 0.137 |  | 7.8889
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.42782 | 4.6744 | 5.1022 | 0.44582 | 5.548
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.2165 | 12.4508 | 13.6673 | 1.2677 | 14.935
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.622 | 16.6011 | 18.2231 | 1.6903 | 19.9134
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.0681 | 20.8847 | 22.9527 | 2.1551 | 25.1078
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.7575 | 28.7853 | 31.5428 | 2.8735 | 34.4163
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.3251 | 33.4688 | 36.7939 | 3.4651 | 40.259 |  | 2026 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.7282 | 37.442 | 41.1702 | 3.8851 | 45.0553 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.3997 | 44.0444 | 48.4441 | 4.5849 | 53.029 | GS 50 to 1,499 kW | 0.02334 | 4.5787 | 2.5918 | 8.0636
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.4743 | 54.62 | 60.0943 | 5.7046 | 65.799 | GS 1,500 to 4,999 kW | 0.02315 | 4.5424 | 2.5712 | 7.705
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 5.5984 | 55.8731 | 61.4715 | 5.834 | 67.3054 | Large Use | 0.02718 | 5.334 | 3.0193 | 7.8982
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.8571 | 58.4703 | 64.3274 | 6.1035 | 70.4309
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 6.2942 | 62.8372 | 69.1314 | 6.5591 | 75.6905
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 6.7313 | 67.2042 | 73.9355 | 7.0146 | 80.9501 | Tier 1 | 0.12 | November 1, 2025 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 7.7058 | 77.1688 | 84.8746 | 8.03 | 92.9046
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 8.3534 | 83.8053 | 92.1586 | 8.7049 | 100.8635
[14 empty] | Tier 2 | 0.142 | November 1, 2025 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.63341 | 6.7588 | 7.3922 | 0.66007 | 8.0523
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.97323 | 10.2424 | 11.2156 | 1.0142 | 12.2298 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.9465 | 20.4848 | 22.4312 | 2.0284 | 24.4596 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.433 | 24.9016 | 27.3347 | 2.5354 | 29.8701 | RRRP | 0.0015
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.244 | 33.2022 | 36.4462 | 3.3806 | 39.8268
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 0.36 | 262.8 | 0.14994 | 27.2436 | 0.50994 | 290.0436 | 3.8604 | 39.736 | 43.5964 | 4.0229 | 47.6193
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.785 | 49.5367 | 54.3217 | 4.9864 | 59.308
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.121 | 52.5007 | 57.6217 | 5.3365 | 62.9582
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.7987 | 58.5037 | 64.3024 | 6.0427 | 70.3451
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 6.2817 | 63.8101 | 70.0918 | 6.546 | 76.6378
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 6.7699 | 69.1902 | 75.9601 | 7.0548 | 83.0149
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 7.2586 | 74.5716 | 81.8302 | 7.564 | 89.3942
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 0.72525 | 529.4325 | 0.30165 | 54.8084 | 1.0269 | 584.2409 | 7.774 | 80.041 | 87.815 | 8.1011 | 95.9161
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 8.7995 | 90.9061 | 99.7056 | 9.1698 | 108.8754
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 12.7536 | 140.5274 | 153.281 | 13.2903 | 166.5713
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 14.7306 | 165.3381 | 180.0687 | 15.3505 | 195.4192
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 16.7076 | 190.1487 | 206.8564 | 17.4107 | 224.2671
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 21.898 | 241.0184 | 262.9164 | 22.8195 | 285.736
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 24.5745 | 272.3544 | 296.9289 | 25.6087 | 322.5376
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 32.847 | 361.5276 | 394.3746 | 34.2293 | 428.6039
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 39.1732 | 433.0333 | 472.2065 | 40.8217 | 513.0282
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 47.0403 | 520.8736 | 567.9139 | 49.0199 | 616.9337
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 55.4752 | 616.2145 | 671.6897 | 57.8097 | 729.4994
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 68.1275 | 759.226 | 827.3535 | 70.9945 | 898.348
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 78.2658 | 877.0692 | 955.335 | 81.5593 | 1036.8943
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2025 RPP Tiered Pricing, WMSR Pricing to be effective January 1, 2026
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2027-FULL
Dry Core Transformer Losses Effective Jan 1, 2027
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 7.571 | 0.137 |  | 8.6758
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.42786 | 4.6744 | 5.1022 | 0.49029 | 5.5925
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.2166 | 12.4508 | 13.6674 | 1.3942 | 15.0616
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.6222 | 16.6011 | 18.2233 | 1.8589 | 20.0821
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.0682 | 20.8847 | 22.9529 | 2.3701 | 25.323
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.7577 | 28.7853 | 31.543 | 3.1601 | 34.7031
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.3254 | 33.4688 | 36.7942 | 3.8107 | 40.6049 |  | 2027 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.7285 | 37.442 | 41.1705 | 4.2726 | 45.4431 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.4001 | 44.0444 | 48.4445 | 5.0422 | 53.4867 | GS 50 to 1,499 kW | 0.02394 | 4.5787 | 2.5918 | 8.7552
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.4747 | 54.62 | 60.0948 | 6.2737 | 66.3684 | GS 1,500 to 4,999 kW | 0.02375 | 4.5424 | 2.5712 | 8.4491
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 5.5988 | 55.8731 | 61.472 | 6.4159 | 67.8878 | Large Use | 0.02789 | 5.334 | 3.0193 | 8.8232
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.8576 | 58.4703 | 64.3279 | 6.7124 | 71.0402
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 6.2947 | 62.8372 | 69.132 | 7.2133 | 76.3453
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 6.7319 | 67.2042 | 73.9361 | 7.7143 | 81.6504 | Tier 1 | 0.12 | November 1, 2025 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 7.7064 | 77.1688 | 84.8752 | 8.831 | 93.7062
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 8.3541 | 83.8053 | 92.1593 | 9.5732 | 101.7325
[14 empty] | Tier 2 | 0.142 | November 1, 2025 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.63347 | 6.7588 | 7.3923 | 0.72591 | 8.1182
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.97331 | 10.2424 | 11.2157 | 1.1153 | 12.331 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.9466 | 20.4848 | 22.4314 | 2.2307 | 24.6621 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.4332 | 24.9016 | 27.3349 | 2.7883 | 30.1232 | RRRP | 0.0015
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.2443 | 33.2022 | 36.4465 | 3.7178 | 40.1643
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 0.36 | 262.8 | 0.14994 | 27.2436 | 0.50994 | 290.0436 | 3.8608 | 39.736 | 43.5967 | 4.4242 | 48.0209
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.7854 | 49.5367 | 54.3221 | 5.4837 | 59.8058
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.1214 | 52.5007 | 57.6221 | 5.8688 | 63.4909
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.7992 | 58.5037 | 64.3029 | 6.6455 | 70.9484
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 6.2822 | 63.8101 | 70.0923 | 7.199 | 77.2913
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 6.7705 | 69.1902 | 75.9607 | 7.7585 | 83.7192
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 7.2592 | 74.5716 | 81.8308 | 8.3185 | 90.1493
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 0.72525 | 529.4325 | 0.30165 | 54.8084 | 1.0269 | 584.2409 | 7.7746 | 80.041 | 87.8156 | 8.9092 | 96.7248
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 8.8003 | 90.9061 | 99.7064 | 10.0845 | 109.7908
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 12.7546 | 140.5274 | 153.2821 | 14.6159 | 167.898
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 14.7318 | 165.3381 | 180.0699 | 16.8817 | 196.9516
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 16.709 | 190.1487 | 206.8578 | 19.1474 | 226.0052
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 21.8999 | 241.0184 | 262.9183 | 25.0957 | 288.014
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 24.5766 | 272.3544 | 296.931 | 28.1631 | 325.094
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 32.8498 | 361.5276 | 394.3774 | 37.6436 | 432.021
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 39.1765 | 433.0333 | 472.2098 | 44.8935 | 517.1034
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 47.0443 | 520.8736 | 567.9178 | 53.9095 | 621.8273
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 55.4799 | 616.2145 | 671.6944 | 63.5761 | 735.2705
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 68.1333 | 759.226 | 827.3593 | 78.076 | 905.4353
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 78.2723 | 877.0692 | 955.3416 | 89.6947 | 1045.0362
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2025 RPP Tiered Pricing, WMSR Pricing to be effective January 1, 2027
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2028-FULL
Dry Core Transformer Losses Effective Jan 1, 2028
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 7.5713 | 0.137 |  | 9.6282
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.42788 | 4.6744 | 5.1022 | 0.54412 | 5.6463
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.2167 | 12.4508 | 13.6675 | 1.5472 | 15.2147
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.6222 | 16.6011 | 18.2233 | 2.0629 | 20.2863
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.0683 | 20.8847 | 22.953 | 2.6302 | 25.5832
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.7578 | 28.7853 | 31.5431 | 3.507 | 35.0502
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.3256 | 33.4688 | 36.7943 | 4.229 | 41.0233 |  | 2028 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.7287 | 37.442 | 41.1707 | 4.7416 | 45.9123 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.4003 | 44.0444 | 48.4447 | 5.5957 | 54.0404 | GS 50 to 1,499 kW | 0.02425 | 4.5787 | 2.5918 | 9.635
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.475 | 54.62 | 60.095 | 6.9624 | 67.0574 | GS 1,500 to 4,999 kW | 0.02406 | 4.5424 | 2.5712 | 9.3969
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 5.5991 | 55.8731 | 61.4722 | 7.1202 | 68.5924 | Large Use | 0.02825 | 5.334 | 3.0193 | 9.8528
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.8578 | 58.4703 | 64.3281 | 7.4492 | 71.7773
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 6.295 | 62.8372 | 69.1322 | 8.0052 | 77.1374
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 6.7322 | 67.2042 | 73.9364 | 8.5611 | 82.4975 | Tier 1 | 0.12 | November 1, 2025 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 7.7067 | 77.1688 | 84.8756 | 9.8005 | 94.676
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 8.3544 | 83.8053 | 92.1597 | 10.6241 | 102.7838
[14 empty] | Tier 2 | 0.142 | November 1, 2025 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.63349 | 6.7588 | 7.3923 | 0.80559 | 8.1979
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.97335 | 10.2424 | 11.2157 | 1.2378 | 12.4535 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.9467 | 20.4848 | 22.4315 | 2.4756 | 24.907 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.4333 | 24.9016 | 27.335 | 3.0944 | 30.4294 | RRRP | 0.0015
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.2445 | 33.2022 | 36.4466 | 4.1259 | 40.5725
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 0.36 | 262.8 | 0.14994 | 27.2436 | 0.50994 | 290.0436 | 3.8609 | 39.736 | 43.5969 | 4.9098 | 48.5067
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.7856 | 49.5367 | 54.3223 | 6.0857 | 60.408
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.1217 | 52.5007 | 57.6224 | 6.5131 | 64.1354
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.7994 | 58.5037 | 64.3032 | 7.375 | 71.6781
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 6.2825 | 63.8101 | 70.0926 | 7.9892 | 78.0818
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 6.7708 | 69.1902 | 75.961 | 8.6102 | 84.5712
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 7.2595 | 74.5716 | 81.8311 | 9.2317 | 91.0628
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 0.72525 | 529.4325 | 0.30165 | 54.8084 | 1.0269 | 584.2409 | 7.775 | 80.041 | 87.816 | 9.8872 | 97.7032
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 8.8006 | 90.9061 | 99.7067 | 11.1915 | 110.8983
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 12.7552 | 140.5274 | 153.2826 | 16.2204 | 169.503
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 14.7325 | 165.3381 | 180.0706 | 18.7349 | 198.8054
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 16.7098 | 190.1487 | 206.8585 | 21.2493 | 228.1078
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 21.9008 | 241.0184 | 262.9192 | 27.8506 | 290.7698
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 24.5776 | 272.3544 | 296.932 | 31.2547 | 328.1867
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 32.8512 | 361.5276 | 394.3788 | 41.7759 | 436.1548
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 39.1782 | 433.0333 | 472.2115 | 49.8218 | 522.0333
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 47.0463 | 520.8736 | 567.9199 | 59.8274 | 627.7473
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 55.4823 | 616.2145 | 671.6968 | 70.5552 | 742.252
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 68.1362 | 759.226 | 827.3622 | 86.6469 | 914.0091
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 78.2757 | 877.0692 | 955.3449 | 99.541 | 1054.8859
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2025 RPP Tiered Pricing, WMSR Pricing to be effective January 1, 2028
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2029-FULL
Dry Core Transformer Losses Effective Jan 1, 2029
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 7.5717 | 0.137 |  | 10.3761
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.4279 | 4.6744 | 5.1023 | 0.58638 | 5.6886
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.2167 | 12.4508 | 13.6676 | 1.6674 | 15.3349
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.6223 | 16.6011 | 18.2234 | 2.2232 | 20.4466
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.0684 | 20.8847 | 22.9531 | 2.8345 | 25.7877
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.758 | 28.7853 | 31.5433 | 3.7794 | 35.3227
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.3257 | 33.4688 | 36.7945 | 4.5575 | 41.352 |  | 2029 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.7289 | 37.442 | 41.1709 | 5.1099 | 46.2808 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.4005 | 44.0444 | 48.4449 | 6.0303 | 54.4753 | GS 50 to 1,499 kW | 0.02465 | 4.5787 | 2.5918 | 10.3217
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.4753 | 54.62 | 60.0953 | 7.5032 | 67.5985 | GS 1,500 to 4,999 kW | 0.02446 | 4.5424 | 2.5712 | 10.138
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 5.5994 | 55.8731 | 61.4725 | 7.6732 | 69.1457 | Large Use | 0.02872 | 5.334 | 3.0193 | 10.6686
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.8581 | 58.4703 | 64.3284 | 8.0278 | 72.3563
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 6.2954 | 62.8372 | 69.1326 | 8.627 | 77.7596
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 6.7326 | 67.2042 | 73.9367 | 9.2261 | 83.1628 | Tier 1 | 0.12 | November 1, 2025 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 7.7072 | 77.1688 | 84.876 | 10.5617 | 95.4377
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 8.3549 | 83.8053 | 92.1601 | 11.4493 | 103.6094
[14 empty] | Tier 2 | 0.142 | November 1, 2025 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.63353 | 6.7588 | 7.3923 | 0.86817 | 8.2605
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.9734 | 10.2424 | 11.2158 | 1.3339 | 12.5497 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.9468 | 20.4848 | 22.4316 | 2.6679 | 25.0994 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.4335 | 24.9016 | 27.3351 | 3.3348 | 30.6699 | RRRP | 0.0015
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.2446 | 33.2022 | 36.4468 | 4.4464 | 40.8932
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 0.36 | 262.8 | 0.14994 | 27.2436 | 0.50994 | 290.0436 | 3.8611 | 39.736 | 43.5971 | 5.2912 | 48.8883
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.7859 | 49.5367 | 54.3225 | 6.5584 | 60.881
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.1219 | 52.5007 | 57.6226 | 7.019 | 64.6416
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.7998 | 58.5037 | 64.3035 | 7.9478 | 72.2513
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 6.2828 | 63.8101 | 70.0929 | 8.6098 | 78.7028
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 6.7712 | 69.1902 | 75.9614 | 9.279 | 85.2404
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 7.2599 | 74.5716 | 81.8315 | 9.9488 | 91.7803
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 0.72525 | 529.4325 | 0.30165 | 54.8084 | 1.0269 | 584.2409 | 7.7754 | 80.041 | 87.8164 | 10.6552 | 98.4716
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 8.8011 | 90.9061 | 99.7072 | 12.0608 | 111.768
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 12.7559 | 140.5274 | 153.2833 | 17.4803 | 170.7637
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 14.7333 | 165.3381 | 180.0714 | 20.1901 | 200.2615
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 16.7107 | 190.1487 | 206.8594 | 22.8998 | 229.7593
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 21.902 | 241.0184 | 262.9204 | 30.0139 | 292.9343
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 24.579 | 272.3544 | 296.9334 | 33.6824 | 330.6158
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 32.853 | 361.5276 | 394.3807 | 45.0209 | 439.4015
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 39.1804 | 433.0333 | 472.2137 | 53.6916 | 525.9054
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 47.0489 | 520.8736 | 567.9225 | 64.4745 | 632.397
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 55.4854 | 616.2145 | 671.6999 | 76.0355 | 747.7354
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 68.14 | 759.226 | 827.366 | 93.3771 | 920.7431
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 78.2801 | 877.0692 | 955.3493 | 107.2728 | 1062.6221
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2025 RPP Tiered Pricing, WMSR Pricing to be effective January 1, 2029
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2030-FULL
Dry Core Transformer Losses Effective Jan 1, 2030
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 7.5722 | 0.137 |  | 11.069
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.42792 | 4.6744 | 5.1023 | 0.62554 | 5.7278
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.2168 | 12.4508 | 13.6676 | 1.7787 | 15.4464
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.6224 | 16.6011 | 18.2235 | 2.3716 | 20.5952
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.0686 | 20.8847 | 22.9532 | 3.0238 | 25.9771
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.7581 | 28.7853 | 31.5434 | 4.0318 | 35.5753
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.3259 | 33.4688 | 36.7947 | 4.8618 | 41.6566 |  | 2030 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.7291 | 37.442 | 41.1711 | 5.4512 | 46.6223 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.4008 | 44.0444 | 48.4452 | 6.433 | 54.8782 | GS 50 to 1,499 kW | 0.02508 | 4.5787 | 2.5918 | 10.9739
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.4756 | 54.62 | 60.0956 | 8.0042 | 68.0999 | GS 1,500 to 4,999 kW | 0.02488 | 4.5424 | 2.5712 | 10.843
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 5.5997 | 55.8731 | 61.4728 | 8.1856 | 69.6585 | Large Use | 0.02922 | 5.334 | 3.0193 | 11.3901
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.8585 | 58.4703 | 64.3288 | 8.5639 | 72.8927
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 6.2957 | 62.8372 | 69.133 | 9.2031 | 78.336
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 6.733 | 67.2042 | 73.9371 | 9.8422 | 83.7794 | Tier 1 | 0.12 | November 1, 2025 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 7.7076 | 77.1688 | 84.8764 | 11.267 | 96.1434
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 8.3554 | 83.8053 | 92.1606 | 12.2139 | 104.3745
[14 empty] | Tier 2 | 0.142 | November 1, 2025 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.63357 | 6.7588 | 7.3924 | 0.92614 | 8.3185
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.97346 | 10.2424 | 11.2158 | 1.423 | 12.6388 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.9469 | 20.4848 | 22.4317 | 2.846 | 25.2777 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.4336 | 24.9016 | 27.3353 | 3.5575 | 30.8927 | RRRP | 0.0015
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.2448 | 33.2022 | 36.447 | 4.7433 | 41.1903
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 0.36 | 262.8 | 0.14994 | 27.2436 | 0.50994 | 290.0436 | 3.8614 | 39.736 | 43.5973 | 5.6445 | 49.2419
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.7862 | 49.5367 | 54.3228 | 6.9964 | 61.3192
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.1222 | 52.5007 | 57.6229 | 7.4877 | 65.1106
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.8001 | 58.5037 | 64.3038 | 8.4786 | 72.7824
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 6.2832 | 63.8101 | 70.0933 | 9.1848 | 79.2781
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 6.7716 | 69.1902 | 75.9618 | 9.8986 | 85.8604
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 7.2603 | 74.5716 | 81.8319 | 10.6131 | 92.4451
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 0.72525 | 529.4325 | 0.30165 | 54.8084 | 1.0269 | 584.2409 | 7.7759 | 80.041 | 87.8169 | 11.3667 | 99.1836
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 8.8017 | 90.9061 | 99.7078 | 12.8662 | 112.574
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 12.7567 | 140.5274 | 153.2841 | 18.6476 | 171.9317
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 14.7342 | 165.3381 | 180.0723 | 21.5384 | 201.6106
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 16.7117 | 190.1487 | 206.8604 | 24.4291 | 231.2895
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 21.9033 | 241.0184 | 262.9217 | 32.0182 | 294.9399
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 24.5805 | 272.3544 | 296.9349 | 35.9316 | 332.8665
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 32.855 | 361.5276 | 394.3826 | 48.0273 | 442.4099
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 39.1827 | 433.0333 | 472.216 | 57.2771 | 529.4931
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 47.0517 | 520.8736 | 567.9253 | 68.78 | 636.7053
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 55.4887 | 616.2145 | 671.7032 | 81.1131 | 752.8163
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 68.1441 | 759.226 | 827.3701 | 99.6127 | 926.9828
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 78.2847 | 877.0692 | 955.354 | 114.4363 | 1069.7903
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2025 RPP Tiered Pricing, WMSR Pricing to be effective January 1, 2030
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2026 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2026
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 7.5704 | 0.137 |  | 7.8889
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.42782 | 4.6744 | 5.1022 | 0.44582 | 5.548
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.2165 | 12.4508 | 13.6673 | 1.2677 | 14.935
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.622 | 16.6011 | 18.2231 | 1.6903 | 19.9134
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.0681 | 20.8847 | 22.9527 | 2.1551 | 25.1078
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.7575 | 28.7853 | 31.5428 | 2.8735 | 34.4163
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.3251 | 33.4688 | 36.7939 | 3.4651 | 40.259
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.7282 | 37.442 | 41.1702 | 3.8851 | 45.0553
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.3997 | 44.0444 | 48.4441 | 4.5849 | 53.029
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.4743 | 54.62 | 60.0943 | 5.7046 | 65.799
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 5.5984 | 55.8731 | 61.4715 | 5.834 | 67.3054
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.8571 | 58.4703 | 64.3274 | 6.1035 | 70.4309
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 6.2942 | 62.8372 | 69.1314 | 6.5591 | 75.6905
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 6.7313 | 67.2042 | 73.9355 | 7.0146 | 80.9501
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 7.7058 | 77.1688 | 84.8746 | 8.03 | 92.9046
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 8.3534 | 83.8053 | 92.1586 | 8.7049 | 100.8635
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.63341 | 6.7588 | 7.3922 | 0.66007 | 8.0523
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.97323 | 10.2424 | 11.2156 | 1.0142 | 12.2298
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.9465 | 20.4848 | 22.4312 | 2.0284 | 24.4596
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.433 | 24.9016 | 27.3347 | 2.5354 | 29.8701
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.244 | 33.2022 | 36.4462 | 3.3806 | 39.8268
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 3.8604 | 39.736 | 43.5964 | 4.0229 | 47.6193
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.785 | 49.5367 | 54.3217 | 4.9864 | 59.308
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.121 | 52.5007 | 57.6217 | 5.3365 | 62.9582
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.7987 | 58.5037 | 64.3024 | 6.0427 | 70.3451
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 6.2817 | 63.8101 | 70.0918 | 6.546 | 76.6378
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 6.7699 | 69.1902 | 75.9601 | 7.0548 | 83.0149
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 7.2586 | 74.5716 | 81.8302 | 7.564 | 89.3942
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 7.774 | 80.041 | 87.815 | 8.1011 | 95.9161
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 8.7995 | 90.9061 | 99.7056 | 9.1698 | 108.8754
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 12.7536 | 140.5274 | 153.281 | 13.2903 | 166.5713
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 14.7306 | 165.3381 | 180.0687 | 15.3505 | 195.4192
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 16.7076 | 190.1487 | 206.8564 | 17.4107 | 224.2671
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 21.898 | 241.0184 | 262.9164 | 22.8195 | 285.736
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 24.5745 | 272.3544 | 296.9289 | 25.6087 | 322.5376
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 32.847 | 361.5276 | 394.3746 | 34.2293 | 428.6039
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 39.1732 | 433.0333 | 472.2065 | 40.8217 | 513.0282
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 47.0403 | 520.8736 | 567.9139 | 49.0199 | 616.9337
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 55.4752 | 616.2145 | 671.6897 | 57.8097 | 729.4994
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 68.1275 | 759.226 | 827.3535 | 70.9945 | 898.348
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 78.2658 | 877.0692 | 955.335 | 81.5593 | 1036.8943
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2027 PDF
PROPOSED - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2027
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 7.571 | 0.137 |  | 8.6758
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.42786 | 4.6744 | 5.1022 | 0.49029 | 5.5925
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.2166 | 12.4508 | 13.6674 | 1.3942 | 15.0616
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.6222 | 16.6011 | 18.2233 | 1.8589 | 20.0821
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.0682 | 20.8847 | 22.9529 | 2.3701 | 25.323
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.7577 | 28.7853 | 31.543 | 3.1601 | 34.7031
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.3254 | 33.4688 | 36.7942 | 3.8107 | 40.6049
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.7285 | 37.442 | 41.1705 | 4.2726 | 45.4431
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.4001 | 44.0444 | 48.4445 | 5.0422 | 53.4867
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.4747 | 54.62 | 60.0948 | 6.2737 | 66.3684
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 5.5988 | 55.8731 | 61.472 | 6.4159 | 67.8878
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.8576 | 58.4703 | 64.3279 | 6.7124 | 71.0402
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 6.2947 | 62.8372 | 69.132 | 7.2133 | 76.3453
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 6.7319 | 67.2042 | 73.9361 | 7.7143 | 81.6504
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 7.7064 | 77.1688 | 84.8752 | 8.831 | 93.7062
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 8.3541 | 83.8053 | 92.1593 | 9.5732 | 101.7325
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.63347 | 6.7588 | 7.3923 | 0.72591 | 8.1182
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.97331 | 10.2424 | 11.2157 | 1.1153 | 12.331
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.9466 | 20.4848 | 22.4314 | 2.2307 | 24.6621
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.4332 | 24.9016 | 27.3349 | 2.7883 | 30.1232
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.2443 | 33.2022 | 36.4465 | 3.7178 | 40.1643
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 3.8608 | 39.736 | 43.5967 | 4.4242 | 48.0209
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.7854 | 49.5367 | 54.3221 | 5.4837 | 59.8058
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.1214 | 52.5007 | 57.6221 | 5.8688 | 63.4909
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.7992 | 58.5037 | 64.3029 | 6.6455 | 70.9484
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 6.2822 | 63.8101 | 70.0923 | 7.199 | 77.2913
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 6.7705 | 69.1902 | 75.9607 | 7.7585 | 83.7192
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 7.2592 | 74.5716 | 81.8308 | 8.3185 | 90.1493
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 7.7746 | 80.041 | 87.8156 | 8.9092 | 96.7248
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 8.8003 | 90.9061 | 99.7064 | 10.0845 | 109.7908
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 12.7546 | 140.5274 | 153.2821 | 14.6159 | 167.898
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 14.7318 | 165.3381 | 180.0699 | 16.8817 | 196.9516
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 16.709 | 190.1487 | 206.8578 | 19.1474 | 226.0052
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 21.8999 | 241.0184 | 262.9183 | 25.0957 | 288.014
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 24.5766 | 272.3544 | 296.931 | 28.1631 | 325.094
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 32.8498 | 361.5276 | 394.3774 | 37.6436 | 432.021
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 39.1765 | 433.0333 | 472.2098 | 44.8935 | 517.1034
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 47.0443 | 520.8736 | 567.9178 | 53.9095 | 621.8273
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 55.4799 | 616.2145 | 671.6944 | 63.5761 | 735.2705
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 68.1333 | 759.226 | 827.3593 | 78.076 | 905.4353
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 78.2723 | 877.0692 | 955.3416 | 89.6947 | 1045.0362
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2028 PDF
PROPOSED - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2028
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 7.5713 | 0.137 |  | 9.6282
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.42788 | 4.6744 | 5.1022 | 0.54412 | 5.6463
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.2167 | 12.4508 | 13.6675 | 1.5472 | 15.2147
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.6222 | 16.6011 | 18.2233 | 2.0629 | 20.2863
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.0683 | 20.8847 | 22.953 | 2.6302 | 25.5832
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.7578 | 28.7853 | 31.5431 | 3.507 | 35.0502
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.3256 | 33.4688 | 36.7943 | 4.229 | 41.0233
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.7287 | 37.442 | 41.1707 | 4.7416 | 45.9123
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.4003 | 44.0444 | 48.4447 | 5.5957 | 54.0404
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.475 | 54.62 | 60.095 | 6.9624 | 67.0574
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 5.5991 | 55.8731 | 61.4722 | 7.1202 | 68.5924
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.8578 | 58.4703 | 64.3281 | 7.4492 | 71.7773
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 6.295 | 62.8372 | 69.1322 | 8.0052 | 77.1374
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 6.7322 | 67.2042 | 73.9364 | 8.5611 | 82.4975
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 7.7067 | 77.1688 | 84.8756 | 9.8005 | 94.676
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 8.3544 | 83.8053 | 92.1597 | 10.6241 | 102.7838
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.63349 | 6.7588 | 7.3923 | 0.80559 | 8.1979
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.97335 | 10.2424 | 11.2157 | 1.2378 | 12.4535
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.9467 | 20.4848 | 22.4315 | 2.4756 | 24.907
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.4333 | 24.9016 | 27.335 | 3.0944 | 30.4294
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.2445 | 33.2022 | 36.4466 | 4.1259 | 40.5725
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 3.8609 | 39.736 | 43.5969 | 4.9098 | 48.5067
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.7856 | 49.5367 | 54.3223 | 6.0857 | 60.408
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.1217 | 52.5007 | 57.6224 | 6.5131 | 64.1354
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.7994 | 58.5037 | 64.3032 | 7.375 | 71.6781
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 6.2825 | 63.8101 | 70.0926 | 7.9892 | 78.0818
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 6.7708 | 69.1902 | 75.961 | 8.6102 | 84.5712
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 7.2595 | 74.5716 | 81.8311 | 9.2317 | 91.0628
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 7.775 | 80.041 | 87.816 | 9.8872 | 97.7032
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 8.8006 | 90.9061 | 99.7067 | 11.1915 | 110.8983
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 12.7552 | 140.5274 | 153.2826 | 16.2204 | 169.503
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 14.7325 | 165.3381 | 180.0706 | 18.7349 | 198.8054
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 16.7098 | 190.1487 | 206.8585 | 21.2493 | 228.1078
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 21.9008 | 241.0184 | 262.9192 | 27.8506 | 290.7698
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 24.5776 | 272.3544 | 296.932 | 31.2547 | 328.1867
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 32.8512 | 361.5276 | 394.3788 | 41.7759 | 436.1548
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 39.1782 | 433.0333 | 472.2115 | 49.8218 | 522.0333
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 47.0463 | 520.8736 | 567.9199 | 59.8274 | 627.7473
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 55.4823 | 616.2145 | 671.6968 | 70.5552 | 742.252
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 68.1362 | 759.226 | 827.3622 | 86.6469 | 914.0091
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 78.2757 | 877.0692 | 955.3449 | 99.541 | 1054.8859
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2029 PDF
PROPOSED - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2029
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 7.5717 | 0.137 |  | 10.3761
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.4279 | 4.6744 | 5.1023 | 0.58638 | 5.6886
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.2167 | 12.4508 | 13.6676 | 1.6674 | 15.3349
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.6223 | 16.6011 | 18.2234 | 2.2232 | 20.4466
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.0684 | 20.8847 | 22.9531 | 2.8345 | 25.7877
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.758 | 28.7853 | 31.5433 | 3.7794 | 35.3227
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.3257 | 33.4688 | 36.7945 | 4.5575 | 41.352
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.7289 | 37.442 | 41.1709 | 5.1099 | 46.2808
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.4005 | 44.0444 | 48.4449 | 6.0303 | 54.4753
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.4753 | 54.62 | 60.0953 | 7.5032 | 67.5985
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 5.5994 | 55.8731 | 61.4725 | 7.6732 | 69.1457
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.8581 | 58.4703 | 64.3284 | 8.0278 | 72.3563
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 6.2954 | 62.8372 | 69.1326 | 8.627 | 77.7596
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 6.7326 | 67.2042 | 73.9367 | 9.2261 | 83.1628
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 7.7072 | 77.1688 | 84.876 | 10.5617 | 95.4377
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 8.3544 | 83.8053 | 92.1601 | 11.4493 | 103.6094
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.63349 | 6.7588 | 7.3923 | 0.86817 | 8.2605
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.97335 | 10.2424 | 11.2158 | 1.3339 | 12.5497
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.9467 | 20.4848 | 22.4316 | 2.6679 | 25.0994
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.4333 | 24.9016 | 27.3351 | 3.3348 | 30.6699
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.2445 | 33.2022 | 36.4468 | 4.4464 | 40.8932
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 3.8609 | 39.736 | 43.5971 | 5.2912 | 48.8883
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.7856 | 49.5367 | 54.3225 | 6.5584 | 60.881
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.1217 | 52.5007 | 57.6226 | 7.019 | 64.6416
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.7994 | 58.5037 | 64.3035 | 7.9478 | 72.2513
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 6.2825 | 63.8101 | 70.0929 | 8.6098 | 78.7028
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 6.7708 | 69.1902 | 75.9614 | 9.279 | 85.2404
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 7.2595 | 74.5716 | 81.8315 | 9.9488 | 91.7803
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 7.775 | 80.041 | 87.8164 | 10.6552 | 98.4716
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 8.8006 | 90.9061 | 99.7072 | 12.0608 | 111.768
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 12.7552 | 140.5274 | 153.2833 | 17.4803 | 170.7637
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 14.7325 | 165.3381 | 180.0714 | 20.1901 | 200.2615
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 16.7098 | 190.1487 | 206.8594 | 22.8998 | 229.7593
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 21.9008 | 241.0184 | 262.9204 | 30.0139 | 292.9343
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 24.5776 | 272.3544 | 296.9334 | 33.6824 | 330.6158
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 32.8512 | 361.5276 | 394.3807 | 45.0209 | 439.4015
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 39.1782 | 433.0333 | 472.2137 | 53.6916 | 525.9054
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 47.0463 | 520.8736 | 567.9225 | 64.4745 | 632.397
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 55.4823 | 616.2145 | 671.6999 | 76.0355 | 747.7354
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 68.1362 | 759.226 | 827.366 | 93.3771 | 920.7431
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 78.2757 | 877.0692 | 955.3493 | 107.2728 | 1062.6221
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2030 PDF
PROPOSED - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2030
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 7.5722 | 0.137 |  | 11.069
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.42792 | 4.6744 | 5.1023 | 0.62554 | 5.7278
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.2168 | 12.4508 | 13.6676 | 1.7787 | 15.4464
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.6224 | 16.6011 | 18.2235 | 2.3716 | 20.5952
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.0686 | 20.8847 | 22.9532 | 3.0238 | 25.9771
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.7581 | 28.7853 | 31.5434 | 4.0318 | 35.5753
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.3259 | 33.4688 | 36.7947 | 4.8618 | 41.6566
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.7291 | 37.442 | 41.1711 | 5.4512 | 46.6223
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.4008 | 44.0444 | 48.4452 | 6.433 | 54.8782
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.4756 | 54.62 | 60.0956 | 8.0042 | 68.0999
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 5.5997 | 55.8731 | 61.4728 | 8.1856 | 69.6585
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.8585 | 58.4703 | 64.3288 | 8.5639 | 72.8927
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 6.2957 | 62.8372 | 69.133 | 9.2031 | 78.336
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 6.733 | 67.2042 | 73.9371 | 9.8422 | 83.7794
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 7.7076 | 77.1688 | 84.8764 | 11.267 | 96.1434
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 8.3554 | 83.8053 | 92.1606 | 12.2139 | 104.3745
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.63357 | 6.7588 | 7.3924 | 0.92614 | 8.3185
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.97346 | 10.2424 | 11.2158 | 1.423 | 12.6388
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.9469 | 20.4848 | 22.4317 | 2.846 | 25.2777
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.4336 | 24.9016 | 27.3353 | 3.5575 | 30.8927
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.2448 | 33.2022 | 36.447 | 4.7433 | 41.1903
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 3.8614 | 39.736 | 43.5973 | 5.6445 | 49.2419
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.7862 | 49.5367 | 54.3228 | 6.9964 | 61.3192
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.1222 | 52.5007 | 57.6229 | 7.4877 | 65.1106
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.8001 | 58.5037 | 64.3038 | 8.4786 | 72.7824
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 6.2832 | 63.8101 | 70.0933 | 9.1848 | 79.2781
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 6.7716 | 69.1902 | 75.9618 | 9.8986 | 85.8604
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 7.2603 | 74.5716 | 81.8319 | 10.6131 | 92.4451
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 7.7759 | 80.041 | 87.8169 | 11.3667 | 99.1836
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 8.8017 | 90.9061 | 99.7078 | 12.8662 | 112.574
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 12.7567 | 140.5274 | 153.2841 | 18.6476 | 171.9317
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 14.7342 | 165.3381 | 180.0723 | 21.5384 | 201.6106
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 16.7117 | 190.1487 | 206.8604 | 24.4291 | 231.2895
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 21.9033 | 241.0184 | 262.9217 | 32.0182 | 294.9399
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 24.5805 | 272.3544 | 296.9349 | 35.9316 | 332.8665
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 32.855 | 361.5276 | 394.3826 | 48.0273 | 442.4099
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 39.1827 | 433.0333 | 472.216 | 57.2771 | 529.4931
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 47.0517 | 520.8736 | 567.9253 | 68.78 | 636.7053
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 55.4887 | 616.2145 | 671.7032 | 81.1131 | 752.8163
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 68.1441 | 759.226 | 827.3701 | 99.6127 | 926.9828
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 78.2847 | 877.0692 | 955.354 | 114.4363 | 1069.7903
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard