## 2026-FULL
Dry Core Transformer Losses Effective Jan 1, 2026
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 7.5703 | 0.1363 |  | 7.9737
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.42782 | 4.6505 | 5.0783 | 0.45061 | 5.5289
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.2165 | 12.3872 | 13.6037 | 1.2813 | 14.8851
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.622 | 16.5163 | 18.1383 | 1.7084 | 19.8467
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.0681 | 20.778 | 22.846 | 2.1783 | 25.0243
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.7575 | 28.6382 | 31.3957 | 2.9044 | 34.3001
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.3251 | 33.2978 | 36.6229 | 3.5023 | 40.1252 |  | 2026 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.7282 | 37.2507 | 40.9789 | 3.9268 | 44.9057 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.3997 | 43.8194 | 48.2191 | 4.6341 | 52.8532 | GS 50 to 1,499 kW | 0.02332 | 4.5787 | 2.5918 | 7.9936
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.4743 | 54.341 | 59.8152 | 5.7659 | 65.5812 | GS 1,500 to 4,999 kW | 0.02313 | 4.5424 | 2.5712 | 7.6669
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 5.5983 | 55.5876 | 61.186 | 5.8966 | 67.0826 | Large Use | 0.02716 | 5.334 | 3.0193 | 8.2606
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.8571 | 58.1715 | 64.0286 | 6.1691 | 70.1977
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 6.2942 | 62.5162 | 68.8103 | 6.6296 | 75.4399
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 6.7313 | 66.8608 | 73.5921 | 7.09 | 80.6821 | Tier 1 | 0.12 | November 1, 2025 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 7.7057 | 76.7745 | 84.4803 | 8.1163 | 92.5966
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 8.3533 | 83.3771 | 91.7304 | 8.7984 | 100.5288
[14 empty] | Tier 2 | 0.142 | November 1, 2025 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.63341 | 6.7243 | 7.3577 | 0.66716 | 8.0249
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.97322 | 10.19 | 11.1633 | 1.0251 | 12.1884 | WMSR | 0.0041 | Jan 1, 2026 Rate
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.9464 | 20.3801 | 22.3265 | 2.0502 | 24.3767 | CBR | 0.0006 | Jan 1, 2026 Rate
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.433 | 24.7744 | 27.2074 | 2.5627 | 29.7701 | RRRP | 0.0006 | Jan 1, 2026 Rate
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.244 | 33.0325 | 36.2766 | 3.4169 | 39.6935
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 0.36 | 262.8 | 0.14994 | 27.2436 | 0.50994 | 290.0436 | 3.8604 | 39.5329 | 43.3934 | 4.0661 | 47.4595
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.785 | 49.2836 | 54.0686 | 5.0399 | 59.1085
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.121 | 52.2324 | 57.3534 | 5.3939 | 62.7473
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.7987 | 58.2048 | 64.0035 | 6.1077 | 70.1111
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 6.2817 | 63.4841 | 69.7657 | 6.6164 | 76.3821
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 6.7699 | 68.8367 | 75.6066 | 7.1306 | 82.7372
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 7.2586 | 74.1906 | 81.4491 | 7.6453 | 89.0944
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 0.72525 | 529.4325 | 0.30165 | 54.8084 | 1.0269 | 584.2409 | 7.774 | 79.632 | 87.406 | 8.1882 | 95.5942
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 8.7995 | 90.4416 | 99.2411 | 9.2683 | 108.5095
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 12.7535 | 139.8094 | 152.5629 | 13.4331 | 165.996
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 14.7306 | 164.4933 | 179.2239 | 15.5154 | 194.7393
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 16.7076 | 189.1772 | 205.8848 | 17.5978 | 223.4826
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 21.898 | 239.7869 | 261.6849 | 23.0647 | 284.7496
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 24.5744 | 270.9628 | 295.5373 | 25.8838 | 321.4211
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 32.8469 | 359.6804 | 392.5273 | 34.5971 | 427.1244
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 39.1731 | 430.8208 | 469.9939 | 41.2603 | 511.2542
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 47.0402 | 518.2122 | 565.2524 | 49.5466 | 614.7989
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 55.475 | 613.066 | 668.541 | 58.4309 | 726.9719
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 68.1274 | 755.3467 | 823.4741 | 71.7573 | 895.2314
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 78.2655 | 872.5878 | 950.8534 | 82.4357 | 1033.2891
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2025 RPP Tiered Pricing, WMSR Pricing to be effective January 1, 2026
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2027-FULL
Dry Core Transformer Losses Effective Jan 1, 2027
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 7.571 | 0.1363 |  | 8.4883
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.42786 | 4.6505 | 5.0783 | 0.4797 | 5.558
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.2166 | 12.3872 | 13.6038 | 1.364 | 14.9678
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.6222 | 16.5163 | 18.1384 | 1.8187 | 19.9571
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.0682 | 20.778 | 22.8462 | 2.3188 | 25.165
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.7577 | 28.6382 | 31.3959 | 3.0918 | 34.4877
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.3254 | 33.2978 | 36.6232 | 3.7283 | 40.3515 |  | 2027 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.7285 | 37.2507 | 40.9792 | 4.1803 | 45.1595 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.4001 | 43.8194 | 48.2194 | 4.9332 | 53.1526 | GS 50 to 1,499 kW | 0.02392 | 4.5787 | 2.5918 | 8.4203
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.4747 | 54.341 | 59.8157 | 6.1381 | 65.9537 | GS 1,500 to 4,999 kW | 0.02373 | 4.5424 | 2.5712 | 8.1407
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 5.5988 | 55.5876 | 61.1865 | 6.2772 | 67.4636 | Large Use | 0.02787 | 5.334 | 3.0193 | 8.9039
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.8575 | 58.1715 | 64.0291 | 6.5673 | 70.5964
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 6.2947 | 62.5162 | 68.8109 | 7.0574 | 75.8683
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 6.7319 | 66.8608 | 73.5927 | 7.5475 | 81.1402 | Tier 1 | 0.12 | November 1, 2025 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 7.7064 | 76.7745 | 84.4809 | 8.6401 | 93.121
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 8.354 | 83.3771 | 91.7311 | 9.3662 | 101.0973
[14 empty] | Tier 2 | 0.142 | November 1, 2025 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.63346 | 6.7243 | 7.3577 | 0.71022 | 8.068
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.97331 | 10.19 | 11.1634 | 1.0912 | 12.2546 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.9466 | 20.3801 | 22.3267 | 2.1825 | 24.5092 | CBR | 0.0006
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.4332 | 24.7744 | 27.2076 | 2.7281 | 29.9357 | RRRP | 0.0006
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.2443 | 33.0325 | 36.2768 | 3.6374 | 39.9143
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 0.36 | 262.8 | 0.14994 | 27.2436 | 0.50994 | 290.0436 | 3.8607 | 39.5329 | 43.3937 | 4.3285 | 47.7222
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.7854 | 49.2836 | 54.069 | 5.3652 | 59.4342
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.1214 | 52.2324 | 57.3539 | 5.742 | 63.0958
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.7992 | 58.2048 | 64.004 | 6.5018 | 70.5058
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 6.2822 | 63.4841 | 69.7663 | 7.0434 | 76.8096
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 6.7705 | 68.8367 | 75.6071 | 7.5908 | 83.198
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 7.2592 | 74.1906 | 81.4498 | 8.1387 | 89.5885
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 0.72525 | 529.4325 | 0.30165 | 54.8084 | 1.0269 | 584.2409 | 7.7746 | 79.632 | 87.4066 | 8.7166 | 96.1233
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 8.8002 | 90.4416 | 99.2419 | 9.8665 | 109.1084
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 12.7546 | 139.8094 | 152.564 | 14.3 | 166.864
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 14.7318 | 164.4933 | 179.2251 | 16.5168 | 195.7418
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 16.709 | 189.1772 | 205.8862 | 18.7335 | 224.6197
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 21.8998 | 239.7869 | 261.6867 | 24.5533 | 286.24
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 24.5765 | 270.9628 | 295.5393 | 27.5543 | 323.0936
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 32.8497 | 359.6804 | 392.5301 | 36.8299 | 429.36
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 39.1764 | 430.8208 | 469.9971 | 43.9231 | 513.9203
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 47.0441 | 518.2122 | 565.2563 | 52.7442 | 618.0005
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 55.4797 | 613.066 | 668.5457 | 62.2018 | 730.7476
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 68.1331 | 755.3467 | 823.4798 | 76.3883 | 899.8682
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 78.2721 | 872.5878 | 950.86 | 87.7559 | 1038.6158
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2025 RPP Tiered Pricing, WMSR Pricing to be effective January 1, 2027
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2028-FULL
Dry Core Transformer Losses Effective Jan 1, 2028
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 7.5713 | 0.1363 |  | 9.1757
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.42787 | 4.6505 | 5.0783 | 0.51855 | 5.5969
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.2167 | 12.3872 | 13.6039 | 1.4745 | 15.0784
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.6222 | 16.5163 | 18.1385 | 1.966 | 20.1045
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.0683 | 20.778 | 22.8463 | 2.5066 | 25.3529
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.7578 | 28.6382 | 31.396 | 3.3422 | 34.7382
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.3255 | 33.2978 | 36.6233 | 4.0303 | 40.6536 |  | 2028 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.7286 | 37.2507 | 40.9794 | 4.5188 | 45.4982 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.4002 | 43.8194 | 48.2196 | 5.3327 | 53.5523 | GS 50 to 1,499 kW | 0.02421 | 4.5787 | 2.5918 | 9.0499
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.4749 | 54.341 | 59.8159 | 6.6352 | 66.4511 | GS 1,500 to 4,999 kW | 0.02402 | 4.5424 | 2.5712 | 8.8403
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 5.599 | 55.5876 | 61.1867 | 6.7856 | 67.9722 | Large Use | 0.02821 | 5.334 | 3.0193 | 9.637
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.8578 | 58.1715 | 64.0293 | 7.0991 | 71.1284
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 6.295 | 62.5162 | 68.8111 | 7.629 | 76.4401
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 6.7322 | 66.8608 | 73.5929 | 8.1588 | 81.7517 | Tier 1 | 0.12 | November 1, 2025 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 7.7067 | 76.7745 | 84.4812 | 9.3399 | 93.8211
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 8.3544 | 83.3771 | 91.7314 | 10.1248 | 101.8562
[14 empty] | Tier 2 | 0.142 | November 1, 2025 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.63349 | 6.7243 | 7.3578 | 0.76773 | 8.1255
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.97334 | 10.19 | 11.1634 | 1.1796 | 12.343 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.9467 | 20.3801 | 22.3268 | 2.3592 | 24.686 | CBR | 0.0006
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.4333 | 24.7744 | 27.2077 | 2.949 | 30.1567 | RRRP | 0.0006
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.2444 | 33.0325 | 36.277 | 3.932 | 40.209
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 0.36 | 262.8 | 0.14994 | 27.2436 | 0.50994 | 290.0436 | 3.8609 | 39.5329 | 43.3938 | 4.6791 | 48.0729
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.7856 | 49.2836 | 54.0691 | 5.7997 | 59.8689
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.1216 | 52.2324 | 57.3541 | 6.207 | 63.561
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.7994 | 58.2048 | 64.0042 | 7.0284 | 71.0326
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 6.2824 | 63.4841 | 69.7665 | 7.6138 | 77.3803
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 6.7707 | 68.8367 | 75.6074 | 8.2056 | 83.813
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 7.2595 | 74.1906 | 81.45 | 8.7978 | 90.2479
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 0.72525 | 529.4325 | 0.30165 | 54.8084 | 1.0269 | 584.2409 | 7.7749 | 79.632 | 87.407 | 9.4225 | 96.8295
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 8.8006 | 90.4416 | 99.2422 | 10.6656 | 109.9078
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 12.7551 | 139.8094 | 152.5645 | 15.4581 | 168.0226
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 14.7324 | 164.4933 | 179.2257 | 17.8544 | 197.0801
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 16.7097 | 189.1772 | 205.8868 | 20.2507 | 226.1375
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 21.9007 | 239.7869 | 261.6876 | 26.5417 | 288.2293
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 24.5775 | 270.9628 | 295.5403 | 29.7858 | 325.3261
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 32.851 | 359.6804 | 392.5314 | 39.8126 | 432.344
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 39.178 | 430.8208 | 469.9987 | 47.4803 | 517.479
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 47.046 | 518.2122 | 565.2582 | 57.0157 | 622.2739
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 55.482 | 613.066 | 668.548 | 67.2393 | 735.7873
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 68.1358 | 755.3467 | 823.4826 | 82.5747 | 906.0573
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 78.2753 | 872.5878 | 950.8631 | 94.8629 | 1045.726
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2025 RPP Tiered Pricing, WMSR Pricing to be effective January 1, 2028
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2029-FULL
Dry Core Transformer Losses Effective Jan 1, 2029
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 7.5717 | 0.1363 |  | 9.6871
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.4279 | 4.6505 | 5.0784 | 0.54745 | 5.6258
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.2167 | 12.3872 | 13.6039 | 1.5567 | 15.1606
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.6223 | 16.5163 | 18.1386 | 2.0756 | 20.2141
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.0684 | 20.778 | 22.8464 | 2.6463 | 25.4927
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.758 | 28.6382 | 31.3962 | 3.5285 | 34.9247
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.3257 | 33.2978 | 36.6235 | 4.2549 | 40.8784 |  | 2029 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.7289 | 37.2507 | 40.9796 | 4.7706 | 45.7502 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.4005 | 43.8194 | 48.2198 | 5.6299 | 53.8498 | GS 50 to 1,499 kW | 0.0246 | 4.5787 | 2.5918 | 9.3849
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.4752 | 54.341 | 59.8162 | 7.005 | 66.8212 | GS 1,500 to 4,999 kW | 0.02441 | 4.5424 | 2.5712 | 9.2127
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 5.5993 | 55.5876 | 61.187 | 7.1637 | 68.3507 | Large Use | 0.02866 | 5.334 | 3.0193 | 10.4638
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.8581 | 58.1715 | 64.0296 | 7.4948 | 71.5244
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 6.2953 | 62.5162 | 68.8115 | 8.0541 | 76.8656
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 6.7325 | 66.8608 | 73.5933 | 8.6135 | 82.2068 | Tier 1 | 0.12 | November 1, 2025 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 7.7071 | 76.7745 | 84.4816 | 9.8604 | 94.342
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 8.3548 | 83.3771 | 91.7319 | 10.6891 | 102.421
[14 empty] | Tier 2 | 0.142 | November 1, 2025 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.63352 | 6.7243 | 7.3578 | 0.81052 | 8.1683
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.9734 | 10.19 | 11.1634 | 1.2454 | 12.4088 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.9468 | 20.3801 | 22.3269 | 2.4907 | 24.8176 | CBR | 0.0006
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.4335 | 24.7744 | 27.2079 | 3.1133 | 30.3212 | RRRP | 0.0006
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.2446 | 33.0325 | 36.2772 | 4.1511 | 40.4283
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 0.36 | 262.8 | 0.14994 | 27.2436 | 0.50994 | 290.0436 | 3.8611 | 39.5329 | 43.3941 | 4.9399 | 48.3339
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.7858 | 49.2836 | 54.0694 | 6.1229 | 60.1924
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.1219 | 52.2324 | 57.3543 | 6.5529 | 63.9073
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.7997 | 58.2048 | 64.0045 | 7.4201 | 71.4246
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 6.2828 | 63.4841 | 69.7669 | 8.0381 | 77.805
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 6.7711 | 68.8367 | 75.6078 | 8.6629 | 84.2707
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 7.2598 | 74.1906 | 81.4504 | 9.2882 | 90.7386
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 0.72525 | 529.4325 | 0.30165 | 54.8084 | 1.0269 | 584.2409 | 7.7753 | 79.632 | 87.4074 | 9.9477 | 97.3551
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 8.8011 | 90.4416 | 99.2427 | 11.26 | 110.5027
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 12.7558 | 139.8094 | 152.5652 | 16.3196 | 168.8849
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 14.7332 | 164.4933 | 179.2265 | 18.8495 | 198.076
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 16.7106 | 189.1772 | 205.8878 | 21.3793 | 227.2671
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 21.9019 | 239.7869 | 261.6888 | 28.021 | 289.7098
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 24.5788 | 270.9628 | 295.5417 | 31.4459 | 326.9875
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 32.8528 | 359.6804 | 392.5332 | 42.0315 | 434.5647
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 39.1801 | 430.8208 | 470.0009 | 50.1266 | 520.1274
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 47.0486 | 518.2122 | 565.2608 | 60.1934 | 625.4542
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 55.485 | 613.066 | 668.551 | 70.9868 | 739.5378
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 68.1395 | 755.3467 | 823.4863 | 87.1769 | 910.6632
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 78.2795 | 872.5878 | 950.8674 | 100.1499 | 1051.0173
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2025 RPP Tiered Pricing, WMSR Pricing to be effective January 1, 2029
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2030-FULL
Dry Core Transformer Losses Effective Jan 1, 2030
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 7.5722 | 0.1363 |  | 10.1694
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.42792 | 4.6505 | 5.0784 | 0.5747 | 5.6531
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.2168 | 12.3872 | 13.604 | 1.6342 | 15.2382
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.6224 | 16.5163 | 18.1387 | 2.1789 | 20.3176
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.0686 | 20.778 | 22.8465 | 2.7781 | 25.6246
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.7581 | 28.6382 | 31.3964 | 3.7042 | 35.1005
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.3259 | 33.2978 | 36.6237 | 4.4667 | 41.0904 |  | 2030 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.7291 | 37.2507 | 40.9798 | 5.0082 | 45.9879 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.4007 | 43.8194 | 48.2201 | 5.9102 | 54.1303 | GS 50 to 1,499 kW | 0.02504 | 4.5787 | 2.5918 | 9.6918
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.4756 | 54.341 | 59.8165 | 7.3537 | 67.1702 | GS 1,500 to 4,999 kW | 0.02484 | 4.5424 | 2.5712 | 9.5539
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 5.5997 | 55.5876 | 61.1873 | 7.5204 | 68.7077 | Large Use | 0.02917 | 5.334 | 3.0193 | 11.2625
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.8585 | 58.1715 | 64.03 | 7.8679 | 71.8979
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 6.2957 | 62.5162 | 68.8119 | 8.4551 | 77.267
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 6.7329 | 66.8608 | 73.5937 | 9.0423 | 82.636 | Tier 1 | 0.12 | November 1, 2025 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 7.7076 | 76.7745 | 84.4821 | 10.3513 | 94.8334
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 8.3553 | 83.3771 | 91.7324 | 11.2212 | 102.9536
[14 empty] | Tier 2 | 0.142 | November 1, 2025 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.63356 | 6.7243 | 7.3578 | 0.85087 | 8.2087
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.97346 | 10.19 | 11.1635 | 1.3074 | 12.4709 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.9469 | 20.3801 | 22.327 | 2.6147 | 24.9417 | CBR | 0.0006
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.4336 | 24.7744 | 27.208 | 3.2683 | 30.4764 | RRRP | 0.0006
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.2448 | 33.0325 | 36.2774 | 4.3578 | 40.6351
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 0.36 | 262.8 | 0.14994 | 27.2436 | 0.50994 | 290.0436 | 3.8613 | 39.5329 | 43.3943 | 5.1858 | 48.5801
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.7861 | 49.2836 | 54.0697 | 6.4278 | 60.4975
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.1222 | 52.2324 | 57.3547 | 6.8791 | 64.2338
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.8001 | 58.2048 | 64.0049 | 7.7895 | 71.7944
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 6.2832 | 63.4841 | 69.7672 | 8.4383 | 78.2055
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 6.7715 | 68.8367 | 75.6082 | 9.0942 | 84.7024
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 7.2603 | 74.1906 | 81.4509 | 9.7506 | 91.2015
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 0.72525 | 529.4325 | 0.30165 | 54.8084 | 1.0269 | 584.2409 | 7.7758 | 79.632 | 87.4079 | 10.4429 | 97.8508
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 8.8016 | 90.4416 | 99.2432 | 11.8206 | 111.0638
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 12.7566 | 139.8094 | 152.566 | 17.1321 | 169.6981
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 14.7341 | 164.4933 | 179.2274 | 19.7879 | 199.0153
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 16.7116 | 189.1772 | 205.8888 | 22.4437 | 228.3324
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 21.9032 | 239.7869 | 261.6901 | 29.416 | 291.1061
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 24.5803 | 270.9628 | 295.5431 | 33.0114 | 328.5545
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 32.8548 | 359.6804 | 392.5352 | 44.124 | 436.6592
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 39.1825 | 430.8208 | 470.0032 | 52.6221 | 522.6253
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 47.0514 | 518.2122 | 565.2636 | 63.1901 | 628.4537
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 55.4883 | 613.066 | 668.5543 | 74.5209 | 743.0752
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 68.1437 | 755.3467 | 823.4904 | 91.517 | 915.0074
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 78.2843 | 872.5878 | 950.8721 | 105.1358 | 1056.008
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2025 RPP Tiered Pricing, WMSR Pricing to be effective January 1, 2030
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2026 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2026
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 7.5703 | 0.1363 |  | 7.9737
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.42782 | 4.6505 | 5.0783 | 0.45061 | 5.5289
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.2165 | 12.3872 | 13.6037 | 1.2813 | 14.8851
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.622 | 16.5163 | 18.1383 | 1.7084 | 19.8467
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.0681 | 20.778 | 22.846 | 2.1783 | 25.0243
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.7575 | 28.6382 | 31.3957 | 2.9044 | 34.3001
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.3251 | 33.2978 | 36.6229 | 3.5023 | 40.1252
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.7282 | 37.2507 | 40.9789 | 3.9268 | 44.9057
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.3997 | 43.8194 | 48.2191 | 4.6341 | 52.8532
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.4743 | 54.341 | 59.8152 | 5.7659 | 65.5812
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 5.5983 | 55.5876 | 61.186 | 5.8966 | 67.0826
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.8571 | 58.1715 | 64.0286 | 6.1691 | 70.1977
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 6.2942 | 62.5162 | 68.8103 | 6.6296 | 75.4399
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 6.7313 | 66.8608 | 73.5921 | 7.09 | 80.6821
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 7.7057 | 76.7745 | 84.4803 | 8.1163 | 92.5966
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 8.3533 | 83.3771 | 91.7304 | 8.7984 | 100.5288
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.63341 | 6.7243 | 7.3577 | 0.66716 | 8.0249
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.97322 | 10.19 | 11.1633 | 1.0251 | 12.1884
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.9464 | 20.3801 | 22.3265 | 2.0502 | 24.3767
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.433 | 24.7744 | 27.2074 | 2.5627 | 29.7701
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.244 | 33.0325 | 36.2766 | 3.4169 | 39.6935
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 3.8604 | 39.5329 | 43.3934 | 4.0661 | 47.4595
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.785 | 49.2836 | 54.0686 | 5.0399 | 59.1085
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.121 | 52.2324 | 57.3534 | 5.3939 | 62.7473
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.7987 | 58.2048 | 64.0035 | 6.1077 | 70.1111
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 6.2817 | 63.4841 | 69.7657 | 6.6164 | 76.3821
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 6.7699 | 68.8367 | 75.6066 | 7.1306 | 82.7372
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 7.2586 | 74.1906 | 81.4491 | 7.6453 | 89.0944
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 7.774 | 79.632 | 87.406 | 8.1882 | 95.5942
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 8.7995 | 90.4416 | 99.2411 | 9.2683 | 108.5095
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 12.7535 | 139.8094 | 152.5629 | 13.4331 | 165.996
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 14.7306 | 164.4933 | 179.2239 | 15.5154 | 194.7393
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 16.7076 | 189.1772 | 205.8848 | 17.5978 | 223.4826
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 21.898 | 239.7869 | 261.6849 | 23.0647 | 284.7496
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 24.5744 | 270.9628 | 295.5373 | 25.8838 | 321.4211
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 32.8469 | 359.6804 | 392.5273 | 34.5971 | 427.1244
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 39.1731 | 430.8208 | 469.9939 | 41.2603 | 511.2542
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 47.0402 | 518.2122 | 565.2524 | 49.5466 | 614.7989
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 55.475 | 613.066 | 668.541 | 58.4309 | 726.9719
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 68.1274 | 755.3467 | 823.4741 | 71.7573 | 895.2314
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 78.2655 | 872.5878 | 950.8534 | 82.4357 | 1033.2891
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2027 PDF
PROPOSED - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2027
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 7.571 | 0.1363 |  | 8.4883
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.42786 | 4.6505 | 5.0783 | 0.4797 | 5.558
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.2166 | 12.3872 | 13.6038 | 1.364 | 14.9678
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.6222 | 16.5163 | 18.1384 | 1.8187 | 19.9571
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.0682 | 20.778 | 22.8462 | 2.3188 | 25.165
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.7577 | 28.6382 | 31.3959 | 3.0918 | 34.4877
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.3254 | 33.2978 | 36.6232 | 3.7283 | 40.3515
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.7285 | 37.2507 | 40.9792 | 4.1803 | 45.1595
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.4001 | 43.8194 | 48.2194 | 4.9332 | 53.1526
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.4747 | 54.341 | 59.8157 | 6.1381 | 65.9537
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 5.5988 | 55.5876 | 61.1865 | 6.2772 | 67.4636
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.8575 | 58.1715 | 64.0291 | 6.5673 | 70.5964
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 6.2947 | 62.5162 | 68.8109 | 7.0574 | 75.8683
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 6.7319 | 66.8608 | 73.5927 | 7.5475 | 81.1402
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 7.7064 | 76.7745 | 84.4809 | 8.6401 | 93.121
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 8.354 | 83.3771 | 91.7311 | 9.3662 | 101.0973
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.63346 | 6.7243 | 7.3577 | 0.71022 | 8.068
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.97331 | 10.19 | 11.1634 | 1.0912 | 12.2546
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.9466 | 20.3801 | 22.3267 | 2.1825 | 24.5092
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.4332 | 24.7744 | 27.2076 | 2.7281 | 29.9357
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.2443 | 33.0325 | 36.2768 | 3.6374 | 39.9143
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 3.8607 | 39.5329 | 43.3937 | 4.3285 | 47.7222
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.7854 | 49.2836 | 54.069 | 5.3652 | 59.4342
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.1214 | 52.2324 | 57.3539 | 5.742 | 63.0958
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.7992 | 58.2048 | 64.004 | 6.5018 | 70.5058
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 6.2822 | 63.4841 | 69.7663 | 7.0434 | 76.8096
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 6.7705 | 68.8367 | 75.6071 | 7.5908 | 83.198
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 7.2592 | 74.1906 | 81.4498 | 8.1387 | 89.5885
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 7.7746 | 79.632 | 87.4066 | 8.7166 | 96.1233
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 8.8002 | 90.4416 | 99.2419 | 9.8665 | 109.1084
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 12.7546 | 139.8094 | 152.564 | 14.3 | 166.864
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 14.7318 | 164.4933 | 179.2251 | 16.5168 | 195.7418
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 16.709 | 189.1772 | 205.8862 | 18.7335 | 224.6197
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 21.8998 | 239.7869 | 261.6867 | 24.5533 | 286.24
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 24.5765 | 270.9628 | 295.5393 | 27.5543 | 323.0936
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 32.8497 | 359.6804 | 392.5301 | 36.8299 | 429.36
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 39.1764 | 430.8208 | 469.9971 | 43.9231 | 513.9203
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 47.0441 | 518.2122 | 565.2563 | 52.7442 | 618.0005
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 55.4797 | 613.066 | 668.5457 | 62.2018 | 730.7476
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 68.1331 | 755.3467 | 823.4798 | 76.3883 | 899.8682
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 78.2721 | 872.5878 | 950.86 | 87.7559 | 1038.6158
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2028 PDF
PROPOSED - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2028
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 7.5713 | 0.1363 |  | 9.1757
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.42787 | 4.6505 | 5.0783 | 0.51855 | 5.5969
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.2167 | 12.3872 | 13.6039 | 1.4745 | 15.0784
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.6222 | 16.5163 | 18.1385 | 1.966 | 20.1045
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.0683 | 20.778 | 22.8463 | 2.5066 | 25.3529
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.7578 | 28.6382 | 31.396 | 3.3422 | 34.7382
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.3255 | 33.2978 | 36.6233 | 4.0303 | 40.6536
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.7286 | 37.2507 | 40.9794 | 4.5188 | 45.4982
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.4002 | 43.8194 | 48.2196 | 5.3327 | 53.5523
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.4749 | 54.341 | 59.8159 | 6.6352 | 66.4511
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 5.599 | 55.5876 | 61.1867 | 6.7856 | 67.9722
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.8578 | 58.1715 | 64.0293 | 7.0991 | 71.1284
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 6.295 | 62.5162 | 68.8111 | 7.629 | 76.4401
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 6.7322 | 66.8608 | 73.5929 | 8.1588 | 81.7517
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 7.7067 | 76.7745 | 84.4812 | 9.3399 | 93.8211
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 8.3544 | 83.3771 | 91.7314 | 10.1248 | 101.8562
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.63349 | 6.7243 | 7.3578 | 0.76773 | 8.1255
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.97334 | 10.19 | 11.1634 | 1.1796 | 12.343
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.9467 | 20.3801 | 22.3268 | 2.3592 | 24.686
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.4333 | 24.7744 | 27.2077 | 2.949 | 30.1567
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.2444 | 33.0325 | 36.277 | 3.932 | 40.209
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 3.8609 | 39.5329 | 43.3938 | 4.6791 | 48.0729
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.7856 | 49.2836 | 54.0691 | 5.7997 | 59.8689
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.1216 | 52.2324 | 57.3541 | 6.207 | 63.561
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.7994 | 58.2048 | 64.0042 | 7.0284 | 71.0326
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 6.2824 | 63.4841 | 69.7665 | 7.6138 | 77.3803
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 6.7707 | 68.8367 | 75.6074 | 8.2056 | 83.813
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 7.2595 | 74.1906 | 81.45 | 8.7978 | 90.2479
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 7.7749 | 79.632 | 87.407 | 9.4225 | 96.8295
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 8.8006 | 90.4416 | 99.2422 | 10.6656 | 109.9078
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 12.7551 | 139.8094 | 152.5645 | 15.4581 | 168.0226
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 14.7324 | 164.4933 | 179.2257 | 17.8544 | 197.0801
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 16.7097 | 189.1772 | 205.8868 | 20.2507 | 226.1375
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 21.9007 | 239.7869 | 261.6876 | 26.5417 | 288.2293
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 24.5775 | 270.9628 | 295.5403 | 29.7858 | 325.3261
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 32.851 | 359.6804 | 392.5314 | 39.8126 | 432.344
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 39.178 | 430.8208 | 469.9987 | 47.4803 | 517.479
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 47.046 | 518.2122 | 565.2582 | 57.0157 | 622.2739
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 55.482 | 613.066 | 668.548 | 67.2393 | 735.7873
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 68.1358 | 755.3467 | 823.4826 | 82.5747 | 906.0573
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 78.2753 | 872.5878 | 950.8631 | 94.8629 | 1045.726
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2029 PDF
PROPOSED - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2029
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 7.5717 | 0.1363 |  | 9.6871
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.4279 | 4.6505 | 5.0784 | 0.54745 | 5.6258
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.2167 | 12.3872 | 13.6039 | 1.5567 | 15.1606
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.6223 | 16.5163 | 18.1386 | 2.0756 | 20.2141
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.0684 | 20.778 | 22.8464 | 2.6463 | 25.4927
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.758 | 28.6382 | 31.3962 | 3.5285 | 34.9247
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.3257 | 33.2978 | 36.6235 | 4.2549 | 40.8784
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.7289 | 37.2507 | 40.9796 | 4.7706 | 45.7502
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.4005 | 43.8194 | 48.2198 | 5.6299 | 53.8498
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.4752 | 54.341 | 59.8162 | 7.005 | 66.8212
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 5.5993 | 55.5876 | 61.187 | 7.1637 | 68.3507
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.8581 | 58.1715 | 64.0296 | 7.4948 | 71.5244
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 6.2953 | 62.5162 | 68.8115 | 8.0541 | 76.8656
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 6.7325 | 66.8608 | 73.5933 | 8.6135 | 82.2068
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 7.7071 | 76.7745 | 84.4816 | 9.8604 | 94.342
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 8.3544 | 83.3771 | 91.7319 | 10.6891 | 102.421
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.63349 | 6.7243 | 7.3578 | 0.81052 | 8.1683
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.97334 | 10.19 | 11.1634 | 1.2454 | 12.4088
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.9467 | 20.3801 | 22.3269 | 2.4907 | 24.8176
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.4333 | 24.7744 | 27.2079 | 3.1133 | 30.3212
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.2444 | 33.0325 | 36.2772 | 4.1511 | 40.4283
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 3.8609 | 39.5329 | 43.3941 | 4.9399 | 48.3339
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.7856 | 49.2836 | 54.0694 | 6.1229 | 60.1924
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.1216 | 52.2324 | 57.3543 | 6.5529 | 63.9073
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.7994 | 58.2048 | 64.0045 | 7.4201 | 71.4246
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 6.2824 | 63.4841 | 69.7669 | 8.0381 | 77.805
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 6.7707 | 68.8367 | 75.6078 | 8.6629 | 84.2707
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 7.2595 | 74.1906 | 81.4504 | 9.2882 | 90.7386
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 7.7749 | 79.632 | 87.4074 | 9.9477 | 97.3551
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 8.8006 | 90.4416 | 99.2427 | 11.26 | 110.5027
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 12.7551 | 139.8094 | 152.5652 | 16.3196 | 168.8849
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 14.7324 | 164.4933 | 179.2265 | 18.8495 | 198.076
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 16.7097 | 189.1772 | 205.8878 | 21.3793 | 227.2671
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 21.9007 | 239.7869 | 261.6888 | 28.021 | 289.7098
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 24.5775 | 270.9628 | 295.5417 | 31.4459 | 326.9875
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 32.851 | 359.6804 | 392.5332 | 42.0315 | 434.5647
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 39.178 | 430.8208 | 470.0009 | 50.1266 | 520.1274
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 47.046 | 518.2122 | 565.2608 | 60.1934 | 625.4542
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 55.482 | 613.066 | 668.551 | 70.9868 | 739.5378
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 68.1358 | 755.3467 | 823.4863 | 87.1769 | 910.6632
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 78.2753 | 872.5878 | 950.8674 | 100.1499 | 1051.0173
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2030 PDF
PROPOSED - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2030
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 7.5722 | 0.1363 |  | 10.1694
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.42792 | 4.6505 | 5.0784 | 0.5747 | 5.6531
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.2168 | 12.3872 | 13.604 | 1.6342 | 15.2382
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.6224 | 16.5163 | 18.1387 | 2.1789 | 20.3176
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.0686 | 20.778 | 22.8465 | 2.7781 | 25.6246
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.7581 | 28.6382 | 31.3964 | 3.7042 | 35.1005
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.3259 | 33.2978 | 36.6237 | 4.4667 | 41.0904
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.7291 | 37.2507 | 40.9798 | 5.0082 | 45.9879
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.4007 | 43.8194 | 48.2201 | 5.9102 | 54.1303
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.4756 | 54.341 | 59.8165 | 7.3537 | 67.1702
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 5.5997 | 55.5876 | 61.1873 | 7.5204 | 68.7077
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.8585 | 58.1715 | 64.03 | 7.8679 | 71.8979
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 6.2957 | 62.5162 | 68.8119 | 8.4551 | 77.267
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 6.7329 | 66.8608 | 73.5937 | 9.0423 | 82.636
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 7.7076 | 76.7745 | 84.4821 | 10.3513 | 94.8334
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 8.3553 | 83.3771 | 91.7324 | 11.2212 | 102.9536
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.63356 | 6.7243 | 7.3578 | 0.85087 | 8.2087
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.97346 | 10.19 | 11.1635 | 1.3074 | 12.4709
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.9469 | 20.3801 | 22.327 | 2.6147 | 24.9417
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.4336 | 24.7744 | 27.208 | 3.2683 | 30.4764
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.2448 | 33.0325 | 36.2774 | 4.3578 | 40.6351
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 3.8613 | 39.5329 | 43.3943 | 5.1858 | 48.5801
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.7861 | 49.2836 | 54.0697 | 6.4278 | 60.4975
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.1222 | 52.2324 | 57.3547 | 6.8791 | 64.2338
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.8001 | 58.2048 | 64.0049 | 7.7895 | 71.7944
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 6.2832 | 63.4841 | 69.7672 | 8.4383 | 78.2055
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 6.7715 | 68.8367 | 75.6082 | 9.0942 | 84.7024
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 7.2603 | 74.1906 | 81.4509 | 9.7506 | 91.2015
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 7.7758 | 79.632 | 87.4079 | 10.4429 | 97.8508
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 8.8016 | 90.4416 | 99.2432 | 11.8206 | 111.0638
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 12.7566 | 139.8094 | 152.566 | 17.1321 | 169.6981
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 14.7341 | 164.4933 | 179.2274 | 19.7879 | 199.0153
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 16.7116 | 189.1772 | 205.8888 | 22.4437 | 228.3324
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 21.9032 | 239.7869 | 261.6901 | 29.416 | 291.1061
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 24.5803 | 270.9628 | 295.5431 | 33.0114 | 328.5545
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 32.8548 | 359.6804 | 392.5352 | 44.124 | 436.6592
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 39.1825 | 430.8208 | 470.0032 | 52.6221 | 522.6253
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 47.0514 | 518.2122 | 565.2636 | 63.1901 | 628.4537
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 55.4883 | 613.066 | 668.5543 | 74.5209 | 743.0752
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 68.1437 | 755.3467 | 823.4904 | 91.517 | 915.0074
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 78.2843 | 872.5878 | 950.8721 | 105.1358 | 1056.008
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard