## Cover
OEB Vulnerability Assessment & System Hardening
VASH Toolkit Model - Version 1.0.0
2025-09-16
Private and confidential
DISCLAIMER
This tool (“Report”) was prepared by Guidehouse Canada Ltd. (“Guidehouse”) pursuant to a contract with the Ontario Energy Board (OEB). Accordingly, Guidehouse disclaims any contractual or other responsibility to others based on their access to or use of the Report. The Report was prepared on the basis of information and assumptions set forth in associated appendices, underlying work papers, and other limiting conditions and assumptions. The work presented in this Report represents Guidehouse’s reasonable professional judgments based on the information available at the time and/or provided to Guidehouse. Guidehouse is not responsible for, and expressly disclaims, the reader’s use of, or reliance upon, the Report, nor any decisions based on the Report. Notice pertaining to certain underlying inputs for climate projection data (provided on a one time basis): With the permission of Canadian Standards Association, (operating as “CSA Group”), 178 Rexdale Blvd., Toronto, ON, M9W 1R3, material is reproduced from CSA Group standard CSA C22.3 No. 1:25, Overhead systems. This material is not the complete and official position of CSA Group on the referenced subjects, which is represented solely by the Standard in its entirety. While use of the material has been authorized, CSA Group is not responsible for the manner in which the data is presented, nor for any representations and interpretations. No further reproduction is permitted. For more information or to purchase standard(s) from CSA Group, please visit store.csagroup.org or call 1-800-463-6727.
CONTACTS
Donald Lau | Zubin Panchal
Manager, Electricity Distribution | Senior Advisor, Electricity Distribution
Donald.Lau@oeb.ca | Zubin.Panchal@oeb.ca
Version History | Date
Version 1.0.0 | 2025-09-16

## Table of Contents
Ontario Energy Board Vulnerability Assessment & System Hardening (VASH) Toolkit - Table of Contents
Disclaimer
Contents
This file contains the following pages:
| Color | Tab Name | Description/Purpose
|  | Table of Contents | Contains a model overview and tab descriptions.
| Tab Link | VA Toolkit User Guide | The User Guide outlines the step-by-step methodology to employ the VA Toolkit model to analyze asset class and location vulnerability to climate perils. The example of reviewing the vulnerability of Class 3 poles in County 1 to high wind probabilities is provided as an illustrative example.
| Tab Link | Model Logic Diagrams | Provides high level and detailed logic and variable flow diagrams for the VA and BCA Toolkits.
| Tab Link | 1. LDC Asset Summary | Summarizes asset counts by analysis location. Locations with no assets of a specific class will have no vulnerability for that class regardless of climate projections. For locations and class combinations with higher vulnerability, an LDC may review its asset counts to understand the pervasiveness of the resiliency challenge.
| Tab Link | 2. Asset Class Failure Thresh | Characterizes the expected resilience of LDC assets identified in the Asset Summary to specific climate perils. Sub classes may be included to better estimate failure thresholds across a variety of perils. The total annual probability of failure is the summation of expected threshold exceedances across climate perils relevant to a particular asset class. LDCs may leverage design standards to quickly review vulnerability or refine failure thresholds with additional condition data of field equipment.
| Tab Link | 3. Climate Severity Calculator | Supports the development of tab '4. Climate Peril Probability'. Users may input chosen climate projections (from ECCC) to estimate annual probabilities of failure at different times in the future.
| Tab Link | 4. Climate Peril Probability | Projects the annual probability of specific events (relevant to assets in the Asset Summary) occurring at targeted grid locations through time. Climate perils and severity thresholds are linked to specific asset failure modes and thresholds. For example, wind gusts may be evaluated at 80, 100, and 120 kph as these relate to different class pole failures.
| Tab Link | 5. VA Heatmap | Categorizes vulnerability for each asset class in 5-year time intervals at a specified location by user-defined vulnerability bins. The annual probability of failures are summed across applicable climate perils based on asset class failure thresholds.
| Tab Link | 6. Generic BCA Inputs | User inputs that describe the unit costs related to asset failure (i.e., repair and replace costs). These costs should be those that scale with asset count. Project level costs such as administration should be entered in tab '7. Project Characteristics'.
| Tab Link | 7. Project Characteristics | User inputs that describe the characteristics of a single project associated with a single location. Users should use this tab to assess the benefits and costs of individual projects. See tab 'BCA Toolkit User Guide' for example project types.
| Tab Link | 8. Project BCA Results | Presents results of project BCA calculations based on inputs provided in tabs 1-7.
The following tabs contain intermediate calculations for the workbook to function and should not be edited.
| Color | Tab Name | Description/Purpose
|  | Calibration | Calculates calibration factor to ground modeled failures against actual observed failures. Calibration accounts for covariance of probability of failure associated with assets (e.g. similar assets in relatively close proximity)
Raw Climate Data
Int VA Calcs
Int BCA Costs
Int BCA Ann Fail Prob
Int BCA Ann Fail Costs
Int BCA Ann PWFC
Int BCA Ann PWVOLL
Indices
Key
User Input
Input from List (Dropdown)
Fixed Input
Calculated Value
Calculated Value
Linked Value
Model Result
The Vulnerability Assessment (VA) and Benefit-Cost Analysis (BCA) Toolkits—together forming the VASH Toolkit—are designed to support Local Distribution Companies (LDCs) in developing asset class- and location-specific climate vulnerability profiles. These vulnerabilities are expressed as the annual probability that a climate event will exceed an asset’s expected failure threshold. The toolkit streamlines the identification of vulnerable assets and locations and supports the evaluation of cost-effective mitigation measures that reduce resiliency risks while prioritizing customer value.
The toolkit illustrates a generic assessment methodology option compliant with OEB expectations for evaluation of resiliency risk, resulting in a heatmap that supports narrowing assets for further review and a summary of project benefit-cost results. Alternatively, LDCs can file a customized VA and BCA as part of their DSP, but it must adhere to principles outlined by the OEB. For this option, while the OEB does not prescribe a data source and LDCs may leverage data commensurate with their planning granularity and needs, the OEB does identify minimum criteria in Section 4.1 of the VASH Report.
The VA Toolkit (tabs 1-5) applies a climate projection to assess vulnerabilities using an asset-based approach by combining climate data, design standards, and asset location summaries. Inputs may be developed by LDCs using a variety of sources including the LDCs internal data, CSA guidelines, publicly available climate data, and proprietary climate data. The output provides a vulnerability heatmap that identifies areas for further investigation and investment prioritization.
The BCA Toolkit (tabs 6-8) is designed to support the evaluation of targeted system hardening projects at specific grid locations evaluated in the VA. The BCA Toolkit provides a generic framework for calculating the lifetime present value of benefits and costs of a project, a benefit-cost ratio (BCR), and the expected annual and lifetime reduction in customer minutes of interruption (CMI). Inputs are based on the utility's existing asset base, proposed replacement assets, projected costs, and criticality values derived from the DOE ICE calculator.
While this toolkit is a fully functioning model that may be used by LDCs, the onus remains on the LDCs to ensure accuracy of the data and results. It is also important to clarify that the use of the VASH Toolkit does not imply OEB endorsement of any specific investment decisions that may be supported by the toolkit’s outputs. The toolkit is intended to assist with planning and justification; however, any proposed investments remain subject to review and approval through the OEB’s adjudicative process, such as during a cost of service proceeding.
This example illustrates the application of the Toolkit to a hypothetical feeder sectionalization project aimed at reducing outage durations. It is provided solely to demonstrate Toolkit's functionality and does not imply regulatory support for the investment.
The Report does not constitute a recommendation on investment decisions nor does it provide investment advice. Guidehouse has not been requested to opine as to, and does not guarantee, warrant or opine upon: (i) any underlying business decision by a user to proceed (or not to proceed) with an investment ; or (ii) whether a proposed investment will be approved by the OEB. Any conclusion expressed in the Report should not amount to any form of guarantee that Guidehouse has determined or predicted future events or circumstances, and no such reliance may be inferred or implied.
Users should populate cells marked as 'User Input' based on the scheme shown below. All other cells are calculated by the model or given as fixed values.

## VA Toolkit User Guide
Ontario Energy Board Vulnerability Assessment Toolkit - User Guide
4. Climate Peril Probability
2. Asset Class Failure
Thresholds
5. Vulnerability Assessment Heatmap
The User Guide outlines the step-by-step methodology to employ the Vulnerability Assessment Toolkit model to analyze asset class and location vulnerability to climate perils. The example of reviewing the vulnerability of Class 3 poles in County 1 to high wind probabilities is provided as an illustrative example.
1. LDC Asset Summary
Step 1: Users should populate the Asset Summary with their installed asset base by location. Asset sub classes may be utilized to add granularity to failure thresholds. Additionally the counts of each asset class or sub class should be included as available. If actual counts are not available, populating with a "1" will ensure correct model calculations. Locations and classes for inclusion are based on user discretion. Generally, locations should be chosen based on likelihood of varying climate conditions and asset classes and sub classes based on variations in the expected weather event resilience of those technologies.
Example: The LDC populates the summary of their poles in Location 1 by Class. Based on the counts, the LDC is interested in the vulnerability of their most populous sub class, Class 3 poles, as it may represent greater risk.
Step 2: Users set up the Asset Class Failure Modes & Thresholds table to include the asset classes and sub classes identified in the Asset Summary process. Leveraging CSA guidelines, OEM design standards, or other engineering resources, asset classes and sub classes are assigned to climate perils, and severity thresholds that pose a threat to the equipment are determined. The unit basis of the climate peril identified should be included and referenced in the development of climate peril probabilities. The OEB notes that utilities may choose to rely upon the CSA Group’s published guidelines for technical standards as an input to the expected failure modes for assets.
Example: The LDC populates the provided table with the asset class and sub classes from Step 1. Wind (1 min gusts measured in kph) is determined to be the primary climate peril applicable to utility poles. Severity thresholds for wind are researched based on manufacturer specifications and populate the remainder of the table. The 150 Class 3 poles in Location 1 are designed to withstand 80 kph gusts.
Step 4: Users set up the Climate Peril Probability Model with the climate perils and severity thresholds identified in Step 2 as relevant to the asset summary at locations identified in Step 1. Leveraging Environment Canada data, CSA working documents, proprietary climate data, or other sources, the annual probability of occurrence is developed for a specific climate peril, severity threshold, location, and time period. Data for climate projections is highly variable, therefore, forecast time periods are discretionary and may be adjusted to match best available data. '3. Climate Severity Calculator' is provided to facilitate populating '4. Climate Peril Probability'. The OEB expects distributors to employ projection data rather than historical actuals to populate the climate peril probability inputs in VAs.
Example: The LDC populates the provided table with the climate perils and thresholds from Step 2 for each location from Step 1. The annual frequency of wind gusts in Location 1 at different thresholds is researched and populated in 5-year increments based on available data. As we know from Step 2, the 150 Class 3 poles in Location 1 are designed to withstand 80 kph gusts; which has a 0.8% annual probability of occurrence in 2025 but increases to a 1.6% annual probability of occurrence by 2050.
Step 5: The Vulnerability Assessment Heatmap will automatically populate after Step 3 is complete. Users may toggle the Location field to view each specified location in Step 1 individually to reveal differences in vulnerability based on the Asset Summary and Climate Peril Probability model. Additionally, users may designate cutoff points for vulnerability categories ranging from Low to High (annual probabilities above the "High" field with be labeled "Very High"). The Annual Probability Bins represent the low end of a probability range considered to be in the category. The resulting heatmap may be used to identify areas of system vulnerability for further research and/or prioritize asset classes and locations for investment review.
Example: The LDC sets the Location field to Location 1 and the Annual Probability Bins at 1%, 5%, and 10% (representing the risk of a 1/100-, 1/20-, and 1/10-year event respectively). The resulting analysis of Class 3 poles in Location 1 shows Low vulnerability (less than 1% per year in this example) until 2035 when the vulnerability becomes Medium (between 1% and 5% per year in this example). The LDC may choose to focus research effort and investment on hardening other locations or asset classes with greater risk and revisit Class 3 poles in Location 1 when developing a future DSP.
3. Climate Severity Calculator
Step 3: Users may leverage climate projections obtained from ECCC to estimate the annual probability of failures that their assets are exposed to. Using the Scenario Selection cells, each climate peril, severity threshold, and location to be populated in the following step (4. Climate Peril Probability) should be evaluated for its exceedance probability in 5-year increments. The results from the Annual Event Probability Projection cells may be copied as values directly into the following step ('4. Climate Peril Probability') to support input development. To maintain consistency with CSA/ECCC standards, the OEB recommends the use of RCP 8.5 for asset classes with expected useful lives less than 60 years and RCP 6.0 for expected useful lives greater than 60 years. However, the ultimate choice of scenario is at the discretion of the distributor, and so is the use of this calculator (i.e., LDCs do not have to leverage the Climate Severity Calculator if they can populate the Annual Event Probabilities for their assets of interest directly into the following step).
Example: The LDC The LDC populates the desired location, climate scenario, climate peril, and severity threshold. For the annual event probability projection to be developed. In this instance, under climate scenario RCP8.5 in Thedford, Wind being selected as a climate peril with a threshold of 100 kph (10-min avg.), the annual event probabilities range from 0.0190 to 0.0212 between 2023 and 2040

## VA Definitions
Ontario Energy Board Vulnerability Assessment Toolkit - Definitions
Term | Definition
Location | A point or an area associated with 1 or more assets. Locations are used to map asset classes to the specific probability of climate perils occurring. Definitions of locations are up to the discretion of the user, and can be chosen to be as granular or as coarse as needed to capture geographic variation in likelihood of climate conditions.
Asset Class | A type of asset, such as a pole or overhead conductor. Asset classes should be chosen to accurately differentiate between the weather event resilience of different assets.
Sub Class | A sub category of asset within an asset class. Sub classes may be used to further differentiate failure thresholds of different assets within a class; for example, to differentiate the resilience of different classes of pole to wind gusts.
Vulnerability | Vulnerability represents the probability that an asset (or group of assets) will fail given it is within the location of occurrence of one or more climate perils.
Risk | Risk quantifies the financial exposure of an asset or group of assets at a location, accounting for probability of failure in response to climate perils as well as criticality of failure (e.g., value of lost load).
Severity Threshold | Estimated point over which a given asset class would be expected to fail in response to a particular climate peril .
Estimated Useful Life (EUL) | The expected period during which an asset can operate efficiently, safely, and economically before it typically needs to be retired or replaced. Also referred to as "lifetime" in the VASH Report. Does not correspond to "End-of-Life", which refers to the lifetime of the asset at its failure.

## Model Logic Diagrams
Ontario Energy Board Vulnerability Assessment Toolkit - Model Logic Diagrams
Diagram 1: Vulnerability Assessment Toolkit Flow Diagram
Diagram 2: Benefit-Cost Analysis Toolkit Flow Diagram
Diagram 3: Avoided Repair and Replacement Benefit Calculation Flow Diagram
Diagram 4: Value of Lost Load Benefit Calculation Flow Diagram
Diagram 5: Project Cost Calculation Flow Diagram
This tab contains five (5) flow diagrams illustrating key model features and how variables interact to calculate project benefits and costs. Diagrams include: Vulnerability Assessment Toolkit flow, Benefit-Cost Analysis Toolkit flow, avoided repair and replacement benefit calculation, value of lost load benefit calculation, and project cost calculation.

## 1. LDC Asset Summary
Table 1: Asset Class Summary |  |  | Table 2: Asset Class and Sub-Class Locations and Counts
Asset Class | Unit Basis |  | Location | Asset Class | Sub Class | Count | Unit Basis
Pole | pole | ThedfordPoleClass 5 | Thedford | Pole | Class 5 | 50 | pole
|  | ThedfordPoleClass 4 | Thedford | Pole | Class 4 | 100 | pole
|  | ThedfordPoleClass 3 | Thedford | Pole | Class 3 | 150 | pole
|  | ThedfordPoleClass 2 | Thedford | Pole | Class 2 | 30 | pole
Users should populate Table 1 with the unique list of asset classes and their unit basis to be included in the assessment. Table 2 should be populated with the installed asset base by location. Asset sub classes may be utilized to add granularity to failure thresholds. Additionally the counts of each asset class or sub class should be included as available. If actual counts are not available, populating with a "1" will ensure correct model calculations. Locations and classes for inclusion are based on user discretion. Generally, locations should be chosen based on likelihood of varying climate conditions and asset classes and sub classes based on variations in the expected weather event resilience of those technologies. A single unit basis should be defined for each Asset Class (Columns C and B). This list should also contain potential replacement assets associated with projects to be defined in Tabs 6 and 7; for example, to describe a program that involves undergrounding of overhead conductors, an asset class of "Underground Conductor" should be included (e.g., with a count of 0, if none exist yet).

## 2. Asset Class Failure Thresh
Asset Class Failure Modes & Thresholds
Table 3: Climate Peril Summary |  | Table 4: Asset Class Failure Thresholds
Climate Peril | Unit Basis | Asset Class | Sub Class | Climate Peril | Severity Threshold | Unit Basis
Wind | kph (10-min avg.) | Pole | Class 5 | Wind | 80 | kph (10-min avg.)
|  | Pole | Class 4 | Wind | 85 | kph (10-min avg.)
|  | Pole | Class 3 | Wind | 100 | kph (10-min avg.)
|  | Pole | Class 2 | Wind | 115 | kph (10-min avg.)
Users populate Table 3 with the unique list of climate perils being assessed and the unit basis by which the severity of this peril will be considered. Table 4 should include the asset classes and sub classes identified in the Asset Summary tab and - leveraging CSA guidelines, OEM design standards, or other engineering resources - be assigned to climate perils, and severity thresholds that pose a threat to the equipment. The unit basis of the climate peril identified should be included and referenced in the development of climate peril probabilities. A single unit basis should be defined for each climate peril.

## 3. Climate Severity Calculator
Asset Sub-Class Probability of Failure Calculator Tool
Scenario Selection
| Location | Ailsa Craig
| Climate Scenario | RCP8.5
| Climate Peril | Wind
| Unit Basis | kph (10-min avg.)
| Severity Threshold | 85
Annual Event Probability Projection
| Climate Peril | Severity Threshold | Unit Basis | Location | 2023 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2055 | 2060 | 2065 | 2070 | 2075 | 2080 | 2085 | 2090 | 2095 | 2100
| Wind | 85 | kph (10-min avg.) | Ailsa Craig | 0.10145 | 0.10194 | 0.10243 | 0.10292 | 0.10308 | 0.10323 | 0.10395 | 0.10452 | 0.10592 | 0.10675 | 0.10831 | 0.10905 | 0.10978 | 0.11075 | 0.11173 | 0.11173 | 0.11173
Return Interval
| Location ID | Year | 10 | 20 | 2023: 50; 2025: 100; 2030: 200; 2035: Estimated Failure Threshold; 2040: Lower Wind Speed; 2045: Upper Wind Speed; 2050: Lower Return Period; 2055: Upper Return Period; 2060: Annual Probability of Failure
Ailsa CraigWind2023RCP8.5 | Ailsa Craig | 2023 | 85.5352 | 92.2975 | 2023: 99.4602; 2025: 106.5797; 2030: 113.7086; 2035: 85; 2040: 0; 2045: 85.5352; 2050: 1; 2055: 10; 2060: 0.10145
Ailsa CraigWind2025RCP8.5 | Ailsa Craig | 2025 | 85.7157 | 92.5344 | 2023: 99.7705; 2025: 106.9537; 2030: 114.148; 2035: 85; 2040: 0; 2045: 85.7157; 2050: 1; 2055: 10; 2060: 0.10194
Ailsa CraigWind2030RCP8.5 | Ailsa Craig | 2030 | 85.8962 | 92.7714 | 2023: 100.0809; 2025: 107.3277; 2030: 114.5875; 2035: 85; 2040: 0; 2045: 85.8962; 2050: 1; 2055: 10; 2060: 0.10243
Ailsa CraigWind2035RCP8.5 | Ailsa Craig | 2035 | 86.0768 | 93.0084 | 2023: 100.3912; 2025: 107.7017; 2030: 115.0269; 2035: 85; 2040: 0; 2045: 86.0768; 2050: 1; 2055: 10; 2060: 0.10292
Ailsa CraigWind2040RCP8.5 | Ailsa Craig | 2040 | 86.1332 | 93.0782 | 2023: 100.4794; 2025: 107.8031; 2030: 115.1386; 2035: 85; 2040: 0; 2045: 86.1332; 2050: 1; 2055: 10; 2060: 0.10308
Ailsa CraigWind2045RCP8.5 | Ailsa Craig | 2045 | 86.1896 | 93.1481 | 2023: 100.5676; 2025: 107.9044; 2030: 115.2504; 2035: 85; 2040: 0; 2045: 86.1896; 2050: 1; 2055: 10; 2060: 0.10323
Ailsa CraigWind2050RCP8.5 | Ailsa Craig | 2050 | 86.4547 | 93.4975 | 2023: 101.0217; 2025: 108.4462; 2030: 115.8834; 2035: 85; 2040: 0; 2045: 86.4547; 2050: 1; 2055: 10; 2060: 0.10395
Ailsa CraigWind2055RCP8.5 | Ailsa Craig | 2055 | 86.6635 | 93.777 | 2023: 101.3875; 2025: 108.8866; 2030: 116.4048; 2035: 85; 2040: 0; 2045: 86.6635; 2050: 1; 2055: 10; 2060: 0.10452
Ailsa CraigWind2060RCP8.5 | Ailsa Craig | 2060 | 87.1768 | 94.421 | 2023: 102.1879; 2025: 109.8269; 2030: 117.4885; 2035: 85; 2040: 0; 2045: 87.1768; 2050: 1; 2055: 10; 2060: 0.10592
Ailsa CraigWind2065RCP8.5 | Ailsa Craig | 2065 | 87.4815 | 94.7856 | 2023: 102.6223; 2025: 110.3267; 2030: 118.0508; 2035: 85; 2040: 0; 2045: 87.4815; 2050: 1; 2055: 10; 2060: 0.10675
Ailsa CraigWind2070RCP8.5 | Ailsa Craig | 2070 | 88.0541 | 95.5026 | 2023: 103.5207; 2025: 111.3788; 2030: 119.2611; 2035: 85; 2040: 0; 2045: 88.0541; 2050: 1; 2055: 10; 2060: 0.10831
Ailsa CraigWind2075RCP8.5 | Ailsa Craig | 2075 | 88.322 | 95.855 | 2023: 103.9845; 2025: 111.9311; 2030: 119.9091; 2035: 85; 2040: 0; 2045: 88.322; 2050: 1; 2055: 10; 2060: 0.10905
Ailsa CraigWind2080RCP8.5 | Ailsa Craig | 2080 | 88.59 | 96.2074 | 2023: 104.4484; 2025: 112.4833; 2030: 120.5571; 2035: 85; 2040: 0; 2045: 88.59; 2050: 1; 2055: 10; 2060: 0.10978
Ailsa CraigWind2085RCP8.5 | Ailsa Craig | 2085 | 88.9454 | 96.6585 | 2023: 105.0217; 2025: 113.1649; 2030: 121.3447; 2035: 85; 2040: 0; 2045: 88.9454; 2050: 1; 2055: 10; 2060: 0.11075
Ailsa CraigWind2090RCP8.5 | Ailsa Craig | 2090 | 89.3008 | 97.1097 | 2023: 105.595; 2025: 113.8465; 2030: 122.1323; 2035: 85; 2040: 0; 2045: 89.3008; 2050: 1; 2055: 10; 2060: 0.11173
Ailsa CraigWind2095RCP8.5 | Ailsa Craig | 2095 | 89.3008 | 97.1097 | 2023: 105.595; 2025: 113.8465; 2030: 122.1323; 2035: 85; 2040: 0; 2045: 89.3008; 2050: 1; 2055: 10; 2060: 0.11173
Ailsa CraigWind2100RCP8.5 | Ailsa Craig | 2100 | 89.3008 | 97.1097 | 2023: 105.595; 2025: 113.8465; 2030: 122.1323; 2035: 85; 2040: 0; 2045: 89.3008; 2050: 1; 2055: 10; 2060: 0.11173
Source: Table I.4, CSA C22.3 No. 1:25, Overhead systems. © 2025 Canadian Standards Association. Please visit store.csagroup.org CSA and ECCC data analysis (OEB 2025)
|  |  | 0.005 | 0.01 | 2023: 0.02; 2025: 0.05; 2030: 0.1
|  | Wind | 114.148 | 106.9537 | 2023: 99.7705; 2025: 92.5344; 2030: 85.7157
|  | Estimated Failure Threshold | 85 | 85 | 2023: 85; 2025: 85; 2030: 85
Users may leverage climate projections obtained from ECCC to estimate the annual probability of failures that their assets are exposed to. Using the Scenario Selection cells below: each climate peril, severity threshold, and location to be populated in '4. Climate Peril Probability' should be evaluated for its exceedance probability in 5-year increments. The results from the Annual Event Probability Projection cells (G18:W18) may be copied as values directly into columns G:W in '4. Climate Peril Probability' to support input development.
To maintain consistency with CSA/ECCC standards, the OEB recommends the use of RCP 8.5 for asset classes with expected useful lives less than 60 years and RCP 6.0 for expected useful lives greater than 60 years. However, the ultimate choice of scenario is at the discretion of the distributor.

## 4. Climate Peril Probability
Climate Peril Probability Model
Table 5: Climate Peril Probability Projections
Annual Event Probability Forecast
| Climate Peril | Severity Threshold | Unit Basis | Location | 2023 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2055 | 2060 | 2065 | 2070 | 2075 | 2080 | 2085 | 2090 | 2095 | 2100
ThedfordWind110 | Wind | 110 | kph (10-min avg.) | Thedford | 0.0071709 | 0.0074565 | 0.007748 | 0.0080455 | 0.0081254 | 0.0082059 | 0.0086518 | 0.0090244 | 0.0098446 | 0.010298 | 0.011293 | 0.011835 | 0.012389 | 0.013092 | 0.013814 | 0.013814 | 0.013814
ThedfordWind100 | Wind | 100 | kph (10-min avg.) | Thedford | 0.018976 | 0.019562 | 0.020204 | 0.020995 | 0.021223 | 0.021452 | 0.02265 | 0.023636 | 0.02589 | 0.027176 | 0.029906 | 0.031338 | 0.032797 | 0.034672 | 0.036595 | 0.036595 | 0.036595
ThedfordWind85 | Wind | 85 | kph (10-min avg.) | Thedford | 0.10145 | 0.10194 | 0.10243 | 0.10292 | 0.10308 | 0.10323 | 0.10395 | 0.10452 | 0.10592 | 0.10675 | 0.10831 | 0.10905 | 0.10978 | 0.11075 | 0.11173 | 0.11173 | 0.11173
ThedfordWind80 | Wind | 80 | kph (10-min avg.) | Thedford | 0.11607 | 0.1166 | 0.11712 | 0.11765 | 0.11782 | 0.11798 | 0.11876 | 0.11937 | 0.12087 | 0.12176 | 0.12344 | 0.12423 | 0.12502 | 0.12606 | 0.1271 | 0.1271 | 0.1271
Users should populate Table 5 with the climate perils and severity thresholds identified in Tab 2 as relevant to the asset summary at locations identified in Tab 1. Leveraging Environment Canada data, CSA working documents, proprietary climate data, or other sources, the annual probability of occurrence is developed for a specific climate peril, severity threshold, location, and time period. Tab '3. Climate Severity Calculator' is available to support generic option input development using ECCC data. This table should include every unique combination of Climate Peril and severity threshold as defined in Tab 2, for each Location of interest.

## 5. VA Heatmap
Vulnerability Heatmap
[19 empty] | Annual Probability Bin Examples |  | List of Locations
[19 empty] | Bin | Definition | Thedford
[19 empty] | 0.01 | 1-in-100 year event
[19 empty] | 0.02 | 1-in-50 year event
[19 empty] | 0.05 | 1-in-20 year event
[19 empty] | 0.1 | 1-in-10 year event
[19 empty] | 0.2 | 1-in-5 year event
| Location |  | Thedford
|  |  | Low | Medium | High | Very High
| Annual Probability Bin |  | 0.02 | 0.1 | 0.2 | >0.2
Asset Vulnerability Heatmap
| Asset Class | Sub Class | 2025 | 2030 | 2035 | 2040 | 2045 | 2040 | 2055 | 2060 | 2065 | 2070 | 2075 | 2080 | 2085 | 2090 | 2095 | 2100 | Heat Map | Bin
ThedfordPoleClass 5 | Pole | Class 5 | 0.1166 | 0.11712 | 0.11765 | 0.11782 | 0.11798 | 0.11876 | 0.11937 | 0.12087 | 0.12176 | 0.12344 | 0.12423 | 0.12502 | 0.12606 | 0.1271 | 0.1271 | 0.1271 |  | Low
ThedfordPoleClass 4 | Pole | Class 4 | 0.10194 | 0.10243 | 0.10292 | 0.10308 | 0.10323 | 0.10395 | 0.10452 | 0.10592 | 0.10675 | 0.10831 | 0.10905 | 0.10978 | 0.11075 | 0.11173 | 0.11173 | 0.11173 |  | Medium
ThedfordPoleClass 3 | Pole | Class 3 | 0.019562 | 0.020204 | 0.020995 | 0.021223 | 0.021452 | 0.02265 | 0.023636 | 0.02589 | 0.027176 | 0.029906 | 0.031338 | 0.032797 | 0.034672 | 0.036595 | 0.036595 | 0.036595 |  | High
ThedfordPoleClass 2 | Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Very High
N/A
The Vulnerability Assessment Heatmap will automatically populate after Tabs 1, 2 and 4 are complete. Users may toggle the Location field to view each user-specified location in Tab 1 individually to reveal differences in vulnerability based on the Asset Summary and Climate Peril Probability model. Additionally, users may designate cutoff points for vulnerability categories ranging from Low to High (annual probabilities above the "High" field with be labeled "Very High"). The Annual Probability Bins represent the low end of a probability range considered to be in the category. The resulting heatmap may be used to identify areas of system vulnerability for further research and/or prioritize asset classes and locations for investment review. Values populating the heatmap cells are the annual probability that a climate peril exceeds the specified asset class' failure thresholds at the specified location. A higher value implies increased vulnerabiltiy. Although applicants may adjust vulnerability bin thresholds to fit their needs, the OEB has suggested standard bins: Low < 2%, Medium < 10%, High < 20%, and Very High > 20%.

## 6. Generic BCA Inputs
Generic BCA Inputs
Table 5: Asset Repair and Replace Costs
| Asset Class | Asset Sub-Class | Unit Basis | Unit | Cost Data Year | Repair Cost | Replace Cost | Replace %
PoleClass 5 | Pole | Class 5 | pole | $/unit | 2025 | 500 | 4000 | 50%
PoleClass 4 | Pole | Class 4 | pole | $/unit | 2025 | 500 | 4400 | 50%
PoleClass 3 | Pole | Class 3 | pole | $/unit | 2025 | 500 | 4840 | 50%
PoleClass 2 | Pole | Class 2 | pole | $/unit | 2025 | 500 | 5324 | 50%
TBD BCA inputs used across projects
In Table 5 users should input the expected costs to repair and replace equipment for the asset classes and sub-classes populated from the VA. Repair and replace costs should represent all capital cost incurred by the utility when addressing asset failures (i.e., equipment cost, labor, etc.) but should only include costs that scale on a per asset basis. Other costs, such as project administration and OM&A, should be included in '7. Project Characteristics'. The repair and replace values may be used across evaluated projects and will derive project budgets and BCA costs.
Additionally, the expected replacement percent should be estimated based on the climate perils and failure thresholds incorporated into the VA. For example, if a specific replacement failure threshold (e.g., from CSA guidelines) was used to analyze vulnerability, this should be set to 100%. If a threshold based on historic asset class outages was used, an estimate of actual repair versus replace expectations may be appropriate. Note that all failures will cause a customer interruption in the model with the replace and repair percentages aligning the capital costs of those failures to LDC experience.

## 7. Project Characteristics
Project Characteristics
Table 6: Project Characteristics
Project Type Inputs
|  |  | Location |  | Thedford
|  |  | Project Type |  | Retrofit
|  |  | Impact Type |  | Criticality
Table 7: Project Economic Variables
|  |  | Variable | Unit | Value
|  |  | Inflation | % | 2%
|  |  | Nominal Utility Discount Rate (WACC) | % | 7%
|  |  | Social Discount Rate | % | 4%
|  |  | Baseline OM&A Cost (% of Total Costs) | % | 1.5%
|  |  | Scenario OM&A Cost (% of Total Costs) | % | 1.5%
|  |  | Tax Rate | % | 26.5%
|  |  | Incremental Project Non-Asset Costs | $ | 250000
Table 8: Project Lifetime Variables
|  |  | Variable | Unit | Value
|  |  | Project Start Year | year | 2026
|  |  | Project Expected Lifetime1 | years | 40
|  |  | Starting Asset's Remaining Useful Lifetime2 | years | 10
1EUL should not exceed 75
2RUL only required for the early retirement program type.
Table 9: Criticality Variables
|  |  | Variable | Unit | Baseline Value | Project Value
|  |  | Average Outage Duration | minutes | 120 | 120
|  |  | Estimated Customers Interrupted (Res) | count | 100 | 70
|  |  | Estimated Customers Interrupted (Small C&I) | count | 5 | 5
|  |  | Estimated Customers Interrupted (Med/Large C&I) | count | 1 | 0
|  |  | Value of Lost Load (VOLL) | $/Outage Event | 17961 | 4468
|  |  | Calibration Year | year | 2025 | N/A
|  |  | Historic Annual Outage Events2 | Count | 2.2 | N/A
2These outages should reflect those caused by the climate perils addressed in this risk analysis. Inclusion of historic outages from other causes will inflate results.
Table 10: Applicable Assets
|  |  | Existing Assets |  |  | Standard Assets |  |  | Replacement Assets |  |  |  | Project Budget | Cost for BCA
Existing | Standard | Replace | Asset Class | Asset Sub-Class | Unit Basis | Code Asset Class | Code Asset Sub-Class | Baseline Count | Replacement Asset Class | Replacement Asset Sub-Class | Project Count | Unit Basis | Budget ($) | BCA Cost ($)
PoleClass 5 |  |  | Pole | Class 5 | pole
PoleClass 4 | PoleClass 4 | PoleClass 4 | Pole | Class 4 | pole | Pole | Class 4 | 100 | Pole | Class 4 | 100 | pole | 0 | 0
PoleClass 3 |  |  | Pole | Class 3 | pole
PoleClass 2 |  |  | Pole | Class 2 | pole
Users should develop project characteristics that accurately reflect a potential VASH investment opportunity. The toolkit is designed to evaluate one project at a time based on the comprehensive VA.
Table 6: Project Characteristics:
The project location is predetermined based on the location being viewed in '5. VA Heatmap'. This location should reflect the region in which the project being evaluated will be implemented by choosing the closest location with climate data. There are three Project Type options based on the status of the LDC's existing assets. End-of-Life should be selected if the project will replace assets that would have been replaced in the absence of resiliency planning due to age or condition. Early Retirement should be selected if the project will replace assets that would have been expected to remain in service beyond the start date of the project. Retrofit should be selected if the project will not impact existing assets (e.g., sectionalizing or back-up generation).
There are three Impact Type Options based on the mitigation goal of the project. Frequency should be selected if the project increases the robustness of assets to climate perils (i.e., changes the expected failure threshold) but does not impact the duration or number of customers impacted by remaining outages at that location. Criticality should be selected if the project reduces the expected outage durations and/or number of customers impacted by an outage but does not reduce the expected frequency of these events. Both should be selected if the project will reduce the frequency and criticality of outages.
Table 7: Project Economic Variables:
Users should input an estimate for common economic analysis variables. Inflation is the expected annual inflation rate for the duration of the project lifetime. The nominal utility discount rate (WACC) is the rate used for present value calculations of utility costs. The societal discount rate is the rate used for customer impact present value calculations (given by IESO at 4%). Baseline OM&A Cost (% of Total Costs) represent the percent of total asset base costs attributable to OM&A. Scenario OM&A Cost (% of Total Costs) represent the percent of total asset scenario costs attributable to OM&A. The tax rate is the combined federal plus provincial tax rate. Project non-asset costs, which are one-time costs that do not scale by the number of assets in the project, must be added to the total asset costs to estimate the full cost of a system hardening project. Examples of these costs include engineering expenses, administrative fees, overhead burden, and any other measurable changes in costs incurred that are attributable to the implementation of the system hardening project.
Table 8: Project Lifetime Variables:
Resiliency investments mitigate risk for the lifetime of installed assets and therefore the lifetime benefits of a project should be analyzed. Users should input the project start year and an estimate for the expected lifetime of the project. Project lifetimes are the expected field life of the assets being invested in. If multiple asset classes are included in the project, a weighted average lifetime may be used. A remaining useful life (RUL) for Existing Assets is required for early retirement projects. This should be the expected number of years that these assets would have continued to be in service in the absence of the resiliency project. This field will be blurred for other Project Types.
Table 9: Criticality Variables:
The BCA Toolkit is designed to leverage per outage event value of lost load (VOLL) estimates for the area impacted by a project. To develop these values using the ICE Calculator, as accepted in the Generic BCA Option, the expected outage duration and number of customers interrupted for three customer classes is required. These values may be input into the ICE Calculator to yield the VOLL in $/outage event. See the BCA Toolkit User Guide for guidance on leveraging the ICE Calculator do develop these inputs. A baseline value is necessary for all Project Types. This scenario's inputs should reflect historical values for outage durations and number of customers impacted for the climate perils that the project will address. For Frequency Impact Type projects, the Project Value should Equal the Baseline Value as there is no change in the criticality of remaining outages after project implementation. For Criticality and Both Project Types, the resulting duration and customer counts should be input into the ICE Calculator as a separate scenario to determine the post-project implementation VOLL. The OEB proposes an acceptable starting point ICE composite value including input variables from the following states: New York, Michigan, Ohio, and Iowa. However, a distributor may choose any single or combination of states as a starting point based on comparability to its territory.
An estimate of the count of historic annual outages for the project location and climate perils addressed should be developed. Counts should be as granular as possible, however, a 5-year average for an applicable feeder, substation, or section is appropriate. If no historic outages tied to cause codes related to the targeted climate peril for mitigation exist for the project location but the VA suggests that a project may be prudent, the system average annual historic outage frequency from these perils may be applied.
Table 10: Applicable Assets:
Users should identify the Existing Asset classes prepopulated from the VA that are relevant to the project being evaluated. Users should then populate the Replacement Assets fields with the asset class, sub-class, and total count of assets in the proposed project. If the Standard asset sub-class is different from the Existing Assets due to a codes/standards change during the Existing Assets' lifetime, users should fill the Standard Assets with what would have been used in the absence of the resiliency investment. If there has not been a change, fill in the Standard Assets with the same sub-class as the Existing Assets. The baseline count should align with the Existing and Standard Assets' unit basis and the project count should align with the Replacement Assets' unit basis (e.g., an undergrounding program Existing may be per pole and the Replacement may be per km).
The total project budget and BCA cost will calculate automatically. Note that the BCA cost will differ from project budget based on the Project Type selected in the Project Characteristics and the adjustment to the present value of customer revenue requirement. For End-of-life and Early Retirement projects, the model will expect to see a change in asset class for project-applicable assets and an appropriate count. For retrofit projects AND projects that are Criticality only, Replacement Assets and counts should equal the Starting Assets that are considered in the development of the historic customer outage estimate. Note: Retrofit AND Criticality only projects will have $0 budget and BCA cost regardless of the asset counts (i.e., the entire project budget is considered in the Incremental Project Non-Asset Costs).

## 8. Project BCA Results
Project BCA Results
Project Summary Metrics
Metric | Unit | Expected Value
Total PV Benefits from Avoided Repairs and Replacements | PV 2026$ | 0
Total PV Benefits from Frequency Reductions (VOLL) | PV 2026$ | 0
Total PV Benefits from Criticality Reductions (VOLL) | PV 2026$ | 541532.5576
Total PV Costs | PV 2026$ | 370595.1716
BCR | ratio | 1.4613
Expected Annual Average CMI Reduction1 | CMI | 8337.9648
Expected Lifetime CMI Reduction | CMI | 333518.5917
1Simple average over project lifetime.
Project BCA results are automatically calculated based of the inputs in each of the previous model tabs. Benefits are provided based on three primary categories: avoided repair and replace costs, VOLL from reductions in outage frequency, and VOLL from reductions in outage criticality. It is common for some benefit categories to be $0 based on project characteristics. A benefit-cost ratio (BCR) greater than 1.0 indicates that the present value of lifecycle benefits of the project being evaluated is greater than the upfront incremental costs of that program. The estimated annual and lifetime reductions in customer minutes of interruption (CMI) for the project is also provided.

## Calibration
Project Scenario PV Benefits |  | Repair/Replace Risk |  | Risk VOLL from Outage Frequency |  | Risk VOLL from Outage Criticality |  | Annual event Theta for Calibration
Asset Class | Asset Sub-Class | Baseline | Project | Baseline | Project | Baseline | Project | Asset Class | Asset Sub-Class | Baseline | Scenario |  | Total Modeled Event Probability | Theta | RUL for Model
Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 |  | Baseline | 10.1941 | 0.21581 | 0
Pole | Class 4 | 550513.4688 | 550513.4688 | 720852.7582 | 720852.7582 | 720852.7582 | 179320.2006 | Pole | Class 4 | 10.1941 |  | Primary Scenario |  | N/A
Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0 |  | Low |  | N/A
Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 0 |  | High |  | N/A
Calculates the calibration multiplier based on historic annual outage input and a sum over the modeled asset failures in the calibration year. RUL for model is used to automatically zero out the RUL for end-of-life and retrofit project types. The PV benefit streams are summarized for incorporation into final outputs.

## Climate Data
Climate Data
Return Interval
| Location ID | Climate Peril | Scenario | Year | 10 | 20 | 50 | 100 | 200 | Location List
Ailsa CraigIce Accretion2023RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425 | Ailsa Craig
Ailsa CraigIce Accretion2025RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2025 | 17.1352 | 20.5563 | 24.8625 | 28.1605 | 31.4423 | Ajax
Ailsa CraigIce Accretion2030RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2030 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542 | Alexandria
Ailsa CraigIce Accretion2035RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2035 | 17.17 | 20.6255 | 24.9875 | 28.3206 | 31.6418 | Alliston
Ailsa CraigIce Accretion2040RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2040 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415 | Almonte
Ailsa CraigIce Accretion2045RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2045 | 17.2048 | 20.6947 | 25.1125 | 28.4807 | 31.8412 | Armstrong
Ailsa CraigIce Accretion2050RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2050 | 17.1526 | 20.6794 | 25.145 | 28.5438 | 31.941 | Arnprior
Ailsa CraigIce Accretion2055RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2055 | 17.083 | 20.6296 | 25.115 | 28.5268 | 31.941 | Atikokan
Ailsa CraigIce Accretion2060RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2060 | 17.0134 | 20.5799 | 25.085 | 28.5099 | 31.941 | Attawapiskat
Ailsa CraigIce Accretion2065RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2065 | 16.9439 | 20.53 | 25.055 | 28.4929 | 31.941 | Aurora
Ailsa CraigIce Accretion2070RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2070 | 16.8743 | 20.4802 | 25.025 | 28.476 | 31.941 | Bancroft
Ailsa CraigIce Accretion2075RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2075 | 16.8424 | 20.4664 | 25.0375 | 28.5042 | 31.9883 | Barrie
Ailsa CraigIce Accretion2080RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2080 | 16.8105 | 20.4526 | 25.05 | 28.5325 | 32.0355 | Barriefield
Ailsa CraigIce Accretion2085RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2085 | 16.7786 | 20.4387 | 25.0625 | 28.5607 | 32.0827 | Beaverton
Ailsa CraigIce Accretion2090RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2090 | 16.7467 | 20.4249 | 25.075 | 28.589 | 32.13 | Belleville
Ailsa CraigIce Accretion2095RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2095 | 16.7148 | 20.4111 | 25.0875 | 28.6172 | 32.1773 | Belmont
Ailsa CraigIce Accretion2100RCP4.5 | Ailsa Craig | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.3972 | 25.1 | 28.6455 | 32.2245 | Bowmanville
Ailsa CraigIce Accretion2023RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425 | Bracebridge
Ailsa CraigIce Accretion2025RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2025 | 17.1352 | 20.5563 | 24.8625 | 28.1605 | 31.4423 | Bradford
Ailsa CraigIce Accretion2030RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2030 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542 | Brampton
Ailsa CraigIce Accretion2035RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2035 | 17.17 | 20.6255 | 24.9875 | 28.3206 | 31.6418 | Brantford
Ailsa CraigIce Accretion2040RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2040 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415 | Brighton
Ailsa CraigIce Accretion2045RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2045 | 17.2048 | 20.6947 | 25.1125 | 28.4807 | 31.8412 | Brockville
Ailsa CraigIce Accretion2050RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2050 | 17.1526 | 20.6794 | 25.145 | 28.5438 | 31.941 | Burk's Falls
Ailsa CraigIce Accretion2055RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2055 | 17.083 | 20.6296 | 25.115 | 28.5268 | 31.941 | Burlington
Ailsa CraigIce Accretion2060RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2060 | 17.0134 | 20.5799 | 25.085 | 28.5099 | 31.941 | CFB Borden
Ailsa CraigIce Accretion2065RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2065 | 16.9439 | 20.53 | 25.055 | 28.4929 | 31.941 | Cambridge
Ailsa CraigIce Accretion2070RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2070 | 16.8743 | 20.4802 | 25.025 | 28.476 | 31.941 | Campbellford
Ailsa CraigIce Accretion2075RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2075 | 16.8264 | 20.4595 | 25.0437 | 28.5184 | 32.0119 | Cannington
Ailsa CraigIce Accretion2080RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2080 | 16.7786 | 20.4387 | 25.0625 | 28.5607 | 32.0827 | Carleton Place
Ailsa CraigIce Accretion2085RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2085 | 16.7308 | 20.418 | 25.0813 | 28.6031 | 32.1536 | Cavan
Ailsa CraigIce Accretion2090RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2090 | 16.4742 | 20.1898 | 24.8833 | 28.4289 | 31.9935 | Centralia
Ailsa CraigIce Accretion2095RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2095 | 16.2654 | 19.9822 | 24.6667 | 28.2123 | 31.7625 | Chapleau
Ailsa CraigIce Accretion2100RCP6.0 | Ailsa Craig | Ice Accretion | RCP6.0 | 2100 | 16.0566 | 19.7747 | 24.45 | 27.9957 | 31.5315 | Chatham
Ailsa CraigIce Accretion2023RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425 | Chesley
Ailsa CraigIce Accretion2025RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2025 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542 | Clinton
Ailsa CraigIce Accretion2030RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2030 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415 | Coboconk
Ailsa CraigIce Accretion2035RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2035 | 17.2222 | 20.7293 | 25.175 | 28.5607 | 31.941 | Cobourg
Ailsa CraigIce Accretion2040RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2040 | 17.1062 | 20.6462 | 25.125 | 28.5325 | 31.941 | Cochrane
Ailsa CraigIce Accretion2045RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2045 | 16.9902 | 20.5633 | 25.075 | 28.5042 | 31.941 | Colborne
Ailsa CraigIce Accretion2050RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2050 | 16.8105 | 20.4526 | 25.05 | 28.5325 | 32.0355 | Collingwood
Ailsa CraigIce Accretion2055RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2055 | 16.7467 | 20.4249 | 25.075 | 28.589 | 32.13 | Cornwall
Ailsa CraigIce Accretion2060RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2060 | 16.4742 | 20.1898 | 24.8833 | 28.4289 | 31.9935 | Corunna
Ailsa CraigIce Accretion2065RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2065 | 16.2654 | 19.9822 | 24.6667 | 28.2123 | 31.7625 | Deep River
Ailsa CraigIce Accretion2070RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2070 | 15.6797 | 19.3528 | 23.975 | 27.4778 | 30.9645 | Deseronto
Ailsa CraigIce Accretion2075RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2075 | 15.3028 | 18.9309 | 23.5 | 26.9599 | 30.3975 | Dorchester
Ailsa CraigIce Accretion2080RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2080 | 14.9259 | 18.509 | 23.025 | 26.442 | 29.8305 | Dorion
Ailsa CraigIce Accretion2085RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2085 | 14.1431 | 17.5856 | 21.925 | 25.2131 | 28.476 | Dresden
Ailsa CraigIce Accretion2090RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2090 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215 | Dryden
Ailsa CraigIce Accretion2095RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2095 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215 | Dundalk
Ailsa CraigIce Accretion2100RCP8.5 | Ailsa Craig | Ice Accretion | RCP8.5 | 2100 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215 | Dunnville
Ailsa CraigWind2023RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086 | Durham
Ailsa CraigWind2025RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283 | Dutton
Ailsa CraigWind2030RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148 | Earlton
Ailsa CraigWind2035RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678 | Edison
Ailsa CraigWind2040RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875 | Elliot Lake
Ailsa CraigWind2045RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072 | Elmvale
Ailsa CraigWind2050RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939 | Embro
Ailsa CraigWind2055RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161 | Englehart
Ailsa CraigWind2060RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228 | Espanola
Ailsa CraigWind2065RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295 | Etobicoke
Ailsa CraigWind2070RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621 | Exeter
Ailsa CraigWind2075RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2075 | 86.3504 | 93.3577 | 100.8387 | 108.226 | 115.6228 | Fenelon Falls
Ailsa CraigWind2080RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2080 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834 | Fergus
Ailsa CraigWind2085RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2085 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441 | Forest
Ailsa CraigWind2090RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2090 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048 | Fort Erie
Ailsa CraigWind2095RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2095 | 86.7678 | 93.9167 | 101.5705 | 109.1068 | 116.6655 | Fort Erie (Ridgeway)
Ailsa CraigWind2100RCP4.5 | Ailsa Craig | Wind | RCP4.5 | 2100 | 86.8722 | 94.0565 | 101.7534 | 109.327 | 116.9262 | Fort Frances
Ailsa CraigWind2023RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086 | Gananoque
Ailsa CraigWind2025RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283 | Geraldton
Ailsa CraigWind2030RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148 | Glencoe
Ailsa CraigWind2035RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678 | Goderich
Ailsa CraigWind2040RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875 | Gore Bay
Ailsa CraigWind2045RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072 | Graham
Ailsa CraigWind2050RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939 | Gravenhurst (Muskoka Airport)
Ailsa CraigWind2055RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161 | Grimsby
Ailsa CraigWind2060RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228 | Guelph
Ailsa CraigWind2065RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295 | Guthrie
Ailsa CraigWind2070RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621 | Haileybury
Ailsa CraigWind2075RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2075 | 86.4026 | 93.4276 | 100.9302 | 108.3361 | 115.7531 | Haldimand (Caledonia)
Ailsa CraigWind2080RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2080 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441 | Haldimand (Hagersville)
Ailsa CraigWind2085RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2085 | 86.7157 | 93.8469 | 101.479 | 108.9967 | 116.5351 | Haliburton
Ailsa CraigWind2090RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2090 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885 | Halton Hills (Georgetown)
Ailsa CraigWind2095RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2095 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508 | Hamilton
Ailsa CraigWind2100RCP6.0 | Ailsa Craig | Wind | RCP6.0 | 2100 | 87.7861 | 95.1502 | 103.0568 | 110.8265 | 118.6131 | Hanover
Ailsa CraigWind2023RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086 | Hastings
Ailsa CraigWind2025RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2025 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148 | Hawkesbury
Ailsa CraigWind2030RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2030 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875 | Hearst
Ailsa CraigWind2035RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2035 | 86.0768 | 93.0084 | 100.3912 | 107.7017 | 115.0269 | Honey Harbour
Ailsa CraigWind2040RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2040 | 86.1332 | 93.0782 | 100.4794 | 107.8031 | 115.1386 | Hornepayne
Ailsa CraigWind2045RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2045 | 86.1896 | 93.1481 | 100.5676 | 107.9044 | 115.2504 | Huntsville
Ailsa CraigWind2050RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2050 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834 | Ingersoll
Ailsa CraigWind2055RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2055 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048 | Iroquois Falls
Ailsa CraigWind2060RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2060 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885 | Jellicoe
Ailsa CraigWind2065RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2065 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508 | Kapuskasing
Ailsa CraigWind2070RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2070 | 88.0541 | 95.5026 | 103.5207 | 111.3788 | 119.2611 | Kemptville
Ailsa CraigWind2075RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2075 | 88.322 | 95.855 | 103.9845 | 111.9311 | 119.9091 | Kenora
Ailsa CraigWind2080RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2080 | 88.59 | 96.2074 | 104.4484 | 112.4833 | 120.5571 | Killaloe
Ailsa CraigWind2085RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2085 | 88.9454 | 96.6585 | 105.0217 | 113.1649 | 121.3447 | Kincardine
Ailsa CraigWind2090RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2090 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323 | Kingston
Ailsa CraigWind2095RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2095 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323 | Kinmount
Ailsa CraigWind2100RCP8.5 | Ailsa Craig | Wind | RCP8.5 | 2100 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323 | Kirkland Lake
AjaxIce Accretion2023RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185 | Kitchener
AjaxIce Accretion2025RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218 | Kitchenuhmaykoosib
AjaxIce Accretion2030RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585 | Lakefield
AjaxIce Accretion2035RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952 | Lansdowne House
AjaxIce Accretion2040RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332 | Leamington
AjaxIce Accretion2045RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687 | Lindsay
AjaxIce Accretion2050RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122 | Lion's Head
AjaxIce Accretion2055RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385 | Listowel
AjaxIce Accretion2060RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555 | London
AjaxIce Accretion2065RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715 | Lucan
AjaxIce Accretion2070RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988 | Maitland
AjaxIce Accretion2075RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195 | Markdale
AjaxIce Accretion2080RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051 | Markham
AjaxIce Accretion2085RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825 | Martin
AjaxIce Accretion2090RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114 | Matheson
AjaxIce Accretion2095RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455 | Mattawa
AjaxIce Accretion2100RCP4.5 | Ajax | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177 | Midland
AjaxIce Accretion2023RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185 | Milton
AjaxIce Accretion2025RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218 | Milverton
AjaxIce Accretion2030RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585 | Minden
AjaxIce Accretion2035RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952 | Mississauga
AjaxIce Accretion2040RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332 | Mississauga Port Credit
AjaxIce Accretion2045RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687 | Mitchell
AjaxIce Accretion2050RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122 | Moosonee
AjaxIce Accretion2055RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385 | Morrisburg
AjaxIce Accretion2060RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555 | Mount Forest
AjaxIce Accretion2065RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715 | Nakina
AjaxIce Accretion2070RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988 | Nanticoke (Jarvis)
AjaxIce Accretion2075RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352 | Nanticoke (Port Dover)
AjaxIce Accretion2080RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825 | Napanee
AjaxIce Accretion2085RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298 | New Liskeard
AjaxIce Accretion2090RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694 | Newcastle
AjaxIce Accretion2095RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211 | Newmarket
AjaxIce Accretion2100RCP6.0 | Ajax | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728 | Niagara Falls
AjaxIce Accretion2023RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185 | North Bay
AjaxIce Accretion2025RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585 | North York
AjaxIce Accretion2030RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332 | Norwood
AjaxIce Accretion2035RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055 | Oakville
AjaxIce Accretion2040RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933 | Orangeville
AjaxIce Accretion2045RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605 | Orillia
AjaxIce Accretion2050RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051 | Oshawa
AjaxIce Accretion2055RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114 | Ottawa (Barrhaven)
AjaxIce Accretion2060RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694 | Ottawa (Kanata)
AjaxIce Accretion2065RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211 | Ottawa (M-C Int'l Airport)
AjaxIce Accretion2070RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085 | Ottawa (Orleans)
AjaxIce Accretion2075RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489 | Ottawa (city hall)
AjaxIce Accretion2080RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695 | Owen Sound
AjaxIce Accretion2085RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157 | Pagwa River
AjaxIce Accretion2090RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562 | Paris
AjaxIce Accretion2095RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562 | Parkhill
AjaxIce Accretion2100RCP8.5 | Ajax | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562 | Parry Sound
AjaxWind2023RCP4.5 | Ajax | Wind | RCP4.5 | 2023 | 83.9588 | 90.3904 | 97.1552 | 103.9249 | 110.6906 | Pelham (Fonthill)
AjaxWind2025RCP4.5 | Ajax | Wind | RCP4.5 | 2025 | 83.9742 | 90.4235 | 97.2086 | 103.9959 | 110.779 | Pembroke
AjaxWind2030RCP4.5 | Ajax | Wind | RCP4.5 | 2030 | 83.9895 | 90.4566 | 97.2619 | 104.0668 | 110.8675 | Penetanguishene
AjaxWind2035RCP4.5 | Ajax | Wind | RCP4.5 | 2035 | 84.0049 | 90.4897 | 97.3152 | 104.1377 | 110.956 | Perth
AjaxWind2040RCP4.5 | Ajax | Wind | RCP4.5 | 2040 | 84.0202 | 90.5227 | 97.3686 | 104.2086 | 111.0444 | Petawawa
AjaxWind2045RCP4.5 | Ajax | Wind | RCP4.5 | 2045 | 84.0356 | 90.5558 | 97.4219 | 104.2795 | 111.1329 | Peterborough
AjaxWind2050RCP4.5 | Ajax | Wind | RCP4.5 | 2050 | 84.133 | 90.6917 | 97.6053 | 104.502 | 111.3983 | Petrolia
AjaxWind2055RCP4.5 | Ajax | Wind | RCP4.5 | 2055 | 84.2151 | 90.7946 | 97.7353 | 104.6535 | 111.5752 | Pickering (Dunbarton)
AjaxWind2060RCP4.5 | Ajax | Wind | RCP4.5 | 2060 | 84.2972 | 90.8974 | 97.8652 | 104.8051 | 111.7521 | Picton
AjaxWind2065RCP4.5 | Ajax | Wind | RCP4.5 | 2065 | 84.3793 | 91.0002 | 97.9952 | 104.9566 | 111.9291 | Plattsville
AjaxWind2070RCP4.5 | Ajax | Wind | RCP4.5 | 2070 | 84.4614 | 91.1031 | 98.1252 | 105.1081 | 112.106 | Point Alexander
AjaxWind2075RCP4.5 | Ajax | Wind | RCP4.5 | 2075 | 84.6037 | 91.2865 | 98.3596 | 105.3866 | 112.4285 | Port Burwell
AjaxWind2080RCP4.5 | Ajax | Wind | RCP4.5 | 2080 | 84.7461 | 91.4699 | 98.594 | 105.6651 | 112.7511 | Port Colborne
AjaxWind2085RCP4.5 | Ajax | Wind | RCP4.5 | 2085 | 84.8885 | 91.6534 | 98.8285 | 105.9436 | 113.0736 | Port Elgin
AjaxWind2090RCP4.5 | Ajax | Wind | RCP4.5 | 2090 | 85.0309 | 91.8368 | 99.0629 | 106.2221 | 113.3961 | Port Hope
AjaxWind2095RCP4.5 | Ajax | Wind | RCP4.5 | 2095 | 85.1733 | 92.0202 | 99.2973 | 106.5006 | 113.7186 | Port Perry
AjaxWind2100RCP4.5 | Ajax | Wind | RCP4.5 | 2100 | 85.3157 | 92.2036 | 99.5317 | 106.7792 | 114.0412 | Port Stanley
AjaxWind2023RCP6.0 | Ajax | Wind | RCP6.0 | 2023 | 83.9588 | 90.3904 | 97.1552 | 103.9249 | 110.6906 | Prescott
AjaxWind2025RCP6.0 | Ajax | Wind | RCP6.0 | 2025 | 83.9742 | 90.4235 | 97.2086 | 103.9959 | 110.779 | Princeton
AjaxWind2030RCP6.0 | Ajax | Wind | RCP6.0 | 2030 | 83.9895 | 90.4566 | 97.2619 | 104.0668 | 110.8675 | Raith
AjaxWind2035RCP6.0 | Ajax | Wind | RCP6.0 | 2035 | 84.0049 | 90.4897 | 97.3152 | 104.1377 | 110.956 | Rayside-Balfour (Chelmsford)
AjaxWind2040RCP6.0 | Ajax | Wind | RCP6.0 | 2040 | 84.0202 | 90.5227 | 97.3686 | 104.2086 | 111.0444 | Red Lake
AjaxWind2045RCP6.0 | Ajax | Wind | RCP6.0 | 2045 | 84.0356 | 90.5558 | 97.4219 | 104.2795 | 111.1329 | Renfrew
AjaxWind2050RCP6.0 | Ajax | Wind | RCP6.0 | 2050 | 84.133 | 90.6917 | 97.6053 | 104.502 | 111.3983 | Richmond Hill
AjaxWind2055RCP6.0 | Ajax | Wind | RCP6.0 | 2055 | 84.2151 | 90.7946 | 97.7353 | 104.6535 | 111.5752 | Rockland
AjaxWind2060RCP6.0 | Ajax | Wind | RCP6.0 | 2060 | 84.2972 | 90.8974 | 97.8652 | 104.8051 | 111.7521 | Sarnia
AjaxWind2065RCP6.0 | Ajax | Wind | RCP6.0 | 2065 | 84.3793 | 91.0002 | 97.9952 | 104.9566 | 111.9291 | Sault Ste. Marie
AjaxWind2070RCP6.0 | Ajax | Wind | RCP6.0 | 2070 | 84.4614 | 91.1031 | 98.1252 | 105.1081 | 112.106 | Scarborough
AjaxWind2075RCP6.0 | Ajax | Wind | RCP6.0 | 2075 | 84.6749 | 91.3782 | 98.4768 | 105.5259 | 112.5898 | Schreiber
AjaxWind2080RCP6.0 | Ajax | Wind | RCP6.0 | 2080 | 84.8885 | 91.6534 | 98.8285 | 105.9436 | 113.0736 | Seaforth
AjaxWind2085RCP6.0 | Ajax | Wind | RCP6.0 | 2085 | 85.1021 | 91.9285 | 99.1801 | 106.3614 | 113.5574 | Shelburne
AjaxWind2090RCP6.0 | Ajax | Wind | RCP6.0 | 2090 | 85.7568 | 92.7449 | 100.201 | 107.5576 | 114.9332 | Simcoe
AjaxWind2095RCP6.0 | Ajax | Wind | RCP6.0 | 2095 | 86.1979 | 93.2862 | 100.8703 | 108.336 | 115.8252 | Sioux Lookout
AjaxWind2100RCP6.0 | Ajax | Wind | RCP6.0 | 2100 | 86.6391 | 93.8274 | 101.5396 | 109.1144 | 116.7172 | Smiths Falls
AjaxWind2023RCP8.5 | Ajax | Wind | RCP8.5 | 2023 | 83.9588 | 90.3904 | 97.1552 | 103.9249 | 110.6906 | Smithville
AjaxWind2025RCP8.5 | Ajax | Wind | RCP8.5 | 2025 | 83.9895 | 90.4566 | 97.2619 | 104.0668 | 110.8675 | Smooth Rock Falls
AjaxWind2030RCP8.5 | Ajax | Wind | RCP8.5 | 2030 | 84.0202 | 90.5227 | 97.3686 | 104.2086 | 111.0444 | South River
AjaxWind2035RCP8.5 | Ajax | Wind | RCP8.5 | 2035 | 84.0509 | 90.5889 | 97.4753 | 104.3505 | 111.2214 | Southampton
AjaxWind2040RCP8.5 | Ajax | Wind | RCP8.5 | 2040 | 84.1878 | 90.7603 | 97.6919 | 104.603 | 111.5162 | St. Catharines
AjaxWind2045RCP8.5 | Ajax | Wind | RCP8.5 | 2045 | 84.3246 | 90.9317 | 97.9086 | 104.8556 | 111.8111 | St. Mary's
AjaxWind2050RCP8.5 | Ajax | Wind | RCP8.5 | 2050 | 84.7461 | 91.4699 | 98.594 | 105.6651 | 112.7511 | St. Thomas
AjaxWind2055RCP8.5 | Ajax | Wind | RCP8.5 | 2055 | 85.0309 | 91.8368 | 99.0629 | 106.2221 | 113.3961 | Stirling
AjaxWind2060RCP8.5 | Ajax | Wind | RCP8.5 | 2060 | 85.7568 | 92.7449 | 100.201 | 107.5576 | 114.9332 | Stratford
AjaxWind2065RCP8.5 | Ajax | Wind | RCP8.5 | 2065 | 86.1979 | 93.2862 | 100.8703 | 108.336 | 115.8252 | Strathroy
AjaxWind2070RCP8.5 | Ajax | Wind | RCP8.5 | 2070 | 86.7703 | 94.0048 | 101.7756 | 109.405 | 117.0563 | Sturgeon Falls
AjaxWind2075RCP8.5 | Ajax | Wind | RCP8.5 | 2075 | 86.9015 | 94.1822 | 102.0117 | 109.6957 | 117.3954 | Sudbury
AjaxWind2080RCP8.5 | Ajax | Wind | RCP8.5 | 2080 | 87.0327 | 94.3597 | 102.2477 | 109.9863 | 117.7345 | Sundridge
AjaxWind2085RCP8.5 | Ajax | Wind | RCP8.5 | 2085 | 87.3133 | 94.7566 | 102.7909 | 110.6505 | 118.5252 | Tavistock
AjaxWind2090RCP8.5 | Ajax | Wind | RCP8.5 | 2090 | 87.5939 | 95.1535 | 103.3341 | 111.3148 | 119.3158 | Temagami
AjaxWind2095RCP8.5 | Ajax | Wind | RCP8.5 | 2095 | 87.5939 | 95.1535 | 103.3341 | 111.3148 | 119.3158 | Thamesford
AjaxWind2100RCP8.5 | Ajax | Wind | RCP8.5 | 2100 | 87.5939 | 95.1535 | 103.3341 | 111.3148 | 119.3158 | Thedford
AlexandriaIce Accretion2023RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2023 | 20.8545 | 24.8751 | 29.94 | 33.8322 | 37.7244 | Thunder Bay
AlexandriaIce Accretion2025RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2025 | 20.8823 | 24.9207 | 30.005 | 33.9113 | 37.8189 | Tillsonburg
AlexandriaIce Accretion2030RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2030 | 20.9102 | 24.9664 | 30.07 | 33.9904 | 37.9134 | Timmins
AlexandriaIce Accretion2035RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2035 | 20.938 | 25.012 | 30.135 | 34.0695 | 38.0079 | Timmins (Porcupine)
AlexandriaIce Accretion2040RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2040 | 20.9658 | 25.0577 | 30.2 | 34.1486 | 38.1024 | Toronto (LBP Int'l Airport)
AlexandriaIce Accretion2045RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2045 | 20.9937 | 25.1033 | 30.265 | 34.2277 | 38.1969 | Toronto (city hall)
AlexandriaIce Accretion2050RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2050 | 21.0299 | 25.1689 | 30.372 | 34.361 | 38.3519 | Trenton
AlexandriaIce Accretion2055RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2055 | 21.0382 | 25.1888 | 30.414 | 34.4153 | 38.4124 | Trout Creek
AlexandriaIce Accretion2060RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2060 | 21.0466 | 25.2088 | 30.456 | 34.4695 | 38.4728 | Uxbridge
AlexandriaIce Accretion2065RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2065 | 21.0549 | 25.2287 | 30.498 | 34.5238 | 38.5333 | Vaughan (Woodbridge)
AlexandriaIce Accretion2070RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2070 | 21.0633 | 25.2486 | 30.54 | 34.578 | 38.5938 | Vittoria
AlexandriaIce Accretion2075RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2075 | 21.1155 | 25.3316 | 30.665 | 34.7362 | 38.7828 | Walkerton
AlexandriaIce Accretion2080RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2080 | 21.1676 | 25.4146 | 30.79 | 34.8944 | 38.9718 | Wallaceburg
AlexandriaIce Accretion2085RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2085 | 21.2198 | 25.4976 | 30.915 | 35.0526 | 39.1608 | Waterloo
AlexandriaIce Accretion2090RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2090 | 21.272 | 25.5806 | 31.04 | 35.2108 | 39.3498 | Watford
AlexandriaIce Accretion2095RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2095 | 21.3242 | 25.6636 | 31.165 | 35.369 | 39.5388 | Wawa
AlexandriaIce Accretion2100RCP4.5 | Alexandria | Ice Accretion | RCP4.5 | 2100 | 21.3764 | 25.7466 | 31.29 | 35.5272 | 39.7278 | Welland
AlexandriaIce Accretion2023RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2023 | 20.8545 | 24.8751 | 29.94 | 33.8322 | 37.7244 | West Lorne
AlexandriaIce Accretion2025RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2025 | 20.8823 | 24.9207 | 30.005 | 33.9113 | 37.8189 | Whitby
AlexandriaIce Accretion2030RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2030 | 20.9102 | 24.9664 | 30.07 | 33.9904 | 37.9134 | Whitby (Brooklin)
AlexandriaIce Accretion2035RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2035 | 20.938 | 25.012 | 30.135 | 34.0695 | 38.0079 | White River
AlexandriaIce Accretion2040RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2040 | 20.9658 | 25.0577 | 30.2 | 34.1486 | 38.1024 | Wiarton
AlexandriaIce Accretion2045RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2045 | 20.9937 | 25.1033 | 30.265 | 34.2277 | 38.1969 | Windsor
AlexandriaIce Accretion2050RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2050 | 21.0299 | 25.1689 | 30.372 | 34.361 | 38.3519 | Wingham
AlexandriaIce Accretion2055RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2055 | 21.0382 | 25.1888 | 30.414 | 34.4153 | 38.4124 | Woodstock
AlexandriaIce Accretion2060RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2060 | 21.0466 | 25.2088 | 30.456 | 34.4695 | 38.4728 | Wyoming
AlexandriaIce Accretion2065RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2065 | 21.0549 | 25.2287 | 30.498 | 34.5238 | 38.5333
AlexandriaIce Accretion2070RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2070 | 21.0633 | 25.2486 | 30.54 | 34.578 | 38.5938
AlexandriaIce Accretion2075RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2075 | 21.1415 | 25.3731 | 30.7275 | 34.8153 | 38.8773
AlexandriaIce Accretion2080RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2080 | 21.2198 | 25.4976 | 30.915 | 35.0526 | 39.1608
AlexandriaIce Accretion2085RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2085 | 21.2981 | 25.6221 | 31.1025 | 35.2899 | 39.4443
AlexandriaIce Accretion2090RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2090 | 21.3346 | 25.7466 | 31.33 | 35.595 | 39.8412
AlexandriaIce Accretion2095RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2095 | 21.2929 | 25.7466 | 31.37 | 35.6628 | 39.9546
AlexandriaIce Accretion2100RCP6.0 | Alexandria | Ice Accretion | RCP6.0 | 2100 | 21.2511 | 25.7466 | 31.41 | 35.7306 | 40.068
AlexandriaIce Accretion2023RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2023 | 20.8545 | 24.8751 | 29.94 | 33.8322 | 37.7244
AlexandriaIce Accretion2025RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2025 | 20.9102 | 24.9664 | 30.07 | 33.9904 | 37.9134
AlexandriaIce Accretion2030RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2030 | 20.9658 | 25.0577 | 30.2 | 34.1486 | 38.1024
AlexandriaIce Accretion2035RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2035 | 21.0215 | 25.149 | 30.33 | 34.3068 | 38.2914
AlexandriaIce Accretion2040RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2040 | 21.0354 | 25.1822 | 30.4 | 34.3972 | 38.3922
AlexandriaIce Accretion2045RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2045 | 21.0493 | 25.2154 | 30.47 | 34.4876 | 38.493
AlexandriaIce Accretion2050RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2050 | 21.1676 | 25.4146 | 30.79 | 34.8944 | 38.9718
AlexandriaIce Accretion2055RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2055 | 21.272 | 25.5806 | 31.04 | 35.2108 | 39.3498
AlexandriaIce Accretion2060RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2060 | 21.3346 | 25.7466 | 31.33 | 35.595 | 39.8412
AlexandriaIce Accretion2065RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2065 | 21.2929 | 25.7466 | 31.37 | 35.6628 | 39.9546
AlexandriaIce Accretion2070RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2070 | 21.0911 | 25.5972 | 31.27 | 35.6063 | 39.942
AlexandriaIce Accretion2075RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2075 | 20.9311 | 25.4478 | 31.13 | 35.482 | 39.816
AlexandriaIce Accretion2080RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2080 | 20.771 | 25.2984 | 30.99 | 35.3577 | 39.69
AlexandriaIce Accretion2085RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2085 | 19.9464 | 24.3771 | 29.94 | 34.2051 | 38.4237
AlexandriaIce Accretion2090RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2090 | 19.1219 | 23.4558 | 28.89 | 33.0525 | 37.1574
AlexandriaIce Accretion2095RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2095 | 19.1219 | 23.4558 | 28.89 | 33.0525 | 37.1574
AlexandriaIce Accretion2100RCP8.5 | Alexandria | Ice Accretion | RCP8.5 | 2100 | 19.1219 | 23.4558 | 28.89 | 33.0525 | 37.1574
AlexandriaWind2023RCP4.5 | Alexandria | Wind | RCP4.5 | 2023 | 77.5502 | 83.4573 | 89.649 | 95.8667 | 102.087
AlexandriaWind2025RCP4.5 | Alexandria | Wind | RCP4.5 | 2025 | 77.593 | 83.5047 | 89.703 | 95.926 | 102.1503
AlexandriaWind2030RCP4.5 | Alexandria | Wind | RCP4.5 | 2030 | 77.6357 | 83.5521 | 89.757 | 95.9854 | 102.2135
AlexandriaWind2035RCP4.5 | Alexandria | Wind | RCP4.5 | 2035 | 77.6784 | 83.5996 | 89.811 | 96.0448 | 102.2768
AlexandriaWind2040RCP4.5 | Alexandria | Wind | RCP4.5 | 2040 | 77.7212 | 83.647 | 89.865 | 96.1042 | 102.3401
AlexandriaWind2045RCP4.5 | Alexandria | Wind | RCP4.5 | 2045 | 77.7639 | 83.6944 | 89.919 | 96.1636 | 102.4033
AlexandriaWind2050RCP4.5 | Alexandria | Wind | RCP4.5 | 2050 | 77.7429 | 83.6699 | 89.8902 | 96.1305 | 102.364
AlexandriaWind2055RCP4.5 | Alexandria | Wind | RCP4.5 | 2055 | 77.6792 | 83.5979 | 89.8074 | 96.0381 | 102.2614
AlexandriaWind2060RCP4.5 | Alexandria | Wind | RCP4.5 | 2060 | 77.6155 | 83.5259 | 89.7246 | 95.9456 | 102.1588
AlexandriaWind2065RCP4.5 | Alexandria | Wind | RCP4.5 | 2065 | 77.5518 | 83.4539 | 89.6418 | 95.8532 | 102.0562
AlexandriaWind2070RCP4.5 | Alexandria | Wind | RCP4.5 | 2070 | 77.488 | 83.3819 | 89.559 | 95.7607 | 101.9536
AlexandriaWind2075RCP4.5 | Alexandria | Wind | RCP4.5 | 2075 | 77.4311 | 83.3164 | 89.484 | 95.6773 | 101.863
AlexandriaWind2080RCP4.5 | Alexandria | Wind | RCP4.5 | 2080 | 77.3741 | 83.2508 | 89.409 | 95.5938 | 101.7724
AlexandriaWind2085RCP4.5 | Alexandria | Wind | RCP4.5 | 2085 | 77.3171 | 83.1852 | 89.334 | 95.5103 | 101.6817
AlexandriaWind2090RCP4.5 | Alexandria | Wind | RCP4.5 | 2090 | 77.2601 | 83.1197 | 89.259 | 95.4269 | 101.5911
AlexandriaWind2095RCP4.5 | Alexandria | Wind | RCP4.5 | 2095 | 77.2031 | 83.0541 | 89.184 | 95.3434 | 101.5005
AlexandriaWind2100RCP4.5 | Alexandria | Wind | RCP4.5 | 2100 | 77.1461 | 82.9886 | 89.109 | 95.26 | 101.4098
AlexandriaWind2023RCP6.0 | Alexandria | Wind | RCP6.0 | 2023 | 77.5502 | 83.4573 | 89.649 | 95.8667 | 102.087
AlexandriaWind2025RCP6.0 | Alexandria | Wind | RCP6.0 | 2025 | 77.593 | 83.5047 | 89.703 | 95.926 | 102.1503
AlexandriaWind2030RCP6.0 | Alexandria | Wind | RCP6.0 | 2030 | 77.6357 | 83.5521 | 89.757 | 95.9854 | 102.2135
AlexandriaWind2035RCP6.0 | Alexandria | Wind | RCP6.0 | 2035 | 77.6784 | 83.5996 | 89.811 | 96.0448 | 102.2768
AlexandriaWind2040RCP6.0 | Alexandria | Wind | RCP6.0 | 2040 | 77.7212 | 83.647 | 89.865 | 96.1042 | 102.3401
AlexandriaWind2045RCP6.0 | Alexandria | Wind | RCP6.0 | 2045 | 77.7639 | 83.6944 | 89.919 | 96.1636 | 102.4033
AlexandriaWind2050RCP6.0 | Alexandria | Wind | RCP6.0 | 2050 | 77.7429 | 83.6699 | 89.8902 | 96.1305 | 102.364
AlexandriaWind2055RCP6.0 | Alexandria | Wind | RCP6.0 | 2055 | 77.6792 | 83.5979 | 89.8074 | 96.0381 | 102.2614
AlexandriaWind2060RCP6.0 | Alexandria | Wind | RCP6.0 | 2060 | 77.6155 | 83.5259 | 89.7246 | 95.9456 | 102.1588
AlexandriaWind2065RCP6.0 | Alexandria | Wind | RCP6.0 | 2065 | 77.5518 | 83.4539 | 89.6418 | 95.8532 | 102.0562
AlexandriaWind2070RCP6.0 | Alexandria | Wind | RCP6.0 | 2070 | 77.488 | 83.3819 | 89.559 | 95.7607 | 101.9536
AlexandriaWind2075RCP6.0 | Alexandria | Wind | RCP6.0 | 2075 | 77.4026 | 83.2836 | 89.4465 | 95.6355 | 101.8177
AlexandriaWind2080RCP6.0 | Alexandria | Wind | RCP6.0 | 2080 | 77.3171 | 83.1852 | 89.334 | 95.5103 | 101.6817
AlexandriaWind2085RCP6.0 | Alexandria | Wind | RCP6.0 | 2085 | 77.2316 | 83.0869 | 89.2215 | 95.3852 | 101.5458
AlexandriaWind2090RCP6.0 | Alexandria | Wind | RCP6.0 | 2090 | 77.1098 | 82.9607 | 89.091 | 95.2503 | 101.4064
AlexandriaWind2095RCP6.0 | Alexandria | Wind | RCP6.0 | 2095 | 77.0736 | 82.9328 | 89.073 | 95.2407 | 101.403
AlexandriaWind2100RCP6.0 | Alexandria | Wind | RCP6.0 | 2100 | 77.0373 | 82.9049 | 89.055 | 95.2311 | 101.3996
AlexandriaWind2023RCP8.5 | Alexandria | Wind | RCP8.5 | 2023 | 77.5502 | 83.4573 | 89.649 | 95.8667 | 102.087
AlexandriaWind2025RCP8.5 | Alexandria | Wind | RCP8.5 | 2025 | 77.6357 | 83.5521 | 89.757 | 95.9854 | 102.2135
AlexandriaWind2030RCP8.5 | Alexandria | Wind | RCP8.5 | 2030 | 77.7212 | 83.647 | 89.865 | 96.1042 | 102.3401
AlexandriaWind2035RCP8.5 | Alexandria | Wind | RCP8.5 | 2035 | 77.8067 | 83.7418 | 89.973 | 96.223 | 102.4666
AlexandriaWind2040RCP8.5 | Alexandria | Wind | RCP8.5 | 2040 | 77.7005 | 83.6219 | 89.835 | 96.0689 | 102.2956
AlexandriaWind2045RCP8.5 | Alexandria | Wind | RCP8.5 | 2045 | 77.5943 | 83.5019 | 89.697 | 95.9148 | 102.1246
AlexandriaWind2050RCP8.5 | Alexandria | Wind | RCP8.5 | 2050 | 77.3741 | 83.2508 | 89.409 | 95.5938 | 101.7724
AlexandriaWind2055RCP8.5 | Alexandria | Wind | RCP8.5 | 2055 | 77.2601 | 83.1197 | 89.259 | 95.4269 | 101.5911
AlexandriaWind2060RCP8.5 | Alexandria | Wind | RCP8.5 | 2060 | 77.1098 | 82.9607 | 89.091 | 95.2503 | 101.4064
AlexandriaWind2065RCP8.5 | Alexandria | Wind | RCP8.5 | 2065 | 77.0736 | 82.9328 | 89.073 | 95.2407 | 101.403
AlexandriaWind2070RCP8.5 | Alexandria | Wind | RCP8.5 | 2070 | 77.1073 | 82.9941 | 89.166 | 95.3627 | 101.5501
AlexandriaWind2075RCP8.5 | Alexandria | Wind | RCP8.5 | 2075 | 77.1772 | 83.0834 | 89.277 | 95.4943 | 101.7005
AlexandriaWind2080RCP8.5 | Alexandria | Wind | RCP8.5 | 2080 | 77.2471 | 83.1727 | 89.388 | 95.6259 | 101.851
AlexandriaWind2085RCP8.5 | Alexandria | Wind | RCP8.5 | 2085 | 77.2277 | 83.1518 | 89.3745 | 95.6115 | 101.8408
AlexandriaWind2090RCP8.5 | Alexandria | Wind | RCP8.5 | 2090 | 77.2083 | 83.1308 | 89.361 | 95.597 | 101.8305
AlexandriaWind2095RCP8.5 | Alexandria | Wind | RCP8.5 | 2095 | 77.2083 | 83.1308 | 89.361 | 95.597 | 101.8305
AlexandriaWind2100RCP8.5 | Alexandria | Wind | RCP8.5 | 2100 | 77.2083 | 83.1308 | 89.361 | 95.597 | 101.8305
AllistonIce Accretion2023RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2023 | 15.9885 | 19.1854 | 23.23 | 26.3279 | 29.4147
AllistonIce Accretion2025RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2025 | 16.0285 | 19.2491 | 23.3258 | 26.4448 | 29.5548
AllistonIce Accretion2030RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2030 | 16.0685 | 19.3127 | 23.4217 | 26.5618 | 29.6948
AllistonIce Accretion2035RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2035 | 16.1085 | 19.3763 | 23.5175 | 26.6787 | 29.8349
AllistonIce Accretion2040RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2040 | 16.1485 | 19.44 | 23.6133 | 26.7957 | 29.975
AllistonIce Accretion2045RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2045 | 16.1885 | 19.5036 | 23.7092 | 26.9126 | 30.1151
AllistonIce Accretion2050RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2050 | 16.1197 | 19.4565 | 23.6854 | 26.9048 | 30.1218
AllistonIce Accretion2055RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2055 | 16.0109 | 19.3458 | 23.5658 | 26.7801 | 29.9885
AllistonIce Accretion2060RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2060 | 15.902 | 19.2351 | 23.4462 | 26.6553 | 29.8552
AllistonIce Accretion2065RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2065 | 15.7932 | 19.1244 | 23.3266 | 26.5306 | 29.7219
AllistonIce Accretion2070RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2070 | 15.6844 | 19.0136 | 23.207 | 26.4058 | 29.5886
AllistonIce Accretion2075RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2075 | 15.6497 | 18.9977 | 23.2147 | 26.4275 | 29.6272
AllistonIce Accretion2080RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2080 | 15.615 | 18.9818 | 23.2223 | 26.4492 | 29.6659
AllistonIce Accretion2085RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2085 | 15.5803 | 18.9659 | 23.23 | 26.4708 | 29.7045
AllistonIce Accretion2090RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2090 | 15.5457 | 18.95 | 23.2377 | 26.4925 | 29.7431
AllistonIce Accretion2095RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2095 | 15.511 | 18.9341 | 23.2453 | 26.5141 | 29.7818
AllistonIce Accretion2100RCP4.5 | Alliston | Ice Accretion | RCP4.5 | 2100 | 15.4763 | 18.9182 | 23.253 | 26.5358 | 29.8204
AllistonIce Accretion2023RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2023 | 15.9885 | 19.1854 | 23.23 | 26.3279 | 29.4147
AllistonIce Accretion2025RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2025 | 16.0285 | 19.2491 | 23.3258 | 26.4448 | 29.5548
AllistonIce Accretion2030RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2030 | 16.0685 | 19.3127 | 23.4217 | 26.5618 | 29.6948
AllistonIce Accretion2035RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2035 | 16.1085 | 19.3763 | 23.5175 | 26.6787 | 29.8349
AllistonIce Accretion2040RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2040 | 16.1485 | 19.44 | 23.6133 | 26.7957 | 29.975
AllistonIce Accretion2045RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2045 | 16.1885 | 19.5036 | 23.7092 | 26.9126 | 30.1151
AllistonIce Accretion2050RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2050 | 16.1197 | 19.4565 | 23.6854 | 26.9048 | 30.1218
AllistonIce Accretion2055RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2055 | 16.0109 | 19.3458 | 23.5658 | 26.7801 | 29.9885
AllistonIce Accretion2060RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2060 | 15.902 | 19.2351 | 23.4462 | 26.6553 | 29.8552
AllistonIce Accretion2065RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2065 | 15.7932 | 19.1244 | 23.3266 | 26.5306 | 29.7219
AllistonIce Accretion2070RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2070 | 15.6844 | 19.0136 | 23.207 | 26.4058 | 29.5886
AllistonIce Accretion2075RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2075 | 15.6324 | 18.9898 | 23.2185 | 26.4383 | 29.6465
AllistonIce Accretion2080RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2080 | 15.5803 | 18.9659 | 23.23 | 26.4708 | 29.7045
AllistonIce Accretion2085RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2085 | 15.5283 | 18.9421 | 23.2415 | 26.5033 | 29.7625
AllistonIce Accretion2090RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2090 | 15.1936 | 18.6191 | 22.931 | 26.2066 | 29.4727
AllistonIce Accretion2095RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2095 | 14.9108 | 18.32 | 22.609 | 25.8774 | 29.1249
AllistonIce Accretion2100RCP6.0 | Alliston | Ice Accretion | RCP6.0 | 2100 | 14.6281 | 18.021 | 22.287 | 25.5482 | 28.7771
AllistonIce Accretion2023RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2023 | 15.9885 | 19.1854 | 23.23 | 26.3279 | 29.4147
AllistonIce Accretion2025RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2025 | 16.0685 | 19.3127 | 23.4217 | 26.5618 | 29.6948
AllistonIce Accretion2030RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2030 | 16.1485 | 19.44 | 23.6133 | 26.7957 | 29.975
AllistonIce Accretion2035RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2035 | 16.2285 | 19.5672 | 23.805 | 27.0296 | 30.2551
AllistonIce Accretion2040RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2040 | 16.0471 | 19.3827 | 23.6057 | 26.8217 | 30.0329
AllistonIce Accretion2045RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2045 | 15.8658 | 19.1982 | 23.4063 | 26.6138 | 29.8108
AllistonIce Accretion2050RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2050 | 15.615 | 18.9818 | 23.2223 | 26.4492 | 29.6659
AllistonIce Accretion2055RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2055 | 15.5457 | 18.95 | 23.2377 | 26.4925 | 29.7431
AllistonIce Accretion2060RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2060 | 15.1936 | 18.6191 | 22.931 | 26.2066 | 29.4727
AllistonIce Accretion2065RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2065 | 14.9108 | 18.32 | 22.609 | 25.8774 | 29.1249
AllistonIce Accretion2070RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2070 | 14.2706 | 17.6392 | 21.873 | 25.0977 | 28.3038
AllistonIce Accretion2075RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2075 | 13.9132 | 17.2574 | 21.459 | 24.6472 | 27.8305
AllistonIce Accretion2080RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2080 | 13.5558 | 16.8756 | 21.045 | 24.1967 | 27.3571
AllistonIce Accretion2085RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2085 | 12.8516 | 16.0451 | 20.056 | 23.0921 | 26.1255
AllistonIce Accretion2090RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2090 | 12.1474 | 15.2147 | 19.067 | 21.9875 | 24.8938
AllistonIce Accretion2095RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2095 | 12.1474 | 15.2147 | 19.067 | 21.9875 | 24.8938
AllistonIce Accretion2100RCP8.5 | Alliston | Ice Accretion | RCP8.5 | 2100 | 12.1474 | 15.2147 | 19.067 | 21.9875 | 24.8938
AllistonWind2023RCP4.5 | Alliston | Wind | RCP4.5 | 2023 | 78.001 | 84.0097 | 90.333 | 96.6563 | 102.9796
AllistonWind2025RCP4.5 | Alliston | Wind | RCP4.5 | 2025 | 78.0256 | 84.0446 | 90.381 | 96.7157 | 103.0514
AllistonWind2030RCP4.5 | Alliston | Wind | RCP4.5 | 2030 | 78.0502 | 84.0794 | 90.429 | 96.7751 | 103.1233
AllistonWind2035RCP4.5 | Alliston | Wind | RCP4.5 | 2035 | 78.0748 | 84.1143 | 90.477 | 96.8345 | 103.1951
AllistonWind2040RCP4.5 | Alliston | Wind | RCP4.5 | 2040 | 78.0994 | 84.1492 | 90.525 | 96.8939 | 103.2669
AllistonWind2045RCP4.5 | Alliston | Wind | RCP4.5 | 2045 | 78.124 | 84.1841 | 90.573 | 96.9532 | 103.3387
AllistonWind2050RCP4.5 | Alliston | Wind | RCP4.5 | 2050 | 78.1999 | 84.2675 | 90.666 | 97.055 | 103.4495
AllistonWind2055RCP4.5 | Alliston | Wind | RCP4.5 | 2055 | 78.2512 | 84.316 | 90.711 | 97.0974 | 103.4885
AllistonWind2060RCP4.5 | Alliston | Wind | RCP4.5 | 2060 | 78.3025 | 84.3646 | 90.756 | 97.1397 | 103.5275
AllistonWind2065RCP4.5 | Alliston | Wind | RCP4.5 | 2065 | 78.3538 | 84.4131 | 90.801 | 97.1821 | 103.5665
AllistonWind2070RCP4.5 | Alliston | Wind | RCP4.5 | 2070 | 78.4051 | 84.4617 | 90.846 | 97.2245 | 103.6055
AllistonWind2075RCP4.5 | Alliston | Wind | RCP4.5 | 2075 | 78.4802 | 84.5649 | 90.984 | 97.3914 | 103.8021
AllistonWind2080RCP4.5 | Alliston | Wind | RCP4.5 | 2080 | 78.5553 | 84.6681 | 91.122 | 97.5583 | 103.9988
AllistonWind2085RCP4.5 | Alliston | Wind | RCP4.5 | 2085 | 78.6304 | 84.7714 | 91.26 | 97.7252 | 104.1954
AllistonWind2090RCP4.5 | Alliston | Wind | RCP4.5 | 2090 | 78.7056 | 84.8746 | 91.398 | 97.8922 | 104.3921
AllistonWind2095RCP4.5 | Alliston | Wind | RCP4.5 | 2095 | 78.7807 | 84.9778 | 91.536 | 98.0591 | 104.5887
AllistonWind2100RCP4.5 | Alliston | Wind | RCP4.5 | 2100 | 78.8558 | 85.0811 | 91.674 | 98.226 | 104.7854
AllistonWind2023RCP6.0 | Alliston | Wind | RCP6.0 | 2023 | 78.001 | 84.0097 | 90.333 | 96.6563 | 102.9796
AllistonWind2025RCP6.0 | Alliston | Wind | RCP6.0 | 2025 | 78.0256 | 84.0446 | 90.381 | 96.7157 | 103.0514
AllistonWind2030RCP6.0 | Alliston | Wind | RCP6.0 | 2030 | 78.0502 | 84.0794 | 90.429 | 96.7751 | 103.1233
AllistonWind2035RCP6.0 | Alliston | Wind | RCP6.0 | 2035 | 78.0748 | 84.1143 | 90.477 | 96.8345 | 103.1951
AllistonWind2040RCP6.0 | Alliston | Wind | RCP6.0 | 2040 | 78.0994 | 84.1492 | 90.525 | 96.8939 | 103.2669
AllistonWind2045RCP6.0 | Alliston | Wind | RCP6.0 | 2045 | 78.124 | 84.1841 | 90.573 | 96.9532 | 103.3387
AllistonWind2050RCP6.0 | Alliston | Wind | RCP6.0 | 2050 | 78.1999 | 84.2675 | 90.666 | 97.055 | 103.4495
AllistonWind2055RCP6.0 | Alliston | Wind | RCP6.0 | 2055 | 78.2512 | 84.316 | 90.711 | 97.0974 | 103.4885
AllistonWind2060RCP6.0 | Alliston | Wind | RCP6.0 | 2060 | 78.3025 | 84.3646 | 90.756 | 97.1397 | 103.5275
AllistonWind2065RCP6.0 | Alliston | Wind | RCP6.0 | 2065 | 78.3538 | 84.4131 | 90.801 | 97.1821 | 103.5665
AllistonWind2070RCP6.0 | Alliston | Wind | RCP6.0 | 2070 | 78.4051 | 84.4617 | 90.846 | 97.2245 | 103.6055
AllistonWind2075RCP6.0 | Alliston | Wind | RCP6.0 | 2075 | 78.5178 | 84.6165 | 91.053 | 97.4749 | 103.9005
AllistonWind2080RCP6.0 | Alliston | Wind | RCP6.0 | 2080 | 78.6304 | 84.7714 | 91.26 | 97.7252 | 104.1954
AllistonWind2085RCP6.0 | Alliston | Wind | RCP6.0 | 2085 | 78.7431 | 84.9262 | 91.467 | 97.9756 | 104.4904
AllistonWind2090RCP6.0 | Alliston | Wind | RCP6.0 | 2090 | 79.1174 | 85.4047 | 92.073 | 98.6915 | 105.3189
AllistonWind2095RCP6.0 | Alliston | Wind | RCP6.0 | 2095 | 79.3791 | 85.7283 | 92.472 | 99.1569 | 105.8524
AllistonWind2100RCP6.0 | Alliston | Wind | RCP6.0 | 2100 | 79.6407 | 86.052 | 92.871 | 99.6224 | 106.3859
AllistonWind2023RCP8.5 | Alliston | Wind | RCP8.5 | 2023 | 78.001 | 84.0097 | 90.333 | 96.6563 | 102.9796
AllistonWind2025RCP8.5 | Alliston | Wind | RCP8.5 | 2025 | 78.0502 | 84.0794 | 90.429 | 96.7751 | 103.1233
AllistonWind2030RCP8.5 | Alliston | Wind | RCP8.5 | 2030 | 78.0994 | 84.1492 | 90.525 | 96.8939 | 103.2669
AllistonWind2035RCP8.5 | Alliston | Wind | RCP8.5 | 2035 | 78.1486 | 84.2189 | 90.621 | 97.0126 | 103.4105
AllistonWind2040RCP8.5 | Alliston | Wind | RCP8.5 | 2040 | 78.2341 | 84.2999 | 90.696 | 97.0832 | 103.4755
AllistonWind2045RCP8.5 | Alliston | Wind | RCP8.5 | 2045 | 78.3196 | 84.3808 | 90.771 | 97.1539 | 103.5405
AllistonWind2050RCP8.5 | Alliston | Wind | RCP8.5 | 2050 | 78.5553 | 84.6681 | 91.122 | 97.5583 | 103.9988
AllistonWind2055RCP8.5 | Alliston | Wind | RCP8.5 | 2055 | 78.7056 | 84.8746 | 91.398 | 97.8922 | 104.3921
AllistonWind2060RCP8.5 | Alliston | Wind | RCP8.5 | 2060 | 79.1174 | 85.4047 | 92.073 | 98.6915 | 105.3189
AllistonWind2065RCP8.5 | Alliston | Wind | RCP8.5 | 2065 | 79.3791 | 85.7283 | 92.472 | 99.1569 | 105.8524
AllistonWind2070RCP8.5 | Alliston | Wind | RCP8.5 | 2070 | 79.8402 | 86.3198 | 93.225 | 100.0493 | 106.8853
AllistonWind2075RCP8.5 | Alliston | Wind | RCP8.5 | 2075 | 80.0396 | 86.5876 | 93.579 | 100.4762 | 107.3846
AllistonWind2080RCP8.5 | Alliston | Wind | RCP8.5 | 2080 | 80.2391 | 86.8555 | 93.933 | 100.9031 | 107.8839
AllistonWind2085RCP8.5 | Alliston | Wind | RCP8.5 | 2085 | 80.3401 | 86.9894 | 94.113 | 101.115 | 108.1353
AllistonWind2090RCP8.5 | Alliston | Wind | RCP8.5 | 2090 | 80.4412 | 87.1233 | 94.293 | 101.3269 | 108.3866
AllistonWind2095RCP8.5 | Alliston | Wind | RCP8.5 | 2095 | 80.4412 | 87.1233 | 94.293 | 101.3269 | 108.3866
AllistonWind2100RCP8.5 | Alliston | Wind | RCP8.5 | 2100 | 80.4412 | 87.1233 | 94.293 | 101.3269 | 108.3866
AlmonteIce Accretion2023RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2023 | 17.9473 | 21.3426 | 25.636 | 28.9393 | 32.2358
AlmonteIce Accretion2025RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2025 | 17.9412 | 21.339 | 25.6403 | 28.9491 | 32.2468
AlmonteIce Accretion2030RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2030 | 17.9352 | 21.3354 | 25.6447 | 28.9589 | 32.2577
AlmonteIce Accretion2035RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2035 | 17.9292 | 21.3318 | 25.649 | 28.9687 | 32.2686
AlmonteIce Accretion2040RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2040 | 17.9231 | 21.3282 | 25.6533 | 28.9785 | 32.2795
AlmonteIce Accretion2045RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2045 | 17.9171 | 21.3246 | 25.6577 | 28.9883 | 32.2904
AlmonteIce Accretion2050RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2050 | 17.9147 | 21.3426 | 25.7036 | 29.0568 | 32.3734
AlmonteIce Accretion2055RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2055 | 17.9183 | 21.3642 | 25.7452 | 29.1156 | 32.4455
AlmonteIce Accretion2060RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2060 | 17.9219 | 21.3858 | 25.7868 | 29.1743 | 32.5176
AlmonteIce Accretion2065RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2065 | 17.9256 | 21.4074 | 25.8284 | 29.2331 | 32.5896
AlmonteIce Accretion2070RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2070 | 17.9292 | 21.4289 | 25.87 | 29.2919 | 32.6617
AlmonteIce Accretion2075RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2075 | 18.0106 | 21.5476 | 26.0347 | 29.4877 | 32.8965
AlmonteIce Accretion2080RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2080 | 18.092 | 21.6663 | 26.1993 | 29.6836 | 33.1313
AlmonteIce Accretion2085RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2085 | 18.1734 | 21.785 | 26.364 | 29.8795 | 33.3661
AlmonteIce Accretion2090RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2090 | 18.2548 | 21.9037 | 26.5287 | 30.0753 | 33.6008
AlmonteIce Accretion2095RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2095 | 18.3362 | 22.0224 | 26.6933 | 30.2712 | 33.8356
AlmonteIce Accretion2100RCP4.5 | Almonte | Ice Accretion | RCP4.5 | 2100 | 18.4177 | 22.1411 | 26.858 | 30.4671 | 34.0704
AlmonteIce Accretion2023RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2023 | 17.9473 | 21.3426 | 25.636 | 28.9393 | 32.2358
AlmonteIce Accretion2025RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2025 | 17.9412 | 21.339 | 25.6403 | 28.9491 | 32.2468
AlmonteIce Accretion2030RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2030 | 17.9352 | 21.3354 | 25.6447 | 28.9589 | 32.2577
AlmonteIce Accretion2035RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2035 | 17.9292 | 21.3318 | 25.649 | 28.9687 | 32.2686
AlmonteIce Accretion2040RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2040 | 17.9231 | 21.3282 | 25.6533 | 28.9785 | 32.2795
AlmonteIce Accretion2045RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2045 | 17.9171 | 21.3246 | 25.6577 | 28.9883 | 32.2904
AlmonteIce Accretion2050RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2050 | 17.9147 | 21.3426 | 25.7036 | 29.0568 | 32.3734
AlmonteIce Accretion2055RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2055 | 17.9183 | 21.3642 | 25.7452 | 29.1156 | 32.4455
AlmonteIce Accretion2060RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2060 | 17.9219 | 21.3858 | 25.7868 | 29.1743 | 32.5176
AlmonteIce Accretion2065RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2065 | 17.9256 | 21.4074 | 25.8284 | 29.2331 | 32.5896
AlmonteIce Accretion2070RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2070 | 17.9292 | 21.4289 | 25.87 | 29.2919 | 32.6617
AlmonteIce Accretion2075RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2075 | 18.0513 | 21.607 | 26.117 | 29.5857 | 33.0139
AlmonteIce Accretion2080RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2080 | 18.1734 | 21.785 | 26.364 | 29.8795 | 33.3661
AlmonteIce Accretion2085RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2085 | 18.2955 | 21.963 | 26.611 | 30.1733 | 33.7182
AlmonteIce Accretion2090RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2090 | 18.4056 | 22.1627 | 26.9273 | 30.5552 | 34.1905
AlmonteIce Accretion2095RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2095 | 18.3935 | 22.1842 | 26.9967 | 30.6433 | 34.3106
AlmonteIce Accretion2100RCP6.0 | Almonte | Ice Accretion | RCP6.0 | 2100 | 18.3815 | 22.2058 | 27.066 | 30.7315 | 34.4308
AlmonteIce Accretion2023RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2023 | 17.9473 | 21.3426 | 25.636 | 28.9393 | 32.2358
AlmonteIce Accretion2025RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2025 | 17.9352 | 21.3354 | 25.6447 | 28.9589 | 32.2577
AlmonteIce Accretion2030RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2030 | 17.9231 | 21.3282 | 25.6533 | 28.9785 | 32.2795
AlmonteIce Accretion2035RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2035 | 17.9111 | 21.321 | 25.662 | 28.9981 | 32.3014
AlmonteIce Accretion2040RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2040 | 17.9171 | 21.357 | 25.7313 | 29.096 | 32.4215
AlmonteIce Accretion2045RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2045 | 17.9231 | 21.393 | 25.8007 | 29.1939 | 32.5416
AlmonteIce Accretion2050RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2050 | 18.092 | 21.6663 | 26.1993 | 29.6836 | 33.1313
AlmonteIce Accretion2055RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2055 | 18.2548 | 21.9037 | 26.5287 | 30.0753 | 33.6008
AlmonteIce Accretion2060RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2060 | 18.4056 | 22.1627 | 26.9273 | 30.5552 | 34.1905
AlmonteIce Accretion2065RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2065 | 18.3935 | 22.1842 | 26.9967 | 30.6433 | 34.3106
AlmonteIce Accretion2070RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2070 | 18.1885 | 22.0044 | 26.8493 | 30.5062 | 34.1905
AlmonteIce Accretion2075RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2075 | 17.9955 | 21.803 | 26.6327 | 30.281 | 33.9503
AlmonteIce Accretion2080RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2080 | 17.8025 | 21.6016 | 26.416 | 30.0557 | 33.71
AlmonteIce Accretion2085RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2085 | 17.0608 | 20.7492 | 25.415 | 28.954 | 32.4979
AlmonteIce Accretion2090RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2090 | 16.319 | 19.8968 | 24.414 | 27.8522 | 31.2858
AlmonteIce Accretion2095RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2095 | 16.319 | 19.8968 | 24.414 | 27.8522 | 31.2858
AlmonteIce Accretion2100RCP8.5 | Almonte | Ice Accretion | RCP8.5 | 2100 | 16.319 | 19.8968 | 24.414 | 27.8522 | 31.2858
AlmonteWind2023RCP4.5 | Almonte | Wind | RCP4.5 | 2023 | 74.8164 | 80.6518 | 86.8084 | 92.9402 | 99.0792
AlmonteWind2025RCP4.5 | Almonte | Wind | RCP4.5 | 2025 | 74.9241 | 80.7811 | 86.9646 | 93.1212 | 99.2851
AlmonteWind2030RCP4.5 | Almonte | Wind | RCP4.5 | 2030 | 75.0318 | 80.9104 | 87.1209 | 93.3021 | 99.491
AlmonteWind2035RCP4.5 | Almonte | Wind | RCP4.5 | 2035 | 75.1395 | 81.0397 | 87.2771 | 93.4831 | 99.6969
AlmonteWind2040RCP4.5 | Almonte | Wind | RCP4.5 | 2040 | 75.2471 | 81.169 | 87.4333 | 93.6641 | 99.9028
AlmonteWind2045RCP4.5 | Almonte | Wind | RCP4.5 | 2045 | 75.3548 | 81.2983 | 87.5896 | 93.8451 | 100.1086
AlmonteWind2050RCP4.5 | Almonte | Wind | RCP4.5 | 2050 | 75.4476 | 81.4052 | 87.7148 | 93.9874 | 100.2675
AlmonteWind2055RCP4.5 | Almonte | Wind | RCP4.5 | 2055 | 75.4328 | 81.3828 | 87.6839 | 93.9487 | 100.2204
AlmonteWind2060RCP4.5 | Almonte | Wind | RCP4.5 | 2060 | 75.4179 | 81.3605 | 87.6529 | 93.9101 | 100.1734
AlmonteWind2065RCP4.5 | Almonte | Wind | RCP4.5 | 2065 | 75.4031 | 81.3381 | 87.622 | 93.8714 | 100.1263
AlmonteWind2070RCP4.5 | Almonte | Wind | RCP4.5 | 2070 | 75.3882 | 81.3157 | 87.591 | 93.8328 | 100.0792
AlmonteWind2075RCP4.5 | Almonte | Wind | RCP4.5 | 2075 | 75.4155 | 81.3517 | 87.6397 | 93.8911 | 100.1462
AlmonteWind2080RCP4.5 | Almonte | Wind | RCP4.5 | 2080 | 75.4427 | 81.3876 | 87.6885 | 93.9494 | 100.2132
AlmonteWind2085RCP4.5 | Almonte | Wind | RCP4.5 | 2085 | 75.4699 | 81.4236 | 87.7372 | 94.0076 | 100.2802
AlmonteWind2090RCP4.5 | Almonte | Wind | RCP4.5 | 2090 | 75.4971 | 81.4596 | 87.7859 | 94.0659 | 100.3472
AlmonteWind2095RCP4.5 | Almonte | Wind | RCP4.5 | 2095 | 75.5244 | 81.4956 | 87.8347 | 94.1242 | 100.4142
AlmonteWind2100RCP4.5 | Almonte | Wind | RCP4.5 | 2100 | 75.5516 | 81.5316 | 87.8834 | 94.1825 | 100.4812
AlmonteWind2023RCP6.0 | Almonte | Wind | RCP6.0 | 2023 | 74.8164 | 80.6518 | 86.8084 | 92.9402 | 99.0792
AlmonteWind2025RCP6.0 | Almonte | Wind | RCP6.0 | 2025 | 74.9241 | 80.7811 | 86.9646 | 93.1212 | 99.2851
AlmonteWind2030RCP6.0 | Almonte | Wind | RCP6.0 | 2030 | 75.0318 | 80.9104 | 87.1209 | 93.3021 | 99.491
AlmonteWind2035RCP6.0 | Almonte | Wind | RCP6.0 | 2035 | 75.1395 | 81.0397 | 87.2771 | 93.4831 | 99.6969
AlmonteWind2040RCP6.0 | Almonte | Wind | RCP6.0 | 2040 | 75.2471 | 81.169 | 87.4333 | 93.6641 | 99.9028
AlmonteWind2045RCP6.0 | Almonte | Wind | RCP6.0 | 2045 | 75.3548 | 81.2983 | 87.5896 | 93.8451 | 100.1086
AlmonteWind2050RCP6.0 | Almonte | Wind | RCP6.0 | 2050 | 75.4476 | 81.4052 | 87.7148 | 93.9874 | 100.2675
AlmonteWind2055RCP6.0 | Almonte | Wind | RCP6.0 | 2055 | 75.4328 | 81.3828 | 87.6839 | 93.9487 | 100.2204
AlmonteWind2060RCP6.0 | Almonte | Wind | RCP6.0 | 2060 | 75.4179 | 81.3605 | 87.6529 | 93.9101 | 100.1734
AlmonteWind2065RCP6.0 | Almonte | Wind | RCP6.0 | 2065 | 75.4031 | 81.3381 | 87.622 | 93.8714 | 100.1263
AlmonteWind2070RCP6.0 | Almonte | Wind | RCP6.0 | 2070 | 75.3882 | 81.3157 | 87.591 | 93.8328 | 100.0792
AlmonteWind2075RCP6.0 | Almonte | Wind | RCP6.0 | 2075 | 75.4291 | 81.3697 | 87.6641 | 93.9202 | 100.1797
AlmonteWind2080RCP6.0 | Almonte | Wind | RCP6.0 | 2080 | 75.4699 | 81.4236 | 87.7372 | 94.0076 | 100.2802
AlmonteWind2085RCP6.0 | Almonte | Wind | RCP6.0 | 2085 | 75.5108 | 81.4776 | 87.8103 | 94.0951 | 100.3807
AlmonteWind2090RCP6.0 | Almonte | Wind | RCP6.0 | 2090 | 75.4971 | 81.449 | 87.7573 | 94.026 | 100.2917
AlmonteWind2095RCP6.0 | Almonte | Wind | RCP6.0 | 2095 | 75.4427 | 81.3663 | 87.6311 | 93.8696 | 100.1021
AlmonteWind2100RCP6.0 | Almonte | Wind | RCP6.0 | 2100 | 75.3882 | 81.2837 | 87.505 | 93.7132 | 99.9126
AlmonteWind2023RCP8.5 | Almonte | Wind | RCP8.5 | 2023 | 74.8164 | 80.6518 | 86.8084 | 92.9402 | 99.0792
AlmonteWind2025RCP8.5 | Almonte | Wind | RCP8.5 | 2025 | 75.0318 | 80.9104 | 87.1209 | 93.3021 | 99.491
AlmonteWind2030RCP8.5 | Almonte | Wind | RCP8.5 | 2030 | 75.2471 | 81.169 | 87.4333 | 93.6641 | 99.9028
AlmonteWind2035RCP8.5 | Almonte | Wind | RCP8.5 | 2035 | 75.4625 | 81.4276 | 87.7458 | 94.026 | 100.3145
AlmonteWind2040RCP8.5 | Almonte | Wind | RCP8.5 | 2040 | 75.4377 | 81.3903 | 87.6942 | 93.9616 | 100.2361
AlmonteWind2045RCP8.5 | Almonte | Wind | RCP8.5 | 2045 | 75.413 | 81.353 | 87.6426 | 93.8972 | 100.1577
AlmonteWind2050RCP8.5 | Almonte | Wind | RCP8.5 | 2050 | 75.4427 | 81.3876 | 87.6885 | 93.9494 | 100.2132
AlmonteWind2055RCP8.5 | Almonte | Wind | RCP8.5 | 2055 | 75.4971 | 81.4596 | 87.7859 | 94.0659 | 100.3472
AlmonteWind2060RCP8.5 | Almonte | Wind | RCP8.5 | 2060 | 75.4971 | 81.449 | 87.7573 | 94.026 | 100.2917
AlmonteWind2065RCP8.5 | Almonte | Wind | RCP8.5 | 2065 | 75.4427 | 81.3663 | 87.6311 | 93.8696 | 100.1021
AlmonteWind2070RCP8.5 | Almonte | Wind | RCP8.5 | 2070 | 75.4204 | 81.313 | 87.5308 | 93.7377 | 99.9354
AlmonteWind2075RCP8.5 | Almonte | Wind | RCP8.5 | 2075 | 75.4526 | 81.3423 | 87.5566 | 93.7622 | 99.9583
AlmonteWind2080RCP8.5 | Almonte | Wind | RCP8.5 | 2080 | 75.4848 | 81.3717 | 87.5824 | 93.7868 | 99.9812
AlmonteWind2085RCP8.5 | Almonte | Wind | RCP8.5 | 2085 | 75.5108 | 81.4116 | 87.6383 | 93.8512 | 100.0596
AlmonteWind2090RCP8.5 | Almonte | Wind | RCP8.5 | 2090 | 75.5368 | 81.4516 | 87.6942 | 93.9156 | 100.1381
AlmonteWind2095RCP8.5 | Almonte | Wind | RCP8.5 | 2095 | 75.5368 | 81.4516 | 87.6942 | 93.9156 | 100.1381
AlmonteWind2100RCP8.5 | Almonte | Wind | RCP8.5 | 2100 | 75.5368 | 81.4516 | 87.6942 | 93.9156 | 100.1381
ArmstrongIce Accretion2023RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2023 | 9.2721 | 11.0382 | 13.299 | 15.0132 | 16.7404
ArmstrongIce Accretion2025RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2025 | 9.3867 | 11.1694 | 13.4463 | 15.1772 | 16.9205
ArmstrongIce Accretion2030RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2030 | 9.5013 | 11.3007 | 13.5937 | 15.3413 | 17.1007
ArmstrongIce Accretion2035RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2035 | 9.6159 | 11.432 | 13.741 | 15.5053 | 17.2809
ArmstrongIce Accretion2040RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2040 | 9.7305 | 11.5633 | 13.8883 | 15.6693 | 17.4611
ArmstrongIce Accretion2045RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2045 | 9.8451 | 11.6946 | 14.0357 | 15.8334 | 17.6413
ArmstrongIce Accretion2050RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2050 | 9.9741 | 11.8409 | 14.2012 | 16.018 | 17.8411
ArmstrongIce Accretion2055RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2055 | 9.9886 | 11.8561 | 14.2194 | 16.0385 | 17.8608
ArmstrongIce Accretion2060RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2060 | 10.0031 | 11.8712 | 14.2376 | 16.0591 | 17.8804
ArmstrongIce Accretion2065RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2065 | 10.0175 | 11.8863 | 14.2558 | 16.0797 | 17.9001
ArmstrongIce Accretion2070RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2070 | 10.032 | 11.9014 | 14.274 | 16.1002 | 17.9197
ArmstrongIce Accretion2075RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2075 | 10.0471 | 11.9212 | 14.2978 | 16.1272 | 17.9525
ArmstrongIce Accretion2080RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2080 | 10.0622 | 11.9409 | 14.3217 | 16.1541 | 17.9852
ArmstrongIce Accretion2085RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2085 | 10.0772 | 11.9607 | 14.3455 | 16.181 | 18.018
ArmstrongIce Accretion2090RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2090 | 10.0923 | 11.9805 | 14.3693 | 16.208 | 18.0508
ArmstrongIce Accretion2095RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2095 | 10.1074 | 12.0003 | 14.3932 | 16.2349 | 18.0835
ArmstrongIce Accretion2100RCP4.5 | Armstrong | Ice Accretion | RCP4.5 | 2100 | 10.1225 | 12.0201 | 14.417 | 16.2618 | 18.1163
ArmstrongIce Accretion2023RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2023 | 9.2721 | 11.0382 | 13.299 | 15.0132 | 16.7404
ArmstrongIce Accretion2025RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2025 | 9.3867 | 11.1694 | 13.4463 | 15.1772 | 16.9205
ArmstrongIce Accretion2030RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2030 | 9.5013 | 11.3007 | 13.5937 | 15.3413 | 17.1007
ArmstrongIce Accretion2035RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2035 | 9.6159 | 11.432 | 13.741 | 15.5053 | 17.2809
ArmstrongIce Accretion2040RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2040 | 9.7305 | 11.5633 | 13.8883 | 15.6693 | 17.4611
ArmstrongIce Accretion2045RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2045 | 9.8451 | 11.6946 | 14.0357 | 15.8334 | 17.6413
ArmstrongIce Accretion2050RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2050 | 9.9741 | 11.8409 | 14.2012 | 16.018 | 17.8411
ArmstrongIce Accretion2055RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2055 | 9.9886 | 11.8561 | 14.2194 | 16.0385 | 17.8608
ArmstrongIce Accretion2060RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2060 | 10.0031 | 11.8712 | 14.2376 | 16.0591 | 17.8804
ArmstrongIce Accretion2065RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2065 | 10.0175 | 11.8863 | 14.2558 | 16.0797 | 17.9001
ArmstrongIce Accretion2070RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2070 | 10.032 | 11.9014 | 14.274 | 16.1002 | 17.9197
ArmstrongIce Accretion2075RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2075 | 10.0546 | 11.931 | 14.3098 | 16.1406 | 17.9689
ArmstrongIce Accretion2080RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2080 | 10.0772 | 11.9607 | 14.3455 | 16.181 | 18.018
ArmstrongIce Accretion2085RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2085 | 10.0999 | 11.9904 | 14.3812 | 16.2214 | 18.0671
ArmstrongIce Accretion2090RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2090 | 10.0863 | 11.9913 | 14.3953 | 16.2471 | 18.0999
ArmstrongIce Accretion2095RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2095 | 10.0501 | 11.9625 | 14.3737 | 16.2324 | 18.0835
ArmstrongIce Accretion2100RCP6.0 | Armstrong | Ice Accretion | RCP6.0 | 2100 | 10.0139 | 11.9337 | 14.352 | 16.2178 | 18.0671
ArmstrongIce Accretion2023RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2023 | 9.2721 | 11.0382 | 13.299 | 15.0132 | 16.7404
ArmstrongIce Accretion2025RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2025 | 9.5013 | 11.3007 | 13.5937 | 15.3413 | 17.1007
ArmstrongIce Accretion2030RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2030 | 9.7305 | 11.5633 | 13.8883 | 15.6693 | 17.4611
ArmstrongIce Accretion2035RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2035 | 9.9596 | 11.8258 | 14.183 | 15.9974 | 17.8214
ArmstrongIce Accretion2040RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2040 | 9.9838 | 11.851 | 14.2133 | 16.0317 | 17.8542
ArmstrongIce Accretion2045RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2045 | 10.0079 | 11.8762 | 14.2437 | 16.066 | 17.887
ArmstrongIce Accretion2050RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2050 | 10.0622 | 11.9409 | 14.3217 | 16.1541 | 17.9852
ArmstrongIce Accretion2055RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2055 | 10.0923 | 11.9805 | 14.3693 | 16.208 | 18.0508
ArmstrongIce Accretion2060RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2060 | 10.0863 | 11.9913 | 14.3953 | 16.2471 | 18.0999
ArmstrongIce Accretion2065RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2065 | 10.0501 | 11.9625 | 14.3737 | 16.2324 | 18.0835
ArmstrongIce Accretion2070RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2070 | 10.0772 | 12.0129 | 14.4603 | 16.3402 | 18.2091
ArmstrongIce Accretion2075RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2075 | 10.1406 | 12.092 | 14.5687 | 16.4626 | 18.3511
ArmstrongIce Accretion2080RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2080 | 10.2039 | 12.1711 | 14.677 | 16.585 | 18.493
ArmstrongIce Accretion2085RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2085 | 10.0184 | 11.9661 | 14.4365 | 16.3206 | 18.1982
ArmstrongIce Accretion2090RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2090 | 9.833 | 11.7611 | 14.196 | 16.0562 | 17.9033
ArmstrongIce Accretion2095RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2095 | 9.833 | 11.7611 | 14.196 | 16.0562 | 17.9033
ArmstrongIce Accretion2100RCP8.5 | Armstrong | Ice Accretion | RCP8.5 | 2100 | 9.833 | 11.7611 | 14.196 | 16.0562 | 17.9033
ArmstrongWind2023RCP4.5 | Armstrong | Wind | RCP4.5 | 2023 | 71.5974 | 77.0588 | 82.7925 | 88.5347 | 94.2888
ArmstrongWind2025RCP4.5 | Armstrong | Wind | RCP4.5 | 2025 | 71.7144 | 77.1964 | 82.9544 | 88.7197 | 94.4938
ArmstrongWind2030RCP4.5 | Armstrong | Wind | RCP4.5 | 2030 | 71.8315 | 77.3341 | 83.1162 | 88.9047 | 94.6988
ArmstrongWind2035RCP4.5 | Armstrong | Wind | RCP4.5 | 2035 | 71.9486 | 77.4717 | 83.2781 | 89.0898 | 94.9039
ArmstrongWind2040RCP4.5 | Armstrong | Wind | RCP4.5 | 2040 | 72.0656 | 77.6094 | 83.4399 | 89.2748 | 95.1089
ArmstrongWind2045RCP4.5 | Armstrong | Wind | RCP4.5 | 2045 | 72.1827 | 77.7471 | 83.6018 | 89.4598 | 95.3139
ArmstrongWind2050RCP4.5 | Armstrong | Wind | RCP4.5 | 2050 | 72.4187 | 78.0237 | 83.9279 | 89.8313 | 95.7289
ArmstrongWind2055RCP4.5 | Armstrong | Wind | RCP4.5 | 2055 | 72.5377 | 78.1626 | 84.0923 | 90.0178 | 95.939
ArmstrongWind2060RCP4.5 | Armstrong | Wind | RCP4.5 | 2060 | 72.6566 | 78.3015 | 84.2566 | 90.2043 | 96.1491
ArmstrongWind2065RCP4.5 | Armstrong | Wind | RCP4.5 | 2065 | 72.7756 | 78.4405 | 84.421 | 90.3908 | 96.3591
ArmstrongWind2070RCP4.5 | Armstrong | Wind | RCP4.5 | 2070 | 72.8946 | 78.5794 | 84.5853 | 90.5773 | 96.5692
ArmstrongWind2075RCP4.5 | Armstrong | Wind | RCP4.5 | 2075 | 72.9746 | 78.6708 | 84.6877 | 90.6898 | 96.6922
ArmstrongWind2080RCP4.5 | Armstrong | Wind | RCP4.5 | 2080 | 73.0546 | 78.7621 | 84.79 | 90.8023 | 96.8152
ArmstrongWind2085RCP4.5 | Armstrong | Wind | RCP4.5 | 2085 | 73.1347 | 78.8534 | 84.8924 | 90.9148 | 96.9382
ArmstrongWind2090RCP4.5 | Armstrong | Wind | RCP4.5 | 2090 | 73.2147 | 78.9448 | 84.9948 | 91.0273 | 97.0612
ArmstrongWind2095RCP4.5 | Armstrong | Wind | RCP4.5 | 2095 | 73.2947 | 79.0361 | 85.0971 | 91.1398 | 97.1842
ArmstrongWind2100RCP4.5 | Armstrong | Wind | RCP4.5 | 2100 | 73.3748 | 79.1275 | 85.1995 | 91.2523 | 97.3072
ArmstrongWind2023RCP6.0 | Armstrong | Wind | RCP6.0 | 2023 | 71.5974 | 77.0588 | 82.7925 | 88.5347 | 94.2888
ArmstrongWind2025RCP6.0 | Armstrong | Wind | RCP6.0 | 2025 | 71.7144 | 77.1964 | 82.9544 | 88.7197 | 94.4938
ArmstrongWind2030RCP6.0 | Armstrong | Wind | RCP6.0 | 2030 | 71.8315 | 77.3341 | 83.1162 | 88.9047 | 94.6988
ArmstrongWind2035RCP6.0 | Armstrong | Wind | RCP6.0 | 2035 | 71.9486 | 77.4717 | 83.2781 | 89.0898 | 94.9039
ArmstrongWind2040RCP6.0 | Armstrong | Wind | RCP6.0 | 2040 | 72.0656 | 77.6094 | 83.4399 | 89.2748 | 95.1089
ArmstrongWind2045RCP6.0 | Armstrong | Wind | RCP6.0 | 2045 | 72.1827 | 77.7471 | 83.6018 | 89.4598 | 95.3139
ArmstrongWind2050RCP6.0 | Armstrong | Wind | RCP6.0 | 2050 | 72.4187 | 78.0237 | 83.9279 | 89.8313 | 95.7289
ArmstrongWind2055RCP6.0 | Armstrong | Wind | RCP6.0 | 2055 | 72.5377 | 78.1626 | 84.0923 | 90.0178 | 95.939
ArmstrongWind2060RCP6.0 | Armstrong | Wind | RCP6.0 | 2060 | 72.6566 | 78.3015 | 84.2566 | 90.2043 | 96.1491
ArmstrongWind2065RCP6.0 | Armstrong | Wind | RCP6.0 | 2065 | 72.7756 | 78.4405 | 84.421 | 90.3908 | 96.3591
ArmstrongWind2070RCP6.0 | Armstrong | Wind | RCP6.0 | 2070 | 72.8946 | 78.5794 | 84.5853 | 90.5773 | 96.5692
ArmstrongWind2075RCP6.0 | Armstrong | Wind | RCP6.0 | 2075 | 73.0146 | 78.7164 | 84.7388 | 90.7461 | 96.7537
ArmstrongWind2080RCP6.0 | Armstrong | Wind | RCP6.0 | 2080 | 73.1347 | 78.8534 | 84.8924 | 90.9148 | 96.9382
ArmstrongWind2085RCP6.0 | Armstrong | Wind | RCP6.0 | 2085 | 73.2547 | 78.9905 | 85.046 | 91.0835 | 97.1227
ArmstrongWind2090RCP6.0 | Armstrong | Wind | RCP6.0 | 2090 | 73.3461 | 79.094 | 85.1608 | 91.2079 | 97.2599
ArmstrongWind2095RCP6.0 | Armstrong | Wind | RCP6.0 | 2095 | 73.3174 | 79.0606 | 85.122 | 91.1635 | 97.2126
ArmstrongWind2100RCP6.0 | Armstrong | Wind | RCP6.0 | 2100 | 73.2888 | 79.0271 | 85.0833 | 91.1191 | 97.1653
ArmstrongWind2023RCP8.5 | Armstrong | Wind | RCP8.5 | 2023 | 71.5974 | 77.0588 | 82.7925 | 88.5347 | 94.2888
ArmstrongWind2025RCP8.5 | Armstrong | Wind | RCP8.5 | 2025 | 71.8315 | 77.3341 | 83.1162 | 88.9047 | 94.6988
ArmstrongWind2030RCP8.5 | Armstrong | Wind | RCP8.5 | 2030 | 72.0656 | 77.6094 | 83.4399 | 89.2748 | 95.1089
ArmstrongWind2035RCP8.5 | Armstrong | Wind | RCP8.5 | 2035 | 72.2997 | 77.8847 | 83.7636 | 89.6448 | 95.5189
ArmstrongWind2040RCP8.5 | Armstrong | Wind | RCP8.5 | 2040 | 72.498 | 78.1163 | 84.0375 | 89.9556 | 95.869
ArmstrongWind2045RCP8.5 | Armstrong | Wind | RCP8.5 | 2045 | 72.6963 | 78.3478 | 84.3114 | 90.2665 | 96.2191
ArmstrongWind2050RCP8.5 | Armstrong | Wind | RCP8.5 | 2050 | 73.0546 | 78.7621 | 84.79 | 90.8023 | 96.8152
ArmstrongWind2055RCP8.5 | Armstrong | Wind | RCP8.5 | 2055 | 73.2147 | 78.9448 | 84.9948 | 91.0273 | 97.0612
ArmstrongWind2060RCP8.5 | Armstrong | Wind | RCP8.5 | 2060 | 73.3461 | 79.094 | 85.1608 | 91.2079 | 97.2599
ArmstrongWind2065RCP8.5 | Armstrong | Wind | RCP8.5 | 2065 | 73.3174 | 79.0606 | 85.122 | 91.1635 | 97.2126
ArmstrongWind2070RCP8.5 | Armstrong | Wind | RCP8.5 | 2070 | 73.4608 | 79.2458 | 85.36 | 91.4447 | 97.5374
ArmstrongWind2075RCP8.5 | Armstrong | Wind | RCP8.5 | 2075 | 73.6328 | 79.4645 | 85.6366 | 91.7703 | 97.9096
ArmstrongWind2080RCP8.5 | Armstrong | Wind | RCP8.5 | 2080 | 73.8048 | 79.6832 | 85.9133 | 92.096 | 98.2818
ArmstrongWind2085RCP8.5 | Armstrong | Wind | RCP8.5 | 2085 | 73.8227 | 79.6987 | 85.9299 | 92.1137 | 98.3007
ArmstrongWind2090RCP8.5 | Armstrong | Wind | RCP8.5 | 2090 | 73.8406 | 79.7141 | 85.9465 | 92.1315 | 98.3196
ArmstrongWind2095RCP8.5 | Armstrong | Wind | RCP8.5 | 2095 | 73.8406 | 79.7141 | 85.9465 | 92.1315 | 98.3196
ArmstrongWind2100RCP8.5 | Armstrong | Wind | RCP8.5 | 2100 | 73.8406 | 79.7141 | 85.9465 | 92.1315 | 98.3196
ArnpriorIce Accretion2023RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2023 | 18.5812 | 22.0739 | 26.514 | 29.8998 | 33.3056
ArnpriorIce Accretion2025RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2025 | 18.578 | 22.0664 | 26.5005 | 29.8845 | 33.2829
ArnpriorIce Accretion2030RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2030 | 18.5749 | 22.0589 | 26.487 | 29.8693 | 33.2602
ArnpriorIce Accretion2035RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2035 | 18.5718 | 22.0514 | 26.4735 | 29.854 | 33.2375
ArnpriorIce Accretion2040RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2040 | 18.5687 | 22.044 | 26.46 | 29.8388 | 33.2149
ArnpriorIce Accretion2045RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2045 | 18.5655 | 22.0365 | 26.4465 | 29.8235 | 33.1922
ArnpriorIce Accretion2050RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2050 | 18.5737 | 22.0604 | 26.4924 | 29.8876 | 33.2648
ArnpriorIce Accretion2055RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2055 | 18.5849 | 22.0918 | 26.5518 | 29.9669 | 33.36
ArnpriorIce Accretion2060RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2060 | 18.5962 | 22.1232 | 26.6112 | 30.0462 | 33.4553
ArnpriorIce Accretion2065RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2065 | 18.6075 | 22.1545 | 26.6706 | 30.1256 | 33.5505
ArnpriorIce Accretion2070RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2070 | 18.6188 | 22.1859 | 26.73 | 30.2049 | 33.6458
ArnpriorIce Accretion2075RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2075 | 18.6876 | 22.2942 | 26.883 | 30.393 | 33.8726
ArnpriorIce Accretion2080RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2080 | 18.7565 | 22.4025 | 27.036 | 30.5812 | 34.0994
ArnpriorIce Accretion2085RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2085 | 18.8254 | 22.5108 | 27.189 | 30.7693 | 34.3262
ArnpriorIce Accretion2090RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2090 | 18.8943 | 22.6192 | 27.342 | 30.9575 | 34.553
ArnpriorIce Accretion2095RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2095 | 18.9632 | 22.7275 | 27.495 | 31.1456 | 34.7798
ArnpriorIce Accretion2100RCP4.5 | Arnprior | Ice Accretion | RCP4.5 | 2100 | 19.0321 | 22.8358 | 27.648 | 31.3338 | 35.0066
ArnpriorIce Accretion2023RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2023 | 18.5812 | 22.0739 | 26.514 | 29.8998 | 33.3056
ArnpriorIce Accretion2025RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2025 | 18.578 | 22.0664 | 26.5005 | 29.8845 | 33.2829
ArnpriorIce Accretion2030RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2030 | 18.5749 | 22.0589 | 26.487 | 29.8693 | 33.2602
ArnpriorIce Accretion2035RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2035 | 18.5718 | 22.0514 | 26.4735 | 29.854 | 33.2375
ArnpriorIce Accretion2040RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2040 | 18.5687 | 22.044 | 26.46 | 29.8388 | 33.2149
ArnpriorIce Accretion2045RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2045 | 18.5655 | 22.0365 | 26.4465 | 29.8235 | 33.1922
ArnpriorIce Accretion2050RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2050 | 18.5737 | 22.0604 | 26.4924 | 29.8876 | 33.2648
ArnpriorIce Accretion2055RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2055 | 18.5849 | 22.0918 | 26.5518 | 29.9669 | 33.36
ArnpriorIce Accretion2060RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2060 | 18.5962 | 22.1232 | 26.6112 | 30.0462 | 33.4553
ArnpriorIce Accretion2065RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2065 | 18.6075 | 22.1545 | 26.6706 | 30.1256 | 33.5505
ArnpriorIce Accretion2070RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2070 | 18.6188 | 22.1859 | 26.73 | 30.2049 | 33.6458
ArnpriorIce Accretion2075RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2075 | 18.7221 | 22.3484 | 26.9595 | 30.4871 | 33.986
ArnpriorIce Accretion2080RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2080 | 18.8254 | 22.5108 | 27.189 | 30.7693 | 34.3262
ArnpriorIce Accretion2085RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2085 | 18.9288 | 22.6733 | 27.4185 | 31.0516 | 34.6664
ArnpriorIce Accretion2090RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2090 | 19.0383 | 22.8881 | 27.765 | 31.4863 | 35.1994
ArnpriorIce Accretion2095RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2095 | 19.0446 | 22.9404 | 27.882 | 31.6389 | 35.3921
ArnpriorIce Accretion2100RCP6.0 | Arnprior | Ice Accretion | RCP6.0 | 2100 | 19.0509 | 22.9927 | 27.999 | 31.7914 | 35.5849
ArnpriorIce Accretion2023RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2023 | 18.5812 | 22.0739 | 26.514 | 29.8998 | 33.3056
ArnpriorIce Accretion2025RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2025 | 18.5749 | 22.0589 | 26.487 | 29.8693 | 33.2602
ArnpriorIce Accretion2030RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2030 | 18.5687 | 22.044 | 26.46 | 29.8388 | 33.2149
ArnpriorIce Accretion2035RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2035 | 18.5624 | 22.029 | 26.433 | 29.8083 | 33.1695
ArnpriorIce Accretion2040RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2040 | 18.5812 | 22.0813 | 26.532 | 29.9405 | 33.3283
ArnpriorIce Accretion2045RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2045 | 18.6 | 22.1336 | 26.631 | 30.0727 | 33.487
ArnpriorIce Accretion2050RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2050 | 18.7565 | 22.4025 | 27.036 | 30.5812 | 34.0994
ArnpriorIce Accretion2055RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2055 | 18.8943 | 22.6192 | 27.342 | 30.9575 | 34.553
ArnpriorIce Accretion2060RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2060 | 19.0383 | 22.8881 | 27.765 | 31.4863 | 35.1994
ArnpriorIce Accretion2065RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2065 | 19.0446 | 22.9404 | 27.882 | 31.6389 | 35.3921
ArnpriorIce Accretion2070RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2070 | 18.9507 | 22.9105 | 27.936 | 31.7507 | 35.5622
ArnpriorIce Accretion2075RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2075 | 18.8505 | 22.8283 | 27.873 | 31.7101 | 35.5396
ArnpriorIce Accretion2080RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2080 | 18.7503 | 22.7461 | 27.81 | 31.6694 | 35.5169
ArnpriorIce Accretion2085RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2085 | 18.1585 | 22.0739 | 27.027 | 30.7998 | 34.5643
ArnpriorIce Accretion2090RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2090 | 17.5666 | 21.4016 | 26.244 | 29.9303 | 33.6118
ArnpriorIce Accretion2095RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2095 | 17.5666 | 21.4016 | 26.244 | 29.9303 | 33.6118
ArnpriorIce Accretion2100RCP8.5 | Arnprior | Ice Accretion | RCP8.5 | 2100 | 17.5666 | 21.4016 | 26.244 | 29.9303 | 33.6118
ArnpriorWind2023RCP4.5 | Arnprior | Wind | RCP4.5 | 2023 | 76.3208 | 82.3065 | 88.6248 | 94.9227 | 101.2229
ArnpriorWind2025RCP4.5 | Arnprior | Wind | RCP4.5 | 2025 | 76.4094 | 82.4197 | 88.77 | 95.0938 | 101.4218
ArnpriorWind2030RCP4.5 | Arnprior | Wind | RCP4.5 | 2030 | 76.4981 | 82.5329 | 88.9152 | 95.2648 | 101.6208
ArnpriorWind2035RCP4.5 | Arnprior | Wind | RCP4.5 | 2035 | 76.5867 | 82.6461 | 89.0604 | 95.4359 | 101.8198
ArnpriorWind2040RCP4.5 | Arnprior | Wind | RCP4.5 | 2040 | 76.6754 | 82.7593 | 89.2056 | 95.6069 | 102.0188
ArnpriorWind2045RCP4.5 | Arnprior | Wind | RCP4.5 | 2045 | 76.764 | 82.8725 | 89.3508 | 95.778 | 102.2177
ArnpriorWind2050RCP4.5 | Arnprior | Wind | RCP4.5 | 2050 | 76.7661 | 82.8679 | 89.3394 | 95.7588 | 102.192
ArnpriorWind2055RCP4.5 | Arnprior | Wind | RCP4.5 | 2055 | 76.6795 | 82.7501 | 89.1827 | 95.5686 | 101.9673
ArnpriorWind2060RCP4.5 | Arnprior | Wind | RCP4.5 | 2060 | 76.5928 | 82.6322 | 89.0261 | 95.3784 | 101.7425
ArnpriorWind2065RCP4.5 | Arnprior | Wind | RCP4.5 | 2065 | 76.5062 | 82.5144 | 88.8694 | 95.1882 | 101.5178
ArnpriorWind2070RCP4.5 | Arnprior | Wind | RCP4.5 | 2070 | 76.4196 | 82.3965 | 88.7128 | 94.998 | 101.2931
ArnpriorWind2075RCP4.5 | Arnprior | Wind | RCP4.5 | 2075 | 76.4614 | 82.4511 | 88.7817 | 95.0796 | 101.3884
ArnpriorWind2080RCP4.5 | Arnprior | Wind | RCP4.5 | 2080 | 76.5032 | 82.5056 | 88.8507 | 95.1612 | 101.4837
ArnpriorWind2085RCP4.5 | Arnprior | Wind | RCP4.5 | 2085 | 76.545 | 82.5602 | 88.9196 | 95.2428 | 101.579
ArnpriorWind2090RCP4.5 | Arnprior | Wind | RCP4.5 | 2090 | 76.5867 | 82.6148 | 88.9885 | 95.3244 | 101.6743
ArnpriorWind2095RCP4.5 | Arnprior | Wind | RCP4.5 | 2095 | 76.6285 | 82.6693 | 89.0575 | 95.4061 | 101.7696
ArnpriorWind2100RCP4.5 | Arnprior | Wind | RCP4.5 | 2100 | 76.6703 | 82.7239 | 89.1264 | 95.4877 | 101.8649
ArnpriorWind2023RCP6.0 | Arnprior | Wind | RCP6.0 | 2023 | 76.3208 | 82.3065 | 88.6248 | 94.9227 | 101.2229
ArnpriorWind2025RCP6.0 | Arnprior | Wind | RCP6.0 | 2025 | 76.4094 | 82.4197 | 88.77 | 95.0938 | 101.4218
ArnpriorWind2030RCP6.0 | Arnprior | Wind | RCP6.0 | 2030 | 76.4981 | 82.5329 | 88.9152 | 95.2648 | 101.6208
ArnpriorWind2035RCP6.0 | Arnprior | Wind | RCP6.0 | 2035 | 76.5867 | 82.6461 | 89.0604 | 95.4359 | 101.8198
ArnpriorWind2040RCP6.0 | Arnprior | Wind | RCP6.0 | 2040 | 76.6754 | 82.7593 | 89.2056 | 95.6069 | 102.0188
ArnpriorWind2045RCP6.0 | Arnprior | Wind | RCP6.0 | 2045 | 76.764 | 82.8725 | 89.3508 | 95.778 | 102.2177
ArnpriorWind2050RCP6.0 | Arnprior | Wind | RCP6.0 | 2050 | 76.7661 | 82.8679 | 89.3394 | 95.7588 | 102.192
ArnpriorWind2055RCP6.0 | Arnprior | Wind | RCP6.0 | 2055 | 76.6795 | 82.7501 | 89.1827 | 95.5686 | 101.9673
ArnpriorWind2060RCP6.0 | Arnprior | Wind | RCP6.0 | 2060 | 76.5928 | 82.6322 | 89.0261 | 95.3784 | 101.7425
ArnpriorWind2065RCP6.0 | Arnprior | Wind | RCP6.0 | 2065 | 76.5062 | 82.5144 | 88.8694 | 95.1882 | 101.5178
ArnpriorWind2070RCP6.0 | Arnprior | Wind | RCP6.0 | 2070 | 76.4196 | 82.3965 | 88.7128 | 94.998 | 101.2931
ArnpriorWind2075RCP6.0 | Arnprior | Wind | RCP6.0 | 2075 | 76.4823 | 82.4784 | 88.8162 | 95.1204 | 101.4361
ArnpriorWind2080RCP6.0 | Arnprior | Wind | RCP6.0 | 2080 | 76.545 | 82.5602 | 88.9196 | 95.2428 | 101.579
ArnpriorWind2085RCP6.0 | Arnprior | Wind | RCP6.0 | 2085 | 76.6076 | 82.642 | 89.023 | 95.3652 | 101.722
ArnpriorWind2090RCP6.0 | Arnprior | Wind | RCP6.0 | 2090 | 76.488 | 82.4865 | 88.8213 | 95.1298 | 101.4469
ArnpriorWind2095RCP6.0 | Arnprior | Wind | RCP6.0 | 2095 | 76.3056 | 82.2492 | 88.5163 | 94.772 | 101.0289
ArnpriorWind2100RCP6.0 | Arnprior | Wind | RCP6.0 | 2100 | 76.1232 | 82.0119 | 88.2112 | 94.4142 | 100.6109
ArnpriorWind2023RCP8.5 | Arnprior | Wind | RCP8.5 | 2023 | 76.3208 | 82.3065 | 88.6248 | 94.9227 | 101.2229
ArnpriorWind2025RCP8.5 | Arnprior | Wind | RCP8.5 | 2025 | 76.4981 | 82.5329 | 88.9152 | 95.2648 | 101.6208
ArnpriorWind2030RCP8.5 | Arnprior | Wind | RCP8.5 | 2030 | 76.6754 | 82.7593 | 89.2056 | 95.6069 | 102.0188
ArnpriorWind2035RCP8.5 | Arnprior | Wind | RCP8.5 | 2035 | 76.8527 | 82.9858 | 89.496 | 95.949 | 102.4167
ArnpriorWind2040RCP8.5 | Arnprior | Wind | RCP8.5 | 2040 | 76.7083 | 82.7893 | 89.2349 | 95.632 | 102.0422
ArnpriorWind2045RCP8.5 | Arnprior | Wind | RCP8.5 | 2045 | 76.564 | 82.5929 | 88.9739 | 95.315 | 101.6676
ArnpriorWind2050RCP8.5 | Arnprior | Wind | RCP8.5 | 2050 | 76.5032 | 82.5056 | 88.8507 | 95.1612 | 101.4837
ArnpriorWind2055RCP8.5 | Arnprior | Wind | RCP8.5 | 2055 | 76.5867 | 82.6148 | 88.9885 | 95.3244 | 101.6743
ArnpriorWind2060RCP8.5 | Arnprior | Wind | RCP8.5 | 2060 | 76.488 | 82.4865 | 88.8213 | 95.1298 | 101.4469
ArnpriorWind2065RCP8.5 | Arnprior | Wind | RCP8.5 | 2065 | 76.3056 | 82.2492 | 88.5163 | 94.772 | 101.0289
ArnpriorWind2070RCP8.5 | Arnprior | Wind | RCP8.5 | 2070 | 76.0928 | 81.9573 | 88.1261 | 94.3012 | 100.4705
ArnpriorWind2075RCP8.5 | Arnprior | Wind | RCP8.5 | 2075 | 76.0624 | 81.9027 | 88.0411 | 94.1882 | 100.33
ArnpriorWind2080RCP8.5 | Arnprior | Wind | RCP8.5 | 2080 | 76.032 | 81.8482 | 87.956 | 94.0753 | 100.1896
ArnpriorWind2085RCP8.5 | Arnprior | Wind | RCP8.5 | 2085 | 75.8231 | 81.5945 | 87.648 | 93.7222 | 99.7883
ArnpriorWind2090RCP8.5 | Arnprior | Wind | RCP8.5 | 2090 | 75.6141 | 81.3408 | 87.34 | 93.3691 | 99.387
ArnpriorWind2095RCP8.5 | Arnprior | Wind | RCP8.5 | 2095 | 75.6141 | 81.3408 | 87.34 | 93.3691 | 99.387
ArnpriorWind2100RCP8.5 | Arnprior | Wind | RCP8.5 | 2100 | 75.6141 | 81.3408 | 87.34 | 93.3691 | 99.387
AtikokanIce Accretion2023RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2023 | 11.0118 | 13.1472 | 15.84 | 17.8992 | 19.9584
AtikokanIce Accretion2025RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2025 | 11.0205 | 13.1555 | 15.8525 | 17.9133 | 19.9742
AtikokanIce Accretion2030RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2030 | 11.0292 | 13.1638 | 15.865 | 17.9275 | 19.9899
AtikokanIce Accretion2035RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2035 | 11.0379 | 13.1721 | 15.8775 | 17.9416 | 20.0056
AtikokanIce Accretion2040RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2040 | 11.0466 | 13.1804 | 15.89 | 17.9557 | 20.0214
AtikokanIce Accretion2045RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2045 | 11.0553 | 13.1887 | 15.9025 | 17.9698 | 20.0371
AtikokanIce Accretion2050RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2050 | 11.018 | 13.1347 | 15.828 | 17.8822 | 19.9357
AtikokanIce Accretion2055RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2055 | 10.9721 | 13.0725 | 15.741 | 17.7805 | 19.8185
AtikokanIce Accretion2060RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2060 | 10.9262 | 13.0102 | 15.654 | 17.6788 | 19.7014
AtikokanIce Accretion2065RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2065 | 10.8802 | 12.948 | 15.567 | 17.5771 | 19.5842
AtikokanIce Accretion2070RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2070 | 10.8343 | 12.8857 | 15.48 | 17.4754 | 19.467
AtikokanIce Accretion2075RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2075 | 10.8187 | 12.8691 | 15.465 | 17.4613 | 19.4512
AtikokanIce Accretion2080RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2080 | 10.803 | 12.8525 | 15.45 | 17.4472 | 19.4355
AtikokanIce Accretion2085RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2085 | 10.7874 | 12.8359 | 15.435 | 17.4331 | 19.4197
AtikokanIce Accretion2090RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2090 | 10.7717 | 12.8193 | 15.42 | 17.4189 | 19.404
AtikokanIce Accretion2095RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2095 | 10.756 | 12.8027 | 15.405 | 17.4048 | 19.3882
AtikokanIce Accretion2100RCP4.5 | Atikokan | Ice Accretion | RCP4.5 | 2100 | 10.7404 | 12.7861 | 15.39 | 17.3907 | 19.3725
AtikokanIce Accretion2023RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2023 | 11.0118 | 13.1472 | 15.84 | 17.8992 | 19.9584
AtikokanIce Accretion2025RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2025 | 11.0205 | 13.1555 | 15.8525 | 17.9133 | 19.9742
AtikokanIce Accretion2030RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2030 | 11.0292 | 13.1638 | 15.865 | 17.9275 | 19.9899
AtikokanIce Accretion2035RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2035 | 11.0379 | 13.1721 | 15.8775 | 17.9416 | 20.0056
AtikokanIce Accretion2040RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2040 | 11.0466 | 13.1804 | 15.89 | 17.9557 | 20.0214
AtikokanIce Accretion2045RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2045 | 11.0553 | 13.1887 | 15.9025 | 17.9698 | 20.0371
AtikokanIce Accretion2050RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2050 | 11.018 | 13.1347 | 15.828 | 17.8822 | 19.9357
AtikokanIce Accretion2055RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2055 | 10.9721 | 13.0725 | 15.741 | 17.7805 | 19.8185
AtikokanIce Accretion2060RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2060 | 10.9262 | 13.0102 | 15.654 | 17.6788 | 19.7014
AtikokanIce Accretion2065RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2065 | 10.8802 | 12.948 | 15.567 | 17.5771 | 19.5842
AtikokanIce Accretion2070RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2070 | 10.8343 | 12.8857 | 15.48 | 17.4754 | 19.467
AtikokanIce Accretion2075RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2075 | 10.8108 | 12.8608 | 15.4575 | 17.4543 | 19.4434
AtikokanIce Accretion2080RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2080 | 10.7874 | 12.8359 | 15.435 | 17.4331 | 19.4197
AtikokanIce Accretion2085RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2085 | 10.7639 | 12.811 | 15.4125 | 17.4119 | 19.3961
AtikokanIce Accretion2090RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2090 | 10.7752 | 12.8359 | 15.46 | 17.4698 | 19.467
AtikokanIce Accretion2095RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2095 | 10.81 | 12.8857 | 15.53 | 17.5489 | 19.5615
AtikokanIce Accretion2100RCP6.0 | Atikokan | Ice Accretion | RCP6.0 | 2100 | 10.8448 | 12.9355 | 15.6 | 17.628 | 19.656
AtikokanIce Accretion2023RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2023 | 11.0118 | 13.1472 | 15.84 | 17.8992 | 19.9584
AtikokanIce Accretion2025RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2025 | 11.0292 | 13.1638 | 15.865 | 17.9275 | 19.9899
AtikokanIce Accretion2030RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2030 | 11.0466 | 13.1804 | 15.89 | 17.9557 | 20.0214
AtikokanIce Accretion2035RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2035 | 11.064 | 13.197 | 15.915 | 17.9839 | 20.0529
AtikokanIce Accretion2040RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2040 | 10.9874 | 13.0932 | 15.77 | 17.8144 | 19.8576
AtikokanIce Accretion2045RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2045 | 10.9109 | 12.9895 | 15.625 | 17.6449 | 19.6623
AtikokanIce Accretion2050RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2050 | 10.803 | 12.8525 | 15.45 | 17.4472 | 19.4355
AtikokanIce Accretion2055RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2055 | 10.7717 | 12.8193 | 15.42 | 17.4189 | 19.404
AtikokanIce Accretion2060RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2060 | 10.7752 | 12.8359 | 15.46 | 17.4698 | 19.467
AtikokanIce Accretion2065RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2065 | 10.81 | 12.8857 | 15.53 | 17.5489 | 19.5615
AtikokanIce Accretion2070RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2070 | 10.7961 | 12.8899 | 15.555 | 17.5828 | 19.6119
AtikokanIce Accretion2075RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2075 | 10.7473 | 12.8442 | 15.51 | 17.5376 | 19.5678
AtikokanIce Accretion2080RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2080 | 10.6986 | 12.7986 | 15.465 | 17.4924 | 19.5237
AtikokanIce Accretion2085RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2085 | 10.3333 | 12.3628 | 14.94 | 16.8991 | 18.8622
AtikokanIce Accretion2090RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2090 | 9.968 | 11.9271 | 14.415 | 16.3059 | 18.2007
AtikokanIce Accretion2095RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2095 | 9.968 | 11.9271 | 14.415 | 16.3059 | 18.2007
AtikokanIce Accretion2100RCP8.5 | Atikokan | Ice Accretion | RCP8.5 | 2100 | 9.968 | 11.9271 | 14.415 | 16.3059 | 18.2007
AtikokanWind2023RCP4.5 | Atikokan | Wind | RCP4.5 | 2023 | 74.2149 | 79.916 | 85.914 | 91.9096 | 97.9125
AtikokanWind2025RCP4.5 | Atikokan | Wind | RCP4.5 | 2025 | 74.2818 | 79.9933 | 86.0043 | 92.0108 | 98.0253
AtikokanWind2030RCP4.5 | Atikokan | Wind | RCP4.5 | 2030 | 74.3486 | 80.0706 | 86.0946 | 92.112 | 98.138
AtikokanWind2035RCP4.5 | Atikokan | Wind | RCP4.5 | 2035 | 74.4154 | 80.148 | 86.1849 | 92.2132 | 98.2508
AtikokanWind2040RCP4.5 | Atikokan | Wind | RCP4.5 | 2040 | 74.4823 | 80.2253 | 86.2752 | 92.3145 | 98.3635
AtikokanWind2045RCP4.5 | Atikokan | Wind | RCP4.5 | 2045 | 74.5491 | 80.3026 | 86.3655 | 92.4157 | 98.4763
AtikokanWind2050RCP4.5 | Atikokan | Wind | RCP4.5 | 2050 | 74.6932 | 80.4743 | 86.571 | 92.6531 | 98.7439
AtikokanWind2055RCP4.5 | Atikokan | Wind | RCP4.5 | 2055 | 74.7704 | 80.5687 | 86.6863 | 92.7893 | 98.8988
AtikokanWind2060RCP4.5 | Atikokan | Wind | RCP4.5 | 2060 | 74.8476 | 80.663 | 86.8015 | 92.9255 | 99.0537
AtikokanWind2065RCP4.5 | Atikokan | Wind | RCP4.5 | 2065 | 74.9249 | 80.7574 | 86.9168 | 93.0617 | 99.2086
AtikokanWind2070RCP4.5 | Atikokan | Wind | RCP4.5 | 2070 | 75.0021 | 80.8518 | 87.032 | 93.1979 | 99.3635
AtikokanWind2075RCP4.5 | Atikokan | Wind | RCP4.5 | 2075 | 75.1073 | 80.9811 | 87.1882 | 93.3773 | 99.5662
AtikokanWind2080RCP4.5 | Atikokan | Wind | RCP4.5 | 2080 | 75.2125 | 81.1104 | 87.3445 | 93.5567 | 99.7688
AtikokanWind2085RCP4.5 | Atikokan | Wind | RCP4.5 | 2085 | 75.3177 | 81.2397 | 87.5007 | 93.7362 | 99.9714
AtikokanWind2090RCP4.5 | Atikokan | Wind | RCP4.5 | 2090 | 75.4229 | 81.369 | 87.6569 | 93.9156 | 100.174
AtikokanWind2095RCP4.5 | Atikokan | Wind | RCP4.5 | 2095 | 75.5281 | 81.4983 | 87.8132 | 94.0951 | 100.3766
AtikokanWind2100RCP4.5 | Atikokan | Wind | RCP4.5 | 2100 | 75.6333 | 81.6276 | 87.9694 | 94.2745 | 100.5792
AtikokanWind2023RCP6.0 | Atikokan | Wind | RCP6.0 | 2023 | 74.2149 | 79.916 | 85.914 | 91.9096 | 97.9125
AtikokanWind2025RCP6.0 | Atikokan | Wind | RCP6.0 | 2025 | 74.2818 | 79.9933 | 86.0043 | 92.0108 | 98.0253
AtikokanWind2030RCP6.0 | Atikokan | Wind | RCP6.0 | 2030 | 74.3486 | 80.0706 | 86.0946 | 92.112 | 98.138
AtikokanWind2035RCP6.0 | Atikokan | Wind | RCP6.0 | 2035 | 74.4154 | 80.148 | 86.1849 | 92.2132 | 98.2508
AtikokanWind2040RCP6.0 | Atikokan | Wind | RCP6.0 | 2040 | 74.4823 | 80.2253 | 86.2752 | 92.3145 | 98.3635
AtikokanWind2045RCP6.0 | Atikokan | Wind | RCP6.0 | 2045 | 74.5491 | 80.3026 | 86.3655 | 92.4157 | 98.4763
AtikokanWind2050RCP6.0 | Atikokan | Wind | RCP6.0 | 2050 | 74.6932 | 80.4743 | 86.571 | 92.6531 | 98.7439
AtikokanWind2055RCP6.0 | Atikokan | Wind | RCP6.0 | 2055 | 74.7704 | 80.5687 | 86.6863 | 92.7893 | 98.8988
AtikokanWind2060RCP6.0 | Atikokan | Wind | RCP6.0 | 2060 | 74.8476 | 80.663 | 86.8015 | 92.9255 | 99.0537
AtikokanWind2065RCP6.0 | Atikokan | Wind | RCP6.0 | 2065 | 74.9249 | 80.7574 | 86.9168 | 93.0617 | 99.2086
AtikokanWind2070RCP6.0 | Atikokan | Wind | RCP6.0 | 2070 | 75.0021 | 80.8518 | 87.032 | 93.1979 | 99.3635
AtikokanWind2075RCP6.0 | Atikokan | Wind | RCP6.0 | 2075 | 75.1599 | 81.0457 | 87.2663 | 93.467 | 99.6675
AtikokanWind2080RCP6.0 | Atikokan | Wind | RCP6.0 | 2080 | 75.3177 | 81.2397 | 87.5007 | 93.7362 | 99.9714
AtikokanWind2085RCP6.0 | Atikokan | Wind | RCP6.0 | 2085 | 75.4755 | 81.4336 | 87.7351 | 94.0053 | 100.2753
AtikokanWind2090RCP6.0 | Atikokan | Wind | RCP6.0 | 2090 | 75.8635 | 81.9422 | 88.3965 | 94.7929 | 101.1904
AtikokanWind2095RCP6.0 | Atikokan | Wind | RCP6.0 | 2095 | 76.0937 | 82.2568 | 88.8237 | 95.3112 | 101.8015
AtikokanWind2100RCP6.0 | Atikokan | Wind | RCP6.0 | 2100 | 76.3239 | 82.5714 | 89.2508 | 95.8296 | 102.4126
AtikokanWind2023RCP8.5 | Atikokan | Wind | RCP8.5 | 2023 | 74.2149 | 79.916 | 85.914 | 91.9096 | 97.9125
AtikokanWind2025RCP8.5 | Atikokan | Wind | RCP8.5 | 2025 | 74.3486 | 80.0706 | 86.0946 | 92.112 | 98.138
AtikokanWind2030RCP8.5 | Atikokan | Wind | RCP8.5 | 2030 | 74.4823 | 80.2253 | 86.2752 | 92.3145 | 98.3635
AtikokanWind2035RCP8.5 | Atikokan | Wind | RCP8.5 | 2035 | 74.6159 | 80.3799 | 86.4558 | 92.5169 | 98.589
AtikokanWind2040RCP8.5 | Atikokan | Wind | RCP8.5 | 2040 | 74.7447 | 80.5372 | 86.6479 | 92.7439 | 98.8472
AtikokanWind2045RCP8.5 | Atikokan | Wind | RCP8.5 | 2045 | 74.8734 | 80.6945 | 86.8399 | 92.9709 | 99.1054
AtikokanWind2050RCP8.5 | Atikokan | Wind | RCP8.5 | 2050 | 75.2125 | 81.1104 | 87.3445 | 93.5567 | 99.7688
AtikokanWind2055RCP8.5 | Atikokan | Wind | RCP8.5 | 2055 | 75.4229 | 81.369 | 87.6569 | 93.9156 | 100.174
AtikokanWind2060RCP8.5 | Atikokan | Wind | RCP8.5 | 2060 | 75.8635 | 81.9422 | 88.3965 | 94.7929 | 101.1904
AtikokanWind2065RCP8.5 | Atikokan | Wind | RCP8.5 | 2065 | 76.0937 | 82.2568 | 88.8237 | 95.3112 | 101.8015
AtikokanWind2070RCP8.5 | Atikokan | Wind | RCP8.5 | 2070 | 76.4427 | 82.7073 | 89.4027 | 95.9983 | 102.6021
AtikokanWind2075RCP8.5 | Atikokan | Wind | RCP8.5 | 2075 | 76.5615 | 82.8433 | 89.5547 | 96.167 | 102.7917
AtikokanWind2080RCP8.5 | Atikokan | Wind | RCP8.5 | 2080 | 76.6803 | 82.9793 | 89.7066 | 96.3357 | 102.9812
AtikokanWind2085RCP8.5 | Atikokan | Wind | RCP8.5 | 2085 | 76.7138 | 83.0112 | 89.7324 | 96.3587 | 102.9959
AtikokanWind2090RCP8.5 | Atikokan | Wind | RCP8.5 | 2090 | 76.7472 | 83.0432 | 89.7582 | 96.3817 | 103.0106
AtikokanWind2095RCP8.5 | Atikokan | Wind | RCP8.5 | 2095 | 76.7472 | 83.0432 | 89.7582 | 96.3817 | 103.0106
AtikokanWind2100RCP8.5 | Atikokan | Wind | RCP8.5 | 2100 | 76.7472 | 83.0432 | 89.7582 | 96.3817 | 103.0106
AttawapiskatIce Accretion2023RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2023 | 10.636 | 12.6865 | 15.285 | 17.272 | 19.2591
AttawapiskatIce Accretion2025RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2025 | 10.6934 | 12.7529 | 15.365 | 17.3624 | 19.3567
AttawapiskatIce Accretion2030RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2030 | 10.7508 | 12.8193 | 15.445 | 17.4528 | 19.4544
AttawapiskatIce Accretion2035RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2035 | 10.8082 | 12.8857 | 15.525 | 17.5432 | 19.552
AttawapiskatIce Accretion2040RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2040 | 10.8656 | 12.9521 | 15.605 | 17.6336 | 19.6497
AttawapiskatIce Accretion2045RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2045 | 10.923 | 13.0185 | 15.685 | 17.724 | 19.7473
AttawapiskatIce Accretion2050RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2050 | 10.9888 | 13.1024 | 15.792 | 17.8483 | 19.8866
AttawapiskatIce Accretion2055RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2055 | 10.9972 | 13.1198 | 15.819 | 17.8822 | 19.9282
AttawapiskatIce Accretion2060RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2060 | 11.0055 | 13.1372 | 15.846 | 17.9161 | 19.9697
AttawapiskatIce Accretion2065RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2065 | 11.0139 | 13.1547 | 15.873 | 17.95 | 20.0113
AttawapiskatIce Accretion2070RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2070 | 11.0222 | 13.1721 | 15.9 | 17.9839 | 20.0529
AttawapiskatIce Accretion2075RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2075 | 10.9178 | 13.0601 | 15.7775 | 17.8512 | 19.9143
AttawapiskatIce Accretion2080RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2080 | 10.8134 | 12.948 | 15.655 | 17.7184 | 19.7757
AttawapiskatIce Accretion2085RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2085 | 10.7091 | 12.836 | 15.5325 | 17.5856 | 19.6371
AttawapiskatIce Accretion2090RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2090 | 10.6047 | 12.7239 | 15.41 | 17.4528 | 19.4985
AttawapiskatIce Accretion2095RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2095 | 10.5003 | 12.6118 | 15.2875 | 17.3201 | 19.3599
AttawapiskatIce Accretion2100RCP4.5 | Attawapiskat | Ice Accretion | RCP4.5 | 2100 | 10.3959 | 12.4998 | 15.165 | 17.1873 | 19.2213
AttawapiskatIce Accretion2023RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2023 | 10.636 | 12.6865 | 15.285 | 17.272 | 19.2591
AttawapiskatIce Accretion2025RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2025 | 10.6934 | 12.7529 | 15.365 | 17.3624 | 19.3567
AttawapiskatIce Accretion2030RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2030 | 10.7508 | 12.8193 | 15.445 | 17.4528 | 19.4544
AttawapiskatIce Accretion2035RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2035 | 10.8082 | 12.8857 | 15.525 | 17.5432 | 19.552
AttawapiskatIce Accretion2040RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2040 | 10.8656 | 12.9521 | 15.605 | 17.6336 | 19.6497
AttawapiskatIce Accretion2045RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2045 | 10.923 | 13.0185 | 15.685 | 17.724 | 19.7473
AttawapiskatIce Accretion2050RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2050 | 10.9888 | 13.1024 | 15.792 | 17.8483 | 19.8866
AttawapiskatIce Accretion2055RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2055 | 10.9972 | 13.1198 | 15.819 | 17.8822 | 19.9282
AttawapiskatIce Accretion2060RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2060 | 11.0055 | 13.1372 | 15.846 | 17.9161 | 19.9697
AttawapiskatIce Accretion2065RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2065 | 11.0139 | 13.1547 | 15.873 | 17.95 | 20.0113
AttawapiskatIce Accretion2070RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2070 | 11.0222 | 13.1721 | 15.9 | 17.9839 | 20.0529
AttawapiskatIce Accretion2075RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2075 | 10.8656 | 13.004 | 15.7163 | 17.7848 | 19.845
AttawapiskatIce Accretion2080RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2080 | 10.7091 | 12.836 | 15.5325 | 17.5856 | 19.6371
AttawapiskatIce Accretion2085RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2085 | 10.5525 | 12.6679 | 15.3487 | 17.3865 | 19.4292
AttawapiskatIce Accretion2090RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2090 | 10.1176 | 12.1968 | 14.825 | 16.8257 | 18.8307
AttawapiskatIce Accretion2095RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2095 | 9.8393 | 11.8939 | 14.485 | 16.4641 | 18.4401
AttawapiskatIce Accretion2100RCP6.0 | Attawapiskat | Ice Accretion | RCP6.0 | 2100 | 9.5609 | 11.5909 | 14.145 | 16.1025 | 18.0495
AttawapiskatIce Accretion2023RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2023 | 10.636 | 12.6865 | 15.285 | 17.272 | 19.2591
AttawapiskatIce Accretion2025RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2025 | 10.7508 | 12.8193 | 15.445 | 17.4528 | 19.4544
AttawapiskatIce Accretion2030RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2030 | 10.8656 | 12.9521 | 15.605 | 17.6336 | 19.6497
AttawapiskatIce Accretion2035RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2035 | 10.9805 | 13.0849 | 15.765 | 17.8144 | 19.845
AttawapiskatIce Accretion2040RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2040 | 10.9944 | 13.114 | 15.81 | 17.8709 | 19.9143
AttawapiskatIce Accretion2045RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2045 | 11.0083 | 13.1431 | 15.855 | 17.9274 | 19.9836
AttawapiskatIce Accretion2050RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2050 | 10.8134 | 12.948 | 15.655 | 17.7184 | 19.7757
AttawapiskatIce Accretion2055RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2055 | 10.6047 | 12.7239 | 15.41 | 17.4528 | 19.4985
AttawapiskatIce Accretion2060RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2060 | 10.1176 | 12.1968 | 14.825 | 16.8257 | 18.8307
AttawapiskatIce Accretion2065RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2065 | 9.8393 | 11.8939 | 14.485 | 16.4641 | 18.4401
AttawapiskatIce Accretion2070RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2070 | 9.2339 | 11.2216 | 13.725 | 15.6392 | 17.5455
AttawapiskatIce Accretion2075RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2075 | 8.9068 | 10.8522 | 13.305 | 15.1759 | 17.0415
AttawapiskatIce Accretion2080RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2080 | 8.5798 | 10.4829 | 12.885 | 14.7126 | 16.5375
AttawapiskatIce Accretion2085RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2085 | 8.1101 | 9.9538 | 12.2775 | 14.0431 | 15.8004
AttawapiskatIce Accretion2090RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2090 | 7.6404 | 9.4246 | 11.67 | 13.3735 | 15.0633
AttawapiskatIce Accretion2095RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2095 | 7.6404 | 9.4246 | 11.67 | 13.3735 | 15.0633
AttawapiskatIce Accretion2100RCP8.5 | Attawapiskat | Ice Accretion | RCP8.5 | 2100 | 7.6404 | 9.4246 | 11.67 | 13.3735 | 15.0633
AttawapiskatWind2023RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2023 | 81.1105 | 87.2015 | 93.5864 | 100.0067 | 106.4206
AttawapiskatWind2025RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2025 | 81.1362 | 87.2233 | 93.5989 | 100.0151 | 106.4224
AttawapiskatWind2030RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2030 | 81.1619 | 87.2452 | 93.6115 | 100.0235 | 106.4242
AttawapiskatWind2035RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2035 | 81.1876 | 87.267 | 93.624 | 100.0318 | 106.426
AttawapiskatWind2040RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2040 | 81.2133 | 87.2889 | 93.6365 | 100.0402 | 106.4277
AttawapiskatWind2045RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2045 | 81.239 | 87.3107 | 93.6491 | 100.0486 | 106.4295
AttawapiskatWind2050RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2050 | 81.354 | 87.4322 | 93.7782 | 100.1837 | 106.5728
AttawapiskatWind2055RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2055 | 81.4433 | 87.5319 | 93.8947 | 100.3104 | 106.7142
AttawapiskatWind2060RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2060 | 81.5326 | 87.6316 | 94.0113 | 100.4372 | 106.8557
AttawapiskatWind2065RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2065 | 81.6219 | 87.7312 | 94.1278 | 100.5639 | 106.9971
AttawapiskatWind2070RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2070 | 81.7112 | 87.8309 | 94.2444 | 100.6906 | 107.1386
AttawapiskatWind2075RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2075 | 81.7477 | 87.8702 | 94.282 | 100.7292 | 107.1779
AttawapiskatWind2080RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2080 | 81.7842 | 87.9096 | 94.3196 | 100.7677 | 107.2172
AttawapiskatWind2085RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2085 | 81.8207 | 87.9489 | 94.3572 | 100.8063 | 107.2564
AttawapiskatWind2090RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2090 | 81.8573 | 87.9882 | 94.3948 | 100.8449 | 107.2957
AttawapiskatWind2095RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2095 | 81.8938 | 88.0276 | 94.4324 | 100.8834 | 107.335
AttawapiskatWind2100RCP4.5 | Attawapiskat | Wind | RCP4.5 | 2100 | 81.9303 | 88.0669 | 94.47 | 100.922 | 107.3743
AttawapiskatWind2023RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2023 | 81.1105 | 87.2015 | 93.5864 | 100.0067 | 106.4206
AttawapiskatWind2025RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2025 | 81.1362 | 87.2233 | 93.5989 | 100.0151 | 106.4224
AttawapiskatWind2030RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2030 | 81.1619 | 87.2452 | 93.6115 | 100.0235 | 106.4242
AttawapiskatWind2035RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2035 | 81.1876 | 87.267 | 93.624 | 100.0318 | 106.426
AttawapiskatWind2040RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2040 | 81.2133 | 87.2889 | 93.6365 | 100.0402 | 106.4277
AttawapiskatWind2045RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2045 | 81.239 | 87.3107 | 93.6491 | 100.0486 | 106.4295
AttawapiskatWind2050RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2050 | 81.354 | 87.4322 | 93.7782 | 100.1837 | 106.5728
AttawapiskatWind2055RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2055 | 81.4433 | 87.5319 | 93.8947 | 100.3104 | 106.7142
AttawapiskatWind2060RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2060 | 81.5326 | 87.6316 | 94.0113 | 100.4372 | 106.8557
AttawapiskatWind2065RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2065 | 81.6219 | 87.7312 | 94.1278 | 100.5639 | 106.9971
AttawapiskatWind2070RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2070 | 81.7112 | 87.8309 | 94.2444 | 100.6906 | 107.1386
AttawapiskatWind2075RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2075 | 81.766 | 87.8899 | 94.3008 | 100.7485 | 107.1975
AttawapiskatWind2080RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2080 | 81.8207 | 87.9489 | 94.3572 | 100.8063 | 107.2564
AttawapiskatWind2085RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2085 | 81.8755 | 88.0079 | 94.4136 | 100.8641 | 107.3154
AttawapiskatWind2090RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2090 | 81.9547 | 88.0844 | 94.4794 | 100.9253 | 107.3707
AttawapiskatWind2095RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2095 | 81.979 | 88.1019 | 94.4888 | 100.9287 | 107.3672
AttawapiskatWind2100RCP6.0 | Attawapiskat | Wind | RCP6.0 | 2100 | 82.0034 | 88.1194 | 94.4982 | 100.932 | 107.3636
AttawapiskatWind2023RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2023 | 81.1105 | 87.2015 | 93.5864 | 100.0067 | 106.4206
AttawapiskatWind2025RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2025 | 81.1619 | 87.2452 | 93.6115 | 100.0235 | 106.4242
AttawapiskatWind2030RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2030 | 81.2133 | 87.2889 | 93.6365 | 100.0402 | 106.4277
AttawapiskatWind2035RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2035 | 81.2647 | 87.3326 | 93.6616 | 100.057 | 106.4313
AttawapiskatWind2040RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2040 | 81.4136 | 87.4987 | 93.8559 | 100.2682 | 106.6671
AttawapiskatWind2045RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2045 | 81.5624 | 87.6648 | 94.0501 | 100.4794 | 106.9028
AttawapiskatWind2050RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2050 | 81.7842 | 87.9096 | 94.3196 | 100.7677 | 107.2172
AttawapiskatWind2055RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2055 | 81.8573 | 87.9882 | 94.3948 | 100.8449 | 107.2957
AttawapiskatWind2060RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2060 | 81.9547 | 88.0844 | 94.4794 | 100.9253 | 107.3707
AttawapiskatWind2065RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2065 | 81.979 | 88.1019 | 94.4888 | 100.9287 | 107.3672
AttawapiskatWind2070RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2070 | 82.1549 | 88.2767 | 94.6674 | 101.1097 | 107.5529
AttawapiskatWind2075RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2075 | 82.3064 | 88.4341 | 94.8366 | 101.2874 | 107.7422
AttawapiskatWind2080RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2080 | 82.4579 | 88.5914 | 95.0058 | 101.4651 | 107.9316
AttawapiskatWind2085RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2085 | 82.7866 | 89.0023 | 95.5087 | 102.0535 | 108.5959
AttawapiskatWind2090RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2090 | 83.1154 | 89.4132 | 96.0116 | 102.6419 | 109.2603
AttawapiskatWind2095RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2095 | 83.1154 | 89.4132 | 96.0116 | 102.6419 | 109.2603
AttawapiskatWind2100RCP8.5 | Attawapiskat | Wind | RCP8.5 | 2100 | 83.1154 | 89.4132 | 96.0116 | 102.6419 | 109.2603
AuroraIce Accretion2023RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
AuroraIce Accretion2025RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2025 | 17.4222 | 20.9229 | 25.3542 | 28.7444 | 32.1247
AuroraIce Accretion2030RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2030 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
AuroraIce Accretion2035RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2035 | 17.5092 | 21.0612 | 25.5625 | 28.9986 | 32.4292
AuroraIce Accretion2040RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2040 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
AuroraIce Accretion2045RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2045 | 17.5962 | 21.1996 | 25.7708 | 29.2529 | 32.7338
AuroraIce Accretion2050RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2050 | 17.5214 | 21.1484 | 25.745 | 29.2444 | 32.7411
AuroraIce Accretion2055RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2055 | 17.4031 | 21.0281 | 25.615 | 29.1088 | 32.5962
AuroraIce Accretion2060RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2060 | 17.2848 | 20.9077 | 25.485 | 28.9732 | 32.4513
AuroraIce Accretion2065RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2065 | 17.1665 | 20.7873 | 25.355 | 28.8376 | 32.3064
AuroraIce Accretion2070RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2070 | 17.0482 | 20.667 | 25.225 | 28.702 | 32.1615
AuroraIce Accretion2075RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2075 | 17.0105 | 20.6497 | 25.2333 | 28.7255 | 32.2035
AuroraIce Accretion2080RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2080 | 16.9728 | 20.6324 | 25.2417 | 28.7491 | 32.2455
AuroraIce Accretion2085RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2085 | 16.9352 | 20.6151 | 25.25 | 28.7726 | 32.2875
AuroraIce Accretion2090RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2090 | 16.8975 | 20.5978 | 25.2583 | 28.7962 | 32.3295
AuroraIce Accretion2095RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2095 | 16.8598 | 20.5805 | 25.2667 | 28.8197 | 32.3715
AuroraIce Accretion2100RCP4.5 | Aurora | Ice Accretion | RCP4.5 | 2100 | 16.8221 | 20.5633 | 25.275 | 28.8432 | 32.4135
AuroraIce Accretion2023RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
AuroraIce Accretion2025RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2025 | 17.4222 | 20.9229 | 25.3542 | 28.7444 | 32.1247
AuroraIce Accretion2030RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2030 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
AuroraIce Accretion2035RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2035 | 17.5092 | 21.0612 | 25.5625 | 28.9986 | 32.4292
AuroraIce Accretion2040RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2040 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
AuroraIce Accretion2045RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2045 | 17.5962 | 21.1996 | 25.7708 | 29.2529 | 32.7338
AuroraIce Accretion2050RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2050 | 17.5214 | 21.1484 | 25.745 | 29.2444 | 32.7411
AuroraIce Accretion2055RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2055 | 17.4031 | 21.0281 | 25.615 | 29.1088 | 32.5962
AuroraIce Accretion2060RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2060 | 17.2848 | 20.9077 | 25.485 | 28.9732 | 32.4513
AuroraIce Accretion2065RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2065 | 17.1665 | 20.7873 | 25.355 | 28.8376 | 32.3064
AuroraIce Accretion2070RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2070 | 17.0482 | 20.667 | 25.225 | 28.702 | 32.1615
AuroraIce Accretion2075RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2075 | 16.9917 | 20.6411 | 25.2375 | 28.7373 | 32.2245
AuroraIce Accretion2080RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2080 | 16.9352 | 20.6151 | 25.25 | 28.7726 | 32.2875
AuroraIce Accretion2085RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2085 | 16.8786 | 20.5892 | 25.2625 | 28.8079 | 32.3505
AuroraIce Accretion2090RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2090 | 16.5147 | 20.2382 | 24.925 | 28.4854 | 32.0355
AuroraIce Accretion2095RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2095 | 16.2074 | 19.9131 | 24.575 | 28.1276 | 31.6575
AuroraIce Accretion2100RCP6.0 | Aurora | Ice Accretion | RCP6.0 | 2100 | 15.9001 | 19.588 | 24.225 | 27.7697 | 31.2795
AuroraIce Accretion2023RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
AuroraIce Accretion2025RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2025 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
AuroraIce Accretion2030RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2030 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
AuroraIce Accretion2035RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2035 | 17.6397 | 21.2687 | 25.875 | 29.38 | 32.886
AuroraIce Accretion2040RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2040 | 17.4425 | 21.0682 | 25.6583 | 29.154 | 32.6445
AuroraIce Accretion2045RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2045 | 17.2454 | 20.8676 | 25.4417 | 28.928 | 32.403
AuroraIce Accretion2050RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2050 | 16.9728 | 20.6324 | 25.2417 | 28.7491 | 32.2455
AuroraIce Accretion2055RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2055 | 16.8975 | 20.5978 | 25.2583 | 28.7962 | 32.3295
AuroraIce Accretion2060RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2060 | 16.5147 | 20.2382 | 24.925 | 28.4854 | 32.0355
AuroraIce Accretion2065RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2065 | 16.2074 | 19.9131 | 24.575 | 28.1276 | 31.6575
AuroraIce Accretion2070RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2070 | 15.5116 | 19.173 | 23.775 | 27.2801 | 30.765
AuroraIce Accretion2075RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2075 | 15.1231 | 18.758 | 23.325 | 26.7904 | 30.2505
AuroraIce Accretion2080RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2080 | 14.7345 | 18.343 | 22.875 | 26.3007 | 29.736
AuroraIce Accretion2085RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2085 | 13.9691 | 17.4404 | 21.8 | 25.1001 | 28.3972
AuroraIce Accretion2090RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2090 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
AuroraIce Accretion2095RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2095 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
AuroraIce Accretion2100RCP8.5 | Aurora | Ice Accretion | RCP8.5 | 2100 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
AuroraWind2023RCP4.5 | Aurora | Wind | RCP4.5 | 2023 | 77.1343 | 83.0762 | 89.3293 | 95.5824 | 101.8354
AuroraWind2025RCP4.5 | Aurora | Wind | RCP4.5 | 2025 | 77.1586 | 83.1107 | 89.3768 | 95.6411 | 101.9064
AuroraWind2030RCP4.5 | Aurora | Wind | RCP4.5 | 2030 | 77.183 | 83.1452 | 89.4242 | 95.6998 | 101.9774
AuroraWind2035RCP4.5 | Aurora | Wind | RCP4.5 | 2035 | 77.2073 | 83.1797 | 89.4717 | 95.7585 | 102.0485
AuroraWind2040RCP4.5 | Aurora | Wind | RCP4.5 | 2040 | 77.2316 | 83.2142 | 89.5192 | 95.8173 | 102.1195
AuroraWind2045RCP4.5 | Aurora | Wind | RCP4.5 | 2045 | 77.256 | 83.2487 | 89.5666 | 95.876 | 102.1905
AuroraWind2050RCP4.5 | Aurora | Wind | RCP4.5 | 2050 | 77.331 | 83.3312 | 89.6586 | 95.9766 | 102.3001
AuroraWind2055RCP4.5 | Aurora | Wind | RCP4.5 | 2055 | 77.3817 | 83.3792 | 89.7031 | 96.0185 | 102.3386
AuroraWind2060RCP4.5 | Aurora | Wind | RCP4.5 | 2060 | 77.4325 | 83.4272 | 89.7476 | 96.0604 | 102.3772
AuroraWind2065RCP4.5 | Aurora | Wind | RCP4.5 | 2065 | 77.4832 | 83.4752 | 89.7921 | 96.1023 | 102.4158
AuroraWind2070RCP4.5 | Aurora | Wind | RCP4.5 | 2070 | 77.5339 | 83.5232 | 89.8366 | 96.1442 | 102.4543
AuroraWind2075RCP4.5 | Aurora | Wind | RCP4.5 | 2075 | 77.6082 | 83.6253 | 89.9731 | 96.3093 | 102.6488
AuroraWind2080RCP4.5 | Aurora | Wind | RCP4.5 | 2080 | 77.6825 | 83.7274 | 90.1095 | 96.4743 | 102.8432
AuroraWind2085RCP4.5 | Aurora | Wind | RCP4.5 | 2085 | 77.7568 | 83.8295 | 90.246 | 96.6394 | 103.0377
AuroraWind2090RCP4.5 | Aurora | Wind | RCP4.5 | 2090 | 77.8311 | 83.9315 | 90.3825 | 96.8045 | 103.2322
AuroraWind2095RCP4.5 | Aurora | Wind | RCP4.5 | 2095 | 77.9053 | 84.0336 | 90.5189 | 96.9695 | 103.4266
AuroraWind2100RCP4.5 | Aurora | Wind | RCP4.5 | 2100 | 77.9796 | 84.1357 | 90.6554 | 97.1346 | 103.6211
AuroraWind2023RCP6.0 | Aurora | Wind | RCP6.0 | 2023 | 77.1343 | 83.0762 | 89.3293 | 95.5824 | 101.8354
AuroraWind2025RCP6.0 | Aurora | Wind | RCP6.0 | 2025 | 77.1586 | 83.1107 | 89.3768 | 95.6411 | 101.9064
AuroraWind2030RCP6.0 | Aurora | Wind | RCP6.0 | 2030 | 77.183 | 83.1452 | 89.4242 | 95.6998 | 101.9774
AuroraWind2035RCP6.0 | Aurora | Wind | RCP6.0 | 2035 | 77.2073 | 83.1797 | 89.4717 | 95.7585 | 102.0485
AuroraWind2040RCP6.0 | Aurora | Wind | RCP6.0 | 2040 | 77.2316 | 83.2142 | 89.5192 | 95.8173 | 102.1195
AuroraWind2045RCP6.0 | Aurora | Wind | RCP6.0 | 2045 | 77.256 | 83.2487 | 89.5666 | 95.876 | 102.1905
AuroraWind2050RCP6.0 | Aurora | Wind | RCP6.0 | 2050 | 77.331 | 83.3312 | 89.6586 | 95.9766 | 102.3001
AuroraWind2055RCP6.0 | Aurora | Wind | RCP6.0 | 2055 | 77.3817 | 83.3792 | 89.7031 | 96.0185 | 102.3386
AuroraWind2060RCP6.0 | Aurora | Wind | RCP6.0 | 2060 | 77.4325 | 83.4272 | 89.7476 | 96.0604 | 102.3772
AuroraWind2065RCP6.0 | Aurora | Wind | RCP6.0 | 2065 | 77.4832 | 83.4752 | 89.7921 | 96.1023 | 102.4158
AuroraWind2070RCP6.0 | Aurora | Wind | RCP6.0 | 2070 | 77.5339 | 83.5232 | 89.8366 | 96.1442 | 102.4543
AuroraWind2075RCP6.0 | Aurora | Wind | RCP6.0 | 2075 | 77.6453 | 83.6763 | 90.0413 | 96.3918 | 102.746
AuroraWind2080RCP6.0 | Aurora | Wind | RCP6.0 | 2080 | 77.7568 | 83.8295 | 90.246 | 96.6394 | 103.0377
AuroraWind2085RCP6.0 | Aurora | Wind | RCP6.0 | 2085 | 77.8682 | 83.9826 | 90.4507 | 96.887 | 103.3294
AuroraWind2090RCP6.0 | Aurora | Wind | RCP6.0 | 2090 | 78.2384 | 84.4557 | 91.05 | 97.5949 | 104.1487
AuroraWind2095RCP6.0 | Aurora | Wind | RCP6.0 | 2095 | 78.4971 | 84.7758 | 91.4445 | 98.0552 | 104.6763
AuroraWind2100RCP6.0 | Aurora | Wind | RCP6.0 | 2100 | 78.7558 | 85.0958 | 91.8391 | 98.5154 | 105.2039
AuroraWind2023RCP8.5 | Aurora | Wind | RCP8.5 | 2023 | 77.1343 | 83.0762 | 89.3293 | 95.5824 | 101.8354
AuroraWind2025RCP8.5 | Aurora | Wind | RCP8.5 | 2025 | 77.183 | 83.1452 | 89.4242 | 95.6998 | 101.9774
AuroraWind2030RCP8.5 | Aurora | Wind | RCP8.5 | 2030 | 77.2316 | 83.2142 | 89.5192 | 95.8173 | 102.1195
AuroraWind2035RCP8.5 | Aurora | Wind | RCP8.5 | 2035 | 77.2803 | 83.2832 | 89.6141 | 95.9347 | 102.2615
AuroraWind2040RCP8.5 | Aurora | Wind | RCP8.5 | 2040 | 77.3648 | 83.3632 | 89.6883 | 96.0045 | 102.3258
AuroraWind2045RCP8.5 | Aurora | Wind | RCP8.5 | 2045 | 77.4494 | 83.4432 | 89.7624 | 96.0744 | 102.3901
AuroraWind2050RCP8.5 | Aurora | Wind | RCP8.5 | 2050 | 77.6825 | 83.7274 | 90.1095 | 96.4743 | 102.8432
AuroraWind2055RCP8.5 | Aurora | Wind | RCP8.5 | 2055 | 77.8311 | 83.9315 | 90.3825 | 96.8045 | 103.2322
AuroraWind2060RCP8.5 | Aurora | Wind | RCP8.5 | 2060 | 78.2384 | 84.4557 | 91.05 | 97.5949 | 104.1487
AuroraWind2065RCP8.5 | Aurora | Wind | RCP8.5 | 2065 | 78.4971 | 84.7758 | 91.4445 | 98.0552 | 104.6763
AuroraWind2070RCP8.5 | Aurora | Wind | RCP8.5 | 2070 | 78.9531 | 85.3607 | 92.1892 | 98.9376 | 105.6976
AuroraWind2075RCP8.5 | Aurora | Wind | RCP8.5 | 2075 | 79.1503 | 85.6256 | 92.5392 | 99.3598 | 106.1914
AuroraWind2080RCP8.5 | Aurora | Wind | RCP8.5 | 2080 | 79.3476 | 85.8904 | 92.8893 | 99.782 | 106.6852
AuroraWind2085RCP8.5 | Aurora | Wind | RCP8.5 | 2085 | 79.4475 | 86.0229 | 93.0673 | 99.9915 | 106.9338
AuroraWind2090RCP8.5 | Aurora | Wind | RCP8.5 | 2090 | 79.5474 | 86.1553 | 93.2453 | 100.201 | 107.1823
AuroraWind2095RCP8.5 | Aurora | Wind | RCP8.5 | 2095 | 79.5474 | 86.1553 | 93.2453 | 100.201 | 107.1823
AuroraWind2100RCP8.5 | Aurora | Wind | RCP8.5 | 2100 | 79.5474 | 86.1553 | 93.2453 | 100.201 | 107.1823
BancroftIce Accretion2023RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2023 | 17.1874 | 20.4802 | 24.675 | 27.8827 | 31.0905
BancroftIce Accretion2025RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2025 | 17.2077 | 20.501 | 24.6958 | 27.9016 | 31.1115
BancroftIce Accretion2030RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2030 | 17.228 | 20.5217 | 24.7167 | 27.9204 | 31.1325
BancroftIce Accretion2035RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2035 | 17.2483 | 20.5425 | 24.7375 | 27.9392 | 31.1535
BancroftIce Accretion2040RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2040 | 17.2686 | 20.5633 | 24.7583 | 27.9581 | 31.1745
BancroftIce Accretion2045RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2045 | 17.2889 | 20.584 | 24.7792 | 27.9769 | 31.1955
BancroftIce Accretion2050RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2050 | 17.2848 | 20.5965 | 24.8 | 28.0127 | 31.2354
BancroftIce Accretion2055RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2055 | 17.2605 | 20.5881 | 24.8 | 28.0296 | 31.2543
BancroftIce Accretion2060RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2060 | 17.2361 | 20.5799 | 24.8 | 28.0466 | 31.2732
BancroftIce Accretion2065RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2065 | 17.2118 | 20.5715 | 24.8 | 28.0635 | 31.2921
BancroftIce Accretion2070RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2070 | 17.1874 | 20.5633 | 24.8 | 28.0805 | 31.311
BancroftIce Accretion2075RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2075 | 17.286 | 20.6947 | 24.9792 | 28.2924 | 31.5577
BancroftIce Accretion2080RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2080 | 17.3846 | 20.8261 | 25.1583 | 28.5042 | 31.8045
BancroftIce Accretion2085RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2085 | 17.4831 | 20.9575 | 25.3375 | 28.7161 | 32.0512
BancroftIce Accretion2090RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2090 | 17.5817 | 21.0889 | 25.5167 | 28.928 | 32.298
BancroftIce Accretion2095RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2095 | 17.6803 | 21.2203 | 25.6958 | 29.1399 | 32.5448
BancroftIce Accretion2100RCP4.5 | Bancroft | Ice Accretion | RCP4.5 | 2100 | 17.7789 | 21.3517 | 25.875 | 29.3517 | 32.7915
BancroftIce Accretion2023RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2023 | 17.1874 | 20.4802 | 24.675 | 27.8827 | 31.0905
BancroftIce Accretion2025RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2025 | 17.2077 | 20.501 | 24.6958 | 27.9016 | 31.1115
BancroftIce Accretion2030RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2030 | 17.228 | 20.5217 | 24.7167 | 27.9204 | 31.1325
BancroftIce Accretion2035RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2035 | 17.2483 | 20.5425 | 24.7375 | 27.9392 | 31.1535
BancroftIce Accretion2040RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2040 | 17.2686 | 20.5633 | 24.7583 | 27.9581 | 31.1745
BancroftIce Accretion2045RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2045 | 17.2889 | 20.584 | 24.7792 | 27.9769 | 31.1955
BancroftIce Accretion2050RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2050 | 17.2848 | 20.5965 | 24.8 | 28.0127 | 31.2354
BancroftIce Accretion2055RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2055 | 17.2605 | 20.5881 | 24.8 | 28.0296 | 31.2543
BancroftIce Accretion2060RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2060 | 17.2361 | 20.5799 | 24.8 | 28.0466 | 31.2732
BancroftIce Accretion2065RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2065 | 17.2118 | 20.5715 | 24.8 | 28.0635 | 31.2921
BancroftIce Accretion2070RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2070 | 17.1874 | 20.5633 | 24.8 | 28.0805 | 31.311
BancroftIce Accretion2075RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2075 | 17.3353 | 20.7604 | 25.0688 | 28.3983 | 31.6811
BancroftIce Accretion2080RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2080 | 17.4831 | 20.9575 | 25.3375 | 28.7161 | 32.0512
BancroftIce Accretion2085RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2085 | 17.631 | 21.1546 | 25.6062 | 29.0339 | 32.4214
BancroftIce Accretion2090RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2090 | 17.7731 | 21.3725 | 25.9333 | 29.4271 | 32.907
BancroftIce Accretion2095RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2095 | 17.7673 | 21.3933 | 25.9917 | 29.5024 | 33.0225
BancroftIce Accretion2100RCP6.0 | Bancroft | Ice Accretion | RCP6.0 | 2100 | 17.7615 | 21.414 | 26.05 | 29.5777 | 33.138
BancroftIce Accretion2023RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2023 | 17.1874 | 20.4802 | 24.675 | 27.8827 | 31.0905
BancroftIce Accretion2025RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2025 | 17.228 | 20.5217 | 24.7167 | 27.9204 | 31.1325
BancroftIce Accretion2030RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2030 | 17.2686 | 20.5633 | 24.7583 | 27.9581 | 31.1745
BancroftIce Accretion2035RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2035 | 17.3092 | 20.6047 | 24.8 | 27.9957 | 31.2165
BancroftIce Accretion2040RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2040 | 17.2686 | 20.5909 | 24.8 | 28.024 | 31.248
BancroftIce Accretion2045RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2045 | 17.228 | 20.5771 | 24.8 | 28.0522 | 31.2795
BancroftIce Accretion2050RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2050 | 17.3846 | 20.8261 | 25.1583 | 28.5042 | 31.8045
BancroftIce Accretion2055RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2055 | 17.5817 | 21.0889 | 25.5167 | 28.928 | 32.298
BancroftIce Accretion2060RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2060 | 17.7731 | 21.3725 | 25.9333 | 29.4271 | 32.907
BancroftIce Accretion2065RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2065 | 17.7673 | 21.3933 | 25.9917 | 29.5024 | 33.0225
BancroftIce Accretion2070RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2070 | 17.7209 | 21.414 | 26.0833 | 29.6437 | 33.222
BancroftIce Accretion2075RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2075 | 17.6803 | 21.414 | 26.1167 | 29.7096 | 33.306
BancroftIce Accretion2080RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2080 | 17.6397 | 21.414 | 26.15 | 29.7755 | 33.39
BancroftIce Accretion2085RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2085 | 17.3092 | 21.0613 | 25.775 | 29.38 | 32.9805
BancroftIce Accretion2090RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2090 | 16.9786 | 20.7085 | 25.4 | 28.9845 | 32.571
BancroftIce Accretion2095RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2095 | 16.9786 | 20.7085 | 25.4 | 28.9845 | 32.571
BancroftIce Accretion2100RCP8.5 | Bancroft | Ice Accretion | RCP8.5 | 2100 | 16.9786 | 20.7085 | 25.4 | 28.9845 | 32.571
BancroftWind2023RCP4.5 | Bancroft | Wind | RCP4.5 | 2023 | 69.5483 | 74.9952 | 80.752 | 86.4817 | 92.2123
BancroftWind2025RCP4.5 | Bancroft | Wind | RCP4.5 | 2025 | 69.6128 | 75.082 | 80.868 | 86.6215 | 92.378
BancroftWind2030RCP4.5 | Bancroft | Wind | RCP4.5 | 2030 | 69.6773 | 75.1688 | 80.984 | 86.7613 | 92.5437
BancroftWind2035RCP4.5 | Bancroft | Wind | RCP4.5 | 2035 | 69.7417 | 75.2556 | 81.1 | 86.9011 | 92.7094
BancroftWind2040RCP4.5 | Bancroft | Wind | RCP4.5 | 2040 | 69.8062 | 75.3424 | 81.216 | 87.0409 | 92.875
BancroftWind2045RCP4.5 | Bancroft | Wind | RCP4.5 | 2045 | 69.8707 | 75.4292 | 81.332 | 87.1807 | 93.0407
BancroftWind2050RCP4.5 | Bancroft | Wind | RCP4.5 | 2050 | 69.9435 | 75.5115 | 81.4256 | 87.2846 | 93.1553
BancroftWind2055RCP4.5 | Bancroft | Wind | RCP4.5 | 2055 | 69.9517 | 75.5071 | 81.4032 | 87.2487 | 93.1043
BancroftWind2060RCP4.5 | Bancroft | Wind | RCP4.5 | 2060 | 69.96 | 75.5026 | 81.3808 | 87.2127 | 93.0532
BancroftWind2065RCP4.5 | Bancroft | Wind | RCP4.5 | 2065 | 69.9683 | 75.4981 | 81.3584 | 87.1768 | 93.0021
BancroftWind2070RCP4.5 | Bancroft | Wind | RCP4.5 | 2070 | 69.9766 | 75.4937 | 81.336 | 87.1408 | 92.951
BancroftWind2075RCP4.5 | Bancroft | Wind | RCP4.5 | 2075 | 69.987 | 75.5024 | 81.3413 | 87.1437 | 92.9526
BancroftWind2080RCP4.5 | Bancroft | Wind | RCP4.5 | 2080 | 69.9973 | 75.511 | 81.3467 | 87.1465 | 92.9541
BancroftWind2085RCP4.5 | Bancroft | Wind | RCP4.5 | 2085 | 70.0077 | 75.5197 | 81.352 | 87.1494 | 92.9556
BancroftWind2090RCP4.5 | Bancroft | Wind | RCP4.5 | 2090 | 70.0181 | 75.5284 | 81.3573 | 87.1522 | 92.9571
BancroftWind2095RCP4.5 | Bancroft | Wind | RCP4.5 | 2095 | 70.0284 | 75.5371 | 81.3627 | 87.1551 | 92.9586
BancroftWind2100RCP4.5 | Bancroft | Wind | RCP4.5 | 2100 | 70.0388 | 75.5458 | 81.368 | 87.1579 | 92.9602
BancroftWind2023RCP6.0 | Bancroft | Wind | RCP6.0 | 2023 | 69.5483 | 74.9952 | 80.752 | 86.4817 | 92.2123
BancroftWind2025RCP6.0 | Bancroft | Wind | RCP6.0 | 2025 | 69.6128 | 75.082 | 80.868 | 86.6215 | 92.378
BancroftWind2030RCP6.0 | Bancroft | Wind | RCP6.0 | 2030 | 69.6773 | 75.1688 | 80.984 | 86.7613 | 92.5437
BancroftWind2035RCP6.0 | Bancroft | Wind | RCP6.0 | 2035 | 69.7417 | 75.2556 | 81.1 | 86.9011 | 92.7094
BancroftWind2040RCP6.0 | Bancroft | Wind | RCP6.0 | 2040 | 69.8062 | 75.3424 | 81.216 | 87.0409 | 92.875
BancroftWind2045RCP6.0 | Bancroft | Wind | RCP6.0 | 2045 | 69.8707 | 75.4292 | 81.332 | 87.1807 | 93.0407
BancroftWind2050RCP6.0 | Bancroft | Wind | RCP6.0 | 2050 | 69.9435 | 75.5115 | 81.4256 | 87.2846 | 93.1553
BancroftWind2055RCP6.0 | Bancroft | Wind | RCP6.0 | 2055 | 69.9517 | 75.5071 | 81.4032 | 87.2487 | 93.1043
BancroftWind2060RCP6.0 | Bancroft | Wind | RCP6.0 | 2060 | 69.96 | 75.5026 | 81.3808 | 87.2127 | 93.0532
BancroftWind2065RCP6.0 | Bancroft | Wind | RCP6.0 | 2065 | 69.9683 | 75.4981 | 81.3584 | 87.1768 | 93.0021
BancroftWind2070RCP6.0 | Bancroft | Wind | RCP6.0 | 2070 | 69.9766 | 75.4937 | 81.336 | 87.1408 | 92.951
BancroftWind2075RCP6.0 | Bancroft | Wind | RCP6.0 | 2075 | 69.9922 | 75.5067 | 81.344 | 87.1451 | 92.9533
BancroftWind2080RCP6.0 | Bancroft | Wind | RCP6.0 | 2080 | 70.0077 | 75.5197 | 81.352 | 87.1494 | 92.9556
BancroftWind2085RCP6.0 | Bancroft | Wind | RCP6.0 | 2085 | 70.0232 | 75.5327 | 81.36 | 87.1536 | 92.9579
BancroftWind2090RCP6.0 | Bancroft | Wind | RCP6.0 | 2090 | 70.0549 | 75.5458 | 81.3467 | 87.1208 | 92.9024
BancroftWind2095RCP6.0 | Bancroft | Wind | RCP6.0 | 2095 | 70.071 | 75.5458 | 81.3253 | 87.0837 | 92.8446
BancroftWind2100RCP6.0 | Bancroft | Wind | RCP6.0 | 2100 | 70.0871 | 75.5458 | 81.304 | 87.0466 | 92.7869
BancroftWind2023RCP8.5 | Bancroft | Wind | RCP8.5 | 2023 | 69.5483 | 74.9952 | 80.752 | 86.4817 | 92.2123
BancroftWind2025RCP8.5 | Bancroft | Wind | RCP8.5 | 2025 | 69.6773 | 75.1688 | 80.984 | 86.7613 | 92.5437
BancroftWind2030RCP8.5 | Bancroft | Wind | RCP8.5 | 2030 | 69.8062 | 75.3424 | 81.216 | 87.0409 | 92.875
BancroftWind2035RCP8.5 | Bancroft | Wind | RCP8.5 | 2035 | 69.9352 | 75.516 | 81.448 | 87.3206 | 93.2064
BancroftWind2040RCP8.5 | Bancroft | Wind | RCP8.5 | 2040 | 69.949 | 75.5086 | 81.4107 | 87.2606 | 93.1213
BancroftWind2045RCP8.5 | Bancroft | Wind | RCP8.5 | 2045 | 69.9628 | 75.5011 | 81.3733 | 87.2007 | 93.0362
BancroftWind2050RCP8.5 | Bancroft | Wind | RCP8.5 | 2050 | 69.9973 | 75.511 | 81.3467 | 87.1465 | 92.9541
BancroftWind2055RCP8.5 | Bancroft | Wind | RCP8.5 | 2055 | 70.0181 | 75.5284 | 81.3573 | 87.1522 | 92.9571
BancroftWind2060RCP8.5 | Bancroft | Wind | RCP8.5 | 2060 | 70.0549 | 75.5458 | 81.3467 | 87.1208 | 92.9024
BancroftWind2065RCP8.5 | Bancroft | Wind | RCP8.5 | 2065 | 70.071 | 75.5458 | 81.3253 | 87.0837 | 92.8446
BancroftWind2070RCP8.5 | Bancroft | Wind | RCP8.5 | 2070 | 70.1217 | 75.5656 | 81.3067 | 87.0381 | 92.7656
BancroftWind2075RCP8.5 | Bancroft | Wind | RCP8.5 | 2075 | 70.1562 | 75.5854 | 81.3093 | 87.0295 | 92.7443
BancroftWind2080RCP8.5 | Bancroft | Wind | RCP8.5 | 2080 | 70.1908 | 75.6053 | 81.312 | 87.021 | 92.723
BancroftWind2085RCP8.5 | Bancroft | Wind | RCP8.5 | 2085 | 70.2978 | 75.7578 | 81.52 | 87.2735 | 93.0194
BancroftWind2090RCP8.5 | Bancroft | Wind | RCP8.5 | 2090 | 70.4049 | 75.9103 | 81.728 | 87.526 | 93.3158
BancroftWind2095RCP8.5 | Bancroft | Wind | RCP8.5 | 2095 | 70.4049 | 75.9103 | 81.728 | 87.526 | 93.3158
BancroftWind2100RCP8.5 | Bancroft | Wind | RCP8.5 | 2100 | 70.4049 | 75.9103 | 81.728 | 87.526 | 93.3158
BarrieIce Accretion2023RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2023 | 15.6684 | 18.7464 | 22.632 | 25.6001 | 28.5453
BarrieIce Accretion2025RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2025 | 15.663 | 18.7432 | 22.6358 | 25.6088 | 28.5646
BarrieIce Accretion2030RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2030 | 15.6577 | 18.74 | 22.6397 | 25.6175 | 28.5839
BarrieIce Accretion2035RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2035 | 15.6524 | 18.7368 | 22.6435 | 25.6261 | 28.6033
BarrieIce Accretion2040RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2040 | 15.647 | 18.7337 | 22.6473 | 25.6348 | 28.6226
BarrieIce Accretion2045RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2045 | 15.6417 | 18.7305 | 22.6512 | 25.6435 | 28.6419
BarrieIce Accretion2050RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2050 | 15.5947 | 18.6967 | 22.6366 | 25.6417 | 28.6554
BarrieIce Accretion2055RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2055 | 15.5531 | 18.6662 | 22.6182 | 25.6313 | 28.6496
BarrieIce Accretion2060RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2060 | 15.5115 | 18.6357 | 22.5998 | 25.6209 | 28.6438
BarrieIce Accretion2065RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2065 | 15.4699 | 18.6051 | 22.5814 | 25.6105 | 28.638
BarrieIce Accretion2070RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2070 | 15.4283 | 18.5746 | 22.563 | 25.6001 | 28.6322
BarrieIce Accretion2075RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2075 | 15.4283 | 18.5968 | 22.6128 | 25.6695 | 28.7192
BarrieIce Accretion2080RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2080 | 15.4283 | 18.6191 | 22.6627 | 25.7388 | 28.8061
BarrieIce Accretion2085RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2085 | 15.4283 | 18.6414 | 22.7125 | 25.8081 | 28.8931
BarrieIce Accretion2090RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2090 | 15.4283 | 18.6637 | 22.7623 | 25.8774 | 28.98
BarrieIce Accretion2095RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2095 | 15.4283 | 18.6859 | 22.8122 | 25.9467 | 29.0669
BarrieIce Accretion2100RCP4.5 | Barrie | Ice Accretion | RCP4.5 | 2100 | 15.4283 | 18.7082 | 22.862 | 26.016 | 29.1539
BarrieIce Accretion2023RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2023 | 15.6684 | 18.7464 | 22.632 | 25.6001 | 28.5453
BarrieIce Accretion2025RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2025 | 15.663 | 18.7432 | 22.6358 | 25.6088 | 28.5646
BarrieIce Accretion2030RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2030 | 15.6577 | 18.74 | 22.6397 | 25.6175 | 28.5839
BarrieIce Accretion2035RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2035 | 15.6524 | 18.7368 | 22.6435 | 25.6261 | 28.6033
BarrieIce Accretion2040RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2040 | 15.647 | 18.7337 | 22.6473 | 25.6348 | 28.6226
BarrieIce Accretion2045RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2045 | 15.6417 | 18.7305 | 22.6512 | 25.6435 | 28.6419
BarrieIce Accretion2050RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2050 | 15.5947 | 18.6967 | 22.6366 | 25.6417 | 28.6554
BarrieIce Accretion2055RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2055 | 15.5531 | 18.6662 | 22.6182 | 25.6313 | 28.6496
BarrieIce Accretion2060RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2060 | 15.5115 | 18.6357 | 22.5998 | 25.6209 | 28.6438
BarrieIce Accretion2065RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2065 | 15.4699 | 18.6051 | 22.5814 | 25.6105 | 28.638
BarrieIce Accretion2070RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2070 | 15.4283 | 18.5746 | 22.563 | 25.6001 | 28.6322
BarrieIce Accretion2075RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2075 | 15.4283 | 18.608 | 22.6377 | 25.7041 | 28.7627
BarrieIce Accretion2080RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2080 | 15.4283 | 18.6414 | 22.7125 | 25.8081 | 28.8931
BarrieIce Accretion2085RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2085 | 15.4283 | 18.6748 | 22.7873 | 25.912 | 29.0235
BarrieIce Accretion2090RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2090 | 15.2523 | 18.53 | 22.6857 | 25.8341 | 28.98
BarrieIce Accretion2095RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2095 | 15.0762 | 18.3519 | 22.5093 | 25.6521 | 28.8061
BarrieIce Accretion2100RCP6.0 | Barrie | Ice Accretion | RCP6.0 | 2100 | 14.9002 | 18.1737 | 22.333 | 25.4702 | 28.6322
BarrieIce Accretion2023RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2023 | 15.6684 | 18.7464 | 22.632 | 25.6001 | 28.5453
BarrieIce Accretion2025RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2025 | 15.6577 | 18.74 | 22.6397 | 25.6175 | 28.5839
BarrieIce Accretion2030RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2030 | 15.647 | 18.7337 | 22.6473 | 25.6348 | 28.6226
BarrieIce Accretion2035RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2035 | 15.6364 | 18.7273 | 22.655 | 25.6521 | 28.6612
BarrieIce Accretion2040RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2040 | 15.567 | 18.6764 | 22.6243 | 25.6348 | 28.6516
BarrieIce Accretion2045RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2045 | 15.4977 | 18.6255 | 22.5937 | 25.6175 | 28.6419
BarrieIce Accretion2050RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2050 | 15.4283 | 18.6191 | 22.6627 | 25.7388 | 28.8061
BarrieIce Accretion2055RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2055 | 15.4283 | 18.6637 | 22.7623 | 25.8774 | 28.98
BarrieIce Accretion2060RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2060 | 15.2523 | 18.53 | 22.6857 | 25.8341 | 28.98
BarrieIce Accretion2065RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2065 | 15.0762 | 18.3519 | 22.5093 | 25.6521 | 28.8061
BarrieIce Accretion2070RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2070 | 14.6441 | 17.9191 | 22.0647 | 25.2016 | 28.3521
BarrieIce Accretion2075RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2075 | 14.388 | 17.6646 | 21.7963 | 24.9331 | 28.072
BarrieIce Accretion2080RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2080 | 14.1319 | 17.4101 | 21.528 | 24.6645 | 27.7918
BarrieIce Accretion2085RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2085 | 13.4758 | 16.6465 | 20.6425 | 23.6769 | 26.6906
BarrieIce Accretion2090RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2090 | 12.8196 | 15.8829 | 19.757 | 22.6893 | 25.5893
BarrieIce Accretion2095RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2095 | 12.8196 | 15.8829 | 19.757 | 22.6893 | 25.5893
BarrieIce Accretion2100RCP8.5 | Barrie | Ice Accretion | RCP8.5 | 2100 | 12.8196 | 15.8829 | 19.757 | 22.6893 | 25.5893
BarrieWind2023RCP4.5 | Barrie | Wind | RCP4.5 | 2023 | 76.374 | 82.2738 | 88.484 | 94.6967 | 100.9019
BarrieWind2025RCP4.5 | Barrie | Wind | RCP4.5 | 2025 | 76.3955 | 82.301 | 88.5192 | 94.7375 | 100.9503
BarrieWind2030RCP4.5 | Barrie | Wind | RCP4.5 | 2030 | 76.417 | 82.3283 | 88.5544 | 94.7783 | 100.9988
BarrieWind2035RCP4.5 | Barrie | Wind | RCP4.5 | 2035 | 76.4386 | 82.3556 | 88.5896 | 94.8191 | 101.0473
BarrieWind2040RCP4.5 | Barrie | Wind | RCP4.5 | 2040 | 76.4601 | 82.3829 | 88.6248 | 94.8599 | 101.0958
BarrieWind2045RCP4.5 | Barrie | Wind | RCP4.5 | 2045 | 76.4816 | 82.4102 | 88.66 | 94.9007 | 101.1443
BarrieWind2050RCP4.5 | Barrie | Wind | RCP4.5 | 2050 | 76.6232 | 82.5766 | 88.8554 | 95.1204 | 101.3914
BarrieWind2055RCP4.5 | Barrie | Wind | RCP4.5 | 2055 | 76.7433 | 82.7157 | 89.0155 | 95.2993 | 101.5901
BarrieWind2060RCP4.5 | Barrie | Wind | RCP4.5 | 2060 | 76.8633 | 82.8548 | 89.1757 | 95.4782 | 101.7887
BarrieWind2065RCP4.5 | Barrie | Wind | RCP4.5 | 2065 | 76.9834 | 82.9939 | 89.3358 | 95.6571 | 101.9873
BarrieWind2070RCP4.5 | Barrie | Wind | RCP4.5 | 2070 | 77.1035 | 83.1331 | 89.496 | 95.836 | 102.186
BarrieWind2075RCP4.5 | Barrie | Wind | RCP4.5 | 2075 | 77.1617 | 83.2095 | 89.5957 | 95.9553 | 102.3231
BarrieWind2080RCP4.5 | Barrie | Wind | RCP4.5 | 2080 | 77.22 | 83.2858 | 89.6955 | 96.0746 | 102.4602
BarrieWind2085RCP4.5 | Barrie | Wind | RCP4.5 | 2085 | 77.2782 | 83.3622 | 89.7952 | 96.1939 | 102.5973
BarrieWind2090RCP4.5 | Barrie | Wind | RCP4.5 | 2090 | 77.3365 | 83.4386 | 89.8949 | 96.3131 | 102.7344
BarrieWind2095RCP4.5 | Barrie | Wind | RCP4.5 | 2095 | 77.3947 | 83.515 | 89.9947 | 96.4324 | 102.8715
BarrieWind2100RCP4.5 | Barrie | Wind | RCP4.5 | 2100 | 77.453 | 83.5914 | 90.0944 | 96.5517 | 103.0086
BarrieWind2023RCP6.0 | Barrie | Wind | RCP6.0 | 2023 | 76.374 | 82.2738 | 88.484 | 94.6967 | 100.9019
BarrieWind2025RCP6.0 | Barrie | Wind | RCP6.0 | 2025 | 76.3955 | 82.301 | 88.5192 | 94.7375 | 100.9503
BarrieWind2030RCP6.0 | Barrie | Wind | RCP6.0 | 2030 | 76.417 | 82.3283 | 88.5544 | 94.7783 | 100.9988
BarrieWind2035RCP6.0 | Barrie | Wind | RCP6.0 | 2035 | 76.4386 | 82.3556 | 88.5896 | 94.8191 | 101.0473
BarrieWind2040RCP6.0 | Barrie | Wind | RCP6.0 | 2040 | 76.4601 | 82.3829 | 88.6248 | 94.8599 | 101.0958
BarrieWind2045RCP6.0 | Barrie | Wind | RCP6.0 | 2045 | 76.4816 | 82.4102 | 88.66 | 94.9007 | 101.1443
BarrieWind2050RCP6.0 | Barrie | Wind | RCP6.0 | 2050 | 76.6232 | 82.5766 | 88.8554 | 95.1204 | 101.3914
BarrieWind2055RCP6.0 | Barrie | Wind | RCP6.0 | 2055 | 76.7433 | 82.7157 | 89.0155 | 95.2993 | 101.5901
BarrieWind2060RCP6.0 | Barrie | Wind | RCP6.0 | 2060 | 76.8633 | 82.8548 | 89.1757 | 95.4782 | 101.7887
BarrieWind2065RCP6.0 | Barrie | Wind | RCP6.0 | 2065 | 76.9834 | 82.9939 | 89.3358 | 95.6571 | 101.9873
BarrieWind2070RCP6.0 | Barrie | Wind | RCP6.0 | 2070 | 77.1035 | 83.1331 | 89.496 | 95.836 | 102.186
BarrieWind2075RCP6.0 | Barrie | Wind | RCP6.0 | 2075 | 77.1908 | 83.2476 | 89.6456 | 96.015 | 102.3916
BarrieWind2080RCP6.0 | Barrie | Wind | RCP6.0 | 2080 | 77.2782 | 83.3622 | 89.7952 | 96.1939 | 102.5973
BarrieWind2085RCP6.0 | Barrie | Wind | RCP6.0 | 2085 | 77.3656 | 83.4768 | 89.9448 | 96.3728 | 102.8029
BarrieWind2090RCP6.0 | Barrie | Wind | RCP6.0 | 2090 | 77.7291 | 83.9242 | 90.4933 | 97.0099 | 103.5302
BarrieWind2095RCP6.0 | Barrie | Wind | RCP6.0 | 2095 | 78.0052 | 84.257 | 90.8923 | 97.4682 | 104.0519
BarrieWind2100RCP6.0 | Barrie | Wind | RCP6.0 | 2100 | 78.2812 | 84.5898 | 91.2912 | 97.9264 | 104.5736
BarrieWind2023RCP8.5 | Barrie | Wind | RCP8.5 | 2023 | 76.374 | 82.2738 | 88.484 | 94.6967 | 100.9019
BarrieWind2025RCP8.5 | Barrie | Wind | RCP8.5 | 2025 | 76.417 | 82.3283 | 88.5544 | 94.7783 | 100.9988
BarrieWind2030RCP8.5 | Barrie | Wind | RCP8.5 | 2030 | 76.4601 | 82.3829 | 88.6248 | 94.8599 | 101.0958
BarrieWind2035RCP8.5 | Barrie | Wind | RCP8.5 | 2035 | 76.5032 | 82.4374 | 88.6952 | 94.9415 | 101.1928
BarrieWind2040RCP8.5 | Barrie | Wind | RCP8.5 | 2040 | 76.7033 | 82.6693 | 88.9621 | 95.2397 | 101.5238
BarrieWind2045RCP8.5 | Barrie | Wind | RCP8.5 | 2045 | 76.9034 | 82.9012 | 89.2291 | 95.5379 | 101.8549
BarrieWind2050RCP8.5 | Barrie | Wind | RCP8.5 | 2050 | 77.22 | 83.2858 | 89.6955 | 96.0746 | 102.4602
BarrieWind2055RCP8.5 | Barrie | Wind | RCP8.5 | 2055 | 77.3365 | 83.4386 | 89.8949 | 96.3131 | 102.7344
BarrieWind2060RCP8.5 | Barrie | Wind | RCP8.5 | 2060 | 77.7291 | 83.9242 | 90.4933 | 97.0099 | 103.5302
BarrieWind2065RCP8.5 | Barrie | Wind | RCP8.5 | 2065 | 78.0052 | 84.257 | 90.8923 | 97.4682 | 104.0519
BarrieWind2070RCP8.5 | Barrie | Wind | RCP8.5 | 2070 | 78.4282 | 84.7671 | 91.5112 | 98.1806 | 104.8612
BarrieWind2075RCP8.5 | Barrie | Wind | RCP8.5 | 2075 | 78.5751 | 84.9445 | 91.7312 | 98.4349 | 105.1487
BarrieWind2080RCP8.5 | Barrie | Wind | RCP8.5 | 2080 | 78.722 | 85.1218 | 91.9512 | 98.6891 | 105.4363
BarrieWind2085RCP8.5 | Barrie | Wind | RCP8.5 | 2085 | 78.7524 | 85.1545 | 91.982 | 98.7221 | 105.4664
BarrieWind2090RCP8.5 | Barrie | Wind | RCP8.5 | 2090 | 78.7828 | 85.1873 | 92.0128 | 98.755 | 105.4965
BarrieWind2095RCP8.5 | Barrie | Wind | RCP8.5 | 2095 | 78.7828 | 85.1873 | 92.0128 | 98.755 | 105.4965
BarrieWind2100RCP8.5 | Barrie | Wind | RCP8.5 | 2100 | 78.7828 | 85.1873 | 92.0128 | 98.755 | 105.4965
BarriefieldIce Accretion2023RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2023 | 18.092 | 21.5584 | 25.974 | 29.3506 | 32.6945
BarriefieldIce Accretion2025RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2025 | 18.1674 | 21.6627 | 26.1127 | 29.5122 | 32.8856
BarriefieldIce Accretion2030RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2030 | 18.2428 | 21.767 | 26.2513 | 29.6738 | 33.0767
BarriefieldIce Accretion2035RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2035 | 18.3181 | 21.8713 | 26.39 | 29.8354 | 33.2678
BarriefieldIce Accretion2040RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2040 | 18.3935 | 21.9756 | 26.5287 | 29.997 | 33.4589
BarriefieldIce Accretion2045RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2045 | 18.4689 | 22.0799 | 26.6673 | 30.1586 | 33.65
BarriefieldIce Accretion2050RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2050 | 18.443 | 22.0807 | 26.6968 | 30.2085 | 33.7297
BarriefieldIce Accretion2055RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2055 | 18.3417 | 21.9771 | 26.5876 | 30.0969 | 33.6183
BarriefieldIce Accretion2060RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2060 | 18.2404 | 21.8735 | 26.4784 | 29.9852 | 33.5069
BarriefieldIce Accretion2065RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2065 | 18.139 | 21.7699 | 26.3692 | 29.8736 | 33.3955
BarriefieldIce Accretion2070RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2070 | 18.0377 | 21.6663 | 26.26 | 29.7619 | 33.2842
BarriefieldIce Accretion2075RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2075 | 18.0498 | 21.7059 | 26.3293 | 29.855 | 33.3988
BarriefieldIce Accretion2080RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2080 | 18.0618 | 21.7454 | 26.3987 | 29.948 | 33.5135
BarriefieldIce Accretion2085RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2085 | 18.0739 | 21.785 | 26.468 | 30.041 | 33.6281
BarriefieldIce Accretion2090RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2090 | 18.086 | 21.8246 | 26.5373 | 30.1341 | 33.7428
BarriefieldIce Accretion2095RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2095 | 18.098 | 21.8641 | 26.6067 | 30.2271 | 33.8575
BarriefieldIce Accretion2100RCP4.5 | Barriefield | Ice Accretion | RCP4.5 | 2100 | 18.1101 | 21.9037 | 26.676 | 30.3202 | 33.9721
BarriefieldIce Accretion2023RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2023 | 18.092 | 21.5584 | 25.974 | 29.3506 | 32.6945
BarriefieldIce Accretion2025RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2025 | 18.1674 | 21.6627 | 26.1127 | 29.5122 | 32.8856
BarriefieldIce Accretion2030RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2030 | 18.2428 | 21.767 | 26.2513 | 29.6738 | 33.0767
BarriefieldIce Accretion2035RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2035 | 18.3181 | 21.8713 | 26.39 | 29.8354 | 33.2678
BarriefieldIce Accretion2040RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2040 | 18.3935 | 21.9756 | 26.5287 | 29.997 | 33.4589
BarriefieldIce Accretion2045RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2045 | 18.4689 | 22.0799 | 26.6673 | 30.1586 | 33.65
BarriefieldIce Accretion2050RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2050 | 18.443 | 22.0807 | 26.6968 | 30.2085 | 33.7297
BarriefieldIce Accretion2055RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2055 | 18.3417 | 21.9771 | 26.5876 | 30.0969 | 33.6183
BarriefieldIce Accretion2060RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2060 | 18.2404 | 21.8735 | 26.4784 | 29.9852 | 33.5069
BarriefieldIce Accretion2065RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2065 | 18.139 | 21.7699 | 26.3692 | 29.8736 | 33.3955
BarriefieldIce Accretion2070RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2070 | 18.0377 | 21.6663 | 26.26 | 29.7619 | 33.2842
BarriefieldIce Accretion2075RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2075 | 18.0558 | 21.7257 | 26.364 | 29.9015 | 33.4562
BarriefieldIce Accretion2080RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2080 | 18.0739 | 21.785 | 26.468 | 30.041 | 33.6281
BarriefieldIce Accretion2085RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2085 | 18.092 | 21.8444 | 26.572 | 30.1806 | 33.8001
BarriefieldIce Accretion2090RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2090 | 17.8025 | 21.5584 | 26.2947 | 29.899 | 33.5135
BarriefieldIce Accretion2095RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2095 | 17.495 | 21.2131 | 25.9133 | 29.4779 | 33.0548
BarriefieldIce Accretion2100RCP6.0 | Barriefield | Ice Accretion | RCP6.0 | 2100 | 17.1874 | 20.8679 | 25.532 | 29.0568 | 32.5962
BarriefieldIce Accretion2023RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2023 | 18.092 | 21.5584 | 25.974 | 29.3506 | 32.6945
BarriefieldIce Accretion2025RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2025 | 18.2428 | 21.767 | 26.2513 | 29.6738 | 33.0767
BarriefieldIce Accretion2030RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2030 | 18.3935 | 21.9756 | 26.5287 | 29.997 | 33.4589
BarriefieldIce Accretion2035RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2035 | 18.5443 | 22.1842 | 26.806 | 30.3202 | 33.8411
BarriefieldIce Accretion2040RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2040 | 18.3754 | 22.0116 | 26.624 | 30.1341 | 33.6554
BarriefieldIce Accretion2045RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2045 | 18.2066 | 21.839 | 26.442 | 29.948 | 33.4698
BarriefieldIce Accretion2050RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2050 | 18.0618 | 21.7454 | 26.3987 | 29.948 | 33.5135
BarriefieldIce Accretion2055RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2055 | 18.086 | 21.8246 | 26.5373 | 30.1341 | 33.7428
BarriefieldIce Accretion2060RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2060 | 17.8025 | 21.5584 | 26.2947 | 29.899 | 33.5135
BarriefieldIce Accretion2065RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2065 | 17.495 | 21.2131 | 25.9133 | 29.4779 | 33.0548
BarriefieldIce Accretion2070RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2070 | 16.9401 | 20.6089 | 25.246 | 28.763 | 32.2795
BarriefieldIce Accretion2075RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2075 | 16.6929 | 20.3499 | 24.96 | 28.4692 | 31.9628
BarriefieldIce Accretion2080RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2080 | 16.4456 | 20.091 | 24.674 | 28.1754 | 31.6462
BarriefieldIce Accretion2085RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2085 | 15.8305 | 19.368 | 23.816 | 27.2059 | 30.5651
BarriefieldIce Accretion2090RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2090 | 15.2154 | 18.6451 | 22.958 | 26.2363 | 29.484
BarriefieldIce Accretion2095RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2095 | 15.2154 | 18.6451 | 22.958 | 26.2363 | 29.484
BarriefieldIce Accretion2100RCP8.5 | Barriefield | Ice Accretion | RCP8.5 | 2100 | 15.2154 | 18.6451 | 22.958 | 26.2363 | 29.484
BarriefieldWind2023RCP4.5 | Barriefield | Wind | RCP4.5 | 2023 | 87.8991 | 94.5754 | 101.592 | 108.627 | 115.6637
BarriefieldWind2025RCP4.5 | Barriefield | Wind | RCP4.5 | 2025 | 87.8829 | 94.547 | 101.5444 | 108.5652 | 115.5862
BarriefieldWind2030RCP4.5 | Barriefield | Wind | RCP4.5 | 2030 | 87.8668 | 94.5185 | 101.4968 | 108.5033 | 115.5087
BarriefieldWind2035RCP4.5 | Barriefield | Wind | RCP4.5 | 2035 | 87.8506 | 94.49 | 101.4492 | 108.4415 | 115.4312
BarriefieldWind2040RCP4.5 | Barriefield | Wind | RCP4.5 | 2040 | 87.8345 | 94.4616 | 101.4016 | 108.3797 | 115.3536
BarriefieldWind2045RCP4.5 | Barriefield | Wind | RCP4.5 | 2045 | 87.8183 | 94.4331 | 101.354 | 108.3178 | 115.2761
BarriefieldWind2050RCP4.5 | Barriefield | Wind | RCP4.5 | 2050 | 87.9131 | 94.5394 | 101.4716 | 108.4459 | 115.4149
BarriefieldWind2055RCP4.5 | Barriefield | Wind | RCP4.5 | 2055 | 88.0241 | 94.6741 | 101.6369 | 108.6358 | 115.6312
BarriefieldWind2060RCP4.5 | Barriefield | Wind | RCP4.5 | 2060 | 88.1351 | 94.8088 | 101.8021 | 108.8257 | 115.8474
BarriefieldWind2065RCP4.5 | Barriefield | Wind | RCP4.5 | 2065 | 88.2461 | 94.9435 | 101.9674 | 109.0156 | 116.0637
BarriefieldWind2070RCP4.5 | Barriefield | Wind | RCP4.5 | 2070 | 88.357 | 95.0782 | 102.1326 | 109.2055 | 116.28
BarriefieldWind2075RCP4.5 | Barriefield | Wind | RCP4.5 | 2075 | 88.4774 | 95.2426 | 102.3502 | 109.4674 | 116.5862
BarriefieldWind2080RCP4.5 | Barriefield | Wind | RCP4.5 | 2080 | 88.5978 | 95.407 | 102.5678 | 109.7294 | 116.8924
BarriefieldWind2085RCP4.5 | Barriefield | Wind | RCP4.5 | 2085 | 88.7182 | 95.5714 | 102.7854 | 109.9913 | 117.1986
BarriefieldWind2090RCP4.5 | Barriefield | Wind | RCP4.5 | 2090 | 88.8385 | 95.7359 | 103.003 | 110.2532 | 117.5048
BarriefieldWind2095RCP4.5 | Barriefield | Wind | RCP4.5 | 2095 | 88.9589 | 95.9003 | 103.2206 | 110.5152 | 117.811
BarriefieldWind2100RCP4.5 | Barriefield | Wind | RCP4.5 | 2100 | 89.0793 | 96.0647 | 103.4382 | 110.7771 | 118.1172
BarriefieldWind2023RCP6.0 | Barriefield | Wind | RCP6.0 | 2023 | 87.8991 | 94.5754 | 101.592 | 108.627 | 115.6637
BarriefieldWind2025RCP6.0 | Barriefield | Wind | RCP6.0 | 2025 | 87.8829 | 94.547 | 101.5444 | 108.5652 | 115.5862
BarriefieldWind2030RCP6.0 | Barriefield | Wind | RCP6.0 | 2030 | 87.8668 | 94.5185 | 101.4968 | 108.5033 | 115.5087
BarriefieldWind2035RCP6.0 | Barriefield | Wind | RCP6.0 | 2035 | 87.8506 | 94.49 | 101.4492 | 108.4415 | 115.4312
BarriefieldWind2040RCP6.0 | Barriefield | Wind | RCP6.0 | 2040 | 87.8345 | 94.4616 | 101.4016 | 108.3797 | 115.3536
BarriefieldWind2045RCP6.0 | Barriefield | Wind | RCP6.0 | 2045 | 87.8183 | 94.4331 | 101.354 | 108.3178 | 115.2761
BarriefieldWind2050RCP6.0 | Barriefield | Wind | RCP6.0 | 2050 | 87.9131 | 94.5394 | 101.4716 | 108.4459 | 115.4149
BarriefieldWind2055RCP6.0 | Barriefield | Wind | RCP6.0 | 2055 | 88.0241 | 94.6741 | 101.6369 | 108.6358 | 115.6312
BarriefieldWind2060RCP6.0 | Barriefield | Wind | RCP6.0 | 2060 | 88.1351 | 94.8088 | 101.8021 | 108.8257 | 115.8474
BarriefieldWind2065RCP6.0 | Barriefield | Wind | RCP6.0 | 2065 | 88.2461 | 94.9435 | 101.9674 | 109.0156 | 116.0637
BarriefieldWind2070RCP6.0 | Barriefield | Wind | RCP6.0 | 2070 | 88.357 | 95.0782 | 102.1326 | 109.2055 | 116.28
BarriefieldWind2075RCP6.0 | Barriefield | Wind | RCP6.0 | 2075 | 88.5376 | 95.3248 | 102.459 | 109.5984 | 116.7393
BarriefieldWind2080RCP6.0 | Barriefield | Wind | RCP6.0 | 2080 | 88.7182 | 95.5714 | 102.7854 | 109.9913 | 117.1986
BarriefieldWind2085RCP6.0 | Barriefield | Wind | RCP6.0 | 2085 | 88.8987 | 95.8181 | 103.1118 | 110.3842 | 117.6579
BarriefieldWind2090RCP6.0 | Barriefield | Wind | RCP6.0 | 2090 | 89.2818 | 96.3272 | 103.7782 | 111.1846 | 118.5901
BarriefieldWind2095RCP6.0 | Barriefield | Wind | RCP6.0 | 2095 | 89.4844 | 96.5896 | 104.1182 | 111.592 | 119.063
BarriefieldWind2100RCP6.0 | Barriefield | Wind | RCP6.0 | 2100 | 89.687 | 96.8521 | 104.4582 | 111.9995 | 119.5358
BarriefieldWind2023RCP8.5 | Barriefield | Wind | RCP8.5 | 2023 | 87.8991 | 94.5754 | 101.592 | 108.627 | 115.6637
BarriefieldWind2025RCP8.5 | Barriefield | Wind | RCP8.5 | 2025 | 87.8668 | 94.5185 | 101.4968 | 108.5033 | 115.5087
BarriefieldWind2030RCP8.5 | Barriefield | Wind | RCP8.5 | 2030 | 87.8345 | 94.4616 | 101.4016 | 108.3797 | 115.3536
BarriefieldWind2035RCP8.5 | Barriefield | Wind | RCP8.5 | 2035 | 87.8022 | 94.4047 | 101.3064 | 108.256 | 115.1986
BarriefieldWind2040RCP8.5 | Barriefield | Wind | RCP8.5 | 2040 | 87.9871 | 94.6292 | 101.5818 | 108.5725 | 115.5591
BarriefieldWind2045RCP8.5 | Barriefield | Wind | RCP8.5 | 2045 | 88.1721 | 94.8537 | 101.8572 | 108.889 | 115.9195
BarriefieldWind2050RCP8.5 | Barriefield | Wind | RCP8.5 | 2050 | 88.5978 | 95.407 | 102.5678 | 109.7294 | 116.8924
BarriefieldWind2055RCP8.5 | Barriefield | Wind | RCP8.5 | 2055 | 88.8385 | 95.7359 | 103.003 | 110.2532 | 117.5048
BarriefieldWind2060RCP8.5 | Barriefield | Wind | RCP8.5 | 2060 | 89.2818 | 96.3272 | 103.7782 | 111.1846 | 118.5901
BarriefieldWind2065RCP8.5 | Barriefield | Wind | RCP8.5 | 2065 | 89.4844 | 96.5896 | 104.1182 | 111.592 | 119.063
BarriefieldWind2070RCP8.5 | Barriefield | Wind | RCP8.5 | 2070 | 89.7604 | 96.9596 | 104.6078 | 112.185 | 119.7568
BarriefieldWind2075RCP8.5 | Barriefield | Wind | RCP8.5 | 2075 | 89.8338 | 97.0671 | 104.7574 | 112.3705 | 119.9777
BarriefieldWind2080RCP8.5 | Barriefield | Wind | RCP8.5 | 2080 | 89.9072 | 97.1746 | 104.907 | 112.5561 | 120.1986
BarriefieldWind2085RCP8.5 | Barriefield | Wind | RCP8.5 | 2085 | 90.0789 | 97.4117 | 105.2283 | 112.9435 | 120.6638
BarriefieldWind2090RCP8.5 | Barriefield | Wind | RCP8.5 | 2090 | 90.2507 | 97.6489 | 105.5496 | 113.331 | 121.1289
BarriefieldWind2095RCP8.5 | Barriefield | Wind | RCP8.5 | 2095 | 90.2507 | 97.6489 | 105.5496 | 113.331 | 121.1289
BarriefieldWind2100RCP8.5 | Barriefield | Wind | RCP8.5 | 2100 | 90.2507 | 97.6489 | 105.5496 | 113.331 | 121.1289
BeavertonIce Accretion2023RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
BeavertonIce Accretion2025RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
BeavertonIce Accretion2030RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
BeavertonIce Accretion2035RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
BeavertonIce Accretion2040RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
BeavertonIce Accretion2045RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
BeavertonIce Accretion2050RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
BeavertonIce Accretion2055RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
BeavertonIce Accretion2060RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
BeavertonIce Accretion2065RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
BeavertonIce Accretion2070RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
BeavertonIce Accretion2075RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2075 | 17.2744 | 20.8814 | 25.4167 | 28.8762 | 32.34
BeavertonIce Accretion2080RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2080 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
BeavertonIce Accretion2085RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2085 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
BeavertonIce Accretion2090RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2090 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
BeavertonIce Accretion2095RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2095 | 17.2048 | 20.9091 | 25.5833 | 29.121 | 32.676
BeavertonIce Accretion2100RCP4.5 | Beaverton | Ice Accretion | RCP4.5 | 2100 | 17.1874 | 20.916 | 25.625 | 29.1822 | 32.76
BeavertonIce Accretion2023RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
BeavertonIce Accretion2025RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
BeavertonIce Accretion2030RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
BeavertonIce Accretion2035RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
BeavertonIce Accretion2040RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
BeavertonIce Accretion2045RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
BeavertonIce Accretion2050RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
BeavertonIce Accretion2055RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
BeavertonIce Accretion2060RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
BeavertonIce Accretion2065RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
BeavertonIce Accretion2070RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
BeavertonIce Accretion2075RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2075 | 17.2657 | 20.8849 | 25.4375 | 28.9068 | 32.382
BeavertonIce Accretion2080RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2080 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
BeavertonIce Accretion2085RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2085 | 17.2135 | 20.9056 | 25.5625 | 29.0904 | 32.634
BeavertonIce Accretion2090RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2090 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
BeavertonIce Accretion2095RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2095 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
BeavertonIce Accretion2100RCP6.0 | Beaverton | Ice Accretion | RCP6.0 | 2100 | 16.2654 | 19.8992 | 24.5 | 27.9957 | 31.4685
BeavertonIce Accretion2023RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
BeavertonIce Accretion2025RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2025 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
BeavertonIce Accretion2030RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2030 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
BeavertonIce Accretion2035RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2035 | 17.6919 | 21.2272 | 25.725 | 29.154 | 32.6025
BeavertonIce Accretion2040RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2040 | 17.5585 | 21.1097 | 25.6083 | 29.041 | 32.487
BeavertonIce Accretion2045RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2045 | 17.4251 | 20.9921 | 25.4917 | 28.928 | 32.3715
BeavertonIce Accretion2050RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2050 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
BeavertonIce Accretion2055RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2055 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
BeavertonIce Accretion2060RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2060 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
BeavertonIce Accretion2065RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2065 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
BeavertonIce Accretion2070RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2070 | 15.9987 | 19.6226 | 24.2083 | 27.685 | 31.143
BeavertonIce Accretion2075RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2075 | 15.7319 | 19.3459 | 23.9167 | 27.3742 | 30.8175
BeavertonIce Accretion2080RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2080 | 15.4652 | 19.0693 | 23.625 | 27.0635 | 30.492
BeavertonIce Accretion2085RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2085 | 14.8911 | 18.426 | 22.8875 | 26.2584 | 29.6258
BeavertonIce Accretion2090RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2090 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
BeavertonIce Accretion2095RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2095 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
BeavertonIce Accretion2100RCP8.5 | Beaverton | Ice Accretion | RCP8.5 | 2100 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
BeavertonWind2023RCP4.5 | Beaverton | Wind | RCP4.5 | 2023 | 73.8804 | 79.5796 | 85.5695 | 91.5594 | 97.5589
BeavertonWind2025RCP4.5 | Beaverton | Wind | RCP4.5 | 2025 | 73.9134 | 79.6231 | 85.6276 | 91.6306 | 97.6413
BeavertonWind2030RCP4.5 | Beaverton | Wind | RCP4.5 | 2030 | 73.9465 | 79.6666 | 85.6857 | 91.7019 | 97.7236
BeavertonWind2035RCP4.5 | Beaverton | Wind | RCP4.5 | 2035 | 73.9795 | 79.7101 | 85.7437 | 91.7731 | 97.806
BeavertonWind2040RCP4.5 | Beaverton | Wind | RCP4.5 | 2040 | 74.0125 | 79.7535 | 85.8018 | 91.8443 | 97.8884
BeavertonWind2045RCP4.5 | Beaverton | Wind | RCP4.5 | 2045 | 74.0456 | 79.797 | 85.8599 | 91.9156 | 97.9707
BeavertonWind2050RCP4.5 | Beaverton | Wind | RCP4.5 | 2050 | 74.1446 | 79.918 | 86.0081 | 92.0869 | 98.1655
BeavertonWind2055RCP4.5 | Beaverton | Wind | RCP4.5 | 2055 | 74.2107 | 79.9954 | 86.0982 | 92.1869 | 98.2779
BeavertonWind2060RCP4.5 | Beaverton | Wind | RCP4.5 | 2060 | 74.2768 | 80.0729 | 86.1883 | 92.287 | 98.3903
BeavertonWind2065RCP4.5 | Beaverton | Wind | RCP4.5 | 2065 | 74.3428 | 80.1504 | 86.2784 | 92.387 | 98.5027
BeavertonWind2070RCP4.5 | Beaverton | Wind | RCP4.5 | 2070 | 74.4089 | 80.2278 | 86.3685 | 92.4871 | 98.6151
BeavertonWind2075RCP4.5 | Beaverton | Wind | RCP4.5 | 2075 | 74.481 | 80.3174 | 86.479 | 92.6174 | 98.7637
BeavertonWind2080RCP4.5 | Beaverton | Wind | RCP4.5 | 2080 | 74.5532 | 80.407 | 86.5895 | 92.7478 | 98.9123
BeavertonWind2085RCP4.5 | Beaverton | Wind | RCP4.5 | 2085 | 74.6254 | 80.4966 | 86.7 | 92.8781 | 99.0609
BeavertonWind2090RCP4.5 | Beaverton | Wind | RCP4.5 | 2090 | 74.6976 | 80.5862 | 86.8105 | 93.0085 | 99.2094
BeavertonWind2095RCP4.5 | Beaverton | Wind | RCP4.5 | 2095 | 74.7697 | 80.6758 | 86.921 | 93.1389 | 99.358
BeavertonWind2100RCP4.5 | Beaverton | Wind | RCP4.5 | 2100 | 74.8419 | 80.7654 | 87.0315 | 93.2692 | 99.5066
BeavertonWind2023RCP6.0 | Beaverton | Wind | RCP6.0 | 2023 | 73.8804 | 79.5796 | 85.5695 | 91.5594 | 97.5589
BeavertonWind2025RCP6.0 | Beaverton | Wind | RCP6.0 | 2025 | 73.9134 | 79.6231 | 85.6276 | 91.6306 | 97.6413
BeavertonWind2030RCP6.0 | Beaverton | Wind | RCP6.0 | 2030 | 73.9465 | 79.6666 | 85.6857 | 91.7019 | 97.7236
BeavertonWind2035RCP6.0 | Beaverton | Wind | RCP6.0 | 2035 | 73.9795 | 79.7101 | 85.7437 | 91.7731 | 97.806
BeavertonWind2040RCP6.0 | Beaverton | Wind | RCP6.0 | 2040 | 74.0125 | 79.7535 | 85.8018 | 91.8443 | 97.8884
BeavertonWind2045RCP6.0 | Beaverton | Wind | RCP6.0 | 2045 | 74.0456 | 79.797 | 85.8599 | 91.9156 | 97.9707
BeavertonWind2050RCP6.0 | Beaverton | Wind | RCP6.0 | 2050 | 74.1446 | 79.918 | 86.0081 | 92.0869 | 98.1655
BeavertonWind2055RCP6.0 | Beaverton | Wind | RCP6.0 | 2055 | 74.2107 | 79.9954 | 86.0982 | 92.1869 | 98.2779
BeavertonWind2060RCP6.0 | Beaverton | Wind | RCP6.0 | 2060 | 74.2768 | 80.0729 | 86.1883 | 92.287 | 98.3903
BeavertonWind2065RCP6.0 | Beaverton | Wind | RCP6.0 | 2065 | 74.3428 | 80.1504 | 86.2784 | 92.387 | 98.5027
BeavertonWind2070RCP6.0 | Beaverton | Wind | RCP6.0 | 2070 | 74.4089 | 80.2278 | 86.3685 | 92.4871 | 98.6151
BeavertonWind2075RCP6.0 | Beaverton | Wind | RCP6.0 | 2075 | 74.5171 | 80.3622 | 86.5343 | 92.6826 | 98.838
BeavertonWind2080RCP6.0 | Beaverton | Wind | RCP6.0 | 2080 | 74.6254 | 80.4966 | 86.7 | 92.8781 | 99.0609
BeavertonWind2085RCP6.0 | Beaverton | Wind | RCP6.0 | 2085 | 74.7336 | 80.631 | 86.8658 | 93.0737 | 99.2837
BeavertonWind2090RCP6.0 | Beaverton | Wind | RCP6.0 | 2090 | 75.0792 | 81.0368 | 87.3488 | 93.6209 | 99.8974
BeavertonWind2095RCP6.0 | Beaverton | Wind | RCP6.0 | 2095 | 75.3165 | 81.3082 | 87.6662 | 93.9726 | 100.2883
BeavertonWind2100RCP6.0 | Beaverton | Wind | RCP6.0 | 2100 | 75.5538 | 81.5796 | 87.9835 | 94.3242 | 100.6791
BeavertonWind2023RCP8.5 | Beaverton | Wind | RCP8.5 | 2023 | 73.8804 | 79.5796 | 85.5695 | 91.5594 | 97.5589
BeavertonWind2025RCP8.5 | Beaverton | Wind | RCP8.5 | 2025 | 73.9465 | 79.6666 | 85.6857 | 91.7019 | 97.7236
BeavertonWind2030RCP8.5 | Beaverton | Wind | RCP8.5 | 2030 | 74.0125 | 79.7535 | 85.8018 | 91.8443 | 97.8884
BeavertonWind2035RCP8.5 | Beaverton | Wind | RCP8.5 | 2035 | 74.0786 | 79.8405 | 85.918 | 91.9868 | 98.0531
BeavertonWind2040RCP8.5 | Beaverton | Wind | RCP8.5 | 2040 | 74.1887 | 79.9696 | 86.0682 | 92.1536 | 98.2404
BeavertonWind2045RCP8.5 | Beaverton | Wind | RCP8.5 | 2045 | 74.2988 | 80.0987 | 86.2183 | 92.3203 | 98.4278
BeavertonWind2050RCP8.5 | Beaverton | Wind | RCP8.5 | 2050 | 74.5532 | 80.407 | 86.5895 | 92.7478 | 98.9123
BeavertonWind2055RCP8.5 | Beaverton | Wind | RCP8.5 | 2055 | 74.6976 | 80.5862 | 86.8105 | 93.0085 | 99.2094
BeavertonWind2060RCP8.5 | Beaverton | Wind | RCP8.5 | 2060 | 75.0792 | 81.0368 | 87.3488 | 93.6209 | 99.8974
BeavertonWind2065RCP8.5 | Beaverton | Wind | RCP8.5 | 2065 | 75.3165 | 81.3082 | 87.6662 | 93.9726 | 100.2883
BeavertonWind2070RCP8.5 | Beaverton | Wind | RCP8.5 | 2070 | 75.637 | 81.6876 | 88.1167 | 94.4819 | 100.8632
BeavertonWind2075RCP8.5 | Beaverton | Wind | RCP8.5 | 2075 | 75.7202 | 81.7957 | 88.2498 | 94.6395 | 101.0473
BeavertonWind2080RCP8.5 | Beaverton | Wind | RCP8.5 | 2080 | 75.8034 | 81.9037 | 88.383 | 94.7972 | 101.2314
BeavertonWind2085RCP8.5 | Beaverton | Wind | RCP8.5 | 2085 | 75.9979 | 82.1764 | 88.7655 | 95.2656 | 101.7886
BeavertonWind2090RCP8.5 | Beaverton | Wind | RCP8.5 | 2090 | 76.1924 | 82.4491 | 89.148 | 95.734 | 102.3458
BeavertonWind2095RCP8.5 | Beaverton | Wind | RCP8.5 | 2095 | 76.1924 | 82.4491 | 89.148 | 95.734 | 102.3458
BeavertonWind2100RCP8.5 | Beaverton | Wind | RCP8.5 | 2100 | 76.1924 | 82.4491 | 89.148 | 95.734 | 102.3458
BellevilleIce Accretion2023RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
BellevilleIce Accretion2025RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
BellevilleIce Accretion2030RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
BellevilleIce Accretion2035RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
BellevilleIce Accretion2040RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
BellevilleIce Accretion2045RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
BellevilleIce Accretion2050RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
BellevilleIce Accretion2055RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
BellevilleIce Accretion2060RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
BellevilleIce Accretion2065RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
BellevilleIce Accretion2070RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
BellevilleIce Accretion2075RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2075 | 16.8859 | 20.3972 | 24.8292 | 28.2123 | 31.5682
BellevilleIce Accretion2080RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2080 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
BellevilleIce Accretion2085RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2085 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
BellevilleIce Accretion2090RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2090 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
BellevilleIce Accretion2095RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2095 | 16.7235 | 20.3142 | 24.8458 | 28.2877 | 31.7152
BellevilleIce Accretion2100RCP4.5 | Belleville | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.2935 | 24.85 | 28.3065 | 31.752
BellevilleIce Accretion2023RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
BellevilleIce Accretion2025RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
BellevilleIce Accretion2030RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
BellevilleIce Accretion2035RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
BellevilleIce Accretion2040RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
BellevilleIce Accretion2045RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
BellevilleIce Accretion2050RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
BellevilleIce Accretion2055RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
BellevilleIce Accretion2060RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
BellevilleIce Accretion2065RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
BellevilleIce Accretion2070RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
BellevilleIce Accretion2075RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2075 | 16.8656 | 20.3869 | 24.8313 | 28.2217 | 31.5866
BellevilleIce Accretion2080RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2080 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
BellevilleIce Accretion2085RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2085 | 16.7438 | 20.3246 | 24.8438 | 28.2782 | 31.6969
BellevilleIce Accretion2090RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2090 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
BellevilleIce Accretion2095RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2095 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
BellevilleIce Accretion2100RCP6.0 | Belleville | Ice Accretion | RCP6.0 | 2100 | 15.6565 | 19.173 | 23.6 | 26.9505 | 30.2715
BellevilleIce Accretion2023RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
BellevilleIce Accretion2025RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2025 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
BellevilleIce Accretion2030RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2030 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
BellevilleIce Accretion2035RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2035 | 17.6745 | 21.2272 | 25.725 | 29.154 | 32.571
BellevilleIce Accretion2040RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2040 | 17.4251 | 20.9575 | 25.425 | 28.8338 | 32.2245
BellevilleIce Accretion2045RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2045 | 17.1758 | 20.6877 | 25.125 | 28.5137 | 31.878
BellevilleIce Accretion2050RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2050 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
BellevilleIce Accretion2055RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2055 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
BellevilleIce Accretion2060RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2060 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
BellevilleIce Accretion2065RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2065 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
BellevilleIce Accretion2070RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2070 | 15.2216 | 18.6888 | 23.05 | 26.3478 | 29.631
BellevilleIce Accretion2075RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2075 | 14.7867 | 18.2047 | 22.5 | 25.7452 | 28.9905
BellevilleIce Accretion2080RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2080 | 14.3518 | 17.7205 | 21.95 | 25.1425 | 28.35
BellevilleIce Accretion2085RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2085 | 13.6908 | 16.9424 | 21.025 | 24.0972 | 27.1845
BellevilleIce Accretion2090RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2090 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
BellevilleIce Accretion2095RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2095 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
BellevilleIce Accretion2100RCP8.5 | Belleville | Ice Accretion | RCP8.5 | 2100 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
BellevilleWind2023RCP4.5 | Belleville | Wind | RCP4.5 | 2023 | 85.129 | 91.7051 | 98.6174 | 105.5311 | 112.4462
BellevilleWind2025RCP4.5 | Belleville | Wind | RCP4.5 | 2025 | 85.0966 | 91.6701 | 98.5831 | 105.4944 | 112.4089
BellevilleWind2030RCP4.5 | Belleville | Wind | RCP4.5 | 2030 | 85.0641 | 91.6352 | 98.5488 | 105.4577 | 112.3717
BellevilleWind2035RCP4.5 | Belleville | Wind | RCP4.5 | 2035 | 85.0317 | 91.6003 | 98.5145 | 105.421 | 112.3345
BellevilleWind2040RCP4.5 | Belleville | Wind | RCP4.5 | 2040 | 84.9993 | 91.5653 | 98.4802 | 105.3843 | 112.2972
BellevilleWind2045RCP4.5 | Belleville | Wind | RCP4.5 | 2045 | 84.9668 | 91.5304 | 98.4459 | 105.3476 | 112.26
BellevilleWind2050RCP4.5 | Belleville | Wind | RCP4.5 | 2050 | 85.0545 | 91.6559 | 98.6213 | 105.5626 | 112.5177
BellevilleWind2055RCP4.5 | Belleville | Wind | RCP4.5 | 2055 | 85.1747 | 91.8163 | 98.831 | 105.8142 | 112.8126
BellevilleWind2060RCP4.5 | Belleville | Wind | RCP4.5 | 2060 | 85.2949 | 91.9767 | 99.0408 | 106.0659 | 113.1076
BellevilleWind2065RCP4.5 | Belleville | Wind | RCP4.5 | 2065 | 85.415 | 92.1371 | 99.2505 | 106.3176 | 113.4025
BellevilleWind2070RCP4.5 | Belleville | Wind | RCP4.5 | 2070 | 85.5352 | 92.2975 | 99.4602 | 106.5692 | 113.6974
BellevilleWind2075RCP4.5 | Belleville | Wind | RCP4.5 | 2075 | 85.5958 | 92.381 | 99.5713 | 106.7038 | 113.8557
BellevilleWind2080RCP4.5 | Belleville | Wind | RCP4.5 | 2080 | 85.6565 | 92.4646 | 99.6823 | 106.8384 | 114.014
BellevilleWind2085RCP4.5 | Belleville | Wind | RCP4.5 | 2085 | 85.7171 | 92.5481 | 99.7934 | 106.9729 | 114.1723
BellevilleWind2090RCP4.5 | Belleville | Wind | RCP4.5 | 2090 | 85.7778 | 92.6317 | 99.9045 | 107.1075 | 114.3305
BellevilleWind2095RCP4.5 | Belleville | Wind | RCP4.5 | 2095 | 85.8384 | 92.7152 | 100.0155 | 107.2421 | 114.4888
BellevilleWind2100RCP4.5 | Belleville | Wind | RCP4.5 | 2100 | 85.8991 | 92.7987 | 100.1266 | 107.3766 | 114.6471
BellevilleWind2023RCP6.0 | Belleville | Wind | RCP6.0 | 2023 | 85.129 | 91.7051 | 98.6174 | 105.5311 | 112.4462
BellevilleWind2025RCP6.0 | Belleville | Wind | RCP6.0 | 2025 | 85.0966 | 91.6701 | 98.5831 | 105.4944 | 112.4089
BellevilleWind2030RCP6.0 | Belleville | Wind | RCP6.0 | 2030 | 85.0641 | 91.6352 | 98.5488 | 105.4577 | 112.3717
BellevilleWind2035RCP6.0 | Belleville | Wind | RCP6.0 | 2035 | 85.0317 | 91.6003 | 98.5145 | 105.421 | 112.3345
BellevilleWind2040RCP6.0 | Belleville | Wind | RCP6.0 | 2040 | 84.9993 | 91.5653 | 98.4802 | 105.3843 | 112.2972
BellevilleWind2045RCP6.0 | Belleville | Wind | RCP6.0 | 2045 | 84.9668 | 91.5304 | 98.4459 | 105.3476 | 112.26
BellevilleWind2050RCP6.0 | Belleville | Wind | RCP6.0 | 2050 | 85.0545 | 91.6559 | 98.6213 | 105.5626 | 112.5177
BellevilleWind2055RCP6.0 | Belleville | Wind | RCP6.0 | 2055 | 85.1747 | 91.8163 | 98.831 | 105.8142 | 112.8126
BellevilleWind2060RCP6.0 | Belleville | Wind | RCP6.0 | 2060 | 85.2949 | 91.9767 | 99.0408 | 106.0659 | 113.1076
BellevilleWind2065RCP6.0 | Belleville | Wind | RCP6.0 | 2065 | 85.415 | 92.1371 | 99.2505 | 106.3176 | 113.4025
BellevilleWind2070RCP6.0 | Belleville | Wind | RCP6.0 | 2070 | 85.5352 | 92.2975 | 99.4602 | 106.5692 | 113.6974
BellevilleWind2075RCP6.0 | Belleville | Wind | RCP6.0 | 2075 | 85.6262 | 92.4228 | 99.6268 | 106.7711 | 113.9348
BellevilleWind2080RCP6.0 | Belleville | Wind | RCP6.0 | 2080 | 85.7171 | 92.5481 | 99.7934 | 106.9729 | 114.1723
BellevilleWind2085RCP6.0 | Belleville | Wind | RCP6.0 | 2085 | 85.8081 | 92.6734 | 99.96 | 107.1748 | 114.4097
BellevilleWind2090RCP6.0 | Belleville | Wind | RCP6.0 | 2090 | 86.1896 | 93.1512 | 100.5578 | 107.88 | 115.2168
BellevilleWind2095RCP6.0 | Belleville | Wind | RCP6.0 | 2095 | 86.4801 | 93.5036 | 100.989 | 108.3833 | 115.7866
BellevilleWind2100RCP6.0 | Belleville | Wind | RCP6.0 | 2100 | 86.7707 | 93.856 | 101.4202 | 108.8866 | 116.3564
BellevilleWind2023RCP8.5 | Belleville | Wind | RCP8.5 | 2023 | 85.129 | 91.7051 | 98.6174 | 105.5311 | 112.4462
BellevilleWind2025RCP8.5 | Belleville | Wind | RCP8.5 | 2025 | 85.0641 | 91.6352 | 98.5488 | 105.4577 | 112.3717
BellevilleWind2030RCP8.5 | Belleville | Wind | RCP8.5 | 2030 | 84.9993 | 91.5653 | 98.4802 | 105.3843 | 112.2972
BellevilleWind2035RCP8.5 | Belleville | Wind | RCP8.5 | 2035 | 84.9344 | 91.4954 | 98.4116 | 105.3109 | 112.2227
BellevilleWind2040RCP8.5 | Belleville | Wind | RCP8.5 | 2040 | 85.1346 | 91.7628 | 98.7611 | 105.7303 | 112.7143
BellevilleWind2045RCP8.5 | Belleville | Wind | RCP8.5 | 2045 | 85.3349 | 92.0301 | 99.1107 | 106.1498 | 113.2059
BellevilleWind2050RCP8.5 | Belleville | Wind | RCP8.5 | 2050 | 85.6565 | 92.4646 | 99.6823 | 106.8384 | 114.014
BellevilleWind2055RCP8.5 | Belleville | Wind | RCP8.5 | 2055 | 85.7778 | 92.6317 | 99.9045 | 107.1075 | 114.3305
BellevilleWind2060RCP8.5 | Belleville | Wind | RCP8.5 | 2060 | 86.1896 | 93.1512 | 100.5578 | 107.88 | 115.2168
BellevilleWind2065RCP8.5 | Belleville | Wind | RCP8.5 | 2065 | 86.4801 | 93.5036 | 100.989 | 108.3833 | 115.7866
BellevilleWind2070RCP8.5 | Belleville | Wind | RCP8.5 | 2070 | 86.6917 | 93.7679 | 101.3189 | 108.7748 | 116.2372
BellevilleWind2075RCP8.5 | Belleville | Wind | RCP8.5 | 2075 | 86.6127 | 93.6798 | 101.2177 | 108.6629 | 116.118
BellevilleWind2080RCP8.5 | Belleville | Wind | RCP8.5 | 2080 | 86.5337 | 93.5917 | 101.1164 | 108.5511 | 115.9989
BellevilleWind2085RCP8.5 | Belleville | Wind | RCP8.5 | 2085 | 86.741 | 93.9061 | 101.5672 | 109.1121 | 116.6748
BellevilleWind2090RCP8.5 | Belleville | Wind | RCP8.5 | 2090 | 86.9484 | 94.2205 | 102.018 | 109.6731 | 117.3507
BellevilleWind2095RCP8.5 | Belleville | Wind | RCP8.5 | 2095 | 86.9484 | 94.2205 | 102.018 | 109.6731 | 117.3507
BellevilleWind2100RCP8.5 | Belleville | Wind | RCP8.5 | 2100 | 86.9484 | 94.2205 | 102.018 | 109.6731 | 117.3507
BelmontIce Accretion2023RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2023 | 20.5831 | 24.7008 | 29.91 | 33.8661 | 37.8378
BelmontIce Accretion2025RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2025 | 20.4614 | 24.568 | 29.765 | 33.7135 | 37.674
BelmontIce Accretion2030RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2030 | 20.3396 | 24.4352 | 29.62 | 33.561 | 37.5102
BelmontIce Accretion2035RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2035 | 20.2178 | 24.3024 | 29.475 | 33.4085 | 37.3464
BelmontIce Accretion2040RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2040 | 20.096 | 24.1696 | 29.33 | 33.2559 | 37.1826
BelmontIce Accretion2045RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2045 | 19.9743 | 24.0368 | 29.185 | 33.1033 | 37.0188
BelmontIce Accretion2050RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2050 | 19.4642 | 23.4757 | 28.554 | 32.422 | 36.2804
BelmontIce Accretion2055RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2055 | 19.0759 | 23.0474 | 28.068 | 31.8931 | 35.7059
BelmontIce Accretion2060RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2060 | 18.6876 | 22.6192 | 27.582 | 31.3643 | 35.1313
BelmontIce Accretion2065RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2065 | 18.2994 | 22.1909 | 27.096 | 30.8354 | 34.5568
BelmontIce Accretion2070RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2070 | 17.9111 | 21.7626 | 26.61 | 30.3066 | 33.9822
BelmontIce Accretion2075RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2075 | 17.7754 | 21.6257 | 26.47 | 30.1597 | 33.831
BelmontIce Accretion2080RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2080 | 17.6397 | 21.4887 | 26.33 | 30.0128 | 33.6798
BelmontIce Accretion2085RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2085 | 17.504 | 21.3517 | 26.19 | 29.8659 | 33.5286
BelmontIce Accretion2090RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2090 | 17.3683 | 21.2148 | 26.05 | 29.719 | 33.3774
BelmontIce Accretion2095RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2095 | 17.2326 | 21.0778 | 25.91 | 29.5721 | 33.2262
BelmontIce Accretion2100RCP4.5 | Belmont | Ice Accretion | RCP4.5 | 2100 | 17.0969 | 20.9409 | 25.77 | 29.4252 | 33.075
BelmontIce Accretion2023RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2023 | 20.5831 | 24.7008 | 29.91 | 33.8661 | 37.8378
BelmontIce Accretion2025RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2025 | 20.4614 | 24.568 | 29.765 | 33.7135 | 37.674
BelmontIce Accretion2030RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2030 | 20.3396 | 24.4352 | 29.62 | 33.561 | 37.5102
BelmontIce Accretion2035RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2035 | 20.2178 | 24.3024 | 29.475 | 33.4085 | 37.3464
BelmontIce Accretion2040RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2040 | 20.096 | 24.1696 | 29.33 | 33.2559 | 37.1826
BelmontIce Accretion2045RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2045 | 19.9743 | 24.0368 | 29.185 | 33.1033 | 37.0188
BelmontIce Accretion2050RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2050 | 19.4642 | 23.4757 | 28.554 | 32.422 | 36.2804
BelmontIce Accretion2055RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2055 | 19.0759 | 23.0474 | 28.068 | 31.8931 | 35.7059
BelmontIce Accretion2060RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2060 | 18.6876 | 22.6192 | 27.582 | 31.3643 | 35.1313
BelmontIce Accretion2065RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2065 | 18.2994 | 22.1909 | 27.096 | 30.8354 | 34.5568
BelmontIce Accretion2070RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2070 | 17.9111 | 21.7626 | 26.61 | 30.3066 | 33.9822
BelmontIce Accretion2075RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2075 | 17.7075 | 21.5572 | 26.4 | 30.0862 | 33.7554
BelmontIce Accretion2080RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2080 | 17.504 | 21.3517 | 26.19 | 29.8659 | 33.5286
BelmontIce Accretion2085RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2085 | 17.3005 | 21.1463 | 25.98 | 29.6456 | 33.3018
BelmontIce Accretion2090RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2090 | 16.6098 | 20.3931 | 25.15 | 28.7472 | 32.3316
BelmontIce Accretion2095RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2095 | 16.1228 | 19.8453 | 24.53 | 28.0692 | 31.5882
BelmontIce Accretion2100RCP6.0 | Belmont | Ice Accretion | RCP6.0 | 2100 | 15.6357 | 19.2975 | 23.91 | 27.3912 | 30.8448
BelmontIce Accretion2023RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2023 | 20.5831 | 24.7008 | 29.91 | 33.8661 | 37.8378
BelmontIce Accretion2025RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2025 | 20.3396 | 24.4352 | 29.62 | 33.561 | 37.5102
BelmontIce Accretion2030RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2030 | 20.096 | 24.1696 | 29.33 | 33.2559 | 37.1826
BelmontIce Accretion2035RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2035 | 19.8525 | 23.904 | 29.04 | 32.9508 | 36.855
BelmontIce Accretion2040RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2040 | 19.2054 | 23.1902 | 28.23 | 32.0694 | 35.8974
BelmontIce Accretion2045RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2045 | 18.5582 | 22.4764 | 27.42 | 31.188 | 34.9398
BelmontIce Accretion2050RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2050 | 17.6397 | 21.4887 | 26.33 | 30.0128 | 33.6798
BelmontIce Accretion2055RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2055 | 17.3683 | 21.2148 | 26.05 | 29.719 | 33.3774
BelmontIce Accretion2060RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2060 | 16.6098 | 20.3931 | 25.15 | 28.7472 | 32.3316
BelmontIce Accretion2065RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2065 | 16.1228 | 19.8453 | 24.53 | 28.0692 | 31.5882
BelmontIce Accretion2070RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2070 | 15.3225 | 18.9655 | 23.55 | 26.9957 | 30.429
BelmontIce Accretion2075RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2075 | 15.0094 | 18.6335 | 23.19 | 26.6002 | 30.0132
BelmontIce Accretion2080RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2080 | 14.6963 | 18.3015 | 22.83 | 26.2047 | 29.5974
BelmontIce Accretion2085RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2085 | 13.7673 | 17.2059 | 21.51 | 24.73 | 27.9531
BelmontIce Accretion2090RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2090 | 12.8384 | 16.1103 | 20.19 | 23.2554 | 26.3088
BelmontIce Accretion2095RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2095 | 12.8384 | 16.1103 | 20.19 | 23.2554 | 26.3088
BelmontIce Accretion2100RCP8.5 | Belmont | Ice Accretion | RCP8.5 | 2100 | 12.8384 | 16.1103 | 20.19 | 23.2554 | 26.3088
BelmontWind2023RCP4.5 | Belmont | Wind | RCP4.5 | 2023 | 88.7974 | 95.7896 | 103.1934 | 110.5588 | 117.9312
BelmontWind2025RCP4.5 | Belmont | Wind | RCP4.5 | 2025 | 88.909 | 95.9382 | 103.3889 | 110.7935 | 118.2064
BelmontWind2030RCP4.5 | Belmont | Wind | RCP4.5 | 2030 | 89.0205 | 96.0869 | 103.5844 | 111.0281 | 118.4816
BelmontWind2035RCP4.5 | Belmont | Wind | RCP4.5 | 2035 | 89.1321 | 96.2355 | 103.7799 | 111.2628 | 118.7568
BelmontWind2040RCP4.5 | Belmont | Wind | RCP4.5 | 2040 | 89.2437 | 96.3841 | 103.9754 | 111.4974 | 119.032
BelmontWind2045RCP4.5 | Belmont | Wind | RCP4.5 | 2045 | 89.3552 | 96.5327 | 104.1709 | 111.7321 | 119.3072
BelmontWind2050RCP4.5 | Belmont | Wind | RCP4.5 | 2050 | 89.5196 | 96.7553 | 104.4684 | 112.0933 | 119.7335
BelmontWind2055RCP4.5 | Belmont | Wind | RCP4.5 | 2055 | 89.5725 | 96.8293 | 104.5704 | 112.2199 | 119.8847
BelmontWind2060RCP4.5 | Belmont | Wind | RCP4.5 | 2060 | 89.6253 | 96.9033 | 104.6724 | 112.3465 | 120.0358
BelmontWind2065RCP4.5 | Belmont | Wind | RCP4.5 | 2065 | 89.6782 | 96.9773 | 104.7744 | 112.4731 | 120.187
BelmontWind2070RCP4.5 | Belmont | Wind | RCP4.5 | 2070 | 89.731 | 97.0513 | 104.8764 | 112.5997 | 120.3382
BelmontWind2075RCP4.5 | Belmont | Wind | RCP4.5 | 2075 | 89.8866 | 97.2536 | 105.1382 | 112.9108 | 120.7006
BelmontWind2080RCP4.5 | Belmont | Wind | RCP4.5 | 2080 | 90.0422 | 97.456 | 105.4 | 113.2218 | 121.063
BelmontWind2085RCP4.5 | Belmont | Wind | RCP4.5 | 2085 | 90.1978 | 97.6584 | 105.6618 | 113.5329 | 121.4254
BelmontWind2090RCP4.5 | Belmont | Wind | RCP4.5 | 2090 | 90.3534 | 97.8607 | 105.9236 | 113.8439 | 121.7878
BelmontWind2095RCP4.5 | Belmont | Wind | RCP4.5 | 2095 | 90.509 | 98.0631 | 106.1854 | 114.155 | 122.1502
BelmontWind2100RCP4.5 | Belmont | Wind | RCP4.5 | 2100 | 90.6646 | 98.2655 | 106.4472 | 114.466 | 122.5126
BelmontWind2023RCP6.0 | Belmont | Wind | RCP6.0 | 2023 | 88.7974 | 95.7896 | 103.1934 | 110.5588 | 117.9312
BelmontWind2025RCP6.0 | Belmont | Wind | RCP6.0 | 2025 | 88.909 | 95.9382 | 103.3889 | 110.7935 | 118.2064
BelmontWind2030RCP6.0 | Belmont | Wind | RCP6.0 | 2030 | 89.0205 | 96.0869 | 103.5844 | 111.0281 | 118.4816
BelmontWind2035RCP6.0 | Belmont | Wind | RCP6.0 | 2035 | 89.1321 | 96.2355 | 103.7799 | 111.2628 | 118.7568
BelmontWind2040RCP6.0 | Belmont | Wind | RCP6.0 | 2040 | 89.2437 | 96.3841 | 103.9754 | 111.4974 | 119.032
BelmontWind2045RCP6.0 | Belmont | Wind | RCP6.0 | 2045 | 89.3552 | 96.5327 | 104.1709 | 111.7321 | 119.3072
BelmontWind2050RCP6.0 | Belmont | Wind | RCP6.0 | 2050 | 89.5196 | 96.7553 | 104.4684 | 112.0933 | 119.7335
BelmontWind2055RCP6.0 | Belmont | Wind | RCP6.0 | 2055 | 89.5725 | 96.8293 | 104.5704 | 112.2199 | 119.8847
BelmontWind2060RCP6.0 | Belmont | Wind | RCP6.0 | 2060 | 89.6253 | 96.9033 | 104.6724 | 112.3465 | 120.0358
BelmontWind2065RCP6.0 | Belmont | Wind | RCP6.0 | 2065 | 89.6782 | 96.9773 | 104.7744 | 112.4731 | 120.187
BelmontWind2070RCP6.0 | Belmont | Wind | RCP6.0 | 2070 | 89.731 | 97.0513 | 104.8764 | 112.5997 | 120.3382
BelmontWind2075RCP6.0 | Belmont | Wind | RCP6.0 | 2075 | 89.9644 | 97.3548 | 105.2691 | 113.0663 | 120.8818
BelmontWind2080RCP6.0 | Belmont | Wind | RCP6.0 | 2080 | 90.1978 | 97.6584 | 105.6618 | 113.5329 | 121.4254
BelmontWind2085RCP6.0 | Belmont | Wind | RCP6.0 | 2085 | 90.4312 | 97.9619 | 106.0545 | 113.9995 | 121.969
BelmontWind2090RCP6.0 | Belmont | Wind | RCP6.0 | 2090 | 91.0492 | 98.7556 | 107.0626 | 115.19 | 123.3498
BelmontWind2095RCP6.0 | Belmont | Wind | RCP6.0 | 2095 | 91.4338 | 99.2457 | 107.678 | 115.914 | 124.187
BelmontWind2100RCP6.0 | Belmont | Wind | RCP6.0 | 2100 | 91.8184 | 99.7358 | 108.2934 | 116.6379 | 125.0243
BelmontWind2023RCP8.5 | Belmont | Wind | RCP8.5 | 2023 | 88.7974 | 95.7896 | 103.1934 | 110.5588 | 117.9312
BelmontWind2025RCP8.5 | Belmont | Wind | RCP8.5 | 2025 | 89.0205 | 96.0869 | 103.5844 | 111.0281 | 118.4816
BelmontWind2030RCP8.5 | Belmont | Wind | RCP8.5 | 2030 | 89.2437 | 96.3841 | 103.9754 | 111.4974 | 119.032
BelmontWind2035RCP8.5 | Belmont | Wind | RCP8.5 | 2035 | 89.4668 | 96.6813 | 104.3664 | 111.9667 | 119.5824
BelmontWind2040RCP8.5 | Belmont | Wind | RCP8.5 | 2040 | 89.5549 | 96.8046 | 104.5364 | 112.1777 | 119.8343
BelmontWind2045RCP8.5 | Belmont | Wind | RCP8.5 | 2045 | 89.6429 | 96.9279 | 104.7064 | 112.3887 | 120.0862
BelmontWind2050RCP8.5 | Belmont | Wind | RCP8.5 | 2050 | 90.0422 | 97.456 | 105.4 | 113.2218 | 121.063
BelmontWind2055RCP8.5 | Belmont | Wind | RCP8.5 | 2055 | 90.3534 | 97.8607 | 105.9236 | 113.8439 | 121.7878
BelmontWind2060RCP8.5 | Belmont | Wind | RCP8.5 | 2060 | 91.0492 | 98.7556 | 107.0626 | 115.19 | 123.3498
BelmontWind2065RCP8.5 | Belmont | Wind | RCP8.5 | 2065 | 91.4338 | 99.2457 | 107.678 | 115.914 | 124.187
BelmontWind2070RCP8.5 | Belmont | Wind | RCP8.5 | 2070 | 92.0562 | 100.033 | 108.6708 | 117.0854 | 125.5398
BelmontWind2075RCP8.5 | Belmont | Wind | RCP8.5 | 2075 | 92.294 | 100.3303 | 109.0482 | 117.5329 | 126.0553
BelmontWind2080RCP8.5 | Belmont | Wind | RCP8.5 | 2080 | 92.5318 | 100.6275 | 109.4256 | 117.9803 | 126.5708
BelmontWind2085RCP8.5 | Belmont | Wind | RCP8.5 | 2085 | 92.937 | 101.1634 | 110.1294 | 118.8207 | 127.5592
BelmontWind2090RCP8.5 | Belmont | Wind | RCP8.5 | 2090 | 93.3421 | 101.6994 | 110.8332 | 119.6611 | 128.5475
BelmontWind2095RCP8.5 | Belmont | Wind | RCP8.5 | 2095 | 93.3421 | 101.6994 | 110.8332 | 119.6611 | 128.5475
BelmontWind2100RCP8.5 | Belmont | Wind | RCP8.5 | 2100 | 93.3421 | 101.6994 | 110.8332 | 119.6611 | 128.5475
BowmanvilleIce Accretion2023RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
BowmanvilleIce Accretion2025RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
BowmanvilleIce Accretion2030RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
BowmanvilleIce Accretion2035RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
BowmanvilleIce Accretion2040RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
BowmanvilleIce Accretion2045RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
BowmanvilleIce Accretion2050RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
BowmanvilleIce Accretion2055RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
BowmanvilleIce Accretion2060RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
BowmanvilleIce Accretion2065RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
BowmanvilleIce Accretion2070RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
BowmanvilleIce Accretion2075RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
BowmanvilleIce Accretion2080RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
BowmanvilleIce Accretion2085RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
BowmanvilleIce Accretion2090RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
BowmanvilleIce Accretion2095RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
BowmanvilleIce Accretion2100RCP4.5 | Bowmanville | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
BowmanvilleIce Accretion2023RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
BowmanvilleIce Accretion2025RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
BowmanvilleIce Accretion2030RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
BowmanvilleIce Accretion2035RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
BowmanvilleIce Accretion2040RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
BowmanvilleIce Accretion2045RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
BowmanvilleIce Accretion2050RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
BowmanvilleIce Accretion2055RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
BowmanvilleIce Accretion2060RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
BowmanvilleIce Accretion2065RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
BowmanvilleIce Accretion2070RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
BowmanvilleIce Accretion2075RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
BowmanvilleIce Accretion2080RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
BowmanvilleIce Accretion2085RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
BowmanvilleIce Accretion2090RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
BowmanvilleIce Accretion2095RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
BowmanvilleIce Accretion2100RCP6.0 | Bowmanville | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
BowmanvilleIce Accretion2023RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
BowmanvilleIce Accretion2025RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
BowmanvilleIce Accretion2030RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
BowmanvilleIce Accretion2035RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
BowmanvilleIce Accretion2040RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
BowmanvilleIce Accretion2045RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
BowmanvilleIce Accretion2050RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
BowmanvilleIce Accretion2055RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
BowmanvilleIce Accretion2060RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
BowmanvilleIce Accretion2065RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
BowmanvilleIce Accretion2070RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
BowmanvilleIce Accretion2075RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
BowmanvilleIce Accretion2080RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
BowmanvilleIce Accretion2085RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
BowmanvilleIce Accretion2090RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
BowmanvilleIce Accretion2095RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
BowmanvilleIce Accretion2100RCP8.5 | Bowmanville | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
BowmanvilleWind2023RCP4.5 | Bowmanville | Wind | RCP4.5 | 2023 | 84.8244 | 91.3223 | 98.1568 | 104.9963 | 111.8317
BowmanvilleWind2025RCP4.5 | Bowmanville | Wind | RCP4.5 | 2025 | 84.8399 | 91.3557 | 98.2107 | 105.068 | 111.9211
BowmanvilleWind2030RCP4.5 | Bowmanville | Wind | RCP4.5 | 2030 | 84.8554 | 91.3891 | 98.2646 | 105.1396 | 112.0105
BowmanvilleWind2035RCP4.5 | Bowmanville | Wind | RCP4.5 | 2035 | 84.8709 | 91.4225 | 98.3185 | 105.2113 | 112.0998
BowmanvilleWind2040RCP4.5 | Bowmanville | Wind | RCP4.5 | 2040 | 84.8864 | 91.456 | 98.3724 | 105.2829 | 112.1892
BowmanvilleWind2045RCP4.5 | Bowmanville | Wind | RCP4.5 | 2045 | 84.9019 | 91.4894 | 98.4263 | 105.3546 | 112.2786
BowmanvilleWind2050RCP4.5 | Bowmanville | Wind | RCP4.5 | 2050 | 85.0004 | 91.6267 | 98.6115 | 105.5793 | 112.5467
BowmanvilleWind2055RCP4.5 | Bowmanville | Wind | RCP4.5 | 2055 | 85.0833 | 91.7306 | 98.7428 | 105.7324 | 112.7255
BowmanvilleWind2060RCP4.5 | Bowmanville | Wind | RCP4.5 | 2060 | 85.1662 | 91.8345 | 98.8742 | 105.8855 | 112.9042
BowmanvilleWind2065RCP4.5 | Bowmanville | Wind | RCP4.5 | 2065 | 85.2492 | 91.9384 | 99.0055 | 106.0386 | 113.083
BowmanvilleWind2070RCP4.5 | Bowmanville | Wind | RCP4.5 | 2070 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2617
BowmanvilleWind2075RCP4.5 | Bowmanville | Wind | RCP4.5 | 2075 | 85.476 | 92.2276 | 99.3736 | 106.4731 | 113.5876
BowmanvilleWind2080RCP4.5 | Bowmanville | Wind | RCP4.5 | 2080 | 85.6198 | 92.4129 | 99.6105 | 106.7545 | 113.9134
BowmanvilleWind2085RCP4.5 | Bowmanville | Wind | RCP4.5 | 2085 | 85.7637 | 92.5982 | 99.8473 | 107.0358 | 114.2393
BowmanvilleWind2090RCP4.5 | Bowmanville | Wind | RCP4.5 | 2090 | 85.9075 | 92.7836 | 100.0841 | 107.3172 | 114.5651
BowmanvilleWind2095RCP4.5 | Bowmanville | Wind | RCP4.5 | 2095 | 86.0514 | 92.9689 | 100.321 | 107.5986 | 114.891
BowmanvilleWind2100RCP4.5 | Bowmanville | Wind | RCP4.5 | 2100 | 86.1952 | 93.1542 | 100.5578 | 107.88 | 115.2168
BowmanvilleWind2023RCP6.0 | Bowmanville | Wind | RCP6.0 | 2023 | 84.8244 | 91.3223 | 98.1568 | 104.9963 | 111.8317
BowmanvilleWind2025RCP6.0 | Bowmanville | Wind | RCP6.0 | 2025 | 84.8399 | 91.3557 | 98.2107 | 105.068 | 111.9211
BowmanvilleWind2030RCP6.0 | Bowmanville | Wind | RCP6.0 | 2030 | 84.8554 | 91.3891 | 98.2646 | 105.1396 | 112.0105
BowmanvilleWind2035RCP6.0 | Bowmanville | Wind | RCP6.0 | 2035 | 84.8709 | 91.4225 | 98.3185 | 105.2113 | 112.0998
BowmanvilleWind2040RCP6.0 | Bowmanville | Wind | RCP6.0 | 2040 | 84.8864 | 91.456 | 98.3724 | 105.2829 | 112.1892
BowmanvilleWind2045RCP6.0 | Bowmanville | Wind | RCP6.0 | 2045 | 84.9019 | 91.4894 | 98.4263 | 105.3546 | 112.2786
BowmanvilleWind2050RCP6.0 | Bowmanville | Wind | RCP6.0 | 2050 | 85.0004 | 91.6267 | 98.6115 | 105.5793 | 112.5467
BowmanvilleWind2055RCP6.0 | Bowmanville | Wind | RCP6.0 | 2055 | 85.0833 | 91.7306 | 98.7428 | 105.7324 | 112.7255
BowmanvilleWind2060RCP6.0 | Bowmanville | Wind | RCP6.0 | 2060 | 85.1662 | 91.8345 | 98.8742 | 105.8855 | 112.9042
BowmanvilleWind2065RCP6.0 | Bowmanville | Wind | RCP6.0 | 2065 | 85.2492 | 91.9384 | 99.0055 | 106.0386 | 113.083
BowmanvilleWind2070RCP6.0 | Bowmanville | Wind | RCP6.0 | 2070 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2617
BowmanvilleWind2075RCP6.0 | Bowmanville | Wind | RCP6.0 | 2075 | 85.5479 | 92.3203 | 99.4921 | 106.6138 | 113.7505
BowmanvilleWind2080RCP6.0 | Bowmanville | Wind | RCP6.0 | 2080 | 85.7637 | 92.5982 | 99.8473 | 107.0358 | 114.2393
BowmanvilleWind2085RCP6.0 | Bowmanville | Wind | RCP6.0 | 2085 | 85.9794 | 92.8762 | 100.2026 | 107.4579 | 114.7281
BowmanvilleWind2090RCP6.0 | Bowmanville | Wind | RCP6.0 | 2090 | 86.6409 | 93.701 | 101.234 | 108.6664 | 116.118
BowmanvilleWind2095RCP6.0 | Bowmanville | Wind | RCP6.0 | 2095 | 87.0866 | 94.2479 | 101.9102 | 109.4529 | 117.0193
BowmanvilleWind2100RCP6.0 | Bowmanville | Wind | RCP6.0 | 2100 | 87.5322 | 94.7947 | 102.5864 | 110.2393 | 117.9205
BowmanvilleWind2023RCP8.5 | Bowmanville | Wind | RCP8.5 | 2023 | 84.8244 | 91.3223 | 98.1568 | 104.9963 | 111.8317
BowmanvilleWind2025RCP8.5 | Bowmanville | Wind | RCP8.5 | 2025 | 84.8554 | 91.3891 | 98.2646 | 105.1396 | 112.0105
BowmanvilleWind2030RCP8.5 | Bowmanville | Wind | RCP8.5 | 2030 | 84.8864 | 91.456 | 98.3724 | 105.2829 | 112.1892
BowmanvilleWind2035RCP8.5 | Bowmanville | Wind | RCP8.5 | 2035 | 84.9175 | 91.5228 | 98.4802 | 105.4262 | 112.368
BowmanvilleWind2040RCP8.5 | Bowmanville | Wind | RCP8.5 | 2040 | 85.0557 | 91.696 | 98.6991 | 105.6814 | 112.6659
BowmanvilleWind2045RCP8.5 | Bowmanville | Wind | RCP8.5 | 2045 | 85.1939 | 91.8691 | 98.9179 | 105.9366 | 112.9638
BowmanvilleWind2050RCP8.5 | Bowmanville | Wind | RCP8.5 | 2050 | 85.6198 | 92.4129 | 99.6105 | 106.7545 | 113.9134
BowmanvilleWind2055RCP8.5 | Bowmanville | Wind | RCP8.5 | 2055 | 85.9075 | 92.7836 | 100.0841 | 107.3172 | 114.5651
BowmanvilleWind2060RCP8.5 | Bowmanville | Wind | RCP8.5 | 2060 | 86.6409 | 93.701 | 101.234 | 108.6664 | 116.118
BowmanvilleWind2065RCP8.5 | Bowmanville | Wind | RCP8.5 | 2065 | 87.0866 | 94.2479 | 101.9102 | 109.4529 | 117.0193
BowmanvilleWind2070RCP8.5 | Bowmanville | Wind | RCP8.5 | 2070 | 87.6648 | 94.974 | 102.8249 | 110.5329 | 118.2631
BowmanvilleWind2075RCP8.5 | Bowmanville | Wind | RCP8.5 | 2075 | 87.7974 | 95.1532 | 103.0633 | 110.8265 | 118.6057
BowmanvilleWind2080RCP8.5 | Bowmanville | Wind | RCP8.5 | 2080 | 87.93 | 95.3324 | 103.3018 | 111.1201 | 118.9483
BowmanvilleWind2085RCP8.5 | Bowmanville | Wind | RCP8.5 | 2085 | 88.2135 | 95.7335 | 103.8506 | 111.7912 | 119.7471
BowmanvilleWind2090RCP8.5 | Bowmanville | Wind | RCP8.5 | 2090 | 88.4969 | 96.1345 | 104.3994 | 112.4624 | 120.5459
BowmanvilleWind2095RCP8.5 | Bowmanville | Wind | RCP8.5 | 2095 | 88.4969 | 96.1345 | 104.3994 | 112.4624 | 120.5459
BowmanvilleWind2100RCP8.5 | Bowmanville | Wind | RCP8.5 | 2100 | 88.4969 | 96.1345 | 104.3994 | 112.4624 | 120.5459
BracebridgeIce Accretion2023RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2023 | 14.5689 | 17.3951 | 20.979 | 23.7063 | 26.4335
BracebridgeIce Accretion2025RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2025 | 14.5665 | 17.398 | 20.9895 | 23.7221 | 26.4556
BracebridgeIce Accretion2030RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2030 | 14.5641 | 17.401 | 21 | 23.7379 | 26.4776
BracebridgeIce Accretion2035RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2035 | 14.5616 | 17.4039 | 21.0105 | 23.7537 | 26.4997
BracebridgeIce Accretion2040RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2040 | 14.5592 | 17.4068 | 21.021 | 23.7695 | 26.5217
BracebridgeIce Accretion2045RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2045 | 14.5568 | 17.4097 | 21.0315 | 23.7854 | 26.5438
BracebridgeIce Accretion2050RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2050 | 14.5455 | 17.4195 | 21.063 | 23.8392 | 26.6188
BracebridgeIce Accretion2055RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2055 | 14.5368 | 17.4265 | 21.084 | 23.8771 | 26.6717
BracebridgeIce Accretion2060RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2060 | 14.528 | 17.4335 | 21.105 | 23.9151 | 26.7246
BracebridgeIce Accretion2065RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2065 | 14.5192 | 17.4405 | 21.126 | 23.9531 | 26.7775
BracebridgeIce Accretion2070RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2070 | 14.5105 | 17.4474 | 21.147 | 23.991 | 26.8304
BracebridgeIce Accretion2075RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2075 | 14.5421 | 17.4968 | 21.224 | 24.082 | 26.9407
BracebridgeIce Accretion2080RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2080 | 14.5738 | 17.5462 | 21.301 | 24.173 | 27.0509
BracebridgeIce Accretion2085RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2085 | 14.6055 | 17.5956 | 21.378 | 24.2639 | 27.1612
BracebridgeIce Accretion2090RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2090 | 14.6371 | 17.645 | 21.455 | 24.3549 | 27.2714
BracebridgeIce Accretion2095RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2095 | 14.6688 | 17.6944 | 21.532 | 24.4459 | 27.3817
BracebridgeIce Accretion2100RCP4.5 | Bracebridge | Ice Accretion | RCP4.5 | 2100 | 14.7004 | 17.7437 | 21.609 | 24.5368 | 27.4919
BracebridgeIce Accretion2023RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2023 | 14.5689 | 17.3951 | 20.979 | 23.7063 | 26.4335
BracebridgeIce Accretion2025RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2025 | 14.5665 | 17.398 | 20.9895 | 23.7221 | 26.4556
BracebridgeIce Accretion2030RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2030 | 14.5641 | 17.401 | 21 | 23.7379 | 26.4776
BracebridgeIce Accretion2035RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2035 | 14.5616 | 17.4039 | 21.0105 | 23.7537 | 26.4997
BracebridgeIce Accretion2040RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2040 | 14.5592 | 17.4068 | 21.021 | 23.7695 | 26.5217
BracebridgeIce Accretion2045RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2045 | 14.5568 | 17.4097 | 21.0315 | 23.7854 | 26.5438
BracebridgeIce Accretion2050RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2050 | 14.5455 | 17.4195 | 21.063 | 23.8392 | 26.6188
BracebridgeIce Accretion2055RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2055 | 14.5368 | 17.4265 | 21.084 | 23.8771 | 26.6717
BracebridgeIce Accretion2060RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2060 | 14.528 | 17.4335 | 21.105 | 23.9151 | 26.7246
BracebridgeIce Accretion2065RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2065 | 14.5192 | 17.4405 | 21.126 | 23.9531 | 26.7775
BracebridgeIce Accretion2070RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2070 | 14.5105 | 17.4474 | 21.147 | 23.991 | 26.8304
BracebridgeIce Accretion2075RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2075 | 14.558 | 17.5215 | 21.2625 | 24.1275 | 26.9958
BracebridgeIce Accretion2080RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2080 | 14.6055 | 17.5956 | 21.378 | 24.2639 | 27.1612
BracebridgeIce Accretion2085RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2085 | 14.653 | 17.6697 | 21.4935 | 24.4004 | 27.3266
BracebridgeIce Accretion2090RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2090 | 14.7345 | 17.8251 | 21.749 | 24.7187 | 27.7124
BracebridgeIce Accretion2095RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2095 | 14.7686 | 17.9064 | 21.889 | 24.9007 | 27.9329
BracebridgeIce Accretion2100RCP6.0 | Bracebridge | Ice Accretion | RCP6.0 | 2100 | 14.8027 | 17.9878 | 22.029 | 25.0826 | 28.1534
BracebridgeIce Accretion2023RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2023 | 14.5689 | 17.3951 | 20.979 | 23.7063 | 26.4335
BracebridgeIce Accretion2025RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2025 | 14.5641 | 17.401 | 21 | 23.7379 | 26.4776
BracebridgeIce Accretion2030RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2030 | 14.5592 | 17.4068 | 21.021 | 23.7695 | 26.5217
BracebridgeIce Accretion2035RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2035 | 14.5543 | 17.4126 | 21.042 | 23.8012 | 26.5658
BracebridgeIce Accretion2040RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2040 | 14.5397 | 17.4242 | 21.077 | 23.8645 | 26.654
BracebridgeIce Accretion2045RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2045 | 14.5251 | 17.4358 | 21.112 | 23.9277 | 26.7422
BracebridgeIce Accretion2050RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2050 | 14.5738 | 17.5462 | 21.301 | 24.173 | 27.0509
BracebridgeIce Accretion2055RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2055 | 14.6371 | 17.645 | 21.455 | 24.3549 | 27.2714
BracebridgeIce Accretion2060RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2060 | 14.7345 | 17.8251 | 21.749 | 24.7187 | 27.7124
BracebridgeIce Accretion2065RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2065 | 14.7686 | 17.9064 | 21.889 | 24.9007 | 27.9329
BracebridgeIce Accretion2070RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2070 | 14.603 | 17.767 | 21.777 | 24.8216 | 27.8712
BracebridgeIce Accretion2075RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2075 | 14.4033 | 17.5462 | 21.525 | 24.5605 | 27.589
BracebridgeIce Accretion2080RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2080 | 14.2036 | 17.3254 | 21.273 | 24.2995 | 27.3067
BracebridgeIce Accretion2085RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2085 | 13.6995 | 16.7589 | 20.622 | 23.5758 | 26.5129
BracebridgeIce Accretion2090RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2090 | 13.1953 | 16.1925 | 19.971 | 22.852 | 25.7191
BracebridgeIce Accretion2095RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2095 | 13.1953 | 16.1925 | 19.971 | 22.852 | 25.7191
BracebridgeIce Accretion2100RCP8.5 | Bracebridge | Ice Accretion | RCP8.5 | 2100 | 13.1953 | 16.1925 | 19.971 | 22.852 | 25.7191
BracebridgeWind2023RCP4.5 | Bracebridge | Wind | RCP4.5 | 2023 | 76.0852 | 81.9055 | 88.0264 | 94.1506 | 100.2799
BracebridgeWind2025RCP4.5 | Bracebridge | Wind | RCP4.5 | 2025 | 76.2055 | 82.0596 | 88.22 | 94.3781 | 100.5407
BracebridgeWind2030RCP4.5 | Bracebridge | Wind | RCP4.5 | 2030 | 76.3259 | 82.2137 | 88.4136 | 94.6057 | 100.8015
BracebridgeWind2035RCP4.5 | Bracebridge | Wind | RCP4.5 | 2035 | 76.4462 | 82.3679 | 88.6072 | 94.8332 | 101.0624
BracebridgeWind2040RCP4.5 | Bracebridge | Wind | RCP4.5 | 2040 | 76.5665 | 82.522 | 88.8008 | 95.0608 | 101.3232
BracebridgeWind2045RCP4.5 | Bracebridge | Wind | RCP4.5 | 2045 | 76.6868 | 82.6761 | 88.9944 | 95.2884 | 101.584
BracebridgeWind2050RCP4.5 | Bracebridge | Wind | RCP4.5 | 2050 | 76.8101 | 82.8123 | 89.144 | 95.45 | 101.7586
BracebridgeWind2055RCP4.5 | Bracebridge | Wind | RCP4.5 | 2055 | 76.8132 | 82.7943 | 89.1 | 95.3841 | 101.6723
BracebridgeWind2060RCP4.5 | Bracebridge | Wind | RCP4.5 | 2060 | 76.8162 | 82.7762 | 89.056 | 95.3182 | 101.586
BracebridgeWind2065RCP4.5 | Bracebridge | Wind | RCP4.5 | 2065 | 76.8193 | 82.7582 | 89.012 | 95.2523 | 101.4998
BracebridgeWind2070RCP4.5 | Bracebridge | Wind | RCP4.5 | 2070 | 76.8223 | 82.7402 | 88.968 | 95.1863 | 101.4135
BracebridgeWind2075RCP4.5 | Bracebridge | Wind | RCP4.5 | 2075 | 76.8489 | 82.7689 | 88.9988 | 95.2209 | 101.4503
BracebridgeWind2080RCP4.5 | Bracebridge | Wind | RCP4.5 | 2080 | 76.8755 | 82.7975 | 89.0296 | 95.2554 | 101.4871
BracebridgeWind2085RCP4.5 | Bracebridge | Wind | RCP4.5 | 2085 | 76.9021 | 82.8262 | 89.0604 | 95.2899 | 101.5238
BracebridgeWind2090RCP4.5 | Bracebridge | Wind | RCP4.5 | 2090 | 76.9287 | 82.8548 | 89.0912 | 95.3244 | 101.5606
BracebridgeWind2095RCP4.5 | Bracebridge | Wind | RCP4.5 | 2095 | 76.9553 | 82.8835 | 89.122 | 95.359 | 101.5974
BracebridgeWind2100RCP4.5 | Bracebridge | Wind | RCP4.5 | 2100 | 76.9819 | 82.9121 | 89.1528 | 95.3935 | 101.6342
BracebridgeWind2023RCP6.0 | Bracebridge | Wind | RCP6.0 | 2023 | 76.0852 | 81.9055 | 88.0264 | 94.1506 | 100.2799
BracebridgeWind2025RCP6.0 | Bracebridge | Wind | RCP6.0 | 2025 | 76.2055 | 82.0596 | 88.22 | 94.3781 | 100.5407
BracebridgeWind2030RCP6.0 | Bracebridge | Wind | RCP6.0 | 2030 | 76.3259 | 82.2137 | 88.4136 | 94.6057 | 100.8015
BracebridgeWind2035RCP6.0 | Bracebridge | Wind | RCP6.0 | 2035 | 76.4462 | 82.3679 | 88.6072 | 94.8332 | 101.0624
BracebridgeWind2040RCP6.0 | Bracebridge | Wind | RCP6.0 | 2040 | 76.5665 | 82.522 | 88.8008 | 95.0608 | 101.3232
BracebridgeWind2045RCP6.0 | Bracebridge | Wind | RCP6.0 | 2045 | 76.6868 | 82.6761 | 88.9944 | 95.2884 | 101.584
BracebridgeWind2050RCP6.0 | Bracebridge | Wind | RCP6.0 | 2050 | 76.8101 | 82.8123 | 89.144 | 95.45 | 101.7586
BracebridgeWind2055RCP6.0 | Bracebridge | Wind | RCP6.0 | 2055 | 76.8132 | 82.7943 | 89.1 | 95.3841 | 101.6723
BracebridgeWind2060RCP6.0 | Bracebridge | Wind | RCP6.0 | 2060 | 76.8162 | 82.7762 | 89.056 | 95.3182 | 101.586
BracebridgeWind2065RCP6.0 | Bracebridge | Wind | RCP6.0 | 2065 | 76.8193 | 82.7582 | 89.012 | 95.2523 | 101.4998
BracebridgeWind2070RCP6.0 | Bracebridge | Wind | RCP6.0 | 2070 | 76.8223 | 82.7402 | 88.968 | 95.1863 | 101.4135
BracebridgeWind2075RCP6.0 | Bracebridge | Wind | RCP6.0 | 2075 | 76.8622 | 82.7832 | 89.0142 | 95.2381 | 101.4687
BracebridgeWind2080RCP6.0 | Bracebridge | Wind | RCP6.0 | 2080 | 76.9021 | 82.8262 | 89.0604 | 95.2899 | 101.5238
BracebridgeWind2085RCP6.0 | Bracebridge | Wind | RCP6.0 | 2085 | 76.942 | 82.8691 | 89.1066 | 95.3417 | 101.579
BracebridgeWind2090RCP6.0 | Bracebridge | Wind | RCP6.0 | 2090 | 76.9034 | 82.8003 | 89.0003 | 95.2083 | 101.4168
BracebridgeWind2095RCP6.0 | Bracebridge | Wind | RCP6.0 | 2095 | 76.8248 | 82.6884 | 88.8477 | 95.0231 | 101.1995
BracebridgeWind2100RCP6.0 | Bracebridge | Wind | RCP6.0 | 2100 | 76.7463 | 82.5766 | 88.6952 | 94.838 | 100.9821
BracebridgeWind2023RCP8.5 | Bracebridge | Wind | RCP8.5 | 2023 | 76.0852 | 81.9055 | 88.0264 | 94.1506 | 100.2799
BracebridgeWind2025RCP8.5 | Bracebridge | Wind | RCP8.5 | 2025 | 76.3259 | 82.2137 | 88.4136 | 94.6057 | 100.8015
BracebridgeWind2030RCP8.5 | Bracebridge | Wind | RCP8.5 | 2030 | 76.5665 | 82.522 | 88.8008 | 95.0608 | 101.3232
BracebridgeWind2035RCP8.5 | Bracebridge | Wind | RCP8.5 | 2035 | 76.8071 | 82.8303 | 89.188 | 95.5159 | 101.8449
BracebridgeWind2040RCP8.5 | Bracebridge | Wind | RCP8.5 | 2040 | 76.8122 | 82.8003 | 89.1147 | 95.4061 | 101.7011
BracebridgeWind2045RCP8.5 | Bracebridge | Wind | RCP8.5 | 2045 | 76.8172 | 82.7702 | 89.0413 | 95.2962 | 101.5573
BracebridgeWind2050RCP8.5 | Bracebridge | Wind | RCP8.5 | 2050 | 76.8755 | 82.7975 | 89.0296 | 95.2554 | 101.4871
BracebridgeWind2055RCP8.5 | Bracebridge | Wind | RCP8.5 | 2055 | 76.9287 | 82.8548 | 89.0912 | 95.3244 | 101.5606
BracebridgeWind2060RCP8.5 | Bracebridge | Wind | RCP8.5 | 2060 | 76.9034 | 82.8003 | 89.0003 | 95.2083 | 101.4168
BracebridgeWind2065RCP8.5 | Bracebridge | Wind | RCP8.5 | 2065 | 76.8248 | 82.6884 | 88.8477 | 95.0231 | 101.1995
BracebridgeWind2070RCP8.5 | Bracebridge | Wind | RCP8.5 | 2070 | 76.8476 | 82.6966 | 88.8389 | 94.998 | 101.1627
BracebridgeWind2075RCP8.5 | Bracebridge | Wind | RCP8.5 | 2075 | 76.9489 | 82.8166 | 88.9827 | 95.1581 | 101.3433
BracebridgeWind2080RCP8.5 | Bracebridge | Wind | RCP8.5 | 2080 | 77.0503 | 82.9367 | 89.1264 | 95.3182 | 101.5238
BracebridgeWind2085RCP8.5 | Bracebridge | Wind | RCP8.5 | 2085 | 77.3732 | 83.3377 | 89.6148 | 95.8878 | 102.1709
BracebridgeWind2090RCP8.5 | Bracebridge | Wind | RCP8.5 | 2090 | 77.6961 | 83.7387 | 90.1032 | 96.4575 | 102.818
BracebridgeWind2095RCP8.5 | Bracebridge | Wind | RCP8.5 | 2095 | 77.6961 | 83.7387 | 90.1032 | 96.4575 | 102.818
BracebridgeWind2100RCP8.5 | Bracebridge | Wind | RCP8.5 | 2100 | 77.6961 | 83.7387 | 90.1032 | 96.4575 | 102.818
BradfordIce Accretion2023RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2023 | 16.6836 | 20.0196 | 24.24 | 27.4726 | 30.6936
BradfordIce Accretion2025RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2025 | 16.7254 | 20.086 | 24.34 | 27.5946 | 30.8398
BradfordIce Accretion2030RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2030 | 16.7671 | 20.1524 | 24.44 | 27.7166 | 30.9859
BradfordIce Accretion2035RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2035 | 16.8089 | 20.2188 | 24.54 | 27.8387 | 31.1321
BradfordIce Accretion2040RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2040 | 16.8506 | 20.2852 | 24.64 | 27.9607 | 31.2782
BradfordIce Accretion2045RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2045 | 16.8924 | 20.3516 | 24.74 | 28.0828 | 31.4244
BradfordIce Accretion2050RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2050 | 16.8205 | 20.3025 | 24.7152 | 28.0746 | 31.4315
BradfordIce Accretion2055RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2055 | 16.707 | 20.1869 | 24.5904 | 27.9444 | 31.2924
BradfordIce Accretion2060RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2060 | 16.5934 | 20.0714 | 24.4656 | 27.8143 | 31.1532
BradfordIce Accretion2065RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2065 | 16.4799 | 19.9559 | 24.3408 | 27.6841 | 31.0141
BradfordIce Accretion2070RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2070 | 16.3663 | 19.8403 | 24.216 | 27.5539 | 30.875
BradfordIce Accretion2075RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2075 | 16.3301 | 19.8237 | 24.224 | 27.5765 | 30.9154
BradfordIce Accretion2080RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2080 | 16.2939 | 19.8071 | 24.232 | 27.5991 | 30.9557
BradfordIce Accretion2085RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2085 | 16.2577 | 19.7905 | 24.24 | 27.6217 | 30.996
BradfordIce Accretion2090RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2090 | 16.2216 | 19.7739 | 24.248 | 27.6443 | 31.0363
BradfordIce Accretion2095RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2095 | 16.1854 | 19.7573 | 24.256 | 27.6669 | 31.0766
BradfordIce Accretion2100RCP4.5 | Bradford | Ice Accretion | RCP4.5 | 2100 | 16.1492 | 19.7407 | 24.264 | 27.6895 | 31.117
BradfordIce Accretion2023RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2023 | 16.6836 | 20.0196 | 24.24 | 27.4726 | 30.6936
BradfordIce Accretion2025RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2025 | 16.7254 | 20.086 | 24.34 | 27.5946 | 30.8398
BradfordIce Accretion2030RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2030 | 16.7671 | 20.1524 | 24.44 | 27.7166 | 30.9859
BradfordIce Accretion2035RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2035 | 16.8089 | 20.2188 | 24.54 | 27.8387 | 31.1321
BradfordIce Accretion2040RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2040 | 16.8506 | 20.2852 | 24.64 | 27.9607 | 31.2782
BradfordIce Accretion2045RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2045 | 16.8924 | 20.3516 | 24.74 | 28.0828 | 31.4244
BradfordIce Accretion2050RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2050 | 16.8205 | 20.3025 | 24.7152 | 28.0746 | 31.4315
BradfordIce Accretion2055RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2055 | 16.707 | 20.1869 | 24.5904 | 27.9444 | 31.2924
BradfordIce Accretion2060RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2060 | 16.5934 | 20.0714 | 24.4656 | 27.8143 | 31.1532
BradfordIce Accretion2065RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2065 | 16.4799 | 19.9559 | 24.3408 | 27.6841 | 31.0141
BradfordIce Accretion2070RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2070 | 16.3663 | 19.8403 | 24.216 | 27.5539 | 30.875
BradfordIce Accretion2075RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2075 | 16.312 | 19.8154 | 24.228 | 27.5878 | 30.9355
BradfordIce Accretion2080RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2080 | 16.2577 | 19.7905 | 24.24 | 27.6217 | 30.996
BradfordIce Accretion2085RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2085 | 16.2035 | 19.7656 | 24.252 | 27.6556 | 31.0565
BradfordIce Accretion2090RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2090 | 15.8542 | 19.4286 | 23.928 | 27.346 | 30.7541
BradfordIce Accretion2095RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2095 | 15.5591 | 19.1166 | 23.592 | 27.0025 | 30.3912
BradfordIce Accretion2100RCP6.0 | Bradford | Ice Accretion | RCP6.0 | 2100 | 15.2641 | 18.8045 | 23.256 | 26.659 | 30.0283
BradfordIce Accretion2023RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2023 | 16.6836 | 20.0196 | 24.24 | 27.4726 | 30.6936
BradfordIce Accretion2025RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2025 | 16.7671 | 20.1524 | 24.44 | 27.7166 | 30.9859
BradfordIce Accretion2030RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2030 | 16.8506 | 20.2852 | 24.64 | 27.9607 | 31.2782
BradfordIce Accretion2035RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2035 | 16.9341 | 20.418 | 24.84 | 28.2048 | 31.5706
BradfordIce Accretion2040RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2040 | 16.7448 | 20.2254 | 24.632 | 27.9878 | 31.3387
BradfordIce Accretion2045RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2045 | 16.5556 | 20.0329 | 24.424 | 27.7709 | 31.1069
BradfordIce Accretion2050RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2050 | 16.2939 | 19.8071 | 24.232 | 27.5991 | 30.9557
BradfordIce Accretion2055RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2055 | 16.2216 | 19.7739 | 24.248 | 27.6443 | 31.0363
BradfordIce Accretion2060RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2060 | 15.8542 | 19.4286 | 23.928 | 27.346 | 30.7541
BradfordIce Accretion2065RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2065 | 15.5591 | 19.1166 | 23.592 | 27.0025 | 30.3912
BradfordIce Accretion2070RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2070 | 14.8911 | 18.4061 | 22.824 | 26.1889 | 29.5344
BradfordIce Accretion2075RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2075 | 14.5181 | 18.0077 | 22.392 | 25.7188 | 29.0405
BradfordIce Accretion2080RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2080 | 14.1452 | 17.6093 | 21.96 | 25.2487 | 28.5466
BradfordIce Accretion2085RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2085 | 13.4103 | 16.7428 | 20.928 | 24.0961 | 27.2614
BradfordIce Accretion2090RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2090 | 12.6755 | 15.8762 | 19.896 | 22.9435 | 25.9762
BradfordIce Accretion2095RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2095 | 12.6755 | 15.8762 | 19.896 | 22.9435 | 25.9762
BradfordIce Accretion2100RCP8.5 | Bradford | Ice Accretion | RCP8.5 | 2100 | 12.6755 | 15.8762 | 19.896 | 22.9435 | 25.9762
BradfordWind2023RCP4.5 | Bradford | Wind | RCP4.5 | 2023 | 76.2676 | 82.1428 | 88.3256 | 94.5084 | 100.6912
BradfordWind2025RCP4.5 | Bradford | Wind | RCP4.5 | 2025 | 76.2917 | 82.1769 | 88.3725 | 94.5665 | 100.7614
BradfordWind2030RCP4.5 | Bradford | Wind | RCP4.5 | 2030 | 76.3157 | 82.211 | 88.4195 | 94.6245 | 100.8316
BradfordWind2035RCP4.5 | Bradford | Wind | RCP4.5 | 2035 | 76.3398 | 82.2451 | 88.4664 | 94.6826 | 100.9019
BradfordWind2040RCP4.5 | Bradford | Wind | RCP4.5 | 2040 | 76.3639 | 82.2792 | 88.5133 | 94.7407 | 100.9721
BradfordWind2045RCP4.5 | Bradford | Wind | RCP4.5 | 2045 | 76.3879 | 82.3133 | 88.5603 | 94.7987 | 101.0423
BradfordWind2050RCP4.5 | Bradford | Wind | RCP4.5 | 2050 | 76.4621 | 82.3949 | 88.6512 | 94.8982 | 101.1506
BradfordWind2055RCP4.5 | Bradford | Wind | RCP4.5 | 2055 | 76.5123 | 82.4423 | 88.6952 | 94.9396 | 101.1888
BradfordWind2060RCP4.5 | Bradford | Wind | RCP4.5 | 2060 | 76.5624 | 82.4898 | 88.7392 | 94.9811 | 101.2269
BradfordWind2065RCP4.5 | Bradford | Wind | RCP4.5 | 2065 | 76.6126 | 82.5373 | 88.7832 | 95.0225 | 101.265
BradfordWind2070RCP4.5 | Bradford | Wind | RCP4.5 | 2070 | 76.6627 | 82.5847 | 88.8272 | 95.0639 | 101.3031
BradfordWind2075RCP4.5 | Bradford | Wind | RCP4.5 | 2075 | 76.7362 | 82.6857 | 88.9621 | 95.2271 | 101.4954
BradfordWind2080RCP4.5 | Bradford | Wind | RCP4.5 | 2080 | 76.8096 | 82.7866 | 89.0971 | 95.3904 | 101.6877
BradfordWind2085RCP4.5 | Bradford | Wind | RCP4.5 | 2085 | 76.8831 | 82.8876 | 89.232 | 95.5536 | 101.88
BradfordWind2090RCP4.5 | Bradford | Wind | RCP4.5 | 2090 | 76.9565 | 82.9885 | 89.3669 | 95.7168 | 102.0723
BradfordWind2095RCP4.5 | Bradford | Wind | RCP4.5 | 2095 | 77.03 | 83.0894 | 89.5019 | 95.88 | 102.2645
BradfordWind2100RCP4.5 | Bradford | Wind | RCP4.5 | 2100 | 77.1035 | 83.1904 | 89.6368 | 96.0432 | 102.4568
BradfordWind2023RCP6.0 | Bradford | Wind | RCP6.0 | 2023 | 76.2676 | 82.1428 | 88.3256 | 94.5084 | 100.6912
BradfordWind2025RCP6.0 | Bradford | Wind | RCP6.0 | 2025 | 76.2917 | 82.1769 | 88.3725 | 94.5665 | 100.7614
BradfordWind2030RCP6.0 | Bradford | Wind | RCP6.0 | 2030 | 76.3157 | 82.211 | 88.4195 | 94.6245 | 100.8316
BradfordWind2035RCP6.0 | Bradford | Wind | RCP6.0 | 2035 | 76.3398 | 82.2451 | 88.4664 | 94.6826 | 100.9019
BradfordWind2040RCP6.0 | Bradford | Wind | RCP6.0 | 2040 | 76.3639 | 82.2792 | 88.5133 | 94.7407 | 100.9721
BradfordWind2045RCP6.0 | Bradford | Wind | RCP6.0 | 2045 | 76.3879 | 82.3133 | 88.5603 | 94.7987 | 101.0423
BradfordWind2050RCP6.0 | Bradford | Wind | RCP6.0 | 2050 | 76.4621 | 82.3949 | 88.6512 | 94.8982 | 101.1506
BradfordWind2055RCP6.0 | Bradford | Wind | RCP6.0 | 2055 | 76.5123 | 82.4423 | 88.6952 | 94.9396 | 101.1888
BradfordWind2060RCP6.0 | Bradford | Wind | RCP6.0 | 2060 | 76.5624 | 82.4898 | 88.7392 | 94.9811 | 101.2269
BradfordWind2065RCP6.0 | Bradford | Wind | RCP6.0 | 2065 | 76.6126 | 82.5373 | 88.7832 | 95.0225 | 101.265
BradfordWind2070RCP6.0 | Bradford | Wind | RCP6.0 | 2070 | 76.6627 | 82.5847 | 88.8272 | 95.0639 | 101.3031
BradfordWind2075RCP6.0 | Bradford | Wind | RCP6.0 | 2075 | 76.7729 | 82.7361 | 89.0296 | 95.3088 | 101.5916
BradfordWind2080RCP6.0 | Bradford | Wind | RCP6.0 | 2080 | 76.8831 | 82.8876 | 89.232 | 95.5536 | 101.88
BradfordWind2085RCP6.0 | Bradford | Wind | RCP6.0 | 2085 | 76.9933 | 83.039 | 89.4344 | 95.7984 | 102.1684
BradfordWind2090RCP6.0 | Bradford | Wind | RCP6.0 | 2090 | 77.3593 | 83.5068 | 90.0269 | 96.4983 | 102.9785
BradfordWind2095RCP6.0 | Bradford | Wind | RCP6.0 | 2095 | 77.6151 | 83.8233 | 90.4171 | 96.9534 | 103.5001
BradfordWind2100RCP6.0 | Bradford | Wind | RCP6.0 | 2100 | 77.8709 | 84.1397 | 90.8072 | 97.4085 | 104.0218
BradfordWind2023RCP8.5 | Bradford | Wind | RCP8.5 | 2023 | 76.2676 | 82.1428 | 88.3256 | 94.5084 | 100.6912
BradfordWind2025RCP8.5 | Bradford | Wind | RCP8.5 | 2025 | 76.3157 | 82.211 | 88.4195 | 94.6245 | 100.8316
BradfordWind2030RCP8.5 | Bradford | Wind | RCP8.5 | 2030 | 76.3639 | 82.2792 | 88.5133 | 94.7407 | 100.9721
BradfordWind2035RCP8.5 | Bradford | Wind | RCP8.5 | 2035 | 76.412 | 82.3474 | 88.6072 | 94.8568 | 101.1125
BradfordWind2040RCP8.5 | Bradford | Wind | RCP8.5 | 2040 | 76.4956 | 82.4265 | 88.6805 | 94.9258 | 101.1761
BradfordWind2045RCP8.5 | Bradford | Wind | RCP8.5 | 2045 | 76.5791 | 82.5056 | 88.7539 | 94.9949 | 101.2396
BradfordWind2050RCP8.5 | Bradford | Wind | RCP8.5 | 2050 | 76.8096 | 82.7866 | 89.0971 | 95.3904 | 101.6877
BradfordWind2055RCP8.5 | Bradford | Wind | RCP8.5 | 2055 | 76.9565 | 82.9885 | 89.3669 | 95.7168 | 102.0723
BradfordWind2060RCP8.5 | Bradford | Wind | RCP8.5 | 2060 | 77.3593 | 83.5068 | 90.0269 | 96.4983 | 102.9785
BradfordWind2065RCP8.5 | Bradford | Wind | RCP8.5 | 2065 | 77.6151 | 83.8233 | 90.4171 | 96.9534 | 103.5001
BradfordWind2070RCP8.5 | Bradford | Wind | RCP8.5 | 2070 | 78.0659 | 84.4016 | 91.1533 | 97.826 | 104.51
BradfordWind2075RCP8.5 | Bradford | Wind | RCP8.5 | 2075 | 78.261 | 84.6635 | 91.4995 | 98.2434 | 104.9983
BradfordWind2080RCP8.5 | Bradford | Wind | RCP8.5 | 2080 | 78.456 | 84.9254 | 91.8456 | 98.6608 | 105.4865
BradfordWind2085RCP8.5 | Bradford | Wind | RCP8.5 | 2085 | 78.5548 | 85.0563 | 92.0216 | 98.868 | 105.7323
BradfordWind2090RCP8.5 | Bradford | Wind | RCP8.5 | 2090 | 78.6536 | 85.1873 | 92.1976 | 99.0752 | 105.978
BradfordWind2095RCP8.5 | Bradford | Wind | RCP8.5 | 2095 | 78.6536 | 85.1873 | 92.1976 | 99.0752 | 105.978
BradfordWind2100RCP8.5 | Bradford | Wind | RCP8.5 | 2100 | 78.6536 | 85.1873 | 92.1976 | 99.0752 | 105.978
BramptonIce Accretion2023RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
BramptonIce Accretion2025RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
BramptonIce Accretion2030RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
BramptonIce Accretion2035RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
BramptonIce Accretion2040RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
BramptonIce Accretion2045RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
BramptonIce Accretion2050RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
BramptonIce Accretion2055RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
BramptonIce Accretion2060RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
BramptonIce Accretion2065RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
BramptonIce Accretion2070RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
BramptonIce Accretion2075RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2075 | 15.5377 | 18.8894 | 23.1125 | 26.329 | 29.5313
BramptonIce Accretion2080RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2080 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
BramptonIce Accretion2085RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2085 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
BramptonIce Accretion2090RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2090 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
BramptonIce Accretion2095RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2095 | 15.3405 | 18.7511 | 23.0625 | 26.329 | 29.5942
BramptonIce Accretion2100RCP4.5 | Brampton | Ice Accretion | RCP4.5 | 2100 | 15.2912 | 18.7165 | 23.05 | 26.329 | 29.61
BramptonIce Accretion2023RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
BramptonIce Accretion2025RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
BramptonIce Accretion2030RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
BramptonIce Accretion2035RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
BramptonIce Accretion2040RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
BramptonIce Accretion2045RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
BramptonIce Accretion2050RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
BramptonIce Accretion2055RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
BramptonIce Accretion2060RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
BramptonIce Accretion2065RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
BramptonIce Accretion2070RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
BramptonIce Accretion2075RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2075 | 15.513 | 18.8721 | 23.1062 | 26.329 | 29.5391
BramptonIce Accretion2080RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2080 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
BramptonIce Accretion2085RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2085 | 15.3652 | 18.7684 | 23.0688 | 26.329 | 29.5864
BramptonIce Accretion2090RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2090 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
BramptonIce Accretion2095RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2095 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
BramptonIce Accretion2100RCP6.0 | Brampton | Ice Accretion | RCP6.0 | 2100 | 14.2127 | 17.596 | 21.825 | 25.0577 | 28.2555
BramptonIce Accretion2023RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
BramptonIce Accretion2025RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2025 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
BramptonIce Accretion2030RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2030 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
BramptonIce Accretion2035RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2035 | 16.6133 | 20.0652 | 24.425 | 27.7415 | 31.059
BramptonIce Accretion2040RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2040 | 16.2712 | 19.6848 | 23.9917 | 27.2707 | 30.5445
BramptonIce Accretion2045RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2045 | 15.9291 | 19.3044 | 23.5583 | 26.7998 | 30.03
BramptonIce Accretion2050RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2050 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
BramptonIce Accretion2055RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2055 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
BramptonIce Accretion2060RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2060 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
BramptonIce Accretion2065RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2065 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
BramptonIce Accretion2070RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2070 | 13.8125 | 17.1464 | 21.325 | 24.5022 | 27.657
BramptonIce Accretion2075RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2075 | 13.4124 | 16.6968 | 20.825 | 23.9466 | 27.0585
BramptonIce Accretion2080RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2080 | 13.0123 | 16.2473 | 20.325 | 23.391 | 26.46
BramptonIce Accretion2085RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2085 | 12.1338 | 15.1994 | 19.0625 | 21.9785 | 24.885
BramptonIce Accretion2090RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2090 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
BramptonIce Accretion2095RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2095 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
BramptonIce Accretion2100RCP8.5 | Brampton | Ice Accretion | RCP8.5 | 2100 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
BramptonWind2023RCP4.5 | Brampton | Wind | RCP4.5 | 2023 | 81.5651 | 87.9008 | 94.5828 | 101.2539 | 107.9208
BramptonWind2025RCP4.5 | Brampton | Wind | RCP4.5 | 2025 | 81.5948 | 87.9445 | 94.6455 | 101.3327 | 108.0155
BramptonWind2030RCP4.5 | Brampton | Wind | RCP4.5 | 2030 | 81.6246 | 87.9882 | 94.7081 | 101.4115 | 108.1102
BramptonWind2035RCP4.5 | Brampton | Wind | RCP4.5 | 2035 | 81.6544 | 88.0319 | 94.7708 | 101.4902 | 108.2048
BramptonWind2040RCP4.5 | Brampton | Wind | RCP4.5 | 2040 | 81.6841 | 88.0756 | 94.8335 | 101.569 | 108.2995
BramptonWind2045RCP4.5 | Brampton | Wind | RCP4.5 | 2045 | 81.7139 | 88.1194 | 94.8961 | 101.6478 | 108.3941
BramptonWind2050RCP4.5 | Brampton | Wind | RCP4.5 | 2050 | 81.8086 | 88.2417 | 95.0547 | 101.8373 | 108.6152
BramptonWind2055RCP4.5 | Brampton | Wind | RCP4.5 | 2055 | 81.8735 | 88.3204 | 95.1506 | 101.9479 | 108.7417
BramptonWind2060RCP4.5 | Brampton | Wind | RCP4.5 | 2060 | 81.9384 | 88.3991 | 95.2464 | 102.0585 | 108.8681
BramptonWind2065RCP4.5 | Brampton | Wind | RCP4.5 | 2065 | 82.0034 | 88.4778 | 95.3423 | 102.1692 | 108.9946
BramptonWind2070RCP4.5 | Brampton | Wind | RCP4.5 | 2070 | 82.0683 | 88.5565 | 95.4382 | 102.2798 | 109.121
BramptonWind2075RCP4.5 | Brampton | Wind | RCP4.5 | 2075 | 82.1576 | 88.6818 | 95.609 | 102.4877 | 109.3675
BramptonWind2080RCP4.5 | Brampton | Wind | RCP4.5 | 2080 | 82.2469 | 88.8071 | 95.7797 | 102.6955 | 109.614
BramptonWind2085RCP4.5 | Brampton | Wind | RCP4.5 | 2085 | 82.3362 | 88.9324 | 95.9505 | 102.9034 | 109.8604
BramptonWind2090RCP4.5 | Brampton | Wind | RCP4.5 | 2090 | 82.4254 | 89.0577 | 96.1213 | 103.1113 | 110.1069
BramptonWind2095RCP4.5 | Brampton | Wind | RCP4.5 | 2095 | 82.5147 | 89.183 | 96.292 | 103.3191 | 110.3534
BramptonWind2100RCP4.5 | Brampton | Wind | RCP4.5 | 2100 | 82.604 | 89.3083 | 96.4628 | 103.527 | 110.5998
BramptonWind2023RCP6.0 | Brampton | Wind | RCP6.0 | 2023 | 81.5651 | 87.9008 | 94.5828 | 101.2539 | 107.9208
BramptonWind2025RCP6.0 | Brampton | Wind | RCP6.0 | 2025 | 81.5948 | 87.9445 | 94.6455 | 101.3327 | 108.0155
BramptonWind2030RCP6.0 | Brampton | Wind | RCP6.0 | 2030 | 81.6246 | 87.9882 | 94.7081 | 101.4115 | 108.1102
BramptonWind2035RCP6.0 | Brampton | Wind | RCP6.0 | 2035 | 81.6544 | 88.0319 | 94.7708 | 101.4902 | 108.2048
BramptonWind2040RCP6.0 | Brampton | Wind | RCP6.0 | 2040 | 81.6841 | 88.0756 | 94.8335 | 101.569 | 108.2995
BramptonWind2045RCP6.0 | Brampton | Wind | RCP6.0 | 2045 | 81.7139 | 88.1194 | 94.8961 | 101.6478 | 108.3941
BramptonWind2050RCP6.0 | Brampton | Wind | RCP6.0 | 2050 | 81.8086 | 88.2417 | 95.0547 | 101.8373 | 108.6152
BramptonWind2055RCP6.0 | Brampton | Wind | RCP6.0 | 2055 | 81.8735 | 88.3204 | 95.1506 | 101.9479 | 108.7417
BramptonWind2060RCP6.0 | Brampton | Wind | RCP6.0 | 2060 | 81.9384 | 88.3991 | 95.2464 | 102.0585 | 108.8681
BramptonWind2065RCP6.0 | Brampton | Wind | RCP6.0 | 2065 | 82.0034 | 88.4778 | 95.3423 | 102.1692 | 108.9946
BramptonWind2070RCP6.0 | Brampton | Wind | RCP6.0 | 2070 | 82.0683 | 88.5565 | 95.4382 | 102.2798 | 109.121
BramptonWind2075RCP6.0 | Brampton | Wind | RCP6.0 | 2075 | 82.2022 | 88.7444 | 95.6944 | 102.5916 | 109.4907
BramptonWind2080RCP6.0 | Brampton | Wind | RCP6.0 | 2080 | 82.3362 | 88.9324 | 95.9505 | 102.9034 | 109.8604
BramptonWind2085RCP6.0 | Brampton | Wind | RCP6.0 | 2085 | 82.4701 | 89.1203 | 96.2066 | 103.2152 | 110.2301
BramptonWind2090RCP6.0 | Brampton | Wind | RCP6.0 | 2090 | 82.8854 | 89.6696 | 96.9234 | 104.0735 | 111.2357
BramptonWind2095RCP6.0 | Brampton | Wind | RCP6.0 | 2095 | 83.1668 | 90.0309 | 97.384 | 104.62 | 111.8715
BramptonWind2100RCP6.0 | Brampton | Wind | RCP6.0 | 2100 | 83.4482 | 90.3923 | 97.8446 | 105.1664 | 112.5073
BramptonWind2023RCP8.5 | Brampton | Wind | RCP8.5 | 2023 | 81.5651 | 87.9008 | 94.5828 | 101.2539 | 107.9208
BramptonWind2025RCP8.5 | Brampton | Wind | RCP8.5 | 2025 | 81.6246 | 87.9882 | 94.7081 | 101.4115 | 108.1102
BramptonWind2030RCP8.5 | Brampton | Wind | RCP8.5 | 2030 | 81.6841 | 88.0756 | 94.8335 | 101.569 | 108.2995
BramptonWind2035RCP8.5 | Brampton | Wind | RCP8.5 | 2035 | 81.7436 | 88.1631 | 94.9588 | 101.7266 | 108.4888
BramptonWind2040RCP8.5 | Brampton | Wind | RCP8.5 | 2040 | 81.8519 | 88.2942 | 95.1186 | 101.911 | 108.6995
BramptonWind2045RCP8.5 | Brampton | Wind | RCP8.5 | 2045 | 81.9601 | 88.4253 | 95.2784 | 102.0954 | 108.9103
BramptonWind2050RCP8.5 | Brampton | Wind | RCP8.5 | 2050 | 82.2469 | 88.8071 | 95.7797 | 102.6955 | 109.614
BramptonWind2055RCP8.5 | Brampton | Wind | RCP8.5 | 2055 | 82.4254 | 89.0577 | 96.1213 | 103.1113 | 110.1069
BramptonWind2060RCP8.5 | Brampton | Wind | RCP8.5 | 2060 | 82.8854 | 89.6696 | 96.9234 | 104.0735 | 111.2357
BramptonWind2065RCP8.5 | Brampton | Wind | RCP8.5 | 2065 | 83.1668 | 90.0309 | 97.384 | 104.62 | 111.8715
BramptonWind2070RCP8.5 | Brampton | Wind | RCP8.5 | 2070 | 83.6078 | 90.6225 | 98.1642 | 105.5587 | 112.9752
BramptonWind2075RCP8.5 | Brampton | Wind | RCP8.5 | 2075 | 83.7674 | 90.8527 | 98.4838 | 105.951 | 113.4431
BramptonWind2080RCP8.5 | Brampton | Wind | RCP8.5 | 2080 | 83.927 | 91.0829 | 98.8034 | 106.3432 | 113.9111
BramptonWind2085RCP8.5 | Brampton | Wind | RCP8.5 | 2085 | 84.1827 | 91.4151 | 99.2311 | 106.8562 | 114.5112
BramptonWind2090RCP8.5 | Brampton | Wind | RCP8.5 | 2090 | 84.4384 | 91.7473 | 99.6588 | 107.3692 | 115.1113
BramptonWind2095RCP8.5 | Brampton | Wind | RCP8.5 | 2095 | 84.4384 | 91.7473 | 99.6588 | 107.3692 | 115.1113
BramptonWind2100RCP8.5 | Brampton | Wind | RCP8.5 | 2100 | 84.4384 | 91.7473 | 99.6588 | 107.3692 | 115.1113
BrantfordIce Accretion2023RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2023 | 20.5414 | 24.6261 | 29.82 | 33.7644 | 37.7244
BrantfordIce Accretion2025RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2025 | 20.437 | 24.514 | 29.695 | 33.6345 | 37.5858
BrantfordIce Accretion2030RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2030 | 20.3326 | 24.402 | 29.57 | 33.5045 | 37.4472
BrantfordIce Accretion2035RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2035 | 20.2282 | 24.2899 | 29.445 | 33.3745 | 37.3086
BrantfordIce Accretion2040RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2040 | 20.1239 | 24.1779 | 29.32 | 33.2446 | 37.17
BrantfordIce Accretion2045RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2045 | 20.0195 | 24.0658 | 29.195 | 33.1146 | 37.0314
BrantfordIce Accretion2050RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2050 | 19.6354 | 23.65 | 28.74 | 32.6254 | 36.5072
BrantfordIce Accretion2055RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2055 | 19.3557 | 23.3462 | 28.41 | 32.266 | 36.1217
BrantfordIce Accretion2060RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2060 | 19.0759 | 23.0425 | 28.08 | 31.9067 | 35.7361
BrantfordIce Accretion2065RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2065 | 18.7962 | 22.7387 | 27.75 | 31.5473 | 35.3506
BrantfordIce Accretion2070RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2070 | 18.5165 | 22.4349 | 27.42 | 31.188 | 34.965
BrantfordIce Accretion2075RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2075 | 18.426 | 22.356 | 27.35 | 31.1258 | 34.902
BrantfordIce Accretion2080RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2080 | 18.3355 | 22.2772 | 27.28 | 31.0637 | 34.839
BrantfordIce Accretion2085RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2085 | 18.2451 | 22.1983 | 27.21 | 31.0016 | 34.776
BrantfordIce Accretion2090RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2090 | 18.1546 | 22.1195 | 27.14 | 30.9394 | 34.713
BrantfordIce Accretion2095RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2095 | 18.0642 | 22.0406 | 27.07 | 30.8773 | 34.65
BrantfordIce Accretion2100RCP4.5 | Brantford | Ice Accretion | RCP4.5 | 2100 | 17.9737 | 21.9618 | 27 | 30.8151 | 34.587
BrantfordIce Accretion2023RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2023 | 20.5414 | 24.6261 | 29.82 | 33.7644 | 37.7244
BrantfordIce Accretion2025RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2025 | 20.437 | 24.514 | 29.695 | 33.6345 | 37.5858
BrantfordIce Accretion2030RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2030 | 20.3326 | 24.402 | 29.57 | 33.5045 | 37.4472
BrantfordIce Accretion2035RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2035 | 20.2282 | 24.2899 | 29.445 | 33.3745 | 37.3086
BrantfordIce Accretion2040RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2040 | 20.1239 | 24.1779 | 29.32 | 33.2446 | 37.17
BrantfordIce Accretion2045RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2045 | 20.0195 | 24.0658 | 29.195 | 33.1146 | 37.0314
BrantfordIce Accretion2050RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2050 | 19.6354 | 23.65 | 28.74 | 32.6254 | 36.5072
BrantfordIce Accretion2055RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2055 | 19.3557 | 23.3462 | 28.41 | 32.266 | 36.1217
BrantfordIce Accretion2060RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2060 | 19.0759 | 23.0425 | 28.08 | 31.9067 | 35.7361
BrantfordIce Accretion2065RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2065 | 18.7962 | 22.7387 | 27.75 | 31.5473 | 35.3506
BrantfordIce Accretion2070RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2070 | 18.5165 | 22.4349 | 27.42 | 31.188 | 34.965
BrantfordIce Accretion2075RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2075 | 18.3808 | 22.3166 | 27.315 | 31.0948 | 34.8705
BrantfordIce Accretion2080RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2080 | 18.2451 | 22.1983 | 27.21 | 31.0016 | 34.776
BrantfordIce Accretion2085RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2085 | 18.1094 | 22.0801 | 27.105 | 30.9083 | 34.6815
BrantfordIce Accretion2090RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2090 | 17.3822 | 21.2895 | 26.22 | 29.9563 | 33.6546
BrantfordIce Accretion2095RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2095 | 16.7908 | 20.6172 | 25.44 | 29.0975 | 32.7222
BrantfordIce Accretion2100RCP6.0 | Brantford | Ice Accretion | RCP6.0 | 2100 | 16.1993 | 19.9449 | 24.66 | 28.2387 | 31.7898
BrantfordIce Accretion2023RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2023 | 20.5414 | 24.6261 | 29.82 | 33.7644 | 37.7244
BrantfordIce Accretion2025RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2025 | 20.3326 | 24.402 | 29.57 | 33.5045 | 37.4472
BrantfordIce Accretion2030RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2030 | 20.1239 | 24.1779 | 29.32 | 33.2446 | 37.17
BrantfordIce Accretion2035RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2035 | 19.9151 | 23.9538 | 29.07 | 32.9847 | 36.8928
BrantfordIce Accretion2040RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2040 | 19.4489 | 23.4475 | 28.52 | 32.3858 | 36.2502
BrantfordIce Accretion2045RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2045 | 18.9827 | 22.9412 | 27.97 | 31.7869 | 35.6076
BrantfordIce Accretion2050RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2050 | 18.3355 | 22.2772 | 27.28 | 31.0637 | 34.839
BrantfordIce Accretion2055RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2055 | 18.1546 | 22.1195 | 27.14 | 30.9394 | 34.713
BrantfordIce Accretion2060RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2060 | 17.3822 | 21.2895 | 26.22 | 29.9563 | 33.6546
BrantfordIce Accretion2065RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2065 | 16.7908 | 20.6172 | 25.44 | 29.0975 | 32.7222
BrantfordIce Accretion2070RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2070 | 15.8166 | 19.5216 | 24.19 | 27.7189 | 31.2354
BrantfordIce Accretion2075RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2075 | 15.4339 | 19.0983 | 23.72 | 27.1991 | 30.681
BrantfordIce Accretion2080RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2080 | 15.0512 | 18.675 | 23.25 | 26.6793 | 30.1266
BrantfordIce Accretion2085RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2085 | 14.0283 | 17.4798 | 21.795 | 25.0521 | 28.3122
BrantfordIce Accretion2090RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2090 | 13.0054 | 16.2846 | 20.34 | 23.4249 | 26.4978
BrantfordIce Accretion2095RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2095 | 13.0054 | 16.2846 | 20.34 | 23.4249 | 26.4978
BrantfordIce Accretion2100RCP8.5 | Brantford | Ice Accretion | RCP8.5 | 2100 | 13.0054 | 16.2846 | 20.34 | 23.4249 | 26.4978
BrantfordWind2023RCP4.5 | Brantford | Wind | RCP4.5 | 2023 | 86.7541 | 93.5301 | 100.69 | 107.8239 | 114.9576
BrantfordWind2025RCP4.5 | Brantford | Wind | RCP4.5 | 2025 | 86.7728 | 93.5627 | 100.74 | 107.8881 | 115.0374
BrantfordWind2030RCP4.5 | Brantford | Wind | RCP4.5 | 2030 | 86.7915 | 93.5952 | 100.79 | 107.9523 | 115.1172
BrantfordWind2035RCP4.5 | Brantford | Wind | RCP4.5 | 2035 | 86.8102 | 93.6278 | 100.84 | 108.0165 | 115.197
BrantfordWind2040RCP4.5 | Brantford | Wind | RCP4.5 | 2040 | 86.8289 | 93.6603 | 100.89 | 108.0807 | 115.2768
BrantfordWind2045RCP4.5 | Brantford | Wind | RCP4.5 | 2045 | 86.8476 | 93.6929 | 100.94 | 108.1449 | 115.3566
BrantfordWind2050RCP4.5 | Brantford | Wind | RCP4.5 | 2050 | 86.9389 | 93.8203 | 101.112 | 108.3568 | 115.6097
BrantfordWind2055RCP4.5 | Brantford | Wind | RCP4.5 | 2055 | 87.0114 | 93.9151 | 101.234 | 108.5044 | 115.783
BrantfordWind2060RCP4.5 | Brantford | Wind | RCP4.5 | 2060 | 87.0839 | 94.01 | 101.356 | 108.6521 | 115.9562
BrantfordWind2065RCP4.5 | Brantford | Wind | RCP4.5 | 2065 | 87.1565 | 94.1048 | 101.478 | 108.7997 | 116.1295
BrantfordWind2070RCP4.5 | Brantford | Wind | RCP4.5 | 2070 | 87.229 | 94.1997 | 101.6 | 108.9474 | 116.3028
BrantfordWind2075RCP4.5 | Brantford | Wind | RCP4.5 | 2075 | 87.3369 | 94.3438 | 101.7883 | 109.1721 | 116.5669
BrantfordWind2080RCP4.5 | Brantford | Wind | RCP4.5 | 2080 | 87.4449 | 94.488 | 101.9767 | 109.3968 | 116.831
BrantfordWind2085RCP4.5 | Brantford | Wind | RCP4.5 | 2085 | 87.5528 | 94.6321 | 102.165 | 109.6215 | 117.0951
BrantfordWind2090RCP4.5 | Brantford | Wind | RCP4.5 | 2090 | 87.6607 | 94.7763 | 102.3533 | 109.8462 | 117.3592
BrantfordWind2095RCP4.5 | Brantford | Wind | RCP4.5 | 2095 | 87.7687 | 94.9205 | 102.5417 | 110.0709 | 117.6233
BrantfordWind2100RCP4.5 | Brantford | Wind | RCP4.5 | 2100 | 87.8766 | 95.0646 | 102.73 | 110.2956 | 117.8874
BrantfordWind2023RCP6.0 | Brantford | Wind | RCP6.0 | 2023 | 86.7541 | 93.5301 | 100.69 | 107.8239 | 114.9576
BrantfordWind2025RCP6.0 | Brantford | Wind | RCP6.0 | 2025 | 86.7728 | 93.5627 | 100.74 | 107.8881 | 115.0374
BrantfordWind2030RCP6.0 | Brantford | Wind | RCP6.0 | 2030 | 86.7915 | 93.5952 | 100.79 | 107.9523 | 115.1172
BrantfordWind2035RCP6.0 | Brantford | Wind | RCP6.0 | 2035 | 86.8102 | 93.6278 | 100.84 | 108.0165 | 115.197
BrantfordWind2040RCP6.0 | Brantford | Wind | RCP6.0 | 2040 | 86.8289 | 93.6603 | 100.89 | 108.0807 | 115.2768
BrantfordWind2045RCP6.0 | Brantford | Wind | RCP6.0 | 2045 | 86.8476 | 93.6929 | 100.94 | 108.1449 | 115.3566
BrantfordWind2050RCP6.0 | Brantford | Wind | RCP6.0 | 2050 | 86.9389 | 93.8203 | 101.112 | 108.3568 | 115.6097
BrantfordWind2055RCP6.0 | Brantford | Wind | RCP6.0 | 2055 | 87.0114 | 93.9151 | 101.234 | 108.5044 | 115.783
BrantfordWind2060RCP6.0 | Brantford | Wind | RCP6.0 | 2060 | 87.0839 | 94.01 | 101.356 | 108.6521 | 115.9562
BrantfordWind2065RCP6.0 | Brantford | Wind | RCP6.0 | 2065 | 87.1565 | 94.1048 | 101.478 | 108.7997 | 116.1295
BrantfordWind2070RCP6.0 | Brantford | Wind | RCP6.0 | 2070 | 87.229 | 94.1997 | 101.6 | 108.9474 | 116.3028
BrantfordWind2075RCP6.0 | Brantford | Wind | RCP6.0 | 2075 | 87.3909 | 94.4159 | 101.8825 | 109.2844 | 116.6989
BrantfordWind2080RCP6.0 | Brantford | Wind | RCP6.0 | 2080 | 87.5528 | 94.6321 | 102.165 | 109.6215 | 117.0951
BrantfordWind2085RCP6.0 | Brantford | Wind | RCP6.0 | 2085 | 87.7147 | 94.8484 | 102.4475 | 109.9586 | 117.4912
BrantfordWind2090RCP6.0 | Brantford | Wind | RCP6.0 | 2090 | 88.1961 | 95.4707 | 103.25 | 110.9126 | 118.6018
BrantfordWind2095RCP6.0 | Brantford | Wind | RCP6.0 | 2095 | 88.5156 | 95.8768 | 103.77 | 111.5297 | 119.3162
BrantfordWind2100RCP6.0 | Brantford | Wind | RCP6.0 | 2100 | 88.8351 | 96.2829 | 104.29 | 112.1467 | 120.0306
BrantfordWind2023RCP8.5 | Brantford | Wind | RCP8.5 | 2023 | 86.7541 | 93.5301 | 100.69 | 107.8239 | 114.9576
BrantfordWind2025RCP8.5 | Brantford | Wind | RCP8.5 | 2025 | 86.7915 | 93.5952 | 100.79 | 107.9523 | 115.1172
BrantfordWind2030RCP8.5 | Brantford | Wind | RCP8.5 | 2030 | 86.8289 | 93.6603 | 100.89 | 108.0807 | 115.2768
BrantfordWind2035RCP8.5 | Brantford | Wind | RCP8.5 | 2035 | 86.8663 | 93.7254 | 100.99 | 108.2091 | 115.4364
BrantfordWind2040RCP8.5 | Brantford | Wind | RCP8.5 | 2040 | 86.9872 | 93.8835 | 101.1933 | 108.4552 | 115.7252
BrantfordWind2045RCP8.5 | Brantford | Wind | RCP8.5 | 2045 | 87.1081 | 94.0416 | 101.3967 | 108.7013 | 116.014
BrantfordWind2050RCP8.5 | Brantford | Wind | RCP8.5 | 2050 | 87.4449 | 94.488 | 101.9767 | 109.3968 | 116.831
BrantfordWind2055RCP8.5 | Brantford | Wind | RCP8.5 | 2055 | 87.6607 | 94.7763 | 102.3533 | 109.8462 | 117.3592
BrantfordWind2060RCP8.5 | Brantford | Wind | RCP8.5 | 2060 | 88.1961 | 95.4707 | 103.25 | 110.9126 | 118.6018
BrantfordWind2065RCP8.5 | Brantford | Wind | RCP8.5 | 2065 | 88.5156 | 95.8768 | 103.77 | 111.5297 | 119.3162
BrantfordWind2070RCP8.5 | Brantford | Wind | RCP8.5 | 2070 | 89.0135 | 96.5309 | 104.63 | 112.5604 | 120.5208
BrantfordWind2075RCP8.5 | Brantford | Wind | RCP8.5 | 2075 | 89.192 | 96.7789 | 104.97 | 112.9742 | 121.011
BrantfordWind2080RCP8.5 | Brantford | Wind | RCP8.5 | 2080 | 89.3704 | 97.0269 | 105.31 | 113.3879 | 121.5012
BrantfordWind2085RCP8.5 | Brantford | Wind | RCP8.5 | 2085 | 89.6424 | 97.3942 | 105.79 | 113.9711 | 122.1852
BrantfordWind2090RCP8.5 | Brantford | Wind | RCP8.5 | 2090 | 89.9144 | 97.7616 | 106.27 | 114.5542 | 122.8692
BrantfordWind2095RCP8.5 | Brantford | Wind | RCP8.5 | 2095 | 89.9144 | 97.7616 | 106.27 | 114.5542 | 122.8692
BrantfordWind2100RCP8.5 | Brantford | Wind | RCP8.5 | 2100 | 89.9144 | 97.7616 | 106.27 | 114.5542 | 122.8692
BrightonIce Accretion2023RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
BrightonIce Accretion2025RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
BrightonIce Accretion2030RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
BrightonIce Accretion2035RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
BrightonIce Accretion2040RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
BrightonIce Accretion2045RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
BrightonIce Accretion2050RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
BrightonIce Accretion2055RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
BrightonIce Accretion2060RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
BrightonIce Accretion2065RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
BrightonIce Accretion2070RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
BrightonIce Accretion2075RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2075 | 16.8859 | 20.3972 | 24.8292 | 28.2123 | 31.5682
BrightonIce Accretion2080RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2080 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
BrightonIce Accretion2085RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2085 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
BrightonIce Accretion2090RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2090 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
BrightonIce Accretion2095RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2095 | 16.7235 | 20.3142 | 24.8458 | 28.2877 | 31.7152
BrightonIce Accretion2100RCP4.5 | Brighton | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.2935 | 24.85 | 28.3065 | 31.752
BrightonIce Accretion2023RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
BrightonIce Accretion2025RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
BrightonIce Accretion2030RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
BrightonIce Accretion2035RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
BrightonIce Accretion2040RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
BrightonIce Accretion2045RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
BrightonIce Accretion2050RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
BrightonIce Accretion2055RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
BrightonIce Accretion2060RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
BrightonIce Accretion2065RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
BrightonIce Accretion2070RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
BrightonIce Accretion2075RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2075 | 16.8656 | 20.3869 | 24.8313 | 28.2217 | 31.5866
BrightonIce Accretion2080RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2080 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
BrightonIce Accretion2085RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2085 | 16.7438 | 20.3246 | 24.8438 | 28.2782 | 31.6969
BrightonIce Accretion2090RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2090 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
BrightonIce Accretion2095RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2095 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
BrightonIce Accretion2100RCP6.0 | Brighton | Ice Accretion | RCP6.0 | 2100 | 15.6565 | 19.173 | 23.6 | 26.9505 | 30.2715
BrightonIce Accretion2023RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
BrightonIce Accretion2025RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2025 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
BrightonIce Accretion2030RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2030 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
BrightonIce Accretion2035RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2035 | 17.6745 | 21.2272 | 25.725 | 29.154 | 32.571
BrightonIce Accretion2040RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2040 | 17.4251 | 20.9575 | 25.425 | 28.8338 | 32.2245
BrightonIce Accretion2045RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2045 | 17.1758 | 20.6877 | 25.125 | 28.5137 | 31.878
BrightonIce Accretion2050RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2050 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
BrightonIce Accretion2055RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2055 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
BrightonIce Accretion2060RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2060 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
BrightonIce Accretion2065RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2065 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
BrightonIce Accretion2070RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2070 | 15.2216 | 18.6888 | 23.05 | 26.3478 | 29.631
BrightonIce Accretion2075RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2075 | 14.7867 | 18.2047 | 22.5 | 25.7452 | 28.9905
BrightonIce Accretion2080RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2080 | 14.3518 | 17.7205 | 21.95 | 25.1425 | 28.35
BrightonIce Accretion2085RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2085 | 13.6908 | 16.9424 | 21.025 | 24.0972 | 27.1845
BrightonIce Accretion2090RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2090 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
BrightonIce Accretion2095RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2095 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
BrightonIce Accretion2100RCP8.5 | Brighton | Ice Accretion | RCP8.5 | 2100 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
BrightonWind2023RCP4.5 | Brighton | Wind | RCP4.5 | 2023 | 87.735 | 94.5124 | 101.6363 | 108.7616 | 115.8884
BrightonWind2025RCP4.5 | Brighton | Wind | RCP4.5 | 2025 | 87.7016 | 94.4764 | 101.6009 | 108.7238 | 115.85
BrightonWind2030RCP4.5 | Brighton | Wind | RCP4.5 | 2030 | 87.6681 | 94.4404 | 101.5656 | 108.686 | 115.8116
BrightonWind2035RCP4.5 | Brighton | Wind | RCP4.5 | 2035 | 87.6347 | 94.4043 | 101.5302 | 108.6482 | 115.7733
BrightonWind2040RCP4.5 | Brighton | Wind | RCP4.5 | 2040 | 87.6013 | 94.3683 | 101.4949 | 108.6103 | 115.7349
BrightonWind2045RCP4.5 | Brighton | Wind | RCP4.5 | 2045 | 87.5678 | 94.3323 | 101.4595 | 108.5725 | 115.6965
BrightonWind2050RCP4.5 | Brighton | Wind | RCP4.5 | 2050 | 87.6582 | 94.4616 | 101.6403 | 108.7941 | 115.9621
BrightonWind2055RCP4.5 | Brighton | Wind | RCP4.5 | 2055 | 87.7821 | 94.627 | 101.8565 | 109.0534 | 116.2661
BrightonWind2060RCP4.5 | Brighton | Wind | RCP4.5 | 2060 | 87.9059 | 94.7923 | 102.0726 | 109.3128 | 116.57
BrightonWind2065RCP4.5 | Brighton | Wind | RCP4.5 | 2065 | 88.0298 | 94.9576 | 102.2888 | 109.5722 | 116.874
BrightonWind2070RCP4.5 | Brighton | Wind | RCP4.5 | 2070 | 88.1536 | 95.1229 | 102.5049 | 109.8315 | 117.178
BrightonWind2075RCP4.5 | Brighton | Wind | RCP4.5 | 2075 | 88.2161 | 95.209 | 102.6194 | 109.9702 | 117.3411
BrightonWind2080RCP4.5 | Brighton | Wind | RCP4.5 | 2080 | 88.2786 | 95.2951 | 102.7338 | 110.1089 | 117.5042
BrightonWind2085RCP4.5 | Brighton | Wind | RCP4.5 | 2085 | 88.3411 | 95.3812 | 102.8483 | 110.2476 | 117.6673
BrightonWind2090RCP4.5 | Brighton | Wind | RCP4.5 | 2090 | 88.4036 | 95.4673 | 102.9628 | 110.3863 | 117.8304
BrightonWind2095RCP4.5 | Brighton | Wind | RCP4.5 | 2095 | 88.4661 | 95.5534 | 103.0772 | 110.525 | 117.9936
BrightonWind2100RCP4.5 | Brighton | Wind | RCP4.5 | 2100 | 88.5286 | 95.6395 | 103.1917 | 110.6637 | 118.1567
BrightonWind2023RCP6.0 | Brighton | Wind | RCP6.0 | 2023 | 87.735 | 94.5124 | 101.6363 | 108.7616 | 115.8884
BrightonWind2025RCP6.0 | Brighton | Wind | RCP6.0 | 2025 | 87.7016 | 94.4764 | 101.6009 | 108.7238 | 115.85
BrightonWind2030RCP6.0 | Brighton | Wind | RCP6.0 | 2030 | 87.6681 | 94.4404 | 101.5656 | 108.686 | 115.8116
BrightonWind2035RCP6.0 | Brighton | Wind | RCP6.0 | 2035 | 87.6347 | 94.4043 | 101.5302 | 108.6482 | 115.7733
BrightonWind2040RCP6.0 | Brighton | Wind | RCP6.0 | 2040 | 87.6013 | 94.3683 | 101.4949 | 108.6103 | 115.7349
BrightonWind2045RCP6.0 | Brighton | Wind | RCP6.0 | 2045 | 87.5678 | 94.3323 | 101.4595 | 108.5725 | 115.6965
BrightonWind2050RCP6.0 | Brighton | Wind | RCP6.0 | 2050 | 87.6582 | 94.4616 | 101.6403 | 108.7941 | 115.9621
BrightonWind2055RCP6.0 | Brighton | Wind | RCP6.0 | 2055 | 87.7821 | 94.627 | 101.8565 | 109.0534 | 116.2661
BrightonWind2060RCP6.0 | Brighton | Wind | RCP6.0 | 2060 | 87.9059 | 94.7923 | 102.0726 | 109.3128 | 116.57
BrightonWind2065RCP6.0 | Brighton | Wind | RCP6.0 | 2065 | 88.0298 | 94.9576 | 102.2888 | 109.5722 | 116.874
BrightonWind2070RCP6.0 | Brighton | Wind | RCP6.0 | 2070 | 88.1536 | 95.1229 | 102.5049 | 109.8315 | 117.178
BrightonWind2075RCP6.0 | Brighton | Wind | RCP6.0 | 2075 | 88.2474 | 95.2521 | 102.6766 | 110.0396 | 117.4227
BrightonWind2080RCP6.0 | Brighton | Wind | RCP6.0 | 2080 | 88.3411 | 95.3812 | 102.8483 | 110.2476 | 117.6673
BrightonWind2085RCP6.0 | Brighton | Wind | RCP6.0 | 2085 | 88.4349 | 95.5104 | 103.02 | 110.4556 | 117.912
BrightonWind2090RCP6.0 | Brighton | Wind | RCP6.0 | 2090 | 88.828 | 96.0027 | 103.6361 | 111.1824 | 118.7439
BrightonWind2095RCP6.0 | Brighton | Wind | RCP6.0 | 2095 | 89.1275 | 96.3659 | 104.0805 | 111.7012 | 119.3311
BrightonWind2100RCP6.0 | Brighton | Wind | RCP6.0 | 2100 | 89.4269 | 96.7291 | 104.5249 | 112.2199 | 119.9183
BrightonWind2023RCP8.5 | Brighton | Wind | RCP8.5 | 2023 | 87.735 | 94.5124 | 101.6363 | 108.7616 | 115.8884
BrightonWind2025RCP8.5 | Brighton | Wind | RCP8.5 | 2025 | 87.6681 | 94.4404 | 101.5656 | 108.686 | 115.8116
BrightonWind2030RCP8.5 | Brighton | Wind | RCP8.5 | 2030 | 87.6013 | 94.3683 | 101.4949 | 108.6103 | 115.7349
BrightonWind2035RCP8.5 | Brighton | Wind | RCP8.5 | 2035 | 87.5344 | 94.2963 | 101.4242 | 108.5347 | 115.6581
BrightonWind2040RCP8.5 | Brighton | Wind | RCP8.5 | 2040 | 87.7408 | 94.5719 | 101.7844 | 108.967 | 116.1647
BrightonWind2045RCP8.5 | Brighton | Wind | RCP8.5 | 2045 | 87.9472 | 94.8474 | 102.1447 | 109.3993 | 116.6714
BrightonWind2050RCP8.5 | Brighton | Wind | RCP8.5 | 2050 | 88.2786 | 95.2951 | 102.7338 | 110.1089 | 117.5042
BrightonWind2055RCP8.5 | Brighton | Wind | RCP8.5 | 2055 | 88.4036 | 95.4673 | 102.9628 | 110.3863 | 117.8304
BrightonWind2060RCP8.5 | Brighton | Wind | RCP8.5 | 2060 | 88.828 | 96.0027 | 103.6361 | 111.1824 | 118.7439
BrightonWind2065RCP8.5 | Brighton | Wind | RCP8.5 | 2065 | 89.1275 | 96.3659 | 104.0805 | 111.7012 | 119.3311
BrightonWind2070RCP8.5 | Brighton | Wind | RCP8.5 | 2070 | 89.3455 | 96.6383 | 104.4205 | 112.1046 | 119.7955
BrightonWind2075RCP8.5 | Brighton | Wind | RCP8.5 | 2075 | 89.2641 | 96.5475 | 104.3162 | 111.9893 | 119.6727
BrightonWind2080RCP8.5 | Brighton | Wind | RCP8.5 | 2080 | 89.1827 | 96.4567 | 104.2118 | 111.8741 | 119.5499
BrightonWind2085RCP8.5 | Brighton | Wind | RCP8.5 | 2085 | 89.3964 | 96.7808 | 104.6764 | 112.4522 | 120.2465
BrightonWind2090RCP8.5 | Brighton | Wind | RCP8.5 | 2090 | 89.61 | 97.1048 | 105.141 | 113.0304 | 120.9431
BrightonWind2095RCP8.5 | Brighton | Wind | RCP8.5 | 2095 | 89.61 | 97.1048 | 105.141 | 113.0304 | 120.9431
BrightonWind2100RCP8.5 | Brighton | Wind | RCP8.5 | 2100 | 89.61 | 97.1048 | 105.141 | 113.0304 | 120.9431
BrockvilleIce Accretion2023RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2023 | 20.6249 | 24.5763 | 29.61 | 33.4593 | 37.3086
BrockvilleIce Accretion2025RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2025 | 20.6945 | 24.6801 | 29.755 | 33.6345 | 37.5102
BrockvilleIce Accretion2030RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2030 | 20.764 | 24.7838 | 29.9 | 33.8096 | 37.7118
BrockvilleIce Accretion2035RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2035 | 20.8336 | 24.8875 | 30.045 | 33.9847 | 37.9134
BrockvilleIce Accretion2040RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2040 | 20.9032 | 24.9913 | 30.19 | 34.1599 | 38.115
BrockvilleIce Accretion2045RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2045 | 20.9728 | 25.0951 | 30.335 | 34.335 | 38.3166
BrockvilleIce Accretion2050RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2050 | 20.9046 | 25.0544 | 30.318 | 34.3339 | 38.3368
BrockvilleIce Accretion2055RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2055 | 20.7668 | 24.91 | 30.156 | 34.1576 | 38.1553
BrockvilleIce Accretion2060RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2060 | 20.6291 | 24.7655 | 29.994 | 33.9814 | 37.9739
BrockvilleIce Accretion2065RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2065 | 20.4913 | 24.6211 | 29.832 | 33.8051 | 37.7924
BrockvilleIce Accretion2070RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2070 | 20.3535 | 24.4767 | 29.67 | 33.6288 | 37.611
BrockvilleIce Accretion2075RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2075 | 20.4231 | 24.5846 | 29.825 | 33.8209 | 37.8378
BrockvilleIce Accretion2080RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2080 | 20.4927 | 24.6925 | 29.98 | 34.013 | 38.0646
BrockvilleIce Accretion2085RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2085 | 20.5623 | 24.8004 | 30.135 | 34.2051 | 38.2914
BrockvilleIce Accretion2090RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2090 | 20.6318 | 24.9083 | 30.29 | 34.3972 | 38.5182
BrockvilleIce Accretion2095RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2095 | 20.7014 | 25.0162 | 30.445 | 34.5893 | 38.745
BrockvilleIce Accretion2100RCP4.5 | Brockville | Ice Accretion | RCP4.5 | 2100 | 20.771 | 25.1241 | 30.6 | 34.7814 | 38.9718
BrockvilleIce Accretion2023RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2023 | 20.6249 | 24.5763 | 29.61 | 33.4593 | 37.3086
BrockvilleIce Accretion2025RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2025 | 20.6945 | 24.6801 | 29.755 | 33.6345 | 37.5102
BrockvilleIce Accretion2030RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2030 | 20.764 | 24.7838 | 29.9 | 33.8096 | 37.7118
BrockvilleIce Accretion2035RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2035 | 20.8336 | 24.8875 | 30.045 | 33.9847 | 37.9134
BrockvilleIce Accretion2040RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2040 | 20.9032 | 24.9913 | 30.19 | 34.1599 | 38.115
BrockvilleIce Accretion2045RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2045 | 20.9728 | 25.0951 | 30.335 | 34.335 | 38.3166
BrockvilleIce Accretion2050RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2050 | 20.9046 | 25.0544 | 30.318 | 34.3339 | 38.3368
BrockvilleIce Accretion2055RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2055 | 20.7668 | 24.91 | 30.156 | 34.1576 | 38.1553
BrockvilleIce Accretion2060RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2060 | 20.6291 | 24.7655 | 29.994 | 33.9814 | 37.9739
BrockvilleIce Accretion2065RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2065 | 20.4913 | 24.6211 | 29.832 | 33.8051 | 37.7924
BrockvilleIce Accretion2070RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2070 | 20.3535 | 24.4767 | 29.67 | 33.6288 | 37.611
BrockvilleIce Accretion2075RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2075 | 20.4579 | 24.6385 | 29.9025 | 33.9169 | 37.9512
BrockvilleIce Accretion2080RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2080 | 20.5623 | 24.8004 | 30.135 | 34.2051 | 38.2914
BrockvilleIce Accretion2085RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2085 | 20.6666 | 24.9622 | 30.3675 | 34.4932 | 38.6316
BrockvilleIce Accretion2090RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2090 | 20.6249 | 24.9913 | 30.49 | 34.6797 | 38.8836
BrockvilleIce Accretion2095RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2095 | 20.4788 | 24.8585 | 30.38 | 34.578 | 38.7954
BrockvilleIce Accretion2100RCP6.0 | Brockville | Ice Accretion | RCP6.0 | 2100 | 20.3326 | 24.7257 | 30.27 | 34.4763 | 38.7072
BrockvilleIce Accretion2023RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2023 | 20.6249 | 24.5763 | 29.61 | 33.4593 | 37.3086
BrockvilleIce Accretion2025RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2025 | 20.764 | 24.7838 | 29.9 | 33.8096 | 37.7118
BrockvilleIce Accretion2030RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2030 | 20.9032 | 24.9913 | 30.19 | 34.1599 | 38.115
BrockvilleIce Accretion2035RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2035 | 21.0424 | 25.1988 | 30.48 | 34.5102 | 38.5182
BrockvilleIce Accretion2040RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2040 | 20.8128 | 24.9581 | 30.21 | 34.2164 | 38.2158
BrockvilleIce Accretion2045RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2045 | 20.5831 | 24.7174 | 29.94 | 33.9226 | 37.9134
BrockvilleIce Accretion2050RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2050 | 20.4927 | 24.6925 | 29.98 | 34.013 | 38.0646
BrockvilleIce Accretion2055RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2055 | 20.6318 | 24.9083 | 30.29 | 34.3972 | 38.5182
BrockvilleIce Accretion2060RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2060 | 20.6249 | 24.9913 | 30.49 | 34.6797 | 38.8836
BrockvilleIce Accretion2065RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2065 | 20.4788 | 24.8585 | 30.38 | 34.578 | 38.7954
BrockvilleIce Accretion2070RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2070 | 20.0473 | 24.4103 | 29.91 | 34.0808 | 38.2662
BrockvilleIce Accretion2075RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2075 | 19.762 | 24.0949 | 29.55 | 33.6853 | 37.8252
BrockvilleIce Accretion2080RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2080 | 19.4767 | 23.7795 | 29.19 | 33.2898 | 37.3842
BrockvilleIce Accretion2085RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2085 | 18.7148 | 22.8831 | 28.14 | 32.1202 | 36.0801
BrockvilleIce Accretion2090RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2090 | 17.9528 | 21.9867 | 27.09 | 30.9507 | 34.776
BrockvilleIce Accretion2095RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2095 | 17.9528 | 21.9867 | 27.09 | 30.9507 | 34.776
BrockvilleIce Accretion2100RCP8.5 | Brockville | Ice Accretion | RCP8.5 | 2100 | 17.9528 | 21.9867 | 27.09 | 30.9507 | 34.776
BrockvilleWind2023RCP4.5 | Brockville | Wind | RCP4.5 | 2023 | 80.1315 | 86.3985 | 93.0212 | 99.6213 | 106.2225
BrockvilleWind2025RCP4.5 | Brockville | Wind | RCP4.5 | 2025 | 80.1355 | 86.3942 | 93.0043 | 99.5934 | 106.1858
BrockvilleWind2030RCP4.5 | Brockville | Wind | RCP4.5 | 2030 | 80.1395 | 86.3899 | 92.9875 | 99.5655 | 106.149
BrockvilleWind2035RCP4.5 | Brockville | Wind | RCP4.5 | 2035 | 80.1434 | 86.3857 | 92.9706 | 99.5376 | 106.1123
BrockvilleWind2040RCP4.5 | Brockville | Wind | RCP4.5 | 2040 | 80.1474 | 86.3814 | 92.9537 | 99.5097 | 106.0756
BrockvilleWind2045RCP4.5 | Brockville | Wind | RCP4.5 | 2045 | 80.1514 | 86.3771 | 92.9369 | 99.4818 | 106.0389
BrockvilleWind2050RCP4.5 | Brockville | Wind | RCP4.5 | 2050 | 80.0743 | 86.2496 | 92.7434 | 99.2354 | 105.7358
BrockvilleWind2055RCP4.5 | Brockville | Wind | RCP4.5 | 2055 | 79.9933 | 86.1264 | 92.5667 | 99.0169 | 105.4694
BrockvilleWind2060RCP4.5 | Brockville | Wind | RCP4.5 | 2060 | 79.9123 | 86.0032 | 92.3901 | 98.7983 | 105.203
BrockvilleWind2065RCP4.5 | Brockville | Wind | RCP4.5 | 2065 | 79.8312 | 85.88 | 92.2134 | 98.5798 | 104.9366
BrockvilleWind2070RCP4.5 | Brockville | Wind | RCP4.5 | 2070 | 79.7502 | 85.7568 | 92.0368 | 98.3612 | 104.6702
BrockvilleWind2075RCP4.5 | Brockville | Wind | RCP4.5 | 2075 | 79.7171 | 85.714 | 91.9847 | 98.3005 | 104.6021
BrockvilleWind2080RCP4.5 | Brockville | Wind | RCP4.5 | 2080 | 79.684 | 85.6712 | 91.9325 | 98.2398 | 104.5339
BrockvilleWind2085RCP4.5 | Brockville | Wind | RCP4.5 | 2085 | 79.6509 | 85.6284 | 91.8804 | 98.1791 | 104.4657
BrockvilleWind2090RCP4.5 | Brockville | Wind | RCP4.5 | 2090 | 79.6178 | 85.5857 | 91.8283 | 98.1184 | 104.3976
BrockvilleWind2095RCP4.5 | Brockville | Wind | RCP4.5 | 2095 | 79.5847 | 85.5429 | 91.7761 | 98.0577 | 104.3294
BrockvilleWind2100RCP4.5 | Brockville | Wind | RCP4.5 | 2100 | 79.5516 | 85.5001 | 91.724 | 97.997 | 104.2612
BrockvilleWind2023RCP6.0 | Brockville | Wind | RCP6.0 | 2023 | 80.1315 | 86.3985 | 93.0212 | 99.6213 | 106.2225
BrockvilleWind2025RCP6.0 | Brockville | Wind | RCP6.0 | 2025 | 80.1355 | 86.3942 | 93.0043 | 99.5934 | 106.1858
BrockvilleWind2030RCP6.0 | Brockville | Wind | RCP6.0 | 2030 | 80.1395 | 86.3899 | 92.9875 | 99.5655 | 106.149
BrockvilleWind2035RCP6.0 | Brockville | Wind | RCP6.0 | 2035 | 80.1434 | 86.3857 | 92.9706 | 99.5376 | 106.1123
BrockvilleWind2040RCP6.0 | Brockville | Wind | RCP6.0 | 2040 | 80.1474 | 86.3814 | 92.9537 | 99.5097 | 106.0756
BrockvilleWind2045RCP6.0 | Brockville | Wind | RCP6.0 | 2045 | 80.1514 | 86.3771 | 92.9369 | 99.4818 | 106.0389
BrockvilleWind2050RCP6.0 | Brockville | Wind | RCP6.0 | 2050 | 80.0743 | 86.2496 | 92.7434 | 99.2354 | 105.7358
BrockvilleWind2055RCP6.0 | Brockville | Wind | RCP6.0 | 2055 | 79.9933 | 86.1264 | 92.5667 | 99.0169 | 105.4694
BrockvilleWind2060RCP6.0 | Brockville | Wind | RCP6.0 | 2060 | 79.9123 | 86.0032 | 92.3901 | 98.7983 | 105.203
BrockvilleWind2065RCP6.0 | Brockville | Wind | RCP6.0 | 2065 | 79.8312 | 85.88 | 92.2134 | 98.5798 | 104.9366
BrockvilleWind2070RCP6.0 | Brockville | Wind | RCP6.0 | 2070 | 79.7502 | 85.7568 | 92.0368 | 98.3612 | 104.6702
BrockvilleWind2075RCP6.0 | Brockville | Wind | RCP6.0 | 2075 | 79.7006 | 85.6926 | 91.9586 | 98.2702 | 104.568
BrockvilleWind2080RCP6.0 | Brockville | Wind | RCP6.0 | 2080 | 79.6509 | 85.6284 | 91.8804 | 98.1791 | 104.4657
BrockvilleWind2085RCP6.0 | Brockville | Wind | RCP6.0 | 2085 | 79.6013 | 85.5643 | 91.8022 | 98.0881 | 104.3635
BrockvilleWind2090RCP6.0 | Brockville | Wind | RCP6.0 | 2090 | 79.4828 | 85.406 | 91.5921 | 97.833 | 104.0619
BrockvilleWind2095RCP6.0 | Brockville | Wind | RCP6.0 | 2095 | 79.4139 | 85.3119 | 91.4603 | 97.6689 | 103.8627
BrockvilleWind2100RCP6.0 | Brockville | Wind | RCP6.0 | 2100 | 79.3451 | 85.2178 | 91.3284 | 97.5048 | 103.6634
BrockvilleWind2023RCP8.5 | Brockville | Wind | RCP8.5 | 2023 | 80.1315 | 86.3985 | 93.0212 | 99.6213 | 106.2225
BrockvilleWind2025RCP8.5 | Brockville | Wind | RCP8.5 | 2025 | 80.1395 | 86.3899 | 92.9875 | 99.5655 | 106.149
BrockvilleWind2030RCP8.5 | Brockville | Wind | RCP8.5 | 2030 | 80.1474 | 86.3814 | 92.9537 | 99.5097 | 106.0756
BrockvilleWind2035RCP8.5 | Brockville | Wind | RCP8.5 | 2035 | 80.1553 | 86.3728 | 92.92 | 99.4539 | 106.0022
BrockvilleWind2040RCP8.5 | Brockville | Wind | RCP8.5 | 2040 | 80.0203 | 86.1675 | 92.6256 | 99.0897 | 105.5582
BrockvilleWind2045RCP8.5 | Brockville | Wind | RCP8.5 | 2045 | 79.8852 | 85.9621 | 92.3312 | 98.7255 | 105.1142
BrockvilleWind2050RCP8.5 | Brockville | Wind | RCP8.5 | 2050 | 79.684 | 85.6712 | 91.9325 | 98.2398 | 104.5339
BrockvilleWind2055RCP8.5 | Brockville | Wind | RCP8.5 | 2055 | 79.6178 | 85.5857 | 91.8283 | 98.1184 | 104.3976
BrockvilleWind2060RCP8.5 | Brockville | Wind | RCP8.5 | 2060 | 79.4828 | 85.406 | 91.5921 | 97.833 | 104.0619
BrockvilleWind2065RCP8.5 | Brockville | Wind | RCP8.5 | 2065 | 79.4139 | 85.3119 | 91.4603 | 97.6689 | 103.8627
BrockvilleWind2070RCP8.5 | Brockville | Wind | RCP8.5 | 2070 | 79.4722 | 85.386 | 91.5492 | 97.7706 | 103.9815
BrockvilleWind2075RCP8.5 | Brockville | Wind | RCP8.5 | 2075 | 79.5993 | 85.5543 | 91.77 | 98.0364 | 104.2997
BrockvilleWind2080RCP8.5 | Brockville | Wind | RCP8.5 | 2080 | 79.7264 | 85.7226 | 91.9908 | 98.3022 | 104.6178
BrockvilleWind2085RCP8.5 | Brockville | Wind | RCP8.5 | 2085 | 79.7105 | 85.7226 | 92.0092 | 98.3366 | 104.665
BrockvilleWind2090RCP8.5 | Brockville | Wind | RCP8.5 | 2090 | 79.6946 | 85.7226 | 92.0276 | 98.3711 | 104.7122
BrockvilleWind2095RCP8.5 | Brockville | Wind | RCP8.5 | 2095 | 79.6946 | 85.7226 | 92.0276 | 98.3711 | 104.7122
BrockvilleWind2100RCP8.5 | Brockville | Wind | RCP8.5 | 2100 | 79.6946 | 85.7226 | 92.0276 | 98.3711 | 104.7122
Burk's FallsIce Accretion2023RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2023 | 15.2321 | 18.1504 | 21.868 | 24.7108 | 27.526
Burk's FallsIce Accretion2025RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2025 | 15.3086 | 18.2509 | 22 | 24.8641 | 27.7061
Burk's FallsIce Accretion2030RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2030 | 15.3852 | 18.3513 | 22.132 | 25.0174 | 27.8863
Burk's FallsIce Accretion2035RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2035 | 15.4617 | 18.4517 | 22.264 | 25.1707 | 28.0665
Burk's FallsIce Accretion2040RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2040 | 15.5382 | 18.5522 | 22.396 | 25.3241 | 28.2467
Burk's FallsIce Accretion2045RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2045 | 15.6148 | 18.6526 | 22.528 | 25.4774 | 28.4269
Burk's FallsIce Accretion2050RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2050 | 15.7373 | 18.8261 | 22.7612 | 25.755 | 28.7512
Burk's FallsIce Accretion2055RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2055 | 15.7832 | 18.8991 | 22.8624 | 25.8793 | 28.8953
Burk's FallsIce Accretion2060RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2060 | 15.8291 | 18.9721 | 22.9636 | 26.0036 | 29.0395
Burk's FallsIce Accretion2065RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2065 | 15.875 | 19.0452 | 23.0648 | 26.1279 | 29.1836
Burk's FallsIce Accretion2070RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2070 | 15.921 | 19.1182 | 23.166 | 26.2522 | 29.3278
Burk's FallsIce Accretion2075RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2075 | 15.9235 | 19.1395 | 23.21 | 26.3143 | 29.4109
Burk's FallsIce Accretion2080RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2080 | 15.9261 | 19.1608 | 23.254 | 26.3765 | 29.4941
Burk's FallsIce Accretion2085RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2085 | 15.9286 | 19.1821 | 23.298 | 26.4386 | 29.5772
Burk's FallsIce Accretion2090RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2090 | 15.9312 | 19.2034 | 23.342 | 26.5008 | 29.6604
Burk's FallsIce Accretion2095RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2095 | 15.9337 | 19.2247 | 23.386 | 26.5629 | 29.7436
Burk's FallsIce Accretion2100RCP4.5 | Burk's Falls | Ice Accretion | RCP4.5 | 2100 | 15.9363 | 19.246 | 23.43 | 26.6251 | 29.8267
Burk's FallsIce Accretion2023RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2023 | 15.2321 | 18.1504 | 21.868 | 24.7108 | 27.526
Burk's FallsIce Accretion2025RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2025 | 15.3086 | 18.2509 | 22 | 24.8641 | 27.7061
Burk's FallsIce Accretion2030RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2030 | 15.3852 | 18.3513 | 22.132 | 25.0174 | 27.8863
Burk's FallsIce Accretion2035RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2035 | 15.4617 | 18.4517 | 22.264 | 25.1707 | 28.0665
Burk's FallsIce Accretion2040RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2040 | 15.5382 | 18.5522 | 22.396 | 25.3241 | 28.2467
Burk's FallsIce Accretion2045RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2045 | 15.6148 | 18.6526 | 22.528 | 25.4774 | 28.4269
Burk's FallsIce Accretion2050RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2050 | 15.7373 | 18.8261 | 22.7612 | 25.755 | 28.7512
Burk's FallsIce Accretion2055RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2055 | 15.7832 | 18.8991 | 22.8624 | 25.8793 | 28.8953
Burk's FallsIce Accretion2060RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2060 | 15.8291 | 18.9721 | 22.9636 | 26.0036 | 29.0395
Burk's FallsIce Accretion2065RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2065 | 15.875 | 19.0452 | 23.0648 | 26.1279 | 29.1836
Burk's FallsIce Accretion2070RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2070 | 15.921 | 19.1182 | 23.166 | 26.2522 | 29.3278
Burk's FallsIce Accretion2075RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2075 | 15.9248 | 19.1502 | 23.232 | 26.3454 | 29.4525
Burk's FallsIce Accretion2080RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2080 | 15.9286 | 19.1821 | 23.298 | 26.4386 | 29.5772
Burk's FallsIce Accretion2085RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2085 | 15.9324 | 19.2141 | 23.364 | 26.5318 | 29.702
Burk's FallsIce Accretion2090RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2090 | 15.9618 | 19.2947 | 23.5107 | 26.7328 | 29.9468
Burk's FallsIce Accretion2095RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2095 | 15.9873 | 19.3434 | 23.5913 | 26.8405 | 30.067
Burk's FallsIce Accretion2100RCP6.0 | Burk's Falls | Ice Accretion | RCP6.0 | 2100 | 16.0128 | 19.3921 | 23.672 | 26.9482 | 30.1871
Burk's FallsIce Accretion2023RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2023 | 15.2321 | 18.1504 | 21.868 | 24.7108 | 27.526
Burk's FallsIce Accretion2025RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2025 | 15.3852 | 18.3513 | 22.132 | 25.0174 | 27.8863
Burk's FallsIce Accretion2030RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2030 | 15.5382 | 18.5522 | 22.396 | 25.3241 | 28.2467
Burk's FallsIce Accretion2035RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2035 | 15.6913 | 18.753 | 22.66 | 25.6307 | 28.607
Burk's FallsIce Accretion2040RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2040 | 15.7679 | 18.8748 | 22.8287 | 25.8378 | 28.8473
Burk's FallsIce Accretion2045RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2045 | 15.8444 | 18.9965 | 22.9973 | 26.045 | 29.0875
Burk's FallsIce Accretion2050RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2050 | 15.9261 | 19.1608 | 23.254 | 26.3765 | 29.4941
Burk's FallsIce Accretion2055RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2055 | 15.9312 | 19.2034 | 23.342 | 26.5008 | 29.6604
Burk's FallsIce Accretion2060RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2060 | 15.9618 | 19.2947 | 23.5107 | 26.7328 | 29.9468
Burk's FallsIce Accretion2065RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2065 | 15.9873 | 19.3434 | 23.5913 | 26.8405 | 30.067
Burk's FallsIce Accretion2070RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2070 | 15.8801 | 19.2521 | 23.5253 | 26.7908 | 30.03
Burk's FallsIce Accretion2075RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2075 | 15.7475 | 19.1121 | 23.3787 | 26.6333 | 29.8729
Burk's FallsIce Accretion2080RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2080 | 15.6148 | 18.9721 | 23.232 | 26.4759 | 29.7158
Burk's FallsIce Accretion2085RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2085 | 15.2091 | 18.5248 | 22.715 | 25.9166 | 29.106
Burk's FallsIce Accretion2090RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2090 | 14.8034 | 18.0774 | 22.198 | 25.3572 | 28.4962
Burk's FallsIce Accretion2095RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2095 | 14.8034 | 18.0774 | 22.198 | 25.3572 | 28.4962
Burk's FallsIce Accretion2100RCP8.5 | Burk's Falls | Ice Accretion | RCP8.5 | 2100 | 14.8034 | 18.0774 | 22.198 | 25.3572 | 28.4962
Burk's FallsWind2023RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2023 | 69.3273 | 74.6976 | 80.36 | 86.0109 | 91.6651
Burk's FallsWind2025RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2025 | 69.371 | 74.7559 | 80.436 | 86.1008 | 91.77
Burk's FallsWind2030RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2030 | 69.4148 | 74.8142 | 80.512 | 86.1906 | 91.8749
Burk's FallsWind2035RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2035 | 69.4585 | 74.8724 | 80.588 | 86.2805 | 91.9798
Burk's FallsWind2040RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2040 | 69.5023 | 74.9307 | 80.664 | 86.3704 | 92.0846
Burk's FallsWind2045RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2045 | 69.546 | 74.989 | 80.74 | 86.4603 | 92.1895
Burk's FallsWind2050RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2050 | 69.5842 | 75.0309 | 80.784 | 86.5091 | 92.2397
Burk's FallsWind2055RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2055 | 69.5787 | 75.0145 | 80.752 | 86.468 | 92.185
Burk's FallsWind2060RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2060 | 69.5732 | 74.9982 | 80.72 | 86.4269 | 92.1302
Burk's FallsWind2065RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2065 | 69.5677 | 74.9818 | 80.688 | 86.3858 | 92.0755
Burk's FallsWind2070RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2070 | 69.5621 | 74.9654 | 80.656 | 86.3447 | 92.0208
Burk's FallsWind2075RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2075 | 69.6347 | 75.0485 | 80.7533 | 86.4531 | 92.1424
Burk's FallsWind2080RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2080 | 69.7072 | 75.1316 | 80.8507 | 86.5616 | 92.264
Burk's FallsWind2085RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2085 | 69.7797 | 75.2147 | 80.948 | 86.67 | 92.3856
Burk's FallsWind2090RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2090 | 69.8523 | 75.2978 | 81.0453 | 86.7784 | 92.5072
Burk's FallsWind2095RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2095 | 69.9248 | 75.3808 | 81.1427 | 86.8869 | 92.6288
Burk's FallsWind2100RCP4.5 | Burk's Falls | Wind | RCP4.5 | 2100 | 69.9973 | 75.4639 | 81.24 | 86.9953 | 92.7504
Burk's FallsWind2023RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2023 | 69.3273 | 74.6976 | 80.36 | 86.0109 | 91.6651
Burk's FallsWind2025RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2025 | 69.371 | 74.7559 | 80.436 | 86.1008 | 91.77
Burk's FallsWind2030RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2030 | 69.4148 | 74.8142 | 80.512 | 86.1906 | 91.8749
Burk's FallsWind2035RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2035 | 69.4585 | 74.8724 | 80.588 | 86.2805 | 91.9798
Burk's FallsWind2040RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2040 | 69.5023 | 74.9307 | 80.664 | 86.3704 | 92.0846
Burk's FallsWind2045RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2045 | 69.546 | 74.989 | 80.74 | 86.4603 | 92.1895
Burk's FallsWind2050RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2050 | 69.5842 | 75.0309 | 80.784 | 86.5091 | 92.2397
Burk's FallsWind2055RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2055 | 69.5787 | 75.0145 | 80.752 | 86.468 | 92.185
Burk's FallsWind2060RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2060 | 69.5732 | 74.9982 | 80.72 | 86.4269 | 92.1302
Burk's FallsWind2065RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2065 | 69.5677 | 74.9818 | 80.688 | 86.3858 | 92.0755
Burk's FallsWind2070RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2070 | 69.5621 | 74.9654 | 80.656 | 86.3447 | 92.0208
Burk's FallsWind2075RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2075 | 69.6709 | 75.0901 | 80.802 | 86.5074 | 92.2032
Burk's FallsWind2080RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2080 | 69.7797 | 75.2147 | 80.948 | 86.67 | 92.3856
Burk's FallsWind2085RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2085 | 69.8885 | 75.3393 | 81.094 | 86.8326 | 92.568
Burk's FallsWind2090RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2090 | 69.8638 | 75.2978 | 81.0293 | 86.7499 | 92.4677
Burk's FallsWind2095RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2095 | 69.7302 | 75.1316 | 80.8187 | 86.5045 | 92.185
Burk's FallsWind2100RCP6.0 | Burk's Falls | Wind | RCP6.0 | 2100 | 69.5967 | 74.9654 | 80.608 | 86.2591 | 91.9022
Burk's FallsWind2023RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2023 | 69.3273 | 74.6976 | 80.36 | 86.0109 | 91.6651
Burk's FallsWind2025RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2025 | 69.4148 | 74.8142 | 80.512 | 86.1906 | 91.8749
Burk's FallsWind2030RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2030 | 69.5023 | 74.9307 | 80.664 | 86.3704 | 92.0846
Burk's FallsWind2035RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2035 | 69.5898 | 75.0473 | 80.816 | 86.5502 | 92.2944
Burk's FallsWind2040RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2040 | 69.5806 | 75.02 | 80.7627 | 86.4817 | 92.2032
Burk's FallsWind2045RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2045 | 69.5714 | 74.9927 | 80.7093 | 86.4132 | 92.112
Burk's FallsWind2050RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2050 | 69.7072 | 75.1316 | 80.8507 | 86.5616 | 92.264
Burk's FallsWind2055RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2055 | 69.8523 | 75.2978 | 81.0453 | 86.7784 | 92.5072
Burk's FallsWind2060RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2060 | 69.8638 | 75.2978 | 81.0293 | 86.7499 | 92.4677
Burk's FallsWind2065RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2065 | 69.7302 | 75.1316 | 80.8187 | 86.5045 | 92.185
Burk's FallsWind2070RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2070 | 69.7302 | 75.1266 | 80.808 | 86.4874 | 92.1637
Burk's FallsWind2075RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2075 | 69.8638 | 75.2878 | 81.008 | 86.7157 | 92.4251
Burk's FallsWind2080RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2080 | 69.9973 | 75.449 | 81.208 | 86.9439 | 92.6866
Burk's FallsWind2085RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2085 | 70.0284 | 75.4676 | 81.208 | 86.9311 | 92.6592
Burk's FallsWind2090RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2090 | 70.0595 | 75.4862 | 81.208 | 86.9182 | 92.6318
Burk's FallsWind2095RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2095 | 70.0595 | 75.4862 | 81.208 | 86.9182 | 92.6318
Burk's FallsWind2100RCP8.5 | Burk's Falls | Wind | RCP8.5 | 2100 | 70.0595 | 75.4862 | 81.208 | 86.9182 | 92.6318
BurlingtonIce Accretion2023RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
BurlingtonIce Accretion2025RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
BurlingtonIce Accretion2030RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
BurlingtonIce Accretion2035RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
BurlingtonIce Accretion2040RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
BurlingtonIce Accretion2045RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
BurlingtonIce Accretion2050RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
BurlingtonIce Accretion2055RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
BurlingtonIce Accretion2060RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
BurlingtonIce Accretion2065RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
BurlingtonIce Accretion2070RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
BurlingtonIce Accretion2075RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2075 | 15.5377 | 18.8894 | 23.1125 | 26.329 | 29.5313
BurlingtonIce Accretion2080RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2080 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
BurlingtonIce Accretion2085RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2085 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
BurlingtonIce Accretion2090RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2090 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
BurlingtonIce Accretion2095RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2095 | 15.3405 | 18.7511 | 23.0625 | 26.329 | 29.5942
BurlingtonIce Accretion2100RCP4.5 | Burlington | Ice Accretion | RCP4.5 | 2100 | 15.2912 | 18.7165 | 23.05 | 26.329 | 29.61
BurlingtonIce Accretion2023RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
BurlingtonIce Accretion2025RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
BurlingtonIce Accretion2030RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
BurlingtonIce Accretion2035RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
BurlingtonIce Accretion2040RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
BurlingtonIce Accretion2045RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
BurlingtonIce Accretion2050RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
BurlingtonIce Accretion2055RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
BurlingtonIce Accretion2060RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
BurlingtonIce Accretion2065RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
BurlingtonIce Accretion2070RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
BurlingtonIce Accretion2075RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2075 | 15.513 | 18.8721 | 23.1062 | 26.329 | 29.5391
BurlingtonIce Accretion2080RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2080 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
BurlingtonIce Accretion2085RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2085 | 15.3652 | 18.7684 | 23.0688 | 26.329 | 29.5864
BurlingtonIce Accretion2090RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2090 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
BurlingtonIce Accretion2095RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2095 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
BurlingtonIce Accretion2100RCP6.0 | Burlington | Ice Accretion | RCP6.0 | 2100 | 14.2127 | 17.596 | 21.825 | 25.0577 | 28.2555
BurlingtonIce Accretion2023RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
BurlingtonIce Accretion2025RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2025 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
BurlingtonIce Accretion2030RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2030 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
BurlingtonIce Accretion2035RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2035 | 16.6133 | 20.0652 | 24.425 | 27.7415 | 31.059
BurlingtonIce Accretion2040RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2040 | 16.2712 | 19.6848 | 23.9917 | 27.2707 | 30.5445
BurlingtonIce Accretion2045RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2045 | 15.9291 | 19.3044 | 23.5583 | 26.7998 | 30.03
BurlingtonIce Accretion2050RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2050 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
BurlingtonIce Accretion2055RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2055 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
BurlingtonIce Accretion2060RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2060 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
BurlingtonIce Accretion2065RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2065 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
BurlingtonIce Accretion2070RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2070 | 13.8125 | 17.1464 | 21.325 | 24.5022 | 27.657
BurlingtonIce Accretion2075RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2075 | 13.4124 | 16.6968 | 20.825 | 23.9466 | 27.0585
BurlingtonIce Accretion2080RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2080 | 13.0123 | 16.2473 | 20.325 | 23.391 | 26.46
BurlingtonIce Accretion2085RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2085 | 12.1338 | 15.1994 | 19.0625 | 21.9785 | 24.885
BurlingtonIce Accretion2090RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2090 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
BurlingtonIce Accretion2095RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2095 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
BurlingtonIce Accretion2100RCP8.5 | Burlington | Ice Accretion | RCP8.5 | 2100 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
BurlingtonWind2023RCP4.5 | Burlington | Wind | RCP4.5 | 2023 | 81.5651 | 87.9008 | 94.5828 | 101.2539 | 107.9208
BurlingtonWind2025RCP4.5 | Burlington | Wind | RCP4.5 | 2025 | 81.5948 | 87.9445 | 94.6455 | 101.3327 | 108.0155
BurlingtonWind2030RCP4.5 | Burlington | Wind | RCP4.5 | 2030 | 81.6246 | 87.9882 | 94.7081 | 101.4115 | 108.1102
BurlingtonWind2035RCP4.5 | Burlington | Wind | RCP4.5 | 2035 | 81.6544 | 88.0319 | 94.7708 | 101.4902 | 108.2048
BurlingtonWind2040RCP4.5 | Burlington | Wind | RCP4.5 | 2040 | 81.6841 | 88.0756 | 94.8335 | 101.569 | 108.2995
BurlingtonWind2045RCP4.5 | Burlington | Wind | RCP4.5 | 2045 | 81.7139 | 88.1194 | 94.8961 | 101.6478 | 108.3941
BurlingtonWind2050RCP4.5 | Burlington | Wind | RCP4.5 | 2050 | 81.8086 | 88.2417 | 95.0547 | 101.8373 | 108.6152
BurlingtonWind2055RCP4.5 | Burlington | Wind | RCP4.5 | 2055 | 81.8735 | 88.3204 | 95.1506 | 101.9479 | 108.7417
BurlingtonWind2060RCP4.5 | Burlington | Wind | RCP4.5 | 2060 | 81.9384 | 88.3991 | 95.2464 | 102.0585 | 108.8681
BurlingtonWind2065RCP4.5 | Burlington | Wind | RCP4.5 | 2065 | 82.0034 | 88.4778 | 95.3423 | 102.1692 | 108.9946
BurlingtonWind2070RCP4.5 | Burlington | Wind | RCP4.5 | 2070 | 82.0683 | 88.5565 | 95.4382 | 102.2798 | 109.121
BurlingtonWind2075RCP4.5 | Burlington | Wind | RCP4.5 | 2075 | 82.1576 | 88.6818 | 95.609 | 102.4877 | 109.3675
BurlingtonWind2080RCP4.5 | Burlington | Wind | RCP4.5 | 2080 | 82.2469 | 88.8071 | 95.7797 | 102.6955 | 109.614
BurlingtonWind2085RCP4.5 | Burlington | Wind | RCP4.5 | 2085 | 82.3362 | 88.9324 | 95.9505 | 102.9034 | 109.8604
BurlingtonWind2090RCP4.5 | Burlington | Wind | RCP4.5 | 2090 | 82.4254 | 89.0577 | 96.1213 | 103.1113 | 110.1069
BurlingtonWind2095RCP4.5 | Burlington | Wind | RCP4.5 | 2095 | 82.5147 | 89.183 | 96.292 | 103.3191 | 110.3534
BurlingtonWind2100RCP4.5 | Burlington | Wind | RCP4.5 | 2100 | 82.604 | 89.3083 | 96.4628 | 103.527 | 110.5998
BurlingtonWind2023RCP6.0 | Burlington | Wind | RCP6.0 | 2023 | 81.5651 | 87.9008 | 94.5828 | 101.2539 | 107.9208
BurlingtonWind2025RCP6.0 | Burlington | Wind | RCP6.0 | 2025 | 81.5948 | 87.9445 | 94.6455 | 101.3327 | 108.0155
BurlingtonWind2030RCP6.0 | Burlington | Wind | RCP6.0 | 2030 | 81.6246 | 87.9882 | 94.7081 | 101.4115 | 108.1102
BurlingtonWind2035RCP6.0 | Burlington | Wind | RCP6.0 | 2035 | 81.6544 | 88.0319 | 94.7708 | 101.4902 | 108.2048
BurlingtonWind2040RCP6.0 | Burlington | Wind | RCP6.0 | 2040 | 81.6841 | 88.0756 | 94.8335 | 101.569 | 108.2995
BurlingtonWind2045RCP6.0 | Burlington | Wind | RCP6.0 | 2045 | 81.7139 | 88.1194 | 94.8961 | 101.6478 | 108.3941
BurlingtonWind2050RCP6.0 | Burlington | Wind | RCP6.0 | 2050 | 81.8086 | 88.2417 | 95.0547 | 101.8373 | 108.6152
BurlingtonWind2055RCP6.0 | Burlington | Wind | RCP6.0 | 2055 | 81.8735 | 88.3204 | 95.1506 | 101.9479 | 108.7417
BurlingtonWind2060RCP6.0 | Burlington | Wind | RCP6.0 | 2060 | 81.9384 | 88.3991 | 95.2464 | 102.0585 | 108.8681
BurlingtonWind2065RCP6.0 | Burlington | Wind | RCP6.0 | 2065 | 82.0034 | 88.4778 | 95.3423 | 102.1692 | 108.9946
BurlingtonWind2070RCP6.0 | Burlington | Wind | RCP6.0 | 2070 | 82.0683 | 88.5565 | 95.4382 | 102.2798 | 109.121
BurlingtonWind2075RCP6.0 | Burlington | Wind | RCP6.0 | 2075 | 82.2022 | 88.7444 | 95.6944 | 102.5916 | 109.4907
BurlingtonWind2080RCP6.0 | Burlington | Wind | RCP6.0 | 2080 | 82.3362 | 88.9324 | 95.9505 | 102.9034 | 109.8604
BurlingtonWind2085RCP6.0 | Burlington | Wind | RCP6.0 | 2085 | 82.4701 | 89.1203 | 96.2066 | 103.2152 | 110.2301
BurlingtonWind2090RCP6.0 | Burlington | Wind | RCP6.0 | 2090 | 82.8854 | 89.6696 | 96.9234 | 104.0735 | 111.2357
BurlingtonWind2095RCP6.0 | Burlington | Wind | RCP6.0 | 2095 | 83.1668 | 90.0309 | 97.384 | 104.62 | 111.8715
BurlingtonWind2100RCP6.0 | Burlington | Wind | RCP6.0 | 2100 | 83.4482 | 90.3923 | 97.8446 | 105.1664 | 112.5073
BurlingtonWind2023RCP8.5 | Burlington | Wind | RCP8.5 | 2023 | 81.5651 | 87.9008 | 94.5828 | 101.2539 | 107.9208
BurlingtonWind2025RCP8.5 | Burlington | Wind | RCP8.5 | 2025 | 81.6246 | 87.9882 | 94.7081 | 101.4115 | 108.1102
BurlingtonWind2030RCP8.5 | Burlington | Wind | RCP8.5 | 2030 | 81.6841 | 88.0756 | 94.8335 | 101.569 | 108.2995
BurlingtonWind2035RCP8.5 | Burlington | Wind | RCP8.5 | 2035 | 81.7436 | 88.1631 | 94.9588 | 101.7266 | 108.4888
BurlingtonWind2040RCP8.5 | Burlington | Wind | RCP8.5 | 2040 | 81.8519 | 88.2942 | 95.1186 | 101.911 | 108.6995
BurlingtonWind2045RCP8.5 | Burlington | Wind | RCP8.5 | 2045 | 81.9601 | 88.4253 | 95.2784 | 102.0954 | 108.9103
BurlingtonWind2050RCP8.5 | Burlington | Wind | RCP8.5 | 2050 | 82.2469 | 88.8071 | 95.7797 | 102.6955 | 109.614
BurlingtonWind2055RCP8.5 | Burlington | Wind | RCP8.5 | 2055 | 82.4254 | 89.0577 | 96.1213 | 103.1113 | 110.1069
BurlingtonWind2060RCP8.5 | Burlington | Wind | RCP8.5 | 2060 | 82.8854 | 89.6696 | 96.9234 | 104.0735 | 111.2357
BurlingtonWind2065RCP8.5 | Burlington | Wind | RCP8.5 | 2065 | 83.1668 | 90.0309 | 97.384 | 104.62 | 111.8715
BurlingtonWind2070RCP8.5 | Burlington | Wind | RCP8.5 | 2070 | 83.6078 | 90.6225 | 98.1642 | 105.5587 | 112.9752
BurlingtonWind2075RCP8.5 | Burlington | Wind | RCP8.5 | 2075 | 83.7674 | 90.8527 | 98.4838 | 105.951 | 113.4431
BurlingtonWind2080RCP8.5 | Burlington | Wind | RCP8.5 | 2080 | 83.927 | 91.0829 | 98.8034 | 106.3432 | 113.9111
BurlingtonWind2085RCP8.5 | Burlington | Wind | RCP8.5 | 2085 | 84.1827 | 91.4151 | 99.2311 | 106.8562 | 114.5112
BurlingtonWind2090RCP8.5 | Burlington | Wind | RCP8.5 | 2090 | 84.4384 | 91.7473 | 99.6588 | 107.3692 | 115.1113
BurlingtonWind2095RCP8.5 | Burlington | Wind | RCP8.5 | 2095 | 84.4384 | 91.7473 | 99.6588 | 107.3692 | 115.1113
BurlingtonWind2100RCP8.5 | Burlington | Wind | RCP8.5 | 2100 | 84.4384 | 91.7473 | 99.6588 | 107.3692 | 115.1113
CFB BordenIce Accretion2023RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2023 | 14.9871 | 17.9313 | 21.648 | 24.4871 | 27.3042
CFB BordenIce Accretion2025RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2025 | 14.982 | 17.9283 | 21.6517 | 24.4954 | 27.3227
CFB BordenIce Accretion2030RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2030 | 14.9769 | 17.9252 | 21.6553 | 24.5037 | 27.3412
CFB BordenIce Accretion2035RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2035 | 14.9718 | 17.9222 | 21.659 | 24.512 | 27.3596
CFB BordenIce Accretion2040RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2040 | 14.9667 | 17.9191 | 21.6627 | 24.5202 | 27.3781
CFB BordenIce Accretion2045RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2045 | 14.9616 | 17.9161 | 21.6663 | 24.5285 | 27.3966
CFB BordenIce Accretion2050RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2050 | 14.9167 | 17.8838 | 21.6524 | 24.5269 | 27.4095
CFB BordenIce Accretion2055RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2055 | 14.8769 | 17.8546 | 21.6348 | 24.5169 | 27.404
CFB BordenIce Accretion2060RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2060 | 14.8371 | 17.8254 | 21.6172 | 24.507 | 27.3984
CFB BordenIce Accretion2065RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2065 | 14.7973 | 17.7962 | 21.5996 | 24.497 | 27.3929
CFB BordenIce Accretion2070RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2070 | 14.7575 | 17.767 | 21.582 | 24.4871 | 27.3874
CFB BordenIce Accretion2075RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2075 | 14.7575 | 17.7883 | 21.6297 | 24.5534 | 27.4705
CFB BordenIce Accretion2080RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2080 | 14.7575 | 17.8096 | 21.6773 | 24.6197 | 27.5537
CFB BordenIce Accretion2085RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2085 | 14.7575 | 17.8309 | 21.725 | 24.686 | 27.6368
CFB BordenIce Accretion2090RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2090 | 14.7575 | 17.8522 | 21.7727 | 24.7523 | 27.72
CFB BordenIce Accretion2095RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2095 | 14.7575 | 17.8735 | 21.8203 | 24.8186 | 27.8032
CFB BordenIce Accretion2100RCP4.5 | CFB Borden | Ice Accretion | RCP4.5 | 2100 | 14.7575 | 17.8948 | 21.868 | 24.8849 | 27.8863
CFB BordenIce Accretion2023RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2023 | 14.9871 | 17.9313 | 21.648 | 24.4871 | 27.3042
CFB BordenIce Accretion2025RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2025 | 14.982 | 17.9283 | 21.6517 | 24.4954 | 27.3227
CFB BordenIce Accretion2030RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2030 | 14.9769 | 17.9252 | 21.6553 | 24.5037 | 27.3412
CFB BordenIce Accretion2035RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2035 | 14.9718 | 17.9222 | 21.659 | 24.512 | 27.3596
CFB BordenIce Accretion2040RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2040 | 14.9667 | 17.9191 | 21.6627 | 24.5202 | 27.3781
CFB BordenIce Accretion2045RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2045 | 14.9616 | 17.9161 | 21.6663 | 24.5285 | 27.3966
CFB BordenIce Accretion2050RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2050 | 14.9167 | 17.8838 | 21.6524 | 24.5269 | 27.4095
CFB BordenIce Accretion2055RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2055 | 14.8769 | 17.8546 | 21.6348 | 24.5169 | 27.404
CFB BordenIce Accretion2060RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2060 | 14.8371 | 17.8254 | 21.6172 | 24.507 | 27.3984
CFB BordenIce Accretion2065RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2065 | 14.7973 | 17.7962 | 21.5996 | 24.497 | 27.3929
CFB BordenIce Accretion2070RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2070 | 14.7575 | 17.767 | 21.582 | 24.4871 | 27.3874
CFB BordenIce Accretion2075RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2075 | 14.7575 | 17.7989 | 21.6535 | 24.5865 | 27.5121
CFB BordenIce Accretion2080RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2080 | 14.7575 | 17.8309 | 21.725 | 24.686 | 27.6368
CFB BordenIce Accretion2085RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2085 | 14.7575 | 17.8628 | 21.7965 | 24.7854 | 27.7616
CFB BordenIce Accretion2090RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2090 | 14.5891 | 17.7244 | 21.6993 | 24.7108 | 27.72
CFB BordenIce Accretion2095RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2095 | 14.4207 | 17.5539 | 21.5307 | 24.5368 | 27.5537
CFB BordenIce Accretion2100RCP6.0 | CFB Borden | Ice Accretion | RCP6.0 | 2100 | 14.2523 | 17.3835 | 21.362 | 24.3628 | 27.3874
CFB BordenIce Accretion2023RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2023 | 14.9871 | 17.9313 | 21.648 | 24.4871 | 27.3042
CFB BordenIce Accretion2025RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2025 | 14.9769 | 17.9252 | 21.6553 | 24.5037 | 27.3412
CFB BordenIce Accretion2030RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2030 | 14.9667 | 17.9191 | 21.6627 | 24.5202 | 27.3781
CFB BordenIce Accretion2035RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2035 | 14.9565 | 17.9131 | 21.67 | 24.5368 | 27.4151
CFB BordenIce Accretion2040RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2040 | 14.8902 | 17.8644 | 21.6407 | 24.5202 | 27.4058
CFB BordenIce Accretion2045RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2045 | 14.8238 | 17.8157 | 21.6113 | 24.5037 | 27.3966
CFB BordenIce Accretion2050RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2050 | 14.7575 | 17.8096 | 21.6773 | 24.6197 | 27.5537
CFB BordenIce Accretion2055RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2055 | 14.7575 | 17.8522 | 21.7727 | 24.7523 | 27.72
CFB BordenIce Accretion2060RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2060 | 14.5891 | 17.7244 | 21.6993 | 24.7108 | 27.72
CFB BordenIce Accretion2065RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2065 | 14.4207 | 17.5539 | 21.5307 | 24.5368 | 27.5537
CFB BordenIce Accretion2070RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2070 | 14.0074 | 17.1401 | 21.1053 | 24.1059 | 27.1194
CFB BordenIce Accretion2075RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2075 | 13.7624 | 16.8966 | 20.8487 | 23.849 | 26.8514
CFB BordenIce Accretion2080RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2080 | 13.5175 | 16.6531 | 20.592 | 23.5921 | 26.5835
CFB BordenIce Accretion2085RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2085 | 12.8899 | 15.9227 | 19.745 | 22.6475 | 25.5301
CFB BordenIce Accretion2090RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2090 | 12.2622 | 15.1923 | 18.898 | 21.7028 | 24.4768
CFB BordenIce Accretion2095RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2095 | 12.2622 | 15.1923 | 18.898 | 21.7028 | 24.4768
CFB BordenIce Accretion2100RCP8.5 | CFB Borden | Ice Accretion | RCP8.5 | 2100 | 12.2622 | 15.1923 | 18.898 | 21.7028 | 24.4768
CFB BordenWind2023RCP4.5 | CFB Borden | Wind | RCP4.5 | 2023 | 76.374 | 82.2738 | 88.484 | 94.6967 | 100.9019
CFB BordenWind2025RCP4.5 | CFB Borden | Wind | RCP4.5 | 2025 | 76.3955 | 82.301 | 88.5192 | 94.7375 | 100.9503
CFB BordenWind2030RCP4.5 | CFB Borden | Wind | RCP4.5 | 2030 | 76.417 | 82.3283 | 88.5544 | 94.7783 | 100.9988
CFB BordenWind2035RCP4.5 | CFB Borden | Wind | RCP4.5 | 2035 | 76.4386 | 82.3556 | 88.5896 | 94.8191 | 101.0473
CFB BordenWind2040RCP4.5 | CFB Borden | Wind | RCP4.5 | 2040 | 76.4601 | 82.3829 | 88.6248 | 94.8599 | 101.0958
CFB BordenWind2045RCP4.5 | CFB Borden | Wind | RCP4.5 | 2045 | 76.4816 | 82.4102 | 88.66 | 94.9007 | 101.1443
CFB BordenWind2050RCP4.5 | CFB Borden | Wind | RCP4.5 | 2050 | 76.6232 | 82.5766 | 88.8554 | 95.1204 | 101.3914
CFB BordenWind2055RCP4.5 | CFB Borden | Wind | RCP4.5 | 2055 | 76.7433 | 82.7157 | 89.0155 | 95.2993 | 101.5901
CFB BordenWind2060RCP4.5 | CFB Borden | Wind | RCP4.5 | 2060 | 76.8633 | 82.8548 | 89.1757 | 95.4782 | 101.7887
CFB BordenWind2065RCP4.5 | CFB Borden | Wind | RCP4.5 | 2065 | 76.9834 | 82.9939 | 89.3358 | 95.6571 | 101.9873
CFB BordenWind2070RCP4.5 | CFB Borden | Wind | RCP4.5 | 2070 | 77.1035 | 83.1331 | 89.496 | 95.836 | 102.186
CFB BordenWind2075RCP4.5 | CFB Borden | Wind | RCP4.5 | 2075 | 77.1617 | 83.2095 | 89.5957 | 95.9553 | 102.3231
CFB BordenWind2080RCP4.5 | CFB Borden | Wind | RCP4.5 | 2080 | 77.22 | 83.2858 | 89.6955 | 96.0746 | 102.4602
CFB BordenWind2085RCP4.5 | CFB Borden | Wind | RCP4.5 | 2085 | 77.2782 | 83.3622 | 89.7952 | 96.1939 | 102.5973
CFB BordenWind2090RCP4.5 | CFB Borden | Wind | RCP4.5 | 2090 | 77.3365 | 83.4386 | 89.8949 | 96.3131 | 102.7344
CFB BordenWind2095RCP4.5 | CFB Borden | Wind | RCP4.5 | 2095 | 77.3947 | 83.515 | 89.9947 | 96.4324 | 102.8715
CFB BordenWind2100RCP4.5 | CFB Borden | Wind | RCP4.5 | 2100 | 77.453 | 83.5914 | 90.0944 | 96.5517 | 103.0086
CFB BordenWind2023RCP6.0 | CFB Borden | Wind | RCP6.0 | 2023 | 76.374 | 82.2738 | 88.484 | 94.6967 | 100.9019
CFB BordenWind2025RCP6.0 | CFB Borden | Wind | RCP6.0 | 2025 | 76.3955 | 82.301 | 88.5192 | 94.7375 | 100.9503
CFB BordenWind2030RCP6.0 | CFB Borden | Wind | RCP6.0 | 2030 | 76.417 | 82.3283 | 88.5544 | 94.7783 | 100.9988
CFB BordenWind2035RCP6.0 | CFB Borden | Wind | RCP6.0 | 2035 | 76.4386 | 82.3556 | 88.5896 | 94.8191 | 101.0473
CFB BordenWind2040RCP6.0 | CFB Borden | Wind | RCP6.0 | 2040 | 76.4601 | 82.3829 | 88.6248 | 94.8599 | 101.0958
CFB BordenWind2045RCP6.0 | CFB Borden | Wind | RCP6.0 | 2045 | 76.4816 | 82.4102 | 88.66 | 94.9007 | 101.1443
CFB BordenWind2050RCP6.0 | CFB Borden | Wind | RCP6.0 | 2050 | 76.6232 | 82.5766 | 88.8554 | 95.1204 | 101.3914
CFB BordenWind2055RCP6.0 | CFB Borden | Wind | RCP6.0 | 2055 | 76.7433 | 82.7157 | 89.0155 | 95.2993 | 101.5901
CFB BordenWind2060RCP6.0 | CFB Borden | Wind | RCP6.0 | 2060 | 76.8633 | 82.8548 | 89.1757 | 95.4782 | 101.7887
CFB BordenWind2065RCP6.0 | CFB Borden | Wind | RCP6.0 | 2065 | 76.9834 | 82.9939 | 89.3358 | 95.6571 | 101.9873
CFB BordenWind2070RCP6.0 | CFB Borden | Wind | RCP6.0 | 2070 | 77.1035 | 83.1331 | 89.496 | 95.836 | 102.186
CFB BordenWind2075RCP6.0 | CFB Borden | Wind | RCP6.0 | 2075 | 77.1908 | 83.2476 | 89.6456 | 96.015 | 102.3916
CFB BordenWind2080RCP6.0 | CFB Borden | Wind | RCP6.0 | 2080 | 77.2782 | 83.3622 | 89.7952 | 96.1939 | 102.5973
CFB BordenWind2085RCP6.0 | CFB Borden | Wind | RCP6.0 | 2085 | 77.3656 | 83.4768 | 89.9448 | 96.3728 | 102.8029
CFB BordenWind2090RCP6.0 | CFB Borden | Wind | RCP6.0 | 2090 | 77.7291 | 83.9242 | 90.4933 | 97.0099 | 103.5302
CFB BordenWind2095RCP6.0 | CFB Borden | Wind | RCP6.0 | 2095 | 78.0052 | 84.257 | 90.8923 | 97.4682 | 104.0519
CFB BordenWind2100RCP6.0 | CFB Borden | Wind | RCP6.0 | 2100 | 78.2812 | 84.5898 | 91.2912 | 97.9264 | 104.5736
CFB BordenWind2023RCP8.5 | CFB Borden | Wind | RCP8.5 | 2023 | 76.374 | 82.2738 | 88.484 | 94.6967 | 100.9019
CFB BordenWind2025RCP8.5 | CFB Borden | Wind | RCP8.5 | 2025 | 76.417 | 82.3283 | 88.5544 | 94.7783 | 100.9988
CFB BordenWind2030RCP8.5 | CFB Borden | Wind | RCP8.5 | 2030 | 76.4601 | 82.3829 | 88.6248 | 94.8599 | 101.0958
CFB BordenWind2035RCP8.5 | CFB Borden | Wind | RCP8.5 | 2035 | 76.5032 | 82.4374 | 88.6952 | 94.9415 | 101.1928
CFB BordenWind2040RCP8.5 | CFB Borden | Wind | RCP8.5 | 2040 | 76.7033 | 82.6693 | 88.9621 | 95.2397 | 101.5238
CFB BordenWind2045RCP8.5 | CFB Borden | Wind | RCP8.5 | 2045 | 76.9034 | 82.9012 | 89.2291 | 95.5379 | 101.8549
CFB BordenWind2050RCP8.5 | CFB Borden | Wind | RCP8.5 | 2050 | 77.22 | 83.2858 | 89.6955 | 96.0746 | 102.4602
CFB BordenWind2055RCP8.5 | CFB Borden | Wind | RCP8.5 | 2055 | 77.3365 | 83.4386 | 89.8949 | 96.3131 | 102.7344
CFB BordenWind2060RCP8.5 | CFB Borden | Wind | RCP8.5 | 2060 | 77.7291 | 83.9242 | 90.4933 | 97.0099 | 103.5302
CFB BordenWind2065RCP8.5 | CFB Borden | Wind | RCP8.5 | 2065 | 78.0052 | 84.257 | 90.8923 | 97.4682 | 104.0519
CFB BordenWind2070RCP8.5 | CFB Borden | Wind | RCP8.5 | 2070 | 78.4282 | 84.7671 | 91.5112 | 98.1806 | 104.8612
CFB BordenWind2075RCP8.5 | CFB Borden | Wind | RCP8.5 | 2075 | 78.5751 | 84.9445 | 91.7312 | 98.4349 | 105.1487
CFB BordenWind2080RCP8.5 | CFB Borden | Wind | RCP8.5 | 2080 | 78.722 | 85.1218 | 91.9512 | 98.6891 | 105.4363
CFB BordenWind2085RCP8.5 | CFB Borden | Wind | RCP8.5 | 2085 | 78.7524 | 85.1545 | 91.982 | 98.7221 | 105.4664
CFB BordenWind2090RCP8.5 | CFB Borden | Wind | RCP8.5 | 2090 | 78.7828 | 85.1873 | 92.0128 | 98.755 | 105.4965
CFB BordenWind2095RCP8.5 | CFB Borden | Wind | RCP8.5 | 2095 | 78.7828 | 85.1873 | 92.0128 | 98.755 | 105.4965
CFB BordenWind2100RCP8.5 | CFB Borden | Wind | RCP8.5 | 2100 | 78.7828 | 85.1873 | 92.0128 | 98.755 | 105.4965
CambridgeIce Accretion2023RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
CambridgeIce Accretion2025RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2025 | 17.3208 | 20.7984 | 25.1958 | 28.5655 | 31.92
CambridgeIce Accretion2030RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2030 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
CambridgeIce Accretion2035RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2035 | 17.3788 | 20.8953 | 25.3375 | 28.7444 | 32.13
CambridgeIce Accretion2040RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2040 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
CambridgeIce Accretion2045RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2045 | 17.4367 | 20.9921 | 25.4792 | 28.9233 | 32.34
CambridgeIce Accretion2050RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2050 | 17.4101 | 20.9907 | 25.51 | 28.9788 | 32.4198
CambridgeIce Accretion2055RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2055 | 17.3544 | 20.9409 | 25.47 | 28.9449 | 32.3946
CambridgeIce Accretion2060RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2060 | 17.2987 | 20.8911 | 25.43 | 28.911 | 32.3694
CambridgeIce Accretion2065RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2065 | 17.2431 | 20.8413 | 25.39 | 28.8771 | 32.3442
CambridgeIce Accretion2070RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2070 | 17.1874 | 20.7915 | 25.35 | 28.8432 | 32.319
CambridgeIce Accretion2075RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2075 | 17.1555 | 20.7846 | 25.3708 | 28.8809 | 32.3768
CambridgeIce Accretion2080RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2080 | 17.1236 | 20.7777 | 25.3917 | 28.9186 | 32.4345
CambridgeIce Accretion2085RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2085 | 17.0917 | 20.7707 | 25.4125 | 28.9562 | 32.4922
CambridgeIce Accretion2090RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2090 | 17.0598 | 20.7638 | 25.4333 | 28.9939 | 32.55
CambridgeIce Accretion2095RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2095 | 17.0279 | 20.7569 | 25.4542 | 29.0316 | 32.6077
CambridgeIce Accretion2100RCP4.5 | Cambridge | Ice Accretion | RCP4.5 | 2100 | 16.996 | 20.75 | 25.475 | 29.0692 | 32.6655
CambridgeIce Accretion2023RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
CambridgeIce Accretion2025RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2025 | 17.3208 | 20.7984 | 25.1958 | 28.5655 | 31.92
CambridgeIce Accretion2030RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2030 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
CambridgeIce Accretion2035RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2035 | 17.3788 | 20.8953 | 25.3375 | 28.7444 | 32.13
CambridgeIce Accretion2040RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2040 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
CambridgeIce Accretion2045RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2045 | 17.4367 | 20.9921 | 25.4792 | 28.9233 | 32.34
CambridgeIce Accretion2050RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2050 | 17.4101 | 20.9907 | 25.51 | 28.9788 | 32.4198
CambridgeIce Accretion2055RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2055 | 17.3544 | 20.9409 | 25.47 | 28.9449 | 32.3946
CambridgeIce Accretion2060RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2060 | 17.2987 | 20.8911 | 25.43 | 28.911 | 32.3694
CambridgeIce Accretion2065RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2065 | 17.2431 | 20.8413 | 25.39 | 28.8771 | 32.3442
CambridgeIce Accretion2070RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2070 | 17.1874 | 20.7915 | 25.35 | 28.8432 | 32.319
CambridgeIce Accretion2075RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2075 | 17.1396 | 20.7811 | 25.3813 | 28.8997 | 32.4056
CambridgeIce Accretion2080RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2080 | 17.0917 | 20.7707 | 25.4125 | 28.9562 | 32.4922
CambridgeIce Accretion2085RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2085 | 17.0439 | 20.7604 | 25.4437 | 29.0127 | 32.5789
CambridgeIce Accretion2090RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2090 | 16.6887 | 20.4249 | 25.1333 | 28.7114 | 32.298
CambridgeIce Accretion2095RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2095 | 16.3814 | 20.0998 | 24.7917 | 28.3536 | 31.9305
CambridgeIce Accretion2100RCP6.0 | Cambridge | Ice Accretion | RCP6.0 | 2100 | 16.074 | 19.7747 | 24.45 | 27.9957 | 31.563
CambridgeIce Accretion2023RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
CambridgeIce Accretion2025RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2025 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
CambridgeIce Accretion2030RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2030 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
CambridgeIce Accretion2035RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2035 | 17.4657 | 21.0405 | 25.55 | 29.0127 | 32.445
CambridgeIce Accretion2040RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2040 | 17.373 | 20.9575 | 25.4833 | 28.9562 | 32.403
CambridgeIce Accretion2045RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2045 | 17.2802 | 20.8745 | 25.4167 | 28.8997 | 32.361
CambridgeIce Accretion2050RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2050 | 17.1236 | 20.7777 | 25.3917 | 28.9186 | 32.4345
CambridgeIce Accretion2055RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2055 | 17.0598 | 20.7638 | 25.4333 | 28.9939 | 32.55
CambridgeIce Accretion2060RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2060 | 16.6887 | 20.4249 | 25.1333 | 28.7114 | 32.298
CambridgeIce Accretion2065RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2065 | 16.3814 | 20.0998 | 24.7917 | 28.3536 | 31.9305
CambridgeIce Accretion2070RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2070 | 15.6507 | 19.3182 | 23.95 | 27.4684 | 30.9855
CambridgeIce Accretion2075RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2075 | 15.2274 | 18.8617 | 23.45 | 26.9411 | 30.408
CambridgeIce Accretion2080RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2080 | 14.8041 | 18.4052 | 22.95 | 26.4137 | 29.8305
CambridgeIce Accretion2085RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2085 | 13.9778 | 17.43 | 21.7875 | 25.086 | 28.3657
CambridgeIce Accretion2090RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2090 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
CambridgeIce Accretion2095RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2095 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
CambridgeIce Accretion2100RCP8.5 | Cambridge | Ice Accretion | RCP8.5 | 2100 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
CambridgeWind2023RCP4.5 | Cambridge | Wind | RCP4.5 | 2023 | 83.2259 | 89.6371 | 96.384 | 103.1309 | 109.8887
CambridgeWind2025RCP4.5 | Cambridge | Wind | RCP4.5 | 2025 | 83.2839 | 89.716 | 96.4912 | 103.261 | 110.0419
CambridgeWind2030RCP4.5 | Cambridge | Wind | RCP4.5 | 2030 | 83.3419 | 89.7948 | 96.5984 | 103.3911 | 110.1951
CambridgeWind2035RCP4.5 | Cambridge | Wind | RCP4.5 | 2035 | 83.4 | 89.8737 | 96.7056 | 103.5212 | 110.3484
CambridgeWind2040RCP4.5 | Cambridge | Wind | RCP4.5 | 2040 | 83.458 | 89.9526 | 96.8128 | 103.6513 | 110.5016
CambridgeWind2045RCP4.5 | Cambridge | Wind | RCP4.5 | 2045 | 83.516 | 90.0314 | 96.92 | 103.7814 | 110.6548
CambridgeWind2050RCP4.5 | Cambridge | Wind | RCP4.5 | 2050 | 83.6387 | 90.1889 | 97.1194 | 104.0184 | 110.9284
CambridgeWind2055RCP4.5 | Cambridge | Wind | RCP4.5 | 2055 | 83.7034 | 90.2674 | 97.2115 | 104.1252 | 111.0488
CambridgeWind2060RCP4.5 | Cambridge | Wind | RCP4.5 | 2060 | 83.768 | 90.346 | 97.3037 | 104.232 | 111.1692
CambridgeWind2065RCP4.5 | Cambridge | Wind | RCP4.5 | 2065 | 83.8327 | 90.4246 | 97.3958 | 104.3389 | 111.2895
CambridgeWind2070RCP4.5 | Cambridge | Wind | RCP4.5 | 2070 | 83.8973 | 90.5031 | 97.488 | 104.4457 | 111.4099
CambridgeWind2075RCP4.5 | Cambridge | Wind | RCP4.5 | 2075 | 83.9678 | 90.6043 | 97.632 | 104.622 | 111.6215
CambridgeWind2080RCP4.5 | Cambridge | Wind | RCP4.5 | 2080 | 84.0383 | 90.7055 | 97.776 | 104.7984 | 111.8331
CambridgeWind2085RCP4.5 | Cambridge | Wind | RCP4.5 | 2085 | 84.1087 | 90.8067 | 97.92 | 104.9747 | 112.0447
CambridgeWind2090RCP4.5 | Cambridge | Wind | RCP4.5 | 2090 | 84.1792 | 90.9079 | 98.064 | 105.151 | 112.2563
CambridgeWind2095RCP4.5 | Cambridge | Wind | RCP4.5 | 2095 | 84.2496 | 91.0091 | 98.208 | 105.3274 | 112.4678
CambridgeWind2100RCP4.5 | Cambridge | Wind | RCP4.5 | 2100 | 84.3201 | 91.1102 | 98.352 | 105.5037 | 112.6794
CambridgeWind2023RCP6.0 | Cambridge | Wind | RCP6.0 | 2023 | 83.2259 | 89.6371 | 96.384 | 103.1309 | 109.8887
CambridgeWind2025RCP6.0 | Cambridge | Wind | RCP6.0 | 2025 | 83.2839 | 89.716 | 96.4912 | 103.261 | 110.0419
CambridgeWind2030RCP6.0 | Cambridge | Wind | RCP6.0 | 2030 | 83.3419 | 89.7948 | 96.5984 | 103.3911 | 110.1951
CambridgeWind2035RCP6.0 | Cambridge | Wind | RCP6.0 | 2035 | 83.4 | 89.8737 | 96.7056 | 103.5212 | 110.3484
CambridgeWind2040RCP6.0 | Cambridge | Wind | RCP6.0 | 2040 | 83.458 | 89.9526 | 96.8128 | 103.6513 | 110.5016
CambridgeWind2045RCP6.0 | Cambridge | Wind | RCP6.0 | 2045 | 83.516 | 90.0314 | 96.92 | 103.7814 | 110.6548
CambridgeWind2050RCP6.0 | Cambridge | Wind | RCP6.0 | 2050 | 83.6387 | 90.1889 | 97.1194 | 104.0184 | 110.9284
CambridgeWind2055RCP6.0 | Cambridge | Wind | RCP6.0 | 2055 | 83.7034 | 90.2674 | 97.2115 | 104.1252 | 111.0488
CambridgeWind2060RCP6.0 | Cambridge | Wind | RCP6.0 | 2060 | 83.768 | 90.346 | 97.3037 | 104.232 | 111.1692
CambridgeWind2065RCP6.0 | Cambridge | Wind | RCP6.0 | 2065 | 83.8327 | 90.4246 | 97.3958 | 104.3389 | 111.2895
CambridgeWind2070RCP6.0 | Cambridge | Wind | RCP6.0 | 2070 | 83.8973 | 90.5031 | 97.488 | 104.4457 | 111.4099
CambridgeWind2075RCP6.0 | Cambridge | Wind | RCP6.0 | 2075 | 84.003 | 90.6549 | 97.704 | 104.7102 | 111.7273
CambridgeWind2080RCP6.0 | Cambridge | Wind | RCP6.0 | 2080 | 84.1087 | 90.8067 | 97.92 | 104.9747 | 112.0447
CambridgeWind2085RCP6.0 | Cambridge | Wind | RCP6.0 | 2085 | 84.2144 | 90.9585 | 98.136 | 105.2392 | 112.362
CambridgeWind2090RCP6.0 | Cambridge | Wind | RCP6.0 | 2090 | 84.6047 | 91.4674 | 98.7968 | 106.0276 | 113.2813
CambridgeWind2095RCP6.0 | Cambridge | Wind | RCP6.0 | 2095 | 84.8893 | 91.8245 | 99.2416 | 106.5515 | 113.8833
CambridgeWind2100RCP6.0 | Cambridge | Wind | RCP6.0 | 2100 | 85.1739 | 92.1816 | 99.6864 | 107.0753 | 114.4852
CambridgeWind2023RCP8.5 | Cambridge | Wind | RCP8.5 | 2023 | 83.2259 | 89.6371 | 96.384 | 103.1309 | 109.8887
CambridgeWind2025RCP8.5 | Cambridge | Wind | RCP8.5 | 2025 | 83.3419 | 89.7948 | 96.5984 | 103.3911 | 110.1951
CambridgeWind2030RCP8.5 | Cambridge | Wind | RCP8.5 | 2030 | 83.458 | 89.9526 | 96.8128 | 103.6513 | 110.5016
CambridgeWind2035RCP8.5 | Cambridge | Wind | RCP8.5 | 2035 | 83.574 | 90.1103 | 97.0272 | 103.9116 | 110.808
CambridgeWind2040RCP8.5 | Cambridge | Wind | RCP8.5 | 2040 | 83.6818 | 90.2412 | 97.1808 | 104.0896 | 111.0086
CambridgeWind2045RCP8.5 | Cambridge | Wind | RCP8.5 | 2045 | 83.7896 | 90.3722 | 97.3344 | 104.2676 | 111.2093
CambridgeWind2050RCP8.5 | Cambridge | Wind | RCP8.5 | 2050 | 84.0383 | 90.7055 | 97.776 | 104.7984 | 111.8331
CambridgeWind2055RCP8.5 | Cambridge | Wind | RCP8.5 | 2055 | 84.1792 | 90.9079 | 98.064 | 105.151 | 112.2563
CambridgeWind2060RCP8.5 | Cambridge | Wind | RCP8.5 | 2060 | 84.6047 | 91.4674 | 98.7968 | 106.0276 | 113.2813
CambridgeWind2065RCP8.5 | Cambridge | Wind | RCP8.5 | 2065 | 84.8893 | 91.8245 | 99.2416 | 106.5515 | 113.8833
CambridgeWind2070RCP8.5 | Cambridge | Wind | RCP8.5 | 2070 | 85.4254 | 92.5209 | 100.1312 | 107.6129 | 115.1163
CambridgeWind2075RCP8.5 | Cambridge | Wind | RCP8.5 | 2075 | 85.6768 | 92.8601 | 100.576 | 108.1505 | 115.7474
CambridgeWind2080RCP8.5 | Cambridge | Wind | RCP8.5 | 2080 | 85.9282 | 93.1994 | 101.0208 | 108.688 | 116.3785
CambridgeWind2085RCP8.5 | Cambridge | Wind | RCP8.5 | 2085 | 86.1728 | 93.5253 | 101.4528 | 109.2016 | 116.9804
CambridgeWind2090RCP8.5 | Cambridge | Wind | RCP8.5 | 2090 | 86.4173 | 93.8511 | 101.8848 | 109.7152 | 117.5823
CambridgeWind2095RCP8.5 | Cambridge | Wind | RCP8.5 | 2095 | 86.4173 | 93.8511 | 101.8848 | 109.7152 | 117.5823
CambridgeWind2100RCP8.5 | Cambridge | Wind | RCP8.5 | 2100 | 86.4173 | 93.8511 | 101.8848 | 109.7152 | 117.5823
CampbellfordIce Accretion2023RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3065 | 31.563
CampbellfordIce Accretion2025RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2025 | 17.544 | 20.9091 | 25.1667 | 28.4148 | 31.6837
CampbellfordIce Accretion2030RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2030 | 17.6049 | 20.9852 | 25.2583 | 28.5231 | 31.8045
CampbellfordIce Accretion2035RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2035 | 17.6658 | 21.0613 | 25.35 | 28.6314 | 31.9252
CampbellfordIce Accretion2040RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2040 | 17.7267 | 21.1373 | 25.4417 | 28.7397 | 32.046
CampbellfordIce Accretion2045RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2045 | 17.7876 | 21.2134 | 25.5333 | 28.848 | 32.1667
CampbellfordIce Accretion2050RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2050 | 17.8032 | 21.248 | 25.595 | 28.928 | 32.2623
CampbellfordIce Accretion2055RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2055 | 17.758 | 21.2065 | 25.565 | 28.8997 | 32.2371
CampbellfordIce Accretion2060RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2060 | 17.7128 | 21.165 | 25.535 | 28.8715 | 32.2119
CampbellfordIce Accretion2065RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2065 | 17.6675 | 21.1235 | 25.505 | 28.8432 | 32.1867
CampbellfordIce Accretion2070RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2070 | 17.6223 | 21.082 | 25.475 | 28.815 | 32.1615
CampbellfordIce Accretion2075RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2075 | 17.6919 | 21.1927 | 25.6375 | 29.0175 | 32.403
CampbellfordIce Accretion2080RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2080 | 17.7615 | 21.3033 | 25.8 | 29.2199 | 32.6445
CampbellfordIce Accretion2085RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2085 | 17.8311 | 21.414 | 25.9625 | 29.4224 | 32.886
CampbellfordIce Accretion2090RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2090 | 17.9006 | 21.5247 | 26.125 | 29.6248 | 33.1275
CampbellfordIce Accretion2095RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2095 | 17.9702 | 21.6353 | 26.2875 | 29.8273 | 33.369
CampbellfordIce Accretion2100RCP4.5 | Campbellford | Ice Accretion | RCP4.5 | 2100 | 18.0398 | 21.746 | 26.45 | 30.0297 | 33.6105
CampbellfordIce Accretion2023RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3065 | 31.563
CampbellfordIce Accretion2025RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2025 | 17.544 | 20.9091 | 25.1667 | 28.4148 | 31.6837
CampbellfordIce Accretion2030RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2030 | 17.6049 | 20.9852 | 25.2583 | 28.5231 | 31.8045
CampbellfordIce Accretion2035RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2035 | 17.6658 | 21.0613 | 25.35 | 28.6314 | 31.9252
CampbellfordIce Accretion2040RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2040 | 17.7267 | 21.1373 | 25.4417 | 28.7397 | 32.046
CampbellfordIce Accretion2045RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2045 | 17.7876 | 21.2134 | 25.5333 | 28.848 | 32.1667
CampbellfordIce Accretion2050RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2050 | 17.8032 | 21.248 | 25.595 | 28.928 | 32.2623
CampbellfordIce Accretion2055RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2055 | 17.758 | 21.2065 | 25.565 | 28.8997 | 32.2371
CampbellfordIce Accretion2060RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2060 | 17.7128 | 21.165 | 25.535 | 28.8715 | 32.2119
CampbellfordIce Accretion2065RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2065 | 17.6675 | 21.1235 | 25.505 | 28.8432 | 32.1867
CampbellfordIce Accretion2070RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2070 | 17.6223 | 21.082 | 25.475 | 28.815 | 32.1615
CampbellfordIce Accretion2075RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2075 | 17.7267 | 21.248 | 25.7188 | 29.1187 | 32.5237
CampbellfordIce Accretion2080RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2080 | 17.8311 | 21.414 | 25.9625 | 29.4224 | 32.886
CampbellfordIce Accretion2085RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2085 | 17.9354 | 21.58 | 26.2063 | 29.7261 | 33.2482
CampbellfordIce Accretion2090RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2090 | 17.7499 | 21.4486 | 26.1333 | 29.7002 | 33.264
CampbellfordIce Accretion2095RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2095 | 17.4599 | 21.1512 | 25.8167 | 29.3706 | 32.9175
CampbellfordIce Accretion2100RCP6.0 | Campbellford | Ice Accretion | RCP6.0 | 2100 | 17.17 | 20.8537 | 25.5 | 29.041 | 32.571
CampbellfordIce Accretion2023RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3065 | 31.563
CampbellfordIce Accretion2025RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2025 | 17.6049 | 20.9852 | 25.2583 | 28.5231 | 31.8045
CampbellfordIce Accretion2030RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2030 | 17.7267 | 21.1373 | 25.4417 | 28.7397 | 32.046
CampbellfordIce Accretion2035RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2035 | 17.8485 | 21.2895 | 25.625 | 28.9562 | 32.2875
CampbellfordIce Accretion2040RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2040 | 17.7731 | 21.2203 | 25.575 | 28.9092 | 32.2455
CampbellfordIce Accretion2045RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2045 | 17.6977 | 21.1512 | 25.525 | 28.8621 | 32.2035
CampbellfordIce Accretion2050RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2050 | 17.7615 | 21.3033 | 25.8 | 29.2199 | 32.6445
CampbellfordIce Accretion2055RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2055 | 17.9006 | 21.5247 | 26.125 | 29.6248 | 33.1275
CampbellfordIce Accretion2060RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2060 | 17.7499 | 21.4486 | 26.1333 | 29.7002 | 33.264
CampbellfordIce Accretion2065RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2065 | 17.4599 | 21.1512 | 25.8167 | 29.3706 | 32.9175
CampbellfordIce Accretion2070RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2070 | 16.8801 | 20.5287 | 25.1417 | 28.6455 | 32.151
CampbellfordIce Accretion2075RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2075 | 16.5901 | 20.2036 | 24.7833 | 28.25 | 31.731
CampbellfordIce Accretion2080RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2080 | 16.3002 | 19.8785 | 24.425 | 27.8545 | 31.311
CampbellfordIce Accretion2085RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2085 | 15.6826 | 19.1626 | 23.5875 | 26.9222 | 30.2715
CampbellfordIce Accretion2090RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2090 | 15.0651 | 18.4468 | 22.75 | 25.99 | 29.232
CampbellfordIce Accretion2095RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2095 | 15.0651 | 18.4468 | 22.75 | 25.99 | 29.232
CampbellfordIce Accretion2100RCP8.5 | Campbellford | Ice Accretion | RCP8.5 | 2100 | 15.0651 | 18.4468 | 22.75 | 25.99 | 29.232
CampbellfordWind2023RCP4.5 | Campbellford | Wind | RCP4.5 | 2023 | 74.4377 | 80.2119 | 86.301 | 92.3697 | 98.4518
CampbellfordWind2025RCP4.5 | Campbellford | Wind | RCP4.5 | 2025 | 74.4674 | 80.2559 | 86.3612 | 92.4464 | 98.5433
CampbellfordWind2030RCP4.5 | Campbellford | Wind | RCP4.5 | 2030 | 74.4971 | 80.2999 | 86.4214 | 92.523 | 98.6348
CampbellfordWind2035RCP4.5 | Campbellford | Wind | RCP4.5 | 2035 | 74.5268 | 80.3439 | 86.4816 | 92.5997 | 98.7263
CampbellfordWind2040RCP4.5 | Campbellford | Wind | RCP4.5 | 2040 | 74.5565 | 80.3879 | 86.5418 | 92.6764 | 98.8178
CampbellfordWind2045RCP4.5 | Campbellford | Wind | RCP4.5 | 2045 | 74.5862 | 80.4319 | 86.602 | 92.7531 | 98.9093
CampbellfordWind2050RCP4.5 | Campbellford | Wind | RCP4.5 | 2050 | 74.5922 | 80.4311 | 86.5951 | 92.7414 | 98.891
CampbellfordWind2055RCP4.5 | Campbellford | Wind | RCP4.5 | 2055 | 74.5684 | 80.3863 | 86.528 | 92.6531 | 98.7812
CampbellfordWind2060RCP4.5 | Campbellford | Wind | RCP4.5 | 2060 | 74.5446 | 80.3415 | 86.461 | 92.5648 | 98.6714
CampbellfordWind2065RCP4.5 | Campbellford | Wind | RCP4.5 | 2065 | 74.5209 | 80.2967 | 86.3939 | 92.4764 | 98.5616
CampbellfordWind2070RCP4.5 | Campbellford | Wind | RCP4.5 | 2070 | 74.4971 | 80.2519 | 86.3268 | 92.3881 | 98.4518
CampbellfordWind2075RCP4.5 | Campbellford | Wind | RCP4.5 | 2075 | 74.4748 | 80.2266 | 86.2967 | 92.3543 | 98.4158
CampbellfordWind2080RCP4.5 | Campbellford | Wind | RCP4.5 | 2080 | 74.4526 | 80.2013 | 86.2666 | 92.3206 | 98.3799
CampbellfordWind2085RCP4.5 | Campbellford | Wind | RCP4.5 | 2085 | 74.4303 | 80.176 | 86.2365 | 92.2869 | 98.3439
CampbellfordWind2090RCP4.5 | Campbellford | Wind | RCP4.5 | 2090 | 74.408 | 80.1506 | 86.2064 | 92.2531 | 98.308
CampbellfordWind2095RCP4.5 | Campbellford | Wind | RCP4.5 | 2095 | 74.3857 | 80.1253 | 86.1763 | 92.2194 | 98.272
CampbellfordWind2100RCP4.5 | Campbellford | Wind | RCP4.5 | 2100 | 74.3635 | 80.1 | 86.1462 | 92.1856 | 98.2361
CampbellfordWind2023RCP6.0 | Campbellford | Wind | RCP6.0 | 2023 | 74.4377 | 80.2119 | 86.301 | 92.3697 | 98.4518
CampbellfordWind2025RCP6.0 | Campbellford | Wind | RCP6.0 | 2025 | 74.4674 | 80.2559 | 86.3612 | 92.4464 | 98.5433
CampbellfordWind2030RCP6.0 | Campbellford | Wind | RCP6.0 | 2030 | 74.4971 | 80.2999 | 86.4214 | 92.523 | 98.6348
CampbellfordWind2035RCP6.0 | Campbellford | Wind | RCP6.0 | 2035 | 74.5268 | 80.3439 | 86.4816 | 92.5997 | 98.7263
CampbellfordWind2040RCP6.0 | Campbellford | Wind | RCP6.0 | 2040 | 74.5565 | 80.3879 | 86.5418 | 92.6764 | 98.8178
CampbellfordWind2045RCP6.0 | Campbellford | Wind | RCP6.0 | 2045 | 74.5862 | 80.4319 | 86.602 | 92.7531 | 98.9093
CampbellfordWind2050RCP6.0 | Campbellford | Wind | RCP6.0 | 2050 | 74.5922 | 80.4311 | 86.5951 | 92.7414 | 98.891
CampbellfordWind2055RCP6.0 | Campbellford | Wind | RCP6.0 | 2055 | 74.5684 | 80.3863 | 86.528 | 92.6531 | 98.7812
CampbellfordWind2060RCP6.0 | Campbellford | Wind | RCP6.0 | 2060 | 74.5446 | 80.3415 | 86.461 | 92.5648 | 98.6714
CampbellfordWind2065RCP6.0 | Campbellford | Wind | RCP6.0 | 2065 | 74.5209 | 80.2967 | 86.3939 | 92.4764 | 98.5616
CampbellfordWind2070RCP6.0 | Campbellford | Wind | RCP6.0 | 2070 | 74.4971 | 80.2519 | 86.3268 | 92.3881 | 98.4518
CampbellfordWind2075RCP6.0 | Campbellford | Wind | RCP6.0 | 2075 | 74.4637 | 80.2139 | 86.2817 | 92.3375 | 98.3978
CampbellfordWind2080RCP6.0 | Campbellford | Wind | RCP6.0 | 2080 | 74.4303 | 80.176 | 86.2365 | 92.2869 | 98.3439
CampbellfordWind2085RCP6.0 | Campbellford | Wind | RCP6.0 | 2085 | 74.3969 | 80.138 | 86.1913 | 92.2362 | 98.29
CampbellfordWind2090RCP6.0 | Campbellford | Wind | RCP6.0 | 2090 | 74.3511 | 80.076 | 86.1061 | 92.1304 | 98.1642
CampbellfordWind2095RCP6.0 | Campbellford | Wind | RCP6.0 | 2095 | 74.3387 | 80.052 | 86.0659 | 92.0752 | 98.0923
CampbellfordWind2100RCP6.0 | Campbellford | Wind | RCP6.0 | 2100 | 74.3263 | 80.028 | 86.0258 | 92.02 | 98.0204
CampbellfordWind2023RCP8.5 | Campbellford | Wind | RCP8.5 | 2023 | 74.4377 | 80.2119 | 86.301 | 92.3697 | 98.4518
CampbellfordWind2025RCP8.5 | Campbellford | Wind | RCP8.5 | 2025 | 74.4971 | 80.2999 | 86.4214 | 92.523 | 98.6348
CampbellfordWind2030RCP8.5 | Campbellford | Wind | RCP8.5 | 2030 | 74.5565 | 80.3879 | 86.5418 | 92.6764 | 98.8178
CampbellfordWind2035RCP8.5 | Campbellford | Wind | RCP8.5 | 2035 | 74.6159 | 80.4759 | 86.6622 | 92.8298 | 99.0008
CampbellfordWind2040RCP8.5 | Campbellford | Wind | RCP8.5 | 2040 | 74.5763 | 80.4012 | 86.5504 | 92.6825 | 98.8178
CampbellfordWind2045RCP8.5 | Campbellford | Wind | RCP8.5 | 2045 | 74.5367 | 80.3266 | 86.4386 | 92.5353 | 98.6348
CampbellfordWind2050RCP8.5 | Campbellford | Wind | RCP8.5 | 2050 | 74.4526 | 80.2013 | 86.2666 | 92.3206 | 98.3799
CampbellfordWind2055RCP8.5 | Campbellford | Wind | RCP8.5 | 2055 | 74.408 | 80.1506 | 86.2064 | 92.2531 | 98.308
CampbellfordWind2060RCP8.5 | Campbellford | Wind | RCP8.5 | 2060 | 74.3511 | 80.076 | 86.1061 | 92.1304 | 98.1642
CampbellfordWind2065RCP8.5 | Campbellford | Wind | RCP8.5 | 2065 | 74.3387 | 80.052 | 86.0659 | 92.0752 | 98.0923
CampbellfordWind2070RCP8.5 | Campbellford | Wind | RCP8.5 | 2070 | 74.2941 | 79.9853 | 85.9713 | 91.9556 | 97.9452
CampbellfordWind2075RCP8.5 | Campbellford | Wind | RCP8.5 | 2075 | 74.262 | 79.9427 | 85.9169 | 91.8912 | 97.8701
CampbellfordWind2080RCP8.5 | Campbellford | Wind | RCP8.5 | 2080 | 74.2298 | 79.9 | 85.8624 | 91.8268 | 97.7949
CampbellfordWind2085RCP8.5 | Campbellford | Wind | RCP8.5 | 2085 | 74.1889 | 79.872 | 85.8495 | 91.8314 | 97.8096
CampbellfordWind2090RCP8.5 | Campbellford | Wind | RCP8.5 | 2090 | 74.1481 | 79.844 | 85.8366 | 91.836 | 97.8243
CampbellfordWind2095RCP8.5 | Campbellford | Wind | RCP8.5 | 2095 | 74.1481 | 79.844 | 85.8366 | 91.836 | 97.8243
CampbellfordWind2100RCP8.5 | Campbellford | Wind | RCP8.5 | 2100 | 74.1481 | 79.844 | 85.8366 | 91.836 | 97.8243
CanningtonIce Accretion2023RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
CanningtonIce Accretion2025RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
CanningtonIce Accretion2030RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
CanningtonIce Accretion2035RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
CanningtonIce Accretion2040RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
CanningtonIce Accretion2045RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
CanningtonIce Accretion2050RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
CanningtonIce Accretion2055RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
CanningtonIce Accretion2060RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
CanningtonIce Accretion2065RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
CanningtonIce Accretion2070RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
CanningtonIce Accretion2075RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2075 | 17.2744 | 20.8814 | 25.4167 | 28.8762 | 32.34
CanningtonIce Accretion2080RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2080 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
CanningtonIce Accretion2085RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2085 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
CanningtonIce Accretion2090RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2090 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
CanningtonIce Accretion2095RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2095 | 17.2048 | 20.9091 | 25.5833 | 29.121 | 32.676
CanningtonIce Accretion2100RCP4.5 | Cannington | Ice Accretion | RCP4.5 | 2100 | 17.1874 | 20.916 | 25.625 | 29.1822 | 32.76
CanningtonIce Accretion2023RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
CanningtonIce Accretion2025RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
CanningtonIce Accretion2030RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
CanningtonIce Accretion2035RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
CanningtonIce Accretion2040RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
CanningtonIce Accretion2045RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
CanningtonIce Accretion2050RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
CanningtonIce Accretion2055RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
CanningtonIce Accretion2060RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
CanningtonIce Accretion2065RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
CanningtonIce Accretion2070RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
CanningtonIce Accretion2075RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2075 | 17.2657 | 20.8849 | 25.4375 | 28.9068 | 32.382
CanningtonIce Accretion2080RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2080 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
CanningtonIce Accretion2085RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2085 | 17.2135 | 20.9056 | 25.5625 | 29.0904 | 32.634
CanningtonIce Accretion2090RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2090 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
CanningtonIce Accretion2095RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2095 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
CanningtonIce Accretion2100RCP6.0 | Cannington | Ice Accretion | RCP6.0 | 2100 | 16.2654 | 19.8992 | 24.5 | 27.9957 | 31.4685
CanningtonIce Accretion2023RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
CanningtonIce Accretion2025RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2025 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
CanningtonIce Accretion2030RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2030 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
CanningtonIce Accretion2035RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2035 | 17.6919 | 21.2272 | 25.725 | 29.154 | 32.6025
CanningtonIce Accretion2040RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2040 | 17.5585 | 21.1097 | 25.6083 | 29.041 | 32.487
CanningtonIce Accretion2045RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2045 | 17.4251 | 20.9921 | 25.4917 | 28.928 | 32.3715
CanningtonIce Accretion2050RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2050 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
CanningtonIce Accretion2055RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2055 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
CanningtonIce Accretion2060RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2060 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
CanningtonIce Accretion2065RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2065 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
CanningtonIce Accretion2070RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2070 | 15.9987 | 19.6226 | 24.2083 | 27.685 | 31.143
CanningtonIce Accretion2075RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2075 | 15.7319 | 19.3459 | 23.9167 | 27.3742 | 30.8175
CanningtonIce Accretion2080RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2080 | 15.4652 | 19.0693 | 23.625 | 27.0635 | 30.492
CanningtonIce Accretion2085RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2085 | 14.8911 | 18.426 | 22.8875 | 26.2584 | 29.6258
CanningtonIce Accretion2090RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2090 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
CanningtonIce Accretion2095RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2095 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
CanningtonIce Accretion2100RCP8.5 | Cannington | Ice Accretion | RCP8.5 | 2100 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
CanningtonWind2023RCP4.5 | Cannington | Wind | RCP4.5 | 2023 | 73.8804 | 79.5796 | 85.5695 | 91.5594 | 97.5589
CanningtonWind2025RCP4.5 | Cannington | Wind | RCP4.5 | 2025 | 73.9134 | 79.6231 | 85.6276 | 91.6306 | 97.6413
CanningtonWind2030RCP4.5 | Cannington | Wind | RCP4.5 | 2030 | 73.9465 | 79.6666 | 85.6857 | 91.7019 | 97.7236
CanningtonWind2035RCP4.5 | Cannington | Wind | RCP4.5 | 2035 | 73.9795 | 79.7101 | 85.7437 | 91.7731 | 97.806
CanningtonWind2040RCP4.5 | Cannington | Wind | RCP4.5 | 2040 | 74.0125 | 79.7535 | 85.8018 | 91.8443 | 97.8884
CanningtonWind2045RCP4.5 | Cannington | Wind | RCP4.5 | 2045 | 74.0456 | 79.797 | 85.8599 | 91.9156 | 97.9707
CanningtonWind2050RCP4.5 | Cannington | Wind | RCP4.5 | 2050 | 74.1446 | 79.918 | 86.0081 | 92.0869 | 98.1655
CanningtonWind2055RCP4.5 | Cannington | Wind | RCP4.5 | 2055 | 74.2107 | 79.9954 | 86.0982 | 92.1869 | 98.2779
CanningtonWind2060RCP4.5 | Cannington | Wind | RCP4.5 | 2060 | 74.2768 | 80.0729 | 86.1883 | 92.287 | 98.3903
CanningtonWind2065RCP4.5 | Cannington | Wind | RCP4.5 | 2065 | 74.3428 | 80.1504 | 86.2784 | 92.387 | 98.5027
CanningtonWind2070RCP4.5 | Cannington | Wind | RCP4.5 | 2070 | 74.4089 | 80.2278 | 86.3685 | 92.4871 | 98.6151
CanningtonWind2075RCP4.5 | Cannington | Wind | RCP4.5 | 2075 | 74.481 | 80.3174 | 86.479 | 92.6174 | 98.7637
CanningtonWind2080RCP4.5 | Cannington | Wind | RCP4.5 | 2080 | 74.5532 | 80.407 | 86.5895 | 92.7478 | 98.9123
CanningtonWind2085RCP4.5 | Cannington | Wind | RCP4.5 | 2085 | 74.6254 | 80.4966 | 86.7 | 92.8781 | 99.0609
CanningtonWind2090RCP4.5 | Cannington | Wind | RCP4.5 | 2090 | 74.6976 | 80.5862 | 86.8105 | 93.0085 | 99.2094
CanningtonWind2095RCP4.5 | Cannington | Wind | RCP4.5 | 2095 | 74.7697 | 80.6758 | 86.921 | 93.1389 | 99.358
CanningtonWind2100RCP4.5 | Cannington | Wind | RCP4.5 | 2100 | 74.8419 | 80.7654 | 87.0315 | 93.2692 | 99.5066
CanningtonWind2023RCP6.0 | Cannington | Wind | RCP6.0 | 2023 | 73.8804 | 79.5796 | 85.5695 | 91.5594 | 97.5589
CanningtonWind2025RCP6.0 | Cannington | Wind | RCP6.0 | 2025 | 73.9134 | 79.6231 | 85.6276 | 91.6306 | 97.6413
CanningtonWind2030RCP6.0 | Cannington | Wind | RCP6.0 | 2030 | 73.9465 | 79.6666 | 85.6857 | 91.7019 | 97.7236
CanningtonWind2035RCP6.0 | Cannington | Wind | RCP6.0 | 2035 | 73.9795 | 79.7101 | 85.7437 | 91.7731 | 97.806
CanningtonWind2040RCP6.0 | Cannington | Wind | RCP6.0 | 2040 | 74.0125 | 79.7535 | 85.8018 | 91.8443 | 97.8884
CanningtonWind2045RCP6.0 | Cannington | Wind | RCP6.0 | 2045 | 74.0456 | 79.797 | 85.8599 | 91.9156 | 97.9707
CanningtonWind2050RCP6.0 | Cannington | Wind | RCP6.0 | 2050 | 74.1446 | 79.918 | 86.0081 | 92.0869 | 98.1655
CanningtonWind2055RCP6.0 | Cannington | Wind | RCP6.0 | 2055 | 74.2107 | 79.9954 | 86.0982 | 92.1869 | 98.2779
CanningtonWind2060RCP6.0 | Cannington | Wind | RCP6.0 | 2060 | 74.2768 | 80.0729 | 86.1883 | 92.287 | 98.3903
CanningtonWind2065RCP6.0 | Cannington | Wind | RCP6.0 | 2065 | 74.3428 | 80.1504 | 86.2784 | 92.387 | 98.5027
CanningtonWind2070RCP6.0 | Cannington | Wind | RCP6.0 | 2070 | 74.4089 | 80.2278 | 86.3685 | 92.4871 | 98.6151
CanningtonWind2075RCP6.0 | Cannington | Wind | RCP6.0 | 2075 | 74.5171 | 80.3622 | 86.5343 | 92.6826 | 98.838
CanningtonWind2080RCP6.0 | Cannington | Wind | RCP6.0 | 2080 | 74.6254 | 80.4966 | 86.7 | 92.8781 | 99.0609
CanningtonWind2085RCP6.0 | Cannington | Wind | RCP6.0 | 2085 | 74.7336 | 80.631 | 86.8658 | 93.0737 | 99.2837
CanningtonWind2090RCP6.0 | Cannington | Wind | RCP6.0 | 2090 | 75.0792 | 81.0368 | 87.3488 | 93.6209 | 99.8974
CanningtonWind2095RCP6.0 | Cannington | Wind | RCP6.0 | 2095 | 75.3165 | 81.3082 | 87.6662 | 93.9726 | 100.2883
CanningtonWind2100RCP6.0 | Cannington | Wind | RCP6.0 | 2100 | 75.5538 | 81.5796 | 87.9835 | 94.3242 | 100.6791
CanningtonWind2023RCP8.5 | Cannington | Wind | RCP8.5 | 2023 | 73.8804 | 79.5796 | 85.5695 | 91.5594 | 97.5589
CanningtonWind2025RCP8.5 | Cannington | Wind | RCP8.5 | 2025 | 73.9465 | 79.6666 | 85.6857 | 91.7019 | 97.7236
CanningtonWind2030RCP8.5 | Cannington | Wind | RCP8.5 | 2030 | 74.0125 | 79.7535 | 85.8018 | 91.8443 | 97.8884
CanningtonWind2035RCP8.5 | Cannington | Wind | RCP8.5 | 2035 | 74.0786 | 79.8405 | 85.918 | 91.9868 | 98.0531
CanningtonWind2040RCP8.5 | Cannington | Wind | RCP8.5 | 2040 | 74.1887 | 79.9696 | 86.0682 | 92.1536 | 98.2404
CanningtonWind2045RCP8.5 | Cannington | Wind | RCP8.5 | 2045 | 74.2988 | 80.0987 | 86.2183 | 92.3203 | 98.4278
CanningtonWind2050RCP8.5 | Cannington | Wind | RCP8.5 | 2050 | 74.5532 | 80.407 | 86.5895 | 92.7478 | 98.9123
CanningtonWind2055RCP8.5 | Cannington | Wind | RCP8.5 | 2055 | 74.6976 | 80.5862 | 86.8105 | 93.0085 | 99.2094
CanningtonWind2060RCP8.5 | Cannington | Wind | RCP8.5 | 2060 | 75.0792 | 81.0368 | 87.3488 | 93.6209 | 99.8974
CanningtonWind2065RCP8.5 | Cannington | Wind | RCP8.5 | 2065 | 75.3165 | 81.3082 | 87.6662 | 93.9726 | 100.2883
CanningtonWind2070RCP8.5 | Cannington | Wind | RCP8.5 | 2070 | 75.637 | 81.6876 | 88.1167 | 94.4819 | 100.8632
CanningtonWind2075RCP8.5 | Cannington | Wind | RCP8.5 | 2075 | 75.7202 | 81.7957 | 88.2498 | 94.6395 | 101.0473
CanningtonWind2080RCP8.5 | Cannington | Wind | RCP8.5 | 2080 | 75.8034 | 81.9037 | 88.383 | 94.7972 | 101.2314
CanningtonWind2085RCP8.5 | Cannington | Wind | RCP8.5 | 2085 | 75.9979 | 82.1764 | 88.7655 | 95.2656 | 101.7886
CanningtonWind2090RCP8.5 | Cannington | Wind | RCP8.5 | 2090 | 76.1924 | 82.4491 | 89.148 | 95.734 | 102.3458
CanningtonWind2095RCP8.5 | Cannington | Wind | RCP8.5 | 2095 | 76.1924 | 82.4491 | 89.148 | 95.734 | 102.3458
CanningtonWind2100RCP8.5 | Cannington | Wind | RCP8.5 | 2100 | 76.1924 | 82.4491 | 89.148 | 95.734 | 102.3458
Carleton PlaceIce Accretion2023RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2023 | 18.6375 | 22.1635 | 26.622 | 30.0523 | 33.4757
Carleton PlaceIce Accretion2025RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2025 | 18.6313 | 22.1598 | 26.6265 | 30.0625 | 33.487
Carleton PlaceIce Accretion2030RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2030 | 18.625 | 22.156 | 26.631 | 30.0727 | 33.4984
Carleton PlaceIce Accretion2035RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2035 | 18.6188 | 22.1523 | 26.6355 | 30.0829 | 33.5097
Carleton PlaceIce Accretion2040RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2040 | 18.6125 | 22.1486 | 26.64 | 30.093 | 33.521
Carleton PlaceIce Accretion2045RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2045 | 18.6062 | 22.1448 | 26.6445 | 30.1032 | 33.5324
Carleton PlaceIce Accretion2050RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2050 | 18.6037 | 22.1635 | 26.6922 | 30.1744 | 33.6186
Carleton PlaceIce Accretion2055RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2055 | 18.6075 | 22.1859 | 26.7354 | 30.2354 | 33.6934
Carleton PlaceIce Accretion2060RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2060 | 18.6112 | 22.2083 | 26.7786 | 30.2964 | 33.7683
Carleton PlaceIce Accretion2065RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2065 | 18.615 | 22.2307 | 26.8218 | 30.3575 | 33.8431
Carleton PlaceIce Accretion2070RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2070 | 18.6188 | 22.2531 | 26.865 | 30.4185 | 33.9179
Carleton PlaceIce Accretion2075RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2075 | 18.7033 | 22.3764 | 27.036 | 30.6219 | 34.1618
Carleton PlaceIce Accretion2080RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2080 | 18.7878 | 22.4996 | 27.207 | 30.8253 | 34.4056
Carleton PlaceIce Accretion2085RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2085 | 18.8724 | 22.6229 | 27.378 | 31.0287 | 34.6494
Carleton PlaceIce Accretion2090RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2090 | 18.9569 | 22.7462 | 27.549 | 31.2321 | 34.8932
Carleton PlaceIce Accretion2095RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2095 | 19.0415 | 22.8694 | 27.72 | 31.4355 | 35.137
Carleton PlaceIce Accretion2100RCP4.5 | Carleton Place | Ice Accretion | RCP4.5 | 2100 | 19.126 | 22.9927 | 27.891 | 31.6389 | 35.3808
Carleton PlaceIce Accretion2023RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2023 | 18.6375 | 22.1635 | 26.622 | 30.0523 | 33.4757
Carleton PlaceIce Accretion2025RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2025 | 18.6313 | 22.1598 | 26.6265 | 30.0625 | 33.487
Carleton PlaceIce Accretion2030RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2030 | 18.625 | 22.156 | 26.631 | 30.0727 | 33.4984
Carleton PlaceIce Accretion2035RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2035 | 18.6188 | 22.1523 | 26.6355 | 30.0829 | 33.5097
Carleton PlaceIce Accretion2040RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2040 | 18.6125 | 22.1486 | 26.64 | 30.093 | 33.521
Carleton PlaceIce Accretion2045RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2045 | 18.6062 | 22.1448 | 26.6445 | 30.1032 | 33.5324
Carleton PlaceIce Accretion2050RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2050 | 18.6037 | 22.1635 | 26.6922 | 30.1744 | 33.6186
Carleton PlaceIce Accretion2055RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2055 | 18.6075 | 22.1859 | 26.7354 | 30.2354 | 33.6934
Carleton PlaceIce Accretion2060RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2060 | 18.6112 | 22.2083 | 26.7786 | 30.2964 | 33.7683
Carleton PlaceIce Accretion2065RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2065 | 18.615 | 22.2307 | 26.8218 | 30.3575 | 33.8431
Carleton PlaceIce Accretion2070RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2070 | 18.6188 | 22.2531 | 26.865 | 30.4185 | 33.9179
Carleton PlaceIce Accretion2075RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2075 | 18.7456 | 22.438 | 27.1215 | 30.7236 | 34.2837
Carleton PlaceIce Accretion2080RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2080 | 18.8724 | 22.6229 | 27.378 | 31.0287 | 34.6494
Carleton PlaceIce Accretion2085RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2085 | 18.9992 | 22.8078 | 27.6345 | 31.3338 | 35.0151
Carleton PlaceIce Accretion2090RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2090 | 19.1135 | 23.0151 | 27.963 | 31.7304 | 35.5055
Carleton PlaceIce Accretion2095RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2095 | 19.101 | 23.0375 | 28.035 | 31.8219 | 35.6303
Carleton PlaceIce Accretion2100RCP6.0 | Carleton Place | Ice Accretion | RCP6.0 | 2100 | 19.0885 | 23.0599 | 28.107 | 31.9135 | 35.755
Carleton PlaceIce Accretion2023RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2023 | 18.6375 | 22.1635 | 26.622 | 30.0523 | 33.4757
Carleton PlaceIce Accretion2025RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2025 | 18.625 | 22.156 | 26.631 | 30.0727 | 33.4984
Carleton PlaceIce Accretion2030RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2030 | 18.6125 | 22.1486 | 26.64 | 30.093 | 33.521
Carleton PlaceIce Accretion2035RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2035 | 18.6 | 22.1411 | 26.649 | 30.1134 | 33.5437
Carleton PlaceIce Accretion2040RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2040 | 18.6062 | 22.1784 | 26.721 | 30.2151 | 33.6685
Carleton PlaceIce Accretion2045RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2045 | 18.6125 | 22.2158 | 26.793 | 30.3168 | 33.7932
Carleton PlaceIce Accretion2050RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2050 | 18.7878 | 22.4996 | 27.207 | 30.8253 | 34.4056
Carleton PlaceIce Accretion2055RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2055 | 18.9569 | 22.7462 | 27.549 | 31.2321 | 34.8932
Carleton PlaceIce Accretion2060RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2060 | 19.1135 | 23.0151 | 27.963 | 31.7304 | 35.5055
Carleton PlaceIce Accretion2065RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2065 | 19.101 | 23.0375 | 28.035 | 31.8219 | 35.6303
Carleton PlaceIce Accretion2070RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2070 | 18.888 | 22.8507 | 27.882 | 31.6795 | 35.5055
Carleton PlaceIce Accretion2075RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2075 | 18.6876 | 22.6416 | 27.657 | 31.4456 | 35.2561
Carleton PlaceIce Accretion2080RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2080 | 18.4872 | 22.4324 | 27.432 | 31.2117 | 35.0066
Carleton PlaceIce Accretion2085RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2085 | 17.7169 | 21.5472 | 26.3925 | 30.0676 | 33.7478
Carleton PlaceIce Accretion2090RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2090 | 16.9466 | 20.662 | 25.353 | 28.9235 | 32.4891
Carleton PlaceIce Accretion2095RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2095 | 16.9466 | 20.662 | 25.353 | 28.9235 | 32.4891
Carleton PlaceIce Accretion2100RCP8.5 | Carleton Place | Ice Accretion | RCP8.5 | 2100 | 16.9466 | 20.662 | 25.353 | 28.9235 | 32.4891
Carleton PlaceWind2023RCP4.5 | Carleton Place | Wind | RCP4.5 | 2023 | 74.8164 | 80.6518 | 86.8084 | 92.9402 | 99.0792
Carleton PlaceWind2025RCP4.5 | Carleton Place | Wind | RCP4.5 | 2025 | 74.9241 | 80.7811 | 86.9646 | 93.1212 | 99.2851
Carleton PlaceWind2030RCP4.5 | Carleton Place | Wind | RCP4.5 | 2030 | 75.0318 | 80.9104 | 87.1209 | 93.3021 | 99.491
Carleton PlaceWind2035RCP4.5 | Carleton Place | Wind | RCP4.5 | 2035 | 75.1395 | 81.0397 | 87.2771 | 93.4831 | 99.6969
Carleton PlaceWind2040RCP4.5 | Carleton Place | Wind | RCP4.5 | 2040 | 75.2471 | 81.169 | 87.4333 | 93.6641 | 99.9028
Carleton PlaceWind2045RCP4.5 | Carleton Place | Wind | RCP4.5 | 2045 | 75.3548 | 81.2983 | 87.5896 | 93.8451 | 100.1086
Carleton PlaceWind2050RCP4.5 | Carleton Place | Wind | RCP4.5 | 2050 | 75.4476 | 81.4052 | 87.7148 | 93.9874 | 100.2675
Carleton PlaceWind2055RCP4.5 | Carleton Place | Wind | RCP4.5 | 2055 | 75.4328 | 81.3828 | 87.6839 | 93.9487 | 100.2204
Carleton PlaceWind2060RCP4.5 | Carleton Place | Wind | RCP4.5 | 2060 | 75.4179 | 81.3605 | 87.6529 | 93.9101 | 100.1734
Carleton PlaceWind2065RCP4.5 | Carleton Place | Wind | RCP4.5 | 2065 | 75.4031 | 81.3381 | 87.622 | 93.8714 | 100.1263
Carleton PlaceWind2070RCP4.5 | Carleton Place | Wind | RCP4.5 | 2070 | 75.3882 | 81.3157 | 87.591 | 93.8328 | 100.0792
Carleton PlaceWind2075RCP4.5 | Carleton Place | Wind | RCP4.5 | 2075 | 75.4155 | 81.3517 | 87.6397 | 93.8911 | 100.1462
Carleton PlaceWind2080RCP4.5 | Carleton Place | Wind | RCP4.5 | 2080 | 75.4427 | 81.3876 | 87.6885 | 93.9494 | 100.2132
Carleton PlaceWind2085RCP4.5 | Carleton Place | Wind | RCP4.5 | 2085 | 75.4699 | 81.4236 | 87.7372 | 94.0076 | 100.2802
Carleton PlaceWind2090RCP4.5 | Carleton Place | Wind | RCP4.5 | 2090 | 75.4971 | 81.4596 | 87.7859 | 94.0659 | 100.3472
Carleton PlaceWind2095RCP4.5 | Carleton Place | Wind | RCP4.5 | 2095 | 75.5244 | 81.4956 | 87.8347 | 94.1242 | 100.4142
Carleton PlaceWind2100RCP4.5 | Carleton Place | Wind | RCP4.5 | 2100 | 75.5516 | 81.5316 | 87.8834 | 94.1825 | 100.4812
Carleton PlaceWind2023RCP6.0 | Carleton Place | Wind | RCP6.0 | 2023 | 74.8164 | 80.6518 | 86.8084 | 92.9402 | 99.0792
Carleton PlaceWind2025RCP6.0 | Carleton Place | Wind | RCP6.0 | 2025 | 74.9241 | 80.7811 | 86.9646 | 93.1212 | 99.2851
Carleton PlaceWind2030RCP6.0 | Carleton Place | Wind | RCP6.0 | 2030 | 75.0318 | 80.9104 | 87.1209 | 93.3021 | 99.491
Carleton PlaceWind2035RCP6.0 | Carleton Place | Wind | RCP6.0 | 2035 | 75.1395 | 81.0397 | 87.2771 | 93.4831 | 99.6969
Carleton PlaceWind2040RCP6.0 | Carleton Place | Wind | RCP6.0 | 2040 | 75.2471 | 81.169 | 87.4333 | 93.6641 | 99.9028
Carleton PlaceWind2045RCP6.0 | Carleton Place | Wind | RCP6.0 | 2045 | 75.3548 | 81.2983 | 87.5896 | 93.8451 | 100.1086
Carleton PlaceWind2050RCP6.0 | Carleton Place | Wind | RCP6.0 | 2050 | 75.4476 | 81.4052 | 87.7148 | 93.9874 | 100.2675
Carleton PlaceWind2055RCP6.0 | Carleton Place | Wind | RCP6.0 | 2055 | 75.4328 | 81.3828 | 87.6839 | 93.9487 | 100.2204
Carleton PlaceWind2060RCP6.0 | Carleton Place | Wind | RCP6.0 | 2060 | 75.4179 | 81.3605 | 87.6529 | 93.9101 | 100.1734
Carleton PlaceWind2065RCP6.0 | Carleton Place | Wind | RCP6.0 | 2065 | 75.4031 | 81.3381 | 87.622 | 93.8714 | 100.1263
Carleton PlaceWind2070RCP6.0 | Carleton Place | Wind | RCP6.0 | 2070 | 75.3882 | 81.3157 | 87.591 | 93.8328 | 100.0792
Carleton PlaceWind2075RCP6.0 | Carleton Place | Wind | RCP6.0 | 2075 | 75.4291 | 81.3697 | 87.6641 | 93.9202 | 100.1797
Carleton PlaceWind2080RCP6.0 | Carleton Place | Wind | RCP6.0 | 2080 | 75.4699 | 81.4236 | 87.7372 | 94.0076 | 100.2802
Carleton PlaceWind2085RCP6.0 | Carleton Place | Wind | RCP6.0 | 2085 | 75.5108 | 81.4776 | 87.8103 | 94.0951 | 100.3807
Carleton PlaceWind2090RCP6.0 | Carleton Place | Wind | RCP6.0 | 2090 | 75.4971 | 81.449 | 87.7573 | 94.026 | 100.2917
Carleton PlaceWind2095RCP6.0 | Carleton Place | Wind | RCP6.0 | 2095 | 75.4427 | 81.3663 | 87.6311 | 93.8696 | 100.1021
Carleton PlaceWind2100RCP6.0 | Carleton Place | Wind | RCP6.0 | 2100 | 75.3882 | 81.2837 | 87.505 | 93.7132 | 99.9126
Carleton PlaceWind2023RCP8.5 | Carleton Place | Wind | RCP8.5 | 2023 | 74.8164 | 80.6518 | 86.8084 | 92.9402 | 99.0792
Carleton PlaceWind2025RCP8.5 | Carleton Place | Wind | RCP8.5 | 2025 | 75.0318 | 80.9104 | 87.1209 | 93.3021 | 99.491
Carleton PlaceWind2030RCP8.5 | Carleton Place | Wind | RCP8.5 | 2030 | 75.2471 | 81.169 | 87.4333 | 93.6641 | 99.9028
Carleton PlaceWind2035RCP8.5 | Carleton Place | Wind | RCP8.5 | 2035 | 75.4625 | 81.4276 | 87.7458 | 94.026 | 100.3145
Carleton PlaceWind2040RCP8.5 | Carleton Place | Wind | RCP8.5 | 2040 | 75.4377 | 81.3903 | 87.6942 | 93.9616 | 100.2361
Carleton PlaceWind2045RCP8.5 | Carleton Place | Wind | RCP8.5 | 2045 | 75.413 | 81.353 | 87.6426 | 93.8972 | 100.1577
Carleton PlaceWind2050RCP8.5 | Carleton Place | Wind | RCP8.5 | 2050 | 75.4427 | 81.3876 | 87.6885 | 93.9494 | 100.2132
Carleton PlaceWind2055RCP8.5 | Carleton Place | Wind | RCP8.5 | 2055 | 75.4971 | 81.4596 | 87.7859 | 94.0659 | 100.3472
Carleton PlaceWind2060RCP8.5 | Carleton Place | Wind | RCP8.5 | 2060 | 75.4971 | 81.449 | 87.7573 | 94.026 | 100.2917
Carleton PlaceWind2065RCP8.5 | Carleton Place | Wind | RCP8.5 | 2065 | 75.4427 | 81.3663 | 87.6311 | 93.8696 | 100.1021
Carleton PlaceWind2070RCP8.5 | Carleton Place | Wind | RCP8.5 | 2070 | 75.4204 | 81.313 | 87.5308 | 93.7377 | 99.9354
Carleton PlaceWind2075RCP8.5 | Carleton Place | Wind | RCP8.5 | 2075 | 75.4526 | 81.3423 | 87.5566 | 93.7622 | 99.9583
Carleton PlaceWind2080RCP8.5 | Carleton Place | Wind | RCP8.5 | 2080 | 75.4848 | 81.3717 | 87.5824 | 93.7868 | 99.9812
Carleton PlaceWind2085RCP8.5 | Carleton Place | Wind | RCP8.5 | 2085 | 75.5108 | 81.4116 | 87.6383 | 93.8512 | 100.0596
Carleton PlaceWind2090RCP8.5 | Carleton Place | Wind | RCP8.5 | 2090 | 75.5368 | 81.4516 | 87.6942 | 93.9156 | 100.1381
Carleton PlaceWind2095RCP8.5 | Carleton Place | Wind | RCP8.5 | 2095 | 75.5368 | 81.4516 | 87.6942 | 93.9156 | 100.1381
Carleton PlaceWind2100RCP8.5 | Carleton Place | Wind | RCP8.5 | 2100 | 75.5368 | 81.4516 | 87.6942 | 93.9156 | 100.1381
CavanIce Accretion2023RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2023 | 17.5875 | 20.999 | 25.325 | 28.6172 | 31.941
CavanIce Accretion2025RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2025 | 17.6542 | 21.0958 | 25.4625 | 28.7867 | 32.1352
CavanIce Accretion2030RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2030 | 17.7209 | 21.1927 | 25.6 | 28.9562 | 32.3295
CavanIce Accretion2035RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2035 | 17.7876 | 21.2895 | 25.7375 | 29.1257 | 32.5237
CavanIce Accretion2040RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2040 | 17.8543 | 21.3863 | 25.875 | 29.2952 | 32.718
CavanIce Accretion2045RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2045 | 17.9209 | 21.4832 | 26.0125 | 29.4647 | 32.9123
CavanIce Accretion2050RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2050 | 17.8867 | 21.4804 | 26.045 | 29.5212 | 32.9931
CavanIce Accretion2055RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2055 | 17.7858 | 21.3808 | 25.94 | 29.4082 | 32.8797
CavanIce Accretion2060RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2060 | 17.6849 | 21.2812 | 25.835 | 29.2952 | 32.7663
CavanIce Accretion2065RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2065 | 17.584 | 21.1816 | 25.73 | 29.1822 | 32.6529
CavanIce Accretion2070RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2070 | 17.4831 | 21.082 | 25.625 | 29.0692 | 32.5395
CavanIce Accretion2075RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2075 | 17.5237 | 21.1615 | 25.7542 | 29.2387 | 32.7442
CavanIce Accretion2080RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2080 | 17.5643 | 21.2411 | 25.8833 | 29.4082 | 32.949
CavanIce Accretion2085RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2085 | 17.6049 | 21.3206 | 26.0125 | 29.5777 | 33.1538
CavanIce Accretion2090RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2090 | 17.6455 | 21.4002 | 26.1417 | 29.7472 | 33.3585
CavanIce Accretion2095RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2095 | 17.6861 | 21.4797 | 26.2708 | 29.9167 | 33.5632
CavanIce Accretion2100RCP4.5 | Cavan | Ice Accretion | RCP4.5 | 2100 | 17.7267 | 21.5592 | 26.4 | 30.0862 | 33.768
CavanIce Accretion2023RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2023 | 17.5875 | 20.999 | 25.325 | 28.6172 | 31.941
CavanIce Accretion2025RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2025 | 17.6542 | 21.0958 | 25.4625 | 28.7867 | 32.1352
CavanIce Accretion2030RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2030 | 17.7209 | 21.1927 | 25.6 | 28.9562 | 32.3295
CavanIce Accretion2035RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2035 | 17.7876 | 21.2895 | 25.7375 | 29.1257 | 32.5237
CavanIce Accretion2040RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2040 | 17.8543 | 21.3863 | 25.875 | 29.2952 | 32.718
CavanIce Accretion2045RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2045 | 17.9209 | 21.4832 | 26.0125 | 29.4647 | 32.9123
CavanIce Accretion2050RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2050 | 17.8867 | 21.4804 | 26.045 | 29.5212 | 32.9931
CavanIce Accretion2055RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2055 | 17.7858 | 21.3808 | 25.94 | 29.4082 | 32.8797
CavanIce Accretion2060RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2060 | 17.6849 | 21.2812 | 25.835 | 29.2952 | 32.7663
CavanIce Accretion2065RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2065 | 17.584 | 21.1816 | 25.73 | 29.1822 | 32.6529
CavanIce Accretion2070RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2070 | 17.4831 | 21.082 | 25.625 | 29.0692 | 32.5395
CavanIce Accretion2075RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2075 | 17.544 | 21.2013 | 25.8187 | 29.3235 | 32.8466
CavanIce Accretion2080RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2080 | 17.6049 | 21.3206 | 26.0125 | 29.5777 | 33.1538
CavanIce Accretion2085RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2085 | 17.6658 | 21.4399 | 26.2063 | 29.832 | 33.4609
CavanIce Accretion2090RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2090 | 17.3498 | 21.1512 | 25.95 | 29.606 | 33.243
CavanIce Accretion2095RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2095 | 16.9728 | 20.7431 | 25.5 | 29.1257 | 32.718
CavanIce Accretion2100RCP6.0 | Cavan | Ice Accretion | RCP6.0 | 2100 | 16.5959 | 20.335 | 25.05 | 28.6455 | 32.193
CavanIce Accretion2023RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2023 | 17.5875 | 20.999 | 25.325 | 28.6172 | 31.941
CavanIce Accretion2025RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2025 | 17.7209 | 21.1927 | 25.6 | 28.9562 | 32.3295
CavanIce Accretion2030RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2030 | 17.8543 | 21.3863 | 25.875 | 29.2952 | 32.718
CavanIce Accretion2035RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2035 | 17.9876 | 21.58 | 26.15 | 29.6342 | 33.1065
CavanIce Accretion2040RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2040 | 17.8195 | 21.414 | 25.975 | 29.4459 | 32.9175
CavanIce Accretion2045RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2045 | 17.6513 | 21.248 | 25.8 | 29.2576 | 32.7285
CavanIce Accretion2050RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2050 | 17.5643 | 21.2411 | 25.8833 | 29.4082 | 32.949
CavanIce Accretion2055RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2055 | 17.6455 | 21.4002 | 26.1417 | 29.7472 | 33.3585
CavanIce Accretion2060RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2060 | 17.3498 | 21.1512 | 25.95 | 29.606 | 33.243
CavanIce Accretion2065RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2065 | 16.9728 | 20.7431 | 25.5 | 29.1257 | 32.718
CavanIce Accretion2070RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2070 | 16.2306 | 19.9338 | 24.6083 | 28.1558 | 31.6785
CavanIce Accretion2075RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2075 | 15.8653 | 19.5327 | 24.1667 | 27.6662 | 31.164
CavanIce Accretion2080RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2080 | 15.5 | 19.1315 | 23.725 | 27.1765 | 30.6495
CavanIce Accretion2085RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2085 | 14.9259 | 18.4779 | 22.9625 | 26.3431 | 29.736
CavanIce Accretion2090RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2090 | 14.3518 | 17.8242 | 22.2 | 25.5097 | 28.8225
CavanIce Accretion2095RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2095 | 14.3518 | 17.8242 | 22.2 | 25.5097 | 28.8225
CavanIce Accretion2100RCP8.5 | Cavan | Ice Accretion | RCP8.5 | 2100 | 14.3518 | 17.8242 | 22.2 | 25.5097 | 28.8225
CavanWind2023RCP4.5 | Cavan | Wind | RCP4.5 | 2023 | 73.5868 | 79.1765 | 85.0425 | 90.9318 | 96.8128
CavanWind2025RCP4.5 | Cavan | Wind | RCP4.5 | 2025 | 73.5917 | 79.1883 | 85.0623 | 90.9576 | 96.8451
CavanWind2030RCP4.5 | Cavan | Wind | RCP4.5 | 2030 | 73.5966 | 79.2002 | 85.0822 | 90.9833 | 96.8774
CavanWind2035RCP4.5 | Cavan | Wind | RCP4.5 | 2035 | 73.6015 | 79.2121 | 85.102 | 91.0091 | 96.9097
CavanWind2040RCP4.5 | Cavan | Wind | RCP4.5 | 2040 | 73.6064 | 79.2239 | 85.1218 | 91.0349 | 96.942
CavanWind2045RCP4.5 | Cavan | Wind | RCP4.5 | 2045 | 73.6113 | 79.2358 | 85.1417 | 91.0607 | 96.9743
CavanWind2050RCP4.5 | Cavan | Wind | RCP4.5 | 2050 | 73.7189 | 79.3788 | 85.3281 | 91.2829 | 97.2333
CavanWind2055RCP4.5 | Cavan | Wind | RCP4.5 | 2055 | 73.8217 | 79.5101 | 85.4947 | 91.4793 | 97.4601
CavanWind2060RCP4.5 | Cavan | Wind | RCP4.5 | 2060 | 73.9245 | 79.6413 | 85.6613 | 91.6758 | 97.6868
CavanWind2065RCP4.5 | Cavan | Wind | RCP4.5 | 2065 | 74.0272 | 79.7725 | 85.8279 | 91.8722 | 97.9136
CavanWind2070RCP4.5 | Cavan | Wind | RCP4.5 | 2070 | 74.13 | 79.9037 | 85.9945 | 92.0687 | 98.1403
CavanWind2075RCP4.5 | Cavan | Wind | RCP4.5 | 2075 | 74.2278 | 80.0315 | 86.1603 | 92.2673 | 98.3729
CavanWind2080RCP4.5 | Cavan | Wind | RCP4.5 | 2080 | 74.3257 | 80.1593 | 86.326 | 92.4658 | 98.6054
CavanWind2085RCP4.5 | Cavan | Wind | RCP4.5 | 2085 | 74.4236 | 80.2871 | 86.4917 | 92.6644 | 98.838
CavanWind2090RCP4.5 | Cavan | Wind | RCP4.5 | 2090 | 74.5214 | 80.4149 | 86.6575 | 92.863 | 99.0706
CavanWind2095RCP4.5 | Cavan | Wind | RCP4.5 | 2095 | 74.6193 | 80.5427 | 86.8233 | 93.0616 | 99.3031
CavanWind2100RCP4.5 | Cavan | Wind | RCP4.5 | 2100 | 74.7171 | 80.6705 | 86.989 | 93.2601 | 99.5357
CavanWind2023RCP6.0 | Cavan | Wind | RCP6.0 | 2023 | 73.5868 | 79.1765 | 85.0425 | 90.9318 | 96.8128
CavanWind2025RCP6.0 | Cavan | Wind | RCP6.0 | 2025 | 73.5917 | 79.1883 | 85.0623 | 90.9576 | 96.8451
CavanWind2030RCP6.0 | Cavan | Wind | RCP6.0 | 2030 | 73.5966 | 79.2002 | 85.0822 | 90.9833 | 96.8774
CavanWind2035RCP6.0 | Cavan | Wind | RCP6.0 | 2035 | 73.6015 | 79.2121 | 85.102 | 91.0091 | 96.9097
CavanWind2040RCP6.0 | Cavan | Wind | RCP6.0 | 2040 | 73.6064 | 79.2239 | 85.1218 | 91.0349 | 96.942
CavanWind2045RCP6.0 | Cavan | Wind | RCP6.0 | 2045 | 73.6113 | 79.2358 | 85.1417 | 91.0607 | 96.9743
CavanWind2050RCP6.0 | Cavan | Wind | RCP6.0 | 2050 | 73.7189 | 79.3788 | 85.3281 | 91.2829 | 97.2333
CavanWind2055RCP6.0 | Cavan | Wind | RCP6.0 | 2055 | 73.8217 | 79.5101 | 85.4947 | 91.4793 | 97.4601
CavanWind2060RCP6.0 | Cavan | Wind | RCP6.0 | 2060 | 73.9245 | 79.6413 | 85.6613 | 91.6758 | 97.6868
CavanWind2065RCP6.0 | Cavan | Wind | RCP6.0 | 2065 | 74.0272 | 79.7725 | 85.8279 | 91.8722 | 97.9136
CavanWind2070RCP6.0 | Cavan | Wind | RCP6.0 | 2070 | 74.13 | 79.9037 | 85.9945 | 92.0687 | 98.1403
CavanWind2075RCP6.0 | Cavan | Wind | RCP6.0 | 2075 | 74.2768 | 80.0954 | 86.2431 | 92.3665 | 98.4892
CavanWind2080RCP6.0 | Cavan | Wind | RCP6.0 | 2080 | 74.4236 | 80.2871 | 86.4917 | 92.6644 | 98.838
CavanWind2085RCP6.0 | Cavan | Wind | RCP6.0 | 2085 | 74.5703 | 80.4788 | 86.7404 | 92.9623 | 99.1868
CavanWind2090RCP6.0 | Cavan | Wind | RCP6.0 | 2090 | 75.0034 | 81.0263 | 87.4338 | 93.7816 | 100.1332
CavanWind2095RCP6.0 | Cavan | Wind | RCP6.0 | 2095 | 75.2896 | 81.382 | 87.8787 | 94.303 | 100.7308
CavanWind2100RCP6.0 | Cavan | Wind | RCP6.0 | 2100 | 75.5759 | 81.7377 | 88.3235 | 94.8245 | 101.3283
CavanWind2023RCP8.5 | Cavan | Wind | RCP8.5 | 2023 | 73.5868 | 79.1765 | 85.0425 | 90.9318 | 96.8128
CavanWind2025RCP8.5 | Cavan | Wind | RCP8.5 | 2025 | 73.5966 | 79.2002 | 85.0822 | 90.9833 | 96.8774
CavanWind2030RCP8.5 | Cavan | Wind | RCP8.5 | 2030 | 73.6064 | 79.2239 | 85.1218 | 91.0349 | 96.942
CavanWind2035RCP8.5 | Cavan | Wind | RCP8.5 | 2035 | 73.6162 | 79.2476 | 85.1615 | 91.0864 | 97.0066
CavanWind2040RCP8.5 | Cavan | Wind | RCP8.5 | 2040 | 73.7875 | 79.4663 | 85.4392 | 91.4138 | 97.3845
CavanWind2045RCP8.5 | Cavan | Wind | RCP8.5 | 2045 | 73.9587 | 79.685 | 85.7168 | 91.7413 | 97.7624
CavanWind2050RCP8.5 | Cavan | Wind | RCP8.5 | 2050 | 74.3257 | 80.1593 | 86.326 | 92.4658 | 98.6054
CavanWind2055RCP8.5 | Cavan | Wind | RCP8.5 | 2055 | 74.5214 | 80.4149 | 86.6575 | 92.863 | 99.0706
CavanWind2060RCP8.5 | Cavan | Wind | RCP8.5 | 2060 | 75.0034 | 81.0263 | 87.4338 | 93.7816 | 100.1332
CavanWind2065RCP8.5 | Cavan | Wind | RCP8.5 | 2065 | 75.2896 | 81.382 | 87.8787 | 94.303 | 100.7308
CavanWind2070RCP8.5 | Cavan | Wind | RCP8.5 | 2070 | 75.5783 | 81.7561 | 88.3603 | 94.873 | 101.3962
CavanWind2075RCP8.5 | Cavan | Wind | RCP8.5 | 2075 | 75.5808 | 81.7746 | 88.3972 | 94.9215 | 101.464
CavanWind2080RCP8.5 | Cavan | Wind | RCP8.5 | 2080 | 75.5832 | 81.793 | 88.434 | 94.97 | 101.5318
CavanWind2085RCP8.5 | Cavan | Wind | RCP8.5 | 2085 | 75.7483 | 82.0302 | 88.7655 | 95.3838 | 102.0212
CavanWind2090RCP8.5 | Cavan | Wind | RCP8.5 | 2090 | 75.9135 | 82.2673 | 89.097 | 95.7976 | 102.5105
CavanWind2095RCP8.5 | Cavan | Wind | RCP8.5 | 2095 | 75.9135 | 82.2673 | 89.097 | 95.7976 | 102.5105
CavanWind2100RCP8.5 | Cavan | Wind | RCP8.5 | 2100 | 75.9135 | 82.2673 | 89.097 | 95.7976 | 102.5105
CentraliaIce Accretion2023RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2023 | 14.379 | 17.2383 | 20.832 | 23.5876 | 26.3277
CentraliaIce Accretion2025RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2025 | 14.3936 | 17.2673 | 20.8845 | 23.6549 | 26.4115
CentraliaIce Accretion2030RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2030 | 14.4082 | 17.2964 | 20.937 | 23.7221 | 26.4953
CentraliaIce Accretion2035RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2035 | 14.4228 | 17.3254 | 20.9895 | 23.7893 | 26.5791
CentraliaIce Accretion2040RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2040 | 14.4374 | 17.3545 | 21.042 | 23.8566 | 26.6629
CentraliaIce Accretion2045RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2045 | 14.452 | 17.3835 | 21.0945 | 23.9238 | 26.7467
CentraliaIce Accretion2050RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2050 | 14.4082 | 17.3707 | 21.1218 | 23.9768 | 26.8304
CentraliaIce Accretion2055RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2055 | 14.3497 | 17.3289 | 21.0966 | 23.9626 | 26.8304
CentraliaIce Accretion2060RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2060 | 14.2913 | 17.2871 | 21.0714 | 23.9483 | 26.8304
CentraliaIce Accretion2065RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2065 | 14.2328 | 17.2452 | 21.0462 | 23.9341 | 26.8304
CentraliaIce Accretion2070RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2070 | 14.1744 | 17.2034 | 21.021 | 23.9198 | 26.8304
CentraliaIce Accretion2075RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2075 | 14.1476 | 17.1918 | 21.0315 | 23.9436 | 26.8701
CentraliaIce Accretion2080RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2080 | 14.1208 | 17.1802 | 21.042 | 23.9673 | 26.9098
CentraliaIce Accretion2085RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2085 | 14.094 | 17.1685 | 21.0525 | 23.991 | 26.9495
CentraliaIce Accretion2090RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2090 | 14.0672 | 17.1569 | 21.063 | 24.0148 | 26.9892
CentraliaIce Accretion2095RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2095 | 14.0404 | 17.1453 | 21.0735 | 24.0385 | 27.0289
CentraliaIce Accretion2100RCP4.5 | Centralia | Ice Accretion | RCP4.5 | 2100 | 14.0136 | 17.1337 | 21.084 | 24.0622 | 27.0686
CentraliaIce Accretion2023RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2023 | 14.379 | 17.2383 | 20.832 | 23.5876 | 26.3277
CentraliaIce Accretion2025RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2025 | 14.3936 | 17.2673 | 20.8845 | 23.6549 | 26.4115
CentraliaIce Accretion2030RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2030 | 14.4082 | 17.2964 | 20.937 | 23.7221 | 26.4953
CentraliaIce Accretion2035RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2035 | 14.4228 | 17.3254 | 20.9895 | 23.7893 | 26.5791
CentraliaIce Accretion2040RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2040 | 14.4374 | 17.3545 | 21.042 | 23.8566 | 26.6629
CentraliaIce Accretion2045RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2045 | 14.452 | 17.3835 | 21.0945 | 23.9238 | 26.7467
CentraliaIce Accretion2050RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2050 | 14.4082 | 17.3707 | 21.1218 | 23.9768 | 26.8304
CentraliaIce Accretion2055RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2055 | 14.3497 | 17.3289 | 21.0966 | 23.9626 | 26.8304
CentraliaIce Accretion2060RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2060 | 14.2913 | 17.2871 | 21.0714 | 23.9483 | 26.8304
CentraliaIce Accretion2065RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2065 | 14.2328 | 17.2452 | 21.0462 | 23.9341 | 26.8304
CentraliaIce Accretion2070RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2070 | 14.1744 | 17.2034 | 21.021 | 23.9198 | 26.8304
CentraliaIce Accretion2075RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2075 | 14.1342 | 17.186 | 21.0367 | 23.9554 | 26.89
CentraliaIce Accretion2080RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2080 | 14.094 | 17.1685 | 21.0525 | 23.991 | 26.9495
CentraliaIce Accretion2085RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2085 | 14.0538 | 17.1511 | 21.0682 | 24.0266 | 27.009
CentraliaIce Accretion2090RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2090 | 13.8383 | 16.9594 | 20.902 | 23.8803 | 26.8745
CentraliaIce Accretion2095RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2095 | 13.6629 | 16.7851 | 20.72 | 23.6984 | 26.6805
CentraliaIce Accretion2100RCP6.0 | Centralia | Ice Accretion | RCP6.0 | 2100 | 13.4876 | 16.6108 | 20.538 | 23.5164 | 26.4865
CentraliaIce Accretion2023RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2023 | 14.379 | 17.2383 | 20.832 | 23.5876 | 26.3277
CentraliaIce Accretion2025RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2025 | 14.4082 | 17.2964 | 20.937 | 23.7221 | 26.4953
CentraliaIce Accretion2030RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2030 | 14.4374 | 17.3545 | 21.042 | 23.8566 | 26.6629
CentraliaIce Accretion2035RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2035 | 14.4666 | 17.4126 | 21.147 | 23.991 | 26.8304
CentraliaIce Accretion2040RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2040 | 14.3692 | 17.3428 | 21.105 | 23.9673 | 26.8304
CentraliaIce Accretion2045RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2045 | 14.2718 | 17.2731 | 21.063 | 23.9436 | 26.8304
CentraliaIce Accretion2050RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2050 | 14.1208 | 17.1802 | 21.042 | 23.9673 | 26.9098
CentraliaIce Accretion2055RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2055 | 14.0672 | 17.1569 | 21.063 | 24.0148 | 26.9892
CentraliaIce Accretion2060RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2060 | 13.8383 | 16.9594 | 20.902 | 23.8803 | 26.8745
CentraliaIce Accretion2065RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2065 | 13.6629 | 16.7851 | 20.72 | 23.6984 | 26.6805
CentraliaIce Accretion2070RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2070 | 13.171 | 16.2564 | 20.139 | 23.0814 | 26.0102
CentraliaIce Accretion2075RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2075 | 12.8544 | 15.902 | 19.74 | 22.6463 | 25.5339
CentraliaIce Accretion2080RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2080 | 12.5378 | 15.5476 | 19.341 | 22.2113 | 25.0576
CentraliaIce Accretion2085RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2085 | 11.8802 | 14.7719 | 18.417 | 21.179 | 23.9198
CentraliaIce Accretion2090RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2090 | 11.2226 | 13.9963 | 17.493 | 20.1468 | 22.7821
CentraliaIce Accretion2095RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2095 | 11.2226 | 13.9963 | 17.493 | 20.1468 | 22.7821
CentraliaIce Accretion2100RCP8.5 | Centralia | Ice Accretion | RCP8.5 | 2100 | 11.2226 | 13.9963 | 17.493 | 20.1468 | 22.7821
CentraliaWind2023RCP4.5 | Centralia | Wind | RCP4.5 | 2023 | 83.7896 | 90.4139 | 97.4304 | 104.4046 | 111.388
CentraliaWind2025RCP4.5 | Centralia | Wind | RCP4.5 | 2025 | 83.878 | 90.5299 | 97.5824 | 104.5878 | 111.6033
CentraliaWind2030RCP4.5 | Centralia | Wind | RCP4.5 | 2030 | 83.9664 | 90.646 | 97.7344 | 104.771 | 111.8185
CentraliaWind2035RCP4.5 | Centralia | Wind | RCP4.5 | 2035 | 84.0548 | 90.762 | 97.8864 | 104.9542 | 112.0337
CentraliaWind2040RCP4.5 | Centralia | Wind | RCP4.5 | 2040 | 84.1433 | 90.8781 | 98.0384 | 105.1373 | 112.249
CentraliaWind2045RCP4.5 | Centralia | Wind | RCP4.5 | 2045 | 84.2317 | 90.9942 | 98.1904 | 105.3205 | 112.4642
CentraliaWind2050RCP4.5 | Centralia | Wind | RCP4.5 | 2050 | 84.3533 | 91.1513 | 98.3942 | 105.5633 | 112.7451
CentraliaWind2055RCP4.5 | Centralia | Wind | RCP4.5 | 2055 | 84.3864 | 91.1924 | 98.4461 | 105.6229 | 112.8108
CentraliaWind2060RCP4.5 | Centralia | Wind | RCP4.5 | 2060 | 84.4196 | 91.2334 | 98.4979 | 105.6824 | 112.8764
CentraliaWind2065RCP4.5 | Centralia | Wind | RCP4.5 | 2065 | 84.4527 | 91.2745 | 98.5498 | 105.742 | 112.9421
CentraliaWind2070RCP4.5 | Centralia | Wind | RCP4.5 | 2070 | 84.4859 | 91.3156 | 98.6016 | 105.8016 | 113.0077
CentraliaWind2075RCP4.5 | Centralia | Wind | RCP4.5 | 2075 | 84.5881 | 91.4525 | 98.7808 | 106.0173 | 113.2631
CentraliaWind2080RCP4.5 | Centralia | Wind | RCP4.5 | 2080 | 84.6904 | 91.5894 | 98.96 | 106.233 | 113.5185
CentraliaWind2085RCP4.5 | Centralia | Wind | RCP4.5 | 2085 | 84.7926 | 91.7263 | 99.1392 | 106.4487 | 113.7738
CentraliaWind2090RCP4.5 | Centralia | Wind | RCP4.5 | 2090 | 84.8948 | 91.8632 | 99.3184 | 106.6644 | 114.0292
CentraliaWind2095RCP4.5 | Centralia | Wind | RCP4.5 | 2095 | 84.9971 | 92.0001 | 99.4976 | 106.8802 | 114.2845
CentraliaWind2100RCP4.5 | Centralia | Wind | RCP4.5 | 2100 | 85.0993 | 92.137 | 99.6768 | 107.0959 | 114.5399
CentraliaWind2023RCP6.0 | Centralia | Wind | RCP6.0 | 2023 | 83.7896 | 90.4139 | 97.4304 | 104.4046 | 111.388
CentraliaWind2025RCP6.0 | Centralia | Wind | RCP6.0 | 2025 | 83.878 | 90.5299 | 97.5824 | 104.5878 | 111.6033
CentraliaWind2030RCP6.0 | Centralia | Wind | RCP6.0 | 2030 | 83.9664 | 90.646 | 97.7344 | 104.771 | 111.8185
CentraliaWind2035RCP6.0 | Centralia | Wind | RCP6.0 | 2035 | 84.0548 | 90.762 | 97.8864 | 104.9542 | 112.0337
CentraliaWind2040RCP6.0 | Centralia | Wind | RCP6.0 | 2040 | 84.1433 | 90.8781 | 98.0384 | 105.1373 | 112.249
CentraliaWind2045RCP6.0 | Centralia | Wind | RCP6.0 | 2045 | 84.2317 | 90.9942 | 98.1904 | 105.3205 | 112.4642
CentraliaWind2050RCP6.0 | Centralia | Wind | RCP6.0 | 2050 | 84.3533 | 91.1513 | 98.3942 | 105.5633 | 112.7451
CentraliaWind2055RCP6.0 | Centralia | Wind | RCP6.0 | 2055 | 84.3864 | 91.1924 | 98.4461 | 105.6229 | 112.8108
CentraliaWind2060RCP6.0 | Centralia | Wind | RCP6.0 | 2060 | 84.4196 | 91.2334 | 98.4979 | 105.6824 | 112.8764
CentraliaWind2065RCP6.0 | Centralia | Wind | RCP6.0 | 2065 | 84.4527 | 91.2745 | 98.5498 | 105.742 | 112.9421
CentraliaWind2070RCP6.0 | Centralia | Wind | RCP6.0 | 2070 | 84.4859 | 91.3156 | 98.6016 | 105.8016 | 113.0077
CentraliaWind2075RCP6.0 | Centralia | Wind | RCP6.0 | 2075 | 84.6392 | 91.5209 | 98.8704 | 106.1252 | 113.3908
CentraliaWind2080RCP6.0 | Centralia | Wind | RCP6.0 | 2080 | 84.7926 | 91.7263 | 99.1392 | 106.4487 | 113.7738
CentraliaWind2085RCP6.0 | Centralia | Wind | RCP6.0 | 2085 | 84.9459 | 91.9316 | 99.408 | 106.7723 | 114.1569
CentraliaWind2090RCP6.0 | Centralia | Wind | RCP6.0 | 2090 | 85.3977 | 92.4941 | 100.1024 | 107.5855 | 115.0908
CentraliaWind2095RCP6.0 | Centralia | Wind | RCP6.0 | 2095 | 85.6961 | 92.8512 | 100.528 | 108.0751 | 115.6416
CentraliaWind2100RCP6.0 | Centralia | Wind | RCP6.0 | 2100 | 85.9946 | 93.2083 | 100.9536 | 108.5648 | 116.1924
CentraliaWind2023RCP8.5 | Centralia | Wind | RCP8.5 | 2023 | 83.7896 | 90.4139 | 97.4304 | 104.4046 | 111.388
CentraliaWind2025RCP8.5 | Centralia | Wind | RCP8.5 | 2025 | 83.9664 | 90.646 | 97.7344 | 104.771 | 111.8185
CentraliaWind2030RCP8.5 | Centralia | Wind | RCP8.5 | 2030 | 84.1433 | 90.8781 | 98.0384 | 105.1373 | 112.249
CentraliaWind2035RCP8.5 | Centralia | Wind | RCP8.5 | 2035 | 84.3201 | 91.1102 | 98.3424 | 105.5037 | 112.6794
CentraliaWind2040RCP8.5 | Centralia | Wind | RCP8.5 | 2040 | 84.3754 | 91.1787 | 98.4288 | 105.603 | 112.7889
CentraliaWind2045RCP8.5 | Centralia | Wind | RCP8.5 | 2045 | 84.4306 | 91.2471 | 98.5152 | 105.7023 | 112.8983
CentraliaWind2050RCP8.5 | Centralia | Wind | RCP8.5 | 2050 | 84.6904 | 91.5894 | 98.96 | 106.233 | 113.5185
CentraliaWind2055RCP8.5 | Centralia | Wind | RCP8.5 | 2055 | 84.8948 | 91.8632 | 99.3184 | 106.6644 | 114.0292
CentraliaWind2060RCP8.5 | Centralia | Wind | RCP8.5 | 2060 | 85.3977 | 92.4941 | 100.1024 | 107.5855 | 115.0908
CentraliaWind2065RCP8.5 | Centralia | Wind | RCP8.5 | 2065 | 85.6961 | 92.8512 | 100.528 | 108.0751 | 115.6416
CentraliaWind2070RCP8.5 | Centralia | Wind | RCP8.5 | 2070 | 86.2571 | 93.5535 | 101.408 | 109.1058 | 116.8272
CentraliaWind2075RCP8.5 | Centralia | Wind | RCP8.5 | 2075 | 86.5196 | 93.8988 | 101.8624 | 109.6468 | 117.462
CentraliaWind2080RCP8.5 | Centralia | Wind | RCP8.5 | 2080 | 86.7821 | 94.244 | 102.3168 | 110.1877 | 118.0967
CentraliaWind2085RCP8.5 | Centralia | Wind | RCP8.5 | 2085 | 87.1302 | 94.6859 | 102.8784 | 110.8554 | 118.8683
CentraliaWind2090RCP8.5 | Centralia | Wind | RCP8.5 | 2090 | 87.4784 | 95.1278 | 103.44 | 111.5231 | 119.6398
CentraliaWind2095RCP8.5 | Centralia | Wind | RCP8.5 | 2095 | 87.4784 | 95.1278 | 103.44 | 111.5231 | 119.6398
CentraliaWind2100RCP8.5 | Centralia | Wind | RCP8.5 | 2100 | 87.4784 | 95.1278 | 103.44 | 111.5231 | 119.6398
ChapleauIce Accretion2023RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2023 | 12.1015 | 14.4486 | 17.408 | 19.671 | 21.9341
ChapleauIce Accretion2025RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2025 | 12.133 | 14.4792 | 17.4392 | 19.7031 | 21.9662
ChapleauIce Accretion2030RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2030 | 12.1645 | 14.5098 | 17.4703 | 19.7351 | 21.9983
ChapleauIce Accretion2035RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2035 | 12.1961 | 14.5404 | 17.5015 | 19.7671 | 22.0305
ChapleauIce Accretion2040RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2040 | 12.2276 | 14.5709 | 17.5327 | 19.7991 | 22.0626
ChapleauIce Accretion2045RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2045 | 12.2592 | 14.6015 | 17.5638 | 19.8311 | 22.0947
ChapleauIce Accretion2050RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2050 | 12.3664 | 14.7224 | 17.7038 | 19.9861 | 22.2639
ChapleauIce Accretion2055RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2055 | 12.4421 | 14.8127 | 17.8126 | 20.109 | 22.401
ChapleauIce Accretion2060RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2060 | 12.5179 | 14.903 | 17.9214 | 20.232 | 22.5381
ChapleauIce Accretion2065RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2065 | 12.5936 | 14.9933 | 18.0302 | 20.3549 | 22.6752
ChapleauIce Accretion2070RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2070 | 12.6693 | 15.0836 | 18.139 | 20.4779 | 22.8123
ChapleauIce Accretion2075RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2075 | 12.6653 | 15.0836 | 18.1447 | 20.4875 | 22.8266
ChapleauIce Accretion2080RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2080 | 12.6614 | 15.0836 | 18.1503 | 20.4971 | 22.8409
ChapleauIce Accretion2085RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2085 | 12.6574 | 15.0836 | 18.156 | 20.5067 | 22.8551
ChapleauIce Accretion2090RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2090 | 12.6535 | 15.0836 | 18.1617 | 20.5163 | 22.8694
ChapleauIce Accretion2095RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2095 | 12.6496 | 15.0836 | 18.1673 | 20.5259 | 22.8837
ChapleauIce Accretion2100RCP4.5 | Chapleau | Ice Accretion | RCP4.5 | 2100 | 12.6456 | 15.0836 | 18.173 | 20.5355 | 22.898
ChapleauIce Accretion2023RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2023 | 12.1015 | 14.4486 | 17.408 | 19.671 | 21.9341
ChapleauIce Accretion2025RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2025 | 12.133 | 14.4792 | 17.4392 | 19.7031 | 21.9662
ChapleauIce Accretion2030RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2030 | 12.1645 | 14.5098 | 17.4703 | 19.7351 | 21.9983
ChapleauIce Accretion2035RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2035 | 12.1961 | 14.5404 | 17.5015 | 19.7671 | 22.0305
ChapleauIce Accretion2040RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2040 | 12.2276 | 14.5709 | 17.5327 | 19.7991 | 22.0626
ChapleauIce Accretion2045RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2045 | 12.2592 | 14.6015 | 17.5638 | 19.8311 | 22.0947
ChapleauIce Accretion2050RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2050 | 12.3664 | 14.7224 | 17.7038 | 19.9861 | 22.2639
ChapleauIce Accretion2055RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2055 | 12.4421 | 14.8127 | 17.8126 | 20.109 | 22.401
ChapleauIce Accretion2060RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2060 | 12.5179 | 14.903 | 17.9214 | 20.232 | 22.5381
ChapleauIce Accretion2065RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2065 | 12.5936 | 14.9933 | 18.0302 | 20.3549 | 22.6752
ChapleauIce Accretion2070RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2070 | 12.6693 | 15.0836 | 18.139 | 20.4779 | 22.8123
ChapleauIce Accretion2075RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2075 | 12.6634 | 15.0836 | 18.1475 | 20.4923 | 22.8337
ChapleauIce Accretion2080RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2080 | 12.6574 | 15.0836 | 18.156 | 20.5067 | 22.8551
ChapleauIce Accretion2085RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2085 | 12.6515 | 15.0836 | 18.1645 | 20.5211 | 22.8766
ChapleauIce Accretion2090RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2090 | 12.5155 | 14.9378 | 18.0143 | 20.3626 | 22.7123
ChapleauIce Accretion2095RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2095 | 12.3854 | 14.792 | 17.8557 | 20.1897 | 22.5267
ChapleauIce Accretion2100RCP6.0 | Chapleau | Ice Accretion | RCP6.0 | 2100 | 12.2552 | 14.6462 | 17.697 | 20.0168 | 22.3411
ChapleauIce Accretion2023RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2023 | 12.1015 | 14.4486 | 17.408 | 19.671 | 21.9341
ChapleauIce Accretion2025RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2025 | 12.1645 | 14.5098 | 17.4703 | 19.7351 | 21.9983
ChapleauIce Accretion2030RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2030 | 12.2276 | 14.5709 | 17.5327 | 19.7991 | 22.0626
ChapleauIce Accretion2035RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2035 | 12.2907 | 14.6321 | 17.595 | 19.8631 | 22.1269
ChapleauIce Accretion2040RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2040 | 12.4169 | 14.7826 | 17.7763 | 20.068 | 22.3553
ChapleauIce Accretion2045RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2045 | 12.5431 | 14.9331 | 17.9577 | 20.273 | 22.5838
ChapleauIce Accretion2050RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2050 | 12.6614 | 15.0836 | 18.1503 | 20.4971 | 22.8409
ChapleauIce Accretion2055RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2055 | 12.6535 | 15.0836 | 18.1617 | 20.5163 | 22.8694
ChapleauIce Accretion2060RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2060 | 12.5155 | 14.9378 | 18.0143 | 20.3626 | 22.7123
ChapleauIce Accretion2065RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2065 | 12.3854 | 14.792 | 17.8557 | 20.1897 | 22.5267
ChapleauIce Accretion2070RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2070 | 12.2671 | 14.6744 | 17.7367 | 20.068 | 22.4053
ChapleauIce Accretion2075RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2075 | 12.2789 | 14.7026 | 17.7763 | 20.1193 | 22.4696
ChapleauIce Accretion2080RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2080 | 12.2907 | 14.7308 | 17.816 | 20.1705 | 22.5338
ChapleauIce Accretion2085RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2085 | 12.2198 | 14.6673 | 17.7565 | 20.1225 | 22.491
ChapleauIce Accretion2090RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2090 | 12.1488 | 14.6038 | 17.697 | 20.0744 | 22.4482
ChapleauIce Accretion2095RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2095 | 12.1488 | 14.6038 | 17.697 | 20.0744 | 22.4482
ChapleauIce Accretion2100RCP8.5 | Chapleau | Ice Accretion | RCP8.5 | 2100 | 12.1488 | 14.6038 | 17.697 | 20.0744 | 22.4482
ChapleauWind2023RCP4.5 | Chapleau | Wind | RCP4.5 | 2023 | 71.3932 | 76.9311 | 82.7708 | 88.5999 | 94.4335
ChapleauWind2025RCP4.5 | Chapleau | Wind | RCP4.5 | 2025 | 71.4452 | 76.9883 | 82.8337 | 88.6686 | 94.5067
ChapleauWind2030RCP4.5 | Chapleau | Wind | RCP4.5 | 2030 | 71.4971 | 77.0455 | 82.8965 | 88.7373 | 94.5799
ChapleauWind2035RCP4.5 | Chapleau | Wind | RCP4.5 | 2035 | 71.549 | 77.1027 | 82.9594 | 88.806 | 94.6532
ChapleauWind2040RCP4.5 | Chapleau | Wind | RCP4.5 | 2040 | 71.6009 | 77.1599 | 83.0223 | 88.8748 | 94.7264
ChapleauWind2045RCP4.5 | Chapleau | Wind | RCP4.5 | 2045 | 71.6529 | 77.2171 | 83.0851 | 88.9435 | 94.7996
ChapleauWind2050RCP4.5 | Chapleau | Wind | RCP4.5 | 2050 | 71.7119 | 77.2651 | 83.1185 | 88.9649 | 94.8093
ChapleauWind2055RCP4.5 | Chapleau | Wind | RCP4.5 | 2055 | 71.719 | 77.256 | 83.089 | 88.9175 | 94.7457
ChapleauWind2060RCP4.5 | Chapleau | Wind | RCP4.5 | 2060 | 71.726 | 77.2468 | 83.0594 | 88.8701 | 94.6822
ChapleauWind2065RCP4.5 | Chapleau | Wind | RCP4.5 | 2065 | 71.7331 | 77.2377 | 83.0299 | 88.8227 | 94.6186
ChapleauWind2070RCP4.5 | Chapleau | Wind | RCP4.5 | 2070 | 71.7402 | 77.2285 | 83.0004 | 88.7753 | 94.555
ChapleauWind2075RCP4.5 | Chapleau | Wind | RCP4.5 | 2075 | 71.8417 | 77.3416 | 83.1248 | 88.9128 | 94.7046
ChapleauWind2080RCP4.5 | Chapleau | Wind | RCP4.5 | 2080 | 71.9432 | 77.4547 | 83.2491 | 89.0503 | 94.8542
ChapleauWind2085RCP4.5 | Chapleau | Wind | RCP4.5 | 2085 | 72.0447 | 77.5679 | 83.3735 | 89.1877 | 95.0037
ChapleauWind2090RCP4.5 | Chapleau | Wind | RCP4.5 | 2090 | 72.1461 | 77.681 | 83.4979 | 89.3252 | 95.1533
ChapleauWind2095RCP4.5 | Chapleau | Wind | RCP4.5 | 2095 | 72.2476 | 77.7941 | 83.6222 | 89.4626 | 95.3029
ChapleauWind2100RCP4.5 | Chapleau | Wind | RCP4.5 | 2100 | 72.3491 | 77.9072 | 83.7466 | 89.6001 | 95.4524
ChapleauWind2023RCP6.0 | Chapleau | Wind | RCP6.0 | 2023 | 71.3932 | 76.9311 | 82.7708 | 88.5999 | 94.4335
ChapleauWind2025RCP6.0 | Chapleau | Wind | RCP6.0 | 2025 | 71.4452 | 76.9883 | 82.8337 | 88.6686 | 94.5067
ChapleauWind2030RCP6.0 | Chapleau | Wind | RCP6.0 | 2030 | 71.4971 | 77.0455 | 82.8965 | 88.7373 | 94.5799
ChapleauWind2035RCP6.0 | Chapleau | Wind | RCP6.0 | 2035 | 71.549 | 77.1027 | 82.9594 | 88.806 | 94.6532
ChapleauWind2040RCP6.0 | Chapleau | Wind | RCP6.0 | 2040 | 71.6009 | 77.1599 | 83.0223 | 88.8748 | 94.7264
ChapleauWind2045RCP6.0 | Chapleau | Wind | RCP6.0 | 2045 | 71.6529 | 77.2171 | 83.0851 | 88.9435 | 94.7996
ChapleauWind2050RCP6.0 | Chapleau | Wind | RCP6.0 | 2050 | 71.7119 | 77.2651 | 83.1185 | 88.9649 | 94.8093
ChapleauWind2055RCP6.0 | Chapleau | Wind | RCP6.0 | 2055 | 71.719 | 77.256 | 83.089 | 88.9175 | 94.7457
ChapleauWind2060RCP6.0 | Chapleau | Wind | RCP6.0 | 2060 | 71.726 | 77.2468 | 83.0594 | 88.8701 | 94.6822
ChapleauWind2065RCP6.0 | Chapleau | Wind | RCP6.0 | 2065 | 71.7331 | 77.2377 | 83.0299 | 88.8227 | 94.6186
ChapleauWind2070RCP6.0 | Chapleau | Wind | RCP6.0 | 2070 | 71.7402 | 77.2285 | 83.0004 | 88.7753 | 94.555
ChapleauWind2075RCP6.0 | Chapleau | Wind | RCP6.0 | 2075 | 71.8924 | 77.3982 | 83.1869 | 88.9815 | 94.7794
ChapleauWind2080RCP6.0 | Chapleau | Wind | RCP6.0 | 2080 | 72.0447 | 77.5679 | 83.3735 | 89.1877 | 95.0037
ChapleauWind2085RCP6.0 | Chapleau | Wind | RCP6.0 | 2085 | 72.1969 | 77.7375 | 83.5601 | 89.3939 | 95.2281
ChapleauWind2090RCP6.0 | Chapleau | Wind | RCP6.0 | 2090 | 72.5639 | 78.1716 | 84.0773 | 89.9832 | 95.8887
ChapleauWind2095RCP6.0 | Chapleau | Wind | RCP6.0 | 2095 | 72.7787 | 78.436 | 84.4081 | 90.3664 | 96.3249
ChapleauWind2100RCP6.0 | Chapleau | Wind | RCP6.0 | 2100 | 72.9935 | 78.7003 | 84.7388 | 90.7495 | 96.7611
ChapleauWind2023RCP8.5 | Chapleau | Wind | RCP8.5 | 2023 | 71.3932 | 76.9311 | 82.7708 | 88.5999 | 94.4335
ChapleauWind2025RCP8.5 | Chapleau | Wind | RCP8.5 | 2025 | 71.4971 | 77.0455 | 82.8965 | 88.7373 | 94.5799
ChapleauWind2030RCP8.5 | Chapleau | Wind | RCP8.5 | 2030 | 71.6009 | 77.1599 | 83.0223 | 88.8748 | 94.7264
ChapleauWind2035RCP8.5 | Chapleau | Wind | RCP8.5 | 2035 | 71.7048 | 77.2743 | 83.148 | 89.0122 | 94.8729
ChapleauWind2040RCP8.5 | Chapleau | Wind | RCP8.5 | 2040 | 71.7166 | 77.259 | 83.0988 | 88.9333 | 94.7669
ChapleauWind2045RCP8.5 | Chapleau | Wind | RCP8.5 | 2045 | 71.7284 | 77.2438 | 83.0496 | 88.8543 | 94.661
ChapleauWind2050RCP8.5 | Chapleau | Wind | RCP8.5 | 2050 | 71.9432 | 77.4547 | 83.2491 | 89.0503 | 94.8542
ChapleauWind2055RCP8.5 | Chapleau | Wind | RCP8.5 | 2055 | 72.1461 | 77.681 | 83.4979 | 89.3252 | 95.1533
ChapleauWind2060RCP8.5 | Chapleau | Wind | RCP8.5 | 2060 | 72.5639 | 78.1716 | 84.0773 | 89.9832 | 95.8887
ChapleauWind2065RCP8.5 | Chapleau | Wind | RCP8.5 | 2065 | 72.7787 | 78.436 | 84.4081 | 90.3664 | 96.3249
ChapleauWind2070RCP8.5 | Chapleau | Wind | RCP8.5 | 2070 | 73.1823 | 78.9164 | 84.9821 | 91.0186 | 97.0572
ChapleauWind2075RCP8.5 | Chapleau | Wind | RCP8.5 | 2075 | 73.3711 | 79.1325 | 85.2253 | 91.2876 | 97.3532
ChapleauWind2080RCP8.5 | Chapleau | Wind | RCP8.5 | 2080 | 73.5599 | 79.3485 | 85.4686 | 91.5567 | 97.6492
ChapleauWind2085RCP8.5 | Chapleau | Wind | RCP8.5 | 2085 | 73.6803 | 79.5087 | 85.6777 | 91.8111 | 97.9437
ChapleauWind2090RCP8.5 | Chapleau | Wind | RCP8.5 | 2090 | 73.8006 | 79.6688 | 85.8868 | 92.0656 | 98.2381
ChapleauWind2095RCP8.5 | Chapleau | Wind | RCP8.5 | 2095 | 73.8006 | 79.6688 | 85.8868 | 92.0656 | 98.2381
ChapleauWind2100RCP8.5 | Chapleau | Wind | RCP8.5 | 2100 | 73.8006 | 79.6688 | 85.8868 | 92.0656 | 98.2381
ChathamIce Accretion2023RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2023 | 19.172 | 22.9844 | 27.804 | 31.4818 | 35.1742
ChathamIce Accretion2025RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2025 | 19.0518 | 22.8643 | 27.6827 | 31.3552 | 35.0389
ChathamIce Accretion2030RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2030 | 18.9317 | 22.7442 | 27.5613 | 31.2287 | 34.9037
ChathamIce Accretion2035RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2035 | 18.8115 | 22.6241 | 27.44 | 31.1021 | 34.7684
ChathamIce Accretion2040RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2040 | 18.6914 | 22.5041 | 27.3187 | 30.9756 | 34.6332
ChathamIce Accretion2045RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2045 | 18.5712 | 22.384 | 27.1973 | 30.849 | 34.498
ChathamIce Accretion2050RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2050 | 18.0107 | 21.7712 | 26.5104 | 30.1023 | 33.6853
ChathamIce Accretion2055RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2055 | 17.5704 | 21.2785 | 25.9448 | 29.4822 | 33.008
ChathamIce Accretion2060RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2060 | 17.1301 | 20.7859 | 25.3792 | 28.862 | 32.3306
ChathamIce Accretion2065RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2065 | 16.6897 | 20.2932 | 24.8136 | 28.2419 | 31.6532
ChathamIce Accretion2070RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2070 | 16.2494 | 19.8005 | 24.248 | 27.6217 | 30.9758
ChathamIce Accretion2075RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2075 | 15.824 | 19.3086 | 23.674 | 26.9836 | 30.2702
ChathamIce Accretion2080RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2080 | 15.3986 | 18.8167 | 23.1 | 26.3456 | 29.5646
ChathamIce Accretion2085RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2085 | 14.9732 | 18.3247 | 22.526 | 25.7075 | 28.859
ChathamIce Accretion2090RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2090 | 14.5478 | 17.8328 | 21.952 | 25.0694 | 28.1534
ChathamIce Accretion2095RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2095 | 14.1224 | 17.3409 | 21.378 | 24.4314 | 27.4478
ChathamIce Accretion2100RCP4.5 | Chatham | Ice Accretion | RCP4.5 | 2100 | 13.697 | 16.849 | 20.804 | 23.7933 | 26.7422
ChathamIce Accretion2023RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2023 | 19.172 | 22.9844 | 27.804 | 31.4818 | 35.1742
ChathamIce Accretion2025RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2025 | 19.0518 | 22.8643 | 27.6827 | 31.3552 | 35.0389
ChathamIce Accretion2030RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2030 | 18.9317 | 22.7442 | 27.5613 | 31.2287 | 34.9037
ChathamIce Accretion2035RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2035 | 18.8115 | 22.6241 | 27.44 | 31.1021 | 34.7684
ChathamIce Accretion2040RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2040 | 18.6914 | 22.5041 | 27.3187 | 30.9756 | 34.6332
ChathamIce Accretion2045RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2045 | 18.5712 | 22.384 | 27.1973 | 30.849 | 34.498
ChathamIce Accretion2050RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2050 | 18.0107 | 21.7712 | 26.5104 | 30.1023 | 33.6853
ChathamIce Accretion2055RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2055 | 17.5704 | 21.2785 | 25.9448 | 29.4822 | 33.008
ChathamIce Accretion2060RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2060 | 17.1301 | 20.7859 | 25.3792 | 28.862 | 32.3306
ChathamIce Accretion2065RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2065 | 16.6897 | 20.2932 | 24.8136 | 28.2419 | 31.6532
ChathamIce Accretion2070RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2070 | 16.2494 | 19.8005 | 24.248 | 27.6217 | 30.9758
ChathamIce Accretion2075RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2075 | 15.6113 | 19.0626 | 23.387 | 26.6646 | 29.9174
ChathamIce Accretion2080RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2080 | 14.9732 | 18.3247 | 22.526 | 25.7075 | 28.859
ChathamIce Accretion2085RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2085 | 14.3351 | 17.5869 | 21.665 | 24.7504 | 27.8006
ChathamIce Accretion2090RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2090 | 12.7229 | 15.687 | 19.3947 | 22.2007 | 24.9665
ChathamIce Accretion2095RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2095 | 11.7487 | 14.525 | 17.9853 | 20.6082 | 23.1907
ChathamIce Accretion2100RCP6.0 | Chatham | Ice Accretion | RCP6.0 | 2100 | 10.7745 | 13.363 | 16.576 | 19.0156 | 21.415
ChathamIce Accretion2023RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2023 | 19.172 | 22.9844 | 27.804 | 31.4818 | 35.1742
ChathamIce Accretion2025RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2025 | 18.9317 | 22.7442 | 27.5613 | 31.2287 | 34.9037
ChathamIce Accretion2030RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2030 | 18.6914 | 22.5041 | 27.3187 | 30.9756 | 34.6332
ChathamIce Accretion2035RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2035 | 18.4511 | 22.2639 | 27.076 | 30.7224 | 34.3627
ChathamIce Accretion2040RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2040 | 17.7172 | 21.4428 | 26.1333 | 29.6889 | 33.2338
ChathamIce Accretion2045RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2045 | 16.9833 | 20.6216 | 25.1907 | 28.6553 | 32.1048
ChathamIce Accretion2050RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2050 | 15.3986 | 18.8167 | 23.1 | 26.3456 | 29.5646
ChathamIce Accretion2055RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2055 | 14.5478 | 17.8328 | 21.952 | 25.0694 | 28.1534
ChathamIce Accretion2060RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2060 | 12.7229 | 15.687 | 19.3947 | 22.2007 | 24.9665
ChathamIce Accretion2065RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2065 | 11.7487 | 14.525 | 17.9853 | 20.6082 | 23.1907
ChathamIce Accretion2070RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2070 | 10.2354 | 12.72 | 15.8013 | 18.1297 | 20.4271
ChathamIce Accretion2075RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2075 | 9.6964 | 12.0771 | 15.0267 | 17.2438 | 19.4393
ChathamIce Accretion2080RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2080 | 9.1573 | 11.4341 | 14.252 | 16.3579 | 18.4514
ChathamIce Accretion2085RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2085 | 8.417 | 10.5393 | 13.174 | 15.1397 | 17.0932
ChathamIce Accretion2090RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2090 | 7.6766 | 9.6446 | 12.096 | 13.9216 | 15.7349
ChathamIce Accretion2095RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2095 | 7.6766 | 9.6446 | 12.096 | 13.9216 | 15.7349
ChathamIce Accretion2100RCP8.5 | Chatham | Ice Accretion | RCP8.5 | 2100 | 7.6766 | 9.6446 | 12.096 | 13.9216 | 15.7349
ChathamWind2023RCP4.5 | Chatham | Wind | RCP4.5 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.368
ChathamWind2025RCP4.5 | Chatham | Wind | RCP4.5 | 2025 | 85.0909 | 91.6975 | 98.6697 | 105.6307 | 112.5951
ChathamWind2030RCP4.5 | Chatham | Wind | RCP4.5 | 2030 | 85.1798 | 91.8175 | 98.8297 | 105.8247 | 112.8223
ChathamWind2035RCP4.5 | Chatham | Wind | RCP4.5 | 2035 | 85.2686 | 91.9375 | 98.9898 | 106.0187 | 113.0495
ChathamWind2040RCP4.5 | Chatham | Wind | RCP4.5 | 2040 | 85.3575 | 92.0575 | 99.1499 | 106.2127 | 113.2766
ChathamWind2045RCP4.5 | Chatham | Wind | RCP4.5 | 2045 | 85.4463 | 92.1775 | 99.3099 | 106.4067 | 113.5038
ChathamWind2050RCP4.5 | Chatham | Wind | RCP4.5 | 2050 | 85.6435 | 92.4415 | 99.6582 | 106.8272 | 113.9969
ChathamWind2055RCP4.5 | Chatham | Wind | RCP4.5 | 2055 | 85.7518 | 92.5855 | 99.8463 | 107.0537 | 114.2627
ChathamWind2060RCP4.5 | Chatham | Wind | RCP4.5 | 2060 | 85.8601 | 92.7295 | 100.0345 | 107.2802 | 114.5286
ChathamWind2065RCP4.5 | Chatham | Wind | RCP4.5 | 2065 | 85.9684 | 92.8735 | 100.2226 | 107.5067 | 114.7945
ChathamWind2070RCP4.5 | Chatham | Wind | RCP4.5 | 2070 | 86.0768 | 93.0175 | 100.4108 | 107.7332 | 115.0604
ChathamWind2075RCP4.5 | Chatham | Wind | RCP4.5 | 2075 | 86.2601 | 93.256 | 100.7179 | 108.0967 | 115.485
ChathamWind2080RCP4.5 | Chatham | Wind | RCP4.5 | 2080 | 86.4435 | 93.4945 | 101.0249 | 108.4602 | 115.9095
ChathamWind2085RCP4.5 | Chatham | Wind | RCP4.5 | 2085 | 86.6268 | 93.7329 | 101.332 | 108.8237 | 116.334
ChathamWind2090RCP4.5 | Chatham | Wind | RCP4.5 | 2090 | 86.8101 | 93.9714 | 101.6391 | 109.1872 | 116.7586
ChathamWind2095RCP4.5 | Chatham | Wind | RCP4.5 | 2095 | 86.9935 | 94.2099 | 101.9461 | 109.5507 | 117.1831
ChathamWind2100RCP4.5 | Chatham | Wind | RCP4.5 | 2100 | 87.1768 | 94.4484 | 102.2532 | 109.9143 | 117.6076
ChathamWind2023RCP6.0 | Chatham | Wind | RCP6.0 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.368
ChathamWind2025RCP6.0 | Chatham | Wind | RCP6.0 | 2025 | 85.0909 | 91.6975 | 98.6697 | 105.6307 | 112.5951
ChathamWind2030RCP6.0 | Chatham | Wind | RCP6.0 | 2030 | 85.1798 | 91.8175 | 98.8297 | 105.8247 | 112.8223
ChathamWind2035RCP6.0 | Chatham | Wind | RCP6.0 | 2035 | 85.2686 | 91.9375 | 98.9898 | 106.0187 | 113.0495
ChathamWind2040RCP6.0 | Chatham | Wind | RCP6.0 | 2040 | 85.3575 | 92.0575 | 99.1499 | 106.2127 | 113.2766
ChathamWind2045RCP6.0 | Chatham | Wind | RCP6.0 | 2045 | 85.4463 | 92.1775 | 99.3099 | 106.4067 | 113.5038
ChathamWind2050RCP6.0 | Chatham | Wind | RCP6.0 | 2050 | 85.6435 | 92.4415 | 99.6582 | 106.8272 | 113.9969
ChathamWind2055RCP6.0 | Chatham | Wind | RCP6.0 | 2055 | 85.7518 | 92.5855 | 99.8463 | 107.0537 | 114.2627
ChathamWind2060RCP6.0 | Chatham | Wind | RCP6.0 | 2060 | 85.8601 | 92.7295 | 100.0345 | 107.2802 | 114.5286
ChathamWind2065RCP6.0 | Chatham | Wind | RCP6.0 | 2065 | 85.9684 | 92.8735 | 100.2226 | 107.5067 | 114.7945
ChathamWind2070RCP6.0 | Chatham | Wind | RCP6.0 | 2070 | 86.0768 | 93.0175 | 100.4108 | 107.7332 | 115.0604
ChathamWind2075RCP6.0 | Chatham | Wind | RCP6.0 | 2075 | 86.3518 | 93.3752 | 100.8714 | 108.2784 | 115.6972
ChathamWind2080RCP6.0 | Chatham | Wind | RCP6.0 | 2080 | 86.6268 | 93.7329 | 101.332 | 108.8237 | 116.334
ChathamWind2085RCP6.0 | Chatham | Wind | RCP6.0 | 2085 | 86.9018 | 94.0907 | 101.7926 | 109.369 | 116.9708
ChathamWind2090RCP6.0 | Chatham | Wind | RCP6.0 | 2090 | 87.5661 | 94.9375 | 102.8673 | 110.6343 | 118.4381
ChathamWind2095RCP6.0 | Chatham | Wind | RCP6.0 | 2095 | 87.9554 | 95.4266 | 103.4815 | 111.3543 | 119.2685
ChathamWind2100RCP6.0 | Chatham | Wind | RCP6.0 | 2100 | 88.3446 | 95.9157 | 104.0956 | 112.0744 | 120.099
ChathamWind2023RCP8.5 | Chatham | Wind | RCP8.5 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.368
ChathamWind2025RCP8.5 | Chatham | Wind | RCP8.5 | 2025 | 85.1798 | 91.8175 | 98.8297 | 105.8247 | 112.8223
ChathamWind2030RCP8.5 | Chatham | Wind | RCP8.5 | 2030 | 85.3575 | 92.0575 | 99.1499 | 106.2127 | 113.2766
ChathamWind2035RCP8.5 | Chatham | Wind | RCP8.5 | 2035 | 85.5352 | 92.2975 | 99.47 | 106.6007 | 113.731
ChathamWind2040RCP8.5 | Chatham | Wind | RCP8.5 | 2040 | 85.7157 | 92.5375 | 99.7836 | 106.9782 | 114.1741
ChathamWind2045RCP8.5 | Chatham | Wind | RCP8.5 | 2045 | 85.8962 | 92.7775 | 100.0972 | 107.3557 | 114.6173
ChathamWind2050RCP8.5 | Chatham | Wind | RCP8.5 | 2050 | 86.4435 | 93.4945 | 101.0249 | 108.4602 | 115.9095
ChathamWind2055RCP8.5 | Chatham | Wind | RCP8.5 | 2055 | 86.8101 | 93.9714 | 101.6391 | 109.1872 | 116.7586
ChathamWind2060RCP8.5 | Chatham | Wind | RCP8.5 | 2060 | 87.5661 | 94.9375 | 102.8673 | 110.6343 | 118.4381
ChathamWind2065RCP8.5 | Chatham | Wind | RCP8.5 | 2065 | 87.9554 | 95.4266 | 103.4815 | 111.3543 | 119.2685
ChathamWind2070RCP8.5 | Chatham | Wind | RCP8.5 | 2070 | 88.5251 | 96.1405 | 104.3733 | 112.3994 | 120.4677
ChathamWind2075RCP8.5 | Chatham | Wind | RCP8.5 | 2075 | 88.7057 | 96.3654 | 104.6509 | 112.7245 | 120.8364
ChathamWind2080RCP8.5 | Chatham | Wind | RCP8.5 | 2080 | 88.8862 | 96.5902 | 104.9286 | 113.0496 | 121.205
ChathamWind2085RCP8.5 | Chatham | Wind | RCP8.5 | 2085 | 89.3855 | 97.219 | 105.7224 | 113.9828 | 122.2831
ChathamWind2090RCP8.5 | Chatham | Wind | RCP8.5 | 2090 | 89.8847 | 97.8479 | 106.5162 | 114.9161 | 123.3612
ChathamWind2095RCP8.5 | Chatham | Wind | RCP8.5 | 2095 | 89.8847 | 97.8479 | 106.5162 | 114.9161 | 123.3612
ChathamWind2100RCP8.5 | Chatham | Wind | RCP8.5 | 2100 | 89.8847 | 97.8479 | 106.5162 | 114.9161 | 123.3612
ChesleyIce Accretion2023RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2023 | 14.5982 | 17.4997 | 21.189 | 23.991 | 26.804
ChesleyIce Accretion2025RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2025 | 14.603 | 17.5201 | 21.2205 | 24.0345 | 26.8613
ChesleyIce Accretion2030RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2030 | 14.6079 | 17.5404 | 21.252 | 24.078 | 26.9186
ChesleyIce Accretion2035RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2035 | 14.6128 | 17.5607 | 21.2835 | 24.1215 | 26.976
ChesleyIce Accretion2040RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2040 | 14.6176 | 17.5811 | 21.315 | 24.165 | 27.0333
ChesleyIce Accretion2045RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2045 | 14.6225 | 17.6014 | 21.3465 | 24.2086 | 27.0906
ChesleyIce Accretion2050RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2050 | 14.6215 | 17.6322 | 21.4158 | 24.309 | 27.222
ChesleyIce Accretion2055RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2055 | 14.6157 | 17.6426 | 21.4536 | 24.366 | 27.2961
ChesleyIce Accretion2060RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2060 | 14.6098 | 17.6531 | 21.4914 | 24.4229 | 27.3702
ChesleyIce Accretion2065RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2065 | 14.604 | 17.6636 | 21.5292 | 24.4799 | 27.4443
ChesleyIce Accretion2070RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2070 | 14.5982 | 17.674 | 21.567 | 24.5368 | 27.5184
ChesleyIce Accretion2075RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2075 | 14.5348 | 17.6217 | 21.532 | 24.5091 | 27.5008
ChesleyIce Accretion2080RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2080 | 14.4715 | 17.5694 | 21.497 | 24.4814 | 27.4831
ChesleyIce Accretion2085RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2085 | 14.4082 | 17.5172 | 21.462 | 24.4538 | 27.4655
ChesleyIce Accretion2090RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2090 | 14.3449 | 17.4649 | 21.427 | 24.4261 | 27.4478
ChesleyIce Accretion2095RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2095 | 14.2815 | 17.4126 | 21.392 | 24.3984 | 27.4302
ChesleyIce Accretion2100RCP4.5 | Chesley | Ice Accretion | RCP4.5 | 2100 | 14.2182 | 17.3603 | 21.357 | 24.3707 | 27.4126
ChesleyIce Accretion2023RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2023 | 14.5982 | 17.4997 | 21.189 | 23.991 | 26.804
ChesleyIce Accretion2025RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2025 | 14.603 | 17.5201 | 21.2205 | 24.0345 | 26.8613
ChesleyIce Accretion2030RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2030 | 14.6079 | 17.5404 | 21.252 | 24.078 | 26.9186
ChesleyIce Accretion2035RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2035 | 14.6128 | 17.5607 | 21.2835 | 24.1215 | 26.976
ChesleyIce Accretion2040RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2040 | 14.6176 | 17.5811 | 21.315 | 24.165 | 27.0333
ChesleyIce Accretion2045RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2045 | 14.6225 | 17.6014 | 21.3465 | 24.2086 | 27.0906
ChesleyIce Accretion2050RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2050 | 14.6215 | 17.6322 | 21.4158 | 24.309 | 27.222
ChesleyIce Accretion2055RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2055 | 14.6157 | 17.6426 | 21.4536 | 24.366 | 27.2961
ChesleyIce Accretion2060RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2060 | 14.6098 | 17.6531 | 21.4914 | 24.4229 | 27.3702
ChesleyIce Accretion2065RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2065 | 14.604 | 17.6636 | 21.5292 | 24.4799 | 27.4443
ChesleyIce Accretion2070RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2070 | 14.5982 | 17.674 | 21.567 | 24.5368 | 27.5184
ChesleyIce Accretion2075RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2075 | 14.5032 | 17.5956 | 21.5145 | 24.4953 | 27.4919
ChesleyIce Accretion2080RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2080 | 14.4082 | 17.5172 | 21.462 | 24.4538 | 27.4655
ChesleyIce Accretion2085RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2085 | 14.3132 | 17.4387 | 21.4095 | 24.4122 | 27.439
ChesleyIce Accretion2090RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2090 | 13.9747 | 17.1046 | 21.07 | 24.0701 | 27.0862
ChesleyIce Accretion2095RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2095 | 13.7311 | 16.849 | 20.783 | 23.7695 | 26.7599
ChesleyIce Accretion2100RCP6.0 | Chesley | Ice Accretion | RCP6.0 | 2100 | 13.4876 | 16.5934 | 20.496 | 23.469 | 26.4335
ChesleyIce Accretion2023RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2023 | 14.5982 | 17.4997 | 21.189 | 23.991 | 26.804
ChesleyIce Accretion2025RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2025 | 14.6079 | 17.5404 | 21.252 | 24.078 | 26.9186
ChesleyIce Accretion2030RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2030 | 14.6176 | 17.5811 | 21.315 | 24.165 | 27.0333
ChesleyIce Accretion2035RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2035 | 14.6274 | 17.6217 | 21.378 | 24.2521 | 27.148
ChesleyIce Accretion2040RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2040 | 14.6176 | 17.6392 | 21.441 | 24.347 | 27.2714
ChesleyIce Accretion2045RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2045 | 14.6079 | 17.6566 | 21.504 | 24.4419 | 27.3949
ChesleyIce Accretion2050RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2050 | 14.4715 | 17.5694 | 21.497 | 24.4814 | 27.4831
ChesleyIce Accretion2055RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2055 | 14.3449 | 17.4649 | 21.427 | 24.4261 | 27.4478
ChesleyIce Accretion2060RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2060 | 13.9747 | 17.1046 | 21.07 | 24.0701 | 27.0862
ChesleyIce Accretion2065RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2065 | 13.7311 | 16.849 | 20.783 | 23.7695 | 26.7599
ChesleyIce Accretion2070RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2070 | 13.0882 | 16.1402 | 19.985 | 22.9074 | 25.825
ChesleyIce Accretion2075RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2075 | 12.6888 | 15.687 | 19.474 | 22.3457 | 25.2164
ChesleyIce Accretion2080RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2080 | 12.2893 | 15.2338 | 18.963 | 21.7841 | 24.6078
ChesleyIce Accretion2085RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2085 | 11.8875 | 14.7894 | 18.459 | 21.2383 | 24.0257
ChesleyIce Accretion2090RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2090 | 11.4856 | 14.3449 | 17.955 | 20.6926 | 23.4436
ChesleyIce Accretion2095RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2095 | 11.4856 | 14.3449 | 17.955 | 20.6926 | 23.4436
ChesleyIce Accretion2100RCP8.5 | Chesley | Ice Accretion | RCP8.5 | 2100 | 11.4856 | 14.3449 | 17.955 | 20.6926 | 23.4436
ChesleyWind2023RCP4.5 | Chesley | Wind | RCP4.5 | 2023 | 83.5906 | 90.1639 | 97.1136 | 104.0245 | 110.9393
ChesleyWind2025RCP4.5 | Chesley | Wind | RCP4.5 | 2025 | 83.6708 | 90.2621 | 97.2368 | 104.1684 | 111.1053
ChesleyWind2030RCP4.5 | Chesley | Wind | RCP4.5 | 2030 | 83.7509 | 90.3603 | 97.36 | 104.3122 | 111.2713
ChesleyWind2035RCP4.5 | Chesley | Wind | RCP4.5 | 2035 | 83.831 | 90.4585 | 97.4832 | 104.456 | 111.4373
ChesleyWind2040RCP4.5 | Chesley | Wind | RCP4.5 | 2040 | 83.9111 | 90.5567 | 97.6064 | 104.5998 | 111.6033
ChesleyWind2045RCP4.5 | Chesley | Wind | RCP4.5 | 2045 | 83.9913 | 90.6549 | 97.7296 | 104.7436 | 111.7692
ChesleyWind2050RCP4.5 | Chesley | Wind | RCP4.5 | 2050 | 84.0847 | 90.7656 | 97.8624 | 104.8956 | 111.9418
ChesleyWind2055RCP4.5 | Chesley | Wind | RCP4.5 | 2055 | 84.0979 | 90.7781 | 97.872 | 104.9038 | 111.9484
ChesleyWind2060RCP4.5 | Chesley | Wind | RCP4.5 | 2060 | 84.1112 | 90.7906 | 97.8816 | 104.912 | 111.9549
ChesleyWind2065RCP4.5 | Chesley | Wind | RCP4.5 | 2065 | 84.1245 | 90.8031 | 97.8912 | 104.9203 | 111.9615
ChesleyWind2070RCP4.5 | Chesley | Wind | RCP4.5 | 2070 | 84.1377 | 90.8156 | 97.9008 | 104.9285 | 111.9681
ChesleyWind2075RCP4.5 | Chesley | Wind | RCP4.5 | 2075 | 84.2192 | 90.9213 | 98.0368 | 105.0911 | 112.1559
ChesleyWind2080RCP4.5 | Chesley | Wind | RCP4.5 | 2080 | 84.3008 | 91.0269 | 98.1728 | 105.2538 | 112.3438
ChesleyWind2085RCP4.5 | Chesley | Wind | RCP4.5 | 2085 | 84.3823 | 91.1326 | 98.3088 | 105.4164 | 112.5317
ChesleyWind2090RCP4.5 | Chesley | Wind | RCP4.5 | 2090 | 84.4638 | 91.2382 | 98.4448 | 105.579 | 112.7196
ChesleyWind2095RCP4.5 | Chesley | Wind | RCP4.5 | 2095 | 84.5453 | 91.3439 | 98.5808 | 105.7417 | 112.9074
ChesleyWind2100RCP4.5 | Chesley | Wind | RCP4.5 | 2100 | 84.6268 | 91.4495 | 98.7168 | 105.9043 | 113.0953
ChesleyWind2023RCP6.0 | Chesley | Wind | RCP6.0 | 2023 | 83.5906 | 90.1639 | 97.1136 | 104.0245 | 110.9393
ChesleyWind2025RCP6.0 | Chesley | Wind | RCP6.0 | 2025 | 83.6708 | 90.2621 | 97.2368 | 104.1684 | 111.1053
ChesleyWind2030RCP6.0 | Chesley | Wind | RCP6.0 | 2030 | 83.7509 | 90.3603 | 97.36 | 104.3122 | 111.2713
ChesleyWind2035RCP6.0 | Chesley | Wind | RCP6.0 | 2035 | 83.831 | 90.4585 | 97.4832 | 104.456 | 111.4373
ChesleyWind2040RCP6.0 | Chesley | Wind | RCP6.0 | 2040 | 83.9111 | 90.5567 | 97.6064 | 104.5998 | 111.6033
ChesleyWind2045RCP6.0 | Chesley | Wind | RCP6.0 | 2045 | 83.9913 | 90.6549 | 97.7296 | 104.7436 | 111.7692
ChesleyWind2050RCP6.0 | Chesley | Wind | RCP6.0 | 2050 | 84.0847 | 90.7656 | 97.8624 | 104.8956 | 111.9418
ChesleyWind2055RCP6.0 | Chesley | Wind | RCP6.0 | 2055 | 84.0979 | 90.7781 | 97.872 | 104.9038 | 111.9484
ChesleyWind2060RCP6.0 | Chesley | Wind | RCP6.0 | 2060 | 84.1112 | 90.7906 | 97.8816 | 104.912 | 111.9549
ChesleyWind2065RCP6.0 | Chesley | Wind | RCP6.0 | 2065 | 84.1245 | 90.8031 | 97.8912 | 104.9203 | 111.9615
ChesleyWind2070RCP6.0 | Chesley | Wind | RCP6.0 | 2070 | 84.1377 | 90.8156 | 97.9008 | 104.9285 | 111.9681
ChesleyWind2075RCP6.0 | Chesley | Wind | RCP6.0 | 2075 | 84.26 | 90.9741 | 98.1048 | 105.1724 | 112.2499
ChesleyWind2080RCP6.0 | Chesley | Wind | RCP6.0 | 2080 | 84.3823 | 91.1326 | 98.3088 | 105.4164 | 112.5317
ChesleyWind2085RCP6.0 | Chesley | Wind | RCP6.0 | 2085 | 84.5045 | 91.291 | 98.5128 | 105.6604 | 112.8135
ChesleyWind2090RCP6.0 | Chesley | Wind | RCP6.0 | 2090 | 85.0302 | 91.9554 | 99.3472 | 106.6439 | 113.9489
ChesleyWind2095RCP6.0 | Chesley | Wind | RCP6.0 | 2095 | 85.4336 | 92.4613 | 99.9776 | 107.3835 | 114.8026
ChesleyWind2100RCP6.0 | Chesley | Wind | RCP6.0 | 2100 | 85.8371 | 92.9673 | 100.608 | 108.1231 | 115.6562
ChesleyWind2023RCP8.5 | Chesley | Wind | RCP8.5 | 2023 | 83.5906 | 90.1639 | 97.1136 | 104.0245 | 110.9393
ChesleyWind2025RCP8.5 | Chesley | Wind | RCP8.5 | 2025 | 83.7509 | 90.3603 | 97.36 | 104.3122 | 111.2713
ChesleyWind2030RCP8.5 | Chesley | Wind | RCP8.5 | 2030 | 83.9111 | 90.5567 | 97.6064 | 104.5998 | 111.6033
ChesleyWind2035RCP8.5 | Chesley | Wind | RCP8.5 | 2035 | 84.0714 | 90.7531 | 97.8528 | 104.8874 | 111.9352
ChesleyWind2040RCP8.5 | Chesley | Wind | RCP8.5 | 2040 | 84.0935 | 90.774 | 97.8688 | 104.9011 | 111.9462
ChesleyWind2045RCP8.5 | Chesley | Wind | RCP8.5 | 2045 | 84.1156 | 90.7948 | 97.8848 | 104.9148 | 111.9571
ChesleyWind2050RCP8.5 | Chesley | Wind | RCP8.5 | 2050 | 84.3008 | 91.0269 | 98.1728 | 105.2538 | 112.3438
ChesleyWind2055RCP8.5 | Chesley | Wind | RCP8.5 | 2055 | 84.4638 | 91.2382 | 98.4448 | 105.579 | 112.7196
ChesleyWind2060RCP8.5 | Chesley | Wind | RCP8.5 | 2060 | 85.0302 | 91.9554 | 99.3472 | 106.6439 | 113.9489
ChesleyWind2065RCP8.5 | Chesley | Wind | RCP8.5 | 2065 | 85.4336 | 92.4613 | 99.9776 | 107.3835 | 114.8026
ChesleyWind2070RCP8.5 | Chesley | Wind | RCP8.5 | 2070 | 86.0471 | 93.2232 | 100.9216 | 108.486 | 116.0684
ChesleyWind2075RCP8.5 | Chesley | Wind | RCP8.5 | 2075 | 86.2571 | 93.4791 | 101.2352 | 108.849 | 116.4806
ChesleyWind2080RCP8.5 | Chesley | Wind | RCP8.5 | 2080 | 86.4671 | 93.7351 | 101.5488 | 109.2119 | 116.8929
ChesleyWind2085RCP8.5 | Chesley | Wind | RCP8.5 | 2085 | 86.4878 | 93.744 | 101.5488 | 109.1965 | 116.871
ChesleyWind2090RCP8.5 | Chesley | Wind | RCP8.5 | 2090 | 86.5085 | 93.7529 | 101.5488 | 109.1811 | 116.8491
ChesleyWind2095RCP8.5 | Chesley | Wind | RCP8.5 | 2095 | 86.5085 | 93.7529 | 101.5488 | 109.1811 | 116.8491
ChesleyWind2100RCP8.5 | Chesley | Wind | RCP8.5 | 2100 | 86.5085 | 93.7529 | 101.5488 | 109.1811 | 116.8491
ClintonIce Accretion2023RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2023 | 14.5105 | 17.4126 | 21.084 | 23.8961 | 26.6981
ClintonIce Accretion2025RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2025 | 14.603 | 17.5346 | 21.2415 | 24.078 | 26.9054
ClintonIce Accretion2030RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2030 | 14.6956 | 17.6566 | 21.399 | 24.26 | 27.1127
ClintonIce Accretion2035RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2035 | 14.7881 | 17.7786 | 21.5565 | 24.4419 | 27.3199
ClintonIce Accretion2040RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2040 | 14.8807 | 17.9006 | 21.714 | 24.6238 | 27.5272
ClintonIce Accretion2045RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2045 | 14.9732 | 18.0226 | 21.8715 | 24.8058 | 27.7345
ClintonIce Accretion2050RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2050 | 15.0716 | 18.1725 | 22.0878 | 25.0684 | 28.0423
ClintonIce Accretion2055RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2055 | 15.0775 | 18.2004 | 22.1466 | 25.1491 | 28.1429
ClintonIce Accretion2060RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2060 | 15.0833 | 18.2283 | 22.2054 | 25.2297 | 28.2434
ClintonIce Accretion2065RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2065 | 15.0891 | 18.2562 | 22.2642 | 25.3104 | 28.344
ClintonIce Accretion2070RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2070 | 15.095 | 18.2841 | 22.323 | 25.3911 | 28.4445
ClintonIce Accretion2075RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2075 | 14.9927 | 18.1795 | 22.211 | 25.2764 | 28.3254
ClintonIce Accretion2080RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2080 | 14.8904 | 18.0749 | 22.099 | 25.1617 | 28.2064
ClintonIce Accretion2085RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2085 | 14.7881 | 17.9703 | 21.987 | 25.047 | 28.0873
ClintonIce Accretion2090RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2090 | 14.6858 | 17.8657 | 21.875 | 24.9323 | 27.9682
ClintonIce Accretion2095RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2095 | 14.5835 | 17.7612 | 21.763 | 24.8176 | 27.8492
ClintonIce Accretion2100RCP4.5 | Clinton | Ice Accretion | RCP4.5 | 2100 | 14.4813 | 17.6566 | 21.651 | 24.7029 | 27.7301
ClintonIce Accretion2023RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2023 | 14.5105 | 17.4126 | 21.084 | 23.8961 | 26.6981
ClintonIce Accretion2025RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2025 | 14.603 | 17.5346 | 21.2415 | 24.078 | 26.9054
ClintonIce Accretion2030RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2030 | 14.6956 | 17.6566 | 21.399 | 24.26 | 27.1127
ClintonIce Accretion2035RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2035 | 14.7881 | 17.7786 | 21.5565 | 24.4419 | 27.3199
ClintonIce Accretion2040RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2040 | 14.8807 | 17.9006 | 21.714 | 24.6238 | 27.5272
ClintonIce Accretion2045RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2045 | 14.9732 | 18.0226 | 21.8715 | 24.8058 | 27.7345
ClintonIce Accretion2050RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2050 | 15.0716 | 18.1725 | 22.0878 | 25.0684 | 28.0423
ClintonIce Accretion2055RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2055 | 15.0775 | 18.2004 | 22.1466 | 25.1491 | 28.1429
ClintonIce Accretion2060RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2060 | 15.0833 | 18.2283 | 22.2054 | 25.2297 | 28.2434
ClintonIce Accretion2065RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2065 | 15.0891 | 18.2562 | 22.2642 | 25.3104 | 28.344
ClintonIce Accretion2070RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2070 | 15.095 | 18.2841 | 22.323 | 25.3911 | 28.4445
ClintonIce Accretion2075RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2075 | 14.9416 | 18.1272 | 22.155 | 25.2191 | 28.2659
ClintonIce Accretion2080RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2080 | 14.7881 | 17.9703 | 21.987 | 25.047 | 28.0873
ClintonIce Accretion2085RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2085 | 14.6347 | 17.8135 | 21.819 | 24.875 | 27.9087
ClintonIce Accretion2090RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2090 | 14.1452 | 17.2847 | 21.231 | 24.2441 | 27.2273
ClintonIce Accretion2095RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2095 | 13.8091 | 16.9129 | 20.811 | 23.7854 | 26.7246
ClintonIce Accretion2100RCP6.0 | Clinton | Ice Accretion | RCP6.0 | 2100 | 13.473 | 16.5411 | 20.391 | 23.3266 | 26.2219
ClintonIce Accretion2023RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2023 | 14.5105 | 17.4126 | 21.084 | 23.8961 | 26.6981
ClintonIce Accretion2025RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2025 | 14.6956 | 17.6566 | 21.399 | 24.26 | 27.1127
ClintonIce Accretion2030RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2030 | 14.8807 | 17.9006 | 21.714 | 24.6238 | 27.5272
ClintonIce Accretion2035RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2035 | 15.0658 | 18.1446 | 22.029 | 24.9877 | 27.9418
ClintonIce Accretion2040RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2040 | 15.0755 | 18.1911 | 22.127 | 25.1222 | 28.1093
ClintonIce Accretion2045RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2045 | 15.0852 | 18.2376 | 22.225 | 25.2566 | 28.2769
ClintonIce Accretion2050RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2050 | 14.8904 | 18.0749 | 22.099 | 25.1617 | 28.2064
ClintonIce Accretion2055RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2055 | 14.6858 | 17.8657 | 21.875 | 24.9323 | 27.9682
ClintonIce Accretion2060RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2060 | 14.1452 | 17.2847 | 21.231 | 24.2441 | 27.2273
ClintonIce Accretion2065RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2065 | 13.8091 | 16.9129 | 20.811 | 23.7854 | 26.7246
ClintonIce Accretion2070RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2070 | 13.02 | 16.0298 | 19.81 | 22.678 | 25.5251
ClintonIce Accretion2075RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2075 | 12.567 | 15.5185 | 19.229 | 22.0293 | 24.8283
ClintonIce Accretion2080RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2080 | 12.114 | 15.0072 | 18.648 | 21.3807 | 24.1315
ClintonIce Accretion2085RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2085 | 11.5149 | 14.31 | 17.8185 | 20.4671 | 23.1128
ClintonIce Accretion2090RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2090 | 10.9157 | 13.6128 | 16.989 | 19.5535 | 22.0941
ClintonIce Accretion2095RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2095 | 10.9157 | 13.6128 | 16.989 | 19.5535 | 22.0941
ClintonIce Accretion2100RCP8.5 | Clinton | Ice Accretion | RCP8.5 | 2100 | 10.9157 | 13.6128 | 16.989 | 19.5535 | 22.0941
ClintonWind2023RCP4.5 | Clinton | Wind | RCP4.5 | 2023 | 86.1344 | 92.8894 | 100.0296 | 107.1482 | 114.2595
ClintonWind2025RCP4.5 | Clinton | Wind | RCP4.5 | 2025 | 86.2014 | 92.9754 | 100.1402 | 107.2788 | 114.4137
ClintonWind2030RCP4.5 | Clinton | Wind | RCP4.5 | 2030 | 86.2684 | 93.0613 | 100.2507 | 107.4095 | 114.5679
ClintonWind2035RCP4.5 | Clinton | Wind | RCP4.5 | 2035 | 86.3353 | 93.1472 | 100.3612 | 107.5401 | 114.7222
ClintonWind2040RCP4.5 | Clinton | Wind | RCP4.5 | 2040 | 86.4023 | 93.2332 | 100.4718 | 107.6708 | 114.8764
ClintonWind2045RCP4.5 | Clinton | Wind | RCP4.5 | 2045 | 86.4693 | 93.3191 | 100.5823 | 107.8014 | 115.0307
ClintonWind2050RCP4.5 | Clinton | Wind | RCP4.5 | 2050 | 86.5567 | 93.4271 | 100.7167 | 107.9575 | 115.212
ClintonWind2055RCP4.5 | Clinton | Wind | RCP4.5 | 2055 | 86.5773 | 93.4492 | 100.7404 | 107.9829 | 115.2391
ClintonWind2060RCP4.5 | Clinton | Wind | RCP4.5 | 2060 | 86.5978 | 93.4713 | 100.7642 | 108.0083 | 115.2662
ClintonWind2065RCP4.5 | Clinton | Wind | RCP4.5 | 2065 | 86.6183 | 93.4934 | 100.7879 | 108.0338 | 115.2933
ClintonWind2070RCP4.5 | Clinton | Wind | RCP4.5 | 2070 | 86.6388 | 93.5155 | 100.8117 | 108.0592 | 115.3203
ClintonWind2075RCP4.5 | Clinton | Wind | RCP4.5 | 2075 | 86.7542 | 93.6674 | 101.0097 | 108.2958 | 115.5969
ClintonWind2080RCP4.5 | Clinton | Wind | RCP4.5 | 2080 | 86.8696 | 93.8193 | 101.2077 | 108.5323 | 115.8734
ClintonWind2085RCP4.5 | Clinton | Wind | RCP4.5 | 2085 | 86.985 | 93.9712 | 101.4057 | 108.7689 | 116.1499
ClintonWind2090RCP4.5 | Clinton | Wind | RCP4.5 | 2090 | 87.1004 | 94.1232 | 101.6037 | 109.0055 | 116.4264
ClintonWind2095RCP4.5 | Clinton | Wind | RCP4.5 | 2095 | 87.2158 | 94.2751 | 101.8017 | 109.2421 | 116.7029
ClintonWind2100RCP4.5 | Clinton | Wind | RCP4.5 | 2100 | 87.3312 | 94.427 | 101.9997 | 109.4787 | 116.9794
ClintonWind2023RCP6.0 | Clinton | Wind | RCP6.0 | 2023 | 86.1344 | 92.8894 | 100.0296 | 107.1482 | 114.2595
ClintonWind2025RCP6.0 | Clinton | Wind | RCP6.0 | 2025 | 86.2014 | 92.9754 | 100.1402 | 107.2788 | 114.4137
ClintonWind2030RCP6.0 | Clinton | Wind | RCP6.0 | 2030 | 86.2684 | 93.0613 | 100.2507 | 107.4095 | 114.5679
ClintonWind2035RCP6.0 | Clinton | Wind | RCP6.0 | 2035 | 86.3353 | 93.1472 | 100.3612 | 107.5401 | 114.7222
ClintonWind2040RCP6.0 | Clinton | Wind | RCP6.0 | 2040 | 86.4023 | 93.2332 | 100.4718 | 107.6708 | 114.8764
ClintonWind2045RCP6.0 | Clinton | Wind | RCP6.0 | 2045 | 86.4693 | 93.3191 | 100.5823 | 107.8014 | 115.0307
ClintonWind2050RCP6.0 | Clinton | Wind | RCP6.0 | 2050 | 86.5567 | 93.4271 | 100.7167 | 107.9575 | 115.212
ClintonWind2055RCP6.0 | Clinton | Wind | RCP6.0 | 2055 | 86.5773 | 93.4492 | 100.7404 | 107.9829 | 115.2391
ClintonWind2060RCP6.0 | Clinton | Wind | RCP6.0 | 2060 | 86.5978 | 93.4713 | 100.7642 | 108.0083 | 115.2662
ClintonWind2065RCP6.0 | Clinton | Wind | RCP6.0 | 2065 | 86.6183 | 93.4934 | 100.7879 | 108.0338 | 115.2933
ClintonWind2070RCP6.0 | Clinton | Wind | RCP6.0 | 2070 | 86.6388 | 93.5155 | 100.8117 | 108.0592 | 115.3203
ClintonWind2075RCP6.0 | Clinton | Wind | RCP6.0 | 2075 | 86.8119 | 93.7434 | 101.1087 | 108.4141 | 115.7351
ClintonWind2080RCP6.0 | Clinton | Wind | RCP6.0 | 2080 | 86.985 | 93.9712 | 101.4057 | 108.7689 | 116.1499
ClintonWind2085RCP6.0 | Clinton | Wind | RCP6.0 | 2085 | 87.1581 | 94.1991 | 101.7027 | 109.1238 | 116.5646
ClintonWind2090RCP6.0 | Clinton | Wind | RCP6.0 | 2090 | 87.7729 | 94.9794 | 102.6861 | 110.2837 | 117.9011
ClintonWind2095RCP6.0 | Clinton | Wind | RCP6.0 | 2095 | 88.2146 | 95.5318 | 103.3725 | 111.0888 | 118.8228
ClintonWind2100RCP6.0 | Clinton | Wind | RCP6.0 | 2100 | 88.6562 | 96.0843 | 104.0589 | 111.8939 | 119.7445
ClintonWind2023RCP8.5 | Clinton | Wind | RCP8.5 | 2023 | 86.1344 | 92.8894 | 100.0296 | 107.1482 | 114.2595
ClintonWind2025RCP8.5 | Clinton | Wind | RCP8.5 | 2025 | 86.2684 | 93.0613 | 100.2507 | 107.4095 | 114.5679
ClintonWind2030RCP8.5 | Clinton | Wind | RCP8.5 | 2030 | 86.4023 | 93.2332 | 100.4718 | 107.6708 | 114.8764
ClintonWind2035RCP8.5 | Clinton | Wind | RCP8.5 | 2035 | 86.5362 | 93.405 | 100.6929 | 107.9321 | 115.1849
ClintonWind2040RCP8.5 | Clinton | Wind | RCP8.5 | 2040 | 86.5704 | 93.4418 | 100.7325 | 107.9744 | 115.2301
ClintonWind2045RCP8.5 | Clinton | Wind | RCP8.5 | 2045 | 86.6046 | 93.4787 | 100.7721 | 108.0168 | 115.2752
ClintonWind2050RCP8.5 | Clinton | Wind | RCP8.5 | 2050 | 86.8696 | 93.8193 | 101.2077 | 108.5323 | 115.8734
ClintonWind2055RCP8.5 | Clinton | Wind | RCP8.5 | 2055 | 87.1004 | 94.1232 | 101.6037 | 109.0055 | 116.4264
ClintonWind2060RCP8.5 | Clinton | Wind | RCP8.5 | 2060 | 87.7729 | 94.9794 | 102.6861 | 110.2837 | 117.9011
ClintonWind2065RCP8.5 | Clinton | Wind | RCP8.5 | 2065 | 88.2146 | 95.5318 | 103.3725 | 111.0888 | 118.8228
ClintonWind2070RCP8.5 | Clinton | Wind | RCP8.5 | 2070 | 88.8643 | 96.339 | 104.3757 | 112.2576 | 120.162
ClintonWind2075RCP8.5 | Clinton | Wind | RCP8.5 | 2075 | 89.0723 | 96.5937 | 104.6925 | 112.6212 | 120.5796
ClintonWind2080RCP8.5 | Clinton | Wind | RCP8.5 | 2080 | 89.2803 | 96.8484 | 105.0093 | 112.9849 | 120.9972
ClintonWind2085RCP8.5 | Clinton | Wind | RCP8.5 | 2085 | 89.4171 | 97.0003 | 105.1776 | 113.1703 | 121.2004
ClintonWind2090RCP8.5 | Clinton | Wind | RCP8.5 | 2090 | 89.5538 | 97.1523 | 105.3459 | 113.3557 | 121.4035
ClintonWind2095RCP8.5 | Clinton | Wind | RCP8.5 | 2095 | 89.5538 | 97.1523 | 105.3459 | 113.3557 | 121.4035
ClintonWind2100RCP8.5 | Clinton | Wind | RCP8.5 | 2100 | 89.5538 | 97.1523 | 105.3459 | 113.3557 | 121.4035
CoboconkIce Accretion2023RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2023 | 17.2396 | 20.584 | 24.825 | 28.0522 | 31.311
CoboconkIce Accretion2025RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2025 | 17.2251 | 20.5771 | 24.825 | 28.057 | 31.3215
CoboconkIce Accretion2030RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2030 | 17.2106 | 20.5702 | 24.825 | 28.0617 | 31.332
CoboconkIce Accretion2035RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2035 | 17.1961 | 20.5633 | 24.825 | 28.0664 | 31.3425
CoboconkIce Accretion2040RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2040 | 17.1816 | 20.5563 | 24.825 | 28.0711 | 31.353
CoboconkIce Accretion2045RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2045 | 17.1671 | 20.5494 | 24.825 | 28.0758 | 31.3635
CoboconkIce Accretion2050RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2050 | 17.1109 | 20.5134 | 24.81 | 28.0748 | 31.374
CoboconkIce Accretion2055RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2055 | 17.0691 | 20.4844 | 24.795 | 28.0692 | 31.374
CoboconkIce Accretion2060RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2060 | 17.0274 | 20.4553 | 24.78 | 28.0635 | 31.374
CoboconkIce Accretion2065RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2065 | 16.9856 | 20.4263 | 24.765 | 28.0579 | 31.374
CoboconkIce Accretion2070RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2070 | 16.9439 | 20.3972 | 24.75 | 28.0522 | 31.374
CoboconkIce Accretion2075RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2075 | 17.0134 | 20.4975 | 24.8875 | 28.2217 | 31.5735
CoboconkIce Accretion2080RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2080 | 17.083 | 20.5978 | 25.025 | 28.3912 | 31.773
CoboconkIce Accretion2085RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2085 | 17.1526 | 20.6981 | 25.1625 | 28.5607 | 31.9725
CoboconkIce Accretion2090RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2090 | 17.2222 | 20.7984 | 25.3 | 28.7302 | 32.172
CoboconkIce Accretion2095RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2095 | 17.2918 | 20.8987 | 25.4375 | 28.8997 | 32.3715
CoboconkIce Accretion2100RCP4.5 | Coboconk | Ice Accretion | RCP4.5 | 2100 | 17.3614 | 20.999 | 25.575 | 29.0692 | 32.571
CoboconkIce Accretion2023RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2023 | 17.2396 | 20.584 | 24.825 | 28.0522 | 31.311
CoboconkIce Accretion2025RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2025 | 17.2251 | 20.5771 | 24.825 | 28.057 | 31.3215
CoboconkIce Accretion2030RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2030 | 17.2106 | 20.5702 | 24.825 | 28.0617 | 31.332
CoboconkIce Accretion2035RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2035 | 17.1961 | 20.5633 | 24.825 | 28.0664 | 31.3425
CoboconkIce Accretion2040RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2040 | 17.1816 | 20.5563 | 24.825 | 28.0711 | 31.353
CoboconkIce Accretion2045RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2045 | 17.1671 | 20.5494 | 24.825 | 28.0758 | 31.3635
CoboconkIce Accretion2050RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2050 | 17.1109 | 20.5134 | 24.81 | 28.0748 | 31.374
CoboconkIce Accretion2055RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2055 | 17.0691 | 20.4844 | 24.795 | 28.0692 | 31.374
CoboconkIce Accretion2060RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2060 | 17.0274 | 20.4553 | 24.78 | 28.0635 | 31.374
CoboconkIce Accretion2065RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2065 | 16.9856 | 20.4263 | 24.765 | 28.0579 | 31.374
CoboconkIce Accretion2070RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2070 | 16.9439 | 20.3972 | 24.75 | 28.0522 | 31.374
CoboconkIce Accretion2075RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2075 | 17.0482 | 20.5477 | 24.9563 | 28.3065 | 31.6732
CoboconkIce Accretion2080RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2080 | 17.1526 | 20.6981 | 25.1625 | 28.5607 | 31.9725
CoboconkIce Accretion2085RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2085 | 17.257 | 20.8486 | 25.3687 | 28.815 | 32.2717
CoboconkIce Accretion2090RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2090 | 17.2512 | 20.916 | 25.5333 | 29.0504 | 32.5815
CoboconkIce Accretion2095RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2095 | 17.141 | 20.833 | 25.4917 | 29.0316 | 32.592
CoboconkIce Accretion2100RCP6.0 | Coboconk | Ice Accretion | RCP6.0 | 2100 | 17.0308 | 20.75 | 25.45 | 29.0127 | 32.6025
CoboconkIce Accretion2023RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2023 | 17.2396 | 20.584 | 24.825 | 28.0522 | 31.311
CoboconkIce Accretion2025RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2025 | 17.2106 | 20.5702 | 24.825 | 28.0617 | 31.332
CoboconkIce Accretion2030RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2030 | 17.1816 | 20.5563 | 24.825 | 28.0711 | 31.353
CoboconkIce Accretion2035RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2035 | 17.1526 | 20.5425 | 24.825 | 28.0805 | 31.374
CoboconkIce Accretion2040RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2040 | 17.083 | 20.4941 | 24.8 | 28.0711 | 31.374
CoboconkIce Accretion2045RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2045 | 17.0134 | 20.4457 | 24.775 | 28.0617 | 31.374
CoboconkIce Accretion2050RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2050 | 17.083 | 20.5978 | 25.025 | 28.3912 | 31.773
CoboconkIce Accretion2055RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2055 | 17.2222 | 20.7984 | 25.3 | 28.7302 | 32.172
CoboconkIce Accretion2060RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2060 | 17.2512 | 20.916 | 25.5333 | 29.0504 | 32.5815
CoboconkIce Accretion2065RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2065 | 17.141 | 20.833 | 25.4917 | 29.0316 | 32.592
CoboconkIce Accretion2070RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2070 | 16.8105 | 20.5218 | 25.2167 | 28.7773 | 32.3505
CoboconkIce Accretion2075RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2075 | 16.5901 | 20.2935 | 24.9833 | 28.5419 | 32.0985
CoboconkIce Accretion2080RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2080 | 16.3698 | 20.0652 | 24.75 | 28.3065 | 31.8465
CoboconkIce Accretion2085RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2085 | 15.6826 | 19.2871 | 23.85 | 27.3177 | 30.7597
CoboconkIce Accretion2090RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2090 | 14.9955 | 18.509 | 22.95 | 26.329 | 29.673
CoboconkIce Accretion2095RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2095 | 14.9955 | 18.509 | 22.95 | 26.329 | 29.673
CoboconkIce Accretion2100RCP8.5 | Coboconk | Ice Accretion | RCP8.5 | 2100 | 14.9955 | 18.509 | 22.95 | 26.329 | 29.673
CoboconkWind2023RCP4.5 | Coboconk | Wind | RCP4.5 | 2023 | 71.0605 | 76.504 | 82.2296 | 87.9594 | 93.6857
CoboconkWind2025RCP4.5 | Coboconk | Wind | RCP4.5 | 2025 | 71.1147 | 76.5676 | 82.3048 | 88.0442 | 93.7807
CoboconkWind2030RCP4.5 | Coboconk | Wind | RCP4.5 | 2030 | 71.169 | 76.6311 | 82.3799 | 88.129 | 93.8757
CoboconkWind2035RCP4.5 | Coboconk | Wind | RCP4.5 | 2035 | 71.2233 | 76.6947 | 82.4551 | 88.2138 | 93.9708
CoboconkWind2040RCP4.5 | Coboconk | Wind | RCP4.5 | 2040 | 71.2776 | 76.7582 | 82.5303 | 88.2986 | 94.0658
CoboconkWind2045RCP4.5 | Coboconk | Wind | RCP4.5 | 2045 | 71.3319 | 76.8218 | 82.6054 | 88.3834 | 94.1608
CoboconkWind2050RCP4.5 | Coboconk | Wind | RCP4.5 | 2050 | 71.4584 | 76.9662 | 82.7692 | 88.5648 | 94.3606
CoboconkWind2055RCP4.5 | Coboconk | Wind | RCP4.5 | 2055 | 71.5306 | 77.047 | 82.8577 | 88.6613 | 94.4653
CoboconkWind2060RCP4.5 | Coboconk | Wind | RCP4.5 | 2060 | 71.6028 | 77.1278 | 82.9463 | 88.7578 | 94.57
CoboconkWind2065RCP4.5 | Coboconk | Wind | RCP4.5 | 2065 | 71.6751 | 77.2087 | 83.0348 | 88.8543 | 94.6747
CoboconkWind2070RCP4.5 | Coboconk | Wind | RCP4.5 | 2070 | 71.7473 | 77.2895 | 83.1234 | 88.9508 | 94.7794
CoboconkWind2075RCP4.5 | Coboconk | Wind | RCP4.5 | 2075 | 71.7249 | 77.2666 | 83.0988 | 88.926 | 94.7544
CoboconkWind2080RCP4.5 | Coboconk | Wind | RCP4.5 | 2080 | 71.7024 | 77.2438 | 83.0742 | 88.9011 | 94.7295
CoboconkWind2085RCP4.5 | Coboconk | Wind | RCP4.5 | 2085 | 71.68 | 77.2209 | 83.0496 | 88.8762 | 94.7046
CoboconkWind2090RCP4.5 | Coboconk | Wind | RCP4.5 | 2090 | 71.6576 | 77.198 | 83.025 | 88.8514 | 94.6797
CoboconkWind2095RCP4.5 | Coboconk | Wind | RCP4.5 | 2095 | 71.6352 | 77.1751 | 83.0004 | 88.8265 | 94.6547
CoboconkWind2100RCP4.5 | Coboconk | Wind | RCP4.5 | 2100 | 71.6127 | 77.1522 | 82.9758 | 88.8017 | 94.6298
CoboconkWind2023RCP6.0 | Coboconk | Wind | RCP6.0 | 2023 | 71.0605 | 76.504 | 82.2296 | 87.9594 | 93.6857
CoboconkWind2025RCP6.0 | Coboconk | Wind | RCP6.0 | 2025 | 71.1147 | 76.5676 | 82.3048 | 88.0442 | 93.7807
CoboconkWind2030RCP6.0 | Coboconk | Wind | RCP6.0 | 2030 | 71.169 | 76.6311 | 82.3799 | 88.129 | 93.8757
CoboconkWind2035RCP6.0 | Coboconk | Wind | RCP6.0 | 2035 | 71.2233 | 76.6947 | 82.4551 | 88.2138 | 93.9708
CoboconkWind2040RCP6.0 | Coboconk | Wind | RCP6.0 | 2040 | 71.2776 | 76.7582 | 82.5303 | 88.2986 | 94.0658
CoboconkWind2045RCP6.0 | Coboconk | Wind | RCP6.0 | 2045 | 71.3319 | 76.8218 | 82.6054 | 88.3834 | 94.1608
CoboconkWind2050RCP6.0 | Coboconk | Wind | RCP6.0 | 2050 | 71.4584 | 76.9662 | 82.7692 | 88.5648 | 94.3606
CoboconkWind2055RCP6.0 | Coboconk | Wind | RCP6.0 | 2055 | 71.5306 | 77.047 | 82.8577 | 88.6613 | 94.4653
CoboconkWind2060RCP6.0 | Coboconk | Wind | RCP6.0 | 2060 | 71.6028 | 77.1278 | 82.9463 | 88.7578 | 94.57
CoboconkWind2065RCP6.0 | Coboconk | Wind | RCP6.0 | 2065 | 71.6751 | 77.2087 | 83.0348 | 88.8543 | 94.6747
CoboconkWind2070RCP6.0 | Coboconk | Wind | RCP6.0 | 2070 | 71.7473 | 77.2895 | 83.1234 | 88.9508 | 94.7794
CoboconkWind2075RCP6.0 | Coboconk | Wind | RCP6.0 | 2075 | 71.7136 | 77.2552 | 83.0865 | 88.9135 | 94.742
CoboconkWind2080RCP6.0 | Coboconk | Wind | RCP6.0 | 2080 | 71.68 | 77.2209 | 83.0496 | 88.8762 | 94.7046
CoboconkWind2085RCP6.0 | Coboconk | Wind | RCP6.0 | 2085 | 71.6464 | 77.1866 | 83.0127 | 88.8389 | 94.6672
CoboconkWind2090RCP6.0 | Coboconk | Wind | RCP6.0 | 2090 | 71.6647 | 77.2107 | 83.0441 | 88.8777 | 94.7139
CoboconkWind2095RCP6.0 | Coboconk | Wind | RCP6.0 | 2095 | 71.7166 | 77.2692 | 83.1125 | 88.9537 | 94.7981
CoboconkWind2100RCP6.0 | Coboconk | Wind | RCP6.0 | 2100 | 71.7685 | 77.3276 | 83.1808 | 89.0298 | 94.8822
CoboconkWind2023RCP8.5 | Coboconk | Wind | RCP8.5 | 2023 | 71.0605 | 76.504 | 82.2296 | 87.9594 | 93.6857
CoboconkWind2025RCP8.5 | Coboconk | Wind | RCP8.5 | 2025 | 71.169 | 76.6311 | 82.3799 | 88.129 | 93.8757
CoboconkWind2030RCP8.5 | Coboconk | Wind | RCP8.5 | 2030 | 71.2776 | 76.7582 | 82.5303 | 88.2986 | 94.0658
CoboconkWind2035RCP8.5 | Coboconk | Wind | RCP8.5 | 2035 | 71.3862 | 76.8853 | 82.6806 | 88.4682 | 94.2559
CoboconkWind2040RCP8.5 | Coboconk | Wind | RCP8.5 | 2040 | 71.5065 | 77.0201 | 82.8282 | 88.6291 | 94.4304
CoboconkWind2045RCP8.5 | Coboconk | Wind | RCP8.5 | 2045 | 71.6269 | 77.1548 | 82.9758 | 88.79 | 94.6049
CoboconkWind2050RCP8.5 | Coboconk | Wind | RCP8.5 | 2050 | 71.7024 | 77.2438 | 83.0742 | 88.9011 | 94.7295
CoboconkWind2055RCP8.5 | Coboconk | Wind | RCP8.5 | 2055 | 71.6576 | 77.198 | 83.025 | 88.8514 | 94.6797
CoboconkWind2060RCP8.5 | Coboconk | Wind | RCP8.5 | 2060 | 71.6647 | 77.2107 | 83.0441 | 88.8777 | 94.7139
CoboconkWind2065RCP8.5 | Coboconk | Wind | RCP8.5 | 2065 | 71.7166 | 77.2692 | 83.1125 | 88.9537 | 94.7981
CoboconkWind2070RCP8.5 | Coboconk | Wind | RCP8.5 | 2070 | 71.785 | 77.3404 | 83.1917 | 89.0386 | 94.8884
CoboconkWind2075RCP8.5 | Coboconk | Wind | RCP8.5 | 2075 | 71.8016 | 77.3531 | 83.2027 | 89.0473 | 94.8947
CoboconkWind2080RCP8.5 | Coboconk | Wind | RCP8.5 | 2080 | 71.8181 | 77.3658 | 83.2136 | 89.0561 | 94.9009
CoboconkWind2085RCP8.5 | Coboconk | Wind | RCP8.5 | 2085 | 71.9207 | 77.4802 | 83.3366 | 89.1877 | 95.0411
CoboconkWind2090RCP8.5 | Coboconk | Wind | RCP8.5 | 2090 | 72.0234 | 77.5946 | 83.4596 | 89.3193 | 95.1813
CoboconkWind2095RCP8.5 | Coboconk | Wind | RCP8.5 | 2095 | 72.0234 | 77.5946 | 83.4596 | 89.3193 | 95.1813
CoboconkWind2100RCP8.5 | Coboconk | Wind | RCP8.5 | 2100 | 72.0234 | 77.5946 | 83.4596 | 89.3193 | 95.1813
CobourgIce Accretion2023RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
CobourgIce Accretion2025RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
CobourgIce Accretion2030RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
CobourgIce Accretion2035RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
CobourgIce Accretion2040RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
CobourgIce Accretion2045RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
CobourgIce Accretion2050RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
CobourgIce Accretion2055RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
CobourgIce Accretion2060RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
CobourgIce Accretion2065RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
CobourgIce Accretion2070RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
CobourgIce Accretion2075RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2075 | 16.8859 | 20.3972 | 24.8292 | 28.2123 | 31.5682
CobourgIce Accretion2080RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2080 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
CobourgIce Accretion2085RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2085 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
CobourgIce Accretion2090RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2090 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
CobourgIce Accretion2095RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2095 | 16.7235 | 20.3142 | 24.8458 | 28.2877 | 31.7152
CobourgIce Accretion2100RCP4.5 | Cobourg | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.2935 | 24.85 | 28.3065 | 31.752
CobourgIce Accretion2023RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
CobourgIce Accretion2025RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
CobourgIce Accretion2030RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
CobourgIce Accretion2035RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
CobourgIce Accretion2040RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
CobourgIce Accretion2045RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
CobourgIce Accretion2050RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
CobourgIce Accretion2055RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
CobourgIce Accretion2060RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
CobourgIce Accretion2065RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
CobourgIce Accretion2070RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
CobourgIce Accretion2075RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2075 | 16.8656 | 20.3869 | 24.8313 | 28.2217 | 31.5866
CobourgIce Accretion2080RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2080 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
CobourgIce Accretion2085RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2085 | 16.7438 | 20.3246 | 24.8438 | 28.2782 | 31.6969
CobourgIce Accretion2090RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2090 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
CobourgIce Accretion2095RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2095 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
CobourgIce Accretion2100RCP6.0 | Cobourg | Ice Accretion | RCP6.0 | 2100 | 15.6565 | 19.173 | 23.6 | 26.9505 | 30.2715
CobourgIce Accretion2023RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
CobourgIce Accretion2025RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2025 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
CobourgIce Accretion2030RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2030 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
CobourgIce Accretion2035RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2035 | 17.6745 | 21.2272 | 25.725 | 29.154 | 32.571
CobourgIce Accretion2040RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2040 | 17.4251 | 20.9575 | 25.425 | 28.8338 | 32.2245
CobourgIce Accretion2045RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2045 | 17.1758 | 20.6877 | 25.125 | 28.5137 | 31.878
CobourgIce Accretion2050RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2050 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
CobourgIce Accretion2055RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2055 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
CobourgIce Accretion2060RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2060 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
CobourgIce Accretion2065RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2065 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
CobourgIce Accretion2070RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2070 | 15.2216 | 18.6888 | 23.05 | 26.3478 | 29.631
CobourgIce Accretion2075RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2075 | 14.7867 | 18.2047 | 22.5 | 25.7452 | 28.9905
CobourgIce Accretion2080RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2080 | 14.3518 | 17.7205 | 21.95 | 25.1425 | 28.35
CobourgIce Accretion2085RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2085 | 13.6908 | 16.9424 | 21.025 | 24.0972 | 27.1845
CobourgIce Accretion2090RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2090 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
CobourgIce Accretion2095RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2095 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
CobourgIce Accretion2100RCP8.5 | Cobourg | Ice Accretion | RCP8.5 | 2100 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
CobourgWind2023RCP4.5 | Cobourg | Wind | RCP4.5 | 2023 | 86.8663 | 93.5766 | 100.63 | 107.6848 | 114.741
CobourgWind2025RCP4.5 | Cobourg | Wind | RCP4.5 | 2025 | 86.8332 | 93.5409 | 100.595 | 107.6473 | 114.703
CobourgWind2030RCP4.5 | Cobourg | Wind | RCP4.5 | 2030 | 86.8001 | 93.5053 | 100.56 | 107.6099 | 114.665
CobourgWind2035RCP4.5 | Cobourg | Wind | RCP4.5 | 2035 | 86.767 | 93.4697 | 100.525 | 107.5725 | 114.627
CobourgWind2040RCP4.5 | Cobourg | Wind | RCP4.5 | 2040 | 86.7339 | 93.434 | 100.49 | 107.535 | 114.589
CobourgWind2045RCP4.5 | Cobourg | Wind | RCP4.5 | 2045 | 86.7008 | 93.3984 | 100.455 | 107.4975 | 114.551
CobourgWind2050RCP4.5 | Cobourg | Wind | RCP4.5 | 2050 | 86.7903 | 93.5264 | 100.634 | 107.7169 | 114.814
CobourgWind2055RCP4.5 | Cobourg | Wind | RCP4.5 | 2055 | 86.913 | 93.6901 | 100.848 | 107.9737 | 115.1149
CobourgWind2060RCP4.5 | Cobourg | Wind | RCP4.5 | 2060 | 87.0356 | 93.8537 | 101.062 | 108.2305 | 115.4159
CobourgWind2065RCP4.5 | Cobourg | Wind | RCP4.5 | 2065 | 87.1582 | 94.0174 | 101.276 | 108.4873 | 115.7168
CobourgWind2070RCP4.5 | Cobourg | Wind | RCP4.5 | 2070 | 87.2808 | 94.1811 | 101.49 | 108.7441 | 116.0178
CobourgWind2075RCP4.5 | Cobourg | Wind | RCP4.5 | 2075 | 87.3427 | 94.2664 | 101.6033 | 108.8814 | 116.1793
CobourgWind2080RCP4.5 | Cobourg | Wind | RCP4.5 | 2080 | 87.4046 | 94.3516 | 101.7167 | 109.0187 | 116.3408
CobourgWind2085RCP4.5 | Cobourg | Wind | RCP4.5 | 2085 | 87.4665 | 94.4368 | 101.83 | 109.156 | 116.5023
CobourgWind2090RCP4.5 | Cobourg | Wind | RCP4.5 | 2090 | 87.5283 | 94.5221 | 101.9433 | 109.2934 | 116.6638
CobourgWind2095RCP4.5 | Cobourg | Wind | RCP4.5 | 2095 | 87.5902 | 94.6073 | 102.0567 | 109.4307 | 116.8253
CobourgWind2100RCP4.5 | Cobourg | Wind | RCP4.5 | 2100 | 87.6521 | 94.6926 | 102.17 | 109.568 | 116.9868
CobourgWind2023RCP6.0 | Cobourg | Wind | RCP6.0 | 2023 | 86.8663 | 93.5766 | 100.63 | 107.6848 | 114.741
CobourgWind2025RCP6.0 | Cobourg | Wind | RCP6.0 | 2025 | 86.8332 | 93.5409 | 100.595 | 107.6473 | 114.703
CobourgWind2030RCP6.0 | Cobourg | Wind | RCP6.0 | 2030 | 86.8001 | 93.5053 | 100.56 | 107.6099 | 114.665
CobourgWind2035RCP6.0 | Cobourg | Wind | RCP6.0 | 2035 | 86.767 | 93.4697 | 100.525 | 107.5725 | 114.627
CobourgWind2040RCP6.0 | Cobourg | Wind | RCP6.0 | 2040 | 86.7339 | 93.434 | 100.49 | 107.535 | 114.589
CobourgWind2045RCP6.0 | Cobourg | Wind | RCP6.0 | 2045 | 86.7008 | 93.3984 | 100.455 | 107.4975 | 114.551
CobourgWind2050RCP6.0 | Cobourg | Wind | RCP6.0 | 2050 | 86.7903 | 93.5264 | 100.634 | 107.7169 | 114.814
CobourgWind2055RCP6.0 | Cobourg | Wind | RCP6.0 | 2055 | 86.913 | 93.6901 | 100.848 | 107.9737 | 115.1149
CobourgWind2060RCP6.0 | Cobourg | Wind | RCP6.0 | 2060 | 87.0356 | 93.8537 | 101.062 | 108.2305 | 115.4159
CobourgWind2065RCP6.0 | Cobourg | Wind | RCP6.0 | 2065 | 87.1582 | 94.0174 | 101.276 | 108.4873 | 115.7168
CobourgWind2070RCP6.0 | Cobourg | Wind | RCP6.0 | 2070 | 87.2808 | 94.1811 | 101.49 | 108.7441 | 116.0178
CobourgWind2075RCP6.0 | Cobourg | Wind | RCP6.0 | 2075 | 87.3736 | 94.309 | 101.66 | 108.9501 | 116.26
CobourgWind2080RCP6.0 | Cobourg | Wind | RCP6.0 | 2080 | 87.4665 | 94.4368 | 101.83 | 109.156 | 116.5023
CobourgWind2085RCP6.0 | Cobourg | Wind | RCP6.0 | 2085 | 87.5593 | 94.5647 | 102 | 109.362 | 116.7445
CobourgWind2090RCP6.0 | Cobourg | Wind | RCP6.0 | 2090 | 87.9486 | 95.0522 | 102.61 | 110.0816 | 117.5682
CobourgWind2095RCP6.0 | Cobourg | Wind | RCP6.0 | 2095 | 88.245 | 95.4118 | 103.05 | 110.5952 | 118.1496
CobourgWind2100RCP6.0 | Cobourg | Wind | RCP6.0 | 2100 | 88.5415 | 95.7714 | 103.49 | 111.1088 | 118.731
CobourgWind2023RCP8.5 | Cobourg | Wind | RCP8.5 | 2023 | 86.8663 | 93.5766 | 100.63 | 107.6848 | 114.741
CobourgWind2025RCP8.5 | Cobourg | Wind | RCP8.5 | 2025 | 86.8001 | 93.5053 | 100.56 | 107.6099 | 114.665
CobourgWind2030RCP8.5 | Cobourg | Wind | RCP8.5 | 2030 | 86.7339 | 93.434 | 100.49 | 107.535 | 114.589
CobourgWind2035RCP8.5 | Cobourg | Wind | RCP8.5 | 2035 | 86.6677 | 93.3627 | 100.42 | 107.4601 | 114.513
CobourgWind2040RCP8.5 | Cobourg | Wind | RCP8.5 | 2040 | 86.8721 | 93.6355 | 100.7767 | 107.8881 | 115.0146
CobourgWind2045RCP8.5 | Cobourg | Wind | RCP8.5 | 2045 | 87.0764 | 93.9083 | 101.1333 | 108.3161 | 115.5162
CobourgWind2050RCP8.5 | Cobourg | Wind | RCP8.5 | 2050 | 87.4046 | 94.3516 | 101.7167 | 109.0187 | 116.3408
CobourgWind2055RCP8.5 | Cobourg | Wind | RCP8.5 | 2055 | 87.5283 | 94.5221 | 101.9433 | 109.2934 | 116.6638
CobourgWind2060RCP8.5 | Cobourg | Wind | RCP8.5 | 2060 | 87.9486 | 95.0522 | 102.61 | 110.0816 | 117.5682
CobourgWind2065RCP8.5 | Cobourg | Wind | RCP8.5 | 2065 | 88.245 | 95.4118 | 103.05 | 110.5952 | 118.1496
CobourgWind2070RCP8.5 | Cobourg | Wind | RCP8.5 | 2070 | 88.4609 | 95.6815 | 103.3867 | 110.9947 | 118.6094
CobourgWind2075RCP8.5 | Cobourg | Wind | RCP8.5 | 2075 | 88.3803 | 95.5916 | 103.2833 | 110.8805 | 118.4878
CobourgWind2080RCP8.5 | Cobourg | Wind | RCP8.5 | 2080 | 88.2997 | 95.5017 | 103.18 | 110.7664 | 118.3662
CobourgWind2085RCP8.5 | Cobourg | Wind | RCP8.5 | 2085 | 88.5113 | 95.8226 | 103.64 | 111.3389 | 119.0559
CobourgWind2090RCP8.5 | Cobourg | Wind | RCP8.5 | 2090 | 88.7228 | 96.1434 | 104.1 | 111.9113 | 119.7456
CobourgWind2095RCP8.5 | Cobourg | Wind | RCP8.5 | 2095 | 88.7228 | 96.1434 | 104.1 | 111.9113 | 119.7456
CobourgWind2100RCP8.5 | Cobourg | Wind | RCP8.5 | 2100 | 88.7228 | 96.1434 | 104.1 | 111.9113 | 119.7456
CochraneIce Accretion2023RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2023 | 11.8176 | 14.0677 | 16.915 | 19.0947 | 21.2701
CochraneIce Accretion2025RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2025 | 11.8491 | 14.1029 | 16.9575 | 19.1428 | 21.3236
CochraneIce Accretion2030RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2030 | 11.8806 | 14.1382 | 17 | 19.1908 | 21.3772
CochraneIce Accretion2035RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2035 | 11.9122 | 14.1735 | 17.0425 | 19.2388 | 21.4307
CochraneIce Accretion2040RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2040 | 11.9437 | 14.2088 | 17.085 | 19.2868 | 21.4843
CochraneIce Accretion2045RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2045 | 11.9753 | 14.244 | 17.1275 | 19.3349 | 21.5378
CochraneIce Accretion2050RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2050 | 12.0873 | 14.3809 | 17.2992 | 19.5327 | 21.7627
CochraneIce Accretion2055RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2055 | 12.1677 | 14.4825 | 17.4284 | 19.6826 | 21.9341
CochraneIce Accretion2060RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2060 | 12.2481 | 14.5841 | 17.5576 | 19.8324 | 22.1054
CochraneIce Accretion2065RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2065 | 12.3286 | 14.6857 | 17.6868 | 19.9822 | 22.2768
CochraneIce Accretion2070RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2070 | 12.409 | 14.7873 | 17.816 | 20.1321 | 22.4482
CochraneIce Accretion2075RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2075 | 12.4307 | 14.8202 | 17.8585 | 20.1833 | 22.5089
CochraneIce Accretion2080RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2080 | 12.4524 | 14.8531 | 17.901 | 20.2345 | 22.5695
CochraneIce Accretion2085RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2085 | 12.4741 | 14.8861 | 17.9435 | 20.2858 | 22.6302
CochraneIce Accretion2090RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2090 | 12.4958 | 14.919 | 17.986 | 20.337 | 22.6909
CochraneIce Accretion2095RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2095 | 12.5175 | 14.9519 | 18.0285 | 20.3882 | 22.7516
CochraneIce Accretion2100RCP4.5 | Cochrane | Ice Accretion | RCP4.5 | 2100 | 12.5391 | 14.9848 | 18.071 | 20.4394 | 22.8123
CochraneIce Accretion2023RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2023 | 11.8176 | 14.0677 | 16.915 | 19.0947 | 21.2701
CochraneIce Accretion2025RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2025 | 11.8491 | 14.1029 | 16.9575 | 19.1428 | 21.3236
CochraneIce Accretion2030RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2030 | 11.8806 | 14.1382 | 17 | 19.1908 | 21.3772
CochraneIce Accretion2035RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2035 | 11.9122 | 14.1735 | 17.0425 | 19.2388 | 21.4307
CochraneIce Accretion2040RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2040 | 11.9437 | 14.2088 | 17.085 | 19.2868 | 21.4843
CochraneIce Accretion2045RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2045 | 11.9753 | 14.244 | 17.1275 | 19.3349 | 21.5378
CochraneIce Accretion2050RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2050 | 12.0873 | 14.3809 | 17.2992 | 19.5327 | 21.7627
CochraneIce Accretion2055RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2055 | 12.1677 | 14.4825 | 17.4284 | 19.6826 | 21.9341
CochraneIce Accretion2060RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2060 | 12.2481 | 14.5841 | 17.5576 | 19.8324 | 22.1054
CochraneIce Accretion2065RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2065 | 12.3286 | 14.6857 | 17.6868 | 19.9822 | 22.2768
CochraneIce Accretion2070RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2070 | 12.409 | 14.7873 | 17.816 | 20.1321 | 22.4482
CochraneIce Accretion2075RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2075 | 12.4416 | 14.8367 | 17.8798 | 20.2089 | 22.5392
CochraneIce Accretion2080RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2080 | 12.4741 | 14.8861 | 17.9435 | 20.2858 | 22.6302
CochraneIce Accretion2085RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2085 | 12.5066 | 14.9354 | 18.0072 | 20.3626 | 22.7213
CochraneIce Accretion2090RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2090 | 12.413 | 14.8531 | 17.935 | 20.2986 | 22.6624
CochraneIce Accretion2095RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2095 | 12.2868 | 14.7214 | 17.799 | 20.1577 | 22.5124
CochraneIce Accretion2100RCP6.0 | Cochrane | Ice Accretion | RCP6.0 | 2100 | 12.1606 | 14.5897 | 17.663 | 20.0168 | 22.3625
CochraneIce Accretion2023RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2023 | 11.8176 | 14.0677 | 16.915 | 19.0947 | 21.2701
CochraneIce Accretion2025RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2025 | 11.8806 | 14.1382 | 17 | 19.1908 | 21.3772
CochraneIce Accretion2030RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2030 | 11.9437 | 14.2088 | 17.085 | 19.2868 | 21.4843
CochraneIce Accretion2035RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2035 | 12.0068 | 14.2793 | 17.17 | 19.3829 | 21.5914
CochraneIce Accretion2040RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2040 | 12.1409 | 14.4486 | 17.3853 | 19.6326 | 21.877
CochraneIce Accretion2045RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2045 | 12.275 | 14.618 | 17.6007 | 19.8823 | 22.1626
CochraneIce Accretion2050RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2050 | 12.4524 | 14.8531 | 17.901 | 20.2345 | 22.5695
CochraneIce Accretion2055RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2055 | 12.4958 | 14.919 | 17.986 | 20.337 | 22.6909
CochraneIce Accretion2060RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2060 | 12.413 | 14.8531 | 17.935 | 20.2986 | 22.6624
CochraneIce Accretion2065RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2065 | 12.2868 | 14.7214 | 17.799 | 20.1577 | 22.5124
CochraneIce Accretion2070RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2070 | 12.0778 | 14.5051 | 17.578 | 19.9272 | 22.2697
CochraneIce Accretion2075RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2075 | 11.995 | 14.4204 | 17.493 | 19.8375 | 22.1768
CochraneIce Accretion2080RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2080 | 11.9122 | 14.3358 | 17.408 | 19.7479 | 22.084
CochraneIce Accretion2085RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2085 | 11.859 | 14.3146 | 17.4165 | 19.7863 | 22.1483
CochraneIce Accretion2090RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2090 | 11.8057 | 14.2934 | 17.425 | 19.8247 | 22.2125
CochraneIce Accretion2095RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2095 | 11.8057 | 14.2934 | 17.425 | 19.8247 | 22.2125
CochraneIce Accretion2100RCP8.5 | Cochrane | Ice Accretion | RCP8.5 | 2100 | 11.8057 | 14.2934 | 17.425 | 19.8247 | 22.2125
CochraneWind2023RCP4.5 | Cochrane | Wind | RCP4.5 | 2023 | 72.8517 | 78.3778 | 84.1764 | 89.9968 | 95.8175
CochraneWind2025RCP4.5 | Cochrane | Wind | RCP4.5 | 2025 | 72.9266 | 78.4637 | 84.2744 | 90.1047 | 95.9356
CochraneWind2030RCP4.5 | Cochrane | Wind | RCP4.5 | 2030 | 73.0016 | 78.5497 | 84.3724 | 90.2126 | 96.0537
CochraneWind2035RCP4.5 | Cochrane | Wind | RCP4.5 | 2035 | 73.0765 | 78.6356 | 84.4704 | 90.3204 | 96.1718
CochraneWind2040RCP4.5 | Cochrane | Wind | RCP4.5 | 2040 | 73.1515 | 78.7215 | 84.5684 | 90.4283 | 96.2899
CochraneWind2045RCP4.5 | Cochrane | Wind | RCP4.5 | 2045 | 73.2264 | 78.8075 | 84.6664 | 90.5361 | 96.408
CochraneWind2050RCP4.5 | Cochrane | Wind | RCP4.5 | 2050 | 73.3304 | 78.9324 | 84.8148 | 90.7051 | 96.5989
CochraneWind2055RCP4.5 | Cochrane | Wind | RCP4.5 | 2055 | 73.3594 | 78.9715 | 84.8652 | 90.7662 | 96.6716
CochraneWind2060RCP4.5 | Cochrane | Wind | RCP4.5 | 2060 | 73.3884 | 79.0106 | 84.9156 | 90.8273 | 96.7444
CochraneWind2065RCP4.5 | Cochrane | Wind | RCP4.5 | 2065 | 73.4174 | 79.0496 | 84.966 | 90.8885 | 96.8172
CochraneWind2070RCP4.5 | Cochrane | Wind | RCP4.5 | 2070 | 73.4464 | 79.0887 | 85.0164 | 90.9496 | 96.89
CochraneWind2075RCP4.5 | Cochrane | Wind | RCP4.5 | 2075 | 73.4996 | 79.1356 | 85.0542 | 90.9825 | 96.9155
CochraneWind2080RCP4.5 | Cochrane | Wind | RCP4.5 | 2080 | 73.5528 | 79.1824 | 85.092 | 91.0155 | 96.941
CochraneWind2085RCP4.5 | Cochrane | Wind | RCP4.5 | 2085 | 73.606 | 79.2293 | 85.1298 | 91.0484 | 96.9666
CochraneWind2090RCP4.5 | Cochrane | Wind | RCP4.5 | 2090 | 73.6592 | 79.2762 | 85.1676 | 91.0814 | 96.9921
CochraneWind2095RCP4.5 | Cochrane | Wind | RCP4.5 | 2095 | 73.7124 | 79.323 | 85.2054 | 91.1144 | 97.0176
CochraneWind2100RCP4.5 | Cochrane | Wind | RCP4.5 | 2100 | 73.7656 | 79.3699 | 85.2432 | 91.1473 | 97.0432
CochraneWind2023RCP6.0 | Cochrane | Wind | RCP6.0 | 2023 | 72.8517 | 78.3778 | 84.1764 | 89.9968 | 95.8175
CochraneWind2025RCP6.0 | Cochrane | Wind | RCP6.0 | 2025 | 72.9266 | 78.4637 | 84.2744 | 90.1047 | 95.9356
CochraneWind2030RCP6.0 | Cochrane | Wind | RCP6.0 | 2030 | 73.0016 | 78.5497 | 84.3724 | 90.2126 | 96.0537
CochraneWind2035RCP6.0 | Cochrane | Wind | RCP6.0 | 2035 | 73.0765 | 78.6356 | 84.4704 | 90.3204 | 96.1718
CochraneWind2040RCP6.0 | Cochrane | Wind | RCP6.0 | 2040 | 73.1515 | 78.7215 | 84.5684 | 90.4283 | 96.2899
CochraneWind2045RCP6.0 | Cochrane | Wind | RCP6.0 | 2045 | 73.2264 | 78.8075 | 84.6664 | 90.5361 | 96.408
CochraneWind2050RCP6.0 | Cochrane | Wind | RCP6.0 | 2050 | 73.3304 | 78.9324 | 84.8148 | 90.7051 | 96.5989
CochraneWind2055RCP6.0 | Cochrane | Wind | RCP6.0 | 2055 | 73.3594 | 78.9715 | 84.8652 | 90.7662 | 96.6716
CochraneWind2060RCP6.0 | Cochrane | Wind | RCP6.0 | 2060 | 73.3884 | 79.0106 | 84.9156 | 90.8273 | 96.7444
CochraneWind2065RCP6.0 | Cochrane | Wind | RCP6.0 | 2065 | 73.4174 | 79.0496 | 84.966 | 90.8885 | 96.8172
CochraneWind2070RCP6.0 | Cochrane | Wind | RCP6.0 | 2070 | 73.4464 | 79.0887 | 85.0164 | 90.9496 | 96.89
CochraneWind2075RCP6.0 | Cochrane | Wind | RCP6.0 | 2075 | 73.5262 | 79.159 | 85.0731 | 90.999 | 96.9283
CochraneWind2080RCP6.0 | Cochrane | Wind | RCP6.0 | 2080 | 73.606 | 79.2293 | 85.1298 | 91.0484 | 96.9666
CochraneWind2085RCP6.0 | Cochrane | Wind | RCP6.0 | 2085 | 73.6858 | 79.2996 | 85.1865 | 91.0979 | 97.0049
CochraneWind2090RCP6.0 | Cochrane | Wind | RCP6.0 | 2090 | 73.8816 | 79.4871 | 85.3636 | 91.2671 | 97.1645
CochraneWind2095RCP6.0 | Cochrane | Wind | RCP6.0 | 2095 | 73.9977 | 79.6043 | 85.484 | 91.387 | 97.2858
CochraneWind2100RCP6.0 | Cochrane | Wind | RCP6.0 | 2100 | 74.1137 | 79.7215 | 85.6044 | 91.5068 | 97.4071
CochraneWind2023RCP8.5 | Cochrane | Wind | RCP8.5 | 2023 | 72.8517 | 78.3778 | 84.1764 | 89.9968 | 95.8175
CochraneWind2025RCP8.5 | Cochrane | Wind | RCP8.5 | 2025 | 73.0016 | 78.5497 | 84.3724 | 90.2126 | 96.0537
CochraneWind2030RCP8.5 | Cochrane | Wind | RCP8.5 | 2030 | 73.1515 | 78.7215 | 84.5684 | 90.4283 | 96.2899
CochraneWind2035RCP8.5 | Cochrane | Wind | RCP8.5 | 2035 | 73.3014 | 78.8934 | 84.7644 | 90.644 | 96.5261
CochraneWind2040RCP8.5 | Cochrane | Wind | RCP8.5 | 2040 | 73.3497 | 78.9585 | 84.8484 | 90.7458 | 96.6474
CochraneWind2045RCP8.5 | Cochrane | Wind | RCP8.5 | 2045 | 73.3981 | 79.0236 | 84.9324 | 90.8477 | 96.7687
CochraneWind2050RCP8.5 | Cochrane | Wind | RCP8.5 | 2050 | 73.5528 | 79.1824 | 85.092 | 91.0155 | 96.941
CochraneWind2055RCP8.5 | Cochrane | Wind | RCP8.5 | 2055 | 73.6592 | 79.2762 | 85.1676 | 91.0814 | 96.9921
CochraneWind2060RCP8.5 | Cochrane | Wind | RCP8.5 | 2060 | 73.8816 | 79.4871 | 85.3636 | 91.2671 | 97.1645
CochraneWind2065RCP8.5 | Cochrane | Wind | RCP8.5 | 2065 | 73.9977 | 79.6043 | 85.484 | 91.387 | 97.2858
CochraneWind2070RCP8.5 | Cochrane | Wind | RCP8.5 | 2070 | 74.2636 | 79.8751 | 85.7556 | 91.6626 | 97.5667
CochraneWind2075RCP8.5 | Cochrane | Wind | RCP8.5 | 2075 | 74.4135 | 80.0287 | 85.9068 | 91.8184 | 97.7263
CochraneWind2080RCP8.5 | Cochrane | Wind | RCP8.5 | 2080 | 74.5634 | 80.1824 | 86.058 | 91.9742 | 97.8859
CochraneWind2085RCP8.5 | Cochrane | Wind | RCP8.5 | 2085 | 74.7303 | 80.4011 | 86.3436 | 92.3113 | 98.2785
CochraneWind2090RCP8.5 | Cochrane | Wind | RCP8.5 | 2090 | 74.8971 | 80.6198 | 86.6292 | 92.6483 | 98.6711
CochraneWind2095RCP8.5 | Cochrane | Wind | RCP8.5 | 2095 | 74.8971 | 80.6198 | 86.6292 | 92.6483 | 98.6711
CochraneWind2100RCP8.5 | Cochrane | Wind | RCP8.5 | 2100 | 74.8971 | 80.6198 | 86.6292 | 92.6483 | 98.6711
ColborneIce Accretion2023RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
ColborneIce Accretion2025RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
ColborneIce Accretion2030RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
ColborneIce Accretion2035RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
ColborneIce Accretion2040RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
ColborneIce Accretion2045RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
ColborneIce Accretion2050RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
ColborneIce Accretion2055RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
ColborneIce Accretion2060RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
ColborneIce Accretion2065RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
ColborneIce Accretion2070RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
ColborneIce Accretion2075RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2075 | 16.8859 | 20.3972 | 24.8292 | 28.2123 | 31.5682
ColborneIce Accretion2080RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2080 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
ColborneIce Accretion2085RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2085 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
ColborneIce Accretion2090RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2090 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
ColborneIce Accretion2095RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2095 | 16.7235 | 20.3142 | 24.8458 | 28.2877 | 31.7152
ColborneIce Accretion2100RCP4.5 | Colborne | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.2935 | 24.85 | 28.3065 | 31.752
ColborneIce Accretion2023RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
ColborneIce Accretion2025RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
ColborneIce Accretion2030RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
ColborneIce Accretion2035RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
ColborneIce Accretion2040RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
ColborneIce Accretion2045RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
ColborneIce Accretion2050RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
ColborneIce Accretion2055RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
ColborneIce Accretion2060RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
ColborneIce Accretion2065RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
ColborneIce Accretion2070RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
ColborneIce Accretion2075RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2075 | 16.8656 | 20.3869 | 24.8313 | 28.2217 | 31.5866
ColborneIce Accretion2080RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2080 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
ColborneIce Accretion2085RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2085 | 16.7438 | 20.3246 | 24.8438 | 28.2782 | 31.6969
ColborneIce Accretion2090RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2090 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
ColborneIce Accretion2095RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2095 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
ColborneIce Accretion2100RCP6.0 | Colborne | Ice Accretion | RCP6.0 | 2100 | 15.6565 | 19.173 | 23.6 | 26.9505 | 30.2715
ColborneIce Accretion2023RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
ColborneIce Accretion2025RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2025 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
ColborneIce Accretion2030RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2030 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
ColborneIce Accretion2035RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2035 | 17.6745 | 21.2272 | 25.725 | 29.154 | 32.571
ColborneIce Accretion2040RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2040 | 17.4251 | 20.9575 | 25.425 | 28.8338 | 32.2245
ColborneIce Accretion2045RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2045 | 17.1758 | 20.6877 | 25.125 | 28.5137 | 31.878
ColborneIce Accretion2050RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2050 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
ColborneIce Accretion2055RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2055 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
ColborneIce Accretion2060RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2060 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
ColborneIce Accretion2065RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2065 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
ColborneIce Accretion2070RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2070 | 15.2216 | 18.6888 | 23.05 | 26.3478 | 29.631
ColborneIce Accretion2075RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2075 | 14.7867 | 18.2047 | 22.5 | 25.7452 | 28.9905
ColborneIce Accretion2080RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2080 | 14.3518 | 17.7205 | 21.95 | 25.1425 | 28.35
ColborneIce Accretion2085RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2085 | 13.6908 | 16.9424 | 21.025 | 24.0972 | 27.1845
ColborneIce Accretion2090RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2090 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
ColborneIce Accretion2095RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2095 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
ColborneIce Accretion2100RCP8.5 | Colborne | Ice Accretion | RCP8.5 | 2100 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
ColborneWind2023RCP4.5 | Colborne | Wind | RCP4.5 | 2023 | 85.9977 | 92.6408 | 99.6237 | 106.608 | 113.5936
ColborneWind2025RCP4.5 | Colborne | Wind | RCP4.5 | 2025 | 85.9649 | 92.6055 | 99.5891 | 106.5709 | 113.556
ColborneWind2030RCP4.5 | Colborne | Wind | RCP4.5 | 2030 | 85.9321 | 92.5702 | 99.5544 | 106.5338 | 113.5183
ColborneWind2035RCP4.5 | Colborne | Wind | RCP4.5 | 2035 | 85.8994 | 92.535 | 99.5198 | 106.4967 | 113.4807
ColborneWind2040RCP4.5 | Colborne | Wind | RCP4.5 | 2040 | 85.8666 | 92.4997 | 99.4851 | 106.4597 | 113.4431
ColborneWind2045RCP4.5 | Colborne | Wind | RCP4.5 | 2045 | 85.8338 | 92.4644 | 99.4505 | 106.4226 | 113.4055
ColborneWind2050RCP4.5 | Colborne | Wind | RCP4.5 | 2050 | 85.9224 | 92.5911 | 99.6277 | 106.6397 | 113.6658
ColborneWind2055RCP4.5 | Colborne | Wind | RCP4.5 | 2055 | 86.0438 | 92.7532 | 99.8395 | 106.894 | 113.9638
ColborneWind2060RCP4.5 | Colborne | Wind | RCP4.5 | 2060 | 86.1652 | 92.9152 | 100.0514 | 107.1482 | 114.2617
ColborneWind2065RCP4.5 | Colborne | Wind | RCP4.5 | 2065 | 86.2866 | 93.0772 | 100.2632 | 107.4024 | 114.5597
ColborneWind2070RCP4.5 | Colborne | Wind | RCP4.5 | 2070 | 86.408 | 93.2393 | 100.4751 | 107.6567 | 114.8576
ColborneWind2075RCP4.5 | Colborne | Wind | RCP4.5 | 2075 | 86.4693 | 93.3237 | 100.5873 | 107.7926 | 115.0175
ColborneWind2080RCP4.5 | Colborne | Wind | RCP4.5 | 2080 | 86.5305 | 93.4081 | 100.6995 | 107.9285 | 115.1774
ColborneWind2085RCP4.5 | Colborne | Wind | RCP4.5 | 2085 | 86.5918 | 93.4925 | 100.8117 | 108.0645 | 115.3373
ColborneWind2090RCP4.5 | Colborne | Wind | RCP4.5 | 2090 | 86.6531 | 93.5769 | 100.9239 | 108.2004 | 115.4972
ColborneWind2095RCP4.5 | Colborne | Wind | RCP4.5 | 2095 | 86.7143 | 93.6613 | 101.0361 | 108.3364 | 115.657
ColborneWind2100RCP4.5 | Colborne | Wind | RCP4.5 | 2100 | 86.7756 | 93.7457 | 101.1483 | 108.4723 | 115.8169
ColborneWind2023RCP6.0 | Colborne | Wind | RCP6.0 | 2023 | 85.9977 | 92.6408 | 99.6237 | 106.608 | 113.5936
ColborneWind2025RCP6.0 | Colborne | Wind | RCP6.0 | 2025 | 85.9649 | 92.6055 | 99.5891 | 106.5709 | 113.556
ColborneWind2030RCP6.0 | Colborne | Wind | RCP6.0 | 2030 | 85.9321 | 92.5702 | 99.5544 | 106.5338 | 113.5183
ColborneWind2035RCP6.0 | Colborne | Wind | RCP6.0 | 2035 | 85.8994 | 92.535 | 99.5198 | 106.4967 | 113.4807
ColborneWind2040RCP6.0 | Colborne | Wind | RCP6.0 | 2040 | 85.8666 | 92.4997 | 99.4851 | 106.4597 | 113.4431
ColborneWind2045RCP6.0 | Colborne | Wind | RCP6.0 | 2045 | 85.8338 | 92.4644 | 99.4505 | 106.4226 | 113.4055
ColborneWind2050RCP6.0 | Colborne | Wind | RCP6.0 | 2050 | 85.9224 | 92.5911 | 99.6277 | 106.6397 | 113.6658
ColborneWind2055RCP6.0 | Colborne | Wind | RCP6.0 | 2055 | 86.0438 | 92.7532 | 99.8395 | 106.894 | 113.9638
ColborneWind2060RCP6.0 | Colborne | Wind | RCP6.0 | 2060 | 86.1652 | 92.9152 | 100.0514 | 107.1482 | 114.2617
ColborneWind2065RCP6.0 | Colborne | Wind | RCP6.0 | 2065 | 86.2866 | 93.0772 | 100.2632 | 107.4024 | 114.5597
ColborneWind2070RCP6.0 | Colborne | Wind | RCP6.0 | 2070 | 86.408 | 93.2393 | 100.4751 | 107.6567 | 114.8576
ColborneWind2075RCP6.0 | Colborne | Wind | RCP6.0 | 2075 | 86.4999 | 93.3659 | 100.6434 | 107.8606 | 115.0974
ColborneWind2080RCP6.0 | Colborne | Wind | RCP6.0 | 2080 | 86.5918 | 93.4925 | 100.8117 | 108.0645 | 115.3373
ColborneWind2085RCP6.0 | Colborne | Wind | RCP6.0 | 2085 | 86.6837 | 93.6191 | 100.98 | 108.2684 | 115.5771
ColborneWind2090RCP6.0 | Colborne | Wind | RCP6.0 | 2090 | 87.0691 | 94.1017 | 101.5839 | 108.9808 | 116.3925
ColborneWind2095RCP6.0 | Colborne | Wind | RCP6.0 | 2095 | 87.3626 | 94.4577 | 102.0195 | 109.4892 | 116.9681
ColborneWind2100RCP6.0 | Colborne | Wind | RCP6.0 | 2100 | 87.6561 | 94.8137 | 102.4551 | 109.9977 | 117.5437
ColborneWind2023RCP8.5 | Colborne | Wind | RCP8.5 | 2023 | 85.9977 | 92.6408 | 99.6237 | 106.608 | 113.5936
ColborneWind2025RCP8.5 | Colborne | Wind | RCP8.5 | 2025 | 85.9321 | 92.5702 | 99.5544 | 106.5338 | 113.5183
ColborneWind2030RCP8.5 | Colborne | Wind | RCP8.5 | 2030 | 85.8666 | 92.4997 | 99.4851 | 106.4597 | 113.4431
ColborneWind2035RCP8.5 | Colborne | Wind | RCP8.5 | 2035 | 85.8011 | 92.4291 | 99.4158 | 106.3855 | 113.3679
ColborneWind2040RCP8.5 | Colborne | Wind | RCP8.5 | 2040 | 86.0034 | 92.6991 | 99.7689 | 106.8092 | 113.8645
ColborneWind2045RCP8.5 | Colborne | Wind | RCP8.5 | 2045 | 86.2057 | 92.9692 | 100.122 | 107.2329 | 114.361
ColborneWind2050RCP8.5 | Colborne | Wind | RCP8.5 | 2050 | 86.5305 | 93.4081 | 100.6995 | 107.9285 | 115.1774
ColborneWind2055RCP8.5 | Colborne | Wind | RCP8.5 | 2055 | 86.6531 | 93.5769 | 100.9239 | 108.2004 | 115.4972
ColborneWind2060RCP8.5 | Colborne | Wind | RCP8.5 | 2060 | 87.0691 | 94.1017 | 101.5839 | 108.9808 | 116.3925
ColborneWind2065RCP8.5 | Colborne | Wind | RCP8.5 | 2065 | 87.3626 | 94.4577 | 102.0195 | 109.4892 | 116.9681
ColborneWind2070RCP8.5 | Colborne | Wind | RCP8.5 | 2070 | 87.5763 | 94.7247 | 102.3528 | 109.8847 | 117.4233
ColborneWind2075RCP8.5 | Colborne | Wind | RCP8.5 | 2075 | 87.4965 | 94.6357 | 102.2505 | 109.7717 | 117.3029
ColborneWind2080RCP8.5 | Colborne | Wind | RCP8.5 | 2080 | 87.4167 | 94.5467 | 102.1482 | 109.6587 | 117.1825
ColborneWind2085RCP8.5 | Colborne | Wind | RCP8.5 | 2085 | 87.6262 | 94.8643 | 102.6036 | 110.2255 | 117.8653
ColborneWind2090RCP8.5 | Colborne | Wind | RCP8.5 | 2090 | 87.8356 | 95.182 | 103.059 | 110.7922 | 118.5481
ColborneWind2095RCP8.5 | Colborne | Wind | RCP8.5 | 2095 | 87.8356 | 95.182 | 103.059 | 110.7922 | 118.5481
ColborneWind2100RCP8.5 | Colborne | Wind | RCP8.5 | 2100 | 87.8356 | 95.182 | 103.059 | 110.7922 | 118.5481
CollingwoodIce Accretion2023RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2023 | 14.0422 | 16.8158 | 20.32 | 22.9842 | 25.6536
CollingwoodIce Accretion2025RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2025 | 14.0399 | 16.8186 | 20.3333 | 23.0068 | 25.683
CollingwoodIce Accretion2030RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2030 | 14.0375 | 16.8213 | 20.3467 | 23.0294 | 25.7124
CollingwoodIce Accretion2035RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2035 | 14.0352 | 16.8241 | 20.36 | 23.052 | 25.7418
CollingwoodIce Accretion2040RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2040 | 14.0329 | 16.8269 | 20.3733 | 23.0746 | 25.7712
CollingwoodIce Accretion2045RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2045 | 14.0306 | 16.8296 | 20.3867 | 23.0972 | 25.8006
CollingwoodIce Accretion2050RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2050 | 14.0004 | 16.8158 | 20.392 | 23.1243 | 25.8401
CollingwoodIce Accretion2055RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2055 | 13.9726 | 16.7992 | 20.384 | 23.1288 | 25.8502
CollingwoodIce Accretion2060RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2060 | 13.9448 | 16.7826 | 20.376 | 23.1334 | 25.8602
CollingwoodIce Accretion2065RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2065 | 13.9169 | 16.766 | 20.368 | 23.1379 | 25.8703
CollingwoodIce Accretion2070RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2070 | 13.8891 | 16.7494 | 20.36 | 23.1424 | 25.8804
CollingwoodIce Accretion2075RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2075 | 13.8729 | 16.7522 | 20.3867 | 23.1838 | 25.9392
CollingwoodIce Accretion2080RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2080 | 13.8566 | 16.7549 | 20.4133 | 23.2253 | 25.998
CollingwoodIce Accretion2085RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2085 | 13.8404 | 16.7577 | 20.44 | 23.2667 | 26.0568
CollingwoodIce Accretion2090RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2090 | 13.8241 | 16.7605 | 20.4667 | 23.3081 | 26.1156
CollingwoodIce Accretion2095RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2095 | 13.8079 | 16.7632 | 20.4933 | 23.3496 | 26.1744
CollingwoodIce Accretion2100RCP4.5 | Collingwood | Ice Accretion | RCP4.5 | 2100 | 13.7917 | 16.766 | 20.52 | 23.391 | 26.2332
CollingwoodIce Accretion2023RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2023 | 14.0422 | 16.8158 | 20.32 | 22.9842 | 25.6536
CollingwoodIce Accretion2025RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2025 | 14.0399 | 16.8186 | 20.3333 | 23.0068 | 25.683
CollingwoodIce Accretion2030RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2030 | 14.0375 | 16.8213 | 20.3467 | 23.0294 | 25.7124
CollingwoodIce Accretion2035RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2035 | 14.0352 | 16.8241 | 20.36 | 23.052 | 25.7418
CollingwoodIce Accretion2040RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2040 | 14.0329 | 16.8269 | 20.3733 | 23.0746 | 25.7712
CollingwoodIce Accretion2045RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2045 | 14.0306 | 16.8296 | 20.3867 | 23.0972 | 25.8006
CollingwoodIce Accretion2050RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2050 | 14.0004 | 16.8158 | 20.392 | 23.1243 | 25.8401
CollingwoodIce Accretion2055RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2055 | 13.9726 | 16.7992 | 20.384 | 23.1288 | 25.8502
CollingwoodIce Accretion2060RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2060 | 13.9448 | 16.7826 | 20.376 | 23.1334 | 25.8602
CollingwoodIce Accretion2065RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2065 | 13.9169 | 16.766 | 20.368 | 23.1379 | 25.8703
CollingwoodIce Accretion2070RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2070 | 13.8891 | 16.7494 | 20.36 | 23.1424 | 25.8804
CollingwoodIce Accretion2075RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2075 | 13.8647 | 16.7535 | 20.4 | 23.2045 | 25.9686
CollingwoodIce Accretion2080RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2080 | 13.8404 | 16.7577 | 20.44 | 23.2667 | 26.0568
CollingwoodIce Accretion2085RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2085 | 13.816 | 16.7618 | 20.48 | 23.3288 | 26.145
CollingwoodIce Accretion2090RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2090 | 13.6571 | 16.6332 | 20.3933 | 23.2629 | 26.1072
CollingwoodIce Accretion2095RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2095 | 13.5226 | 16.5004 | 20.2667 | 23.1349 | 25.9812
CollingwoodIce Accretion2100RCP6.0 | Collingwood | Ice Accretion | RCP6.0 | 2100 | 13.3881 | 16.3676 | 20.14 | 23.0068 | 25.8552
CollingwoodIce Accretion2023RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2023 | 14.0422 | 16.8158 | 20.32 | 22.9842 | 25.6536
CollingwoodIce Accretion2025RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2025 | 14.0375 | 16.8213 | 20.3467 | 23.0294 | 25.7124
CollingwoodIce Accretion2030RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2030 | 14.0329 | 16.8269 | 20.3733 | 23.0746 | 25.7712
CollingwoodIce Accretion2035RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2035 | 14.0283 | 16.8324 | 20.4 | 23.1198 | 25.83
CollingwoodIce Accretion2040RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2040 | 13.9819 | 16.8047 | 20.3867 | 23.1273 | 25.8468
CollingwoodIce Accretion2045RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2045 | 13.9355 | 16.7771 | 20.3733 | 23.1349 | 25.8636
CollingwoodIce Accretion2050RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2050 | 13.8566 | 16.7549 | 20.4133 | 23.2253 | 25.998
CollingwoodIce Accretion2055RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2055 | 13.8241 | 16.7605 | 20.4667 | 23.3081 | 26.1156
CollingwoodIce Accretion2060RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2060 | 13.6571 | 16.6332 | 20.3933 | 23.2629 | 26.1072
CollingwoodIce Accretion2065RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2065 | 13.5226 | 16.5004 | 20.2667 | 23.1349 | 25.9812
CollingwoodIce Accretion2070RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2070 | 13.1283 | 16.0965 | 19.8467 | 22.6979 | 25.536
CollingwoodIce Accretion2075RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2075 | 12.8685 | 15.8253 | 19.5533 | 22.3891 | 25.2168
CollingwoodIce Accretion2080RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2080 | 12.6087 | 15.5542 | 19.26 | 22.0802 | 24.8976
CollingwoodIce Accretion2085RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2085 | 11.9755 | 14.8155 | 18.4 | 21.1197 | 23.8266
CollingwoodIce Accretion2090RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2090 | 11.3423 | 14.0768 | 17.54 | 20.1592 | 22.7556
CollingwoodIce Accretion2095RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2095 | 11.3423 | 14.0768 | 17.54 | 20.1592 | 22.7556
CollingwoodIce Accretion2100RCP8.5 | Collingwood | Ice Accretion | RCP8.5 | 2100 | 11.3423 | 14.0768 | 17.54 | 20.1592 | 22.7556
CollingwoodWind2023RCP4.5 | Collingwood | Wind | RCP4.5 | 2023 | 81.1673 | 87.3763 | 93.8966 | 100.4392 | 106.9671
CollingwoodWind2025RCP4.5 | Collingwood | Wind | RCP4.5 | 2025 | 81.1633 | 87.369 | 93.8856 | 100.4224 | 106.9493
CollingwoodWind2030RCP4.5 | Collingwood | Wind | RCP4.5 | 2030 | 81.1592 | 87.3617 | 93.8747 | 100.4057 | 106.9314
CollingwoodWind2035RCP4.5 | Collingwood | Wind | RCP4.5 | 2035 | 81.1552 | 87.3544 | 93.8637 | 100.3889 | 106.9135
CollingwoodWind2040RCP4.5 | Collingwood | Wind | RCP4.5 | 2040 | 81.1511 | 87.3472 | 93.8527 | 100.3721 | 106.8957
CollingwoodWind2045RCP4.5 | Collingwood | Wind | RCP4.5 | 2045 | 81.1471 | 87.3399 | 93.8418 | 100.3554 | 106.8778
CollingwoodWind2050RCP4.5 | Collingwood | Wind | RCP4.5 | 2050 | 81.1381 | 87.3168 | 93.8007 | 100.2984 | 106.8064
CollingwoodWind2055RCP4.5 | Collingwood | Wind | RCP4.5 | 2055 | 81.1333 | 87.3011 | 93.7706 | 100.2581 | 106.7528
CollingwoodWind2060RCP4.5 | Collingwood | Wind | RCP4.5 | 2060 | 81.1284 | 87.2854 | 93.7406 | 100.2179 | 106.6992
CollingwoodWind2065RCP4.5 | Collingwood | Wind | RCP4.5 | 2065 | 81.1235 | 87.2696 | 93.7105 | 100.1777 | 106.6456
CollingwoodWind2070RCP4.5 | Collingwood | Wind | RCP4.5 | 2070 | 81.1186 | 87.2539 | 93.6804 | 100.1374 | 106.5921
CollingwoodWind2075RCP4.5 | Collingwood | Wind | RCP4.5 | 2075 | 81.1552 | 87.3078 | 93.7556 | 100.2313 | 106.7028
CollingwoodWind2080RCP4.5 | Collingwood | Wind | RCP4.5 | 2080 | 81.1917 | 87.3617 | 93.8308 | 100.3252 | 106.8135
CollingwoodWind2085RCP4.5 | Collingwood | Wind | RCP4.5 | 2085 | 81.2282 | 87.4156 | 93.906 | 100.4191 | 106.9242
CollingwoodWind2090RCP4.5 | Collingwood | Wind | RCP4.5 | 2090 | 81.2647 | 87.4695 | 93.9812 | 100.5129 | 107.035
CollingwoodWind2095RCP4.5 | Collingwood | Wind | RCP4.5 | 2095 | 81.3013 | 87.5234 | 94.0564 | 100.6068 | 107.1457
CollingwoodWind2100RCP4.5 | Collingwood | Wind | RCP4.5 | 2100 | 81.3378 | 87.5774 | 94.1316 | 100.7007 | 107.2564
CollingwoodWind2023RCP6.0 | Collingwood | Wind | RCP6.0 | 2023 | 81.1673 | 87.3763 | 93.8966 | 100.4392 | 106.9671
CollingwoodWind2025RCP6.0 | Collingwood | Wind | RCP6.0 | 2025 | 81.1633 | 87.369 | 93.8856 | 100.4224 | 106.9493
CollingwoodWind2030RCP6.0 | Collingwood | Wind | RCP6.0 | 2030 | 81.1592 | 87.3617 | 93.8747 | 100.4057 | 106.9314
CollingwoodWind2035RCP6.0 | Collingwood | Wind | RCP6.0 | 2035 | 81.1552 | 87.3544 | 93.8637 | 100.3889 | 106.9135
CollingwoodWind2040RCP6.0 | Collingwood | Wind | RCP6.0 | 2040 | 81.1511 | 87.3472 | 93.8527 | 100.3721 | 106.8957
CollingwoodWind2045RCP6.0 | Collingwood | Wind | RCP6.0 | 2045 | 81.1471 | 87.3399 | 93.8418 | 100.3554 | 106.8778
CollingwoodWind2050RCP6.0 | Collingwood | Wind | RCP6.0 | 2050 | 81.1381 | 87.3168 | 93.8007 | 100.2984 | 106.8064
CollingwoodWind2055RCP6.0 | Collingwood | Wind | RCP6.0 | 2055 | 81.1333 | 87.3011 | 93.7706 | 100.2581 | 106.7528
CollingwoodWind2060RCP6.0 | Collingwood | Wind | RCP6.0 | 2060 | 81.1284 | 87.2854 | 93.7406 | 100.2179 | 106.6992
CollingwoodWind2065RCP6.0 | Collingwood | Wind | RCP6.0 | 2065 | 81.1235 | 87.2696 | 93.7105 | 100.1777 | 106.6456
CollingwoodWind2070RCP6.0 | Collingwood | Wind | RCP6.0 | 2070 | 81.1186 | 87.2539 | 93.6804 | 100.1374 | 106.5921
CollingwoodWind2075RCP6.0 | Collingwood | Wind | RCP6.0 | 2075 | 81.1734 | 87.3348 | 93.7932 | 100.2783 | 106.7582
CollingwoodWind2080RCP6.0 | Collingwood | Wind | RCP6.0 | 2080 | 81.2282 | 87.4156 | 93.906 | 100.4191 | 106.9242
CollingwoodWind2085RCP6.0 | Collingwood | Wind | RCP6.0 | 2085 | 81.283 | 87.4965 | 94.0188 | 100.5599 | 107.0903
CollingwoodWind2090RCP6.0 | Collingwood | Wind | RCP6.0 | 2090 | 81.5434 | 87.825 | 94.4324 | 101.0427 | 107.6458
CollingwoodWind2095RCP6.0 | Collingwood | Wind | RCP6.0 | 2095 | 81.749 | 88.0727 | 94.7332 | 101.3846 | 108.0351
CollingwoodWind2100RCP6.0 | Collingwood | Wind | RCP6.0 | 2100 | 81.9547 | 88.3204 | 95.034 | 101.7266 | 108.4245
CollingwoodWind2023RCP8.5 | Collingwood | Wind | RCP8.5 | 2023 | 81.1673 | 87.3763 | 93.8966 | 100.4392 | 106.9671
CollingwoodWind2025RCP8.5 | Collingwood | Wind | RCP8.5 | 2025 | 81.1592 | 87.3617 | 93.8747 | 100.4057 | 106.9314
CollingwoodWind2030RCP8.5 | Collingwood | Wind | RCP8.5 | 2030 | 81.1511 | 87.3472 | 93.8527 | 100.3721 | 106.8957
CollingwoodWind2035RCP8.5 | Collingwood | Wind | RCP8.5 | 2035 | 81.143 | 87.3326 | 93.8308 | 100.3386 | 106.86
CollingwoodWind2040RCP8.5 | Collingwood | Wind | RCP8.5 | 2040 | 81.1349 | 87.3064 | 93.7807 | 100.2716 | 106.7707
CollingwoodWind2045RCP8.5 | Collingwood | Wind | RCP8.5 | 2045 | 81.1268 | 87.2801 | 93.7305 | 100.2045 | 106.6814
CollingwoodWind2050RCP8.5 | Collingwood | Wind | RCP8.5 | 2050 | 81.1917 | 87.3617 | 93.8308 | 100.3252 | 106.8135
CollingwoodWind2055RCP8.5 | Collingwood | Wind | RCP8.5 | 2055 | 81.2647 | 87.4695 | 93.9812 | 100.5129 | 107.035
CollingwoodWind2060RCP8.5 | Collingwood | Wind | RCP8.5 | 2060 | 81.5434 | 87.825 | 94.4324 | 101.0427 | 107.6458
CollingwoodWind2065RCP8.5 | Collingwood | Wind | RCP8.5 | 2065 | 81.749 | 88.0727 | 94.7332 | 101.3846 | 108.0351
CollingwoodWind2070RCP8.5 | Collingwood | Wind | RCP8.5 | 2070 | 82.0602 | 88.4486 | 95.1875 | 101.9043 | 108.6245
CollingwoodWind2075RCP8.5 | Collingwood | Wind | RCP8.5 | 2075 | 82.1657 | 88.5769 | 95.3411 | 102.082 | 108.8246
CollingwoodWind2080RCP8.5 | Collingwood | Wind | RCP8.5 | 2080 | 82.2712 | 88.7051 | 95.4946 | 102.2597 | 109.0246
CollingwoodWind2085RCP8.5 | Collingwood | Wind | RCP8.5 | 2085 | 82.3727 | 88.8275 | 95.645 | 102.4307 | 109.2175
CollingwoodWind2090RCP8.5 | Collingwood | Wind | RCP8.5 | 2090 | 82.4741 | 88.9499 | 95.7954 | 102.6017 | 109.4104
CollingwoodWind2095RCP8.5 | Collingwood | Wind | RCP8.5 | 2095 | 82.4741 | 88.9499 | 95.7954 | 102.6017 | 109.4104
CollingwoodWind2100RCP8.5 | Collingwood | Wind | RCP8.5 | 2100 | 82.4741 | 88.9499 | 95.7954 | 102.6017 | 109.4104
CornwallIce Accretion2023RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2023 | 21.0215 | 25.0743 | 30.21 | 34.1373 | 38.0646
CornwallIce Accretion2025RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2025 | 21.0737 | 25.1531 | 30.325 | 34.2842 | 38.2347
CornwallIce Accretion2030RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2030 | 21.1259 | 25.232 | 30.44 | 34.4311 | 38.4048
CornwallIce Accretion2035RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2035 | 21.1781 | 25.3108 | 30.555 | 34.578 | 38.5749
CornwallIce Accretion2040RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2040 | 21.2303 | 25.3897 | 30.67 | 34.7249 | 38.745
CornwallIce Accretion2045RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2045 | 21.2825 | 25.4686 | 30.785 | 34.8718 | 38.9151
CornwallIce Accretion2050RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2050 | 21.3054 | 25.5325 | 30.9 | 35.0187 | 39.1003
CornwallIce Accretion2055RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2055 | 21.2762 | 25.5175 | 30.9 | 35.0187 | 39.1154
CornwallIce Accretion2060RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2060 | 21.247 | 25.5026 | 30.9 | 35.0187 | 39.1306
CornwallIce Accretion2065RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2065 | 21.2177 | 25.4876 | 30.9 | 35.0187 | 39.1457
CornwallIce Accretion2070RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2070 | 21.1885 | 25.4727 | 30.9 | 35.0187 | 39.1608
CornwallIce Accretion2075RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2075 | 21.2859 | 25.6138 | 31.1 | 35.2616 | 39.4443
CornwallIce Accretion2080RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2080 | 21.3834 | 25.7549 | 31.3 | 35.5046 | 39.7278
CornwallIce Accretion2085RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2085 | 21.4808 | 25.896 | 31.5 | 35.7475 | 40.0113
CornwallIce Accretion2090RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2090 | 21.5782 | 26.0371 | 31.7 | 35.9905 | 40.2948
CornwallIce Accretion2095RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2095 | 21.6756 | 26.1782 | 31.9 | 36.2334 | 40.5783
CornwallIce Accretion2100RCP4.5 | Cornwall | Ice Accretion | RCP4.5 | 2100 | 21.773 | 26.3193 | 32.1 | 36.4764 | 40.8618
CornwallIce Accretion2023RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2023 | 21.0215 | 25.0743 | 30.21 | 34.1373 | 38.0646
CornwallIce Accretion2025RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2025 | 21.0737 | 25.1531 | 30.325 | 34.2842 | 38.2347
CornwallIce Accretion2030RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2030 | 21.1259 | 25.232 | 30.44 | 34.4311 | 38.4048
CornwallIce Accretion2035RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2035 | 21.1781 | 25.3108 | 30.555 | 34.578 | 38.5749
CornwallIce Accretion2040RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2040 | 21.2303 | 25.3897 | 30.67 | 34.7249 | 38.745
CornwallIce Accretion2045RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2045 | 21.2825 | 25.4686 | 30.785 | 34.8718 | 38.9151
CornwallIce Accretion2050RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2050 | 21.3054 | 25.5325 | 30.9 | 35.0187 | 39.1003
CornwallIce Accretion2055RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2055 | 21.2762 | 25.5175 | 30.9 | 35.0187 | 39.1154
CornwallIce Accretion2060RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2060 | 21.247 | 25.5026 | 30.9 | 35.0187 | 39.1306
CornwallIce Accretion2065RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2065 | 21.2177 | 25.4876 | 30.9 | 35.0187 | 39.1457
CornwallIce Accretion2070RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2070 | 21.1885 | 25.4727 | 30.9 | 35.0187 | 39.1608
CornwallIce Accretion2075RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2075 | 21.3346 | 25.6843 | 31.2 | 35.3831 | 39.586
CornwallIce Accretion2080RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2080 | 21.4808 | 25.896 | 31.5 | 35.7475 | 40.0113
CornwallIce Accretion2085RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2085 | 21.6269 | 26.1076 | 31.8 | 36.112 | 40.4365
CornwallIce Accretion2090RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2090 | 21.6269 | 26.1948 | 31.98 | 36.3634 | 40.761
CornwallIce Accretion2095RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2095 | 21.4808 | 26.0703 | 31.86 | 36.2504 | 40.6602
CornwallIce Accretion2100RCP6.0 | Cornwall | Ice Accretion | RCP6.0 | 2100 | 21.3346 | 25.9458 | 31.74 | 36.1374 | 40.5594
CornwallIce Accretion2023RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2023 | 21.0215 | 25.0743 | 30.21 | 34.1373 | 38.0646
CornwallIce Accretion2025RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2025 | 21.1259 | 25.232 | 30.44 | 34.4311 | 38.4048
CornwallIce Accretion2030RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2030 | 21.2303 | 25.3897 | 30.67 | 34.7249 | 38.745
CornwallIce Accretion2035RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2035 | 21.3346 | 25.5474 | 30.9 | 35.0187 | 39.0852
CornwallIce Accretion2040RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2040 | 21.2859 | 25.5225 | 30.9 | 35.0187 | 39.1104
CornwallIce Accretion2045RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2045 | 21.2372 | 25.4976 | 30.9 | 35.0187 | 39.1356
CornwallIce Accretion2050RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2050 | 21.3834 | 25.7549 | 31.3 | 35.5046 | 39.7278
CornwallIce Accretion2055RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2055 | 21.5782 | 26.0371 | 31.7 | 35.9905 | 40.2948
CornwallIce Accretion2060RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2060 | 21.6269 | 26.1948 | 31.98 | 36.3634 | 40.761
CornwallIce Accretion2065RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2065 | 21.4808 | 26.0703 | 31.86 | 36.2504 | 40.6602
CornwallIce Accretion2070RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2070 | 21.0563 | 25.6387 | 31.4 | 35.7758 | 40.1688
CornwallIce Accretion2075RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2075 | 20.778 | 25.3316 | 31.06 | 35.4142 | 39.7782
CornwallIce Accretion2080RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2080 | 20.4996 | 25.0245 | 30.72 | 35.0526 | 39.3876
CornwallIce Accretion2085RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2085 | 19.6333 | 24.0036 | 29.52 | 33.6966 | 37.8756
CornwallIce Accretion2090RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2090 | 18.767 | 22.9827 | 28.32 | 32.3406 | 36.3636
CornwallIce Accretion2095RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2095 | 18.767 | 22.9827 | 28.32 | 32.3406 | 36.3636
CornwallIce Accretion2100RCP8.5 | Cornwall | Ice Accretion | RCP8.5 | 2100 | 18.767 | 22.9827 | 28.32 | 32.3406 | 36.3636
CornwallWind2023RCP4.5 | Cornwall | Wind | RCP4.5 | 2023 | 81.8005 | 88.1806 | 94.9024 | 101.616 | 108.3173
CornwallWind2025RCP4.5 | Cornwall | Wind | RCP4.5 | 2025 | 81.8437 | 88.2214 | 94.9416 | 101.6545 | 108.3548
CornwallWind2030RCP4.5 | Cornwall | Wind | RCP4.5 | 2030 | 81.887 | 88.2621 | 94.9807 | 101.6931 | 108.3923
CornwallWind2035RCP4.5 | Cornwall | Wind | RCP4.5 | 2035 | 81.9303 | 88.3029 | 95.0199 | 101.7316 | 108.4298
CornwallWind2040RCP4.5 | Cornwall | Wind | RCP4.5 | 2040 | 81.9736 | 88.3437 | 95.0591 | 101.7702 | 108.4674
CornwallWind2045RCP4.5 | Cornwall | Wind | RCP4.5 | 2045 | 82.0169 | 88.3845 | 95.0982 | 101.8088 | 108.5049
CornwallWind2050RCP4.5 | Cornwall | Wind | RCP4.5 | 2050 | 82.0358 | 88.3956 | 95.1017 | 101.8031 | 108.4931
CornwallWind2055RCP4.5 | Cornwall | Wind | RCP4.5 | 2055 | 82.0115 | 88.3659 | 95.066 | 101.7588 | 108.4438
CornwallWind2060RCP4.5 | Cornwall | Wind | RCP4.5 | 2060 | 81.9871 | 88.3362 | 95.0302 | 101.7145 | 108.3945
CornwallWind2065RCP4.5 | Cornwall | Wind | RCP4.5 | 2065 | 81.9628 | 88.3064 | 94.9945 | 101.6703 | 108.3452
CornwallWind2070RCP4.5 | Cornwall | Wind | RCP4.5 | 2070 | 81.9384 | 88.2767 | 94.9588 | 101.626 | 108.2959
CornwallWind2075RCP4.5 | Cornwall | Wind | RCP4.5 | 2075 | 81.9181 | 88.2549 | 94.9353 | 101.6026 | 108.2709
CornwallWind2080RCP4.5 | Cornwall | Wind | RCP4.5 | 2080 | 81.8979 | 88.233 | 94.9118 | 101.5791 | 108.2459
CornwallWind2085RCP4.5 | Cornwall | Wind | RCP4.5 | 2085 | 81.8776 | 88.2112 | 94.8883 | 101.5556 | 108.2209
CornwallWind2090RCP4.5 | Cornwall | Wind | RCP4.5 | 2090 | 81.8573 | 88.1893 | 94.8648 | 101.5322 | 108.1959
CornwallWind2095RCP4.5 | Cornwall | Wind | RCP4.5 | 2095 | 81.837 | 88.1674 | 94.8413 | 101.5087 | 108.1709
CornwallWind2100RCP4.5 | Cornwall | Wind | RCP4.5 | 2100 | 81.8167 | 88.1456 | 94.8178 | 101.4852 | 108.1459
CornwallWind2023RCP6.0 | Cornwall | Wind | RCP6.0 | 2023 | 81.8005 | 88.1806 | 94.9024 | 101.616 | 108.3173
CornwallWind2025RCP6.0 | Cornwall | Wind | RCP6.0 | 2025 | 81.8437 | 88.2214 | 94.9416 | 101.6545 | 108.3548
CornwallWind2030RCP6.0 | Cornwall | Wind | RCP6.0 | 2030 | 81.887 | 88.2621 | 94.9807 | 101.6931 | 108.3923
CornwallWind2035RCP6.0 | Cornwall | Wind | RCP6.0 | 2035 | 81.9303 | 88.3029 | 95.0199 | 101.7316 | 108.4298
CornwallWind2040RCP6.0 | Cornwall | Wind | RCP6.0 | 2040 | 81.9736 | 88.3437 | 95.0591 | 101.7702 | 108.4674
CornwallWind2045RCP6.0 | Cornwall | Wind | RCP6.0 | 2045 | 82.0169 | 88.3845 | 95.0982 | 101.8088 | 108.5049
CornwallWind2050RCP6.0 | Cornwall | Wind | RCP6.0 | 2050 | 82.0358 | 88.3956 | 95.1017 | 101.8031 | 108.4931
CornwallWind2055RCP6.0 | Cornwall | Wind | RCP6.0 | 2055 | 82.0115 | 88.3659 | 95.066 | 101.7588 | 108.4438
CornwallWind2060RCP6.0 | Cornwall | Wind | RCP6.0 | 2060 | 81.9871 | 88.3362 | 95.0302 | 101.7145 | 108.3945
CornwallWind2065RCP6.0 | Cornwall | Wind | RCP6.0 | 2065 | 81.9628 | 88.3064 | 94.9945 | 101.6703 | 108.3452
CornwallWind2070RCP6.0 | Cornwall | Wind | RCP6.0 | 2070 | 81.9384 | 88.2767 | 94.9588 | 101.626 | 108.2959
CornwallWind2075RCP6.0 | Cornwall | Wind | RCP6.0 | 2075 | 81.908 | 88.2439 | 94.9235 | 101.5908 | 108.2584
CornwallWind2080RCP6.0 | Cornwall | Wind | RCP6.0 | 2080 | 81.8776 | 88.2112 | 94.8883 | 101.5556 | 108.2209
CornwallWind2085RCP6.0 | Cornwall | Wind | RCP6.0 | 2085 | 81.8471 | 88.1784 | 94.853 | 101.5204 | 108.1834
CornwallWind2090RCP6.0 | Cornwall | Wind | RCP6.0 | 2090 | 81.7653 | 88.0844 | 94.7426 | 101.3981 | 108.0494
CornwallWind2095RCP6.0 | Cornwall | Wind | RCP6.0 | 2095 | 81.7139 | 88.0232 | 94.6674 | 101.3109 | 107.953
CornwallWind2100RCP6.0 | Cornwall | Wind | RCP6.0 | 2100 | 81.6625 | 87.962 | 94.5922 | 101.2237 | 107.8565
CornwallWind2023RCP8.5 | Cornwall | Wind | RCP8.5 | 2023 | 81.8005 | 88.1806 | 94.9024 | 101.616 | 108.3173
CornwallWind2025RCP8.5 | Cornwall | Wind | RCP8.5 | 2025 | 81.887 | 88.2621 | 94.9807 | 101.6931 | 108.3923
CornwallWind2030RCP8.5 | Cornwall | Wind | RCP8.5 | 2030 | 81.9736 | 88.3437 | 95.0591 | 101.7702 | 108.4674
CornwallWind2035RCP8.5 | Cornwall | Wind | RCP8.5 | 2035 | 82.0602 | 88.4253 | 95.1374 | 101.8473 | 108.5424
CornwallWind2040RCP8.5 | Cornwall | Wind | RCP8.5 | 2040 | 82.0196 | 88.3758 | 95.0779 | 101.7735 | 108.4602
CornwallWind2045RCP8.5 | Cornwall | Wind | RCP8.5 | 2045 | 81.979 | 88.3263 | 95.0183 | 101.6998 | 108.3781
CornwallWind2050RCP8.5 | Cornwall | Wind | RCP8.5 | 2050 | 81.8979 | 88.233 | 94.9118 | 101.5791 | 108.2459
CornwallWind2055RCP8.5 | Cornwall | Wind | RCP8.5 | 2055 | 81.8573 | 88.1893 | 94.8648 | 101.5322 | 108.1959
CornwallWind2060RCP8.5 | Cornwall | Wind | RCP8.5 | 2060 | 81.7653 | 88.0844 | 94.7426 | 101.3981 | 108.0494
CornwallWind2065RCP8.5 | Cornwall | Wind | RCP8.5 | 2065 | 81.7139 | 88.0232 | 94.6674 | 101.3109 | 107.953
CornwallWind2070RCP8.5 | Cornwall | Wind | RCP8.5 | 2070 | 81.8221 | 88.1747 | 94.8711 | 101.559 | 108.2459
CornwallWind2075RCP8.5 | Cornwall | Wind | RCP8.5 | 2075 | 81.9817 | 88.3874 | 95.1499 | 101.8942 | 108.6352
CornwallWind2080RCP8.5 | Cornwall | Wind | RCP8.5 | 2080 | 82.1414 | 88.6002 | 95.4288 | 102.2295 | 109.0246
CornwallWind2085RCP8.5 | Cornwall | Wind | RCP8.5 | 2085 | 82.0196 | 88.421 | 95.1797 | 101.9227 | 108.6549
CornwallWind2090RCP8.5 | Cornwall | Wind | RCP8.5 | 2090 | 81.8979 | 88.2417 | 94.9306 | 101.616 | 108.2852
CornwallWind2095RCP8.5 | Cornwall | Wind | RCP8.5 | 2095 | 81.8979 | 88.2417 | 94.9306 | 101.616 | 108.2852
CornwallWind2100RCP8.5 | Cornwall | Wind | RCP8.5 | 2100 | 81.8979 | 88.2417 | 94.9306 | 101.616 | 108.2852
CorunnaIce Accretion2023RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2023 | 14.5432 | 17.4931 | 21.208 | 24.0396 | 26.8607
CorunnaIce Accretion2025RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2025 | 14.5917 | 17.56 | 21.3033 | 24.1515 | 26.9947
CorunnaIce Accretion2030RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2030 | 14.6401 | 17.627 | 21.3987 | 24.2634 | 27.1286
CorunnaIce Accretion2035RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2035 | 14.6886 | 17.6939 | 21.494 | 24.3752 | 27.2626
CorunnaIce Accretion2040RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2040 | 14.7371 | 17.7609 | 21.5893 | 24.4871 | 27.3966
CorunnaIce Accretion2045RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2045 | 14.7856 | 17.8278 | 21.6847 | 24.599 | 27.5306
CorunnaIce Accretion2050RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2050 | 14.6167 | 17.6647 | 21.5248 | 24.4374 | 27.3707
CorunnaIce Accretion2055RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2055 | 14.3993 | 17.4346 | 21.2696 | 24.1639 | 27.0769
CorunnaIce Accretion2060RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2060 | 14.1819 | 17.2046 | 21.0144 | 23.8905 | 26.7831
CorunnaIce Accretion2065RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2065 | 13.9645 | 16.9745 | 20.7592 | 23.617 | 26.4892
CorunnaIce Accretion2070RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2070 | 13.7471 | 16.7444 | 20.504 | 23.3435 | 26.1954
CorunnaIce Accretion2075RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2075 | 13.5047 | 16.4675 | 20.1813 | 22.9914 | 25.8073
CorunnaIce Accretion2080RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2080 | 13.2624 | 16.1905 | 19.8587 | 22.6392 | 25.4192
CorunnaIce Accretion2085RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2085 | 13.02 | 15.9136 | 19.536 | 22.287 | 25.0312
CorunnaIce Accretion2090RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2090 | 12.7776 | 15.6366 | 19.2133 | 21.9348 | 24.6431
CorunnaIce Accretion2095RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2095 | 12.5352 | 15.3597 | 18.8907 | 21.5826 | 24.255
CorunnaIce Accretion2100RCP4.5 | Corunna | Ice Accretion | RCP4.5 | 2100 | 12.2928 | 15.0828 | 18.568 | 21.2304 | 23.8669
CorunnaIce Accretion2023RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2023 | 14.5432 | 17.4931 | 21.208 | 24.0396 | 26.8607
CorunnaIce Accretion2025RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2025 | 14.5917 | 17.56 | 21.3033 | 24.1515 | 26.9947
CorunnaIce Accretion2030RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2030 | 14.6401 | 17.627 | 21.3987 | 24.2634 | 27.1286
CorunnaIce Accretion2035RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2035 | 14.6886 | 17.6939 | 21.494 | 24.3752 | 27.2626
CorunnaIce Accretion2040RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2040 | 14.7371 | 17.7609 | 21.5893 | 24.4871 | 27.3966
CorunnaIce Accretion2045RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2045 | 14.7856 | 17.8278 | 21.6847 | 24.599 | 27.5306
CorunnaIce Accretion2050RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2050 | 14.6167 | 17.6647 | 21.5248 | 24.4374 | 27.3707
CorunnaIce Accretion2055RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2055 | 14.3993 | 17.4346 | 21.2696 | 24.1639 | 27.0769
CorunnaIce Accretion2060RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2060 | 14.1819 | 17.2046 | 21.0144 | 23.8905 | 26.7831
CorunnaIce Accretion2065RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2065 | 13.9645 | 16.9745 | 20.7592 | 23.617 | 26.4892
CorunnaIce Accretion2070RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2070 | 13.7471 | 16.7444 | 20.504 | 23.3435 | 26.1954
CorunnaIce Accretion2075RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2075 | 13.3836 | 16.329 | 20.02 | 22.8153 | 25.6133
CorunnaIce Accretion2080RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2080 | 13.02 | 15.9136 | 19.536 | 22.287 | 25.0312
CorunnaIce Accretion2085RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2085 | 12.6564 | 15.4982 | 19.052 | 21.7587 | 24.449
CorunnaIce Accretion2090RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2090 | 11.7774 | 14.4802 | 17.864 | 20.4349 | 22.9891
CorunnaIce Accretion2095RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2095 | 11.262 | 13.8776 | 17.16 | 19.6394 | 22.1113
CorunnaIce Accretion2100RCP6.0 | Corunna | Ice Accretion | RCP6.0 | 2100 | 10.7466 | 13.275 | 16.456 | 18.8439 | 21.2335
CorunnaIce Accretion2023RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2023 | 14.5432 | 17.4931 | 21.208 | 24.0396 | 26.8607
CorunnaIce Accretion2025RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2025 | 14.6401 | 17.627 | 21.3987 | 24.2634 | 27.1286
CorunnaIce Accretion2030RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2030 | 14.7371 | 17.7609 | 21.5893 | 24.4871 | 27.3966
CorunnaIce Accretion2035RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2035 | 14.834 | 17.8948 | 21.78 | 24.7108 | 27.6646
CorunnaIce Accretion2040RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2040 | 14.4717 | 17.5113 | 21.3547 | 24.2551 | 27.1748
CorunnaIce Accretion2045RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2045 | 14.1094 | 17.1279 | 20.9293 | 23.7993 | 26.6851
CorunnaIce Accretion2050RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2050 | 13.2624 | 16.1905 | 19.8587 | 22.6392 | 25.4192
CorunnaIce Accretion2055RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2055 | 12.7776 | 15.6366 | 19.2133 | 21.9348 | 24.6431
CorunnaIce Accretion2060RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2060 | 11.7774 | 14.4802 | 17.864 | 20.4349 | 22.9891
CorunnaIce Accretion2065RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2065 | 11.262 | 13.8776 | 17.16 | 19.6394 | 22.1113
CorunnaIce Accretion2070RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2070 | 10.3231 | 12.7942 | 15.8987 | 18.2307 | 20.559
CorunnaIce Accretion2075RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2075 | 9.8996 | 12.3133 | 15.3413 | 17.6175 | 19.8845
CorunnaIce Accretion2080RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2080 | 9.476 | 11.8325 | 14.784 | 17.0042 | 19.21
CorunnaIce Accretion2085RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2085 | 8.6647 | 10.8647 | 13.596 | 15.6618 | 17.7131
CorunnaIce Accretion2090RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2090 | 7.8533 | 9.8969 | 12.408 | 14.3194 | 16.2162
CorunnaIce Accretion2095RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2095 | 7.8533 | 9.8969 | 12.408 | 14.3194 | 16.2162
CorunnaIce Accretion2100RCP8.5 | Corunna | Ice Accretion | RCP8.5 | 2100 | 7.8533 | 9.8969 | 12.408 | 14.3194 | 16.2162
CorunnaWind2023RCP4.5 | Corunna | Wind | RCP4.5 | 2023 | 85.0444 | 91.6139 | 98.5292 | 105.4367 | 112.3456
CorunnaWind2025RCP4.5 | Corunna | Wind | RCP4.5 | 2025 | 85.105 | 91.6838 | 98.6109 | 105.5311 | 112.4499
CorunnaWind2030RCP4.5 | Corunna | Wind | RCP4.5 | 2030 | 85.1657 | 91.7537 | 98.6925 | 105.6255 | 112.5542
CorunnaWind2035RCP4.5 | Corunna | Wind | RCP4.5 | 2035 | 85.2263 | 91.8236 | 98.7742 | 105.7199 | 112.6584
CorunnaWind2040RCP4.5 | Corunna | Wind | RCP4.5 | 2040 | 85.287 | 91.8934 | 98.8559 | 105.8142 | 112.7627
CorunnaWind2045RCP4.5 | Corunna | Wind | RCP4.5 | 2045 | 85.3476 | 91.9633 | 98.9375 | 105.9086 | 112.867
CorunnaWind2050RCP4.5 | Corunna | Wind | RCP4.5 | 2050 | 85.4083 | 92.0332 | 99.0192 | 106.0009 | 112.9713
CorunnaWind2055RCP4.5 | Corunna | Wind | RCP4.5 | 2055 | 85.4083 | 92.0332 | 99.0192 | 105.9988 | 112.9713
CorunnaWind2060RCP4.5 | Corunna | Wind | RCP4.5 | 2060 | 85.4083 | 92.0332 | 99.0192 | 105.9967 | 112.9713
CorunnaWind2065RCP4.5 | Corunna | Wind | RCP4.5 | 2065 | 85.4083 | 92.0332 | 99.0192 | 105.9946 | 112.9713
CorunnaWind2070RCP4.5 | Corunna | Wind | RCP4.5 | 2070 | 85.4083 | 92.0332 | 99.0192 | 105.9925 | 112.9713
CorunnaWind2075RCP4.5 | Corunna | Wind | RCP4.5 | 2075 | 85.538 | 92.1957 | 99.2201 | 106.2284 | 113.2413
CorunnaWind2080RCP4.5 | Corunna | Wind | RCP4.5 | 2080 | 85.6678 | 92.3582 | 99.421 | 106.4644 | 113.5112
CorunnaWind2085RCP4.5 | Corunna | Wind | RCP4.5 | 2085 | 85.7975 | 92.5208 | 99.6219 | 106.7003 | 113.7812
CorunnaWind2090RCP4.5 | Corunna | Wind | RCP4.5 | 2090 | 85.9273 | 92.6833 | 99.8228 | 106.9362 | 114.0512
CorunnaWind2095RCP4.5 | Corunna | Wind | RCP4.5 | 2095 | 86.057 | 92.8458 | 100.0237 | 107.1722 | 114.3212
CorunnaWind2100RCP4.5 | Corunna | Wind | RCP4.5 | 2100 | 86.1868 | 93.0084 | 100.2246 | 107.4081 | 114.5912
CorunnaWind2023RCP6.0 | Corunna | Wind | RCP6.0 | 2023 | 85.0444 | 91.6139 | 98.5292 | 105.4367 | 112.3456
CorunnaWind2025RCP6.0 | Corunna | Wind | RCP6.0 | 2025 | 85.105 | 91.6838 | 98.6109 | 105.5311 | 112.4499
CorunnaWind2030RCP6.0 | Corunna | Wind | RCP6.0 | 2030 | 85.1657 | 91.7537 | 98.6925 | 105.6255 | 112.5542
CorunnaWind2035RCP6.0 | Corunna | Wind | RCP6.0 | 2035 | 85.2263 | 91.8236 | 98.7742 | 105.7199 | 112.6584
CorunnaWind2040RCP6.0 | Corunna | Wind | RCP6.0 | 2040 | 85.287 | 91.8934 | 98.8559 | 105.8142 | 112.7627
CorunnaWind2045RCP6.0 | Corunna | Wind | RCP6.0 | 2045 | 85.3476 | 91.9633 | 98.9375 | 105.9086 | 112.867
CorunnaWind2050RCP6.0 | Corunna | Wind | RCP6.0 | 2050 | 85.4083 | 92.0332 | 99.0192 | 106.0009 | 112.9713
CorunnaWind2055RCP6.0 | Corunna | Wind | RCP6.0 | 2055 | 85.4083 | 92.0332 | 99.0192 | 105.9988 | 112.9713
CorunnaWind2060RCP6.0 | Corunna | Wind | RCP6.0 | 2060 | 85.4083 | 92.0332 | 99.0192 | 105.9967 | 112.9713
CorunnaWind2065RCP6.0 | Corunna | Wind | RCP6.0 | 2065 | 85.4083 | 92.0332 | 99.0192 | 105.9946 | 112.9713
CorunnaWind2070RCP6.0 | Corunna | Wind | RCP6.0 | 2070 | 85.4083 | 92.0332 | 99.0192 | 105.9925 | 112.9713
CorunnaWind2075RCP6.0 | Corunna | Wind | RCP6.0 | 2075 | 85.6029 | 92.277 | 99.3205 | 106.3464 | 113.3762
CorunnaWind2080RCP6.0 | Corunna | Wind | RCP6.0 | 2080 | 85.7975 | 92.5208 | 99.6219 | 106.7003 | 113.7812
CorunnaWind2085RCP6.0 | Corunna | Wind | RCP6.0 | 2085 | 85.9921 | 92.7646 | 99.9232 | 107.0542 | 114.1862
CorunnaWind2090RCP6.0 | Corunna | Wind | RCP6.0 | 2090 | 86.4463 | 93.3304 | 100.6264 | 107.8765 | 115.1275
CorunnaWind2095RCP6.0 | Corunna | Wind | RCP6.0 | 2095 | 86.7058 | 93.6524 | 101.0282 | 108.3448 | 115.6637
CorunnaWind2100RCP6.0 | Corunna | Wind | RCP6.0 | 2100 | 86.9653 | 93.9745 | 101.43 | 108.8132 | 116.2
CorunnaWind2023RCP8.5 | Corunna | Wind | RCP8.5 | 2023 | 85.0444 | 91.6139 | 98.5292 | 105.4367 | 112.3456
CorunnaWind2025RCP8.5 | Corunna | Wind | RCP8.5 | 2025 | 85.1657 | 91.7537 | 98.6925 | 105.6255 | 112.5542
CorunnaWind2030RCP8.5 | Corunna | Wind | RCP8.5 | 2030 | 85.287 | 91.8934 | 98.8559 | 105.8142 | 112.7627
CorunnaWind2035RCP8.5 | Corunna | Wind | RCP8.5 | 2035 | 85.4083 | 92.0332 | 99.0192 | 106.003 | 112.9713
CorunnaWind2040RCP8.5 | Corunna | Wind | RCP8.5 | 2040 | 85.4083 | 92.0332 | 99.0192 | 105.9995 | 112.9713
CorunnaWind2045RCP8.5 | Corunna | Wind | RCP8.5 | 2045 | 85.4083 | 92.0332 | 99.0192 | 105.996 | 112.9713
CorunnaWind2050RCP8.5 | Corunna | Wind | RCP8.5 | 2050 | 85.6678 | 92.3582 | 99.421 | 106.4644 | 113.5112
CorunnaWind2055RCP8.5 | Corunna | Wind | RCP8.5 | 2055 | 85.9273 | 92.6833 | 99.8228 | 106.9362 | 114.0512
CorunnaWind2060RCP8.5 | Corunna | Wind | RCP8.5 | 2060 | 86.4463 | 93.3304 | 100.6264 | 107.8765 | 115.1275
CorunnaWind2065RCP8.5 | Corunna | Wind | RCP8.5 | 2065 | 86.7058 | 93.6524 | 101.0282 | 108.3448 | 115.6637
CorunnaWind2070RCP8.5 | Corunna | Wind | RCP8.5 | 2070 | 87.2474 | 94.3238 | 101.8612 | 109.3131 | 116.7697
CorunnaWind2075RCP8.5 | Corunna | Wind | RCP8.5 | 2075 | 87.5294 | 94.6732 | 102.2924 | 109.8129 | 117.3395
CorunnaWind2080RCP8.5 | Corunna | Wind | RCP8.5 | 2080 | 87.8115 | 95.0226 | 102.7236 | 110.3127 | 117.9093
CorunnaWind2085RCP8.5 | Corunna | Wind | RCP8.5 | 2085 | 87.968 | 95.2367 | 103.0176 | 110.6692 | 118.3394
CorunnaWind2090RCP8.5 | Corunna | Wind | RCP8.5 | 2090 | 88.1246 | 95.4509 | 103.3116 | 111.0258 | 118.7695
CorunnaWind2095RCP8.5 | Corunna | Wind | RCP8.5 | 2095 | 88.1246 | 95.4509 | 103.3116 | 111.0258 | 118.7695
CorunnaWind2100RCP8.5 | Corunna | Wind | RCP8.5 | 2100 | 88.1246 | 95.4509 | 103.3116 | 111.0258 | 118.7695
Deep RiverIce Accretion2023RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2023 | 13.0012 | 15.5525 | 18.792 | 21.2756 | 23.746
Deep RiverIce Accretion2025RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2025 | 13.0513 | 15.6123 | 18.861 | 21.3502 | 23.8291
Deep RiverIce Accretion2030RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2030 | 13.1014 | 15.6721 | 18.93 | 21.4248 | 23.9123
Deep RiverIce Accretion2035RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2035 | 13.1515 | 15.7318 | 18.999 | 21.4994 | 23.9954
Deep RiverIce Accretion2040RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2040 | 13.2016 | 15.7916 | 19.068 | 21.574 | 24.0786
Deep RiverIce Accretion2045RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2045 | 13.2517 | 15.8513 | 19.137 | 21.6485 | 24.1618
Deep RiverIce Accretion2050RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2050 | 13.2993 | 15.9171 | 19.2276 | 21.7557 | 24.2903
Deep RiverIce Accretion2055RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2055 | 13.2968 | 15.9231 | 19.2492 | 21.7882 | 24.3356
Deep RiverIce Accretion2060RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2060 | 13.2943 | 15.929 | 19.2708 | 21.8208 | 24.381
Deep RiverIce Accretion2065RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2065 | 13.2918 | 15.935 | 19.2924 | 21.8533 | 24.4264
Deep RiverIce Accretion2070RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2070 | 13.2893 | 15.941 | 19.314 | 21.8858 | 24.4717
Deep RiverIce Accretion2075RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2075 | 13.2747 | 15.931 | 19.311 | 21.8858 | 24.4717
Deep RiverIce Accretion2080RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2080 | 13.26 | 15.9211 | 19.308 | 21.8858 | 24.4717
Deep RiverIce Accretion2085RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2085 | 13.2454 | 15.9111 | 19.305 | 21.8858 | 24.4717
Deep RiverIce Accretion2090RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2090 | 13.2308 | 15.9011 | 19.302 | 21.8858 | 24.4717
Deep RiverIce Accretion2095RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2095 | 13.2162 | 15.8912 | 19.299 | 21.8858 | 24.4717
Deep RiverIce Accretion2100RCP4.5 | Deep River | Ice Accretion | RCP4.5 | 2100 | 13.2016 | 15.8812 | 19.296 | 21.8858 | 24.4717
Deep RiverIce Accretion2023RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2023 | 13.0012 | 15.5525 | 18.792 | 21.2756 | 23.746
Deep RiverIce Accretion2025RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2025 | 13.0513 | 15.6123 | 18.861 | 21.3502 | 23.8291
Deep RiverIce Accretion2030RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2030 | 13.1014 | 15.6721 | 18.93 | 21.4248 | 23.9123
Deep RiverIce Accretion2035RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2035 | 13.1515 | 15.7318 | 18.999 | 21.4994 | 23.9954
Deep RiverIce Accretion2040RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2040 | 13.2016 | 15.7916 | 19.068 | 21.574 | 24.0786
Deep RiverIce Accretion2045RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2045 | 13.2517 | 15.8513 | 19.137 | 21.6485 | 24.1618
Deep RiverIce Accretion2050RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2050 | 13.2993 | 15.9171 | 19.2276 | 21.7557 | 24.2903
Deep RiverIce Accretion2055RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2055 | 13.2968 | 15.9231 | 19.2492 | 21.7882 | 24.3356
Deep RiverIce Accretion2060RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2060 | 13.2943 | 15.929 | 19.2708 | 21.8208 | 24.381
Deep RiverIce Accretion2065RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2065 | 13.2918 | 15.935 | 19.2924 | 21.8533 | 24.4264
Deep RiverIce Accretion2070RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2070 | 13.2893 | 15.941 | 19.314 | 21.8858 | 24.4717
Deep RiverIce Accretion2075RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2075 | 13.2673 | 15.926 | 19.3095 | 21.8858 | 24.4717
Deep RiverIce Accretion2080RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2080 | 13.2454 | 15.9111 | 19.305 | 21.8858 | 24.4717
Deep RiverIce Accretion2085RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2085 | 13.2235 | 15.8962 | 19.3005 | 21.8858 | 24.4717
Deep RiverIce Accretion2090RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2090 | 13.2099 | 15.9211 | 19.374 | 22.0011 | 24.6229
Deep RiverIce Accretion2095RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2095 | 13.2183 | 15.9609 | 19.452 | 22.1164 | 24.7741
Deep RiverIce Accretion2100RCP6.0 | Deep River | Ice Accretion | RCP6.0 | 2100 | 13.2266 | 16.0007 | 19.53 | 22.2316 | 24.9253
Deep RiverIce Accretion2023RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2023 | 13.0012 | 15.5525 | 18.792 | 21.2756 | 23.746
Deep RiverIce Accretion2025RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2025 | 13.1014 | 15.6721 | 18.93 | 21.4248 | 23.9123
Deep RiverIce Accretion2030RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2030 | 13.2016 | 15.7916 | 19.068 | 21.574 | 24.0786
Deep RiverIce Accretion2035RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2035 | 13.3018 | 15.9111 | 19.206 | 21.7231 | 24.2449
Deep RiverIce Accretion2040RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2040 | 13.2976 | 15.9211 | 19.242 | 21.7774 | 24.3205
Deep RiverIce Accretion2045RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2045 | 13.2934 | 15.931 | 19.278 | 21.8316 | 24.3961
Deep RiverIce Accretion2050RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2050 | 13.26 | 15.9211 | 19.308 | 21.8858 | 24.4717
Deep RiverIce Accretion2055RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2055 | 13.2308 | 15.9011 | 19.302 | 21.8858 | 24.4717
Deep RiverIce Accretion2060RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2060 | 13.2099 | 15.9211 | 19.374 | 22.0011 | 24.6229
Deep RiverIce Accretion2065RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2065 | 13.2183 | 15.9609 | 19.452 | 22.1164 | 24.7741
Deep RiverIce Accretion2070RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2070 | 13.2016 | 15.9908 | 19.53 | 22.2384 | 24.9404
Deep RiverIce Accretion2075RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2075 | 13.1765 | 15.9808 | 19.53 | 22.2452 | 24.9556
Deep RiverIce Accretion2080RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2080 | 13.1515 | 15.9709 | 19.53 | 22.252 | 24.9707
Deep RiverIce Accretion2085RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2085 | 12.926 | 15.7243 | 19.26 | 21.957 | 24.6532
Deep RiverIce Accretion2090RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2090 | 12.7006 | 15.4778 | 18.99 | 21.6621 | 24.3356
Deep RiverIce Accretion2095RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2095 | 12.7006 | 15.4778 | 18.99 | 21.6621 | 24.3356
Deep RiverIce Accretion2100RCP8.5 | Deep River | Ice Accretion | RCP8.5 | 2100 | 12.7006 | 15.4778 | 18.99 | 21.6621 | 24.3356
Deep RiverWind2023RCP4.5 | Deep River | Wind | RCP4.5 | 2023 | 77.3571 | 83.2997 | 89.5429 | 95.7919 | 102.0383
Deep RiverWind2025RCP4.5 | Deep River | Wind | RCP4.5 | 2025 | 77.4173 | 83.3604 | 89.6037 | 95.8538 | 102.1026
Deep RiverWind2030RCP4.5 | Deep River | Wind | RCP4.5 | 2030 | 77.4775 | 83.4211 | 89.6645 | 95.9157 | 102.1668
Deep RiverWind2035RCP4.5 | Deep River | Wind | RCP4.5 | 2035 | 77.5377 | 83.4818 | 89.7253 | 95.9776 | 102.2311
Deep RiverWind2040RCP4.5 | Deep River | Wind | RCP4.5 | 2040 | 77.5979 | 83.5425 | 89.7862 | 96.0395 | 102.2954
Deep RiverWind2045RCP4.5 | Deep River | Wind | RCP4.5 | 2045 | 77.6581 | 83.6032 | 89.847 | 96.1014 | 102.3596
Deep RiverWind2050RCP4.5 | Deep River | Wind | RCP4.5 | 2050 | 77.7937 | 83.755 | 90.0164 | 96.289 | 102.5639
Deep RiverWind2055RCP4.5 | Deep River | Wind | RCP4.5 | 2055 | 77.869 | 83.846 | 90.125 | 96.4147 | 102.7039
Deep RiverWind2060RCP4.5 | Deep River | Wind | RCP4.5 | 2060 | 77.9443 | 83.9371 | 90.2335 | 96.5404 | 102.8439
Deep RiverWind2065RCP4.5 | Deep River | Wind | RCP4.5 | 2065 | 78.0196 | 84.0281 | 90.3421 | 96.6661 | 102.9839
Deep RiverWind2070RCP4.5 | Deep River | Wind | RCP4.5 | 2070 | 78.0949 | 84.1192 | 90.4507 | 96.7918 | 103.1239
Deep RiverWind2075RCP4.5 | Deep River | Wind | RCP4.5 | 2075 | 78.1884 | 84.2336 | 90.5916 | 96.9537 | 103.31
Deep RiverWind2080RCP4.5 | Deep River | Wind | RCP4.5 | 2080 | 78.2819 | 84.3481 | 90.7325 | 97.1156 | 103.496
Deep RiverWind2085RCP4.5 | Deep River | Wind | RCP4.5 | 2085 | 78.3754 | 84.4626 | 90.8734 | 97.2774 | 103.682
Deep RiverWind2090RCP4.5 | Deep River | Wind | RCP4.5 | 2090 | 78.4689 | 84.5771 | 91.0144 | 97.4393 | 103.868
Deep RiverWind2095RCP4.5 | Deep River | Wind | RCP4.5 | 2095 | 78.5624 | 84.6916 | 91.1553 | 97.6012 | 104.054
Deep RiverWind2100RCP4.5 | Deep River | Wind | RCP4.5 | 2100 | 78.6559 | 84.8061 | 91.2962 | 97.7631 | 104.24
Deep RiverWind2023RCP6.0 | Deep River | Wind | RCP6.0 | 2023 | 77.3571 | 83.2997 | 89.5429 | 95.7919 | 102.0383
Deep RiverWind2025RCP6.0 | Deep River | Wind | RCP6.0 | 2025 | 77.4173 | 83.3604 | 89.6037 | 95.8538 | 102.1026
Deep RiverWind2030RCP6.0 | Deep River | Wind | RCP6.0 | 2030 | 77.4775 | 83.4211 | 89.6645 | 95.9157 | 102.1668
Deep RiverWind2035RCP6.0 | Deep River | Wind | RCP6.0 | 2035 | 77.5377 | 83.4818 | 89.7253 | 95.9776 | 102.2311
Deep RiverWind2040RCP6.0 | Deep River | Wind | RCP6.0 | 2040 | 77.5979 | 83.5425 | 89.7862 | 96.0395 | 102.2954
Deep RiverWind2045RCP6.0 | Deep River | Wind | RCP6.0 | 2045 | 77.6581 | 83.6032 | 89.847 | 96.1014 | 102.3596
Deep RiverWind2050RCP6.0 | Deep River | Wind | RCP6.0 | 2050 | 77.7937 | 83.755 | 90.0164 | 96.289 | 102.5639
Deep RiverWind2055RCP6.0 | Deep River | Wind | RCP6.0 | 2055 | 77.869 | 83.846 | 90.125 | 96.4147 | 102.7039
Deep RiverWind2060RCP6.0 | Deep River | Wind | RCP6.0 | 2060 | 77.9443 | 83.9371 | 90.2335 | 96.5404 | 102.8439
Deep RiverWind2065RCP6.0 | Deep River | Wind | RCP6.0 | 2065 | 78.0196 | 84.0281 | 90.3421 | 96.6661 | 102.9839
Deep RiverWind2070RCP6.0 | Deep River | Wind | RCP6.0 | 2070 | 78.0949 | 84.1192 | 90.4507 | 96.7918 | 103.1239
Deep RiverWind2075RCP6.0 | Deep River | Wind | RCP6.0 | 2075 | 78.2352 | 84.2909 | 90.6621 | 97.0346 | 103.403
Deep RiverWind2080RCP6.0 | Deep River | Wind | RCP6.0 | 2080 | 78.3754 | 84.4626 | 90.8734 | 97.2774 | 103.682
Deep RiverWind2085RCP6.0 | Deep River | Wind | RCP6.0 | 2085 | 78.5157 | 84.6344 | 91.0848 | 97.5203 | 103.961
Deep RiverWind2090RCP6.0 | Deep River | Wind | RCP6.0 | 2090 | 78.7481 | 84.9303 | 91.4653 | 97.9663 | 104.4767
Deep RiverWind2095RCP6.0 | Deep River | Wind | RCP6.0 | 2095 | 78.8403 | 85.0545 | 91.6344 | 98.1694 | 104.7135
Deep RiverWind2100RCP6.0 | Deep River | Wind | RCP6.0 | 2100 | 78.9326 | 85.1786 | 91.8035 | 98.3726 | 104.9502
Deep RiverWind2023RCP8.5 | Deep River | Wind | RCP8.5 | 2023 | 77.3571 | 83.2997 | 89.5429 | 95.7919 | 102.0383
Deep RiverWind2025RCP8.5 | Deep River | Wind | RCP8.5 | 2025 | 77.4775 | 83.4211 | 89.6645 | 95.9157 | 102.1668
Deep RiverWind2030RCP8.5 | Deep River | Wind | RCP8.5 | 2030 | 77.5979 | 83.5425 | 89.7862 | 96.0395 | 102.2954
Deep RiverWind2035RCP8.5 | Deep River | Wind | RCP8.5 | 2035 | 77.7183 | 83.6639 | 89.9078 | 96.1633 | 102.4239
Deep RiverWind2040RCP8.5 | Deep River | Wind | RCP8.5 | 2040 | 77.8439 | 83.8157 | 90.0888 | 96.3728 | 102.6572
Deep RiverWind2045RCP8.5 | Deep River | Wind | RCP8.5 | 2045 | 77.9694 | 83.9674 | 90.2697 | 96.5823 | 102.8906
Deep RiverWind2050RCP8.5 | Deep River | Wind | RCP8.5 | 2050 | 78.2819 | 84.3481 | 90.7325 | 97.1156 | 103.496
Deep RiverWind2055RCP8.5 | Deep River | Wind | RCP8.5 | 2055 | 78.4689 | 84.5771 | 91.0144 | 97.4393 | 103.868
Deep RiverWind2060RCP8.5 | Deep River | Wind | RCP8.5 | 2060 | 78.7481 | 84.9303 | 91.4653 | 97.9663 | 104.4767
Deep RiverWind2065RCP8.5 | Deep River | Wind | RCP8.5 | 2065 | 78.8403 | 85.0545 | 91.6344 | 98.1694 | 104.7135
Deep RiverWind2070RCP8.5 | Deep River | Wind | RCP8.5 | 2070 | 78.9556 | 85.1841 | 91.7798 | 98.3313 | 104.8893
Deep RiverWind2075RCP8.5 | Deep River | Wind | RCP8.5 | 2075 | 78.9787 | 85.1896 | 91.756 | 98.2901 | 104.8285
Deep RiverWind2080RCP8.5 | Deep River | Wind | RCP8.5 | 2080 | 79.0017 | 85.1952 | 91.7323 | 98.2488 | 104.7676
Deep RiverWind2085RCP8.5 | Deep River | Wind | RCP8.5 | 2085 | 79.0517 | 85.2531 | 91.799 | 98.3202 | 104.8488
Deep RiverWind2090RCP8.5 | Deep River | Wind | RCP8.5 | 2090 | 79.1016 | 85.311 | 91.8658 | 98.3916 | 104.9299
Deep RiverWind2095RCP8.5 | Deep River | Wind | RCP8.5 | 2095 | 79.1016 | 85.311 | 91.8658 | 98.3916 | 104.9299
Deep RiverWind2100RCP8.5 | Deep River | Wind | RCP8.5 | 2100 | 79.1016 | 85.311 | 91.8658 | 98.3916 | 104.9299
DeserontoIce Accretion2023RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3347 | 31.5945
DeserontoIce Accretion2025RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2025 | 17.5121 | 20.8745 | 25.1292 | 28.4007 | 31.668
DeserontoIce Accretion2030RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2030 | 17.5411 | 20.916 | 25.1833 | 28.4666 | 31.7415
DeserontoIce Accretion2035RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2035 | 17.5701 | 20.9575 | 25.2375 | 28.5325 | 31.815
DeserontoIce Accretion2040RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2040 | 17.5991 | 20.999 | 25.2917 | 28.5984 | 31.8885
DeserontoIce Accretion2045RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2045 | 17.6281 | 21.0405 | 25.3458 | 28.6643 | 31.962
DeserontoIce Accretion2050RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2050 | 17.584 | 21.0073 | 25.325 | 28.6511 | 31.9536
DeserontoIce Accretion2055RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2055 | 17.511 | 20.9326 | 25.25 | 28.572 | 31.8717
DeserontoIce Accretion2060RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2060 | 17.4379 | 20.8579 | 25.175 | 28.4929 | 31.7898
DeserontoIce Accretion2065RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2065 | 17.3648 | 20.7832 | 25.1 | 28.4138 | 31.7079
DeserontoIce Accretion2070RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2070 | 17.2918 | 20.7085 | 25.025 | 28.3347 | 31.626
DeserontoIce Accretion2075RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2075 | 17.3266 | 20.7777 | 25.1375 | 28.476 | 31.7993
DeserontoIce Accretion2080RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2080 | 17.3614 | 20.8468 | 25.25 | 28.6172 | 31.9725
DeserontoIce Accretion2085RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2085 | 17.3962 | 20.916 | 25.3625 | 28.7585 | 32.1457
DeserontoIce Accretion2090RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2090 | 17.4309 | 20.9852 | 25.475 | 28.8997 | 32.319
DeserontoIce Accretion2095RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2095 | 17.4657 | 21.0543 | 25.5875 | 29.041 | 32.4922
DeserontoIce Accretion2100RCP4.5 | Deseronto | Ice Accretion | RCP4.5 | 2100 | 17.5005 | 21.1235 | 25.7 | 29.1822 | 32.6655
DeserontoIce Accretion2023RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3347 | 31.5945
DeserontoIce Accretion2025RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2025 | 17.5121 | 20.8745 | 25.1292 | 28.4007 | 31.668
DeserontoIce Accretion2030RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2030 | 17.5411 | 20.916 | 25.1833 | 28.4666 | 31.7415
DeserontoIce Accretion2035RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2035 | 17.5701 | 20.9575 | 25.2375 | 28.5325 | 31.815
DeserontoIce Accretion2040RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2040 | 17.5991 | 20.999 | 25.2917 | 28.5984 | 31.8885
DeserontoIce Accretion2045RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2045 | 17.6281 | 21.0405 | 25.3458 | 28.6643 | 31.962
DeserontoIce Accretion2050RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2050 | 17.584 | 21.0073 | 25.325 | 28.6511 | 31.9536
DeserontoIce Accretion2055RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2055 | 17.511 | 20.9326 | 25.25 | 28.572 | 31.8717
DeserontoIce Accretion2060RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2060 | 17.4379 | 20.8579 | 25.175 | 28.4929 | 31.7898
DeserontoIce Accretion2065RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2065 | 17.3648 | 20.7832 | 25.1 | 28.4138 | 31.7079
DeserontoIce Accretion2070RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2070 | 17.2918 | 20.7085 | 25.025 | 28.3347 | 31.626
DeserontoIce Accretion2075RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2075 | 17.344 | 20.8122 | 25.1937 | 28.5466 | 31.8859
DeserontoIce Accretion2080RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2080 | 17.3962 | 20.916 | 25.3625 | 28.7585 | 32.1457
DeserontoIce Accretion2085RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2085 | 17.4483 | 21.0198 | 25.5312 | 28.9704 | 32.4056
DeserontoIce Accretion2090RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2090 | 17.315 | 20.9367 | 25.5083 | 28.9845 | 32.466
DeserontoIce Accretion2095RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2095 | 17.1294 | 20.75 | 25.3167 | 28.7867 | 32.2665
DeserontoIce Accretion2100RCP6.0 | Deseronto | Ice Accretion | RCP6.0 | 2100 | 16.9439 | 20.5633 | 25.125 | 28.589 | 32.067
DeserontoIce Accretion2023RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3347 | 31.5945
DeserontoIce Accretion2025RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2025 | 17.5411 | 20.916 | 25.1833 | 28.4666 | 31.7415
DeserontoIce Accretion2030RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2030 | 17.5991 | 20.999 | 25.2917 | 28.5984 | 31.8885
DeserontoIce Accretion2035RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2035 | 17.6571 | 21.082 | 25.4 | 28.7302 | 32.0355
DeserontoIce Accretion2040RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2040 | 17.5353 | 20.9575 | 25.275 | 28.5984 | 31.899
DeserontoIce Accretion2045RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2045 | 17.4135 | 20.833 | 25.15 | 28.4666 | 31.7625
DeserontoIce Accretion2050RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2050 | 17.3614 | 20.8468 | 25.25 | 28.6172 | 31.9725
DeserontoIce Accretion2055RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2055 | 17.4309 | 20.9852 | 25.475 | 28.8997 | 32.319
DeserontoIce Accretion2060RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2060 | 17.315 | 20.9367 | 25.5083 | 28.9845 | 32.466
DeserontoIce Accretion2065RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2065 | 17.1294 | 20.75 | 25.3167 | 28.7867 | 32.2665
DeserontoIce Accretion2070RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2070 | 16.6133 | 20.1898 | 24.6917 | 28.1182 | 31.542
DeserontoIce Accretion2075RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2075 | 16.2828 | 19.8163 | 24.2583 | 27.6473 | 31.017
DeserontoIce Accretion2080RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2080 | 15.9523 | 19.4428 | 23.825 | 27.1765 | 30.492
DeserontoIce Accretion2085RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2085 | 15.2825 | 18.6542 | 22.8875 | 26.1171 | 29.3265
DeserontoIce Accretion2090RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2090 | 14.6128 | 17.8657 | 21.95 | 25.0577 | 28.161
DeserontoIce Accretion2095RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2095 | 14.6128 | 17.8657 | 21.95 | 25.0577 | 28.161
DeserontoIce Accretion2100RCP8.5 | Deseronto | Ice Accretion | RCP8.5 | 2100 | 14.6128 | 17.8657 | 21.95 | 25.0577 | 28.161
DeserontoWind2023RCP4.5 | Deseronto | Wind | RCP4.5 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.3568
DeserontoWind2025RCP4.5 | Deseronto | Wind | RCP4.5 | 2025 | 85.0176 | 91.5972 | 98.5341 | 105.4647 | 112.3885
DeserontoWind2030RCP4.5 | Deseronto | Wind | RCP4.5 | 2030 | 85.0331 | 91.617 | 98.5586 | 105.4927 | 112.4201
DeserontoWind2035RCP4.5 | Deseronto | Wind | RCP4.5 | 2035 | 85.0486 | 91.6367 | 98.5831 | 105.5206 | 112.4518
DeserontoWind2040RCP4.5 | Deseronto | Wind | RCP4.5 | 2040 | 85.0641 | 91.6565 | 98.6076 | 105.5486 | 112.4834
DeserontoWind2045RCP4.5 | Deseronto | Wind | RCP4.5 | 2045 | 85.0796 | 91.6762 | 98.6321 | 105.5765 | 112.5151
DeserontoWind2050RCP4.5 | Deseronto | Wind | RCP4.5 | 2050 | 85.1747 | 91.7944 | 98.7781 | 105.745 | 112.7076
DeserontoWind2055RCP4.5 | Deseronto | Wind | RCP4.5 | 2055 | 85.2542 | 91.8928 | 98.8996 | 105.8855 | 112.8685
DeserontoWind2060RCP4.5 | Deseronto | Wind | RCP4.5 | 2060 | 85.3338 | 91.9912 | 99.0212 | 106.026 | 113.0294
DeserontoWind2065RCP4.5 | Deseronto | Wind | RCP4.5 | 2065 | 85.4133 | 92.0897 | 99.1427 | 106.1666 | 113.1902
DeserontoWind2070RCP4.5 | Deseronto | Wind | RCP4.5 | 2070 | 85.4929 | 92.1881 | 99.2642 | 106.3071 | 113.3511
DeserontoWind2075RCP4.5 | Deseronto | Wind | RCP4.5 | 2075 | 85.5549 | 92.2671 | 99.3638 | 106.4259 | 113.4889
DeserontoWind2080RCP4.5 | Deseronto | Wind | RCP4.5 | 2080 | 85.617 | 92.3461 | 99.4635 | 106.5448 | 113.6267
DeserontoWind2085RCP4.5 | Deseronto | Wind | RCP4.5 | 2085 | 85.679 | 92.4251 | 99.5631 | 106.6636 | 113.7645
DeserontoWind2090RCP4.5 | Deseronto | Wind | RCP4.5 | 2090 | 85.7411 | 92.5041 | 99.6627 | 106.7824 | 113.9023
DeserontoWind2095RCP4.5 | Deseronto | Wind | RCP4.5 | 2095 | 85.8032 | 92.5831 | 99.7624 | 106.9013 | 114.0401
DeserontoWind2100RCP4.5 | Deseronto | Wind | RCP4.5 | 2100 | 85.8652 | 92.662 | 99.862 | 107.0201 | 114.1778
DeserontoWind2023RCP6.0 | Deseronto | Wind | RCP6.0 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.3568
DeserontoWind2025RCP6.0 | Deseronto | Wind | RCP6.0 | 2025 | 85.0176 | 91.5972 | 98.5341 | 105.4647 | 112.3885
DeserontoWind2030RCP6.0 | Deseronto | Wind | RCP6.0 | 2030 | 85.0331 | 91.617 | 98.5586 | 105.4927 | 112.4201
DeserontoWind2035RCP6.0 | Deseronto | Wind | RCP6.0 | 2035 | 85.0486 | 91.6367 | 98.5831 | 105.5206 | 112.4518
DeserontoWind2040RCP6.0 | Deseronto | Wind | RCP6.0 | 2040 | 85.0641 | 91.6565 | 98.6076 | 105.5486 | 112.4834
DeserontoWind2045RCP6.0 | Deseronto | Wind | RCP6.0 | 2045 | 85.0796 | 91.6762 | 98.6321 | 105.5765 | 112.5151
DeserontoWind2050RCP6.0 | Deseronto | Wind | RCP6.0 | 2050 | 85.1747 | 91.7944 | 98.7781 | 105.745 | 112.7076
DeserontoWind2055RCP6.0 | Deseronto | Wind | RCP6.0 | 2055 | 85.2542 | 91.8928 | 98.8996 | 105.8855 | 112.8685
DeserontoWind2060RCP6.0 | Deseronto | Wind | RCP6.0 | 2060 | 85.3338 | 91.9912 | 99.0212 | 106.026 | 113.0294
DeserontoWind2065RCP6.0 | Deseronto | Wind | RCP6.0 | 2065 | 85.4133 | 92.0897 | 99.1427 | 106.1666 | 113.1902
DeserontoWind2070RCP6.0 | Deseronto | Wind | RCP6.0 | 2070 | 85.4929 | 92.1881 | 99.2642 | 106.3071 | 113.3511
DeserontoWind2075RCP6.0 | Deseronto | Wind | RCP6.0 | 2075 | 85.586 | 92.3066 | 99.4136 | 106.4853 | 113.5578
DeserontoWind2080RCP6.0 | Deseronto | Wind | RCP6.0 | 2080 | 85.679 | 92.4251 | 99.5631 | 106.6636 | 113.7645
DeserontoWind2085RCP6.0 | Deseronto | Wind | RCP6.0 | 2085 | 85.7721 | 92.5436 | 99.7125 | 106.8419 | 113.9712
DeserontoWind2090RCP6.0 | Deseronto | Wind | RCP6.0 | 2090 | 86.0091 | 92.817 | 100.0253 | 107.1914 | 114.3603
DeserontoWind2095RCP6.0 | Deseronto | Wind | RCP6.0 | 2095 | 86.1529 | 92.9719 | 100.1887 | 107.3627 | 114.5428
DeserontoWind2100RCP6.0 | Deseronto | Wind | RCP6.0 | 2100 | 86.2968 | 93.1269 | 100.352 | 107.5339 | 114.7253
DeserontoWind2023RCP8.5 | Deseronto | Wind | RCP8.5 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.3568
DeserontoWind2025RCP8.5 | Deseronto | Wind | RCP8.5 | 2025 | 85.0331 | 91.617 | 98.5586 | 105.4927 | 112.4201
DeserontoWind2030RCP8.5 | Deseronto | Wind | RCP8.5 | 2030 | 85.0641 | 91.6565 | 98.6076 | 105.5486 | 112.4834
DeserontoWind2035RCP8.5 | Deseronto | Wind | RCP8.5 | 2035 | 85.0952 | 91.696 | 98.6566 | 105.6045 | 112.5467
DeserontoWind2040RCP8.5 | Deseronto | Wind | RCP8.5 | 2040 | 85.2277 | 91.86 | 98.8591 | 105.8387 | 112.8149
DeserontoWind2045RCP8.5 | Deseronto | Wind | RCP8.5 | 2045 | 85.3603 | 92.0241 | 99.0617 | 106.0729 | 113.083
DeserontoWind2050RCP8.5 | Deseronto | Wind | RCP8.5 | 2050 | 85.617 | 92.3461 | 99.4635 | 106.5448 | 113.6267
DeserontoWind2055RCP8.5 | Deseronto | Wind | RCP8.5 | 2055 | 85.7411 | 92.5041 | 99.6627 | 106.7824 | 113.9023
DeserontoWind2060RCP8.5 | Deseronto | Wind | RCP8.5 | 2060 | 86.0091 | 92.817 | 100.0253 | 107.1914 | 114.3603
DeserontoWind2065RCP8.5 | Deseronto | Wind | RCP8.5 | 2065 | 86.1529 | 92.9719 | 100.1887 | 107.3627 | 114.5428
DeserontoWind2070RCP8.5 | Deseronto | Wind | RCP8.5 | 2070 | 86.3081 | 93.142 | 100.3749 | 107.5619 | 114.7588
DeserontoWind2075RCP8.5 | Deseronto | Wind | RCP8.5 | 2075 | 86.3193 | 93.1572 | 100.3977 | 107.5899 | 114.7923
DeserontoWind2080RCP8.5 | Deseronto | Wind | RCP8.5 | 2080 | 86.3306 | 93.1724 | 100.4206 | 107.6178 | 114.8258
DeserontoWind2085RCP8.5 | Deseronto | Wind | RCP8.5 | 2085 | 86.4279 | 93.3091 | 100.6117 | 107.8538 | 115.1051
DeserontoWind2090RCP8.5 | Deseronto | Wind | RCP8.5 | 2090 | 86.5253 | 93.4458 | 100.8028 | 108.0897 | 115.3844
DeserontoWind2095RCP8.5 | Deseronto | Wind | RCP8.5 | 2095 | 86.5253 | 93.4458 | 100.8028 | 108.0897 | 115.3844
DeserontoWind2100RCP8.5 | Deseronto | Wind | RCP8.5 | 2100 | 86.5253 | 93.4458 | 100.8028 | 108.0897 | 115.3844
DorchesterIce Accretion2023RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2023 | 21.9553 | 26.3475 | 31.904 | 36.1238 | 40.3603
DorchesterIce Accretion2025RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2025 | 21.8254 | 26.2059 | 31.7493 | 35.9611 | 40.1856
DorchesterIce Accretion2030RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2030 | 21.6956 | 26.0642 | 31.5947 | 35.7984 | 40.0109
DorchesterIce Accretion2035RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2035 | 21.5657 | 25.9226 | 31.44 | 35.6357 | 39.8362
DorchesterIce Accretion2040RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2040 | 21.4358 | 25.7809 | 31.2853 | 35.473 | 39.6614
DorchesterIce Accretion2045RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2045 | 21.3059 | 25.6393 | 31.1307 | 35.3102 | 39.4867
DorchesterIce Accretion2050RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2050 | 20.7618 | 25.0408 | 30.4576 | 34.5834 | 38.6991
DorchesterIce Accretion2055RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2055 | 20.3477 | 24.5839 | 29.9392 | 34.0193 | 38.0863
DorchesterIce Accretion2060RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2060 | 19.9335 | 24.1271 | 29.4208 | 33.4552 | 37.4734
DorchesterIce Accretion2065RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2065 | 19.5193 | 23.6703 | 28.9024 | 32.8911 | 36.8605
DorchesterIce Accretion2070RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2070 | 19.1052 | 23.2134 | 28.384 | 32.327 | 36.2477
DorchesterIce Accretion2075RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2075 | 18.9604 | 23.0674 | 28.2347 | 32.1703 | 36.0864
DorchesterIce Accretion2080RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2080 | 18.8157 | 22.9213 | 28.0853 | 32.0137 | 35.9251
DorchesterIce Accretion2085RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2085 | 18.6709 | 22.7752 | 27.936 | 31.857 | 35.7638
DorchesterIce Accretion2090RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2090 | 18.5262 | 22.6291 | 27.7867 | 31.7003 | 35.6026
DorchesterIce Accretion2095RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2095 | 18.3815 | 22.483 | 27.6373 | 31.5436 | 35.4413
DorchesterIce Accretion2100RCP4.5 | Dorchester | Ice Accretion | RCP4.5 | 2100 | 18.2367 | 22.337 | 27.488 | 31.3869 | 35.28
DorchesterIce Accretion2023RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2023 | 21.9553 | 26.3475 | 31.904 | 36.1238 | 40.3603
DorchesterIce Accretion2025RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2025 | 21.8254 | 26.2059 | 31.7493 | 35.9611 | 40.1856
DorchesterIce Accretion2030RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2030 | 21.6956 | 26.0642 | 31.5947 | 35.7984 | 40.0109
DorchesterIce Accretion2035RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2035 | 21.5657 | 25.9226 | 31.44 | 35.6357 | 39.8362
DorchesterIce Accretion2040RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2040 | 21.4358 | 25.7809 | 31.2853 | 35.473 | 39.6614
DorchesterIce Accretion2045RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2045 | 21.3059 | 25.6393 | 31.1307 | 35.3102 | 39.4867
DorchesterIce Accretion2050RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2050 | 20.7618 | 25.0408 | 30.4576 | 34.5834 | 38.6991
DorchesterIce Accretion2055RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2055 | 20.3477 | 24.5839 | 29.9392 | 34.0193 | 38.0863
DorchesterIce Accretion2060RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2060 | 19.9335 | 24.1271 | 29.4208 | 33.4552 | 37.4734
DorchesterIce Accretion2065RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2065 | 19.5193 | 23.6703 | 28.9024 | 32.8911 | 36.8605
DorchesterIce Accretion2070RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2070 | 19.1052 | 23.2134 | 28.384 | 32.327 | 36.2477
DorchesterIce Accretion2075RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2075 | 18.888 | 22.9943 | 28.16 | 32.092 | 36.0058
DorchesterIce Accretion2080RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2080 | 18.6709 | 22.7752 | 27.936 | 31.857 | 35.7638
DorchesterIce Accretion2085RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2085 | 18.4538 | 22.5561 | 27.712 | 31.6219 | 35.5219
DorchesterIce Accretion2090RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2090 | 17.7172 | 21.7526 | 26.8267 | 30.6637 | 34.487
DorchesterIce Accretion2095RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2095 | 17.1976 | 21.1683 | 26.1653 | 29.9405 | 33.6941
DorchesterIce Accretion2100RCP6.0 | Dorchester | Ice Accretion | RCP6.0 | 2100 | 16.678 | 20.584 | 25.504 | 29.2173 | 32.9011
DorchesterIce Accretion2023RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2023 | 21.9553 | 26.3475 | 31.904 | 36.1238 | 40.3603
DorchesterIce Accretion2025RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2025 | 21.6956 | 26.0642 | 31.5947 | 35.7984 | 40.0109
DorchesterIce Accretion2030RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2030 | 21.4358 | 25.7809 | 31.2853 | 35.473 | 39.6614
DorchesterIce Accretion2035RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2035 | 21.176 | 25.4976 | 30.976 | 35.1475 | 39.312
DorchesterIce Accretion2040RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2040 | 20.4857 | 24.7362 | 30.112 | 34.2074 | 38.2906
DorchesterIce Accretion2045RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2045 | 19.7954 | 23.9748 | 29.248 | 33.2672 | 37.2691
DorchesterIce Accretion2050RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2050 | 18.8157 | 22.9213 | 28.0853 | 32.0137 | 35.9251
DorchesterIce Accretion2055RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2055 | 18.5262 | 22.6291 | 27.7867 | 31.7003 | 35.6026
DorchesterIce Accretion2060RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2060 | 17.7172 | 21.7526 | 26.8267 | 30.6637 | 34.487
DorchesterIce Accretion2065RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2065 | 17.1976 | 21.1683 | 26.1653 | 29.9405 | 33.6941
DorchesterIce Accretion2070RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2070 | 16.344 | 20.2299 | 25.12 | 28.7954 | 32.4576
DorchesterIce Accretion2075RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2075 | 16.01 | 19.8757 | 24.736 | 28.3735 | 32.0141
DorchesterIce Accretion2080RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2080 | 15.676 | 19.5216 | 24.352 | 27.9517 | 31.5706
DorchesterIce Accretion2085RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2085 | 14.6851 | 18.353 | 22.944 | 26.3787 | 29.8166
DorchesterIce Accretion2090RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2090 | 13.6943 | 17.1843 | 21.536 | 24.8058 | 28.0627
DorchesterIce Accretion2095RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2095 | 13.6943 | 17.1843 | 21.536 | 24.8058 | 28.0627
DorchesterIce Accretion2100RCP8.5 | Dorchester | Ice Accretion | RCP8.5 | 2100 | 13.6943 | 17.1843 | 21.536 | 24.8058 | 28.0627
DorchesterWind2023RCP4.5 | Dorchester | Wind | RCP4.5 | 2023 | 88.7974 | 95.7896 | 103.1934 | 110.5588 | 117.9312
DorchesterWind2025RCP4.5 | Dorchester | Wind | RCP4.5 | 2025 | 88.909 | 95.9382 | 103.3889 | 110.7935 | 118.2064
DorchesterWind2030RCP4.5 | Dorchester | Wind | RCP4.5 | 2030 | 89.0205 | 96.0869 | 103.5844 | 111.0281 | 118.4816
DorchesterWind2035RCP4.5 | Dorchester | Wind | RCP4.5 | 2035 | 89.1321 | 96.2355 | 103.7799 | 111.2628 | 118.7568
DorchesterWind2040RCP4.5 | Dorchester | Wind | RCP4.5 | 2040 | 89.2437 | 96.3841 | 103.9754 | 111.4974 | 119.032
DorchesterWind2045RCP4.5 | Dorchester | Wind | RCP4.5 | 2045 | 89.3552 | 96.5327 | 104.1709 | 111.7321 | 119.3072
DorchesterWind2050RCP4.5 | Dorchester | Wind | RCP4.5 | 2050 | 89.5196 | 96.7553 | 104.4684 | 112.0933 | 119.7335
DorchesterWind2055RCP4.5 | Dorchester | Wind | RCP4.5 | 2055 | 89.5725 | 96.8293 | 104.5704 | 112.2199 | 119.8847
DorchesterWind2060RCP4.5 | Dorchester | Wind | RCP4.5 | 2060 | 89.6253 | 96.9033 | 104.6724 | 112.3465 | 120.0358
DorchesterWind2065RCP4.5 | Dorchester | Wind | RCP4.5 | 2065 | 89.6782 | 96.9773 | 104.7744 | 112.4731 | 120.187
DorchesterWind2070RCP4.5 | Dorchester | Wind | RCP4.5 | 2070 | 89.731 | 97.0513 | 104.8764 | 112.5997 | 120.3382
DorchesterWind2075RCP4.5 | Dorchester | Wind | RCP4.5 | 2075 | 89.8866 | 97.2536 | 105.1382 | 112.9108 | 120.7006
DorchesterWind2080RCP4.5 | Dorchester | Wind | RCP4.5 | 2080 | 90.0422 | 97.456 | 105.4 | 113.2218 | 121.063
DorchesterWind2085RCP4.5 | Dorchester | Wind | RCP4.5 | 2085 | 90.1978 | 97.6584 | 105.6618 | 113.5329 | 121.4254
DorchesterWind2090RCP4.5 | Dorchester | Wind | RCP4.5 | 2090 | 90.3534 | 97.8607 | 105.9236 | 113.8439 | 121.7878
DorchesterWind2095RCP4.5 | Dorchester | Wind | RCP4.5 | 2095 | 90.509 | 98.0631 | 106.1854 | 114.155 | 122.1502
DorchesterWind2100RCP4.5 | Dorchester | Wind | RCP4.5 | 2100 | 90.6646 | 98.2655 | 106.4472 | 114.466 | 122.5126
DorchesterWind2023RCP6.0 | Dorchester | Wind | RCP6.0 | 2023 | 88.7974 | 95.7896 | 103.1934 | 110.5588 | 117.9312
DorchesterWind2025RCP6.0 | Dorchester | Wind | RCP6.0 | 2025 | 88.909 | 95.9382 | 103.3889 | 110.7935 | 118.2064
DorchesterWind2030RCP6.0 | Dorchester | Wind | RCP6.0 | 2030 | 89.0205 | 96.0869 | 103.5844 | 111.0281 | 118.4816
DorchesterWind2035RCP6.0 | Dorchester | Wind | RCP6.0 | 2035 | 89.1321 | 96.2355 | 103.7799 | 111.2628 | 118.7568
DorchesterWind2040RCP6.0 | Dorchester | Wind | RCP6.0 | 2040 | 89.2437 | 96.3841 | 103.9754 | 111.4974 | 119.032
DorchesterWind2045RCP6.0 | Dorchester | Wind | RCP6.0 | 2045 | 89.3552 | 96.5327 | 104.1709 | 111.7321 | 119.3072
DorchesterWind2050RCP6.0 | Dorchester | Wind | RCP6.0 | 2050 | 89.5196 | 96.7553 | 104.4684 | 112.0933 | 119.7335
DorchesterWind2055RCP6.0 | Dorchester | Wind | RCP6.0 | 2055 | 89.5725 | 96.8293 | 104.5704 | 112.2199 | 119.8847
DorchesterWind2060RCP6.0 | Dorchester | Wind | RCP6.0 | 2060 | 89.6253 | 96.9033 | 104.6724 | 112.3465 | 120.0358
DorchesterWind2065RCP6.0 | Dorchester | Wind | RCP6.0 | 2065 | 89.6782 | 96.9773 | 104.7744 | 112.4731 | 120.187
DorchesterWind2070RCP6.0 | Dorchester | Wind | RCP6.0 | 2070 | 89.731 | 97.0513 | 104.8764 | 112.5997 | 120.3382
DorchesterWind2075RCP6.0 | Dorchester | Wind | RCP6.0 | 2075 | 89.9644 | 97.3548 | 105.2691 | 113.0663 | 120.8818
DorchesterWind2080RCP6.0 | Dorchester | Wind | RCP6.0 | 2080 | 90.1978 | 97.6584 | 105.6618 | 113.5329 | 121.4254
DorchesterWind2085RCP6.0 | Dorchester | Wind | RCP6.0 | 2085 | 90.4312 | 97.9619 | 106.0545 | 113.9995 | 121.969
DorchesterWind2090RCP6.0 | Dorchester | Wind | RCP6.0 | 2090 | 91.0492 | 98.7556 | 107.0626 | 115.19 | 123.3498
DorchesterWind2095RCP6.0 | Dorchester | Wind | RCP6.0 | 2095 | 91.4338 | 99.2457 | 107.678 | 115.914 | 124.187
DorchesterWind2100RCP6.0 | Dorchester | Wind | RCP6.0 | 2100 | 91.8184 | 99.7358 | 108.2934 | 116.6379 | 125.0243
DorchesterWind2023RCP8.5 | Dorchester | Wind | RCP8.5 | 2023 | 88.7974 | 95.7896 | 103.1934 | 110.5588 | 117.9312
DorchesterWind2025RCP8.5 | Dorchester | Wind | RCP8.5 | 2025 | 89.0205 | 96.0869 | 103.5844 | 111.0281 | 118.4816
DorchesterWind2030RCP8.5 | Dorchester | Wind | RCP8.5 | 2030 | 89.2437 | 96.3841 | 103.9754 | 111.4974 | 119.032
DorchesterWind2035RCP8.5 | Dorchester | Wind | RCP8.5 | 2035 | 89.4668 | 96.6813 | 104.3664 | 111.9667 | 119.5824
DorchesterWind2040RCP8.5 | Dorchester | Wind | RCP8.5 | 2040 | 89.5549 | 96.8046 | 104.5364 | 112.1777 | 119.8343
DorchesterWind2045RCP8.5 | Dorchester | Wind | RCP8.5 | 2045 | 89.6429 | 96.9279 | 104.7064 | 112.3887 | 120.0862
DorchesterWind2050RCP8.5 | Dorchester | Wind | RCP8.5 | 2050 | 90.0422 | 97.456 | 105.4 | 113.2218 | 121.063
DorchesterWind2055RCP8.5 | Dorchester | Wind | RCP8.5 | 2055 | 90.3534 | 97.8607 | 105.9236 | 113.8439 | 121.7878
DorchesterWind2060RCP8.5 | Dorchester | Wind | RCP8.5 | 2060 | 91.0492 | 98.7556 | 107.0626 | 115.19 | 123.3498
DorchesterWind2065RCP8.5 | Dorchester | Wind | RCP8.5 | 2065 | 91.4338 | 99.2457 | 107.678 | 115.914 | 124.187
DorchesterWind2070RCP8.5 | Dorchester | Wind | RCP8.5 | 2070 | 92.0562 | 100.033 | 108.6708 | 117.0854 | 125.5398
DorchesterWind2075RCP8.5 | Dorchester | Wind | RCP8.5 | 2075 | 92.294 | 100.3303 | 109.0482 | 117.5329 | 126.0553
DorchesterWind2080RCP8.5 | Dorchester | Wind | RCP8.5 | 2080 | 92.5318 | 100.6275 | 109.4256 | 117.9803 | 126.5708
DorchesterWind2085RCP8.5 | Dorchester | Wind | RCP8.5 | 2085 | 92.937 | 101.1634 | 110.1294 | 118.8207 | 127.5592
DorchesterWind2090RCP8.5 | Dorchester | Wind | RCP8.5 | 2090 | 93.3421 | 101.6994 | 110.8332 | 119.6611 | 128.5475
DorchesterWind2095RCP8.5 | Dorchester | Wind | RCP8.5 | 2095 | 93.3421 | 101.6994 | 110.8332 | 119.6611 | 128.5475
DorchesterWind2100RCP8.5 | Dorchester | Wind | RCP8.5 | 2100 | 93.3421 | 101.6994 | 110.8332 | 119.6611 | 128.5475
DorionIce Accretion2023RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2023 | 11.7793 | 14.0901 | 17.024 | 19.2552 | 21.4906
DorionIce Accretion2025RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2025 | 11.7904 | 14.1011 | 17.032 | 19.2612 | 21.4973
DorionIce Accretion2030RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2030 | 11.8016 | 14.1122 | 17.04 | 19.2673 | 21.504
DorionIce Accretion2035RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2035 | 11.8127 | 14.1233 | 17.048 | 19.2733 | 21.5107
DorionIce Accretion2040RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2040 | 11.8238 | 14.1343 | 17.056 | 19.2793 | 21.5174
DorionIce Accretion2045RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2045 | 11.835 | 14.1454 | 17.064 | 19.2853 | 21.5242
DorionIce Accretion2050RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2050 | 11.8862 | 14.199 | 17.1232 | 19.3492 | 21.5914
DorionIce Accretion2055RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2055 | 11.9262 | 14.2415 | 17.1744 | 19.4071 | 21.6518
DorionIce Accretion2060RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2060 | 11.9663 | 14.284 | 17.2256 | 19.4649 | 21.7123
DorionIce Accretion2065RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2065 | 12.0064 | 14.3265 | 17.2768 | 19.5228 | 21.7728
DorionIce Accretion2070RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2070 | 12.0465 | 14.369 | 17.328 | 19.5806 | 21.8333
DorionIce Accretion2075RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2075 | 12.0762 | 14.411 | 17.384 | 19.6469 | 21.9106
DorionIce Accretion2080RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2080 | 12.1059 | 14.4531 | 17.44 | 19.7132 | 21.9878
DorionIce Accretion2085RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2085 | 12.1356 | 14.4951 | 17.496 | 19.7795 | 22.0651
DorionIce Accretion2090RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2090 | 12.1652 | 14.5372 | 17.552 | 19.8458 | 22.1424
DorionIce Accretion2095RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2095 | 12.1949 | 14.5792 | 17.608 | 19.9121 | 22.2197
DorionIce Accretion2100RCP4.5 | Dorion | Ice Accretion | RCP4.5 | 2100 | 12.2246 | 14.6213 | 17.664 | 19.9784 | 22.297
DorionIce Accretion2023RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2023 | 11.7793 | 14.0901 | 17.024 | 19.2552 | 21.4906
DorionIce Accretion2025RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2025 | 11.7904 | 14.1011 | 17.032 | 19.2612 | 21.4973
DorionIce Accretion2030RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2030 | 11.8016 | 14.1122 | 17.04 | 19.2673 | 21.504
DorionIce Accretion2035RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2035 | 11.8127 | 14.1233 | 17.048 | 19.2733 | 21.5107
DorionIce Accretion2040RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2040 | 11.8238 | 14.1343 | 17.056 | 19.2793 | 21.5174
DorionIce Accretion2045RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2045 | 11.835 | 14.1454 | 17.064 | 19.2853 | 21.5242
DorionIce Accretion2050RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2050 | 11.8862 | 14.199 | 17.1232 | 19.3492 | 21.5914
DorionIce Accretion2055RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2055 | 11.9262 | 14.2415 | 17.1744 | 19.4071 | 21.6518
DorionIce Accretion2060RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2060 | 11.9663 | 14.284 | 17.2256 | 19.4649 | 21.7123
DorionIce Accretion2065RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2065 | 12.0064 | 14.3265 | 17.2768 | 19.5228 | 21.7728
DorionIce Accretion2070RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2070 | 12.0465 | 14.369 | 17.328 | 19.5806 | 21.8333
DorionIce Accretion2075RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2075 | 12.091 | 14.432 | 17.412 | 19.6801 | 21.9492
DorionIce Accretion2080RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2080 | 12.1356 | 14.4951 | 17.496 | 19.7795 | 22.0651
DorionIce Accretion2085RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2085 | 12.1801 | 14.5582 | 17.58 | 19.879 | 22.181
DorionIce Accretion2090RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2090 | 12.2358 | 14.6434 | 17.7013 | 20.0266 | 22.3574
DorionIce Accretion2095RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2095 | 12.2469 | 14.6655 | 17.7387 | 20.0748 | 22.4179
DorionIce Accretion2100RCP6.0 | Dorion | Ice Accretion | RCP6.0 | 2100 | 12.258 | 14.6877 | 17.776 | 20.123 | 22.4784
DorionIce Accretion2023RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2023 | 11.7793 | 14.0901 | 17.024 | 19.2552 | 21.4906
DorionIce Accretion2025RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2025 | 11.8016 | 14.1122 | 17.04 | 19.2673 | 21.504
DorionIce Accretion2030RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2030 | 11.8238 | 14.1343 | 17.056 | 19.2793 | 21.5174
DorionIce Accretion2035RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2035 | 11.8461 | 14.1565 | 17.072 | 19.2914 | 21.5309
DorionIce Accretion2040RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2040 | 11.9129 | 14.2273 | 17.1573 | 19.3878 | 21.6317
DorionIce Accretion2045RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2045 | 11.9797 | 14.2981 | 17.2427 | 19.4842 | 21.7325
DorionIce Accretion2050RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2050 | 12.1059 | 14.4531 | 17.44 | 19.7132 | 21.9878
DorionIce Accretion2055RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2055 | 12.1652 | 14.5372 | 17.552 | 19.8458 | 22.1424
DorionIce Accretion2060RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2060 | 12.2358 | 14.6434 | 17.7013 | 20.0266 | 22.3574
DorionIce Accretion2065RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2065 | 12.2469 | 14.6655 | 17.7387 | 20.0748 | 22.4179
DorionIce Accretion2070RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2070 | 12.2246 | 14.67 | 17.7707 | 20.1291 | 22.4918
DorionIce Accretion2075RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2075 | 12.1912 | 14.6523 | 17.7653 | 20.1351 | 22.5053
DorionIce Accretion2080RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2080 | 12.1578 | 14.6346 | 17.76 | 20.1411 | 22.5187
DorionIce Accretion2085RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2085 | 11.8628 | 14.2826 | 17.344 | 19.671 | 21.9946
DorionIce Accretion2090RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2090 | 11.5677 | 13.9307 | 16.928 | 19.201 | 21.4704
DorionIce Accretion2095RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2095 | 11.5677 | 13.9307 | 16.928 | 19.201 | 21.4704
DorionIce Accretion2100RCP8.5 | Dorion | Ice Accretion | RCP8.5 | 2100 | 11.5677 | 13.9307 | 16.928 | 19.201 | 21.4704
DorionWind2023RCP4.5 | Dorion | Wind | RCP4.5 | 2023 | 81.4514 | 87.7085 | 94.282 | 100.8616 | 107.4493
DorionWind2025RCP4.5 | Dorion | Wind | RCP4.5 | 2025 | 81.6719 | 87.9868 | 94.6345 | 101.2757 | 107.9262
DorionWind2030RCP4.5 | Dorion | Wind | RCP4.5 | 2030 | 81.8924 | 88.2651 | 94.987 | 101.6897 | 108.4031
DorionWind2035RCP4.5 | Dorion | Wind | RCP4.5 | 2035 | 82.1129 | 88.5433 | 95.3395 | 102.1038 | 108.8799
DorionWind2040RCP4.5 | Dorion | Wind | RCP4.5 | 2040 | 82.3335 | 88.8216 | 95.692 | 102.5178 | 109.3568
DorionWind2045RCP4.5 | Dorion | Wind | RCP4.5 | 2045 | 82.554 | 89.0999 | 96.0445 | 102.9319 | 109.8336
DorionWind2050RCP4.5 | Dorion | Wind | RCP4.5 | 2050 | 82.9141 | 89.5426 | 96.5869 | 103.5612 | 110.5505
DorionWind2055RCP4.5 | Dorion | Wind | RCP4.5 | 2055 | 83.0537 | 89.7069 | 96.7768 | 103.7764 | 110.7906
DorionWind2060RCP4.5 | Dorion | Wind | RCP4.5 | 2060 | 83.1933 | 89.8713 | 96.9666 | 103.9917 | 111.0306
DorionWind2065RCP4.5 | Dorion | Wind | RCP4.5 | 2065 | 83.3329 | 90.0356 | 97.1565 | 104.2069 | 111.2707
DorionWind2070RCP4.5 | Dorion | Wind | RCP4.5 | 2070 | 83.4725 | 90.2 | 97.3464 | 104.4222 | 111.5107
DorionWind2075RCP4.5 | Dorion | Wind | RCP4.5 | 2075 | 83.4982 | 90.2131 | 97.3448 | 104.4071 | 111.4839
DorionWind2080RCP4.5 | Dorion | Wind | RCP4.5 | 2080 | 83.5239 | 90.2262 | 97.3433 | 104.392 | 111.4571
DorionWind2085RCP4.5 | Dorion | Wind | RCP4.5 | 2085 | 83.5496 | 90.2393 | 97.3417 | 104.3769 | 111.4303
DorionWind2090RCP4.5 | Dorion | Wind | RCP4.5 | 2090 | 83.5753 | 90.2524 | 97.3401 | 104.3618 | 111.4035
DorionWind2095RCP4.5 | Dorion | Wind | RCP4.5 | 2095 | 83.601 | 90.2655 | 97.3386 | 104.3467 | 111.3767
DorionWind2100RCP4.5 | Dorion | Wind | RCP4.5 | 2100 | 83.6267 | 90.2786 | 97.337 | 104.3316 | 111.35
DorionWind2023RCP6.0 | Dorion | Wind | RCP6.0 | 2023 | 81.4514 | 87.7085 | 94.282 | 100.8616 | 107.4493
DorionWind2025RCP6.0 | Dorion | Wind | RCP6.0 | 2025 | 81.6719 | 87.9868 | 94.6345 | 101.2757 | 107.9262
DorionWind2030RCP6.0 | Dorion | Wind | RCP6.0 | 2030 | 81.8924 | 88.2651 | 94.987 | 101.6897 | 108.4031
DorionWind2035RCP6.0 | Dorion | Wind | RCP6.0 | 2035 | 82.1129 | 88.5433 | 95.3395 | 102.1038 | 108.8799
DorionWind2040RCP6.0 | Dorion | Wind | RCP6.0 | 2040 | 82.3335 | 88.8216 | 95.692 | 102.5178 | 109.3568
DorionWind2045RCP6.0 | Dorion | Wind | RCP6.0 | 2045 | 82.554 | 89.0999 | 96.0445 | 102.9319 | 109.8336
DorionWind2050RCP6.0 | Dorion | Wind | RCP6.0 | 2050 | 82.9141 | 89.5426 | 96.5869 | 103.5612 | 110.5505
DorionWind2055RCP6.0 | Dorion | Wind | RCP6.0 | 2055 | 83.0537 | 89.7069 | 96.7768 | 103.7764 | 110.7906
DorionWind2060RCP6.0 | Dorion | Wind | RCP6.0 | 2060 | 83.1933 | 89.8713 | 96.9666 | 103.9917 | 111.0306
DorionWind2065RCP6.0 | Dorion | Wind | RCP6.0 | 2065 | 83.3329 | 90.0356 | 97.1565 | 104.2069 | 111.2707
DorionWind2070RCP6.0 | Dorion | Wind | RCP6.0 | 2070 | 83.4725 | 90.2 | 97.3464 | 104.4222 | 111.5107
DorionWind2075RCP6.0 | Dorion | Wind | RCP6.0 | 2075 | 83.5111 | 90.2196 | 97.3441 | 104.3995 | 111.4705
DorionWind2080RCP6.0 | Dorion | Wind | RCP6.0 | 2080 | 83.5496 | 90.2393 | 97.3417 | 104.3769 | 111.4303
DorionWind2085RCP6.0 | Dorion | Wind | RCP6.0 | 2085 | 83.5882 | 90.259 | 97.3393 | 104.3543 | 111.3901
DorionWind2090RCP6.0 | Dorion | Wind | RCP6.0 | 2090 | 83.6592 | 90.3019 | 97.3495 | 104.3383 | 111.3464
DorionWind2095RCP6.0 | Dorion | Wind | RCP6.0 | 2095 | 83.6917 | 90.3253 | 97.3621 | 104.345 | 111.3428
DorionWind2100RCP6.0 | Dorion | Wind | RCP6.0 | 2100 | 83.7241 | 90.3486 | 97.3746 | 104.3518 | 111.3392
DorionWind2023RCP8.5 | Dorion | Wind | RCP8.5 | 2023 | 81.4514 | 87.7085 | 94.282 | 100.8616 | 107.4493
DorionWind2025RCP8.5 | Dorion | Wind | RCP8.5 | 2025 | 81.8924 | 88.2651 | 94.987 | 101.6897 | 108.4031
DorionWind2030RCP8.5 | Dorion | Wind | RCP8.5 | 2030 | 82.3335 | 88.8216 | 95.692 | 102.5178 | 109.3568
DorionWind2035RCP8.5 | Dorion | Wind | RCP8.5 | 2035 | 82.7745 | 89.3782 | 96.397 | 103.346 | 110.3105
DorionWind2040RCP8.5 | Dorion | Wind | RCP8.5 | 2040 | 83.0071 | 89.6521 | 96.7135 | 103.7047 | 110.7106
DorionWind2045RCP8.5 | Dorion | Wind | RCP8.5 | 2045 | 83.2398 | 89.926 | 97.0299 | 104.0634 | 111.1106
DorionWind2050RCP8.5 | Dorion | Wind | RCP8.5 | 2050 | 83.5239 | 90.2262 | 97.3433 | 104.392 | 111.4571
DorionWind2055RCP8.5 | Dorion | Wind | RCP8.5 | 2055 | 83.5753 | 90.2524 | 97.3401 | 104.3618 | 111.4035
DorionWind2060RCP8.5 | Dorion | Wind | RCP8.5 | 2060 | 83.6592 | 90.3019 | 97.3495 | 104.3383 | 111.3464
DorionWind2065RCP8.5 | Dorion | Wind | RCP8.5 | 2065 | 83.6917 | 90.3253 | 97.3621 | 104.345 | 111.3428
DorionWind2070RCP8.5 | Dorion | Wind | RCP8.5 | 2070 | 83.9054 | 90.5788 | 97.6597 | 104.687 | 111.725
DorionWind2075RCP8.5 | Dorion | Wind | RCP8.5 | 2075 | 84.0867 | 90.809 | 97.9449 | 105.0223 | 112.1108
DorionWind2080RCP8.5 | Dorion | Wind | RCP8.5 | 2080 | 84.2679 | 91.0392 | 98.23 | 105.3576 | 112.4966
DorionWind2085RCP8.5 | Dorion | Wind | RCP8.5 | 2085 | 84.6332 | 91.5069 | 98.8222 | 106.0566 | 113.3056
DorionWind2090RCP8.5 | Dorion | Wind | RCP8.5 | 2090 | 84.9984 | 91.9746 | 99.4144 | 106.7556 | 114.1147
DorionWind2095RCP8.5 | Dorion | Wind | RCP8.5 | 2095 | 84.9984 | 91.9746 | 99.4144 | 106.7556 | 114.1147
DorionWind2100RCP8.5 | Dorion | Wind | RCP8.5 | 2100 | 84.9984 | 91.9746 | 99.4144 | 106.7556 | 114.1147
DresdenIce Accretion2023RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2023 | 17.1178 | 20.5218 | 24.825 | 28.1087 | 31.4055
DresdenIce Accretion2025RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2025 | 17.0105 | 20.4145 | 24.7167 | 27.9957 | 31.2847
DresdenIce Accretion2030RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2030 | 16.9033 | 20.3073 | 24.6083 | 27.8827 | 31.164
DresdenIce Accretion2035RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2035 | 16.796 | 20.2001 | 24.5 | 27.7697 | 31.0433
DresdenIce Accretion2040RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2040 | 16.6887 | 20.0929 | 24.3917 | 27.6567 | 30.9225
DresdenIce Accretion2045RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2045 | 16.5814 | 19.9857 | 24.2833 | 27.5437 | 30.8018
DresdenIce Accretion2050RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2050 | 16.081 | 19.4386 | 23.67 | 26.877 | 30.0762
DresdenIce Accretion2055RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2055 | 15.6879 | 18.9987 | 23.165 | 26.3233 | 29.4714
DresdenIce Accretion2060RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2060 | 15.2947 | 18.5588 | 22.66 | 25.7696 | 28.8666
DresdenIce Accretion2065RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2065 | 14.9015 | 18.1189 | 22.155 | 25.2159 | 28.2618
DresdenIce Accretion2070RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2070 | 14.5084 | 17.679 | 21.65 | 24.6622 | 27.657
DresdenIce Accretion2075RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2075 | 14.1286 | 17.2398 | 21.1375 | 24.0925 | 27.027
DresdenIce Accretion2080RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2080 | 13.7488 | 16.8006 | 20.625 | 23.5228 | 26.397
DresdenIce Accretion2085RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2085 | 13.3689 | 16.3614 | 20.1125 | 22.9531 | 25.767
DresdenIce Accretion2090RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2090 | 12.9891 | 15.9222 | 19.6 | 22.3834 | 25.137
DresdenIce Accretion2095RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2095 | 12.6093 | 15.483 | 19.0875 | 21.8137 | 24.507
DresdenIce Accretion2100RCP4.5 | Dresden | Ice Accretion | RCP4.5 | 2100 | 12.2295 | 15.0437 | 18.575 | 21.244 | 23.877
DresdenIce Accretion2023RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2023 | 17.1178 | 20.5218 | 24.825 | 28.1087 | 31.4055
DresdenIce Accretion2025RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2025 | 17.0105 | 20.4145 | 24.7167 | 27.9957 | 31.2847
DresdenIce Accretion2030RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2030 | 16.9033 | 20.3073 | 24.6083 | 27.8827 | 31.164
DresdenIce Accretion2035RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2035 | 16.796 | 20.2001 | 24.5 | 27.7697 | 31.0433
DresdenIce Accretion2040RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2040 | 16.6887 | 20.0929 | 24.3917 | 27.6567 | 30.9225
DresdenIce Accretion2045RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2045 | 16.5814 | 19.9857 | 24.2833 | 27.5437 | 30.8018
DresdenIce Accretion2050RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2050 | 16.081 | 19.4386 | 23.67 | 26.877 | 30.0762
DresdenIce Accretion2055RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2055 | 15.6879 | 18.9987 | 23.165 | 26.3233 | 29.4714
DresdenIce Accretion2060RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2060 | 15.2947 | 18.5588 | 22.66 | 25.7696 | 28.8666
DresdenIce Accretion2065RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2065 | 14.9015 | 18.1189 | 22.155 | 25.2159 | 28.2618
DresdenIce Accretion2070RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2070 | 14.5084 | 17.679 | 21.65 | 24.6622 | 27.657
DresdenIce Accretion2075RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2075 | 13.9387 | 17.0202 | 20.8812 | 23.8077 | 26.712
DresdenIce Accretion2080RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2080 | 13.3689 | 16.3614 | 20.1125 | 22.9531 | 25.767
DresdenIce Accretion2085RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2085 | 12.7992 | 15.7026 | 19.3438 | 22.0986 | 24.822
DresdenIce Accretion2090RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2090 | 11.3597 | 14.0062 | 17.3167 | 19.8221 | 22.2915
DresdenIce Accretion2095RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2095 | 10.4899 | 12.9687 | 16.0583 | 18.4002 | 20.706
DresdenIce Accretion2100RCP6.0 | Dresden | Ice Accretion | RCP6.0 | 2100 | 9.6201 | 11.9312 | 14.8 | 16.9782 | 19.1205
DresdenIce Accretion2023RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2023 | 17.1178 | 20.5218 | 24.825 | 28.1087 | 31.4055
DresdenIce Accretion2025RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2025 | 16.9033 | 20.3073 | 24.6083 | 27.8827 | 31.164
DresdenIce Accretion2030RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2030 | 16.6887 | 20.0929 | 24.3917 | 27.6567 | 30.9225
DresdenIce Accretion2035RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2035 | 16.4742 | 19.8785 | 24.175 | 27.4307 | 30.681
DresdenIce Accretion2040RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2040 | 15.8189 | 19.1453 | 23.3333 | 26.5079 | 29.673
DresdenIce Accretion2045RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2045 | 15.1636 | 18.4122 | 22.4917 | 25.5851 | 28.665
DresdenIce Accretion2050RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2050 | 13.7488 | 16.8006 | 20.625 | 23.5228 | 26.397
DresdenIce Accretion2055RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2055 | 12.9891 | 15.9222 | 19.6 | 22.3834 | 25.137
DresdenIce Accretion2060RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2060 | 11.3597 | 14.0062 | 17.3167 | 19.8221 | 22.2915
DresdenIce Accretion2065RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2065 | 10.4899 | 12.9687 | 16.0583 | 18.4002 | 20.706
DresdenIce Accretion2070RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2070 | 9.1388 | 11.3572 | 14.1083 | 16.1872 | 18.2385
DresdenIce Accretion2075RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2075 | 8.6575 | 10.7831 | 13.4167 | 15.3962 | 17.3565
DresdenIce Accretion2080RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2080 | 8.1762 | 10.209 | 12.725 | 14.6052 | 16.4745
DresdenIce Accretion2085RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2085 | 7.5151 | 9.4101 | 11.7625 | 13.5176 | 15.2617
DresdenIce Accretion2090RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2090 | 6.8541 | 8.6113 | 10.8 | 12.43 | 14.049
DresdenIce Accretion2095RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2095 | 6.8541 | 8.6113 | 10.8 | 12.43 | 14.049
DresdenIce Accretion2100RCP8.5 | Dresden | Ice Accretion | RCP8.5 | 2100 | 6.8541 | 8.6113 | 10.8 | 12.43 | 14.049
DresdenWind2023RCP4.5 | Dresden | Wind | RCP4.5 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.368
DresdenWind2025RCP4.5 | Dresden | Wind | RCP4.5 | 2025 | 85.0909 | 91.6975 | 98.6697 | 105.6307 | 112.5951
DresdenWind2030RCP4.5 | Dresden | Wind | RCP4.5 | 2030 | 85.1798 | 91.8175 | 98.8297 | 105.8247 | 112.8223
DresdenWind2035RCP4.5 | Dresden | Wind | RCP4.5 | 2035 | 85.2686 | 91.9375 | 98.9898 | 106.0187 | 113.0495
DresdenWind2040RCP4.5 | Dresden | Wind | RCP4.5 | 2040 | 85.3575 | 92.0575 | 99.1499 | 106.2127 | 113.2766
DresdenWind2045RCP4.5 | Dresden | Wind | RCP4.5 | 2045 | 85.4463 | 92.1775 | 99.3099 | 106.4067 | 113.5038
DresdenWind2050RCP4.5 | Dresden | Wind | RCP4.5 | 2050 | 85.6435 | 92.4415 | 99.6582 | 106.8272 | 113.9969
DresdenWind2055RCP4.5 | Dresden | Wind | RCP4.5 | 2055 | 85.7518 | 92.5855 | 99.8463 | 107.0537 | 114.2627
DresdenWind2060RCP4.5 | Dresden | Wind | RCP4.5 | 2060 | 85.8601 | 92.7295 | 100.0345 | 107.2802 | 114.5286
DresdenWind2065RCP4.5 | Dresden | Wind | RCP4.5 | 2065 | 85.9684 | 92.8735 | 100.2226 | 107.5067 | 114.7945
DresdenWind2070RCP4.5 | Dresden | Wind | RCP4.5 | 2070 | 86.0768 | 93.0175 | 100.4108 | 107.7332 | 115.0604
DresdenWind2075RCP4.5 | Dresden | Wind | RCP4.5 | 2075 | 86.2601 | 93.256 | 100.7179 | 108.0967 | 115.485
DresdenWind2080RCP4.5 | Dresden | Wind | RCP4.5 | 2080 | 86.4435 | 93.4945 | 101.0249 | 108.4602 | 115.9095
DresdenWind2085RCP4.5 | Dresden | Wind | RCP4.5 | 2085 | 86.6268 | 93.7329 | 101.332 | 108.8237 | 116.334
DresdenWind2090RCP4.5 | Dresden | Wind | RCP4.5 | 2090 | 86.8101 | 93.9714 | 101.6391 | 109.1872 | 116.7586
DresdenWind2095RCP4.5 | Dresden | Wind | RCP4.5 | 2095 | 86.9935 | 94.2099 | 101.9461 | 109.5507 | 117.1831
DresdenWind2100RCP4.5 | Dresden | Wind | RCP4.5 | 2100 | 87.1768 | 94.4484 | 102.2532 | 109.9143 | 117.6076
DresdenWind2023RCP6.0 | Dresden | Wind | RCP6.0 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.368
DresdenWind2025RCP6.0 | Dresden | Wind | RCP6.0 | 2025 | 85.0909 | 91.6975 | 98.6697 | 105.6307 | 112.5951
DresdenWind2030RCP6.0 | Dresden | Wind | RCP6.0 | 2030 | 85.1798 | 91.8175 | 98.8297 | 105.8247 | 112.8223
DresdenWind2035RCP6.0 | Dresden | Wind | RCP6.0 | 2035 | 85.2686 | 91.9375 | 98.9898 | 106.0187 | 113.0495
DresdenWind2040RCP6.0 | Dresden | Wind | RCP6.0 | 2040 | 85.3575 | 92.0575 | 99.1499 | 106.2127 | 113.2766
DresdenWind2045RCP6.0 | Dresden | Wind | RCP6.0 | 2045 | 85.4463 | 92.1775 | 99.3099 | 106.4067 | 113.5038
DresdenWind2050RCP6.0 | Dresden | Wind | RCP6.0 | 2050 | 85.6435 | 92.4415 | 99.6582 | 106.8272 | 113.9969
DresdenWind2055RCP6.0 | Dresden | Wind | RCP6.0 | 2055 | 85.7518 | 92.5855 | 99.8463 | 107.0537 | 114.2627
DresdenWind2060RCP6.0 | Dresden | Wind | RCP6.0 | 2060 | 85.8601 | 92.7295 | 100.0345 | 107.2802 | 114.5286
DresdenWind2065RCP6.0 | Dresden | Wind | RCP6.0 | 2065 | 85.9684 | 92.8735 | 100.2226 | 107.5067 | 114.7945
DresdenWind2070RCP6.0 | Dresden | Wind | RCP6.0 | 2070 | 86.0768 | 93.0175 | 100.4108 | 107.7332 | 115.0604
DresdenWind2075RCP6.0 | Dresden | Wind | RCP6.0 | 2075 | 86.3518 | 93.3752 | 100.8714 | 108.2784 | 115.6972
DresdenWind2080RCP6.0 | Dresden | Wind | RCP6.0 | 2080 | 86.6268 | 93.7329 | 101.332 | 108.8237 | 116.334
DresdenWind2085RCP6.0 | Dresden | Wind | RCP6.0 | 2085 | 86.9018 | 94.0907 | 101.7926 | 109.369 | 116.9708
DresdenWind2090RCP6.0 | Dresden | Wind | RCP6.0 | 2090 | 87.5661 | 94.9375 | 102.8673 | 110.6343 | 118.4381
DresdenWind2095RCP6.0 | Dresden | Wind | RCP6.0 | 2095 | 87.9554 | 95.4266 | 103.4815 | 111.3543 | 119.2685
DresdenWind2100RCP6.0 | Dresden | Wind | RCP6.0 | 2100 | 88.3446 | 95.9157 | 104.0956 | 112.0744 | 120.099
DresdenWind2023RCP8.5 | Dresden | Wind | RCP8.5 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.368
DresdenWind2025RCP8.5 | Dresden | Wind | RCP8.5 | 2025 | 85.1798 | 91.8175 | 98.8297 | 105.8247 | 112.8223
DresdenWind2030RCP8.5 | Dresden | Wind | RCP8.5 | 2030 | 85.3575 | 92.0575 | 99.1499 | 106.2127 | 113.2766
DresdenWind2035RCP8.5 | Dresden | Wind | RCP8.5 | 2035 | 85.5352 | 92.2975 | 99.47 | 106.6007 | 113.731
DresdenWind2040RCP8.5 | Dresden | Wind | RCP8.5 | 2040 | 85.7157 | 92.5375 | 99.7836 | 106.9782 | 114.1741
DresdenWind2045RCP8.5 | Dresden | Wind | RCP8.5 | 2045 | 85.8962 | 92.7775 | 100.0972 | 107.3557 | 114.6173
DresdenWind2050RCP8.5 | Dresden | Wind | RCP8.5 | 2050 | 86.4435 | 93.4945 | 101.0249 | 108.4602 | 115.9095
DresdenWind2055RCP8.5 | Dresden | Wind | RCP8.5 | 2055 | 86.8101 | 93.9714 | 101.6391 | 109.1872 | 116.7586
DresdenWind2060RCP8.5 | Dresden | Wind | RCP8.5 | 2060 | 87.5661 | 94.9375 | 102.8673 | 110.6343 | 118.4381
DresdenWind2065RCP8.5 | Dresden | Wind | RCP8.5 | 2065 | 87.9554 | 95.4266 | 103.4815 | 111.3543 | 119.2685
DresdenWind2070RCP8.5 | Dresden | Wind | RCP8.5 | 2070 | 88.5251 | 96.1405 | 104.3733 | 112.3994 | 120.4677
DresdenWind2075RCP8.5 | Dresden | Wind | RCP8.5 | 2075 | 88.7057 | 96.3654 | 104.6509 | 112.7245 | 120.8364
DresdenWind2080RCP8.5 | Dresden | Wind | RCP8.5 | 2080 | 88.8862 | 96.5902 | 104.9286 | 113.0496 | 121.205
DresdenWind2085RCP8.5 | Dresden | Wind | RCP8.5 | 2085 | 89.3855 | 97.219 | 105.7224 | 113.9828 | 122.2831
DresdenWind2090RCP8.5 | Dresden | Wind | RCP8.5 | 2090 | 89.8847 | 97.8479 | 106.5162 | 114.9161 | 123.3612
DresdenWind2095RCP8.5 | Dresden | Wind | RCP8.5 | 2095 | 89.8847 | 97.8479 | 106.5162 | 114.9161 | 123.3612
DresdenWind2100RCP8.5 | Dresden | Wind | RCP8.5 | 2100 | 89.8847 | 97.8479 | 106.5162 | 114.9161 | 123.3612
DrydenIce Accretion2023RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2023 | 10.3458 | 12.3637 | 14.924 | 16.8799 | 18.8219
DrydenIce Accretion2025RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2025 | 10.3767 | 12.4005 | 14.9683 | 16.93 | 18.8777
DrydenIce Accretion2030RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2030 | 10.4075 | 12.4373 | 15.0127 | 16.9801 | 18.9336
DrydenIce Accretion2035RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2035 | 10.4384 | 12.4741 | 15.057 | 17.0302 | 18.9895
DrydenIce Accretion2040RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2040 | 10.4692 | 12.5109 | 15.1013 | 17.0803 | 19.0453
DrydenIce Accretion2045RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2045 | 10.5001 | 12.5477 | 15.1457 | 17.1304 | 19.1012
DrydenIce Accretion2050RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2050 | 10.5387 | 12.5891 | 15.19 | 17.1774 | 19.1535
DrydenIce Accretion2055RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2055 | 10.5465 | 12.5938 | 15.19 | 17.1742 | 19.15
DrydenIce Accretion2060RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2060 | 10.5543 | 12.5984 | 15.19 | 17.171 | 19.1465
DrydenIce Accretion2065RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2065 | 10.5621 | 12.6031 | 15.19 | 17.1679 | 19.1429
DrydenIce Accretion2070RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2070 | 10.5699 | 12.6077 | 15.19 | 17.1647 | 19.1394
DrydenIce Accretion2075RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2075 | 10.5585 | 12.5922 | 15.1713 | 17.1436 | 19.1159
DrydenIce Accretion2080RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2080 | 10.5472 | 12.5767 | 15.1527 | 17.1225 | 19.0924
DrydenIce Accretion2085RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2085 | 10.5358 | 12.5612 | 15.134 | 17.1014 | 19.0688
DrydenIce Accretion2090RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2090 | 10.5244 | 12.5457 | 15.1153 | 17.0803 | 19.0453
DrydenIce Accretion2095RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2095 | 10.5131 | 12.5302 | 15.0967 | 17.0592 | 19.0218
DrydenIce Accretion2100RCP4.5 | Dryden | Ice Accretion | RCP4.5 | 2100 | 10.5017 | 12.5147 | 15.078 | 17.0381 | 18.9983
DrydenIce Accretion2023RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2023 | 10.3458 | 12.3637 | 14.924 | 16.8799 | 18.8219
DrydenIce Accretion2025RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2025 | 10.3767 | 12.4005 | 14.9683 | 16.93 | 18.8777
DrydenIce Accretion2030RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2030 | 10.4075 | 12.4373 | 15.0127 | 16.9801 | 18.9336
DrydenIce Accretion2035RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2035 | 10.4384 | 12.4741 | 15.057 | 17.0302 | 18.9895
DrydenIce Accretion2040RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2040 | 10.4692 | 12.5109 | 15.1013 | 17.0803 | 19.0453
DrydenIce Accretion2045RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2045 | 10.5001 | 12.5477 | 15.1457 | 17.1304 | 19.1012
DrydenIce Accretion2050RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2050 | 10.5387 | 12.5891 | 15.19 | 17.1774 | 19.1535
DrydenIce Accretion2055RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2055 | 10.5465 | 12.5938 | 15.19 | 17.1742 | 19.15
DrydenIce Accretion2060RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2060 | 10.5543 | 12.5984 | 15.19 | 17.171 | 19.1465
DrydenIce Accretion2065RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2065 | 10.5621 | 12.6031 | 15.19 | 17.1679 | 19.1429
DrydenIce Accretion2070RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2070 | 10.5699 | 12.6077 | 15.19 | 17.1647 | 19.1394
DrydenIce Accretion2075RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2075 | 10.5529 | 12.5845 | 15.162 | 17.1331 | 19.1041
DrydenIce Accretion2080RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2080 | 10.5358 | 12.5612 | 15.134 | 17.1014 | 19.0688
DrydenIce Accretion2085RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2085 | 10.5188 | 12.538 | 15.106 | 17.0698 | 19.0336
DrydenIce Accretion2090RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2090 | 10.5374 | 12.5612 | 15.134 | 17.1014 | 19.0688
DrydenIce Accretion2095RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2095 | 10.5731 | 12.6077 | 15.19 | 17.1647 | 19.1394
DrydenIce Accretion2100RCP6.0 | Dryden | Ice Accretion | RCP6.0 | 2100 | 10.6089 | 12.6542 | 15.246 | 17.228 | 19.21
DrydenIce Accretion2023RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2023 | 10.3458 | 12.3637 | 14.924 | 16.8799 | 18.8219
DrydenIce Accretion2025RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2025 | 10.4075 | 12.4373 | 15.0127 | 16.9801 | 18.9336
DrydenIce Accretion2030RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2030 | 10.4692 | 12.5109 | 15.1013 | 17.0803 | 19.0453
DrydenIce Accretion2035RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2035 | 10.5309 | 12.5845 | 15.19 | 17.1805 | 19.157
DrydenIce Accretion2040RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2040 | 10.5439 | 12.5922 | 15.19 | 17.1752 | 19.1512
DrydenIce Accretion2045RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2045 | 10.5569 | 12.6 | 15.19 | 17.17 | 19.1453
DrydenIce Accretion2050RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2050 | 10.5472 | 12.5767 | 15.1527 | 17.1225 | 19.0924
DrydenIce Accretion2055RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2055 | 10.5244 | 12.5457 | 15.1153 | 17.0803 | 19.0453
DrydenIce Accretion2060RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2060 | 10.5374 | 12.5612 | 15.134 | 17.1014 | 19.0688
DrydenIce Accretion2065RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2065 | 10.5731 | 12.6077 | 15.19 | 17.1647 | 19.1394
DrydenIce Accretion2070RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2070 | 10.7095 | 12.7859 | 15.4187 | 17.4336 | 19.4452
DrydenIce Accretion2075RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2075 | 10.8102 | 12.9176 | 15.5913 | 17.6393 | 19.6804
DrydenIce Accretion2080RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2080 | 10.9109 | 13.0493 | 15.764 | 17.845 | 19.9156
DrydenIce Accretion2085RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2085 | 10.6868 | 12.7762 | 15.428 | 17.4574 | 19.4746
DrydenIce Accretion2090RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2090 | 10.4627 | 12.5031 | 15.092 | 17.0698 | 19.0336
DrydenIce Accretion2095RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2095 | 10.4627 | 12.5031 | 15.092 | 17.0698 | 19.0336
DrydenIce Accretion2100RCP8.5 | Dryden | Ice Accretion | RCP8.5 | 2100 | 10.4627 | 12.5031 | 15.092 | 17.0698 | 19.0336
DrydenWind2023RCP4.5 | Dryden | Wind | RCP4.5 | 2023 | 72.4672 | 78.0497 | 83.9328 | 89.8171 | 95.693
DrydenWind2025RCP4.5 | Dryden | Wind | RCP4.5 | 2025 | 72.5035 | 78.0809 | 83.9538 | 89.8306 | 95.7009
DrydenWind2030RCP4.5 | Dryden | Wind | RCP4.5 | 2030 | 72.5398 | 78.1122 | 83.9748 | 89.844 | 95.7089
DrydenWind2035RCP4.5 | Dryden | Wind | RCP4.5 | 2035 | 72.576 | 78.1434 | 83.9958 | 89.8575 | 95.7169
DrydenWind2040RCP4.5 | Dryden | Wind | RCP4.5 | 2040 | 72.6123 | 78.1747 | 84.0168 | 89.871 | 95.7249
DrydenWind2045RCP4.5 | Dryden | Wind | RCP4.5 | 2045 | 72.6486 | 78.2059 | 84.0378 | 89.8845 | 95.7329
DrydenWind2050RCP4.5 | Dryden | Wind | RCP4.5 | 2050 | 72.7777 | 78.3434 | 84.1831 | 90.0382 | 95.8941
DrydenWind2055RCP4.5 | Dryden | Wind | RCP4.5 | 2055 | 72.8705 | 78.4497 | 84.3074 | 90.1784 | 96.0473
DrydenWind2060RCP4.5 | Dryden | Wind | RCP4.5 | 2060 | 72.9634 | 78.5559 | 84.4318 | 90.3186 | 96.2005
DrydenWind2065RCP4.5 | Dryden | Wind | RCP4.5 | 2065 | 73.0562 | 78.6622 | 84.5561 | 90.4588 | 96.3537
DrydenWind2070RCP4.5 | Dryden | Wind | RCP4.5 | 2070 | 73.1491 | 78.7684 | 84.6804 | 90.599 | 96.5069
DrydenWind2075RCP4.5 | Dryden | Wind | RCP4.5 | 2075 | 73.2216 | 78.8504 | 84.7742 | 90.7024 | 96.6218
DrydenWind2080RCP4.5 | Dryden | Wind | RCP4.5 | 2080 | 73.2941 | 78.9324 | 84.868 | 90.8058 | 96.7368
DrydenWind2085RCP4.5 | Dryden | Wind | RCP4.5 | 2085 | 73.3666 | 79.0145 | 84.9618 | 90.9091 | 96.8517
DrydenWind2090RCP4.5 | Dryden | Wind | RCP4.5 | 2090 | 73.4392 | 79.0965 | 85.0556 | 91.0125 | 96.9666
DrydenWind2095RCP4.5 | Dryden | Wind | RCP4.5 | 2095 | 73.5117 | 79.1785 | 85.1494 | 91.1158 | 97.0815
DrydenWind2100RCP4.5 | Dryden | Wind | RCP4.5 | 2100 | 73.5842 | 79.2606 | 85.2432 | 91.2192 | 97.1964
DrydenWind2023RCP6.0 | Dryden | Wind | RCP6.0 | 2023 | 72.4672 | 78.0497 | 83.9328 | 89.8171 | 95.693
DrydenWind2025RCP6.0 | Dryden | Wind | RCP6.0 | 2025 | 72.5035 | 78.0809 | 83.9538 | 89.8306 | 95.7009
DrydenWind2030RCP6.0 | Dryden | Wind | RCP6.0 | 2030 | 72.5398 | 78.1122 | 83.9748 | 89.844 | 95.7089
DrydenWind2035RCP6.0 | Dryden | Wind | RCP6.0 | 2035 | 72.576 | 78.1434 | 83.9958 | 89.8575 | 95.7169
DrydenWind2040RCP6.0 | Dryden | Wind | RCP6.0 | 2040 | 72.6123 | 78.1747 | 84.0168 | 89.871 | 95.7249
DrydenWind2045RCP6.0 | Dryden | Wind | RCP6.0 | 2045 | 72.6486 | 78.2059 | 84.0378 | 89.8845 | 95.7329
DrydenWind2050RCP6.0 | Dryden | Wind | RCP6.0 | 2050 | 72.7777 | 78.3434 | 84.1831 | 90.0382 | 95.8941
DrydenWind2055RCP6.0 | Dryden | Wind | RCP6.0 | 2055 | 72.8705 | 78.4497 | 84.3074 | 90.1784 | 96.0473
DrydenWind2060RCP6.0 | Dryden | Wind | RCP6.0 | 2060 | 72.9634 | 78.5559 | 84.4318 | 90.3186 | 96.2005
DrydenWind2065RCP6.0 | Dryden | Wind | RCP6.0 | 2065 | 73.0562 | 78.6622 | 84.5561 | 90.4588 | 96.3537
DrydenWind2070RCP6.0 | Dryden | Wind | RCP6.0 | 2070 | 73.1491 | 78.7684 | 84.6804 | 90.599 | 96.5069
DrydenWind2075RCP6.0 | Dryden | Wind | RCP6.0 | 2075 | 73.2578 | 78.8914 | 84.8211 | 90.7541 | 96.6793
DrydenWind2080RCP6.0 | Dryden | Wind | RCP6.0 | 2080 | 73.3666 | 79.0145 | 84.9618 | 90.9091 | 96.8517
DrydenWind2085RCP6.0 | Dryden | Wind | RCP6.0 | 2085 | 73.4754 | 79.1375 | 85.1025 | 91.0642 | 97.024
DrydenWind2090RCP6.0 | Dryden | Wind | RCP6.0 | 2090 | 73.8091 | 79.5626 | 85.638 | 91.6926 | 97.7518
DrydenWind2095RCP6.0 | Dryden | Wind | RCP6.0 | 2095 | 74.0339 | 79.8647 | 86.0328 | 92.1659 | 98.3072
DrydenWind2100RCP6.0 | Dryden | Wind | RCP6.0 | 2100 | 74.2588 | 80.1667 | 86.4276 | 92.6393 | 98.8626
DrydenWind2023RCP8.5 | Dryden | Wind | RCP8.5 | 2023 | 72.4672 | 78.0497 | 83.9328 | 89.8171 | 95.693
DrydenWind2025RCP8.5 | Dryden | Wind | RCP8.5 | 2025 | 72.5398 | 78.1122 | 83.9748 | 89.844 | 95.7089
DrydenWind2030RCP8.5 | Dryden | Wind | RCP8.5 | 2030 | 72.6123 | 78.1747 | 84.0168 | 89.871 | 95.7249
DrydenWind2035RCP8.5 | Dryden | Wind | RCP8.5 | 2035 | 72.6848 | 78.2372 | 84.0588 | 89.898 | 95.7408
DrydenWind2040RCP8.5 | Dryden | Wind | RCP8.5 | 2040 | 72.8396 | 78.4143 | 84.266 | 90.1317 | 95.9962
DrydenWind2045RCP8.5 | Dryden | Wind | RCP8.5 | 2045 | 72.9943 | 78.5913 | 84.4732 | 90.3654 | 96.2516
DrydenWind2050RCP8.5 | Dryden | Wind | RCP8.5 | 2050 | 73.2941 | 78.9324 | 84.868 | 90.8058 | 96.7368
DrydenWind2055RCP8.5 | Dryden | Wind | RCP8.5 | 2055 | 73.4392 | 79.0965 | 85.0556 | 91.0125 | 96.9666
DrydenWind2060RCP8.5 | Dryden | Wind | RCP8.5 | 2060 | 73.8091 | 79.5626 | 85.638 | 91.6926 | 97.7518
DrydenWind2065RCP8.5 | Dryden | Wind | RCP8.5 | 2065 | 74.0339 | 79.8647 | 86.0328 | 92.1659 | 98.3072
DrydenWind2070RCP8.5 | Dryden | Wind | RCP8.5 | 2070 | 74.4643 | 80.4193 | 86.7356 | 92.9988 | 99.2712
DrydenWind2075RCP8.5 | Dryden | Wind | RCP8.5 | 2075 | 74.6698 | 80.6719 | 87.0436 | 93.3584 | 99.6798
DrydenWind2080RCP8.5 | Dryden | Wind | RCP8.5 | 2080 | 74.8753 | 80.9245 | 87.3516 | 93.7179 | 100.0884
DrydenWind2085RCP8.5 | Dryden | Wind | RCP8.5 | 2085 | 75.1038 | 81.2136 | 87.717 | 94.1448 | 100.5815
DrydenWind2090RCP8.5 | Dryden | Wind | RCP8.5 | 2090 | 75.3323 | 81.5026 | 88.0824 | 94.5717 | 101.0747
DrydenWind2095RCP8.5 | Dryden | Wind | RCP8.5 | 2095 | 75.3323 | 81.5026 | 88.0824 | 94.5717 | 101.0747
DrydenWind2100RCP8.5 | Dryden | Wind | RCP8.5 | 2100 | 75.3323 | 81.5026 | 88.0824 | 94.5717 | 101.0747
DundalkIce Accretion2023RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2023 | 15.4005 | 18.4791 | 22.396 | 25.3821 | 28.3576
DundalkIce Accretion2025RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2025 | 15.4209 | 18.5156 | 22.451 | 25.4525 | 28.4407
DundalkIce Accretion2030RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2030 | 15.4413 | 18.5522 | 22.506 | 25.5229 | 28.5239
DundalkIce Accretion2035RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2035 | 15.4617 | 18.5887 | 22.561 | 25.5934 | 28.607
DundalkIce Accretion2040RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2040 | 15.4821 | 18.6252 | 22.616 | 25.6638 | 28.6902
DundalkIce Accretion2045RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2045 | 15.5025 | 18.6617 | 22.671 | 25.7342 | 28.7734
DundalkIce Accretion2050RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2050 | 15.4893 | 18.6727 | 22.7128 | 25.7997 | 28.8676
DundalkIce Accretion2055RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2055 | 15.4556 | 18.6471 | 22.6996 | 25.7947 | 28.8787
DundalkIce Accretion2060RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2060 | 15.4219 | 18.6215 | 22.6864 | 25.7898 | 28.8898
DundalkIce Accretion2065RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2065 | 15.3882 | 18.596 | 22.6732 | 25.7848 | 28.9009
DundalkIce Accretion2070RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2070 | 15.3545 | 18.5704 | 22.66 | 25.7798 | 28.912
DundalkIce Accretion2075RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2075 | 15.3341 | 18.5735 | 22.6893 | 25.8295 | 28.9813
DundalkIce Accretion2080RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2080 | 15.3137 | 18.5765 | 22.7187 | 25.8793 | 29.0506
DundalkIce Accretion2085RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2085 | 15.2933 | 18.5795 | 22.748 | 25.929 | 29.1199
DundalkIce Accretion2090RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2090 | 15.2729 | 18.5826 | 22.7773 | 25.9787 | 29.1892
DundalkIce Accretion2095RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2095 | 15.2525 | 18.5856 | 22.8067 | 26.0284 | 29.2585
DundalkIce Accretion2100RCP4.5 | Dundalk | Ice Accretion | RCP4.5 | 2100 | 15.2321 | 18.5887 | 22.836 | 26.0781 | 29.3278
DundalkIce Accretion2023RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2023 | 15.4005 | 18.4791 | 22.396 | 25.3821 | 28.3576
DundalkIce Accretion2025RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2025 | 15.4209 | 18.5156 | 22.451 | 25.4525 | 28.4407
DundalkIce Accretion2030RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2030 | 15.4413 | 18.5522 | 22.506 | 25.5229 | 28.5239
DundalkIce Accretion2035RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2035 | 15.4617 | 18.5887 | 22.561 | 25.5934 | 28.607
DundalkIce Accretion2040RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2040 | 15.4821 | 18.6252 | 22.616 | 25.6638 | 28.6902
DundalkIce Accretion2045RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2045 | 15.5025 | 18.6617 | 22.671 | 25.7342 | 28.7734
DundalkIce Accretion2050RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2050 | 15.4893 | 18.6727 | 22.7128 | 25.7997 | 28.8676
DundalkIce Accretion2055RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2055 | 15.4556 | 18.6471 | 22.6996 | 25.7947 | 28.8787
DundalkIce Accretion2060RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2060 | 15.4219 | 18.6215 | 22.6864 | 25.7898 | 28.8898
DundalkIce Accretion2065RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2065 | 15.3882 | 18.596 | 22.6732 | 25.7848 | 28.9009
DundalkIce Accretion2070RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2070 | 15.3545 | 18.5704 | 22.66 | 25.7798 | 28.912
DundalkIce Accretion2075RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2075 | 15.3239 | 18.575 | 22.704 | 25.8544 | 29.0159
DundalkIce Accretion2080RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2080 | 15.2933 | 18.5795 | 22.748 | 25.929 | 29.1199
DundalkIce Accretion2085RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2085 | 15.2627 | 18.5841 | 22.792 | 26.0036 | 29.2238
DundalkIce Accretion2090RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2090 | 15.0331 | 18.3939 | 22.6453 | 25.8875 | 29.1245
DundalkIce Accretion2095RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2095 | 14.834 | 18.1991 | 22.4547 | 25.697 | 28.9212
DundalkIce Accretion2100RCP6.0 | Dundalk | Ice Accretion | RCP6.0 | 2100 | 14.635 | 18.0044 | 22.264 | 25.5064 | 28.7179
DundalkIce Accretion2023RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2023 | 15.4005 | 18.4791 | 22.396 | 25.3821 | 28.3576
DundalkIce Accretion2025RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2025 | 15.4413 | 18.5522 | 22.506 | 25.5229 | 28.5239
DundalkIce Accretion2030RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2030 | 15.4821 | 18.6252 | 22.616 | 25.6638 | 28.6902
DundalkIce Accretion2035RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2035 | 15.5229 | 18.6982 | 22.726 | 25.8047 | 28.8565
DundalkIce Accretion2040RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2040 | 15.4668 | 18.6556 | 22.704 | 25.7964 | 28.875
DundalkIce Accretion2045RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2045 | 15.4107 | 18.613 | 22.682 | 25.7881 | 28.8935
DundalkIce Accretion2050RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2050 | 15.3137 | 18.5765 | 22.7187 | 25.8793 | 29.0506
DundalkIce Accretion2055RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2055 | 15.2729 | 18.5826 | 22.7773 | 25.9787 | 29.1892
DundalkIce Accretion2060RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2060 | 15.0331 | 18.3939 | 22.6453 | 25.8875 | 29.1245
DundalkIce Accretion2065RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2065 | 14.834 | 18.1991 | 22.4547 | 25.697 | 28.9212
DundalkIce Accretion2070RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2070 | 14.2778 | 17.6087 | 21.8167 | 25.0174 | 28.2005
DundalkIce Accretion2075RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2075 | 13.9206 | 17.2131 | 21.3693 | 24.5285 | 27.683
DundalkIce Accretion2080RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2080 | 13.5634 | 16.8175 | 20.922 | 24.0396 | 27.1656
DundalkIce Accretion2085RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2085 | 12.9817 | 16.1601 | 20.174 | 23.2192 | 26.2647
DundalkIce Accretion2090RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2090 | 12.4 | 15.5027 | 19.426 | 22.3989 | 25.3638
DundalkIce Accretion2095RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2095 | 12.4 | 15.5027 | 19.426 | 22.3989 | 25.3638
DundalkIce Accretion2100RCP8.5 | Dundalk | Ice Accretion | RCP8.5 | 2100 | 12.4 | 15.5027 | 19.426 | 22.3989 | 25.3638
DundalkWind2023RCP4.5 | Dundalk | Wind | RCP4.5 | 2023 | 81.4271 | 87.7172 | 94.3384 | 100.9521 | 107.5672
DundalkWind2025RCP4.5 | Dundalk | Wind | RCP4.5 | 2025 | 81.4352 | 87.7318 | 94.3619 | 100.9823 | 107.6065
DundalkWind2030RCP4.5 | Dundalk | Wind | RCP4.5 | 2030 | 81.4433 | 87.7464 | 94.3854 | 101.0125 | 107.6458
DundalkWind2035RCP4.5 | Dundalk | Wind | RCP4.5 | 2035 | 81.4514 | 87.7609 | 94.4089 | 101.0427 | 107.6851
DundalkWind2040RCP4.5 | Dundalk | Wind | RCP4.5 | 2040 | 81.4596 | 87.7755 | 94.4324 | 101.0728 | 107.7244
DundalkWind2045RCP4.5 | Dundalk | Wind | RCP4.5 | 2045 | 81.4677 | 87.7901 | 94.4559 | 101.103 | 107.7637
DundalkWind2050RCP4.5 | Dundalk | Wind | RCP4.5 | 2050 | 81.531 | 87.8641 | 94.5433 | 101.2016 | 107.8758
DundalkWind2055RCP4.5 | Dundalk | Wind | RCP4.5 | 2055 | 81.5862 | 87.9235 | 94.6072 | 101.27 | 107.9487
DundalkWind2060RCP4.5 | Dundalk | Wind | RCP4.5 | 2060 | 81.6414 | 87.983 | 94.6712 | 101.3384 | 108.0216
DundalkWind2065RCP4.5 | Dundalk | Wind | RCP4.5 | 2065 | 81.6966 | 88.0424 | 94.7351 | 101.4068 | 108.0944
DundalkWind2070RCP4.5 | Dundalk | Wind | RCP4.5 | 2070 | 81.7518 | 88.1019 | 94.799 | 101.4752 | 108.1673
DundalkWind2075RCP4.5 | Dundalk | Wind | RCP4.5 | 2075 | 81.8207 | 88.1951 | 94.9243 | 101.6294 | 108.3477
DundalkWind2080RCP4.5 | Dundalk | Wind | RCP4.5 | 2080 | 81.8897 | 88.2884 | 95.0497 | 101.7836 | 108.5281
DundalkWind2085RCP4.5 | Dundalk | Wind | RCP4.5 | 2085 | 81.9587 | 88.3816 | 95.175 | 101.9378 | 108.7085
DundalkWind2090RCP4.5 | Dundalk | Wind | RCP4.5 | 2090 | 82.0277 | 88.4749 | 95.3003 | 102.0921 | 108.8888
DundalkWind2095RCP4.5 | Dundalk | Wind | RCP4.5 | 2095 | 82.0967 | 88.5681 | 95.4257 | 102.2463 | 109.0692
DundalkWind2100RCP4.5 | Dundalk | Wind | RCP4.5 | 2100 | 82.1657 | 88.6614 | 95.551 | 102.4005 | 109.2496
DundalkWind2023RCP6.0 | Dundalk | Wind | RCP6.0 | 2023 | 81.4271 | 87.7172 | 94.3384 | 100.9521 | 107.5672
DundalkWind2025RCP6.0 | Dundalk | Wind | RCP6.0 | 2025 | 81.4352 | 87.7318 | 94.3619 | 100.9823 | 107.6065
DundalkWind2030RCP6.0 | Dundalk | Wind | RCP6.0 | 2030 | 81.4433 | 87.7464 | 94.3854 | 101.0125 | 107.6458
DundalkWind2035RCP6.0 | Dundalk | Wind | RCP6.0 | 2035 | 81.4514 | 87.7609 | 94.4089 | 101.0427 | 107.6851
DundalkWind2040RCP6.0 | Dundalk | Wind | RCP6.0 | 2040 | 81.4596 | 87.7755 | 94.4324 | 101.0728 | 107.7244
DundalkWind2045RCP6.0 | Dundalk | Wind | RCP6.0 | 2045 | 81.4677 | 87.7901 | 94.4559 | 101.103 | 107.7637
DundalkWind2050RCP6.0 | Dundalk | Wind | RCP6.0 | 2050 | 81.531 | 87.8641 | 94.5433 | 101.2016 | 107.8758
DundalkWind2055RCP6.0 | Dundalk | Wind | RCP6.0 | 2055 | 81.5862 | 87.9235 | 94.6072 | 101.27 | 107.9487
DundalkWind2060RCP6.0 | Dundalk | Wind | RCP6.0 | 2060 | 81.6414 | 87.983 | 94.6712 | 101.3384 | 108.0216
DundalkWind2065RCP6.0 | Dundalk | Wind | RCP6.0 | 2065 | 81.6966 | 88.0424 | 94.7351 | 101.4068 | 108.0944
DundalkWind2070RCP6.0 | Dundalk | Wind | RCP6.0 | 2070 | 81.7518 | 88.1019 | 94.799 | 101.4752 | 108.1673
DundalkWind2075RCP6.0 | Dundalk | Wind | RCP6.0 | 2075 | 81.8552 | 88.2417 | 94.987 | 101.7065 | 108.4379
DundalkWind2080RCP6.0 | Dundalk | Wind | RCP6.0 | 2080 | 81.9587 | 88.3816 | 95.175 | 101.9378 | 108.7085
DundalkWind2085RCP6.0 | Dundalk | Wind | RCP6.0 | 2085 | 82.0622 | 88.5215 | 95.363 | 102.1692 | 108.979
DundalkWind2090RCP6.0 | Dundalk | Wind | RCP6.0 | 2090 | 82.5526 | 89.1393 | 96.1369 | 103.0811 | 110.0247
DundalkWind2095RCP6.0 | Dundalk | Wind | RCP6.0 | 2095 | 82.9395 | 89.6172 | 96.7229 | 103.7617 | 110.7999
DundalkWind2100RCP6.0 | Dundalk | Wind | RCP6.0 | 2100 | 83.3264 | 90.0951 | 97.3088 | 104.4423 | 111.575
DundalkWind2023RCP8.5 | Dundalk | Wind | RCP8.5 | 2023 | 81.4271 | 87.7172 | 94.3384 | 100.9521 | 107.5672
DundalkWind2025RCP8.5 | Dundalk | Wind | RCP8.5 | 2025 | 81.4433 | 87.7464 | 94.3854 | 101.0125 | 107.6458
DundalkWind2030RCP8.5 | Dundalk | Wind | RCP8.5 | 2030 | 81.4596 | 87.7755 | 94.4324 | 101.0728 | 107.7244
DundalkWind2035RCP8.5 | Dundalk | Wind | RCP8.5 | 2035 | 81.4758 | 87.8046 | 94.4794 | 101.1332 | 107.803
DundalkWind2040RCP8.5 | Dundalk | Wind | RCP8.5 | 2040 | 81.5678 | 87.9037 | 94.5859 | 101.2472 | 107.9244
DundalkWind2045RCP8.5 | Dundalk | Wind | RCP8.5 | 2045 | 81.6598 | 88.0028 | 94.6925 | 101.3612 | 108.0459
DundalkWind2050RCP8.5 | Dundalk | Wind | RCP8.5 | 2050 | 81.8897 | 88.2884 | 95.0497 | 101.7836 | 108.5281
DundalkWind2055RCP8.5 | Dundalk | Wind | RCP8.5 | 2055 | 82.0277 | 88.4749 | 95.3003 | 102.0921 | 108.8888
DundalkWind2060RCP8.5 | Dundalk | Wind | RCP8.5 | 2060 | 82.5526 | 89.1393 | 96.1369 | 103.0811 | 110.0247
DundalkWind2065RCP8.5 | Dundalk | Wind | RCP8.5 | 2065 | 82.9395 | 89.6172 | 96.7229 | 103.7617 | 110.7999
DundalkWind2070RCP8.5 | Dundalk | Wind | RCP8.5 | 2070 | 83.5401 | 90.369 | 97.6597 | 104.8513 | 112.0501
DundalkWind2075RCP8.5 | Dundalk | Wind | RCP8.5 | 2075 | 83.7539 | 90.6429 | 98.0107 | 105.2603 | 112.5251
DundalkWind2080RCP8.5 | Dundalk | Wind | RCP8.5 | 2080 | 83.9676 | 90.9168 | 98.3616 | 105.6693 | 113.0002
DundalkWind2085RCP8.5 | Dundalk | Wind | RCP8.5 | 2085 | 84.1462 | 91.1354 | 98.6295 | 105.9811 | 113.3592
DundalkWind2090RCP8.5 | Dundalk | Wind | RCP8.5 | 2090 | 84.3248 | 91.3539 | 98.8974 | 106.2929 | 113.7182
DundalkWind2095RCP8.5 | Dundalk | Wind | RCP8.5 | 2095 | 84.3248 | 91.3539 | 98.8974 | 106.2929 | 113.7182
DundalkWind2100RCP8.5 | Dundalk | Wind | RCP8.5 | 2100 | 84.3248 | 91.3539 | 98.8974 | 106.2929 | 113.7182
DunnvilleIce Accretion2023RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
DunnvilleIce Accretion2025RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2025 | 21.9182 | 26.3121 | 31.8773 | 36.1299 | 40.3738
DunnvilleIce Accretion2030RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2030 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
DunnvilleIce Accretion2035RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2035 | 21.7104 | 26.0819 | 31.632 | 35.8526 | 40.0781
DunnvilleIce Accretion2040RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2040 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
DunnvilleIce Accretion2045RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2045 | 21.5026 | 25.8517 | 31.3867 | 35.5754 | 39.7824
DunnvilleIce Accretion2050RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2050 | 20.9221 | 25.2001 | 30.6368 | 34.7425 | 38.8765
DunnvilleIce Accretion2055RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2055 | 20.4456 | 24.6636 | 30.0096 | 34.0483 | 38.1185
DunnvilleIce Accretion2060RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2060 | 19.9691 | 24.1271 | 29.3824 | 33.354 | 37.3605
DunnvilleIce Accretion2065RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2065 | 19.4926 | 23.5906 | 28.7552 | 32.6597 | 36.6025
DunnvilleIce Accretion2070RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2070 | 19.0161 | 23.0541 | 28.128 | 31.9654 | 35.8445
DunnvilleIce Accretion2075RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2075 | 18.8379 | 22.8682 | 27.9307 | 31.7605 | 35.6294
DunnvilleIce Accretion2080RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2080 | 18.6598 | 22.6822 | 27.7333 | 31.5556 | 35.4144
DunnvilleIce Accretion2085RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2085 | 18.4817 | 22.4963 | 27.536 | 31.3507 | 35.1994
DunnvilleIce Accretion2090RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2090 | 18.3035 | 22.3104 | 27.3387 | 31.1458 | 34.9843
DunnvilleIce Accretion2095RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2095 | 18.1254 | 22.1245 | 27.1413 | 30.9409 | 34.7693
DunnvilleIce Accretion2100RCP4.5 | Dunnville | Ice Accretion | RCP4.5 | 2100 | 17.9473 | 21.9386 | 26.944 | 30.736 | 34.5542
DunnvilleIce Accretion2023RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
DunnvilleIce Accretion2025RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2025 | 21.9182 | 26.3121 | 31.8773 | 36.1299 | 40.3738
DunnvilleIce Accretion2030RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2030 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
DunnvilleIce Accretion2035RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2035 | 21.7104 | 26.0819 | 31.632 | 35.8526 | 40.0781
DunnvilleIce Accretion2040RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2040 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
DunnvilleIce Accretion2045RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2045 | 21.5026 | 25.8517 | 31.3867 | 35.5754 | 39.7824
DunnvilleIce Accretion2050RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2050 | 20.9221 | 25.2001 | 30.6368 | 34.7425 | 38.8765
DunnvilleIce Accretion2055RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2055 | 20.4456 | 24.6636 | 30.0096 | 34.0483 | 38.1185
DunnvilleIce Accretion2060RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2060 | 19.9691 | 24.1271 | 29.3824 | 33.354 | 37.3605
DunnvilleIce Accretion2065RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2065 | 19.4926 | 23.5906 | 28.7552 | 32.6597 | 36.6025
DunnvilleIce Accretion2070RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2070 | 19.0161 | 23.0541 | 28.128 | 31.9654 | 35.8445
DunnvilleIce Accretion2075RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2075 | 18.7489 | 22.7752 | 27.832 | 31.6581 | 35.5219
DunnvilleIce Accretion2080RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2080 | 18.4817 | 22.4963 | 27.536 | 31.3507 | 35.1994
DunnvilleIce Accretion2085RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2085 | 18.2145 | 22.2174 | 27.24 | 31.0434 | 34.8768
DunnvilleIce Accretion2090RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2090 | 17.2199 | 21.1063 | 25.9733 | 29.6633 | 33.3581
DunnvilleIce Accretion2095RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2095 | 16.4925 | 20.2741 | 25.0027 | 28.5905 | 32.1619
DunnvilleIce Accretion2100RCP6.0 | Dunnville | Ice Accretion | RCP6.0 | 2100 | 15.7651 | 19.4419 | 24.032 | 27.5178 | 30.9658
DunnvilleIce Accretion2023RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
DunnvilleIce Accretion2025RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2025 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
DunnvilleIce Accretion2030RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2030 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
DunnvilleIce Accretion2035RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2035 | 21.3987 | 25.7366 | 31.264 | 35.4368 | 39.6346
DunnvilleIce Accretion2040RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2040 | 20.6045 | 24.8425 | 30.2187 | 34.2797 | 38.3712
DunnvilleIce Accretion2045RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2045 | 19.8103 | 23.9483 | 29.1733 | 33.1226 | 37.1078
DunnvilleIce Accretion2050RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2050 | 18.6598 | 22.6822 | 27.7333 | 31.5556 | 35.4144
DunnvilleIce Accretion2055RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2055 | 18.3035 | 22.3104 | 27.3387 | 31.1458 | 34.9843
DunnvilleIce Accretion2060RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2060 | 17.2199 | 21.1063 | 25.9733 | 29.6633 | 33.3581
DunnvilleIce Accretion2065RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2065 | 16.4925 | 20.2741 | 25.0027 | 28.5905 | 32.1619
DunnvilleIce Accretion2070RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2070 | 15.4014 | 19.0258 | 23.5627 | 26.9995 | 30.4013
DunnvilleIce Accretion2075RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2075 | 15.0377 | 18.6097 | 23.0933 | 26.4812 | 29.8368
DunnvilleIce Accretion2080RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2080 | 14.674 | 18.1936 | 22.624 | 25.9629 | 29.2723
DunnvilleIce Accretion2085RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2085 | 13.8501 | 17.2242 | 21.456 | 24.643 | 27.8006
DunnvilleIce Accretion2090RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2090 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
DunnvilleIce Accretion2095RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2095 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
DunnvilleIce Accretion2100RCP8.5 | Dunnville | Ice Accretion | RCP8.5 | 2100 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
DunnvilleWind2023RCP4.5 | Dunnville | Wind | RCP4.5 | 2023 | 88.9824 | 96.0647 | 103.581 | 111.05 | 118.5126
DunnvilleWind2025RCP4.5 | Dunnville | Wind | RCP4.5 | 2025 | 88.953 | 96.0347 | 103.5487 | 111.0154 | 118.4758
DunnvilleWind2030RCP4.5 | Dunnville | Wind | RCP4.5 | 2030 | 88.9237 | 96.0046 | 103.5164 | 110.9808 | 118.4389
DunnvilleWind2035RCP4.5 | Dunnville | Wind | RCP4.5 | 2035 | 88.8943 | 95.9746 | 103.4841 | 110.9463 | 118.4021
DunnvilleWind2040RCP4.5 | Dunnville | Wind | RCP4.5 | 2040 | 88.8649 | 95.9446 | 103.4518 | 110.9117 | 118.3653
DunnvilleWind2045RCP4.5 | Dunnville | Wind | RCP4.5 | 2045 | 88.8356 | 95.9145 | 103.4195 | 110.8771 | 118.3285
DunnvilleWind2050RCP4.5 | Dunnville | Wind | RCP4.5 | 2050 | 88.8644 | 95.9585 | 103.4831 | 110.9539 | 118.4219
DunnvilleWind2055RCP4.5 | Dunnville | Wind | RCP4.5 | 2055 | 88.9225 | 96.0325 | 103.579 | 111.0652 | 118.5521
DunnvilleWind2060RCP4.5 | Dunnville | Wind | RCP4.5 | 2060 | 88.9806 | 96.1065 | 103.6748 | 111.1766 | 118.6823
DunnvilleWind2065RCP4.5 | Dunnville | Wind | RCP4.5 | 2065 | 89.0388 | 96.1805 | 103.7707 | 111.2879 | 118.8126
DunnvilleWind2070RCP4.5 | Dunnville | Wind | RCP4.5 | 2070 | 89.0969 | 96.2544 | 103.8666 | 111.3992 | 118.9428
DunnvilleWind2075RCP4.5 | Dunnville | Wind | RCP4.5 | 2075 | 89.1791 | 96.3699 | 104.0247 | 111.592 | 119.1734
DunnvilleWind2080RCP4.5 | Dunnville | Wind | RCP4.5 | 2080 | 89.2613 | 96.4853 | 104.1828 | 111.7848 | 119.4041
DunnvilleWind2085RCP4.5 | Dunnville | Wind | RCP4.5 | 2085 | 89.3435 | 96.6007 | 104.3409 | 111.9776 | 119.6347
DunnvilleWind2090RCP4.5 | Dunnville | Wind | RCP4.5 | 2090 | 89.4257 | 96.7161 | 104.499 | 112.1705 | 119.8653
DunnvilleWind2095RCP4.5 | Dunnville | Wind | RCP4.5 | 2095 | 89.5079 | 96.8315 | 104.6571 | 112.3633 | 120.0959
DunnvilleWind2100RCP4.5 | Dunnville | Wind | RCP4.5 | 2100 | 89.5901 | 96.9469 | 104.8152 | 112.5561 | 120.3265
DunnvilleWind2023RCP6.0 | Dunnville | Wind | RCP6.0 | 2023 | 88.9824 | 96.0647 | 103.581 | 111.05 | 118.5126
DunnvilleWind2025RCP6.0 | Dunnville | Wind | RCP6.0 | 2025 | 88.953 | 96.0347 | 103.5487 | 111.0154 | 118.4758
DunnvilleWind2030RCP6.0 | Dunnville | Wind | RCP6.0 | 2030 | 88.9237 | 96.0046 | 103.5164 | 110.9808 | 118.4389
DunnvilleWind2035RCP6.0 | Dunnville | Wind | RCP6.0 | 2035 | 88.8943 | 95.9746 | 103.4841 | 110.9463 | 118.4021
DunnvilleWind2040RCP6.0 | Dunnville | Wind | RCP6.0 | 2040 | 88.8649 | 95.9446 | 103.4518 | 110.9117 | 118.3653
DunnvilleWind2045RCP6.0 | Dunnville | Wind | RCP6.0 | 2045 | 88.8356 | 95.9145 | 103.4195 | 110.8771 | 118.3285
DunnvilleWind2050RCP6.0 | Dunnville | Wind | RCP6.0 | 2050 | 88.8644 | 95.9585 | 103.4831 | 110.9539 | 118.4219
DunnvilleWind2055RCP6.0 | Dunnville | Wind | RCP6.0 | 2055 | 88.9225 | 96.0325 | 103.579 | 111.0652 | 118.5521
DunnvilleWind2060RCP6.0 | Dunnville | Wind | RCP6.0 | 2060 | 88.9806 | 96.1065 | 103.6748 | 111.1766 | 118.6823
DunnvilleWind2065RCP6.0 | Dunnville | Wind | RCP6.0 | 2065 | 89.0388 | 96.1805 | 103.7707 | 111.2879 | 118.8126
DunnvilleWind2070RCP6.0 | Dunnville | Wind | RCP6.0 | 2070 | 89.0969 | 96.2544 | 103.8666 | 111.3992 | 118.9428
DunnvilleWind2075RCP6.0 | Dunnville | Wind | RCP6.0 | 2075 | 89.2202 | 96.4276 | 104.1038 | 111.6884 | 119.2887
DunnvilleWind2080RCP6.0 | Dunnville | Wind | RCP6.0 | 2080 | 89.3435 | 96.6007 | 104.3409 | 111.9776 | 119.6347
DunnvilleWind2085RCP6.0 | Dunnville | Wind | RCP6.0 | 2085 | 89.4668 | 96.7738 | 104.5781 | 112.2669 | 119.9806
DunnvilleWind2090RCP6.0 | Dunnville | Wind | RCP6.0 | 2090 | 89.778 | 97.1872 | 105.1178 | 112.9162 | 120.7452
DunnvilleWind2095RCP6.0 | Dunnville | Wind | RCP6.0 | 2095 | 89.9659 | 97.4275 | 105.4204 | 113.2764 | 121.1638
DunnvilleWind2100RCP6.0 | Dunnville | Wind | RCP6.0 | 2100 | 90.1538 | 97.6679 | 105.723 | 113.6366 | 121.5824
DunnvilleWind2023RCP8.5 | Dunnville | Wind | RCP8.5 | 2023 | 88.9824 | 96.0647 | 103.581 | 111.05 | 118.5126
DunnvilleWind2025RCP8.5 | Dunnville | Wind | RCP8.5 | 2025 | 88.9237 | 96.0046 | 103.5164 | 110.9808 | 118.4389
DunnvilleWind2030RCP8.5 | Dunnville | Wind | RCP8.5 | 2030 | 88.8649 | 95.9446 | 103.4518 | 110.9117 | 118.3653
DunnvilleWind2035RCP8.5 | Dunnville | Wind | RCP8.5 | 2035 | 88.8062 | 95.8845 | 103.3872 | 110.8426 | 118.2916
DunnvilleWind2040RCP8.5 | Dunnville | Wind | RCP8.5 | 2040 | 88.9031 | 96.0078 | 103.547 | 111.0281 | 118.5087
DunnvilleWind2045RCP8.5 | Dunnville | Wind | RCP8.5 | 2045 | 89 | 96.1311 | 103.7068 | 111.2137 | 118.7258
DunnvilleWind2050RCP8.5 | Dunnville | Wind | RCP8.5 | 2050 | 89.2613 | 96.4853 | 104.1828 | 111.7848 | 119.4041
DunnvilleWind2055RCP8.5 | Dunnville | Wind | RCP8.5 | 2055 | 89.4257 | 96.7161 | 104.499 | 112.1705 | 119.8653
DunnvilleWind2060RCP8.5 | Dunnville | Wind | RCP8.5 | 2060 | 89.778 | 97.1872 | 105.1178 | 112.9162 | 120.7452
DunnvilleWind2065RCP8.5 | Dunnville | Wind | RCP8.5 | 2065 | 89.9659 | 97.4275 | 105.4204 | 113.2764 | 121.1638
DunnvilleWind2070RCP8.5 | Dunnville | Wind | RCP8.5 | 2070 | 90.2154 | 97.7722 | 105.8896 | 113.8548 | 121.8459
DunnvilleWind2075RCP8.5 | Dunnville | Wind | RCP8.5 | 2075 | 90.2771 | 97.8765 | 106.0562 | 114.0731 | 122.1095
DunnvilleWind2080RCP8.5 | Dunnville | Wind | RCP8.5 | 2080 | 90.3387 | 97.9809 | 106.2228 | 114.2914 | 122.3731
DunnvilleWind2085RCP8.5 | Dunnville | Wind | RCP8.5 | 2085 | 90.4048 | 98.09 | 106.3809 | 114.4879 | 122.6173
DunnvilleWind2090RCP8.5 | Dunnville | Wind | RCP8.5 | 2090 | 90.4709 | 98.1991 | 106.539 | 114.6843 | 122.8614
DunnvilleWind2095RCP8.5 | Dunnville | Wind | RCP8.5 | 2095 | 90.4709 | 98.1991 | 106.539 | 114.6843 | 122.8614
DunnvilleWind2100RCP8.5 | Dunnville | Wind | RCP8.5 | 2100 | 90.4709 | 98.1991 | 106.539 | 114.6843 | 122.8614
DurhamIce Accretion2023RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2023 | 15.2933 | 18.333 | 22.198 | 25.1335 | 28.0804
DurhamIce Accretion2025RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2025 | 15.2984 | 18.3543 | 22.231 | 25.179 | 28.1404
DurhamIce Accretion2030RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2030 | 15.3035 | 18.3756 | 22.264 | 25.2246 | 28.2005
DurhamIce Accretion2035RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2035 | 15.3086 | 18.3969 | 22.297 | 25.2702 | 28.2605
DurhamIce Accretion2040RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2040 | 15.3137 | 18.4183 | 22.33 | 25.3158 | 28.3206
DurhamIce Accretion2045RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2045 | 15.3188 | 18.4396 | 22.363 | 25.3613 | 28.3807
DurhamIce Accretion2050RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2050 | 15.3178 | 18.4718 | 22.4356 | 25.4666 | 28.5183
DurhamIce Accretion2055RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2055 | 15.3117 | 18.4828 | 22.4752 | 25.5262 | 28.596
DurhamIce Accretion2060RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2060 | 15.3056 | 18.4937 | 22.5148 | 25.5859 | 28.6736
DurhamIce Accretion2065RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2065 | 15.2994 | 18.5047 | 22.5544 | 25.6456 | 28.7512
DurhamIce Accretion2070RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2070 | 15.2933 | 18.5156 | 22.594 | 25.7052 | 28.8288
DurhamIce Accretion2075RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2075 | 15.227 | 18.4609 | 22.5573 | 25.6762 | 28.8103
DurhamIce Accretion2080RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2080 | 15.1606 | 18.4061 | 22.5207 | 25.6472 | 28.7918
DurhamIce Accretion2085RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2085 | 15.0943 | 18.3513 | 22.484 | 25.6182 | 28.7734
DurhamIce Accretion2090RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2090 | 15.028 | 18.2965 | 22.4473 | 25.5892 | 28.7549
DurhamIce Accretion2095RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2095 | 14.9616 | 18.2417 | 22.4107 | 25.5602 | 28.7364
DurhamIce Accretion2100RCP4.5 | Durham | Ice Accretion | RCP4.5 | 2100 | 14.8953 | 18.187 | 22.374 | 25.5312 | 28.7179
DurhamIce Accretion2023RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2023 | 15.2933 | 18.333 | 22.198 | 25.1335 | 28.0804
DurhamIce Accretion2025RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2025 | 15.2984 | 18.3543 | 22.231 | 25.179 | 28.1404
DurhamIce Accretion2030RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2030 | 15.3035 | 18.3756 | 22.264 | 25.2246 | 28.2005
DurhamIce Accretion2035RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2035 | 15.3086 | 18.3969 | 22.297 | 25.2702 | 28.2605
DurhamIce Accretion2040RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2040 | 15.3137 | 18.4183 | 22.33 | 25.3158 | 28.3206
DurhamIce Accretion2045RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2045 | 15.3188 | 18.4396 | 22.363 | 25.3613 | 28.3807
DurhamIce Accretion2050RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2050 | 15.3178 | 18.4718 | 22.4356 | 25.4666 | 28.5183
DurhamIce Accretion2055RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2055 | 15.3117 | 18.4828 | 22.4752 | 25.5262 | 28.596
DurhamIce Accretion2060RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2060 | 15.3056 | 18.4937 | 22.5148 | 25.5859 | 28.6736
DurhamIce Accretion2065RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2065 | 15.2994 | 18.5047 | 22.5544 | 25.6456 | 28.7512
DurhamIce Accretion2070RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2070 | 15.2933 | 18.5156 | 22.594 | 25.7052 | 28.8288
DurhamIce Accretion2075RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2075 | 15.1938 | 18.4335 | 22.539 | 25.6617 | 28.8011
DurhamIce Accretion2080RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2080 | 15.0943 | 18.3513 | 22.484 | 25.6182 | 28.7734
DurhamIce Accretion2085RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2085 | 14.9948 | 18.2691 | 22.429 | 25.5747 | 28.7456
DurhamIce Accretion2090RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2090 | 14.6401 | 17.9191 | 22.0733 | 25.2163 | 28.376
DurhamIce Accretion2095RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2095 | 14.385 | 17.6513 | 21.7727 | 24.9014 | 28.0342
DurhamIce Accretion2100RCP6.0 | Durham | Ice Accretion | RCP6.0 | 2100 | 14.1299 | 17.3835 | 21.472 | 24.5865 | 27.6923
DurhamIce Accretion2023RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2023 | 15.2933 | 18.333 | 22.198 | 25.1335 | 28.0804
DurhamIce Accretion2025RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2025 | 15.3035 | 18.3756 | 22.264 | 25.2246 | 28.2005
DurhamIce Accretion2030RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2030 | 15.3137 | 18.4183 | 22.33 | 25.3158 | 28.3206
DurhamIce Accretion2035RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2035 | 15.3239 | 18.4609 | 22.396 | 25.4069 | 28.4407
DurhamIce Accretion2040RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2040 | 15.3137 | 18.4791 | 22.462 | 25.5064 | 28.5701
DurhamIce Accretion2045RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2045 | 15.3035 | 18.4974 | 22.528 | 25.6058 | 28.6994
DurhamIce Accretion2050RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2050 | 15.1606 | 18.4061 | 22.5207 | 25.6472 | 28.7918
DurhamIce Accretion2055RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2055 | 15.028 | 18.2965 | 22.4473 | 25.5892 | 28.7549
DurhamIce Accretion2060RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2060 | 14.6401 | 17.9191 | 22.0733 | 25.2163 | 28.376
DurhamIce Accretion2065RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2065 | 14.385 | 17.6513 | 21.7727 | 24.9014 | 28.0342
DurhamIce Accretion2070RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2070 | 13.7114 | 16.9088 | 20.9367 | 23.9982 | 27.0547
DurhamIce Accretion2075RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2075 | 13.293 | 16.434 | 20.4013 | 23.4098 | 26.4172
DurhamIce Accretion2080RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2080 | 12.8745 | 15.9592 | 19.866 | 22.8215 | 25.7796
DurhamIce Accretion2085RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2085 | 12.4536 | 15.4936 | 19.338 | 22.2497 | 25.1698
DurhamIce Accretion2090RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2090 | 12.0326 | 15.028 | 18.81 | 21.6779 | 24.5599
DurhamIce Accretion2095RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2095 | 12.0326 | 15.028 | 18.81 | 21.6779 | 24.5599
DurhamIce Accretion2100RCP8.5 | Durham | Ice Accretion | RCP8.5 | 2100 | 12.0326 | 15.028 | 18.81 | 21.6779 | 24.5599
DurhamWind2023RCP4.5 | Durham | Wind | RCP4.5 | 2023 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2506
DurhamWind2025RCP4.5 | Durham | Wind | RCP4.5 | 2025 | 85.4139 | 92.1425 | 99.2626 | 106.3385 | 113.42
DurhamWind2030RCP4.5 | Durham | Wind | RCP4.5 | 2030 | 85.4957 | 92.2428 | 99.3883 | 106.4853 | 113.5894
DurhamWind2035RCP4.5 | Durham | Wind | RCP4.5 | 2035 | 85.5775 | 92.343 | 99.5141 | 106.6321 | 113.7589
DurhamWind2040RCP4.5 | Durham | Wind | RCP4.5 | 2040 | 85.6593 | 92.4433 | 99.6399 | 106.7789 | 113.9283
DurhamWind2045RCP4.5 | Durham | Wind | RCP4.5 | 2045 | 85.7411 | 92.5436 | 99.7656 | 106.9257 | 114.0978
DurhamWind2050RCP4.5 | Durham | Wind | RCP4.5 | 2050 | 85.8364 | 92.6566 | 99.9012 | 107.0809 | 114.2739
DurhamWind2055RCP4.5 | Durham | Wind | RCP4.5 | 2055 | 85.85 | 92.6693 | 99.911 | 107.0893 | 114.2806
DurhamWind2060RCP4.5 | Durham | Wind | RCP4.5 | 2060 | 85.8635 | 92.6821 | 99.9208 | 107.0977 | 114.2873
DurhamWind2065RCP4.5 | Durham | Wind | RCP4.5 | 2065 | 85.8771 | 92.6948 | 99.9306 | 107.1061 | 114.294
DurhamWind2070RCP4.5 | Durham | Wind | RCP4.5 | 2070 | 85.8906 | 92.7076 | 99.9404 | 107.1145 | 114.3007
DurhamWind2075RCP4.5 | Durham | Wind | RCP4.5 | 2075 | 85.9738 | 92.8155 | 100.0792 | 107.2805 | 114.4925
DurhamWind2080RCP4.5 | Durham | Wind | RCP4.5 | 2080 | 86.057 | 92.9233 | 100.2181 | 107.4465 | 114.6843
DurhamWind2085RCP4.5 | Durham | Wind | RCP4.5 | 2085 | 86.1402 | 93.0312 | 100.3569 | 107.6126 | 114.8761
DurhamWind2090RCP4.5 | Durham | Wind | RCP4.5 | 2090 | 86.2234 | 93.139 | 100.4957 | 107.7786 | 115.0679
DurhamWind2095RCP4.5 | Durham | Wind | RCP4.5 | 2095 | 86.3067 | 93.2469 | 100.6346 | 107.9446 | 115.2597
DurhamWind2100RCP4.5 | Durham | Wind | RCP4.5 | 2100 | 86.3899 | 93.3547 | 100.7734 | 108.1107 | 115.4514
DurhamWind2023RCP6.0 | Durham | Wind | RCP6.0 | 2023 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2506
DurhamWind2025RCP6.0 | Durham | Wind | RCP6.0 | 2025 | 85.4139 | 92.1425 | 99.2626 | 106.3385 | 113.42
DurhamWind2030RCP6.0 | Durham | Wind | RCP6.0 | 2030 | 85.4957 | 92.2428 | 99.3883 | 106.4853 | 113.5894
DurhamWind2035RCP6.0 | Durham | Wind | RCP6.0 | 2035 | 85.5775 | 92.343 | 99.5141 | 106.6321 | 113.7589
DurhamWind2040RCP6.0 | Durham | Wind | RCP6.0 | 2040 | 85.6593 | 92.4433 | 99.6399 | 106.7789 | 113.9283
DurhamWind2045RCP6.0 | Durham | Wind | RCP6.0 | 2045 | 85.7411 | 92.5436 | 99.7656 | 106.9257 | 114.0978
DurhamWind2050RCP6.0 | Durham | Wind | RCP6.0 | 2050 | 85.8364 | 92.6566 | 99.9012 | 107.0809 | 114.2739
DurhamWind2055RCP6.0 | Durham | Wind | RCP6.0 | 2055 | 85.85 | 92.6693 | 99.911 | 107.0893 | 114.2806
DurhamWind2060RCP6.0 | Durham | Wind | RCP6.0 | 2060 | 85.8635 | 92.6821 | 99.9208 | 107.0977 | 114.2873
DurhamWind2065RCP6.0 | Durham | Wind | RCP6.0 | 2065 | 85.8771 | 92.6948 | 99.9306 | 107.1061 | 114.294
DurhamWind2070RCP6.0 | Durham | Wind | RCP6.0 | 2070 | 85.8906 | 92.7076 | 99.9404 | 107.1145 | 114.3007
DurhamWind2075RCP6.0 | Durham | Wind | RCP6.0 | 2075 | 86.0154 | 92.8694 | 100.1487 | 107.3635 | 114.5884
DurhamWind2080RCP6.0 | Durham | Wind | RCP6.0 | 2080 | 86.1402 | 93.0312 | 100.3569 | 107.6126 | 114.8761
DurhamWind2085RCP6.0 | Durham | Wind | RCP6.0 | 2085 | 86.265 | 93.1929 | 100.5652 | 107.8616 | 115.1638
DurhamWind2090RCP6.0 | Durham | Wind | RCP6.0 | 2090 | 86.8017 | 93.8712 | 101.4169 | 108.8657 | 116.3229
DurhamWind2095RCP6.0 | Durham | Wind | RCP6.0 | 2095 | 87.2135 | 94.3876 | 102.0605 | 109.6206 | 117.1943
DurhamWind2100RCP6.0 | Durham | Wind | RCP6.0 | 2100 | 87.6253 | 94.9041 | 102.704 | 110.3756 | 118.0657
DurhamWind2023RCP8.5 | Durham | Wind | RCP8.5 | 2023 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2506
DurhamWind2025RCP8.5 | Durham | Wind | RCP8.5 | 2025 | 85.4957 | 92.2428 | 99.3883 | 106.4853 | 113.5894
DurhamWind2030RCP8.5 | Durham | Wind | RCP8.5 | 2030 | 85.6593 | 92.4433 | 99.6399 | 106.7789 | 113.9283
DurhamWind2035RCP8.5 | Durham | Wind | RCP8.5 | 2035 | 85.8229 | 92.6438 | 99.8914 | 107.0725 | 114.2672
DurhamWind2040RCP8.5 | Durham | Wind | RCP8.5 | 2040 | 85.8455 | 92.6651 | 99.9077 | 107.0865 | 114.2784
DurhamWind2045RCP8.5 | Durham | Wind | RCP8.5 | 2045 | 85.868 | 92.6863 | 99.9241 | 107.1005 | 114.2896
DurhamWind2050RCP8.5 | Durham | Wind | RCP8.5 | 2050 | 86.057 | 92.9233 | 100.2181 | 107.4465 | 114.6843
DurhamWind2055RCP8.5 | Durham | Wind | RCP8.5 | 2055 | 86.2234 | 93.139 | 100.4957 | 107.7786 | 115.0679
DurhamWind2060RCP8.5 | Durham | Wind | RCP8.5 | 2060 | 86.8017 | 93.8712 | 101.4169 | 108.8657 | 116.3229
DurhamWind2065RCP8.5 | Durham | Wind | RCP8.5 | 2065 | 87.2135 | 94.3876 | 102.0605 | 109.6206 | 117.1943
DurhamWind2070RCP8.5 | Durham | Wind | RCP8.5 | 2070 | 87.8397 | 95.1653 | 103.0241 | 110.7461 | 118.4865
DurhamWind2075RCP8.5 | Durham | Wind | RCP8.5 | 2075 | 88.0541 | 95.4266 | 103.3443 | 111.1166 | 118.9073
DurhamWind2080RCP8.5 | Durham | Wind | RCP8.5 | 2080 | 88.2685 | 95.6879 | 103.6644 | 111.4872 | 119.3281
DurhamWind2085RCP8.5 | Durham | Wind | RCP8.5 | 2085 | 88.2896 | 95.697 | 103.6644 | 111.4714 | 119.3058
DurhamWind2090RCP8.5 | Durham | Wind | RCP8.5 | 2090 | 88.3108 | 95.7061 | 103.6644 | 111.4557 | 119.2834
DurhamWind2095RCP8.5 | Durham | Wind | RCP8.5 | 2095 | 88.3108 | 95.7061 | 103.6644 | 111.4557 | 119.2834
DurhamWind2100RCP8.5 | Durham | Wind | RCP8.5 | 2100 | 88.3108 | 95.7061 | 103.6644 | 111.4557 | 119.2834
DuttonIce Accretion2023RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2023 | 20.5831 | 24.7008 | 29.91 | 33.8661 | 37.8378
DuttonIce Accretion2025RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2025 | 20.4614 | 24.568 | 29.765 | 33.7135 | 37.674
DuttonIce Accretion2030RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2030 | 20.3396 | 24.4352 | 29.62 | 33.561 | 37.5102
DuttonIce Accretion2035RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2035 | 20.2178 | 24.3024 | 29.475 | 33.4085 | 37.3464
DuttonIce Accretion2040RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2040 | 20.096 | 24.1696 | 29.33 | 33.2559 | 37.1826
DuttonIce Accretion2045RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2045 | 19.9743 | 24.0368 | 29.185 | 33.1033 | 37.0188
DuttonIce Accretion2050RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2050 | 19.4642 | 23.4757 | 28.554 | 32.422 | 36.2804
DuttonIce Accretion2055RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2055 | 19.0759 | 23.0474 | 28.068 | 31.8931 | 35.7059
DuttonIce Accretion2060RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2060 | 18.6876 | 22.6192 | 27.582 | 31.3643 | 35.1313
DuttonIce Accretion2065RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2065 | 18.2994 | 22.1909 | 27.096 | 30.8354 | 34.5568
DuttonIce Accretion2070RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2070 | 17.9111 | 21.7626 | 26.61 | 30.3066 | 33.9822
DuttonIce Accretion2075RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2075 | 17.7754 | 21.6257 | 26.47 | 30.1597 | 33.831
DuttonIce Accretion2080RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2080 | 17.6397 | 21.4887 | 26.33 | 30.0128 | 33.6798
DuttonIce Accretion2085RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2085 | 17.504 | 21.3517 | 26.19 | 29.8659 | 33.5286
DuttonIce Accretion2090RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2090 | 17.3683 | 21.2148 | 26.05 | 29.719 | 33.3774
DuttonIce Accretion2095RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2095 | 17.2326 | 21.0778 | 25.91 | 29.5721 | 33.2262
DuttonIce Accretion2100RCP4.5 | Dutton | Ice Accretion | RCP4.5 | 2100 | 17.0969 | 20.9409 | 25.77 | 29.4252 | 33.075
DuttonIce Accretion2023RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2023 | 20.5831 | 24.7008 | 29.91 | 33.8661 | 37.8378
DuttonIce Accretion2025RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2025 | 20.4614 | 24.568 | 29.765 | 33.7135 | 37.674
DuttonIce Accretion2030RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2030 | 20.3396 | 24.4352 | 29.62 | 33.561 | 37.5102
DuttonIce Accretion2035RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2035 | 20.2178 | 24.3024 | 29.475 | 33.4085 | 37.3464
DuttonIce Accretion2040RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2040 | 20.096 | 24.1696 | 29.33 | 33.2559 | 37.1826
DuttonIce Accretion2045RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2045 | 19.9743 | 24.0368 | 29.185 | 33.1033 | 37.0188
DuttonIce Accretion2050RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2050 | 19.4642 | 23.4757 | 28.554 | 32.422 | 36.2804
DuttonIce Accretion2055RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2055 | 19.0759 | 23.0474 | 28.068 | 31.8931 | 35.7059
DuttonIce Accretion2060RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2060 | 18.6876 | 22.6192 | 27.582 | 31.3643 | 35.1313
DuttonIce Accretion2065RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2065 | 18.2994 | 22.1909 | 27.096 | 30.8354 | 34.5568
DuttonIce Accretion2070RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2070 | 17.9111 | 21.7626 | 26.61 | 30.3066 | 33.9822
DuttonIce Accretion2075RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2075 | 17.7075 | 21.5572 | 26.4 | 30.0862 | 33.7554
DuttonIce Accretion2080RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2080 | 17.504 | 21.3517 | 26.19 | 29.8659 | 33.5286
DuttonIce Accretion2085RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2085 | 17.3005 | 21.1463 | 25.98 | 29.6456 | 33.3018
DuttonIce Accretion2090RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2090 | 16.6098 | 20.3931 | 25.15 | 28.7472 | 32.3316
DuttonIce Accretion2095RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2095 | 16.1228 | 19.8453 | 24.53 | 28.0692 | 31.5882
DuttonIce Accretion2100RCP6.0 | Dutton | Ice Accretion | RCP6.0 | 2100 | 15.6357 | 19.2975 | 23.91 | 27.3912 | 30.8448
DuttonIce Accretion2023RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2023 | 20.5831 | 24.7008 | 29.91 | 33.8661 | 37.8378
DuttonIce Accretion2025RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2025 | 20.3396 | 24.4352 | 29.62 | 33.561 | 37.5102
DuttonIce Accretion2030RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2030 | 20.096 | 24.1696 | 29.33 | 33.2559 | 37.1826
DuttonIce Accretion2035RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2035 | 19.8525 | 23.904 | 29.04 | 32.9508 | 36.855
DuttonIce Accretion2040RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2040 | 19.2054 | 23.1902 | 28.23 | 32.0694 | 35.8974
DuttonIce Accretion2045RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2045 | 18.5582 | 22.4764 | 27.42 | 31.188 | 34.9398
DuttonIce Accretion2050RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2050 | 17.6397 | 21.4887 | 26.33 | 30.0128 | 33.6798
DuttonIce Accretion2055RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2055 | 17.3683 | 21.2148 | 26.05 | 29.719 | 33.3774
DuttonIce Accretion2060RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2060 | 16.6098 | 20.3931 | 25.15 | 28.7472 | 32.3316
DuttonIce Accretion2065RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2065 | 16.1228 | 19.8453 | 24.53 | 28.0692 | 31.5882
DuttonIce Accretion2070RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2070 | 15.3225 | 18.9655 | 23.55 | 26.9957 | 30.429
DuttonIce Accretion2075RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2075 | 15.0094 | 18.6335 | 23.19 | 26.6002 | 30.0132
DuttonIce Accretion2080RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2080 | 14.6963 | 18.3015 | 22.83 | 26.2047 | 29.5974
DuttonIce Accretion2085RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2085 | 13.7673 | 17.2059 | 21.51 | 24.73 | 27.9531
DuttonIce Accretion2090RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2090 | 12.8384 | 16.1103 | 20.19 | 23.2554 | 26.3088
DuttonIce Accretion2095RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2095 | 12.8384 | 16.1103 | 20.19 | 23.2554 | 26.3088
DuttonIce Accretion2100RCP8.5 | Dutton | Ice Accretion | RCP8.5 | 2100 | 12.8384 | 16.1103 | 20.19 | 23.2554 | 26.3088
DuttonWind2023RCP4.5 | Dutton | Wind | RCP4.5 | 2023 | 87.0563 | 93.9114 | 101.17 | 108.391 | 115.6188
DuttonWind2025RCP4.5 | Dutton | Wind | RCP4.5 | 2025 | 87.1657 | 94.0571 | 101.3617 | 108.621 | 115.8886
DuttonWind2030RCP4.5 | Dutton | Wind | RCP4.5 | 2030 | 87.275 | 94.2028 | 101.5533 | 108.8511 | 116.1584
DuttonWind2035RCP4.5 | Dutton | Wind | RCP4.5 | 2035 | 87.3844 | 94.3485 | 101.745 | 109.0811 | 116.4282
DuttonWind2040RCP4.5 | Dutton | Wind | RCP4.5 | 2040 | 87.4938 | 94.4942 | 101.9367 | 109.3112 | 116.698
DuttonWind2045RCP4.5 | Dutton | Wind | RCP4.5 | 2045 | 87.6032 | 94.6399 | 102.1283 | 109.5412 | 116.9678
DuttonWind2050RCP4.5 | Dutton | Wind | RCP4.5 | 2050 | 87.7644 | 94.8581 | 102.42 | 109.8954 | 117.3858
DuttonWind2055RCP4.5 | Dutton | Wind | RCP4.5 | 2055 | 87.8162 | 94.9307 | 102.52 | 110.0195 | 117.534
DuttonWind2060RCP4.5 | Dutton | Wind | RCP4.5 | 2060 | 87.868 | 95.0032 | 102.62 | 110.1437 | 117.6822
DuttonWind2065RCP4.5 | Dutton | Wind | RCP4.5 | 2065 | 87.9198 | 95.0758 | 102.72 | 110.2678 | 117.8304
DuttonWind2070RCP4.5 | Dutton | Wind | RCP4.5 | 2070 | 87.9716 | 95.1483 | 102.82 | 110.3919 | 117.9786
DuttonWind2075RCP4.5 | Dutton | Wind | RCP4.5 | 2075 | 88.1241 | 95.3467 | 103.0767 | 110.6969 | 118.3339
DuttonWind2080RCP4.5 | Dutton | Wind | RCP4.5 | 2080 | 88.2767 | 95.5451 | 103.3333 | 111.0018 | 118.6892
DuttonWind2085RCP4.5 | Dutton | Wind | RCP4.5 | 2085 | 88.4292 | 95.7435 | 103.59 | 111.3067 | 119.0445
DuttonWind2090RCP4.5 | Dutton | Wind | RCP4.5 | 2090 | 88.5818 | 95.9419 | 103.8467 | 111.6117 | 119.3998
DuttonWind2095RCP4.5 | Dutton | Wind | RCP4.5 | 2095 | 88.7343 | 96.1403 | 104.1033 | 111.9167 | 119.7551
DuttonWind2100RCP4.5 | Dutton | Wind | RCP4.5 | 2100 | 88.8869 | 96.3387 | 104.36 | 112.2216 | 120.1104
DuttonWind2023RCP6.0 | Dutton | Wind | RCP6.0 | 2023 | 87.0563 | 93.9114 | 101.17 | 108.391 | 115.6188
DuttonWind2025RCP6.0 | Dutton | Wind | RCP6.0 | 2025 | 87.1657 | 94.0571 | 101.3617 | 108.621 | 115.8886
DuttonWind2030RCP6.0 | Dutton | Wind | RCP6.0 | 2030 | 87.275 | 94.2028 | 101.5533 | 108.8511 | 116.1584
DuttonWind2035RCP6.0 | Dutton | Wind | RCP6.0 | 2035 | 87.3844 | 94.3485 | 101.745 | 109.0811 | 116.4282
DuttonWind2040RCP6.0 | Dutton | Wind | RCP6.0 | 2040 | 87.4938 | 94.4942 | 101.9367 | 109.3112 | 116.698
DuttonWind2045RCP6.0 | Dutton | Wind | RCP6.0 | 2045 | 87.6032 | 94.6399 | 102.1283 | 109.5412 | 116.9678
DuttonWind2050RCP6.0 | Dutton | Wind | RCP6.0 | 2050 | 87.7644 | 94.8581 | 102.42 | 109.8954 | 117.3858
DuttonWind2055RCP6.0 | Dutton | Wind | RCP6.0 | 2055 | 87.8162 | 94.9307 | 102.52 | 110.0195 | 117.534
DuttonWind2060RCP6.0 | Dutton | Wind | RCP6.0 | 2060 | 87.868 | 95.0032 | 102.62 | 110.1437 | 117.6822
DuttonWind2065RCP6.0 | Dutton | Wind | RCP6.0 | 2065 | 87.9198 | 95.0758 | 102.72 | 110.2678 | 117.8304
DuttonWind2070RCP6.0 | Dutton | Wind | RCP6.0 | 2070 | 87.9716 | 95.1483 | 102.82 | 110.3919 | 117.9786
DuttonWind2075RCP6.0 | Dutton | Wind | RCP6.0 | 2075 | 88.2004 | 95.4459 | 103.205 | 110.8493 | 118.5115
DuttonWind2080RCP6.0 | Dutton | Wind | RCP6.0 | 2080 | 88.4292 | 95.7435 | 103.59 | 111.3067 | 119.0445
DuttonWind2085RCP6.0 | Dutton | Wind | RCP6.0 | 2085 | 88.6581 | 96.0411 | 103.975 | 111.7642 | 119.5774
DuttonWind2090RCP6.0 | Dutton | Wind | RCP6.0 | 2090 | 89.2639 | 96.8192 | 104.9633 | 112.9314 | 120.9312
DuttonWind2095RCP6.0 | Dutton | Wind | RCP6.0 | 2095 | 89.641 | 97.2997 | 105.5667 | 113.6411 | 121.752
DuttonWind2100RCP6.0 | Dutton | Wind | RCP6.0 | 2100 | 90.018 | 97.7802 | 106.17 | 114.3509 | 122.5728
DuttonWind2023RCP8.5 | Dutton | Wind | RCP8.5 | 2023 | 87.0563 | 93.9114 | 101.17 | 108.391 | 115.6188
DuttonWind2025RCP8.5 | Dutton | Wind | RCP8.5 | 2025 | 87.275 | 94.2028 | 101.5533 | 108.8511 | 116.1584
DuttonWind2030RCP8.5 | Dutton | Wind | RCP8.5 | 2030 | 87.4938 | 94.4942 | 101.9367 | 109.3112 | 116.698
DuttonWind2035RCP8.5 | Dutton | Wind | RCP8.5 | 2035 | 87.7125 | 94.7856 | 102.32 | 109.7713 | 117.2376
DuttonWind2040RCP8.5 | Dutton | Wind | RCP8.5 | 2040 | 87.7989 | 94.9065 | 102.4867 | 109.9782 | 117.4846
DuttonWind2045RCP8.5 | Dutton | Wind | RCP8.5 | 2045 | 87.8852 | 95.0274 | 102.6533 | 110.185 | 117.7316
DuttonWind2050RCP8.5 | Dutton | Wind | RCP8.5 | 2050 | 88.2767 | 95.5451 | 103.3333 | 111.0018 | 118.6892
DuttonWind2055RCP8.5 | Dutton | Wind | RCP8.5 | 2055 | 88.5818 | 95.9419 | 103.8467 | 111.6117 | 119.3998
DuttonWind2060RCP8.5 | Dutton | Wind | RCP8.5 | 2060 | 89.2639 | 96.8192 | 104.9633 | 112.9314 | 120.9312
DuttonWind2065RCP8.5 | Dutton | Wind | RCP8.5 | 2065 | 89.641 | 97.2997 | 105.5667 | 113.6411 | 121.752
DuttonWind2070RCP8.5 | Dutton | Wind | RCP8.5 | 2070 | 90.2512 | 98.0716 | 106.54 | 114.7896 | 123.0782
DuttonWind2075RCP8.5 | Dutton | Wind | RCP8.5 | 2075 | 90.4843 | 98.363 | 106.91 | 115.2283 | 123.5836
DuttonWind2080RCP8.5 | Dutton | Wind | RCP8.5 | 2080 | 90.7175 | 98.6544 | 107.28 | 115.667 | 124.089
DuttonWind2085RCP8.5 | Dutton | Wind | RCP8.5 | 2085 | 91.1147 | 99.1799 | 107.97 | 116.4909 | 125.058
DuttonWind2090RCP8.5 | Dutton | Wind | RCP8.5 | 2090 | 91.5119 | 99.7053 | 108.66 | 117.3148 | 126.027
DuttonWind2095RCP8.5 | Dutton | Wind | RCP8.5 | 2095 | 91.5119 | 99.7053 | 108.66 | 117.3148 | 126.027
DuttonWind2100RCP8.5 | Dutton | Wind | RCP8.5 | 2100 | 91.5119 | 99.7053 | 108.66 | 117.3148 | 126.027
EarltonIce Accretion2023RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2023 | 14.7519 | 17.6458 | 21.32 | 24.1142 | 26.9136
EarltonIce Accretion2025RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2025 | 14.7311 | 17.6209 | 21.2867 | 24.0765 | 26.8716
EarltonIce Accretion2030RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2030 | 14.7102 | 17.596 | 21.2533 | 24.0389 | 26.8296
EarltonIce Accretion2035RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2035 | 14.6893 | 17.5711 | 21.22 | 24.0012 | 26.7876
EarltonIce Accretion2040RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2040 | 14.6684 | 17.5462 | 21.1867 | 23.9635 | 26.7456
EarltonIce Accretion2045RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2045 | 14.6476 | 17.5213 | 21.1533 | 23.9259 | 26.7036
EarltonIce Accretion2050RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2050 | 14.635 | 17.5064 | 21.128 | 23.8972 | 26.6717
EarltonIce Accretion2055RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2055 | 14.6434 | 17.5163 | 21.136 | 23.9063 | 26.6818
EarltonIce Accretion2060RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2060 | 14.6517 | 17.5263 | 21.144 | 23.9153 | 26.6918
EarltonIce Accretion2065RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2065 | 14.6601 | 17.5362 | 21.152 | 23.9244 | 26.7019
EarltonIce Accretion2070RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2070 | 14.6684 | 17.5462 | 21.16 | 23.9334 | 26.712
EarltonIce Accretion2075RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2075 | 14.7055 | 17.5988 | 21.2367 | 24.0276 | 26.8212
EarltonIce Accretion2080RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2080 | 14.7427 | 17.6513 | 21.3133 | 24.1217 | 26.9304
EarltonIce Accretion2085RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2085 | 14.7798 | 17.7039 | 21.39 | 24.2159 | 27.0396
EarltonIce Accretion2090RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2090 | 14.8169 | 17.7565 | 21.4667 | 24.3101 | 27.1488
EarltonIce Accretion2095RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2095 | 14.854 | 17.809 | 21.5433 | 24.4042 | 27.258
EarltonIce Accretion2100RCP4.5 | Earlton | Ice Accretion | RCP4.5 | 2100 | 14.8911 | 17.8616 | 21.62 | 24.4984 | 27.3672
EarltonIce Accretion2023RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2023 | 14.7519 | 17.6458 | 21.32 | 24.1142 | 26.9136
EarltonIce Accretion2025RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2025 | 14.7311 | 17.6209 | 21.2867 | 24.0765 | 26.8716
EarltonIce Accretion2030RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2030 | 14.7102 | 17.596 | 21.2533 | 24.0389 | 26.8296
EarltonIce Accretion2035RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2035 | 14.6893 | 17.5711 | 21.22 | 24.0012 | 26.7876
EarltonIce Accretion2040RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2040 | 14.6684 | 17.5462 | 21.1867 | 23.9635 | 26.7456
EarltonIce Accretion2045RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2045 | 14.6476 | 17.5213 | 21.1533 | 23.9259 | 26.7036
EarltonIce Accretion2050RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2050 | 14.635 | 17.5064 | 21.128 | 23.8972 | 26.6717
EarltonIce Accretion2055RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2055 | 14.6434 | 17.5163 | 21.136 | 23.9063 | 26.6818
EarltonIce Accretion2060RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2060 | 14.6517 | 17.5263 | 21.144 | 23.9153 | 26.6918
EarltonIce Accretion2065RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2065 | 14.6601 | 17.5362 | 21.152 | 23.9244 | 26.7019
EarltonIce Accretion2070RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2070 | 14.6684 | 17.5462 | 21.16 | 23.9334 | 26.712
EarltonIce Accretion2075RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2075 | 14.7241 | 17.625 | 21.275 | 24.0746 | 26.8758
EarltonIce Accretion2080RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2080 | 14.7798 | 17.7039 | 21.39 | 24.2159 | 27.0396
EarltonIce Accretion2085RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2085 | 14.8354 | 17.7828 | 21.505 | 24.3571 | 27.2034
EarltonIce Accretion2090RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2090 | 14.9375 | 17.9225 | 21.7067 | 24.6039 | 27.4848
EarltonIce Accretion2095RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2095 | 14.9839 | 17.9833 | 21.7933 | 24.7093 | 27.6024
EarltonIce Accretion2100RCP6.0 | Earlton | Ice Accretion | RCP6.0 | 2100 | 15.0303 | 18.0442 | 21.88 | 24.8148 | 27.72
EarltonIce Accretion2023RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2023 | 14.7519 | 17.6458 | 21.32 | 24.1142 | 26.9136
EarltonIce Accretion2025RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2025 | 14.7102 | 17.596 | 21.2533 | 24.0389 | 26.8296
EarltonIce Accretion2030RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2030 | 14.6684 | 17.5462 | 21.1867 | 23.9635 | 26.7456
EarltonIce Accretion2035RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2035 | 14.6267 | 17.4964 | 21.12 | 23.8882 | 26.6616
EarltonIce Accretion2040RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2040 | 14.6406 | 17.513 | 21.1333 | 23.9033 | 26.6784
EarltonIce Accretion2045RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2045 | 14.6545 | 17.5296 | 21.1467 | 23.9183 | 26.6952
EarltonIce Accretion2050RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2050 | 14.7427 | 17.6513 | 21.3133 | 24.1217 | 26.9304
EarltonIce Accretion2055RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2055 | 14.8169 | 17.7565 | 21.4667 | 24.3101 | 27.1488
EarltonIce Accretion2060RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2060 | 14.9375 | 17.9225 | 21.7067 | 24.6039 | 27.4848
EarltonIce Accretion2065RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2065 | 14.9839 | 17.9833 | 21.7933 | 24.7093 | 27.6024
EarltonIce Accretion2070RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2070 | 14.8633 | 17.8616 | 21.6667 | 24.5737 | 27.4596
EarltonIce Accretion2075RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2075 | 14.6963 | 17.679 | 21.4533 | 24.3327 | 27.1992
EarltonIce Accretion2080RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2080 | 14.5293 | 17.4964 | 21.24 | 24.0916 | 26.9388
EarltonIce Accretion2085RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2085 | 14.5641 | 17.5711 | 21.36 | 24.2611 | 27.1404
EarltonIce Accretion2090RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2090 | 14.5989 | 17.6458 | 21.48 | 24.4306 | 27.342
EarltonIce Accretion2095RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2095 | 14.5989 | 17.6458 | 21.48 | 24.4306 | 27.342
EarltonIce Accretion2100RCP8.5 | Earlton | Ice Accretion | RCP8.5 | 2100 | 14.5989 | 17.6458 | 21.48 | 24.4306 | 27.342
EarltonWind2023RCP4.5 | Earlton | Wind | RCP4.5 | 2023 | 76.1156 | 81.9218 | 88.0088 | 94.1129 | 100.2197
EarltonWind2025RCP4.5 | Earlton | Wind | RCP4.5 | 2025 | 76.122 | 81.9259 | 88.0132 | 94.1176 | 100.223
EarltonWind2030RCP4.5 | Earlton | Wind | RCP4.5 | 2030 | 76.1283 | 81.93 | 88.0176 | 94.1223 | 100.2264
EarltonWind2035RCP4.5 | Earlton | Wind | RCP4.5 | 2035 | 76.1346 | 81.9341 | 88.022 | 94.127 | 100.2297
EarltonWind2040RCP4.5 | Earlton | Wind | RCP4.5 | 2040 | 76.141 | 81.9382 | 88.0264 | 94.1318 | 100.2331
EarltonWind2045RCP4.5 | Earlton | Wind | RCP4.5 | 2045 | 76.1473 | 81.9423 | 88.0308 | 94.1365 | 100.2364
EarltonWind2050RCP4.5 | Earlton | Wind | RCP4.5 | 2050 | 76.1551 | 81.9448 | 88.0246 | 94.1261 | 100.2197
EarltonWind2055RCP4.5 | Earlton | Wind | RCP4.5 | 2055 | 76.1567 | 81.9431 | 88.0141 | 94.111 | 100.1996
EarltonWind2060RCP4.5 | Earlton | Wind | RCP4.5 | 2060 | 76.1582 | 81.9415 | 88.0035 | 94.096 | 100.1796
EarltonWind2065RCP4.5 | Earlton | Wind | RCP4.5 | 2065 | 76.1597 | 81.9398 | 87.993 | 94.0809 | 100.1595
EarltonWind2070RCP4.5 | Earlton | Wind | RCP4.5 | 2070 | 76.1612 | 81.9382 | 87.9824 | 94.0658 | 100.1394
EarltonWind2075RCP4.5 | Earlton | Wind | RCP4.5 | 2075 | 76.2182 | 82.0078 | 88.0689 | 94.1647 | 100.2514
EarltonWind2080RCP4.5 | Earlton | Wind | RCP4.5 | 2080 | 76.2752 | 82.0773 | 88.1555 | 94.2636 | 100.3635
EarltonWind2085RCP4.5 | Earlton | Wind | RCP4.5 | 2085 | 76.3322 | 82.1469 | 88.242 | 94.3624 | 100.4755
EarltonWind2090RCP4.5 | Earlton | Wind | RCP4.5 | 2090 | 76.3892 | 82.2165 | 88.3285 | 94.4613 | 100.5875
EarltonWind2095RCP4.5 | Earlton | Wind | RCP4.5 | 2095 | 76.4462 | 82.286 | 88.4151 | 94.5602 | 100.6995
EarltonWind2100RCP4.5 | Earlton | Wind | RCP4.5 | 2100 | 76.5032 | 82.3556 | 88.5016 | 94.659 | 100.8116
EarltonWind2023RCP6.0 | Earlton | Wind | RCP6.0 | 2023 | 76.1156 | 81.9218 | 88.0088 | 94.1129 | 100.2197
EarltonWind2025RCP6.0 | Earlton | Wind | RCP6.0 | 2025 | 76.122 | 81.9259 | 88.0132 | 94.1176 | 100.223
EarltonWind2030RCP6.0 | Earlton | Wind | RCP6.0 | 2030 | 76.1283 | 81.93 | 88.0176 | 94.1223 | 100.2264
EarltonWind2035RCP6.0 | Earlton | Wind | RCP6.0 | 2035 | 76.1346 | 81.9341 | 88.022 | 94.127 | 100.2297
EarltonWind2040RCP6.0 | Earlton | Wind | RCP6.0 | 2040 | 76.141 | 81.9382 | 88.0264 | 94.1318 | 100.2331
EarltonWind2045RCP6.0 | Earlton | Wind | RCP6.0 | 2045 | 76.1473 | 81.9423 | 88.0308 | 94.1365 | 100.2364
EarltonWind2050RCP6.0 | Earlton | Wind | RCP6.0 | 2050 | 76.1551 | 81.9448 | 88.0246 | 94.1261 | 100.2197
EarltonWind2055RCP6.0 | Earlton | Wind | RCP6.0 | 2055 | 76.1567 | 81.9431 | 88.0141 | 94.111 | 100.1996
EarltonWind2060RCP6.0 | Earlton | Wind | RCP6.0 | 2060 | 76.1582 | 81.9415 | 88.0035 | 94.096 | 100.1796
EarltonWind2065RCP6.0 | Earlton | Wind | RCP6.0 | 2065 | 76.1597 | 81.9398 | 87.993 | 94.0809 | 100.1595
EarltonWind2070RCP6.0 | Earlton | Wind | RCP6.0 | 2070 | 76.1612 | 81.9382 | 87.9824 | 94.0658 | 100.1394
EarltonWind2075RCP6.0 | Earlton | Wind | RCP6.0 | 2075 | 76.2467 | 82.0426 | 88.1122 | 94.2141 | 100.3075
EarltonWind2080RCP6.0 | Earlton | Wind | RCP6.0 | 2080 | 76.3322 | 82.1469 | 88.242 | 94.3624 | 100.4755
EarltonWind2085RCP6.0 | Earlton | Wind | RCP6.0 | 2085 | 76.4177 | 82.2512 | 88.3718 | 94.5107 | 100.6435
EarltonWind2090RCP6.0 | Earlton | Wind | RCP6.0 | 2090 | 76.493 | 82.331 | 88.4576 | 94.6026 | 100.7413
EarltonWind2095RCP6.0 | Earlton | Wind | RCP6.0 | 2095 | 76.4829 | 82.3065 | 88.4136 | 94.5461 | 100.6711
EarltonWind2100RCP6.0 | Earlton | Wind | RCP6.0 | 2100 | 76.4728 | 82.2819 | 88.3696 | 94.4896 | 100.6009
EarltonWind2023RCP8.5 | Earlton | Wind | RCP8.5 | 2023 | 76.1156 | 81.9218 | 88.0088 | 94.1129 | 100.2197
EarltonWind2025RCP8.5 | Earlton | Wind | RCP8.5 | 2025 | 76.1283 | 81.93 | 88.0176 | 94.1223 | 100.2264
EarltonWind2030RCP8.5 | Earlton | Wind | RCP8.5 | 2030 | 76.141 | 81.9382 | 88.0264 | 94.1318 | 100.2331
EarltonWind2035RCP8.5 | Earlton | Wind | RCP8.5 | 2035 | 76.1536 | 81.9464 | 88.0352 | 94.1412 | 100.2397
EarltonWind2040RCP8.5 | Earlton | Wind | RCP8.5 | 2040 | 76.1562 | 81.9437 | 88.0176 | 94.1161 | 100.2063
EarltonWind2045RCP8.5 | Earlton | Wind | RCP8.5 | 2045 | 76.1587 | 81.9409 | 88 | 94.0909 | 100.1729
EarltonWind2050RCP8.5 | Earlton | Wind | RCP8.5 | 2050 | 76.2752 | 82.0773 | 88.1555 | 94.2636 | 100.3635
EarltonWind2055RCP8.5 | Earlton | Wind | RCP8.5 | 2055 | 76.3892 | 82.2165 | 88.3285 | 94.4613 | 100.5875
EarltonWind2060RCP8.5 | Earlton | Wind | RCP8.5 | 2060 | 76.493 | 82.331 | 88.4576 | 94.6026 | 100.7413
EarltonWind2065RCP8.5 | Earlton | Wind | RCP8.5 | 2065 | 76.4829 | 82.3065 | 88.4136 | 94.5461 | 100.6711
EarltonWind2070RCP8.5 | Earlton | Wind | RCP8.5 | 2070 | 76.5488 | 82.3665 | 88.4635 | 94.59 | 100.7112
EarltonWind2075RCP8.5 | Earlton | Wind | RCP8.5 | 2075 | 76.6247 | 82.4511 | 88.5573 | 94.6904 | 100.8216
EarltonWind2080RCP8.5 | Earlton | Wind | RCP8.5 | 2080 | 76.7007 | 82.5356 | 88.6512 | 94.7909 | 100.932
EarltonWind2085RCP8.5 | Earlton | Wind | RCP8.5 | 2085 | 76.8299 | 82.7075 | 88.8756 | 95.0592 | 101.248
EarltonWind2090RCP8.5 | Earlton | Wind | RCP8.5 | 2090 | 76.9591 | 82.8794 | 89.1 | 95.3276 | 101.564
EarltonWind2095RCP8.5 | Earlton | Wind | RCP8.5 | 2095 | 76.9591 | 82.8794 | 89.1 | 95.3276 | 101.564
EarltonWind2100RCP8.5 | Earlton | Wind | RCP8.5 | 2100 | 76.9591 | 82.8794 | 89.1 | 95.3276 | 101.564
EdisonIce Accretion2023RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2023 | 10.2679 | 12.2591 | 14.784 | 16.7217 | 18.6455
EdisonIce Accretion2025RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2025 | 10.2793 | 12.2727 | 14.8003 | 16.7402 | 18.6661
EdisonIce Accretion2030RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2030 | 10.2906 | 12.2862 | 14.8167 | 16.7587 | 18.6866
EdisonIce Accretion2035RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2035 | 10.302 | 12.2998 | 14.833 | 16.7771 | 18.7072
EdisonIce Accretion2040RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2040 | 10.3134 | 12.3133 | 14.8493 | 16.7956 | 18.7278
EdisonIce Accretion2045RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2045 | 10.3247 | 12.3269 | 14.8657 | 16.814 | 18.7484
EdisonIce Accretion2050RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2050 | 10.3809 | 12.3916 | 14.9408 | 16.8958 | 18.8395
EdisonIce Accretion2055RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2055 | 10.4257 | 12.4427 | 14.9996 | 16.959 | 18.9101
EdisonIce Accretion2060RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2060 | 10.4705 | 12.4938 | 15.0584 | 17.0223 | 18.9806
EdisonIce Accretion2065RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2065 | 10.5153 | 12.545 | 15.1172 | 17.0856 | 19.0512
EdisonIce Accretion2070RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2070 | 10.5602 | 12.5961 | 15.176 | 17.1489 | 19.1218
EdisonIce Accretion2075RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2075 | 10.591 | 12.6348 | 15.2227 | 17.2016 | 19.1806
EdisonIce Accretion2080RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2080 | 10.6219 | 12.6735 | 15.2693 | 17.2543 | 19.2394
EdisonIce Accretion2085RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2085 | 10.6527 | 12.7123 | 15.316 | 17.3071 | 19.2982
EdisonIce Accretion2090RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2090 | 10.6836 | 12.751 | 15.3627 | 17.3598 | 19.357
EdisonIce Accretion2095RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2095 | 10.7144 | 12.7897 | 15.4093 | 17.4125 | 19.4158
EdisonIce Accretion2100RCP4.5 | Edison | Ice Accretion | RCP4.5 | 2100 | 10.7453 | 12.8285 | 15.456 | 17.4653 | 19.4746
EdisonIce Accretion2023RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2023 | 10.2679 | 12.2591 | 14.784 | 16.7217 | 18.6455
EdisonIce Accretion2025RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2025 | 10.2793 | 12.2727 | 14.8003 | 16.7402 | 18.6661
EdisonIce Accretion2030RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2030 | 10.2906 | 12.2862 | 14.8167 | 16.7587 | 18.6866
EdisonIce Accretion2035RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2035 | 10.302 | 12.2998 | 14.833 | 16.7771 | 18.7072
EdisonIce Accretion2040RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2040 | 10.3134 | 12.3133 | 14.8493 | 16.7956 | 18.7278
EdisonIce Accretion2045RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2045 | 10.3247 | 12.3269 | 14.8657 | 16.814 | 18.7484
EdisonIce Accretion2050RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2050 | 10.3809 | 12.3916 | 14.9408 | 16.8958 | 18.8395
EdisonIce Accretion2055RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2055 | 10.4257 | 12.4427 | 14.9996 | 16.959 | 18.9101
EdisonIce Accretion2060RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2060 | 10.4705 | 12.4938 | 15.0584 | 17.0223 | 18.9806
EdisonIce Accretion2065RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2065 | 10.5153 | 12.545 | 15.1172 | 17.0856 | 19.0512
EdisonIce Accretion2070RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2070 | 10.5602 | 12.5961 | 15.176 | 17.1489 | 19.1218
EdisonIce Accretion2075RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2075 | 10.6064 | 12.6542 | 15.246 | 17.228 | 19.21
EdisonIce Accretion2080RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2080 | 10.6527 | 12.7123 | 15.316 | 17.3071 | 19.2982
EdisonIce Accretion2085RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2085 | 10.699 | 12.7704 | 15.386 | 17.3862 | 19.3864
EdisonIce Accretion2090RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2090 | 10.7453 | 12.8246 | 15.4513 | 17.4547 | 19.4628
EdisonIce Accretion2095RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2095 | 10.7453 | 12.8207 | 15.4467 | 17.4442 | 19.451
EdisonIce Accretion2100RCP6.0 | Edison | Ice Accretion | RCP6.0 | 2100 | 10.7453 | 12.8169 | 15.442 | 17.4336 | 19.4393
EdisonIce Accretion2023RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2023 | 10.2679 | 12.2591 | 14.784 | 16.7217 | 18.6455
EdisonIce Accretion2025RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2025 | 10.2906 | 12.2862 | 14.8167 | 16.7587 | 18.6866
EdisonIce Accretion2030RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2030 | 10.3134 | 12.3133 | 14.8493 | 16.7956 | 18.7278
EdisonIce Accretion2035RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2035 | 10.3361 | 12.3404 | 14.882 | 16.8325 | 18.769
EdisonIce Accretion2040RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2040 | 10.4108 | 12.4257 | 14.98 | 16.9379 | 18.8866
EdisonIce Accretion2045RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2045 | 10.4855 | 12.5109 | 15.078 | 17.0434 | 19.0042
EdisonIce Accretion2050RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2050 | 10.6219 | 12.6735 | 15.2693 | 17.2543 | 19.2394
EdisonIce Accretion2055RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2055 | 10.6836 | 12.751 | 15.3627 | 17.3598 | 19.357
EdisonIce Accretion2060RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2060 | 10.7453 | 12.8246 | 15.4513 | 17.4547 | 19.4628
EdisonIce Accretion2065RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2065 | 10.7453 | 12.8207 | 15.4467 | 17.4442 | 19.451
EdisonIce Accretion2070RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2070 | 10.7485 | 12.8246 | 15.456 | 17.4547 | 19.4687
EdisonIce Accretion2075RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2075 | 10.7518 | 12.8324 | 15.47 | 17.4758 | 19.4981
EdisonIce Accretion2080RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2080 | 10.755 | 12.8401 | 15.484 | 17.4969 | 19.5275
EdisonIce Accretion2085RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2085 | 10.5212 | 12.5554 | 15.134 | 17.1014 | 19.0777
EdisonIce Accretion2090RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2090 | 10.2874 | 12.2707 | 14.784 | 16.7059 | 18.6278
EdisonIce Accretion2095RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2095 | 10.2874 | 12.2707 | 14.784 | 16.7059 | 18.6278
EdisonIce Accretion2100RCP8.5 | Edison | Ice Accretion | RCP8.5 | 2100 | 10.2874 | 12.2707 | 14.784 | 16.7059 | 18.6278
EdisonWind2023RCP4.5 | Edison | Wind | RCP4.5 | 2023 | 73.9171 | 79.6982 | 85.8075 | 91.8868 | 97.9659
EdisonWind2025RCP4.5 | Edison | Wind | RCP4.5 | 2025 | 73.9465 | 79.7167 | 85.8103 | 91.8792 | 97.9481
EdisonWind2030RCP4.5 | Edison | Wind | RCP4.5 | 2030 | 73.9758 | 79.7351 | 85.8132 | 91.8716 | 97.9304
EdisonWind2035RCP4.5 | Edison | Wind | RCP4.5 | 2035 | 74.0052 | 79.7535 | 85.816 | 91.864 | 97.9126
EdisonWind2040RCP4.5 | Edison | Wind | RCP4.5 | 2040 | 74.0346 | 79.772 | 85.8188 | 91.8565 | 97.8948
EdisonWind2045RCP4.5 | Edison | Wind | RCP4.5 | 2045 | 74.0639 | 79.7904 | 85.8217 | 91.8489 | 97.8771
EdisonWind2050RCP4.5 | Edison | Wind | RCP4.5 | 2050 | 74.1902 | 79.9259 | 85.9656 | 92.0032 | 98.0434
EdisonWind2055RCP4.5 | Edison | Wind | RCP4.5 | 2055 | 74.287 | 80.0429 | 86.1067 | 92.1651 | 98.2275
EdisonWind2060RCP4.5 | Edison | Wind | RCP4.5 | 2060 | 74.3839 | 80.1599 | 86.2478 | 92.327 | 98.4116
EdisonWind2065RCP4.5 | Edison | Wind | RCP4.5 | 2065 | 74.4808 | 80.2769 | 86.3889 | 92.4889 | 98.5957
EdisonWind2070RCP4.5 | Edison | Wind | RCP4.5 | 2070 | 74.5777 | 80.3938 | 86.53 | 92.6508 | 98.7799
EdisonWind2075RCP4.5 | Edison | Wind | RCP4.5 | 2075 | 74.6156 | 80.4373 | 86.581 | 92.7084 | 98.8428
EdisonWind2080RCP4.5 | Edison | Wind | RCP4.5 | 2080 | 74.6535 | 80.4808 | 86.632 | 92.766 | 98.9058
EdisonWind2085RCP4.5 | Edison | Wind | RCP4.5 | 2085 | 74.6914 | 80.5243 | 86.683 | 92.8236 | 98.9688
EdisonWind2090RCP4.5 | Edison | Wind | RCP4.5 | 2090 | 74.7294 | 80.5678 | 86.734 | 92.8812 | 99.0318
EdisonWind2095RCP4.5 | Edison | Wind | RCP4.5 | 2095 | 74.7673 | 80.6112 | 86.785 | 92.9388 | 99.0948
EdisonWind2100RCP4.5 | Edison | Wind | RCP4.5 | 2100 | 74.8052 | 80.6547 | 86.836 | 92.9964 | 99.1578
EdisonWind2023RCP6.0 | Edison | Wind | RCP6.0 | 2023 | 73.9171 | 79.6982 | 85.8075 | 91.8868 | 97.9659
EdisonWind2025RCP6.0 | Edison | Wind | RCP6.0 | 2025 | 73.9465 | 79.7167 | 85.8103 | 91.8792 | 97.9481
EdisonWind2030RCP6.0 | Edison | Wind | RCP6.0 | 2030 | 73.9758 | 79.7351 | 85.8132 | 91.8716 | 97.9304
EdisonWind2035RCP6.0 | Edison | Wind | RCP6.0 | 2035 | 74.0052 | 79.7535 | 85.816 | 91.864 | 97.9126
EdisonWind2040RCP6.0 | Edison | Wind | RCP6.0 | 2040 | 74.0346 | 79.772 | 85.8188 | 91.8565 | 97.8948
EdisonWind2045RCP6.0 | Edison | Wind | RCP6.0 | 2045 | 74.0639 | 79.7904 | 85.8217 | 91.8489 | 97.8771
EdisonWind2050RCP6.0 | Edison | Wind | RCP6.0 | 2050 | 74.1902 | 79.9259 | 85.9656 | 92.0032 | 98.0434
EdisonWind2055RCP6.0 | Edison | Wind | RCP6.0 | 2055 | 74.287 | 80.0429 | 86.1067 | 92.1651 | 98.2275
EdisonWind2060RCP6.0 | Edison | Wind | RCP6.0 | 2060 | 74.3839 | 80.1599 | 86.2478 | 92.327 | 98.4116
EdisonWind2065RCP6.0 | Edison | Wind | RCP6.0 | 2065 | 74.4808 | 80.2769 | 86.3889 | 92.4889 | 98.5957
EdisonWind2070RCP6.0 | Edison | Wind | RCP6.0 | 2070 | 74.5777 | 80.3938 | 86.53 | 92.6508 | 98.7799
EdisonWind2075RCP6.0 | Edison | Wind | RCP6.0 | 2075 | 74.6346 | 80.4591 | 86.6065 | 92.7372 | 98.8743
EdisonWind2080RCP6.0 | Edison | Wind | RCP6.0 | 2080 | 74.6914 | 80.5243 | 86.683 | 92.8236 | 98.9688
EdisonWind2085RCP6.0 | Edison | Wind | RCP6.0 | 2085 | 74.7483 | 80.5895 | 86.7595 | 92.91 | 99.0633
EdisonWind2090RCP6.0 | Edison | Wind | RCP6.0 | 2090 | 75.0376 | 80.963 | 87.2355 | 93.4754 | 99.7166
EdisonWind2095RCP6.0 | Edison | Wind | RCP6.0 | 2095 | 75.2701 | 81.2713 | 87.635 | 93.9544 | 100.2753
EdisonWind2100RCP6.0 | Edison | Wind | RCP6.0 | 2100 | 75.5025 | 81.5796 | 88.0345 | 94.4334 | 100.8341
EdisonWind2023RCP8.5 | Edison | Wind | RCP8.5 | 2023 | 73.9171 | 79.6982 | 85.8075 | 91.8868 | 97.9659
EdisonWind2025RCP8.5 | Edison | Wind | RCP8.5 | 2025 | 73.9758 | 79.7351 | 85.8132 | 91.8716 | 97.9304
EdisonWind2030RCP8.5 | Edison | Wind | RCP8.5 | 2030 | 74.0346 | 79.772 | 85.8188 | 91.8565 | 97.8948
EdisonWind2035RCP8.5 | Edison | Wind | RCP8.5 | 2035 | 74.0933 | 79.8089 | 85.8245 | 91.8413 | 97.8593
EdisonWind2040RCP8.5 | Edison | Wind | RCP8.5 | 2040 | 74.2547 | 80.0039 | 86.0597 | 92.1111 | 98.1662
EdisonWind2045RCP8.5 | Edison | Wind | RCP8.5 | 2045 | 74.4162 | 80.1989 | 86.2948 | 92.3809 | 98.473
EdisonWind2050RCP8.5 | Edison | Wind | RCP8.5 | 2050 | 74.6535 | 80.4808 | 86.632 | 92.766 | 98.9058
EdisonWind2055RCP8.5 | Edison | Wind | RCP8.5 | 2055 | 74.7294 | 80.5678 | 86.734 | 92.8812 | 99.0318
EdisonWind2060RCP8.5 | Edison | Wind | RCP8.5 | 2060 | 75.0376 | 80.963 | 87.2355 | 93.4754 | 99.7166
EdisonWind2065RCP8.5 | Edison | Wind | RCP8.5 | 2065 | 75.2701 | 81.2713 | 87.635 | 93.9544 | 100.2753
EdisonWind2070RCP8.5 | Edison | Wind | RCP8.5 | 2070 | 75.6909 | 81.7957 | 88.2838 | 94.7093 | 101.141
EdisonWind2075RCP8.5 | Edison | Wind | RCP8.5 | 2075 | 75.8792 | 82.0117 | 88.5332 | 94.9851 | 101.4478
EdisonWind2080RCP8.5 | Edison | Wind | RCP8.5 | 2080 | 76.0676 | 82.2278 | 88.7825 | 95.261 | 101.7547
EdisonWind2085RCP8.5 | Edison | Wind | RCP8.5 | 2085 | 76.3318 | 82.5519 | 89.1863 | 95.7294 | 102.2828
EdisonWind2090RCP8.5 | Edison | Wind | RCP8.5 | 2090 | 76.5961 | 82.876 | 89.59 | 96.1978 | 102.8109
EdisonWind2095RCP8.5 | Edison | Wind | RCP8.5 | 2095 | 76.5961 | 82.876 | 89.59 | 96.1978 | 102.8109
EdisonWind2100RCP8.5 | Edison | Wind | RCP8.5 | 2100 | 76.5961 | 82.876 | 89.59 | 96.1978 | 102.8109
Elliot Lake Ice Accretion2023RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2023 | 15.3086 | 18.2783 | 22.066 | 24.9346 | 27.8309
Elliot Lake Ice Accretion2025RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2025 | 15.2576 | 18.2204 | 22 | 24.8641 | 27.7523
Elliot Lake Ice Accretion2030RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2030 | 15.2066 | 18.1626 | 21.934 | 24.7937 | 27.6738
Elliot Lake Ice Accretion2035RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2035 | 15.1555 | 18.1048 | 21.868 | 24.7233 | 27.5953
Elliot Lake Ice Accretion2040RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2040 | 15.1045 | 18.047 | 21.802 | 24.6528 | 27.5167
Elliot Lake Ice Accretion2045RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2045 | 15.0535 | 17.9891 | 21.736 | 24.5824 | 27.4382
Elliot Lake Ice Accretion2050RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2050 | 15.1739 | 18.1504 | 21.9472 | 24.8351 | 27.7255
Elliot Lake Ice Accretion2055RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2055 | 15.3454 | 18.3696 | 22.2244 | 25.1583 | 28.0914
Elliot Lake Ice Accretion2060RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2060 | 15.5168 | 18.5887 | 22.5016 | 25.4815 | 28.4574
Elliot Lake Ice Accretion2065RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2065 | 15.6883 | 18.8078 | 22.7788 | 25.8047 | 28.8233
Elliot Lake Ice Accretion2070RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2070 | 15.8597 | 19.0269 | 23.056 | 26.1279 | 29.1892
Elliot Lake Ice Accretion2075RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2075 | 15.8521 | 19.0269 | 23.0633 | 26.1403 | 29.2076
Elliot Lake Ice Accretion2080RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2080 | 15.8444 | 19.0269 | 23.0707 | 26.1527 | 29.2261
Elliot Lake Ice Accretion2085RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2085 | 15.8368 | 19.0269 | 23.078 | 26.1651 | 29.2446
Elliot Lake Ice Accretion2090RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2090 | 15.8291 | 19.0269 | 23.0853 | 26.1776 | 29.2631
Elliot Lake Ice Accretion2095RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2095 | 15.8215 | 19.0269 | 23.0927 | 26.19 | 29.2816
Elliot Lake Ice Accretion2100RCP4.5 | Elliot Lake | Ice Accretion | RCP4.5 | 2100 | 15.8138 | 19.0269 | 23.1 | 26.2024 | 29.3
Elliot Lake Ice Accretion2023RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2023 | 15.3086 | 18.2783 | 22.066 | 24.9346 | 27.8309
Elliot Lake Ice Accretion2025RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2025 | 15.2576 | 18.2204 | 22 | 24.8641 | 27.7523
Elliot Lake Ice Accretion2030RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2030 | 15.2066 | 18.1626 | 21.934 | 24.7937 | 27.6738
Elliot Lake Ice Accretion2035RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2035 | 15.1555 | 18.1048 | 21.868 | 24.7233 | 27.5953
Elliot Lake Ice Accretion2040RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2040 | 15.1045 | 18.047 | 21.802 | 24.6528 | 27.5167
Elliot Lake Ice Accretion2045RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2045 | 15.0535 | 17.9891 | 21.736 | 24.5824 | 27.4382
Elliot Lake Ice Accretion2050RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2050 | 15.1739 | 18.1504 | 21.9472 | 24.8351 | 27.7255
Elliot Lake Ice Accretion2055RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2055 | 15.3454 | 18.3696 | 22.2244 | 25.1583 | 28.0914
Elliot Lake Ice Accretion2060RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2060 | 15.5168 | 18.5887 | 22.5016 | 25.4815 | 28.4574
Elliot Lake Ice Accretion2065RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2065 | 15.6883 | 18.8078 | 22.7788 | 25.8047 | 28.8233
Elliot Lake Ice Accretion2070RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2070 | 15.8597 | 19.0269 | 23.056 | 26.1279 | 29.1892
Elliot Lake Ice Accretion2075RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2075 | 15.8482 | 19.0269 | 23.067 | 26.1465 | 29.2169
Elliot Lake Ice Accretion2080RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2080 | 15.8368 | 19.0269 | 23.078 | 26.1651 | 29.2446
Elliot Lake Ice Accretion2085RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2085 | 15.8253 | 19.0269 | 23.089 | 26.1838 | 29.2723
Elliot Lake Ice Accretion2090RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2090 | 15.8903 | 19.1487 | 23.276 | 26.4262 | 29.568
Elliot Lake Ice Accretion2095RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2095 | 15.9669 | 19.2704 | 23.452 | 26.6499 | 29.836
Elliot Lake Ice Accretion2100RCP6.0 | Elliot Lake | Ice Accretion | RCP6.0 | 2100 | 16.0434 | 19.3921 | 23.628 | 26.8737 | 30.1039
Elliot Lake Ice Accretion2023RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2023 | 15.3086 | 18.2783 | 22.066 | 24.9346 | 27.8309
Elliot Lake Ice Accretion2025RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2025 | 15.2066 | 18.1626 | 21.934 | 24.7937 | 27.6738
Elliot Lake Ice Accretion2030RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2030 | 15.1045 | 18.047 | 21.802 | 24.6528 | 27.5167
Elliot Lake Ice Accretion2035RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2035 | 15.0024 | 17.9313 | 21.67 | 24.512 | 27.3596
Elliot Lake Ice Accretion2040RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2040 | 15.2882 | 18.2965 | 22.132 | 25.0506 | 27.9695
Elliot Lake Ice Accretion2045RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2045 | 15.574 | 18.6617 | 22.594 | 25.5892 | 28.5793
Elliot Lake Ice Accretion2050RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2050 | 15.8444 | 19.0269 | 23.0707 | 26.1527 | 29.2261
Elliot Lake Ice Accretion2055RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2055 | 15.8291 | 19.0269 | 23.0853 | 26.1776 | 29.2631
Elliot Lake Ice Accretion2060RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2060 | 15.8903 | 19.1487 | 23.276 | 26.4262 | 29.568
Elliot Lake Ice Accretion2065RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2065 | 15.9669 | 19.2704 | 23.452 | 26.6499 | 29.836
Elliot Lake Ice Accretion2070RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2070 | 15.6913 | 18.9965 | 23.1807 | 26.3765 | 29.5588
Elliot Lake Ice Accretion2075RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2075 | 15.3392 | 18.6009 | 22.7333 | 25.8793 | 29.0136
Elliot Lake Ice Accretion2080RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2080 | 14.9871 | 18.2052 | 22.286 | 25.3821 | 28.4684
Elliot Lake Ice Accretion2085RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2085 | 15.0101 | 18.26 | 22.374 | 25.4939 | 28.607
Elliot Lake Ice Accretion2090RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2090 | 15.0331 | 18.3148 | 22.462 | 25.6058 | 28.7456
Elliot Lake Ice Accretion2095RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2095 | 15.0331 | 18.3148 | 22.462 | 25.6058 | 28.7456
Elliot Lake Ice Accretion2100RCP8.5 | Elliot Lake | Ice Accretion | RCP8.5 | 2100 | 15.0331 | 18.3148 | 22.462 | 25.6058 | 28.7456
Elliot Lake Wind2023RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2023 | 76.8375 | 82.8057 | 89.0912 | 95.3747 | 101.6543
Elliot Lake Wind2025RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2025 | 76.9021 | 82.8739 | 89.1645 | 95.4516 | 101.7345
Elliot Lake Wind2030RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2030 | 76.9667 | 82.9421 | 89.2379 | 95.5285 | 101.8148
Elliot Lake Wind2035RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2035 | 77.0313 | 83.0103 | 89.3112 | 95.6054 | 101.895
Elliot Lake Wind2040RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2040 | 77.0959 | 83.0785 | 89.3845 | 95.6823 | 101.9753
Elliot Lake Wind2045RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2045 | 77.1604 | 83.1467 | 89.4579 | 95.7592 | 102.0555
Elliot Lake Wind2050RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2050 | 77.2843 | 83.2755 | 89.591 | 95.8982 | 102.2
Elliot Lake Wind2055RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2055 | 77.3436 | 83.336 | 89.6509 | 95.9603 | 102.2642
Elliot Lake Wind2060RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2060 | 77.4028 | 83.3966 | 89.7107 | 96.0225 | 102.3284
Elliot Lake Wind2065RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2065 | 77.4621 | 83.4572 | 89.7706 | 96.0846 | 102.3926
Elliot Lake Wind2070RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2070 | 77.5214 | 83.5177 | 89.8304 | 96.1468 | 102.4568
Elliot Lake Wind2075RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2075 | 77.5492 | 83.5532 | 89.8759 | 96.2001 | 102.5187
Elliot Lake Wind2080RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2080 | 77.5771 | 83.5886 | 89.9213 | 96.2535 | 102.5805
Elliot Lake Wind2085RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2085 | 77.605 | 83.6241 | 89.9668 | 96.3068 | 102.6424
Elliot Lake Wind2090RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2090 | 77.6328 | 83.6596 | 90.0123 | 96.3602 | 102.7043
Elliot Lake Wind2095RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2095 | 77.6607 | 83.695 | 90.0577 | 96.4136 | 102.7661
Elliot Lake Wind2100RCP4.5 | Elliot Lake | Wind | RCP4.5 | 2100 | 77.6886 | 83.7305 | 90.1032 | 96.4669 | 102.828
Elliot Lake Wind2023RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2023 | 76.8375 | 82.8057 | 89.0912 | 95.3747 | 101.6543
Elliot Lake Wind2025RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2025 | 76.9021 | 82.8739 | 89.1645 | 95.4516 | 101.7345
Elliot Lake Wind2030RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2030 | 76.9667 | 82.9421 | 89.2379 | 95.5285 | 101.8148
Elliot Lake Wind2035RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2035 | 77.0313 | 83.0103 | 89.3112 | 95.6054 | 101.895
Elliot Lake Wind2040RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2040 | 77.0959 | 83.0785 | 89.3845 | 95.6823 | 101.9753
Elliot Lake Wind2045RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2045 | 77.1604 | 83.1467 | 89.4579 | 95.7592 | 102.0555
Elliot Lake Wind2050RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2050 | 77.2843 | 83.2755 | 89.591 | 95.8982 | 102.2
Elliot Lake Wind2055RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2055 | 77.3436 | 83.336 | 89.6509 | 95.9603 | 102.2642
Elliot Lake Wind2060RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2060 | 77.4028 | 83.3966 | 89.7107 | 96.0225 | 102.3284
Elliot Lake Wind2065RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2065 | 77.4621 | 83.4572 | 89.7706 | 96.0846 | 102.3926
Elliot Lake Wind2070RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2070 | 77.5214 | 83.5177 | 89.8304 | 96.1468 | 102.4568
Elliot Lake Wind2075RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2075 | 77.5632 | 83.5709 | 89.8986 | 96.2268 | 102.5496
Elliot Lake Wind2080RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2080 | 77.605 | 83.6241 | 89.9668 | 96.3068 | 102.6424
Elliot Lake Wind2085RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2085 | 77.6468 | 83.6773 | 90.035 | 96.3869 | 102.7352
Elliot Lake Wind2090RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2090 | 77.9165 | 84.0142 | 90.4523 | 96.8687 | 103.2861
Elliot Lake Wind2095RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2095 | 78.1445 | 84.2979 | 90.8013 | 97.2704 | 103.7443
Elliot Lake Wind2100RCP6.0 | Elliot Lake | Wind | RCP6.0 | 2100 | 78.3724 | 84.5816 | 91.1504 | 97.6722 | 104.2024
Elliot Lake Wind2023RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2023 | 76.8375 | 82.8057 | 89.0912 | 95.3747 | 101.6543
Elliot Lake Wind2025RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2025 | 76.9667 | 82.9421 | 89.2379 | 95.5285 | 101.8148
Elliot Lake Wind2030RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2030 | 77.0959 | 83.0785 | 89.3845 | 95.6823 | 101.9753
Elliot Lake Wind2035RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2035 | 77.225 | 83.2149 | 89.5312 | 95.836 | 102.1358
Elliot Lake Wind2040RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2040 | 77.3238 | 83.3158 | 89.6309 | 95.9396 | 102.2428
Elliot Lake Wind2045RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2045 | 77.4226 | 83.4168 | 89.7307 | 96.0432 | 102.3498
Elliot Lake Wind2050RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2050 | 77.5771 | 83.5886 | 89.9213 | 96.2535 | 102.5805
Elliot Lake Wind2055RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2055 | 77.6328 | 83.6596 | 90.0123 | 96.3602 | 102.7043
Elliot Lake Wind2060RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2060 | 77.9165 | 84.0142 | 90.4523 | 96.8687 | 103.2861
Elliot Lake Wind2065RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2065 | 78.1445 | 84.2979 | 90.8013 | 97.2704 | 103.7443
Elliot Lake Wind2070RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2070 | 78.6865 | 84.9745 | 91.6403 | 98.2465 | 104.8612
Elliot Lake Wind2075RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2075 | 79.0006 | 85.3673 | 92.1301 | 98.8209 | 105.5199
Elliot Lake Wind2080RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2080 | 79.3147 | 85.7601 | 92.62 | 99.3953 | 106.1787
Elliot Lake Wind2085RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2085 | 79.516 | 85.9566 | 92.8048 | 99.5742 | 106.3542
Elliot Lake Wind2090RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2090 | 79.7174 | 86.153 | 92.9896 | 99.7531 | 106.5298
Elliot Lake Wind2095RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2095 | 79.7174 | 86.153 | 92.9896 | 99.7531 | 106.5298
Elliot Lake Wind2100RCP8.5 | Elliot Lake | Wind | RCP8.5 | 2100 | 79.7174 | 86.153 | 92.9896 | 99.7531 | 106.5298
ElmvaleIce Accretion2023RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2023 | 14.3059 | 17.1163 | 20.664 | 23.374 | 26.0631
ElmvaleIce Accretion2025RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2025 | 14.301 | 17.1134 | 20.6675 | 23.382 | 26.0807
ElmvaleIce Accretion2030RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2030 | 14.2962 | 17.1105 | 20.671 | 23.3899 | 26.0984
ElmvaleIce Accretion2035RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2035 | 14.2913 | 17.1075 | 20.6745 | 23.3978 | 26.116
ElmvaleIce Accretion2040RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2040 | 14.2864 | 17.1046 | 20.678 | 23.4057 | 26.1337
ElmvaleIce Accretion2045RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2045 | 14.2815 | 17.1017 | 20.6815 | 23.4136 | 26.1513
ElmvaleIce Accretion2050RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2050 | 14.2387 | 17.0709 | 20.6682 | 23.412 | 26.1636
ElmvaleIce Accretion2055RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2055 | 14.2007 | 17.0431 | 20.6514 | 23.4025 | 26.1584
ElmvaleIce Accretion2060RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2060 | 14.1627 | 17.0152 | 20.6346 | 23.393 | 26.1531
ElmvaleIce Accretion2065RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2065 | 14.1247 | 16.9873 | 20.6178 | 23.3835 | 26.1478
ElmvaleIce Accretion2070RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2070 | 14.0867 | 16.9594 | 20.601 | 23.374 | 26.1425
ElmvaleIce Accretion2075RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2075 | 14.0867 | 16.9797 | 20.6465 | 23.4373 | 26.2219
ElmvaleIce Accretion2080RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2080 | 14.0867 | 17.0001 | 20.692 | 23.5006 | 26.3012
ElmvaleIce Accretion2085RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2085 | 14.0867 | 17.0204 | 20.7375 | 23.5639 | 26.3806
ElmvaleIce Accretion2090RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2090 | 14.0867 | 17.0407 | 20.783 | 23.6272 | 26.46
ElmvaleIce Accretion2095RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2095 | 14.0867 | 17.0611 | 20.8285 | 23.6904 | 26.5394
ElmvaleIce Accretion2100RCP4.5 | Elmvale | Ice Accretion | RCP4.5 | 2100 | 14.0867 | 17.0814 | 20.874 | 23.7537 | 26.6188
ElmvaleIce Accretion2023RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2023 | 14.3059 | 17.1163 | 20.664 | 23.374 | 26.0631
ElmvaleIce Accretion2025RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2025 | 14.301 | 17.1134 | 20.6675 | 23.382 | 26.0807
ElmvaleIce Accretion2030RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2030 | 14.2962 | 17.1105 | 20.671 | 23.3899 | 26.0984
ElmvaleIce Accretion2035RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2035 | 14.2913 | 17.1075 | 20.6745 | 23.3978 | 26.116
ElmvaleIce Accretion2040RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2040 | 14.2864 | 17.1046 | 20.678 | 23.4057 | 26.1337
ElmvaleIce Accretion2045RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2045 | 14.2815 | 17.1017 | 20.6815 | 23.4136 | 26.1513
ElmvaleIce Accretion2050RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2050 | 14.2387 | 17.0709 | 20.6682 | 23.412 | 26.1636
ElmvaleIce Accretion2055RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2055 | 14.2007 | 17.0431 | 20.6514 | 23.4025 | 26.1584
ElmvaleIce Accretion2060RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2060 | 14.1627 | 17.0152 | 20.6346 | 23.393 | 26.1531
ElmvaleIce Accretion2065RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2065 | 14.1247 | 16.9873 | 20.6178 | 23.3835 | 26.1478
ElmvaleIce Accretion2070RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2070 | 14.0867 | 16.9594 | 20.601 | 23.374 | 26.1425
ElmvaleIce Accretion2075RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2075 | 14.0867 | 16.9899 | 20.6692 | 23.469 | 26.2615
ElmvaleIce Accretion2080RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2080 | 14.0867 | 17.0204 | 20.7375 | 23.5639 | 26.3806
ElmvaleIce Accretion2085RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2085 | 14.0867 | 17.0509 | 20.8057 | 23.6588 | 26.4997
ElmvaleIce Accretion2090RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2090 | 13.926 | 16.9187 | 20.713 | 23.5876 | 26.46
ElmvaleIce Accretion2095RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2095 | 13.7652 | 16.756 | 20.552 | 23.4215 | 26.3012
ElmvaleIce Accretion2100RCP6.0 | Elmvale | Ice Accretion | RCP6.0 | 2100 | 13.6045 | 16.5934 | 20.391 | 23.2554 | 26.1425
ElmvaleIce Accretion2023RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2023 | 14.3059 | 17.1163 | 20.664 | 23.374 | 26.0631
ElmvaleIce Accretion2025RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2025 | 14.2962 | 17.1105 | 20.671 | 23.3899 | 26.0984
ElmvaleIce Accretion2030RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2030 | 14.2864 | 17.1046 | 20.678 | 23.4057 | 26.1337
ElmvaleIce Accretion2035RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2035 | 14.2767 | 17.0988 | 20.685 | 23.4215 | 26.1689
ElmvaleIce Accretion2040RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2040 | 14.2134 | 17.0524 | 20.657 | 23.4057 | 26.1601
ElmvaleIce Accretion2045RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2045 | 14.15 | 17.0059 | 20.629 | 23.3899 | 26.1513
ElmvaleIce Accretion2050RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2050 | 14.0867 | 17.0001 | 20.692 | 23.5006 | 26.3012
ElmvaleIce Accretion2055RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2055 | 14.0867 | 17.0407 | 20.783 | 23.6272 | 26.46
ElmvaleIce Accretion2060RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2060 | 13.926 | 16.9187 | 20.713 | 23.5876 | 26.46
ElmvaleIce Accretion2065RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2065 | 13.7652 | 16.756 | 20.552 | 23.4215 | 26.3012
ElmvaleIce Accretion2070RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2070 | 13.3707 | 16.361 | 20.146 | 23.0102 | 25.8867
ElmvaleIce Accretion2075RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2075 | 13.1369 | 16.1286 | 19.901 | 22.765 | 25.6309
ElmvaleIce Accretion2080RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2080 | 12.9031 | 15.8962 | 19.656 | 22.5198 | 25.3751
ElmvaleIce Accretion2085RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2085 | 12.304 | 15.199 | 18.8475 | 21.618 | 24.3697
ElmvaleIce Accretion2090RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2090 | 11.7048 | 14.5018 | 18.039 | 20.7163 | 23.3642
ElmvaleIce Accretion2095RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2095 | 11.7048 | 14.5018 | 18.039 | 20.7163 | 23.3642
ElmvaleIce Accretion2100RCP8.5 | Elmvale | Ice Accretion | RCP8.5 | 2100 | 11.7048 | 14.5018 | 18.039 | 20.7163 | 23.3642
ElmvaleWind2023RCP4.5 | Elmvale | Wind | RCP4.5 | 2023 | 77.2419 | 83.2087 | 89.4895 | 95.7728 | 102.0485
ElmvaleWind2025RCP4.5 | Elmvale | Wind | RCP4.5 | 2025 | 77.2636 | 83.2363 | 89.5251 | 95.8141 | 102.0975
ElmvaleWind2030RCP4.5 | Elmvale | Wind | RCP4.5 | 2030 | 77.2854 | 83.2639 | 89.5607 | 95.8553 | 102.1465
ElmvaleWind2035RCP4.5 | Elmvale | Wind | RCP4.5 | 2035 | 77.3072 | 83.2915 | 89.5963 | 95.8966 | 102.1956
ElmvaleWind2040RCP4.5 | Elmvale | Wind | RCP4.5 | 2040 | 77.329 | 83.319 | 89.6319 | 95.9379 | 102.2446
ElmvaleWind2045RCP4.5 | Elmvale | Wind | RCP4.5 | 2045 | 77.3507 | 83.3466 | 89.6675 | 95.9791 | 102.2937
ElmvaleWind2050RCP4.5 | Elmvale | Wind | RCP4.5 | 2050 | 77.4939 | 83.5149 | 89.8651 | 96.2013 | 102.5436
ElmvaleWind2055RCP4.5 | Elmvale | Wind | RCP4.5 | 2055 | 77.6154 | 83.6556 | 90.0271 | 96.3823 | 102.7445
ElmvaleWind2060RCP4.5 | Elmvale | Wind | RCP4.5 | 2060 | 77.7368 | 83.7963 | 90.189 | 96.5632 | 102.9454
ElmvaleWind2065RCP4.5 | Elmvale | Wind | RCP4.5 | 2065 | 77.8582 | 83.9371 | 90.351 | 96.7442 | 103.1463
ElmvaleWind2070RCP4.5 | Elmvale | Wind | RCP4.5 | 2070 | 77.9796 | 84.0778 | 90.513 | 96.9251 | 103.3472
ElmvaleWind2075RCP4.5 | Elmvale | Wind | RCP4.5 | 2075 | 78.0385 | 84.155 | 90.6139 | 97.0457 | 103.4858
ElmvaleWind2080RCP4.5 | Elmvale | Wind | RCP4.5 | 2080 | 78.0975 | 84.2323 | 90.7147 | 97.1663 | 103.6245
ElmvaleWind2085RCP4.5 | Elmvale | Wind | RCP4.5 | 2085 | 78.1564 | 84.3095 | 90.8156 | 97.287 | 103.7631
ElmvaleWind2090RCP4.5 | Elmvale | Wind | RCP4.5 | 2090 | 78.2153 | 84.3868 | 90.9165 | 97.4076 | 103.9018
ElmvaleWind2095RCP4.5 | Elmvale | Wind | RCP4.5 | 2095 | 78.2742 | 84.464 | 91.0173 | 97.5282 | 104.0405
ElmvaleWind2100RCP4.5 | Elmvale | Wind | RCP4.5 | 2100 | 78.3331 | 84.5413 | 91.1182 | 97.6488 | 104.1791
ElmvaleWind2023RCP6.0 | Elmvale | Wind | RCP6.0 | 2023 | 77.2419 | 83.2087 | 89.4895 | 95.7728 | 102.0485
ElmvaleWind2025RCP6.0 | Elmvale | Wind | RCP6.0 | 2025 | 77.2636 | 83.2363 | 89.5251 | 95.8141 | 102.0975
ElmvaleWind2030RCP6.0 | Elmvale | Wind | RCP6.0 | 2030 | 77.2854 | 83.2639 | 89.5607 | 95.8553 | 102.1465
ElmvaleWind2035RCP6.0 | Elmvale | Wind | RCP6.0 | 2035 | 77.3072 | 83.2915 | 89.5963 | 95.8966 | 102.1956
ElmvaleWind2040RCP6.0 | Elmvale | Wind | RCP6.0 | 2040 | 77.329 | 83.319 | 89.6319 | 95.9379 | 102.2446
ElmvaleWind2045RCP6.0 | Elmvale | Wind | RCP6.0 | 2045 | 77.3507 | 83.3466 | 89.6675 | 95.9791 | 102.2937
ElmvaleWind2050RCP6.0 | Elmvale | Wind | RCP6.0 | 2050 | 77.4939 | 83.5149 | 89.8651 | 96.2013 | 102.5436
ElmvaleWind2055RCP6.0 | Elmvale | Wind | RCP6.0 | 2055 | 77.6154 | 83.6556 | 90.0271 | 96.3823 | 102.7445
ElmvaleWind2060RCP6.0 | Elmvale | Wind | RCP6.0 | 2060 | 77.7368 | 83.7963 | 90.189 | 96.5632 | 102.9454
ElmvaleWind2065RCP6.0 | Elmvale | Wind | RCP6.0 | 2065 | 77.8582 | 83.9371 | 90.351 | 96.7442 | 103.1463
ElmvaleWind2070RCP6.0 | Elmvale | Wind | RCP6.0 | 2070 | 77.9796 | 84.0778 | 90.513 | 96.9251 | 103.3472
ElmvaleWind2075RCP6.0 | Elmvale | Wind | RCP6.0 | 2075 | 78.068 | 84.1936 | 90.6643 | 97.106 | 103.5551
ElmvaleWind2080RCP6.0 | Elmvale | Wind | RCP6.0 | 2080 | 78.1564 | 84.3095 | 90.8156 | 97.287 | 103.7631
ElmvaleWind2085RCP6.0 | Elmvale | Wind | RCP6.0 | 2085 | 78.2448 | 84.4254 | 90.9669 | 97.4679 | 103.9711
ElmvaleWind2090RCP6.0 | Elmvale | Wind | RCP6.0 | 2090 | 78.6124 | 84.8779 | 91.5217 | 98.1123 | 104.7067
ElmvaleWind2095RCP6.0 | Elmvale | Wind | RCP6.0 | 2095 | 78.8916 | 85.2145 | 91.9251 | 98.5757 | 105.2343
ElmvaleWind2100RCP6.0 | Elmvale | Wind | RCP6.0 | 2100 | 79.1708 | 85.5511 | 92.3286 | 99.0392 | 105.7619
ElmvaleWind2023RCP8.5 | Elmvale | Wind | RCP8.5 | 2023 | 77.2419 | 83.2087 | 89.4895 | 95.7728 | 102.0485
ElmvaleWind2025RCP8.5 | Elmvale | Wind | RCP8.5 | 2025 | 77.2854 | 83.2639 | 89.5607 | 95.8553 | 102.1465
ElmvaleWind2030RCP8.5 | Elmvale | Wind | RCP8.5 | 2030 | 77.329 | 83.319 | 89.6319 | 95.9379 | 102.2446
ElmvaleWind2035RCP8.5 | Elmvale | Wind | RCP8.5 | 2035 | 77.3725 | 83.3742 | 89.7031 | 96.0204 | 102.3427
ElmvaleWind2040RCP8.5 | Elmvale | Wind | RCP8.5 | 2040 | 77.5749 | 83.6087 | 89.9731 | 96.322 | 102.6775
ElmvaleWind2045RCP8.5 | Elmvale | Wind | RCP8.5 | 2045 | 77.7773 | 83.8433 | 90.243 | 96.6235 | 103.0123
ElmvaleWind2050RCP8.5 | Elmvale | Wind | RCP8.5 | 2050 | 78.0975 | 84.2323 | 90.7147 | 97.1663 | 103.6245
ElmvaleWind2055RCP8.5 | Elmvale | Wind | RCP8.5 | 2055 | 78.2153 | 84.3868 | 90.9165 | 97.4076 | 103.9018
ElmvaleWind2060RCP8.5 | Elmvale | Wind | RCP8.5 | 2060 | 78.6124 | 84.8779 | 91.5217 | 98.1123 | 104.7067
ElmvaleWind2065RCP8.5 | Elmvale | Wind | RCP8.5 | 2065 | 78.8916 | 85.2145 | 91.9251 | 98.5757 | 105.2343
ElmvaleWind2070RCP8.5 | Elmvale | Wind | RCP8.5 | 2070 | 79.3194 | 85.7304 | 92.5511 | 99.2963 | 106.0528
ElmvaleWind2075RCP8.5 | Elmvale | Wind | RCP8.5 | 2075 | 79.468 | 85.9097 | 92.7736 | 99.5534 | 106.3436
ElmvaleWind2080RCP8.5 | Elmvale | Wind | RCP8.5 | 2080 | 79.6165 | 86.0891 | 92.9961 | 99.8106 | 106.6345
ElmvaleWind2085RCP8.5 | Elmvale | Wind | RCP8.5 | 2085 | 79.6473 | 86.1222 | 93.0273 | 99.8439 | 106.6649
ElmvaleWind2090RCP8.5 | Elmvale | Wind | RCP8.5 | 2090 | 79.678 | 86.1553 | 93.0584 | 99.8772 | 106.6953
ElmvaleWind2095RCP8.5 | Elmvale | Wind | RCP8.5 | 2095 | 79.678 | 86.1553 | 93.0584 | 99.8772 | 106.6953
ElmvaleWind2100RCP8.5 | Elmvale | Wind | RCP8.5 | 2100 | 79.678 | 86.1553 | 93.0584 | 99.8772 | 106.6953
EmbroIce Accretion2023RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
EmbroIce Accretion2025RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2025 | 20.3952 | 24.4642 | 29.605 | 33.5328 | 37.4661
EmbroIce Accretion2030RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2030 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
EmbroIce Accretion2035RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2035 | 20.3117 | 24.3895 | 29.535 | 33.4763 | 37.4031
EmbroIce Accretion2040RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2040 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
EmbroIce Accretion2045RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2045 | 20.2282 | 24.3148 | 29.465 | 33.4198 | 37.3401
EmbroIce Accretion2050RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2050 | 20.0571 | 24.153 | 29.316 | 33.2762 | 37.2028
EmbroIce Accretion2055RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2055 | 19.9276 | 24.0285 | 29.202 | 33.161 | 37.0969
EmbroIce Accretion2060RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2060 | 19.7982 | 23.904 | 29.088 | 33.0457 | 36.9911
EmbroIce Accretion2065RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2065 | 19.6688 | 23.7795 | 28.974 | 32.9305 | 36.8852
EmbroIce Accretion2070RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2070 | 19.5394 | 23.655 | 28.86 | 32.8152 | 36.7794
EmbroIce Accretion2075RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2075 | 19.4837 | 23.6135 | 28.84 | 32.8095 | 36.7857
EmbroIce Accretion2080RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2080 | 19.428 | 23.572 | 28.82 | 32.8039 | 36.792
EmbroIce Accretion2085RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2085 | 19.3724 | 23.5305 | 28.8 | 32.7982 | 36.7983
EmbroIce Accretion2090RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2090 | 19.3167 | 23.489 | 28.78 | 32.7926 | 36.8046
EmbroIce Accretion2095RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2095 | 19.261 | 23.4475 | 28.76 | 32.7869 | 36.8109
EmbroIce Accretion2100RCP4.5 | Embro | Ice Accretion | RCP4.5 | 2100 | 19.2054 | 23.406 | 28.74 | 32.7813 | 36.8172
EmbroIce Accretion2023RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
EmbroIce Accretion2025RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2025 | 20.3952 | 24.4642 | 29.605 | 33.5328 | 37.4661
EmbroIce Accretion2030RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2030 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
EmbroIce Accretion2035RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2035 | 20.3117 | 24.3895 | 29.535 | 33.4763 | 37.4031
EmbroIce Accretion2040RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2040 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
EmbroIce Accretion2045RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2045 | 20.2282 | 24.3148 | 29.465 | 33.4198 | 37.3401
EmbroIce Accretion2050RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2050 | 20.0571 | 24.153 | 29.316 | 33.2762 | 37.2028
EmbroIce Accretion2055RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2055 | 19.9276 | 24.0285 | 29.202 | 33.161 | 37.0969
EmbroIce Accretion2060RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2060 | 19.7982 | 23.904 | 29.088 | 33.0457 | 36.9911
EmbroIce Accretion2065RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2065 | 19.6688 | 23.7795 | 28.974 | 32.9305 | 36.8852
EmbroIce Accretion2070RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2070 | 19.5394 | 23.655 | 28.86 | 32.8152 | 36.7794
EmbroIce Accretion2075RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2075 | 19.4559 | 23.5927 | 28.83 | 32.8067 | 36.7888
EmbroIce Accretion2080RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2080 | 19.3724 | 23.5305 | 28.8 | 32.7982 | 36.7983
EmbroIce Accretion2085RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2085 | 19.2889 | 23.4682 | 28.77 | 32.7898 | 36.8077
EmbroIce Accretion2090RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2090 | 18.7739 | 22.9412 | 28.21 | 32.2163 | 36.1998
EmbroIce Accretion2095RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2095 | 18.3425 | 22.4764 | 27.68 | 31.6513 | 35.5824
EmbroIce Accretion2100RCP6.0 | Embro | Ice Accretion | RCP6.0 | 2100 | 17.9111 | 22.0116 | 27.15 | 31.0863 | 34.965
EmbroIce Accretion2023RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
EmbroIce Accretion2025RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2025 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
EmbroIce Accretion2030RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2030 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
EmbroIce Accretion2035RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2035 | 20.1865 | 24.2775 | 29.43 | 33.3915 | 37.3086
EmbroIce Accretion2040RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2040 | 19.9708 | 24.07 | 29.24 | 33.1994 | 37.1322
EmbroIce Accretion2045RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2045 | 19.7551 | 23.8625 | 29.05 | 33.0073 | 36.9558
EmbroIce Accretion2050RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2050 | 19.428 | 23.572 | 28.82 | 32.8039 | 36.792
EmbroIce Accretion2055RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2055 | 19.3167 | 23.489 | 28.78 | 32.7926 | 36.8046
EmbroIce Accretion2060RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2060 | 18.7739 | 22.9412 | 28.21 | 32.2163 | 36.1998
EmbroIce Accretion2065RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2065 | 18.3425 | 22.4764 | 27.68 | 31.6513 | 35.5824
EmbroIce Accretion2070RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2070 | 17.5353 | 21.6049 | 26.71 | 30.6117 | 34.461
EmbroIce Accretion2075RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2075 | 17.1596 | 21.1982 | 26.27 | 30.1371 | 33.957
EmbroIce Accretion2080RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2080 | 16.7838 | 20.7915 | 25.83 | 29.6625 | 33.453
EmbroIce Accretion2085RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2085 | 15.8549 | 19.7208 | 24.57 | 28.2387 | 31.9032
EmbroIce Accretion2090RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2090 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
EmbroIce Accretion2095RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2095 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
EmbroIce Accretion2100RCP8.5 | Embro | Ice Accretion | RCP8.5 | 2100 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
EmbroWind2023RCP4.5 | Embro | Wind | RCP4.5 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
EmbroWind2025RCP4.5 | Embro | Wind | RCP4.5 | 2025 | 87.206 | 94.102 | 101.4083 | 108.6746 | 115.9494
EmbroWind2030RCP4.5 | Embro | Wind | RCP4.5 | 2030 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
EmbroWind2035RCP4.5 | Embro | Wind | RCP4.5 | 2035 | 87.3672 | 94.316 | 101.685 | 109.0063 | 116.337
EmbroWind2040RCP4.5 | Embro | Wind | RCP4.5 | 2040 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
EmbroWind2045RCP4.5 | Embro | Wind | RCP4.5 | 2045 | 87.5283 | 94.5299 | 101.9617 | 109.338 | 116.7246
EmbroWind2050RCP4.5 | Embro | Wind | RCP4.5 | 2050 | 87.678 | 94.7205 | 102.206 | 109.6258 | 117.0575
EmbroWind2055RCP4.5 | Embro | Wind | RCP4.5 | 2055 | 87.7471 | 94.8042 | 102.312 | 109.7478 | 117.1966
EmbroWind2060RCP4.5 | Embro | Wind | RCP4.5 | 2060 | 87.8162 | 94.8879 | 102.418 | 109.8697 | 117.3356
EmbroWind2065RCP4.5 | Embro | Wind | RCP4.5 | 2065 | 87.8852 | 94.9716 | 102.524 | 109.9917 | 117.4747
EmbroWind2070RCP4.5 | Embro | Wind | RCP4.5 | 2070 | 87.9543 | 95.0553 | 102.63 | 110.1137 | 117.6138
EmbroWind2075RCP4.5 | Embro | Wind | RCP4.5 | 2075 | 88.0407 | 95.1746 | 102.7917 | 110.3117 | 117.8494
EmbroWind2080RCP4.5 | Embro | Wind | RCP4.5 | 2080 | 88.127 | 95.294 | 102.9533 | 110.5096 | 118.085
EmbroWind2085RCP4.5 | Embro | Wind | RCP4.5 | 2085 | 88.2134 | 95.4134 | 103.115 | 110.7075 | 118.3206
EmbroWind2090RCP4.5 | Embro | Wind | RCP4.5 | 2090 | 88.2997 | 95.5327 | 103.2767 | 110.9055 | 118.5562
EmbroWind2095RCP4.5 | Embro | Wind | RCP4.5 | 2095 | 88.3861 | 95.6521 | 103.4383 | 111.1034 | 118.7918
EmbroWind2100RCP4.5 | Embro | Wind | RCP4.5 | 2100 | 88.4724 | 95.7714 | 103.6 | 111.3014 | 119.0274
EmbroWind2023RCP6.0 | Embro | Wind | RCP6.0 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
EmbroWind2025RCP6.0 | Embro | Wind | RCP6.0 | 2025 | 87.206 | 94.102 | 101.4083 | 108.6746 | 115.9494
EmbroWind2030RCP6.0 | Embro | Wind | RCP6.0 | 2030 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
EmbroWind2035RCP6.0 | Embro | Wind | RCP6.0 | 2035 | 87.3672 | 94.316 | 101.685 | 109.0063 | 116.337
EmbroWind2040RCP6.0 | Embro | Wind | RCP6.0 | 2040 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
EmbroWind2045RCP6.0 | Embro | Wind | RCP6.0 | 2045 | 87.5283 | 94.5299 | 101.9617 | 109.338 | 116.7246
EmbroWind2050RCP6.0 | Embro | Wind | RCP6.0 | 2050 | 87.678 | 94.7205 | 102.206 | 109.6258 | 117.0575
EmbroWind2055RCP6.0 | Embro | Wind | RCP6.0 | 2055 | 87.7471 | 94.8042 | 102.312 | 109.7478 | 117.1966
EmbroWind2060RCP6.0 | Embro | Wind | RCP6.0 | 2060 | 87.8162 | 94.8879 | 102.418 | 109.8697 | 117.3356
EmbroWind2065RCP6.0 | Embro | Wind | RCP6.0 | 2065 | 87.8852 | 94.9716 | 102.524 | 109.9917 | 117.4747
EmbroWind2070RCP6.0 | Embro | Wind | RCP6.0 | 2070 | 87.9543 | 95.0553 | 102.63 | 110.1137 | 117.6138
EmbroWind2075RCP6.0 | Embro | Wind | RCP6.0 | 2075 | 88.0838 | 95.2343 | 102.8725 | 110.4106 | 117.9672
EmbroWind2080RCP6.0 | Embro | Wind | RCP6.0 | 2080 | 88.2134 | 95.4134 | 103.115 | 110.7075 | 118.3206
EmbroWind2085RCP6.0 | Embro | Wind | RCP6.0 | 2085 | 88.3429 | 95.5924 | 103.3575 | 111.0045 | 118.674
EmbroWind2090RCP6.0 | Embro | Wind | RCP6.0 | 2090 | 88.8264 | 96.2271 | 104.18 | 111.9862 | 119.8216
EmbroWind2095RCP6.0 | Embro | Wind | RCP6.0 | 2095 | 89.1805 | 96.6828 | 104.76 | 112.671 | 120.6158
EmbroWind2100RCP6.0 | Embro | Wind | RCP6.0 | 2100 | 89.5345 | 97.1385 | 105.34 | 113.3558 | 121.41
EmbroWind2023RCP8.5 | Embro | Wind | RCP8.5 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
EmbroWind2025RCP8.5 | Embro | Wind | RCP8.5 | 2025 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
EmbroWind2030RCP8.5 | Embro | Wind | RCP8.5 | 2030 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
EmbroWind2035RCP8.5 | Embro | Wind | RCP8.5 | 2035 | 87.6089 | 94.6368 | 102.1 | 109.5038 | 116.9184
EmbroWind2040RCP8.5 | Embro | Wind | RCP8.5 | 2040 | 87.7241 | 94.7763 | 102.2767 | 109.7071 | 117.1502
EmbroWind2045RCP8.5 | Embro | Wind | RCP8.5 | 2045 | 87.8392 | 94.9158 | 102.4533 | 109.9104 | 117.382
EmbroWind2050RCP8.5 | Embro | Wind | RCP8.5 | 2050 | 88.127 | 95.294 | 102.9533 | 110.5096 | 118.085
EmbroWind2055RCP8.5 | Embro | Wind | RCP8.5 | 2055 | 88.2997 | 95.5327 | 103.2767 | 110.9055 | 118.5562
EmbroWind2060RCP8.5 | Embro | Wind | RCP8.5 | 2060 | 88.8264 | 96.2271 | 104.18 | 111.9862 | 119.8216
EmbroWind2065RCP8.5 | Embro | Wind | RCP8.5 | 2065 | 89.1805 | 96.6828 | 104.76 | 112.671 | 120.6158
EmbroWind2070RCP8.5 | Embro | Wind | RCP8.5 | 2070 | 89.759 | 97.4392 | 105.7367 | 113.8337 | 121.9724
EmbroWind2075RCP8.5 | Embro | Wind | RCP8.5 | 2075 | 89.9835 | 97.7399 | 106.1333 | 114.3117 | 122.5348
EmbroWind2080RCP8.5 | Embro | Wind | RCP8.5 | 2080 | 90.208 | 98.0406 | 106.53 | 114.7896 | 123.0972
EmbroWind2085RCP8.5 | Embro | Wind | RCP8.5 | 2085 | 90.6484 | 98.6172 | 107.285 | 115.6937 | 124.1517
EmbroWind2090RCP8.5 | Embro | Wind | RCP8.5 | 2090 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
EmbroWind2095RCP8.5 | Embro | Wind | RCP8.5 | 2095 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
EmbroWind2100RCP8.5 | Embro | Wind | RCP8.5 | 2100 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
EnglehartIce Accretion2023RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2023 | 14.6545 | 17.5296 | 21.16 | 23.9334 | 26.712
EnglehartIce Accretion2025RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2025 | 14.6638 | 17.5407 | 21.1733 | 23.9522 | 26.733
EnglehartIce Accretion2030RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2030 | 14.6731 | 17.5517 | 21.1867 | 23.9711 | 26.754
EnglehartIce Accretion2035RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2035 | 14.6824 | 17.5628 | 21.2 | 23.9899 | 26.775
EnglehartIce Accretion2040RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2040 | 14.6916 | 17.5739 | 21.2133 | 24.0087 | 26.796
EnglehartIce Accretion2045RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2045 | 14.7009 | 17.5849 | 21.2267 | 24.0276 | 26.817
EnglehartIce Accretion2050RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2050 | 14.816 | 17.7321 | 21.416 | 24.2498 | 27.0698
EnglehartIce Accretion2055RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2055 | 14.9217 | 17.8682 | 21.592 | 24.4532 | 27.3017
EnglehartIce Accretion2060RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2060 | 15.0275 | 18.0044 | 21.768 | 24.6566 | 27.5335
EnglehartIce Accretion2065RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2065 | 15.1333 | 18.1405 | 21.944 | 24.86 | 27.7654
EnglehartIce Accretion2070RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2070 | 15.239 | 18.2766 | 22.12 | 25.0634 | 27.9972
EnglehartIce Accretion2075RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2075 | 15.3249 | 18.39 | 22.2667 | 25.2367 | 28.1988
EnglehartIce Accretion2080RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2080 | 15.4107 | 18.5035 | 22.4133 | 25.4099 | 28.4004
EnglehartIce Accretion2085RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2085 | 15.4965 | 18.6169 | 22.56 | 25.5832 | 28.602
EnglehartIce Accretion2090RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2090 | 15.5823 | 18.7303 | 22.7067 | 25.7565 | 28.8036
EnglehartIce Accretion2095RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2095 | 15.6681 | 18.8438 | 22.8533 | 25.9297 | 29.0052
EnglehartIce Accretion2100RCP4.5 | Englehart | Ice Accretion | RCP4.5 | 2100 | 15.754 | 18.9572 | 23 | 26.103 | 29.2068
EnglehartIce Accretion2023RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2023 | 14.6545 | 17.5296 | 21.16 | 23.9334 | 26.712
EnglehartIce Accretion2025RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2025 | 14.6638 | 17.5407 | 21.1733 | 23.9522 | 26.733
EnglehartIce Accretion2030RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2030 | 14.6731 | 17.5517 | 21.1867 | 23.9711 | 26.754
EnglehartIce Accretion2035RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2035 | 14.6824 | 17.5628 | 21.2 | 23.9899 | 26.775
EnglehartIce Accretion2040RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2040 | 14.6916 | 17.5739 | 21.2133 | 24.0087 | 26.796
EnglehartIce Accretion2045RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2045 | 14.7009 | 17.5849 | 21.2267 | 24.0276 | 26.817
EnglehartIce Accretion2050RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2050 | 14.816 | 17.7321 | 21.416 | 24.2498 | 27.0698
EnglehartIce Accretion2055RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2055 | 14.9217 | 17.8682 | 21.592 | 24.4532 | 27.3017
EnglehartIce Accretion2060RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2060 | 15.0275 | 18.0044 | 21.768 | 24.6566 | 27.5335
EnglehartIce Accretion2065RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2065 | 15.1333 | 18.1405 | 21.944 | 24.86 | 27.7654
EnglehartIce Accretion2070RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2070 | 15.239 | 18.2766 | 22.12 | 25.0634 | 27.9972
EnglehartIce Accretion2075RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2075 | 15.3678 | 18.4467 | 22.34 | 25.3233 | 28.2996
EnglehartIce Accretion2080RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2080 | 15.4965 | 18.6169 | 22.56 | 25.5832 | 28.602
EnglehartIce Accretion2085RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2085 | 15.6252 | 18.787 | 22.78 | 25.8431 | 28.9044
EnglehartIce Accretion2090RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2090 | 15.7586 | 18.9793 | 23.0467 | 26.1633 | 29.274
EnglehartIce Accretion2095RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2095 | 15.7632 | 19.0015 | 23.0933 | 26.2235 | 29.3412
EnglehartIce Accretion2100RCP6.0 | Englehart | Ice Accretion | RCP6.0 | 2100 | 15.7679 | 19.0236 | 23.14 | 26.2838 | 29.4084
EnglehartIce Accretion2023RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2023 | 14.6545 | 17.5296 | 21.16 | 23.9334 | 26.712
EnglehartIce Accretion2025RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2025 | 14.6731 | 17.5517 | 21.1867 | 23.9711 | 26.754
EnglehartIce Accretion2030RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2030 | 14.6916 | 17.5739 | 21.2133 | 24.0087 | 26.796
EnglehartIce Accretion2035RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2035 | 14.7102 | 17.596 | 21.24 | 24.0464 | 26.838
EnglehartIce Accretion2040RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2040 | 14.8865 | 17.8229 | 21.5333 | 24.3854 | 27.2244
EnglehartIce Accretion2045RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2045 | 15.0627 | 18.0497 | 21.8267 | 24.7244 | 27.6108
EnglehartIce Accretion2050RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2050 | 15.4107 | 18.5035 | 22.4133 | 25.4099 | 28.4004
EnglehartIce Accretion2055RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2055 | 15.5823 | 18.7303 | 22.7067 | 25.7565 | 28.8036
EnglehartIce Accretion2060RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2060 | 15.7586 | 18.9793 | 23.0467 | 26.1633 | 29.274
EnglehartIce Accretion2065RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2065 | 15.7632 | 19.0015 | 23.0933 | 26.2235 | 29.3412
EnglehartIce Accretion2070RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2070 | 15.5359 | 18.7469 | 22.8067 | 25.9071 | 28.9968
EnglehartIce Accretion2075RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2075 | 15.304 | 18.4703 | 22.4733 | 25.5305 | 28.5852
EnglehartIce Accretion2080RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2080 | 15.072 | 18.1936 | 22.14 | 25.1538 | 28.1736
EnglehartIce Accretion2085RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2085 | 14.8841 | 18.0027 | 21.94 | 24.9391 | 27.9468
EnglehartIce Accretion2090RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2090 | 14.6963 | 17.8118 | 21.74 | 24.7244 | 27.72
EnglehartIce Accretion2095RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2095 | 14.6963 | 17.8118 | 21.74 | 24.7244 | 27.72
EnglehartIce Accretion2100RCP8.5 | Englehart | Ice Accretion | RCP8.5 | 2100 | 14.6963 | 17.8118 | 21.74 | 24.7244 | 27.72
EnglehartWind2023RCP4.5 | Englehart | Wind | RCP4.5 | 2023 | 73.004 | 78.6043 | 84.4788 | 90.3654 | 96.258
EnglehartWind2025RCP4.5 | Englehart | Wind | RCP4.5 | 2025 | 73.0668 | 78.6707 | 84.553 | 90.4447 | 96.3425
EnglehartWind2030RCP4.5 | Englehart | Wind | RCP4.5 | 2030 | 73.1297 | 78.7371 | 84.6272 | 90.5241 | 96.4271
EnglehartWind2035RCP4.5 | Englehart | Wind | RCP4.5 | 2035 | 73.1926 | 78.8036 | 84.7014 | 90.6035 | 96.5117
EnglehartWind2040RCP4.5 | Englehart | Wind | RCP4.5 | 2040 | 73.2554 | 78.87 | 84.7756 | 90.6829 | 96.5963
EnglehartWind2045RCP4.5 | Englehart | Wind | RCP4.5 | 2045 | 73.3183 | 78.9364 | 84.8498 | 90.7623 | 96.6809
EnglehartWind2050RCP4.5 | Englehart | Wind | RCP4.5 | 2050 | 73.4 | 79.0168 | 84.929 | 90.8417 | 96.7578
EnglehartWind2055RCP4.5 | Englehart | Wind | RCP4.5 | 2055 | 73.4189 | 79.0309 | 84.9341 | 90.8417 | 96.7502
EnglehartWind2060RCP4.5 | Englehart | Wind | RCP4.5 | 2060 | 73.4377 | 79.0449 | 84.9391 | 90.8417 | 96.7425
EnglehartWind2065RCP4.5 | Englehart | Wind | RCP4.5 | 2065 | 73.4566 | 79.059 | 84.9442 | 90.8417 | 96.7348
EnglehartWind2070RCP4.5 | Englehart | Wind | RCP4.5 | 2070 | 73.4754 | 79.0731 | 84.9492 | 90.8417 | 96.7272
EnglehartWind2075RCP4.5 | Englehart | Wind | RCP4.5 | 2075 | 73.5165 | 79.1225 | 85.008 | 90.9091 | 96.8038
EnglehartWind2080RCP4.5 | Englehart | Wind | RCP4.5 | 2080 | 73.5577 | 79.172 | 85.0668 | 90.9765 | 96.8804
EnglehartWind2085RCP4.5 | Englehart | Wind | RCP4.5 | 2085 | 73.5988 | 79.2215 | 85.1256 | 91.0439 | 96.957
EnglehartWind2090RCP4.5 | Englehart | Wind | RCP4.5 | 2090 | 73.6399 | 79.271 | 85.1844 | 91.1114 | 97.0336
EnglehartWind2095RCP4.5 | Englehart | Wind | RCP4.5 | 2095 | 73.681 | 79.3204 | 85.2432 | 91.1788 | 97.1102
EnglehartWind2100RCP4.5 | Englehart | Wind | RCP4.5 | 2100 | 73.7221 | 79.3699 | 85.302 | 91.2462 | 97.1868
EnglehartWind2023RCP6.0 | Englehart | Wind | RCP6.0 | 2023 | 73.004 | 78.6043 | 84.4788 | 90.3654 | 96.258
EnglehartWind2025RCP6.0 | Englehart | Wind | RCP6.0 | 2025 | 73.0668 | 78.6707 | 84.553 | 90.4447 | 96.3425
EnglehartWind2030RCP6.0 | Englehart | Wind | RCP6.0 | 2030 | 73.1297 | 78.7371 | 84.6272 | 90.5241 | 96.4271
EnglehartWind2035RCP6.0 | Englehart | Wind | RCP6.0 | 2035 | 73.1926 | 78.8036 | 84.7014 | 90.6035 | 96.5117
EnglehartWind2040RCP6.0 | Englehart | Wind | RCP6.0 | 2040 | 73.2554 | 78.87 | 84.7756 | 90.6829 | 96.5963
EnglehartWind2045RCP6.0 | Englehart | Wind | RCP6.0 | 2045 | 73.3183 | 78.9364 | 84.8498 | 90.7623 | 96.6809
EnglehartWind2050RCP6.0 | Englehart | Wind | RCP6.0 | 2050 | 73.4 | 79.0168 | 84.929 | 90.8417 | 96.7578
EnglehartWind2055RCP6.0 | Englehart | Wind | RCP6.0 | 2055 | 73.4189 | 79.0309 | 84.9341 | 90.8417 | 96.7502
EnglehartWind2060RCP6.0 | Englehart | Wind | RCP6.0 | 2060 | 73.4377 | 79.0449 | 84.9391 | 90.8417 | 96.7425
EnglehartWind2065RCP6.0 | Englehart | Wind | RCP6.0 | 2065 | 73.4566 | 79.059 | 84.9442 | 90.8417 | 96.7348
EnglehartWind2070RCP6.0 | Englehart | Wind | RCP6.0 | 2070 | 73.4754 | 79.0731 | 84.9492 | 90.8417 | 96.7272
EnglehartWind2075RCP6.0 | Englehart | Wind | RCP6.0 | 2075 | 73.5371 | 79.1473 | 85.0374 | 90.9428 | 96.8421
EnglehartWind2080RCP6.0 | Englehart | Wind | RCP6.0 | 2080 | 73.5988 | 79.2215 | 85.1256 | 91.0439 | 96.957
EnglehartWind2085RCP6.0 | Englehart | Wind | RCP6.0 | 2085 | 73.6604 | 79.2957 | 85.2138 | 91.1451 | 97.0719
EnglehartWind2090RCP6.0 | Englehart | Wind | RCP6.0 | 2090 | 73.7632 | 79.409 | 85.3412 | 91.2851 | 97.2283
EnglehartWind2095RCP6.0 | Englehart | Wind | RCP6.0 | 2095 | 73.8043 | 79.448 | 85.3804 | 91.3241 | 97.2698
EnglehartWind2100RCP6.0 | Englehart | Wind | RCP6.0 | 2100 | 73.8454 | 79.4871 | 85.4196 | 91.363 | 97.3113
EnglehartWind2023RCP8.5 | Englehart | Wind | RCP8.5 | 2023 | 73.004 | 78.6043 | 84.4788 | 90.3654 | 96.258
EnglehartWind2025RCP8.5 | Englehart | Wind | RCP8.5 | 2025 | 73.1297 | 78.7371 | 84.6272 | 90.5241 | 96.4271
EnglehartWind2030RCP8.5 | Englehart | Wind | RCP8.5 | 2030 | 73.2554 | 78.87 | 84.7756 | 90.6829 | 96.5963
EnglehartWind2035RCP8.5 | Englehart | Wind | RCP8.5 | 2035 | 73.3812 | 79.0028 | 84.924 | 90.8417 | 96.7655
EnglehartWind2040RCP8.5 | Englehart | Wind | RCP8.5 | 2040 | 73.4126 | 79.0262 | 84.9324 | 90.8417 | 96.7527
EnglehartWind2045RCP8.5 | Englehart | Wind | RCP8.5 | 2045 | 73.444 | 79.0496 | 84.9408 | 90.8417 | 96.7399
EnglehartWind2050RCP8.5 | Englehart | Wind | RCP8.5 | 2050 | 73.5577 | 79.172 | 85.0668 | 90.9765 | 96.8804
EnglehartWind2055RCP8.5 | Englehart | Wind | RCP8.5 | 2055 | 73.6399 | 79.271 | 85.1844 | 91.1114 | 97.0336
EnglehartWind2060RCP8.5 | Englehart | Wind | RCP8.5 | 2060 | 73.7632 | 79.409 | 85.3412 | 91.2851 | 97.2283
EnglehartWind2065RCP8.5 | Englehart | Wind | RCP8.5 | 2065 | 73.8043 | 79.448 | 85.3804 | 91.3241 | 97.2698
EnglehartWind2070RCP8.5 | Englehart | Wind | RCP8.5 | 2070 | 73.959 | 79.6017 | 85.5344 | 91.4799 | 97.4262
EnglehartWind2075RCP8.5 | Englehart | Wind | RCP8.5 | 2075 | 74.0726 | 79.7163 | 85.6492 | 91.5967 | 97.5411
EnglehartWind2080RCP8.5 | Englehart | Wind | RCP8.5 | 2080 | 74.1863 | 79.8308 | 85.764 | 91.7136 | 97.656
EnglehartWind2085RCP8.5 | Englehart | Wind | RCP8.5 | 2085 | 74.1863 | 79.8425 | 85.7892 | 91.7495 | 97.7039
EnglehartWind2090RCP8.5 | Englehart | Wind | RCP8.5 | 2090 | 74.1863 | 79.8543 | 85.8144 | 91.7855 | 97.7518
EnglehartWind2095RCP8.5 | Englehart | Wind | RCP8.5 | 2095 | 74.1863 | 79.8543 | 85.8144 | 91.7855 | 97.7518
EnglehartWind2100RCP8.5 | Englehart | Wind | RCP8.5 | 2100 | 74.1863 | 79.8543 | 85.8144 | 91.7855 | 97.7518
EspanolaIce Accretion2023RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2023 | 15.7066 | 18.8261 | 22.792 | 25.8295 | 28.8288
EspanolaIce Accretion2025RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2025 | 15.6888 | 18.8169 | 22.792 | 25.8337 | 28.8427
EspanolaIce Accretion2030RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2030 | 15.6709 | 18.8078 | 22.792 | 25.8378 | 28.8565
EspanolaIce Accretion2035RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2035 | 15.6531 | 18.7987 | 22.792 | 25.842 | 28.8704
EspanolaIce Accretion2040RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2040 | 15.6352 | 18.7895 | 22.792 | 25.8461 | 28.8842
EspanolaIce Accretion2045RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2045 | 15.6173 | 18.7804 | 22.792 | 25.8503 | 28.8981
EspanolaIce Accretion2050RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2050 | 15.6607 | 18.8626 | 22.924 | 26.0185 | 29.106
EspanolaIce Accretion2055RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2055 | 15.7219 | 18.9539 | 23.056 | 26.1826 | 29.3
EspanolaIce Accretion2060RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2060 | 15.7832 | 19.0452 | 23.188 | 26.3466 | 29.4941
EspanolaIce Accretion2065RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2065 | 15.8444 | 19.1365 | 23.32 | 26.5107 | 29.6881
EspanolaIce Accretion2070RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2070 | 15.9057 | 19.2278 | 23.452 | 26.6748 | 29.8822
EspanolaIce Accretion2075RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2075 | 15.7781 | 19.0847 | 23.287 | 26.4925 | 29.6835
EspanolaIce Accretion2080RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2080 | 15.6505 | 18.9417 | 23.122 | 26.3102 | 29.4848
EspanolaIce Accretion2085RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2085 | 15.5229 | 18.7987 | 22.957 | 26.1279 | 29.2862
EspanolaIce Accretion2090RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2090 | 15.3954 | 18.6556 | 22.792 | 25.9456 | 29.0875
EspanolaIce Accretion2095RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2095 | 15.2678 | 18.5126 | 22.627 | 25.7632 | 28.8889
EspanolaIce Accretion2100RCP4.5 | Espanola | Ice Accretion | RCP4.5 | 2100 | 15.1402 | 18.3696 | 22.462 | 25.5809 | 28.6902
EspanolaIce Accretion2023RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2023 | 15.7066 | 18.8261 | 22.792 | 25.8295 | 28.8288
EspanolaIce Accretion2025RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2025 | 15.6888 | 18.8169 | 22.792 | 25.8337 | 28.8427
EspanolaIce Accretion2030RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2030 | 15.6709 | 18.8078 | 22.792 | 25.8378 | 28.8565
EspanolaIce Accretion2035RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2035 | 15.6531 | 18.7987 | 22.792 | 25.842 | 28.8704
EspanolaIce Accretion2040RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2040 | 15.6352 | 18.7895 | 22.792 | 25.8461 | 28.8842
EspanolaIce Accretion2045RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2045 | 15.6173 | 18.7804 | 22.792 | 25.8503 | 28.8981
EspanolaIce Accretion2050RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2050 | 15.6607 | 18.8626 | 22.924 | 26.0185 | 29.106
EspanolaIce Accretion2055RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2055 | 15.7219 | 18.9539 | 23.056 | 26.1826 | 29.3
EspanolaIce Accretion2060RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2060 | 15.7832 | 19.0452 | 23.188 | 26.3466 | 29.4941
EspanolaIce Accretion2065RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2065 | 15.8444 | 19.1365 | 23.32 | 26.5107 | 29.6881
EspanolaIce Accretion2070RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2070 | 15.9057 | 19.2278 | 23.452 | 26.6748 | 29.8822
EspanolaIce Accretion2075RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2075 | 15.7143 | 19.0132 | 23.2045 | 26.4013 | 29.5842
EspanolaIce Accretion2080RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2080 | 15.5229 | 18.7987 | 22.957 | 26.1279 | 29.2862
EspanolaIce Accretion2085RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2085 | 15.3316 | 18.5841 | 22.7095 | 25.8544 | 28.9882
EspanolaIce Accretion2090RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2090 | 15.1351 | 18.3939 | 22.5207 | 25.6638 | 28.7918
EspanolaIce Accretion2095RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2095 | 15.13 | 18.4183 | 22.5793 | 25.7467 | 28.8935
EspanolaIce Accretion2100RCP6.0 | Espanola | Ice Accretion | RCP6.0 | 2100 | 15.1249 | 18.4426 | 22.638 | 25.8295 | 28.9951
EspanolaIce Accretion2023RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2023 | 15.7066 | 18.8261 | 22.792 | 25.8295 | 28.8288
EspanolaIce Accretion2025RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2025 | 15.6709 | 18.8078 | 22.792 | 25.8378 | 28.8565
EspanolaIce Accretion2030RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2030 | 15.6352 | 18.7895 | 22.792 | 25.8461 | 28.8842
EspanolaIce Accretion2035RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2035 | 15.5995 | 18.7713 | 22.792 | 25.8544 | 28.912
EspanolaIce Accretion2040RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2040 | 15.7015 | 18.9234 | 23.012 | 26.1279 | 29.2354
EspanolaIce Accretion2045RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2045 | 15.8036 | 19.0756 | 23.232 | 26.4013 | 29.5588
EspanolaIce Accretion2050RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2050 | 15.6505 | 18.9417 | 23.122 | 26.3102 | 29.4848
EspanolaIce Accretion2055RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2055 | 15.3954 | 18.6556 | 22.792 | 25.9456 | 29.0875
EspanolaIce Accretion2060RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2060 | 15.1351 | 18.3939 | 22.5207 | 25.6638 | 28.7918
EspanolaIce Accretion2065RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2065 | 15.13 | 18.4183 | 22.5793 | 25.7467 | 28.8935
EspanolaIce Accretion2070RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2070 | 14.6248 | 17.8583 | 21.9487 | 25.0589 | 28.145
EspanolaIce Accretion2075RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2075 | 14.1247 | 17.274 | 21.2593 | 24.2882 | 27.295
EspanolaIce Accretion2080RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2080 | 13.6247 | 16.6896 | 20.57 | 23.5176 | 26.4449
EspanolaIce Accretion2085RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2085 | 13.3185 | 16.361 | 20.207 | 23.1198 | 26.0291
EspanolaIce Accretion2090RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2090 | 13.0123 | 16.0323 | 19.844 | 22.722 | 25.6133
EspanolaIce Accretion2095RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2095 | 13.0123 | 16.0323 | 19.844 | 22.722 | 25.6133
EspanolaIce Accretion2100RCP8.5 | Espanola | Ice Accretion | RCP8.5 | 2100 | 13.0123 | 16.0323 | 19.844 | 22.722 | 25.6133
EspanolaWind2023RCP4.5 | Espanola | Wind | RCP4.5 | 2023 | 81.9141 | 88.233 | 94.893 | 101.5456 | 108.1887
EspanolaWind2025RCP4.5 | Espanola | Wind | RCP4.5 | 2025 | 82.0237 | 88.3612 | 95.0418 | 101.7149 | 108.3781
EspanolaWind2030RCP4.5 | Espanola | Wind | RCP4.5 | 2030 | 82.1332 | 88.4894 | 95.1907 | 101.8842 | 108.5674
EspanolaWind2035RCP4.5 | Espanola | Wind | RCP4.5 | 2035 | 82.2428 | 88.6177 | 95.3395 | 102.0535 | 108.7567
EspanolaWind2040RCP4.5 | Espanola | Wind | RCP4.5 | 2040 | 82.3524 | 88.7459 | 95.4883 | 102.2228 | 108.946
EspanolaWind2045RCP4.5 | Espanola | Wind | RCP4.5 | 2045 | 82.462 | 88.8741 | 95.6372 | 102.3921 | 109.1353
EspanolaWind2050RCP4.5 | Espanola | Wind | RCP4.5 | 2050 | 82.6771 | 89.1264 | 95.9326 | 102.7264 | 109.5111
EspanolaWind2055RCP4.5 | Espanola | Wind | RCP4.5 | 2055 | 82.7826 | 89.2506 | 96.0793 | 102.8913 | 109.6975
EspanolaWind2060RCP4.5 | Espanola | Wind | RCP4.5 | 2060 | 82.8881 | 89.3747 | 96.2259 | 103.0563 | 109.884
EspanolaWind2065RCP4.5 | Espanola | Wind | RCP4.5 | 2065 | 82.9936 | 89.4988 | 96.3726 | 103.2212 | 110.0705
EspanolaWind2070RCP4.5 | Espanola | Wind | RCP4.5 | 2070 | 83.0991 | 89.623 | 96.5192 | 103.3862 | 110.2569
EspanolaWind2075RCP4.5 | Espanola | Wind | RCP4.5 | 2075 | 83.1465 | 89.6827 | 96.5944 | 103.475 | 110.3587
EspanolaWind2080RCP4.5 | Espanola | Wind | RCP4.5 | 2080 | 83.1938 | 89.7425 | 96.6696 | 103.5639 | 110.4605
EspanolaWind2085RCP4.5 | Espanola | Wind | RCP4.5 | 2085 | 83.2412 | 89.8022 | 96.7448 | 103.6527 | 110.5623
EspanolaWind2090RCP4.5 | Espanola | Wind | RCP4.5 | 2090 | 83.2885 | 89.8619 | 96.82 | 103.7416 | 110.6641
EspanolaWind2095RCP4.5 | Espanola | Wind | RCP4.5 | 2095 | 83.3359 | 89.9217 | 96.8952 | 103.8304 | 110.7659
EspanolaWind2100RCP4.5 | Espanola | Wind | RCP4.5 | 2100 | 83.3832 | 89.9814 | 96.9704 | 103.9193 | 110.8677
EspanolaWind2023RCP6.0 | Espanola | Wind | RCP6.0 | 2023 | 81.9141 | 88.233 | 94.893 | 101.5456 | 108.1887
EspanolaWind2025RCP6.0 | Espanola | Wind | RCP6.0 | 2025 | 82.0237 | 88.3612 | 95.0418 | 101.7149 | 108.3781
EspanolaWind2030RCP6.0 | Espanola | Wind | RCP6.0 | 2030 | 82.1332 | 88.4894 | 95.1907 | 101.8842 | 108.5674
EspanolaWind2035RCP6.0 | Espanola | Wind | RCP6.0 | 2035 | 82.2428 | 88.6177 | 95.3395 | 102.0535 | 108.7567
EspanolaWind2040RCP6.0 | Espanola | Wind | RCP6.0 | 2040 | 82.3524 | 88.7459 | 95.4883 | 102.2228 | 108.946
EspanolaWind2045RCP6.0 | Espanola | Wind | RCP6.0 | 2045 | 82.462 | 88.8741 | 95.6372 | 102.3921 | 109.1353
EspanolaWind2050RCP6.0 | Espanola | Wind | RCP6.0 | 2050 | 82.6771 | 89.1264 | 95.9326 | 102.7264 | 109.5111
EspanolaWind2055RCP6.0 | Espanola | Wind | RCP6.0 | 2055 | 82.7826 | 89.2506 | 96.0793 | 102.8913 | 109.6975
EspanolaWind2060RCP6.0 | Espanola | Wind | RCP6.0 | 2060 | 82.8881 | 89.3747 | 96.2259 | 103.0563 | 109.884
EspanolaWind2065RCP6.0 | Espanola | Wind | RCP6.0 | 2065 | 82.9936 | 89.4988 | 96.3726 | 103.2212 | 110.0705
EspanolaWind2070RCP6.0 | Espanola | Wind | RCP6.0 | 2070 | 83.0991 | 89.623 | 96.5192 | 103.3862 | 110.2569
EspanolaWind2075RCP6.0 | Espanola | Wind | RCP6.0 | 2075 | 83.1702 | 89.7126 | 96.632 | 103.5195 | 110.4096
EspanolaWind2080RCP6.0 | Espanola | Wind | RCP6.0 | 2080 | 83.2412 | 89.8022 | 96.7448 | 103.6527 | 110.5623
EspanolaWind2085RCP6.0 | Espanola | Wind | RCP6.0 | 2085 | 83.3122 | 89.8918 | 96.8576 | 103.786 | 110.715
EspanolaWind2090RCP6.0 | Espanola | Wind | RCP6.0 | 2090 | 83.6673 | 90.3398 | 97.4247 | 104.4523 | 111.4821
EspanolaWind2095RCP6.0 | Espanola | Wind | RCP6.0 | 2095 | 83.9514 | 90.6983 | 97.8791 | 104.9854 | 112.0965
EspanolaWind2100RCP6.0 | Espanola | Wind | RCP6.0 | 2100 | 84.2355 | 91.0567 | 98.3334 | 105.5185 | 112.7109
EspanolaWind2023RCP8.5 | Espanola | Wind | RCP8.5 | 2023 | 81.9141 | 88.233 | 94.893 | 101.5456 | 108.1887
EspanolaWind2025RCP8.5 | Espanola | Wind | RCP8.5 | 2025 | 82.1332 | 88.4894 | 95.1907 | 101.8842 | 108.5674
EspanolaWind2030RCP8.5 | Espanola | Wind | RCP8.5 | 2030 | 82.3524 | 88.7459 | 95.4883 | 102.2228 | 108.946
EspanolaWind2035RCP8.5 | Espanola | Wind | RCP8.5 | 2035 | 82.5715 | 89.0023 | 95.786 | 102.5614 | 109.3246
EspanolaWind2040RCP8.5 | Espanola | Wind | RCP8.5 | 2040 | 82.7474 | 89.2092 | 96.0304 | 102.8363 | 109.6354
EspanolaWind2045RCP8.5 | Espanola | Wind | RCP8.5 | 2045 | 82.9233 | 89.4161 | 96.2748 | 103.1113 | 109.9462
EspanolaWind2050RCP8.5 | Espanola | Wind | RCP8.5 | 2050 | 83.1938 | 89.7425 | 96.6696 | 103.5639 | 110.4605
EspanolaWind2055RCP8.5 | Espanola | Wind | RCP8.5 | 2055 | 83.2885 | 89.8619 | 96.82 | 103.7416 | 110.6641
EspanolaWind2060RCP8.5 | Espanola | Wind | RCP8.5 | 2060 | 83.6673 | 90.3398 | 97.4247 | 104.4523 | 111.4821
EspanolaWind2065RCP8.5 | Espanola | Wind | RCP8.5 | 2065 | 83.9514 | 90.6983 | 97.8791 | 104.9854 | 112.0965
EspanolaWind2070RCP8.5 | Espanola | Wind | RCP8.5 | 2070 | 84.4817 | 91.351 | 98.6843 | 105.9208 | 113.1645
EspanolaWind2075RCP8.5 | Espanola | Wind | RCP8.5 | 2075 | 84.7279 | 91.6453 | 99.0353 | 106.3231 | 113.6182
EspanolaWind2080RCP8.5 | Espanola | Wind | RCP8.5 | 2080 | 84.9741 | 91.9396 | 99.3862 | 106.7254 | 114.0718
EspanolaWind2085RCP8.5 | Espanola | Wind | RCP8.5 | 2085 | 85.3353 | 92.3942 | 99.9549 | 107.3893 | 114.8327
EspanolaWind2090RCP8.5 | Espanola | Wind | RCP8.5 | 2090 | 85.6965 | 92.8488 | 100.5236 | 108.0531 | 115.5935
EspanolaWind2095RCP8.5 | Espanola | Wind | RCP8.5 | 2095 | 85.6965 | 92.8488 | 100.5236 | 108.0531 | 115.5935
EspanolaWind2100RCP8.5 | Espanola | Wind | RCP8.5 | 2100 | 85.6965 | 92.8488 | 100.5236 | 108.0531 | 115.5935
EtobicokeIce Accretion2023RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
EtobicokeIce Accretion2025RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2025 | 17.4222 | 20.9229 | 25.3542 | 28.7444 | 32.1247
EtobicokeIce Accretion2030RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2030 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
EtobicokeIce Accretion2035RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2035 | 17.5092 | 21.0612 | 25.5625 | 28.9986 | 32.4292
EtobicokeIce Accretion2040RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2040 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
EtobicokeIce Accretion2045RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2045 | 17.5962 | 21.1996 | 25.7708 | 29.2529 | 32.7338
EtobicokeIce Accretion2050RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2050 | 17.5214 | 21.1484 | 25.745 | 29.2444 | 32.7411
EtobicokeIce Accretion2055RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2055 | 17.4031 | 21.0281 | 25.615 | 29.1088 | 32.5962
EtobicokeIce Accretion2060RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2060 | 17.2848 | 20.9077 | 25.485 | 28.9732 | 32.4513
EtobicokeIce Accretion2065RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2065 | 17.1665 | 20.7873 | 25.355 | 28.8376 | 32.3064
EtobicokeIce Accretion2070RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2070 | 17.0482 | 20.667 | 25.225 | 28.702 | 32.1615
EtobicokeIce Accretion2075RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2075 | 17.0105 | 20.6497 | 25.2333 | 28.7255 | 32.2035
EtobicokeIce Accretion2080RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2080 | 16.9728 | 20.6324 | 25.2417 | 28.7491 | 32.2455
EtobicokeIce Accretion2085RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2085 | 16.9352 | 20.6151 | 25.25 | 28.7726 | 32.2875
EtobicokeIce Accretion2090RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2090 | 16.8975 | 20.5978 | 25.2583 | 28.7962 | 32.3295
EtobicokeIce Accretion2095RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2095 | 16.8598 | 20.5805 | 25.2667 | 28.8197 | 32.3715
EtobicokeIce Accretion2100RCP4.5 | Etobicoke | Ice Accretion | RCP4.5 | 2100 | 16.8221 | 20.5633 | 25.275 | 28.8432 | 32.4135
EtobicokeIce Accretion2023RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
EtobicokeIce Accretion2025RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2025 | 17.4222 | 20.9229 | 25.3542 | 28.7444 | 32.1247
EtobicokeIce Accretion2030RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2030 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
EtobicokeIce Accretion2035RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2035 | 17.5092 | 21.0612 | 25.5625 | 28.9986 | 32.4292
EtobicokeIce Accretion2040RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2040 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
EtobicokeIce Accretion2045RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2045 | 17.5962 | 21.1996 | 25.7708 | 29.2529 | 32.7338
EtobicokeIce Accretion2050RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2050 | 17.5214 | 21.1484 | 25.745 | 29.2444 | 32.7411
EtobicokeIce Accretion2055RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2055 | 17.4031 | 21.0281 | 25.615 | 29.1088 | 32.5962
EtobicokeIce Accretion2060RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2060 | 17.2848 | 20.9077 | 25.485 | 28.9732 | 32.4513
EtobicokeIce Accretion2065RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2065 | 17.1665 | 20.7873 | 25.355 | 28.8376 | 32.3064
EtobicokeIce Accretion2070RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2070 | 17.0482 | 20.667 | 25.225 | 28.702 | 32.1615
EtobicokeIce Accretion2075RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2075 | 16.9917 | 20.6411 | 25.2375 | 28.7373 | 32.2245
EtobicokeIce Accretion2080RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2080 | 16.9352 | 20.6151 | 25.25 | 28.7726 | 32.2875
EtobicokeIce Accretion2085RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2085 | 16.8786 | 20.5892 | 25.2625 | 28.8079 | 32.3505
EtobicokeIce Accretion2090RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2090 | 16.5147 | 20.2382 | 24.925 | 28.4854 | 32.0355
EtobicokeIce Accretion2095RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2095 | 16.2074 | 19.9131 | 24.575 | 28.1276 | 31.6575
EtobicokeIce Accretion2100RCP6.0 | Etobicoke | Ice Accretion | RCP6.0 | 2100 | 15.9001 | 19.588 | 24.225 | 27.7697 | 31.2795
EtobicokeIce Accretion2023RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
EtobicokeIce Accretion2025RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2025 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
EtobicokeIce Accretion2030RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2030 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
EtobicokeIce Accretion2035RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2035 | 17.6397 | 21.2687 | 25.875 | 29.38 | 32.886
EtobicokeIce Accretion2040RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2040 | 17.4425 | 21.0682 | 25.6583 | 29.154 | 32.6445
EtobicokeIce Accretion2045RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2045 | 17.2454 | 20.8676 | 25.4417 | 28.928 | 32.403
EtobicokeIce Accretion2050RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2050 | 16.9728 | 20.6324 | 25.2417 | 28.7491 | 32.2455
EtobicokeIce Accretion2055RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2055 | 16.8975 | 20.5978 | 25.2583 | 28.7962 | 32.3295
EtobicokeIce Accretion2060RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2060 | 16.5147 | 20.2382 | 24.925 | 28.4854 | 32.0355
EtobicokeIce Accretion2065RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2065 | 16.2074 | 19.9131 | 24.575 | 28.1276 | 31.6575
EtobicokeIce Accretion2070RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2070 | 15.5116 | 19.173 | 23.775 | 27.2801 | 30.765
EtobicokeIce Accretion2075RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2075 | 15.1231 | 18.758 | 23.325 | 26.7904 | 30.2505
EtobicokeIce Accretion2080RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2080 | 14.7345 | 18.343 | 22.875 | 26.3007 | 29.736
EtobicokeIce Accretion2085RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2085 | 13.9691 | 17.4404 | 21.8 | 25.1001 | 28.3972
EtobicokeIce Accretion2090RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2090 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
EtobicokeIce Accretion2095RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2095 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
EtobicokeIce Accretion2100RCP8.5 | Etobicoke | Ice Accretion | RCP8.5 | 2100 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
EtobicokeWind2023RCP4.5 | Etobicoke | Wind | RCP4.5 | 2023 | 84.9344 | 91.4772 | 98.3626 | 105.248 | 112.1334
EtobicokeWind2025RCP4.5 | Etobicoke | Wind | RCP4.5 | 2025 | 84.9612 | 91.5152 | 98.4149 | 105.3126 | 112.2116
EtobicokeWind2030RCP4.5 | Etobicoke | Wind | RCP4.5 | 2030 | 84.988 | 91.5532 | 98.4671 | 105.3773 | 112.2898
EtobicokeWind2035RCP4.5 | Etobicoke | Wind | RCP4.5 | 2035 | 85.0148 | 91.5911 | 98.5194 | 105.442 | 112.368
EtobicokeWind2040RCP4.5 | Etobicoke | Wind | RCP4.5 | 2040 | 85.0416 | 91.6291 | 98.5717 | 105.5066 | 112.4462
EtobicokeWind2045RCP4.5 | Etobicoke | Wind | RCP4.5 | 2045 | 85.0684 | 91.6671 | 98.6239 | 105.5713 | 112.5244
EtobicokeWind2050RCP4.5 | Etobicoke | Wind | RCP4.5 | 2050 | 85.151 | 91.7579 | 98.7252 | 105.6821 | 112.645
EtobicokeWind2055RCP4.5 | Etobicoke | Wind | RCP4.5 | 2055 | 85.2069 | 91.8108 | 98.7742 | 105.7282 | 112.6875
EtobicokeWind2060RCP4.5 | Etobicoke | Wind | RCP4.5 | 2060 | 85.2627 | 91.8637 | 98.8232 | 105.7744 | 112.7299
EtobicokeWind2065RCP4.5 | Etobicoke | Wind | RCP4.5 | 2065 | 85.3186 | 91.9165 | 98.8722 | 105.8205 | 112.7724
EtobicokeWind2070RCP4.5 | Etobicoke | Wind | RCP4.5 | 2070 | 85.3744 | 91.9694 | 98.9212 | 105.8667 | 112.8149
EtobicokeWind2075RCP4.5 | Etobicoke | Wind | RCP4.5 | 2075 | 85.4562 | 92.0818 | 99.0715 | 106.0484 | 113.029
EtobicokeWind2080RCP4.5 | Etobicoke | Wind | RCP4.5 | 2080 | 85.538 | 92.1942 | 99.2217 | 106.2302 | 113.2431
EtobicokeWind2085RCP4.5 | Etobicoke | Wind | RCP4.5 | 2085 | 85.6198 | 92.3066 | 99.372 | 106.4119 | 113.4572
EtobicokeWind2090RCP4.5 | Etobicoke | Wind | RCP4.5 | 2090 | 85.7016 | 92.419 | 99.5223 | 106.5937 | 113.6714
EtobicokeWind2095RCP4.5 | Etobicoke | Wind | RCP4.5 | 2095 | 85.7834 | 92.5314 | 99.6725 | 106.7754 | 113.8855
EtobicokeWind2100RCP4.5 | Etobicoke | Wind | RCP4.5 | 2100 | 85.8652 | 92.6438 | 99.8228 | 106.9572 | 114.0996
EtobicokeWind2023RCP6.0 | Etobicoke | Wind | RCP6.0 | 2023 | 84.9344 | 91.4772 | 98.3626 | 105.248 | 112.1334
EtobicokeWind2025RCP6.0 | Etobicoke | Wind | RCP6.0 | 2025 | 84.9612 | 91.5152 | 98.4149 | 105.3126 | 112.2116
EtobicokeWind2030RCP6.0 | Etobicoke | Wind | RCP6.0 | 2030 | 84.988 | 91.5532 | 98.4671 | 105.3773 | 112.2898
EtobicokeWind2035RCP6.0 | Etobicoke | Wind | RCP6.0 | 2035 | 85.0148 | 91.5911 | 98.5194 | 105.442 | 112.368
EtobicokeWind2040RCP6.0 | Etobicoke | Wind | RCP6.0 | 2040 | 85.0416 | 91.6291 | 98.5717 | 105.5066 | 112.4462
EtobicokeWind2045RCP6.0 | Etobicoke | Wind | RCP6.0 | 2045 | 85.0684 | 91.6671 | 98.6239 | 105.5713 | 112.5244
EtobicokeWind2050RCP6.0 | Etobicoke | Wind | RCP6.0 | 2050 | 85.151 | 91.7579 | 98.7252 | 105.6821 | 112.645
EtobicokeWind2055RCP6.0 | Etobicoke | Wind | RCP6.0 | 2055 | 85.2069 | 91.8108 | 98.7742 | 105.7282 | 112.6875
EtobicokeWind2060RCP6.0 | Etobicoke | Wind | RCP6.0 | 2060 | 85.2627 | 91.8637 | 98.8232 | 105.7744 | 112.7299
EtobicokeWind2065RCP6.0 | Etobicoke | Wind | RCP6.0 | 2065 | 85.3186 | 91.9165 | 98.8722 | 105.8205 | 112.7724
EtobicokeWind2070RCP6.0 | Etobicoke | Wind | RCP6.0 | 2070 | 85.3744 | 91.9694 | 98.9212 | 105.8667 | 112.8149
EtobicokeWind2075RCP6.0 | Etobicoke | Wind | RCP6.0 | 2075 | 85.4971 | 92.138 | 99.1466 | 106.1393 | 113.1361
EtobicokeWind2080RCP6.0 | Etobicoke | Wind | RCP6.0 | 2080 | 85.6198 | 92.3066 | 99.372 | 106.4119 | 113.4572
EtobicokeWind2085RCP6.0 | Etobicoke | Wind | RCP6.0 | 2085 | 85.7425 | 92.4752 | 99.5974 | 106.6846 | 113.7784
EtobicokeWind2090RCP6.0 | Etobicoke | Wind | RCP6.0 | 2090 | 86.1501 | 92.9962 | 100.2573 | 107.464 | 114.6806
EtobicokeWind2095RCP6.0 | Etobicoke | Wind | RCP6.0 | 2095 | 86.435 | 93.3486 | 100.6917 | 107.9708 | 115.2615
EtobicokeWind2100RCP6.0 | Etobicoke | Wind | RCP6.0 | 2100 | 86.7199 | 93.701 | 101.1262 | 108.4777 | 115.8425
EtobicokeWind2023RCP8.5 | Etobicoke | Wind | RCP8.5 | 2023 | 84.9344 | 91.4772 | 98.3626 | 105.248 | 112.1334
EtobicokeWind2025RCP8.5 | Etobicoke | Wind | RCP8.5 | 2025 | 84.988 | 91.5532 | 98.4671 | 105.3773 | 112.2898
EtobicokeWind2030RCP8.5 | Etobicoke | Wind | RCP8.5 | 2030 | 85.0416 | 91.6291 | 98.5717 | 105.5066 | 112.4462
EtobicokeWind2035RCP8.5 | Etobicoke | Wind | RCP8.5 | 2035 | 85.0952 | 91.7051 | 98.6762 | 105.636 | 112.6026
EtobicokeWind2040RCP8.5 | Etobicoke | Wind | RCP8.5 | 2040 | 85.1882 | 91.7932 | 98.7579 | 105.7129 | 112.6733
EtobicokeWind2045RCP8.5 | Etobicoke | Wind | RCP8.5 | 2045 | 85.2813 | 91.8813 | 98.8395 | 105.7898 | 112.7441
EtobicokeWind2050RCP8.5 | Etobicoke | Wind | RCP8.5 | 2050 | 85.538 | 92.1942 | 99.2217 | 106.2302 | 113.2431
EtobicokeWind2055RCP8.5 | Etobicoke | Wind | RCP8.5 | 2055 | 85.7016 | 92.419 | 99.5223 | 106.5937 | 113.6714
EtobicokeWind2060RCP8.5 | Etobicoke | Wind | RCP8.5 | 2060 | 86.1501 | 92.9962 | 100.2573 | 107.464 | 114.6806
EtobicokeWind2065RCP8.5 | Etobicoke | Wind | RCP8.5 | 2065 | 86.435 | 93.3486 | 100.6917 | 107.9708 | 115.2615
EtobicokeWind2070RCP8.5 | Etobicoke | Wind | RCP8.5 | 2070 | 86.9371 | 93.9927 | 101.5117 | 108.9425 | 116.3862
EtobicokeWind2075RCP8.5 | Etobicoke | Wind | RCP8.5 | 2075 | 87.1543 | 94.2843 | 101.8971 | 109.4074 | 116.9299
EtobicokeWind2080RCP8.5 | Etobicoke | Wind | RCP8.5 | 2080 | 87.3715 | 94.576 | 102.2826 | 109.8723 | 117.4736
EtobicokeWind2085RCP8.5 | Etobicoke | Wind | RCP8.5 | 2085 | 87.4815 | 94.7218 | 102.4786 | 110.103 | 117.7473
EtobicokeWind2090RCP8.5 | Etobicoke | Wind | RCP8.5 | 2090 | 87.5915 | 94.8676 | 102.6746 | 110.3337 | 118.021
EtobicokeWind2095RCP8.5 | Etobicoke | Wind | RCP8.5 | 2095 | 87.5915 | 94.8676 | 102.6746 | 110.3337 | 118.021
EtobicokeWind2100RCP8.5 | Etobicoke | Wind | RCP8.5 | 2100 | 87.5915 | 94.8676 | 102.6746 | 110.3337 | 118.021
ExeterIce Accretion2023RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2023 | 15.0637 | 18.0591 | 21.824 | 24.7108 | 27.5814
ExeterIce Accretion2025RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2025 | 15.079 | 18.0896 | 21.879 | 24.7813 | 27.6692
ExeterIce Accretion2030RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2030 | 15.0943 | 18.12 | 21.934 | 24.8517 | 27.757
ExeterIce Accretion2035RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2035 | 15.1096 | 18.1504 | 21.989 | 24.9221 | 27.8447
ExeterIce Accretion2040RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2040 | 15.1249 | 18.1809 | 22.044 | 24.9926 | 27.9325
ExeterIce Accretion2045RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2045 | 15.1402 | 18.2113 | 22.099 | 25.063 | 28.0203
ExeterIce Accretion2050RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2050 | 15.0943 | 18.1979 | 22.1276 | 25.1185 | 28.1081
ExeterIce Accretion2055RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2055 | 15.0331 | 18.1541 | 22.1012 | 25.1036 | 28.1081
ExeterIce Accretion2060RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2060 | 14.9718 | 18.1103 | 22.0748 | 25.0887 | 28.1081
ExeterIce Accretion2065RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2065 | 14.9106 | 18.0664 | 22.0484 | 25.0738 | 28.1081
ExeterIce Accretion2070RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2070 | 14.8494 | 18.0226 | 22.022 | 25.0589 | 28.1081
ExeterIce Accretion2075RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2075 | 14.8213 | 18.0104 | 22.033 | 25.0837 | 28.1497
ExeterIce Accretion2080RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2080 | 14.7932 | 17.9983 | 22.044 | 25.1086 | 28.1912
ExeterIce Accretion2085RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2085 | 14.7652 | 17.9861 | 22.055 | 25.1335 | 28.2328
ExeterIce Accretion2090RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2090 | 14.7371 | 17.9739 | 22.066 | 25.1583 | 28.2744
ExeterIce Accretion2095RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2095 | 14.709 | 17.9618 | 22.077 | 25.1832 | 28.316
ExeterIce Accretion2100RCP4.5 | Exeter | Ice Accretion | RCP4.5 | 2100 | 14.681 | 17.9496 | 22.088 | 25.208 | 28.3576
ExeterIce Accretion2023RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2023 | 15.0637 | 18.0591 | 21.824 | 24.7108 | 27.5814
ExeterIce Accretion2025RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2025 | 15.079 | 18.0896 | 21.879 | 24.7813 | 27.6692
ExeterIce Accretion2030RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2030 | 15.0943 | 18.12 | 21.934 | 24.8517 | 27.757
ExeterIce Accretion2035RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2035 | 15.1096 | 18.1504 | 21.989 | 24.9221 | 27.8447
ExeterIce Accretion2040RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2040 | 15.1249 | 18.1809 | 22.044 | 24.9926 | 27.9325
ExeterIce Accretion2045RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2045 | 15.1402 | 18.2113 | 22.099 | 25.063 | 28.0203
ExeterIce Accretion2050RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2050 | 15.0943 | 18.1979 | 22.1276 | 25.1185 | 28.1081
ExeterIce Accretion2055RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2055 | 15.0331 | 18.1541 | 22.1012 | 25.1036 | 28.1081
ExeterIce Accretion2060RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2060 | 14.9718 | 18.1103 | 22.0748 | 25.0887 | 28.1081
ExeterIce Accretion2065RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2065 | 14.9106 | 18.0664 | 22.0484 | 25.0738 | 28.1081
ExeterIce Accretion2070RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2070 | 14.8494 | 18.0226 | 22.022 | 25.0589 | 28.1081
ExeterIce Accretion2075RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2075 | 14.8073 | 18.0044 | 22.0385 | 25.0962 | 28.1704
ExeterIce Accretion2080RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2080 | 14.7652 | 17.9861 | 22.055 | 25.1335 | 28.2328
ExeterIce Accretion2085RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2085 | 14.7231 | 17.9678 | 22.0715 | 25.1707 | 28.2952
ExeterIce Accretion2090RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2090 | 14.4973 | 17.767 | 21.8973 | 25.0174 | 28.1543
ExeterIce Accretion2095RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2095 | 14.3136 | 17.5844 | 21.7067 | 24.8269 | 27.951
ExeterIce Accretion2100RCP6.0 | Exeter | Ice Accretion | RCP6.0 | 2100 | 14.1299 | 17.4018 | 21.516 | 24.6363 | 27.7477
ExeterIce Accretion2023RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2023 | 15.0637 | 18.0591 | 21.824 | 24.7108 | 27.5814
ExeterIce Accretion2025RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2025 | 15.0943 | 18.12 | 21.934 | 24.8517 | 27.757
ExeterIce Accretion2030RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2030 | 15.1249 | 18.1809 | 22.044 | 24.9926 | 27.9325
ExeterIce Accretion2035RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2035 | 15.1555 | 18.2417 | 22.154 | 25.1335 | 28.1081
ExeterIce Accretion2040RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2040 | 15.0535 | 18.1687 | 22.11 | 25.1086 | 28.1081
ExeterIce Accretion2045RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2045 | 14.9514 | 18.0957 | 22.066 | 25.0837 | 28.1081
ExeterIce Accretion2050RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2050 | 14.7932 | 17.9983 | 22.044 | 25.1086 | 28.1912
ExeterIce Accretion2055RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2055 | 14.7371 | 17.9739 | 22.066 | 25.1583 | 28.2744
ExeterIce Accretion2060RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2060 | 14.4973 | 17.767 | 21.8973 | 25.0174 | 28.1543
ExeterIce Accretion2065RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2065 | 14.3136 | 17.5844 | 21.7067 | 24.8269 | 27.951
ExeterIce Accretion2070RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2070 | 13.7982 | 17.0305 | 21.098 | 24.1805 | 27.2488
ExeterIce Accretion2075RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2075 | 13.4665 | 16.6592 | 20.68 | 23.7247 | 26.7498
ExeterIce Accretion2080RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2080 | 13.1348 | 16.2879 | 20.262 | 23.269 | 26.2508
ExeterIce Accretion2085RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2085 | 12.4459 | 15.4753 | 19.294 | 22.1875 | 25.0589
ExeterIce Accretion2090RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2090 | 11.757 | 14.6628 | 18.326 | 21.1061 | 23.8669
ExeterIce Accretion2095RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2095 | 11.757 | 14.6628 | 18.326 | 21.1061 | 23.8669
ExeterIce Accretion2100RCP8.5 | Exeter | Ice Accretion | RCP8.5 | 2100 | 11.757 | 14.6628 | 18.326 | 21.1061 | 23.8669
ExeterWind2023RCP4.5 | Exeter | Wind | RCP4.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
ExeterWind2025RCP4.5 | Exeter | Wind | RCP4.5 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
ExeterWind2030RCP4.5 | Exeter | Wind | RCP4.5 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
ExeterWind2035RCP4.5 | Exeter | Wind | RCP4.5 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
ExeterWind2040RCP4.5 | Exeter | Wind | RCP4.5 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
ExeterWind2045RCP4.5 | Exeter | Wind | RCP4.5 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
ExeterWind2050RCP4.5 | Exeter | Wind | RCP4.5 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
ExeterWind2055RCP4.5 | Exeter | Wind | RCP4.5 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
ExeterWind2060RCP4.5 | Exeter | Wind | RCP4.5 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
ExeterWind2065RCP4.5 | Exeter | Wind | RCP4.5 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
ExeterWind2070RCP4.5 | Exeter | Wind | RCP4.5 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
ExeterWind2075RCP4.5 | Exeter | Wind | RCP4.5 | 2075 | 86.3504 | 93.3577 | 100.8387 | 108.226 | 115.6228
ExeterWind2080RCP4.5 | Exeter | Wind | RCP4.5 | 2080 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
ExeterWind2085RCP4.5 | Exeter | Wind | RCP4.5 | 2085 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
ExeterWind2090RCP4.5 | Exeter | Wind | RCP4.5 | 2090 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
ExeterWind2095RCP4.5 | Exeter | Wind | RCP4.5 | 2095 | 86.7678 | 93.9167 | 101.5705 | 109.1068 | 116.6655
ExeterWind2100RCP4.5 | Exeter | Wind | RCP4.5 | 2100 | 86.8722 | 94.0565 | 101.7534 | 109.327 | 116.9262
ExeterWind2023RCP6.0 | Exeter | Wind | RCP6.0 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
ExeterWind2025RCP6.0 | Exeter | Wind | RCP6.0 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
ExeterWind2030RCP6.0 | Exeter | Wind | RCP6.0 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
ExeterWind2035RCP6.0 | Exeter | Wind | RCP6.0 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
ExeterWind2040RCP6.0 | Exeter | Wind | RCP6.0 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
ExeterWind2045RCP6.0 | Exeter | Wind | RCP6.0 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
ExeterWind2050RCP6.0 | Exeter | Wind | RCP6.0 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
ExeterWind2055RCP6.0 | Exeter | Wind | RCP6.0 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
ExeterWind2060RCP6.0 | Exeter | Wind | RCP6.0 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
ExeterWind2065RCP6.0 | Exeter | Wind | RCP6.0 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
ExeterWind2070RCP6.0 | Exeter | Wind | RCP6.0 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
ExeterWind2075RCP6.0 | Exeter | Wind | RCP6.0 | 2075 | 86.4026 | 93.4276 | 100.9302 | 108.3361 | 115.7531
ExeterWind2080RCP6.0 | Exeter | Wind | RCP6.0 | 2080 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
ExeterWind2085RCP6.0 | Exeter | Wind | RCP6.0 | 2085 | 86.7157 | 93.8469 | 101.479 | 108.9967 | 116.5351
ExeterWind2090RCP6.0 | Exeter | Wind | RCP6.0 | 2090 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
ExeterWind2095RCP6.0 | Exeter | Wind | RCP6.0 | 2095 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
ExeterWind2100RCP6.0 | Exeter | Wind | RCP6.0 | 2100 | 87.7861 | 95.1502 | 103.0568 | 110.8265 | 118.6131
ExeterWind2023RCP8.5 | Exeter | Wind | RCP8.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
ExeterWind2025RCP8.5 | Exeter | Wind | RCP8.5 | 2025 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
ExeterWind2030RCP8.5 | Exeter | Wind | RCP8.5 | 2030 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
ExeterWind2035RCP8.5 | Exeter | Wind | RCP8.5 | 2035 | 86.0768 | 93.0084 | 100.3912 | 107.7017 | 115.0269
ExeterWind2040RCP8.5 | Exeter | Wind | RCP8.5 | 2040 | 86.1332 | 93.0782 | 100.4794 | 107.8031 | 115.1386
ExeterWind2045RCP8.5 | Exeter | Wind | RCP8.5 | 2045 | 86.1896 | 93.1481 | 100.5676 | 107.9044 | 115.2504
ExeterWind2050RCP8.5 | Exeter | Wind | RCP8.5 | 2050 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
ExeterWind2055RCP8.5 | Exeter | Wind | RCP8.5 | 2055 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
ExeterWind2060RCP8.5 | Exeter | Wind | RCP8.5 | 2060 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
ExeterWind2065RCP8.5 | Exeter | Wind | RCP8.5 | 2065 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
ExeterWind2070RCP8.5 | Exeter | Wind | RCP8.5 | 2070 | 88.0541 | 95.5026 | 103.5207 | 111.3788 | 119.2611
ExeterWind2075RCP8.5 | Exeter | Wind | RCP8.5 | 2075 | 88.322 | 95.855 | 103.9845 | 111.9311 | 119.9091
ExeterWind2080RCP8.5 | Exeter | Wind | RCP8.5 | 2080 | 88.59 | 96.2074 | 104.4484 | 112.4833 | 120.5571
ExeterWind2085RCP8.5 | Exeter | Wind | RCP8.5 | 2085 | 88.9454 | 96.6585 | 105.0217 | 113.1649 | 121.3447
ExeterWind2090RCP8.5 | Exeter | Wind | RCP8.5 | 2090 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
ExeterWind2095RCP8.5 | Exeter | Wind | RCP8.5 | 2095 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
ExeterWind2100RCP8.5 | Exeter | Wind | RCP8.5 | 2100 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
Fenelon FallsIce Accretion2023RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2023 | 17.2396 | 20.584 | 24.825 | 28.0522 | 31.311
Fenelon FallsIce Accretion2025RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2025 | 17.2251 | 20.5771 | 24.825 | 28.057 | 31.3215
Fenelon FallsIce Accretion2030RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2030 | 17.2106 | 20.5702 | 24.825 | 28.0617 | 31.332
Fenelon FallsIce Accretion2035RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2035 | 17.1961 | 20.5633 | 24.825 | 28.0664 | 31.3425
Fenelon FallsIce Accretion2040RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2040 | 17.1816 | 20.5563 | 24.825 | 28.0711 | 31.353
Fenelon FallsIce Accretion2045RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2045 | 17.1671 | 20.5494 | 24.825 | 28.0758 | 31.3635
Fenelon FallsIce Accretion2050RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2050 | 17.1109 | 20.5134 | 24.81 | 28.0748 | 31.374
Fenelon FallsIce Accretion2055RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2055 | 17.0691 | 20.4844 | 24.795 | 28.0692 | 31.374
Fenelon FallsIce Accretion2060RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2060 | 17.0274 | 20.4553 | 24.78 | 28.0635 | 31.374
Fenelon FallsIce Accretion2065RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2065 | 16.9856 | 20.4263 | 24.765 | 28.0579 | 31.374
Fenelon FallsIce Accretion2070RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2070 | 16.9439 | 20.3972 | 24.75 | 28.0522 | 31.374
Fenelon FallsIce Accretion2075RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2075 | 17.0134 | 20.4975 | 24.8875 | 28.2217 | 31.5735
Fenelon FallsIce Accretion2080RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2080 | 17.083 | 20.5978 | 25.025 | 28.3912 | 31.773
Fenelon FallsIce Accretion2085RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2085 | 17.1526 | 20.6981 | 25.1625 | 28.5607 | 31.9725
Fenelon FallsIce Accretion2090RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2090 | 17.2222 | 20.7984 | 25.3 | 28.7302 | 32.172
Fenelon FallsIce Accretion2095RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2095 | 17.2918 | 20.8987 | 25.4375 | 28.8997 | 32.3715
Fenelon FallsIce Accretion2100RCP4.5 | Fenelon Falls | Ice Accretion | RCP4.5 | 2100 | 17.3614 | 20.999 | 25.575 | 29.0692 | 32.571
Fenelon FallsIce Accretion2023RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2023 | 17.2396 | 20.584 | 24.825 | 28.0522 | 31.311
Fenelon FallsIce Accretion2025RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2025 | 17.2251 | 20.5771 | 24.825 | 28.057 | 31.3215
Fenelon FallsIce Accretion2030RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2030 | 17.2106 | 20.5702 | 24.825 | 28.0617 | 31.332
Fenelon FallsIce Accretion2035RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2035 | 17.1961 | 20.5633 | 24.825 | 28.0664 | 31.3425
Fenelon FallsIce Accretion2040RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2040 | 17.1816 | 20.5563 | 24.825 | 28.0711 | 31.353
Fenelon FallsIce Accretion2045RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2045 | 17.1671 | 20.5494 | 24.825 | 28.0758 | 31.3635
Fenelon FallsIce Accretion2050RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2050 | 17.1109 | 20.5134 | 24.81 | 28.0748 | 31.374
Fenelon FallsIce Accretion2055RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2055 | 17.0691 | 20.4844 | 24.795 | 28.0692 | 31.374
Fenelon FallsIce Accretion2060RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2060 | 17.0274 | 20.4553 | 24.78 | 28.0635 | 31.374
Fenelon FallsIce Accretion2065RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2065 | 16.9856 | 20.4263 | 24.765 | 28.0579 | 31.374
Fenelon FallsIce Accretion2070RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2070 | 16.9439 | 20.3972 | 24.75 | 28.0522 | 31.374
Fenelon FallsIce Accretion2075RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2075 | 17.0482 | 20.5477 | 24.9563 | 28.3065 | 31.6732
Fenelon FallsIce Accretion2080RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2080 | 17.1526 | 20.6981 | 25.1625 | 28.5607 | 31.9725
Fenelon FallsIce Accretion2085RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2085 | 17.257 | 20.8486 | 25.3687 | 28.815 | 32.2717
Fenelon FallsIce Accretion2090RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2090 | 17.2512 | 20.916 | 25.5333 | 29.0504 | 32.5815
Fenelon FallsIce Accretion2095RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2095 | 17.141 | 20.833 | 25.4917 | 29.0316 | 32.592
Fenelon FallsIce Accretion2100RCP6.0 | Fenelon Falls | Ice Accretion | RCP6.0 | 2100 | 17.0308 | 20.75 | 25.45 | 29.0127 | 32.6025
Fenelon FallsIce Accretion2023RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2023 | 17.2396 | 20.584 | 24.825 | 28.0522 | 31.311
Fenelon FallsIce Accretion2025RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2025 | 17.2106 | 20.5702 | 24.825 | 28.0617 | 31.332
Fenelon FallsIce Accretion2030RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2030 | 17.1816 | 20.5563 | 24.825 | 28.0711 | 31.353
Fenelon FallsIce Accretion2035RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2035 | 17.1526 | 20.5425 | 24.825 | 28.0805 | 31.374
Fenelon FallsIce Accretion2040RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2040 | 17.083 | 20.4941 | 24.8 | 28.0711 | 31.374
Fenelon FallsIce Accretion2045RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2045 | 17.0134 | 20.4457 | 24.775 | 28.0617 | 31.374
Fenelon FallsIce Accretion2050RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2050 | 17.083 | 20.5978 | 25.025 | 28.3912 | 31.773
Fenelon FallsIce Accretion2055RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2055 | 17.2222 | 20.7984 | 25.3 | 28.7302 | 32.172
Fenelon FallsIce Accretion2060RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2060 | 17.2512 | 20.916 | 25.5333 | 29.0504 | 32.5815
Fenelon FallsIce Accretion2065RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2065 | 17.141 | 20.833 | 25.4917 | 29.0316 | 32.592
Fenelon FallsIce Accretion2070RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2070 | 16.8105 | 20.5218 | 25.2167 | 28.7773 | 32.3505
Fenelon FallsIce Accretion2075RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2075 | 16.5901 | 20.2935 | 24.9833 | 28.5419 | 32.0985
Fenelon FallsIce Accretion2080RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2080 | 16.3698 | 20.0652 | 24.75 | 28.3065 | 31.8465
Fenelon FallsIce Accretion2085RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2085 | 15.6826 | 19.2871 | 23.85 | 27.3177 | 30.7597
Fenelon FallsIce Accretion2090RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2090 | 14.9955 | 18.509 | 22.95 | 26.329 | 29.673
Fenelon FallsIce Accretion2095RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2095 | 14.9955 | 18.509 | 22.95 | 26.329 | 29.673
Fenelon FallsIce Accretion2100RCP8.5 | Fenelon Falls | Ice Accretion | RCP8.5 | 2100 | 14.9955 | 18.509 | 22.95 | 26.329 | 29.673
Fenelon FallsWind2023RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2023 | 72.7936 | 78.37 | 84.2352 | 90.1047 | 95.9707
Fenelon FallsWind2025RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2025 | 72.8492 | 78.4351 | 84.3122 | 90.1916 | 96.068
Fenelon FallsWind2030RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2030 | 72.9049 | 78.5002 | 84.3892 | 90.2785 | 96.1654
Fenelon FallsWind2035RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2035 | 72.9605 | 78.5653 | 84.4662 | 90.3654 | 96.2627
Fenelon FallsWind2040RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2040 | 73.0161 | 78.6304 | 84.5432 | 90.4522 | 96.3601
Fenelon FallsWind2045RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2045 | 73.0717 | 78.6955 | 84.6202 | 90.5391 | 96.4575
Fenelon FallsWind2050RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2050 | 73.2013 | 78.8434 | 84.7879 | 90.7249 | 96.6621
Fenelon FallsWind2055RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2055 | 73.2753 | 78.9262 | 84.8786 | 90.8237 | 96.7693
Fenelon FallsWind2060RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2060 | 73.3492 | 79.009 | 84.9694 | 90.9226 | 96.8766
Fenelon FallsWind2065RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2065 | 73.4232 | 79.0918 | 85.0601 | 91.0215 | 96.9838
Fenelon FallsWind2070RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2070 | 73.4972 | 79.1746 | 85.1508 | 91.1203 | 97.0911
Fenelon FallsWind2075RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2075 | 73.4742 | 79.1512 | 85.1256 | 91.0949 | 97.0655
Fenelon FallsWind2080RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2080 | 73.4513 | 79.1277 | 85.1004 | 91.0694 | 97.04
Fenelon FallsWind2085RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2085 | 73.4283 | 79.1043 | 85.0752 | 91.0439 | 97.0145
Fenelon FallsWind2090RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2090 | 73.4053 | 79.0809 | 85.05 | 91.0185 | 96.9889
Fenelon FallsWind2095RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2095 | 73.3824 | 79.0574 | 85.0248 | 90.993 | 96.9634
Fenelon FallsWind2100RCP4.5 | Fenelon Falls | Wind | RCP4.5 | 2100 | 73.3594 | 79.034 | 84.9996 | 90.9675 | 96.9378
Fenelon FallsWind2023RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2023 | 72.7936 | 78.37 | 84.2352 | 90.1047 | 95.9707
Fenelon FallsWind2025RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2025 | 72.8492 | 78.4351 | 84.3122 | 90.1916 | 96.068
Fenelon FallsWind2030RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2030 | 72.9049 | 78.5002 | 84.3892 | 90.2785 | 96.1654
Fenelon FallsWind2035RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2035 | 72.9605 | 78.5653 | 84.4662 | 90.3654 | 96.2627
Fenelon FallsWind2040RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2040 | 73.0161 | 78.6304 | 84.5432 | 90.4522 | 96.3601
Fenelon FallsWind2045RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2045 | 73.0717 | 78.6955 | 84.6202 | 90.5391 | 96.4575
Fenelon FallsWind2050RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2050 | 73.2013 | 78.8434 | 84.7879 | 90.7249 | 96.6621
Fenelon FallsWind2055RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2055 | 73.2753 | 78.9262 | 84.8786 | 90.8237 | 96.7693
Fenelon FallsWind2060RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2060 | 73.3492 | 79.009 | 84.9694 | 90.9226 | 96.8766
Fenelon FallsWind2065RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2065 | 73.4232 | 79.0918 | 85.0601 | 91.0215 | 96.9838
Fenelon FallsWind2070RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2070 | 73.4972 | 79.1746 | 85.1508 | 91.1203 | 97.0911
Fenelon FallsWind2075RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2075 | 73.4628 | 79.1395 | 85.113 | 91.0821 | 97.0528
Fenelon FallsWind2080RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2080 | 73.4283 | 79.1043 | 85.0752 | 91.0439 | 97.0145
Fenelon FallsWind2085RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2085 | 73.3938 | 79.0692 | 85.0374 | 91.0057 | 96.9762
Fenelon FallsWind2090RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2090 | 73.4126 | 79.0939 | 85.0696 | 91.0454 | 97.024
Fenelon FallsWind2095RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2095 | 73.4658 | 79.1538 | 85.1396 | 91.1233 | 97.1102
Fenelon FallsWind2100RCP6.0 | Fenelon Falls | Wind | RCP6.0 | 2100 | 73.519 | 79.2137 | 85.2096 | 91.2012 | 97.1964
Fenelon FallsWind2023RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2023 | 72.7936 | 78.37 | 84.2352 | 90.1047 | 95.9707
Fenelon FallsWind2025RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2025 | 72.9049 | 78.5002 | 84.3892 | 90.2785 | 96.1654
Fenelon FallsWind2030RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2030 | 73.0161 | 78.6304 | 84.5432 | 90.4522 | 96.3601
Fenelon FallsWind2035RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2035 | 73.1273 | 78.7606 | 84.6972 | 90.626 | 96.5548
Fenelon FallsWind2040RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2040 | 73.2506 | 78.8986 | 84.8484 | 90.7908 | 96.7336
Fenelon FallsWind2045RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2045 | 73.3739 | 79.0366 | 84.9996 | 90.9556 | 96.9123
Fenelon FallsWind2050RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2050 | 73.4513 | 79.1277 | 85.1004 | 91.0694 | 97.04
Fenelon FallsWind2055RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2055 | 73.4053 | 79.0809 | 85.05 | 91.0185 | 96.9889
Fenelon FallsWind2060RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2060 | 73.4126 | 79.0939 | 85.0696 | 91.0454 | 97.024
Fenelon FallsWind2065RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2065 | 73.4658 | 79.1538 | 85.1396 | 91.1233 | 97.1102
Fenelon FallsWind2070RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2070 | 73.5359 | 79.2267 | 85.2208 | 91.2102 | 97.2028
Fenelon FallsWind2075RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2075 | 73.5528 | 79.2397 | 85.232 | 91.2192 | 97.2092
Fenelon FallsWind2080RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2080 | 73.5697 | 79.2527 | 85.2432 | 91.2282 | 97.2156
Fenelon FallsWind2085RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2085 | 73.6749 | 79.3699 | 85.3692 | 91.363 | 97.3592
Fenelon FallsWind2090RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2090 | 73.7801 | 79.4871 | 85.4952 | 91.4978 | 97.5028
Fenelon FallsWind2095RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2095 | 73.7801 | 79.4871 | 85.4952 | 91.4978 | 97.5028
Fenelon FallsWind2100RCP8.5 | Fenelon Falls | Wind | RCP8.5 | 2100 | 73.7801 | 79.4871 | 85.4952 | 91.4978 | 97.5028
FergusIce Accretion2023RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2023 | 16.6001 | 19.92 | 24.12 | 27.337 | 30.5424
FergusIce Accretion2025RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2025 | 16.6279 | 19.9665 | 24.188 | 27.4228 | 30.6432
FergusIce Accretion2030RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2030 | 16.6558 | 20.013 | 24.256 | 27.5087 | 30.744
FergusIce Accretion2035RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2035 | 16.6836 | 20.0594 | 24.324 | 27.5946 | 30.8448
FergusIce Accretion2040RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2040 | 16.7114 | 20.1059 | 24.392 | 27.6805 | 30.9456
FergusIce Accretion2045RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2045 | 16.7393 | 20.1524 | 24.46 | 27.7664 | 31.0464
FergusIce Accretion2050RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2050 | 16.7137 | 20.1511 | 24.4896 | 27.8197 | 31.123
FergusIce Accretion2055RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2055 | 16.6602 | 20.1033 | 24.4512 | 27.7872 | 31.0988
FergusIce Accretion2060RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2060 | 16.6068 | 20.0555 | 24.4128 | 27.7546 | 31.0746
FergusIce Accretion2065RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2065 | 16.5533 | 20.0076 | 24.3744 | 27.7221 | 31.0504
FergusIce Accretion2070RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2070 | 16.4999 | 19.9598 | 24.336 | 27.6895 | 31.0262
FergusIce Accretion2075RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2075 | 16.4693 | 19.9532 | 24.356 | 27.7257 | 31.0817
FergusIce Accretion2080RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2080 | 16.4387 | 19.9466 | 24.376 | 27.7618 | 31.1371
FergusIce Accretion2085RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2085 | 16.4081 | 19.9399 | 24.396 | 27.798 | 31.1926
FergusIce Accretion2090RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2090 | 16.3774 | 19.9333 | 24.416 | 27.8342 | 31.248
FergusIce Accretion2095RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2095 | 16.3468 | 19.9266 | 24.436 | 27.8703 | 31.3034
FergusIce Accretion2100RCP4.5 | Fergus | Ice Accretion | RCP4.5 | 2100 | 16.3162 | 19.92 | 24.456 | 27.9065 | 31.3589
FergusIce Accretion2023RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2023 | 16.6001 | 19.92 | 24.12 | 27.337 | 30.5424
FergusIce Accretion2025RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2025 | 16.6279 | 19.9665 | 24.188 | 27.4228 | 30.6432
FergusIce Accretion2030RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2030 | 16.6558 | 20.013 | 24.256 | 27.5087 | 30.744
FergusIce Accretion2035RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2035 | 16.6836 | 20.0594 | 24.324 | 27.5946 | 30.8448
FergusIce Accretion2040RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2040 | 16.7114 | 20.1059 | 24.392 | 27.6805 | 30.9456
FergusIce Accretion2045RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2045 | 16.7393 | 20.1524 | 24.46 | 27.7664 | 31.0464
FergusIce Accretion2050RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2050 | 16.7137 | 20.1511 | 24.4896 | 27.8197 | 31.123
FergusIce Accretion2055RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2055 | 16.6602 | 20.1033 | 24.4512 | 27.7872 | 31.0988
FergusIce Accretion2060RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2060 | 16.6068 | 20.0555 | 24.4128 | 27.7546 | 31.0746
FergusIce Accretion2065RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2065 | 16.5533 | 20.0076 | 24.3744 | 27.7221 | 31.0504
FergusIce Accretion2070RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2070 | 16.4999 | 19.9598 | 24.336 | 27.6895 | 31.0262
FergusIce Accretion2075RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2075 | 16.454 | 19.9499 | 24.366 | 27.7438 | 31.1094
FergusIce Accretion2080RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2080 | 16.4081 | 19.9399 | 24.396 | 27.798 | 31.1926
FergusIce Accretion2085RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2085 | 16.3621 | 19.93 | 24.426 | 27.8522 | 31.2757
FergusIce Accretion2090RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2090 | 16.0212 | 19.6079 | 24.128 | 27.563 | 31.0061
FergusIce Accretion2095RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2095 | 15.7261 | 19.2958 | 23.8 | 27.2194 | 30.6533
FergusIce Accretion2100RCP6.0 | Fergus | Ice Accretion | RCP6.0 | 2100 | 15.4311 | 18.9838 | 23.472 | 26.8759 | 30.3005
FergusIce Accretion2023RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2023 | 16.6001 | 19.92 | 24.12 | 27.337 | 30.5424
FergusIce Accretion2025RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2025 | 16.6558 | 20.013 | 24.256 | 27.5087 | 30.744
FergusIce Accretion2030RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2030 | 16.7114 | 20.1059 | 24.392 | 27.6805 | 30.9456
FergusIce Accretion2035RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2035 | 16.7671 | 20.1989 | 24.528 | 27.8522 | 31.1472
FergusIce Accretion2040RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2040 | 16.678 | 20.1192 | 24.464 | 27.798 | 31.1069
FergusIce Accretion2045RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2045 | 16.589 | 20.0395 | 24.4 | 27.7438 | 31.0666
FergusIce Accretion2050RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2050 | 16.4387 | 19.9466 | 24.376 | 27.7618 | 31.1371
FergusIce Accretion2055RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2055 | 16.3774 | 19.9333 | 24.416 | 27.8342 | 31.248
FergusIce Accretion2060RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2060 | 16.0212 | 19.6079 | 24.128 | 27.563 | 31.0061
FergusIce Accretion2065RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2065 | 15.7261 | 19.2958 | 23.8 | 27.2194 | 30.6533
FergusIce Accretion2070RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2070 | 15.0247 | 18.5455 | 22.992 | 26.3697 | 29.7461
FergusIce Accretion2075RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2075 | 14.6183 | 18.1073 | 22.512 | 25.8634 | 29.1917
FergusIce Accretion2080RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2080 | 14.212 | 17.669 | 22.032 | 25.3572 | 28.6373
FergusIce Accretion2085RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2085 | 13.4187 | 16.7328 | 20.916 | 24.0826 | 27.2311
FergusIce Accretion2090RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2090 | 12.6254 | 15.7966 | 19.8 | 22.8079 | 25.825
FergusIce Accretion2095RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2095 | 12.6254 | 15.7966 | 19.8 | 22.8079 | 25.825
FergusIce Accretion2100RCP8.5 | Fergus | Ice Accretion | RCP8.5 | 2100 | 12.6254 | 15.7966 | 19.8 | 22.8079 | 25.825
FergusWind2023RCP4.5 | Fergus | Wind | RCP4.5 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
FergusWind2025RCP4.5 | Fergus | Wind | RCP4.5 | 2025 | 81.5488 | 87.8469 | 94.481 | 101.1097 | 107.7494
FergusWind2030RCP4.5 | Fergus | Wind | RCP4.5 | 2030 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
FergusWind2035RCP4.5 | Fergus | Wind | RCP4.5 | 2035 | 81.6625 | 88.0013 | 94.6909 | 101.3645 | 108.0494
FergusWind2040RCP4.5 | Fergus | Wind | RCP4.5 | 2040 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
FergusWind2045RCP4.5 | Fergus | Wind | RCP4.5 | 2045 | 81.7761 | 88.1558 | 94.9008 | 101.6193 | 108.3495
FergusWind2050RCP4.5 | Fergus | Wind | RCP4.5 | 2050 | 81.8962 | 88.3099 | 95.096 | 101.8513 | 108.6174
FergusWind2055RCP4.5 | Fergus | Wind | RCP4.5 | 2055 | 81.9595 | 88.3869 | 95.1863 | 101.9559 | 108.7353
FergusWind2060RCP4.5 | Fergus | Wind | RCP4.5 | 2060 | 82.0229 | 88.4638 | 95.2765 | 102.0605 | 108.8531
FergusWind2065RCP4.5 | Fergus | Wind | RCP4.5 | 2065 | 82.0862 | 88.5407 | 95.3668 | 102.1651 | 108.971
FergusWind2070RCP4.5 | Fergus | Wind | RCP4.5 | 2070 | 82.1495 | 88.6177 | 95.457 | 102.2697 | 109.0889
FergusWind2075RCP4.5 | Fergus | Wind | RCP4.5 | 2075 | 82.2185 | 88.7167 | 95.598 | 102.4424 | 109.2961
FergusWind2080RCP4.5 | Fergus | Wind | RCP4.5 | 2080 | 82.2875 | 88.8158 | 95.739 | 102.6151 | 109.5032
FergusWind2085RCP4.5 | Fergus | Wind | RCP4.5 | 2085 | 82.3564 | 88.9149 | 95.88 | 102.7877 | 109.7104
FergusWind2090RCP4.5 | Fergus | Wind | RCP4.5 | 2090 | 82.4254 | 89.014 | 96.021 | 102.9604 | 109.9176
FergusWind2095RCP4.5 | Fergus | Wind | RCP4.5 | 2095 | 82.4944 | 89.113 | 96.162 | 103.1331 | 110.1248
FergusWind2100RCP4.5 | Fergus | Wind | RCP4.5 | 2100 | 82.5634 | 89.2121 | 96.303 | 103.3057 | 110.3319
FergusWind2023RCP6.0 | Fergus | Wind | RCP6.0 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
FergusWind2025RCP6.0 | Fergus | Wind | RCP6.0 | 2025 | 81.5488 | 87.8469 | 94.481 | 101.1097 | 107.7494
FergusWind2030RCP6.0 | Fergus | Wind | RCP6.0 | 2030 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
FergusWind2035RCP6.0 | Fergus | Wind | RCP6.0 | 2035 | 81.6625 | 88.0013 | 94.6909 | 101.3645 | 108.0494
FergusWind2040RCP6.0 | Fergus | Wind | RCP6.0 | 2040 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
FergusWind2045RCP6.0 | Fergus | Wind | RCP6.0 | 2045 | 81.7761 | 88.1558 | 94.9008 | 101.6193 | 108.3495
FergusWind2050RCP6.0 | Fergus | Wind | RCP6.0 | 2050 | 81.8962 | 88.3099 | 95.096 | 101.8513 | 108.6174
FergusWind2055RCP6.0 | Fergus | Wind | RCP6.0 | 2055 | 81.9595 | 88.3869 | 95.1863 | 101.9559 | 108.7353
FergusWind2060RCP6.0 | Fergus | Wind | RCP6.0 | 2060 | 82.0229 | 88.4638 | 95.2765 | 102.0605 | 108.8531
FergusWind2065RCP6.0 | Fergus | Wind | RCP6.0 | 2065 | 82.0862 | 88.5407 | 95.3668 | 102.1651 | 108.971
FergusWind2070RCP6.0 | Fergus | Wind | RCP6.0 | 2070 | 82.1495 | 88.6177 | 95.457 | 102.2697 | 109.0889
FergusWind2075RCP6.0 | Fergus | Wind | RCP6.0 | 2075 | 82.253 | 88.7663 | 95.6685 | 102.5287 | 109.3996
FergusWind2080RCP6.0 | Fergus | Wind | RCP6.0 | 2080 | 82.3564 | 88.9149 | 95.88 | 102.7877 | 109.7104
FergusWind2085RCP6.0 | Fergus | Wind | RCP6.0 | 2085 | 82.4599 | 89.0635 | 96.0915 | 103.0467 | 110.0212
FergusWind2090RCP6.0 | Fergus | Wind | RCP6.0 | 2090 | 82.8421 | 89.5618 | 96.7385 | 103.8187 | 110.9213
FergusWind2095RCP6.0 | Fergus | Wind | RCP6.0 | 2095 | 83.1208 | 89.9115 | 97.1741 | 104.3316 | 111.5107
FergusWind2100RCP6.0 | Fergus | Wind | RCP6.0 | 2100 | 83.3995 | 90.2612 | 97.6096 | 104.8446 | 112.1001
FergusWind2023RCP8.5 | Fergus | Wind | RCP8.5 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
FergusWind2025RCP8.5 | Fergus | Wind | RCP8.5 | 2025 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
FergusWind2030RCP8.5 | Fergus | Wind | RCP8.5 | 2030 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
FergusWind2035RCP8.5 | Fergus | Wind | RCP8.5 | 2035 | 81.8329 | 88.233 | 95.0058 | 101.7467 | 108.4995
FergusWind2040RCP8.5 | Fergus | Wind | RCP8.5 | 2040 | 81.9384 | 88.3612 | 95.1562 | 101.9211 | 108.696
FergusWind2045RCP8.5 | Fergus | Wind | RCP8.5 | 2045 | 82.044 | 88.4894 | 95.3066 | 102.0954 | 108.8924
FergusWind2050RCP8.5 | Fergus | Wind | RCP8.5 | 2050 | 82.2875 | 88.8158 | 95.739 | 102.6151 | 109.5032
FergusWind2055RCP8.5 | Fergus | Wind | RCP8.5 | 2055 | 82.4254 | 89.014 | 96.021 | 102.9604 | 109.9176
FergusWind2060RCP8.5 | Fergus | Wind | RCP8.5 | 2060 | 82.8421 | 89.5618 | 96.7385 | 103.8187 | 110.9213
FergusWind2065RCP8.5 | Fergus | Wind | RCP8.5 | 2065 | 83.1208 | 89.9115 | 97.1741 | 104.3316 | 111.5107
FergusWind2070RCP8.5 | Fergus | Wind | RCP8.5 | 2070 | 83.6457 | 90.5933 | 98.0451 | 105.371 | 112.718
FergusWind2075RCP8.5 | Fergus | Wind | RCP8.5 | 2075 | 83.8919 | 90.9255 | 98.4807 | 105.8973 | 113.336
FergusWind2080RCP8.5 | Fergus | Wind | RCP8.5 | 2080 | 84.1381 | 91.2577 | 98.9162 | 106.4237 | 113.9539
FergusWind2085RCP8.5 | Fergus | Wind | RCP8.5 | 2085 | 84.3775 | 91.5768 | 99.3392 | 106.9266 | 114.5433
FergusWind2090RCP8.5 | Fergus | Wind | RCP8.5 | 2090 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
FergusWind2095RCP8.5 | Fergus | Wind | RCP8.5 | 2095 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
FergusWind2100RCP8.5 | Fergus | Wind | RCP8.5 | 2100 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
ForestIce Accretion2023RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2023 | 14.7422 | 17.6939 | 21.428 | 24.2634 | 27.1102
ForestIce Accretion2025RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2025 | 14.6835 | 17.6361 | 21.3693 | 24.2054 | 27.0501
ForestIce Accretion2030RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2030 | 14.6248 | 17.5783 | 21.3107 | 24.1473 | 26.99
ForestIce Accretion2035RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2035 | 14.5661 | 17.5205 | 21.252 | 24.0893 | 26.93
ForestIce Accretion2040RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2040 | 14.5075 | 17.4626 | 21.1933 | 24.0313 | 26.8699
ForestIce Accretion2045RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2045 | 14.4488 | 17.4048 | 21.1347 | 23.9733 | 26.8099
ForestIce Accretion2050RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2050 | 14.1207 | 17.0475 | 20.7328 | 23.5424 | 26.3451
ForestIce Accretion2055RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2055 | 13.8512 | 16.7481 | 20.3896 | 23.1695 | 25.9404
ForestIce Accretion2060RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2060 | 13.5818 | 16.4486 | 20.0464 | 22.7966 | 25.5357
ForestIce Accretion2065RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2065 | 13.3124 | 16.1491 | 19.7032 | 22.4237 | 25.131
ForestIce Accretion2070RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2070 | 13.0429 | 15.8497 | 19.36 | 22.0508 | 24.7262
ForestIce Accretion2075RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2075 | 12.9205 | 15.7219 | 19.228 | 21.9099 | 24.5784
ForestIce Accretion2080RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2080 | 12.798 | 15.594 | 19.096 | 21.7691 | 24.4306
ForestIce Accretion2085RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2085 | 12.6755 | 15.4662 | 18.964 | 21.6282 | 24.2827
ForestIce Accretion2090RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2090 | 12.5531 | 15.3384 | 18.832 | 21.4873 | 24.1349
ForestIce Accretion2095RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2095 | 12.4306 | 15.2106 | 18.7 | 21.3465 | 23.987
ForestIce Accretion2100RCP4.5 | Forest | Ice Accretion | RCP4.5 | 2100 | 12.3081 | 15.0828 | 18.568 | 21.2056 | 23.8392
ForestIce Accretion2023RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2023 | 14.7422 | 17.6939 | 21.428 | 24.2634 | 27.1102
ForestIce Accretion2025RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2025 | 14.6835 | 17.6361 | 21.3693 | 24.2054 | 27.0501
ForestIce Accretion2030RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2030 | 14.6248 | 17.5783 | 21.3107 | 24.1473 | 26.99
ForestIce Accretion2035RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2035 | 14.5661 | 17.5205 | 21.252 | 24.0893 | 26.93
ForestIce Accretion2040RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2040 | 14.5075 | 17.4626 | 21.1933 | 24.0313 | 26.8699
ForestIce Accretion2045RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2045 | 14.4488 | 17.4048 | 21.1347 | 23.9733 | 26.8099
ForestIce Accretion2050RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2050 | 14.1207 | 17.0475 | 20.7328 | 23.5424 | 26.3451
ForestIce Accretion2055RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2055 | 13.8512 | 16.7481 | 20.3896 | 23.1695 | 25.9404
ForestIce Accretion2060RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2060 | 13.5818 | 16.4486 | 20.0464 | 22.7966 | 25.5357
ForestIce Accretion2065RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2065 | 13.3124 | 16.1491 | 19.7032 | 22.4237 | 25.131
ForestIce Accretion2070RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2070 | 13.0429 | 15.8497 | 19.36 | 22.0508 | 24.7262
ForestIce Accretion2075RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2075 | 12.8592 | 15.6579 | 19.162 | 21.8395 | 24.5045
ForestIce Accretion2080RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2080 | 12.6755 | 15.4662 | 18.964 | 21.6282 | 24.2827
ForestIce Accretion2085RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2085 | 12.4918 | 15.2745 | 18.766 | 21.4169 | 24.061
ForestIce Accretion2090RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2090 | 11.9356 | 14.6628 | 18.084 | 20.6669 | 23.2478
ForestIce Accretion2095RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2095 | 11.5631 | 14.2428 | 17.6 | 20.1283 | 22.6565
ForestIce Accretion2100RCP6.0 | Forest | Ice Accretion | RCP6.0 | 2100 | 11.1906 | 13.8228 | 17.116 | 19.5897 | 22.0651
ForestIce Accretion2023RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2023 | 14.7422 | 17.6939 | 21.428 | 24.2634 | 27.1102
ForestIce Accretion2025RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2025 | 14.6248 | 17.5783 | 21.3107 | 24.1473 | 26.99
ForestIce Accretion2030RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2030 | 14.5075 | 17.4626 | 21.1933 | 24.0313 | 26.8699
ForestIce Accretion2035RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2035 | 14.3901 | 17.347 | 21.076 | 23.9153 | 26.7498
ForestIce Accretion2040RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2040 | 13.941 | 16.8479 | 20.504 | 23.2938 | 26.0753
ForestIce Accretion2045RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2045 | 13.492 | 16.3488 | 19.932 | 22.6723 | 25.4008
ForestIce Accretion2050RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2050 | 12.798 | 15.594 | 19.096 | 21.7691 | 24.4306
ForestIce Accretion2055RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2055 | 12.5531 | 15.3384 | 18.832 | 21.4873 | 24.1349
ForestIce Accretion2060RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2060 | 11.9356 | 14.6628 | 18.084 | 20.6669 | 23.2478
ForestIce Accretion2065RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2065 | 11.5631 | 14.2428 | 17.6 | 20.1283 | 22.6565
ForestIce Accretion2070RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2070 | 10.8997 | 13.5063 | 16.7567 | 19.2085 | 21.6493
ForestIce Accretion2075RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2075 | 10.6089 | 13.1898 | 16.3973 | 18.8273 | 21.2335
ForestIce Accretion2080RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2080 | 10.318 | 12.8733 | 16.038 | 18.4461 | 20.8177
ForestIce Accretion2085RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2085 | 9.6138 | 12.0333 | 15.037 | 17.3026 | 19.5565
ForestIce Accretion2090RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2090 | 8.9096 | 11.1934 | 14.036 | 16.159 | 18.2952
ForestIce Accretion2095RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2095 | 8.9096 | 11.1934 | 14.036 | 16.159 | 18.2952
ForestIce Accretion2100RCP8.5 | Forest | Ice Accretion | RCP8.5 | 2100 | 8.9096 | 11.1934 | 14.036 | 16.159 | 18.2952
ForestWind2023RCP4.5 | Forest | Wind | RCP4.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
ForestWind2025RCP4.5 | Forest | Wind | RCP4.5 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
ForestWind2030RCP4.5 | Forest | Wind | RCP4.5 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
ForestWind2035RCP4.5 | Forest | Wind | RCP4.5 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
ForestWind2040RCP4.5 | Forest | Wind | RCP4.5 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
ForestWind2045RCP4.5 | Forest | Wind | RCP4.5 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
ForestWind2050RCP4.5 | Forest | Wind | RCP4.5 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
ForestWind2055RCP4.5 | Forest | Wind | RCP4.5 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
ForestWind2060RCP4.5 | Forest | Wind | RCP4.5 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
ForestWind2065RCP4.5 | Forest | Wind | RCP4.5 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
ForestWind2070RCP4.5 | Forest | Wind | RCP4.5 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
ForestWind2075RCP4.5 | Forest | Wind | RCP4.5 | 2075 | 85.7411 | 92.542 | 99.746 | 106.9048 | 114.0736
ForestWind2080RCP4.5 | Forest | Wind | RCP4.5 | 2080 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
ForestWind2085RCP4.5 | Forest | Wind | RCP4.5 | 2085 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
ForestWind2090RCP4.5 | Forest | Wind | RCP4.5 | 2090 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
ForestWind2095RCP4.5 | Forest | Wind | RCP4.5 | 2095 | 86.3278 | 93.3015 | 100.7326 | 108.0792 | 115.444
ForestWind2100RCP4.5 | Forest | Wind | RCP4.5 | 2100 | 86.4745 | 93.4914 | 100.9792 | 108.3728 | 115.7866
ForestWind2023RCP6.0 | Forest | Wind | RCP6.0 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
ForestWind2025RCP6.0 | Forest | Wind | RCP6.0 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
ForestWind2030RCP6.0 | Forest | Wind | RCP6.0 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
ForestWind2035RCP6.0 | Forest | Wind | RCP6.0 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
ForestWind2040RCP6.0 | Forest | Wind | RCP6.0 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
ForestWind2045RCP6.0 | Forest | Wind | RCP6.0 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
ForestWind2050RCP6.0 | Forest | Wind | RCP6.0 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
ForestWind2055RCP6.0 | Forest | Wind | RCP6.0 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
ForestWind2060RCP6.0 | Forest | Wind | RCP6.0 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
ForestWind2065RCP6.0 | Forest | Wind | RCP6.0 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
ForestWind2070RCP6.0 | Forest | Wind | RCP6.0 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
ForestWind2075RCP6.0 | Forest | Wind | RCP6.0 | 2075 | 85.8144 | 92.637 | 99.8693 | 107.0516 | 114.2449
ForestWind2080RCP6.0 | Forest | Wind | RCP6.0 | 2080 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
ForestWind2085RCP6.0 | Forest | Wind | RCP6.0 | 2085 | 86.2545 | 93.2066 | 100.6093 | 107.9324 | 115.2727
ForestWind2090RCP6.0 | Forest | Wind | RCP6.0 | 2090 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
ForestWind2095RCP6.0 | Forest | Wind | RCP6.0 | 2095 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
ForestWind2100RCP6.0 | Forest | Wind | RCP6.0 | 2100 | 87.5746 | 94.8494 | 102.6452 | 110.3127 | 117.9987
ForestWind2023RCP8.5 | Forest | Wind | RCP8.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
ForestWind2025RCP8.5 | Forest | Wind | RCP8.5 | 2025 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
ForestWind2030RCP8.5 | Forest | Wind | RCP8.5 | 2030 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
ForestWind2035RCP8.5 | Forest | Wind | RCP8.5 | 2035 | 85.586 | 92.3248 | 99.4504 | 106.5378 | 113.6304
ForestWind2040RCP8.5 | Forest | Wind | RCP8.5 | 2040 | 85.5888 | 92.3339 | 99.4667 | 106.5622 | 113.6639
ForestWind2045RCP8.5 | Forest | Wind | RCP8.5 | 2045 | 85.5916 | 92.343 | 99.4831 | 106.5867 | 113.6974
ForestWind2050RCP8.5 | Forest | Wind | RCP8.5 | 2050 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
ForestWind2055RCP8.5 | Forest | Wind | RCP8.5 | 2055 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
ForestWind2060RCP8.5 | Forest | Wind | RCP8.5 | 2060 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
ForestWind2065RCP8.5 | Forest | Wind | RCP8.5 | 2065 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
ForestWind2070RCP8.5 | Forest | Wind | RCP8.5 | 2070 | 87.882 | 95.2383 | 103.1385 | 110.8929 | 118.669
ForestWind2075RCP8.5 | Forest | Wind | RCP8.5 | 2075 | 88.1895 | 95.6271 | 103.6317 | 111.4732 | 119.3393
ForestWind2080RCP8.5 | Forest | Wind | RCP8.5 | 2080 | 88.4969 | 96.016 | 104.125 | 112.0534 | 120.0096
ForestWind2085RCP8.5 | Forest | Wind | RCP8.5 | 2085 | 88.8396 | 96.4489 | 104.664 | 112.6826 | 120.7358
ForestWind2090RCP8.5 | Forest | Wind | RCP8.5 | 2090 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
ForestWind2095RCP8.5 | Forest | Wind | RCP8.5 | 2095 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
ForestWind2100RCP8.5 | Forest | Wind | RCP8.5 | 2100 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
Fort ErieIce Accretion2023RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2023 | 20.7501 | 24.8253 | 29.97 | 33.9339 | 37.8378
Fort ErieIce Accretion2025RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2025 | 20.7084 | 24.7838 | 29.935 | 33.8943 | 37.8
Fort ErieIce Accretion2030RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2030 | 20.6666 | 24.7423 | 29.9 | 33.8548 | 37.7622
Fort ErieIce Accretion2035RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2035 | 20.6249 | 24.7008 | 29.865 | 33.8152 | 37.7244
Fort ErieIce Accretion2040RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2040 | 20.5831 | 24.6593 | 29.83 | 33.7757 | 37.6866
Fort ErieIce Accretion2045RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2045 | 20.5414 | 24.6178 | 29.795 | 33.7361 | 37.6488
Fort ErieIce Accretion2050RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2050 | 20.1531 | 24.1879 | 29.31 | 33.2017 | 37.0742
Fort ErieIce Accretion2055RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2055 | 19.8066 | 23.7994 | 28.86 | 32.7067 | 36.5375
Fort ErieIce Accretion2060RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2060 | 19.46 | 23.411 | 28.41 | 32.2118 | 36.0007
Fort ErieIce Accretion2065RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2065 | 19.1135 | 23.0225 | 27.96 | 31.7168 | 35.464
Fort ErieIce Accretion2070RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2070 | 18.767 | 22.6341 | 27.51 | 31.2219 | 34.9272
Fort ErieIce Accretion2075RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2075 | 18.6139 | 22.4806 | 27.355 | 31.0637 | 34.7634
Fort ErieIce Accretion2080RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2080 | 18.4608 | 22.327 | 27.2 | 30.9055 | 34.5996
Fort ErieIce Accretion2085RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2085 | 18.3077 | 22.1734 | 27.045 | 30.7473 | 34.4358
Fort ErieIce Accretion2090RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2090 | 18.1546 | 22.0199 | 26.89 | 30.5891 | 34.272
Fort ErieIce Accretion2095RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2095 | 18.0015 | 21.8663 | 26.735 | 30.4309 | 34.1082
Fort ErieIce Accretion2100RCP4.5 | Fort Erie | Ice Accretion | RCP4.5 | 2100 | 17.8485 | 21.7128 | 26.58 | 30.2727 | 33.9444
Fort ErieIce Accretion2023RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2023 | 20.7501 | 24.8253 | 29.97 | 33.9339 | 37.8378
Fort ErieIce Accretion2025RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2025 | 20.7084 | 24.7838 | 29.935 | 33.8943 | 37.8
Fort ErieIce Accretion2030RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2030 | 20.6666 | 24.7423 | 29.9 | 33.8548 | 37.7622
Fort ErieIce Accretion2035RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2035 | 20.6249 | 24.7008 | 29.865 | 33.8152 | 37.7244
Fort ErieIce Accretion2040RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2040 | 20.5831 | 24.6593 | 29.83 | 33.7757 | 37.6866
Fort ErieIce Accretion2045RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2045 | 20.5414 | 24.6178 | 29.795 | 33.7361 | 37.6488
Fort ErieIce Accretion2050RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2050 | 20.1531 | 24.1879 | 29.31 | 33.2017 | 37.0742
Fort ErieIce Accretion2055RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2055 | 19.8066 | 23.7994 | 28.86 | 32.7067 | 36.5375
Fort ErieIce Accretion2060RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2060 | 19.46 | 23.411 | 28.41 | 32.2118 | 36.0007
Fort ErieIce Accretion2065RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2065 | 19.1135 | 23.0225 | 27.96 | 31.7168 | 35.464
Fort ErieIce Accretion2070RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2070 | 18.767 | 22.6341 | 27.51 | 31.2219 | 34.9272
Fort ErieIce Accretion2075RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2075 | 18.5373 | 22.4038 | 27.2775 | 30.9846 | 34.6815
Fort ErieIce Accretion2080RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2080 | 18.3077 | 22.1734 | 27.045 | 30.7473 | 34.4358
Fort ErieIce Accretion2085RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2085 | 18.0781 | 21.9431 | 26.8125 | 30.51 | 34.1901
Fort ErieIce Accretion2090RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2090 | 17.2848 | 21.082 | 25.85 | 29.4704 | 33.075
Fort ErieIce Accretion2095RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2095 | 16.7212 | 20.4512 | 25.12 | 28.6681 | 32.2056
Fort ErieIce Accretion2100RCP6.0 | Fort Erie | Ice Accretion | RCP6.0 | 2100 | 16.1575 | 19.8204 | 24.39 | 27.8658 | 31.3362
Fort ErieIce Accretion2023RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2023 | 20.7501 | 24.8253 | 29.97 | 33.9339 | 37.8378
Fort ErieIce Accretion2025RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2025 | 20.6666 | 24.7423 | 29.9 | 33.8548 | 37.7622
Fort ErieIce Accretion2030RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2030 | 20.5831 | 24.6593 | 29.83 | 33.7757 | 37.6866
Fort ErieIce Accretion2035RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2035 | 20.4996 | 24.5763 | 29.76 | 33.6966 | 37.611
Fort ErieIce Accretion2040RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2040 | 19.9221 | 23.9289 | 29.01 | 32.8717 | 36.7164
Fort ErieIce Accretion2045RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2045 | 19.3445 | 23.2815 | 28.26 | 32.0468 | 35.8218
Fort ErieIce Accretion2050RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2050 | 18.4608 | 22.327 | 27.2 | 30.9055 | 34.5996
Fort ErieIce Accretion2055RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2055 | 18.1546 | 22.0199 | 26.89 | 30.5891 | 34.272
Fort ErieIce Accretion2060RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2060 | 17.2848 | 21.082 | 25.85 | 29.4704 | 33.075
Fort ErieIce Accretion2065RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2065 | 16.7212 | 20.4512 | 25.12 | 28.6681 | 32.2056
Fort ErieIce Accretion2070RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2070 | 15.9418 | 19.588 | 24.14 | 27.6059 | 31.0464
Fort ErieIce Accretion2075RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2075 | 15.7261 | 19.3556 | 23.89 | 27.346 | 30.7566
Fort ErieIce Accretion2080RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2080 | 15.5104 | 19.1232 | 23.64 | 27.0861 | 30.4668
Fort ErieIce Accretion2085RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2085 | 14.8946 | 18.426 | 22.83 | 26.1878 | 29.484
Fort ErieIce Accretion2090RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2090 | 14.2788 | 17.7288 | 22.02 | 25.2894 | 28.5012
Fort ErieIce Accretion2095RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2095 | 14.2788 | 17.7288 | 22.02 | 25.2894 | 28.5012
Fort ErieIce Accretion2100RCP8.5 | Fort Erie | Ice Accretion | RCP8.5 | 2100 | 14.2788 | 17.7288 | 22.02 | 25.2894 | 28.5012
Fort ErieWind2023RCP4.5 | Fort Erie | Wind | RCP4.5 | 2023 | 89.1233 | 96.1501 | 103.581 | 110.9736 | 118.373
Fort ErieWind2025RCP4.5 | Fort Erie | Wind | RCP4.5 | 2025 | 89.1204 | 96.1533 | 103.5929 | 110.9917 | 118.3982
Fort ErieWind2030RCP4.5 | Fort Erie | Wind | RCP4.5 | 2030 | 89.1174 | 96.1564 | 103.6048 | 111.0099 | 118.4234
Fort ErieWind2035RCP4.5 | Fort Erie | Wind | RCP4.5 | 2035 | 89.1145 | 96.1596 | 103.6167 | 111.0281 | 118.4486
Fort ErieWind2040RCP4.5 | Fort Erie | Wind | RCP4.5 | 2040 | 89.1116 | 96.1627 | 103.6286 | 111.0463 | 118.4738
Fort ErieWind2045RCP4.5 | Fort Erie | Wind | RCP4.5 | 2045 | 89.1086 | 96.1659 | 103.6405 | 111.0645 | 118.499
Fort ErieWind2050RCP4.5 | Fort Erie | Wind | RCP4.5 | 2050 | 89.1074 | 96.1823 | 103.683 | 111.1263 | 118.58
Fort ErieWind2055RCP4.5 | Fort Erie | Wind | RCP4.5 | 2055 | 89.1092 | 96.1956 | 103.7136 | 111.17 | 118.6358
Fort ErieWind2060RCP4.5 | Fort Erie | Wind | RCP4.5 | 2060 | 89.111 | 96.2089 | 103.7442 | 111.2137 | 118.6916
Fort ErieWind2065RCP4.5 | Fort Erie | Wind | RCP4.5 | 2065 | 89.1127 | 96.2222 | 103.7748 | 111.2573 | 118.7475
Fort ErieWind2070RCP4.5 | Fort Erie | Wind | RCP4.5 | 2070 | 89.1145 | 96.2355 | 103.8054 | 111.301 | 118.8033
Fort ErieWind2075RCP4.5 | Fort Erie | Wind | RCP4.5 | 2075 | 89.135 | 96.2671 | 103.8513 | 111.3592 | 118.873
Fort ErieWind2080RCP4.5 | Fort Erie | Wind | RCP4.5 | 2080 | 89.1556 | 96.2987 | 103.8972 | 111.4174 | 118.9428
Fort ErieWind2085RCP4.5 | Fort Erie | Wind | RCP4.5 | 2085 | 89.1761 | 96.3303 | 103.9431 | 111.4756 | 119.0126
Fort ErieWind2090RCP4.5 | Fort Erie | Wind | RCP4.5 | 2090 | 89.1967 | 96.3619 | 103.989 | 111.5338 | 119.0823
Fort ErieWind2095RCP4.5 | Fort Erie | Wind | RCP4.5 | 2095 | 89.2172 | 96.3936 | 104.0349 | 111.592 | 119.1521
Fort ErieWind2100RCP4.5 | Fort Erie | Wind | RCP4.5 | 2100 | 89.2378 | 96.4252 | 104.0808 | 111.6502 | 119.2219
Fort ErieWind2023RCP6.0 | Fort Erie | Wind | RCP6.0 | 2023 | 89.1233 | 96.1501 | 103.581 | 110.9736 | 118.373
Fort ErieWind2025RCP6.0 | Fort Erie | Wind | RCP6.0 | 2025 | 89.1204 | 96.1533 | 103.5929 | 110.9917 | 118.3982
Fort ErieWind2030RCP6.0 | Fort Erie | Wind | RCP6.0 | 2030 | 89.1174 | 96.1564 | 103.6048 | 111.0099 | 118.4234
Fort ErieWind2035RCP6.0 | Fort Erie | Wind | RCP6.0 | 2035 | 89.1145 | 96.1596 | 103.6167 | 111.0281 | 118.4486
Fort ErieWind2040RCP6.0 | Fort Erie | Wind | RCP6.0 | 2040 | 89.1116 | 96.1627 | 103.6286 | 111.0463 | 118.4738
Fort ErieWind2045RCP6.0 | Fort Erie | Wind | RCP6.0 | 2045 | 89.1086 | 96.1659 | 103.6405 | 111.0645 | 118.499
Fort ErieWind2050RCP6.0 | Fort Erie | Wind | RCP6.0 | 2050 | 89.1074 | 96.1823 | 103.683 | 111.1263 | 118.58
Fort ErieWind2055RCP6.0 | Fort Erie | Wind | RCP6.0 | 2055 | 89.1092 | 96.1956 | 103.7136 | 111.17 | 118.6358
Fort ErieWind2060RCP6.0 | Fort Erie | Wind | RCP6.0 | 2060 | 89.111 | 96.2089 | 103.7442 | 111.2137 | 118.6916
Fort ErieWind2065RCP6.0 | Fort Erie | Wind | RCP6.0 | 2065 | 89.1127 | 96.2222 | 103.7748 | 111.2573 | 118.7475
Fort ErieWind2070RCP6.0 | Fort Erie | Wind | RCP6.0 | 2070 | 89.1145 | 96.2355 | 103.8054 | 111.301 | 118.8033
Fort ErieWind2075RCP6.0 | Fort Erie | Wind | RCP6.0 | 2075 | 89.1453 | 96.2829 | 103.8743 | 111.3883 | 118.9079
Fort ErieWind2080RCP6.0 | Fort Erie | Wind | RCP6.0 | 2080 | 89.1761 | 96.3303 | 103.9431 | 111.4756 | 119.0126
Fort ErieWind2085RCP6.0 | Fort Erie | Wind | RCP6.0 | 2085 | 89.207 | 96.3778 | 104.0119 | 111.5629 | 119.1172
Fort ErieWind2090RCP6.0 | Fort Erie | Wind | RCP6.0 | 2090 | 89.3406 | 96.5706 | 104.2746 | 111.8867 | 119.5087
Fort ErieWind2095RCP6.0 | Fort Erie | Wind | RCP6.0 | 2095 | 89.4433 | 96.7161 | 104.4684 | 112.1232 | 119.7955
Fort ErieWind2100RCP6.0 | Fort Erie | Wind | RCP6.0 | 2100 | 89.5461 | 96.8615 | 104.6622 | 112.3596 | 120.0824
Fort ErieWind2023RCP8.5 | Fort Erie | Wind | RCP8.5 | 2023 | 89.1233 | 96.1501 | 103.581 | 110.9736 | 118.373
Fort ErieWind2025RCP8.5 | Fort Erie | Wind | RCP8.5 | 2025 | 89.1174 | 96.1564 | 103.6048 | 111.0099 | 118.4234
Fort ErieWind2030RCP8.5 | Fort Erie | Wind | RCP8.5 | 2030 | 89.1116 | 96.1627 | 103.6286 | 111.0463 | 118.4738
Fort ErieWind2035RCP8.5 | Fort Erie | Wind | RCP8.5 | 2035 | 89.1057 | 96.1691 | 103.6524 | 111.0827 | 118.5242
Fort ErieWind2040RCP8.5 | Fort Erie | Wind | RCP8.5 | 2040 | 89.1086 | 96.1912 | 103.7034 | 111.1555 | 118.6172
Fort ErieWind2045RCP8.5 | Fort Erie | Wind | RCP8.5 | 2045 | 89.1116 | 96.2133 | 103.7544 | 111.2282 | 118.7103
Fort ErieWind2050RCP8.5 | Fort Erie | Wind | RCP8.5 | 2050 | 89.1556 | 96.2987 | 103.8972 | 111.4174 | 118.9428
Fort ErieWind2055RCP8.5 | Fort Erie | Wind | RCP8.5 | 2055 | 89.1967 | 96.3619 | 103.989 | 111.5338 | 119.0823
Fort ErieWind2060RCP8.5 | Fort Erie | Wind | RCP8.5 | 2060 | 89.3406 | 96.5706 | 104.2746 | 111.8867 | 119.5087
Fort ErieWind2065RCP8.5 | Fort Erie | Wind | RCP8.5 | 2065 | 89.4433 | 96.7161 | 104.4684 | 112.1232 | 119.7955
Fort ErieWind2070RCP8.5 | Fort Erie | Wind | RCP8.5 | 2070 | 89.549 | 96.8868 | 104.72 | 112.4433 | 120.187
Fort ErieWind2075RCP8.5 | Fort Erie | Wind | RCP8.5 | 2075 | 89.5519 | 96.9121 | 104.7778 | 112.527 | 120.2917
Fort ErieWind2080RCP8.5 | Fort Erie | Wind | RCP8.5 | 2080 | 89.5549 | 96.9374 | 104.8356 | 112.6107 | 120.3963
Fort ErieWind2085RCP8.5 | Fort Erie | Wind | RCP8.5 | 2085 | 89.5901 | 97.0465 | 105.0345 | 112.8835 | 120.7452
Fort ErieWind2090RCP8.5 | Fort Erie | Wind | RCP8.5 | 2090 | 89.6253 | 97.1556 | 105.2334 | 113.1564 | 121.094
Fort ErieWind2095RCP8.5 | Fort Erie | Wind | RCP8.5 | 2095 | 89.6253 | 97.1556 | 105.2334 | 113.1564 | 121.094
Fort ErieWind2100RCP8.5 | Fort Erie | Wind | RCP8.5 | 2100 | 89.6253 | 97.1556 | 105.2334 | 113.1564 | 121.094
Fort Erie (Ridgeway)Ice Accretion2023RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2023 | 20.7501 | 24.8253 | 29.97 | 33.9339 | 37.8378
Fort Erie (Ridgeway)Ice Accretion2025RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2025 | 20.7084 | 24.7838 | 29.935 | 33.8943 | 37.8
Fort Erie (Ridgeway)Ice Accretion2030RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2030 | 20.6666 | 24.7423 | 29.9 | 33.8548 | 37.7622
Fort Erie (Ridgeway)Ice Accretion2035RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2035 | 20.6249 | 24.7008 | 29.865 | 33.8152 | 37.7244
Fort Erie (Ridgeway)Ice Accretion2040RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2040 | 20.5831 | 24.6593 | 29.83 | 33.7757 | 37.6866
Fort Erie (Ridgeway)Ice Accretion2045RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2045 | 20.5414 | 24.6178 | 29.795 | 33.7361 | 37.6488
Fort Erie (Ridgeway)Ice Accretion2050RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2050 | 20.1531 | 24.1879 | 29.31 | 33.2017 | 37.0742
Fort Erie (Ridgeway)Ice Accretion2055RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2055 | 19.8066 | 23.7994 | 28.86 | 32.7067 | 36.5375
Fort Erie (Ridgeway)Ice Accretion2060RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2060 | 19.46 | 23.411 | 28.41 | 32.2118 | 36.0007
Fort Erie (Ridgeway)Ice Accretion2065RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2065 | 19.1135 | 23.0225 | 27.96 | 31.7168 | 35.464
Fort Erie (Ridgeway)Ice Accretion2070RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2070 | 18.767 | 22.6341 | 27.51 | 31.2219 | 34.9272
Fort Erie (Ridgeway)Ice Accretion2075RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2075 | 18.6139 | 22.4806 | 27.355 | 31.0637 | 34.7634
Fort Erie (Ridgeway)Ice Accretion2080RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2080 | 18.4608 | 22.327 | 27.2 | 30.9055 | 34.5996
Fort Erie (Ridgeway)Ice Accretion2085RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2085 | 18.3077 | 22.1734 | 27.045 | 30.7473 | 34.4358
Fort Erie (Ridgeway)Ice Accretion2090RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2090 | 18.1546 | 22.0199 | 26.89 | 30.5891 | 34.272
Fort Erie (Ridgeway)Ice Accretion2095RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2095 | 18.0015 | 21.8663 | 26.735 | 30.4309 | 34.1082
Fort Erie (Ridgeway)Ice Accretion2100RCP4.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP4.5 | 2100 | 17.8485 | 21.7128 | 26.58 | 30.2727 | 33.9444
Fort Erie (Ridgeway)Ice Accretion2023RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2023 | 20.7501 | 24.8253 | 29.97 | 33.9339 | 37.8378
Fort Erie (Ridgeway)Ice Accretion2025RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2025 | 20.7084 | 24.7838 | 29.935 | 33.8943 | 37.8
Fort Erie (Ridgeway)Ice Accretion2030RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2030 | 20.6666 | 24.7423 | 29.9 | 33.8548 | 37.7622
Fort Erie (Ridgeway)Ice Accretion2035RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2035 | 20.6249 | 24.7008 | 29.865 | 33.8152 | 37.7244
Fort Erie (Ridgeway)Ice Accretion2040RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2040 | 20.5831 | 24.6593 | 29.83 | 33.7757 | 37.6866
Fort Erie (Ridgeway)Ice Accretion2045RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2045 | 20.5414 | 24.6178 | 29.795 | 33.7361 | 37.6488
Fort Erie (Ridgeway)Ice Accretion2050RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2050 | 20.1531 | 24.1879 | 29.31 | 33.2017 | 37.0742
Fort Erie (Ridgeway)Ice Accretion2055RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2055 | 19.8066 | 23.7994 | 28.86 | 32.7067 | 36.5375
Fort Erie (Ridgeway)Ice Accretion2060RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2060 | 19.46 | 23.411 | 28.41 | 32.2118 | 36.0007
Fort Erie (Ridgeway)Ice Accretion2065RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2065 | 19.1135 | 23.0225 | 27.96 | 31.7168 | 35.464
Fort Erie (Ridgeway)Ice Accretion2070RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2070 | 18.767 | 22.6341 | 27.51 | 31.2219 | 34.9272
Fort Erie (Ridgeway)Ice Accretion2075RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2075 | 18.5373 | 22.4038 | 27.2775 | 30.9846 | 34.6815
Fort Erie (Ridgeway)Ice Accretion2080RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2080 | 18.3077 | 22.1734 | 27.045 | 30.7473 | 34.4358
Fort Erie (Ridgeway)Ice Accretion2085RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2085 | 18.0781 | 21.9431 | 26.8125 | 30.51 | 34.1901
Fort Erie (Ridgeway)Ice Accretion2090RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2090 | 17.2848 | 21.082 | 25.85 | 29.4704 | 33.075
Fort Erie (Ridgeway)Ice Accretion2095RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2095 | 16.7212 | 20.4512 | 25.12 | 28.6681 | 32.2056
Fort Erie (Ridgeway)Ice Accretion2100RCP6.0 | Fort Erie (Ridgeway) | Ice Accretion | RCP6.0 | 2100 | 16.1575 | 19.8204 | 24.39 | 27.8658 | 31.3362
Fort Erie (Ridgeway)Ice Accretion2023RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2023 | 20.7501 | 24.8253 | 29.97 | 33.9339 | 37.8378
Fort Erie (Ridgeway)Ice Accretion2025RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2025 | 20.6666 | 24.7423 | 29.9 | 33.8548 | 37.7622
Fort Erie (Ridgeway)Ice Accretion2030RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2030 | 20.5831 | 24.6593 | 29.83 | 33.7757 | 37.6866
Fort Erie (Ridgeway)Ice Accretion2035RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2035 | 20.4996 | 24.5763 | 29.76 | 33.6966 | 37.611
Fort Erie (Ridgeway)Ice Accretion2040RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2040 | 19.9221 | 23.9289 | 29.01 | 32.8717 | 36.7164
Fort Erie (Ridgeway)Ice Accretion2045RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2045 | 19.3445 | 23.2815 | 28.26 | 32.0468 | 35.8218
Fort Erie (Ridgeway)Ice Accretion2050RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2050 | 18.4608 | 22.327 | 27.2 | 30.9055 | 34.5996
Fort Erie (Ridgeway)Ice Accretion2055RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2055 | 18.1546 | 22.0199 | 26.89 | 30.5891 | 34.272
Fort Erie (Ridgeway)Ice Accretion2060RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2060 | 17.2848 | 21.082 | 25.85 | 29.4704 | 33.075
Fort Erie (Ridgeway)Ice Accretion2065RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2065 | 16.7212 | 20.4512 | 25.12 | 28.6681 | 32.2056
Fort Erie (Ridgeway)Ice Accretion2070RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2070 | 15.9418 | 19.588 | 24.14 | 27.6059 | 31.0464
Fort Erie (Ridgeway)Ice Accretion2075RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2075 | 15.7261 | 19.3556 | 23.89 | 27.346 | 30.7566
Fort Erie (Ridgeway)Ice Accretion2080RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2080 | 15.5104 | 19.1232 | 23.64 | 27.0861 | 30.4668
Fort Erie (Ridgeway)Ice Accretion2085RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2085 | 14.8946 | 18.426 | 22.83 | 26.1878 | 29.484
Fort Erie (Ridgeway)Ice Accretion2090RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2090 | 14.2788 | 17.7288 | 22.02 | 25.2894 | 28.5012
Fort Erie (Ridgeway)Ice Accretion2095RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2095 | 14.2788 | 17.7288 | 22.02 | 25.2894 | 28.5012
Fort Erie (Ridgeway)Ice Accretion2100RCP8.5 | Fort Erie (Ridgeway) | Ice Accretion | RCP8.5 | 2100 | 14.2788 | 17.7288 | 22.02 | 25.2894 | 28.5012
Fort Erie (Ridgeway)Wind2023RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2023 | 89.1233 | 96.1501 | 103.581 | 110.9736 | 118.373
Fort Erie (Ridgeway)Wind2025RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2025 | 89.1204 | 96.1533 | 103.5929 | 110.9917 | 118.3982
Fort Erie (Ridgeway)Wind2030RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2030 | 89.1174 | 96.1564 | 103.6048 | 111.0099 | 118.4234
Fort Erie (Ridgeway)Wind2035RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2035 | 89.1145 | 96.1596 | 103.6167 | 111.0281 | 118.4486
Fort Erie (Ridgeway)Wind2040RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2040 | 89.1116 | 96.1627 | 103.6286 | 111.0463 | 118.4738
Fort Erie (Ridgeway)Wind2045RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2045 | 89.1086 | 96.1659 | 103.6405 | 111.0645 | 118.499
Fort Erie (Ridgeway)Wind2050RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2050 | 89.1074 | 96.1823 | 103.683 | 111.1263 | 118.58
Fort Erie (Ridgeway)Wind2055RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2055 | 89.1092 | 96.1956 | 103.7136 | 111.17 | 118.6358
Fort Erie (Ridgeway)Wind2060RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2060 | 89.111 | 96.2089 | 103.7442 | 111.2137 | 118.6916
Fort Erie (Ridgeway)Wind2065RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2065 | 89.1127 | 96.2222 | 103.7748 | 111.2573 | 118.7475
Fort Erie (Ridgeway)Wind2070RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2070 | 89.1145 | 96.2355 | 103.8054 | 111.301 | 118.8033
Fort Erie (Ridgeway)Wind2075RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2075 | 89.135 | 96.2671 | 103.8513 | 111.3592 | 118.873
Fort Erie (Ridgeway)Wind2080RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2080 | 89.1556 | 96.2987 | 103.8972 | 111.4174 | 118.9428
Fort Erie (Ridgeway)Wind2085RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2085 | 89.1761 | 96.3303 | 103.9431 | 111.4756 | 119.0126
Fort Erie (Ridgeway)Wind2090RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2090 | 89.1967 | 96.3619 | 103.989 | 111.5338 | 119.0823
Fort Erie (Ridgeway)Wind2095RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2095 | 89.2172 | 96.3936 | 104.0349 | 111.592 | 119.1521
Fort Erie (Ridgeway)Wind2100RCP4.5 | Fort Erie (Ridgeway) | Wind | RCP4.5 | 2100 | 89.2378 | 96.4252 | 104.0808 | 111.6502 | 119.2219
Fort Erie (Ridgeway)Wind2023RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2023 | 89.1233 | 96.1501 | 103.581 | 110.9736 | 118.373
Fort Erie (Ridgeway)Wind2025RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2025 | 89.1204 | 96.1533 | 103.5929 | 110.9917 | 118.3982
Fort Erie (Ridgeway)Wind2030RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2030 | 89.1174 | 96.1564 | 103.6048 | 111.0099 | 118.4234
Fort Erie (Ridgeway)Wind2035RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2035 | 89.1145 | 96.1596 | 103.6167 | 111.0281 | 118.4486
Fort Erie (Ridgeway)Wind2040RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2040 | 89.1116 | 96.1627 | 103.6286 | 111.0463 | 118.4738
Fort Erie (Ridgeway)Wind2045RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2045 | 89.1086 | 96.1659 | 103.6405 | 111.0645 | 118.499
Fort Erie (Ridgeway)Wind2050RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2050 | 89.1074 | 96.1823 | 103.683 | 111.1263 | 118.58
Fort Erie (Ridgeway)Wind2055RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2055 | 89.1092 | 96.1956 | 103.7136 | 111.17 | 118.6358
Fort Erie (Ridgeway)Wind2060RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2060 | 89.111 | 96.2089 | 103.7442 | 111.2137 | 118.6916
Fort Erie (Ridgeway)Wind2065RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2065 | 89.1127 | 96.2222 | 103.7748 | 111.2573 | 118.7475
Fort Erie (Ridgeway)Wind2070RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2070 | 89.1145 | 96.2355 | 103.8054 | 111.301 | 118.8033
Fort Erie (Ridgeway)Wind2075RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2075 | 89.1453 | 96.2829 | 103.8743 | 111.3883 | 118.9079
Fort Erie (Ridgeway)Wind2080RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2080 | 89.1761 | 96.3303 | 103.9431 | 111.4756 | 119.0126
Fort Erie (Ridgeway)Wind2085RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2085 | 89.207 | 96.3778 | 104.0119 | 111.5629 | 119.1172
Fort Erie (Ridgeway)Wind2090RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2090 | 89.3406 | 96.5706 | 104.2746 | 111.8867 | 119.5087
Fort Erie (Ridgeway)Wind2095RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2095 | 89.4433 | 96.7161 | 104.4684 | 112.1232 | 119.7955
Fort Erie (Ridgeway)Wind2100RCP6.0 | Fort Erie (Ridgeway) | Wind | RCP6.0 | 2100 | 89.5461 | 96.8615 | 104.6622 | 112.3596 | 120.0824
Fort Erie (Ridgeway)Wind2023RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2023 | 89.1233 | 96.1501 | 103.581 | 110.9736 | 118.373
Fort Erie (Ridgeway)Wind2025RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2025 | 89.1174 | 96.1564 | 103.6048 | 111.0099 | 118.4234
Fort Erie (Ridgeway)Wind2030RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2030 | 89.1116 | 96.1627 | 103.6286 | 111.0463 | 118.4738
Fort Erie (Ridgeway)Wind2035RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2035 | 89.1057 | 96.1691 | 103.6524 | 111.0827 | 118.5242
Fort Erie (Ridgeway)Wind2040RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2040 | 89.1086 | 96.1912 | 103.7034 | 111.1555 | 118.6172
Fort Erie (Ridgeway)Wind2045RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2045 | 89.1116 | 96.2133 | 103.7544 | 111.2282 | 118.7103
Fort Erie (Ridgeway)Wind2050RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2050 | 89.1556 | 96.2987 | 103.8972 | 111.4174 | 118.9428
Fort Erie (Ridgeway)Wind2055RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2055 | 89.1967 | 96.3619 | 103.989 | 111.5338 | 119.0823
Fort Erie (Ridgeway)Wind2060RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2060 | 89.3406 | 96.5706 | 104.2746 | 111.8867 | 119.5087
Fort Erie (Ridgeway)Wind2065RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2065 | 89.4433 | 96.7161 | 104.4684 | 112.1232 | 119.7955
Fort Erie (Ridgeway)Wind2070RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2070 | 89.549 | 96.8868 | 104.72 | 112.4433 | 120.187
Fort Erie (Ridgeway)Wind2075RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2075 | 89.5519 | 96.9121 | 104.7778 | 112.527 | 120.2917
Fort Erie (Ridgeway)Wind2080RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2080 | 89.5549 | 96.9374 | 104.8356 | 112.6107 | 120.3963
Fort Erie (Ridgeway)Wind2085RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2085 | 89.5901 | 97.0465 | 105.0345 | 112.8835 | 120.7452
Fort Erie (Ridgeway)Wind2090RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2090 | 89.6253 | 97.1556 | 105.2334 | 113.1564 | 121.094
Fort Erie (Ridgeway)Wind2095RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2095 | 89.6253 | 97.1556 | 105.2334 | 113.1564 | 121.094
Fort Erie (Ridgeway)Wind2100RCP8.5 | Fort Erie (Ridgeway) | Wind | RCP8.5 | 2100 | 89.6253 | 97.1556 | 105.2334 | 113.1564 | 121.094
Fort FrancesIce Accretion2023RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2023 | 10.7717 | 12.7986 | 15.375 | 17.3398 | 19.3158
Fort FrancesIce Accretion2025RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2025 | 10.8048 | 12.8297 | 15.4075 | 17.3737 | 19.3504
Fort FrancesIce Accretion2030RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2030 | 10.8378 | 12.8608 | 15.44 | 17.4076 | 19.3851
Fort FrancesIce Accretion2035RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2035 | 10.8709 | 12.892 | 15.4725 | 17.4415 | 19.4198
Fort FrancesIce Accretion2040RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2040 | 10.9039 | 12.9231 | 15.505 | 17.4754 | 19.4544
Fort FrancesIce Accretion2045RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2045 | 10.937 | 12.9542 | 15.5375 | 17.5093 | 19.489
Fort FrancesIce Accretion2050RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2050 | 11.0807 | 13.1223 | 15.738 | 17.7365 | 19.7392
Fort FrancesIce Accretion2055RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2055 | 11.1913 | 13.2592 | 15.906 | 17.9297 | 19.9546
Fort FrancesIce Accretion2060RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2060 | 11.3019 | 13.3962 | 16.074 | 18.1229 | 20.1701
Fort FrancesIce Accretion2065RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2065 | 11.4126 | 13.5331 | 16.242 | 18.3162 | 20.3855
Fort FrancesIce Accretion2070RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2070 | 11.5232 | 13.6701 | 16.41 | 18.5094 | 20.601
Fort FrancesIce Accretion2075RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2075 | 11.5197 | 13.668 | 16.405 | 18.5038 | 20.5978
Fort FrancesIce Accretion2080RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2080 | 11.5163 | 13.6659 | 16.4 | 18.4981 | 20.5947
Fort FrancesIce Accretion2085RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2085 | 11.5128 | 13.6639 | 16.395 | 18.4924 | 20.5915
Fort FrancesIce Accretion2090RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2090 | 11.5093 | 13.6618 | 16.39 | 18.4868 | 20.5884
Fort FrancesIce Accretion2095RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2095 | 11.5058 | 13.6597 | 16.385 | 18.4811 | 20.5852
Fort FrancesIce Accretion2100RCP4.5 | Fort Frances | Ice Accretion | RCP4.5 | 2100 | 11.5023 | 13.6576 | 16.38 | 18.4755 | 20.5821
Fort FrancesIce Accretion2023RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2023 | 10.7717 | 12.7986 | 15.375 | 17.3398 | 19.3158
Fort FrancesIce Accretion2025RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2025 | 10.8048 | 12.8297 | 15.4075 | 17.3737 | 19.3504
Fort FrancesIce Accretion2030RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2030 | 10.8378 | 12.8608 | 15.44 | 17.4076 | 19.3851
Fort FrancesIce Accretion2035RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2035 | 10.8709 | 12.892 | 15.4725 | 17.4415 | 19.4198
Fort FrancesIce Accretion2040RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2040 | 10.9039 | 12.9231 | 15.505 | 17.4754 | 19.4544
Fort FrancesIce Accretion2045RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2045 | 10.937 | 12.9542 | 15.5375 | 17.5093 | 19.489
Fort FrancesIce Accretion2050RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2050 | 11.0807 | 13.1223 | 15.738 | 17.7365 | 19.7392
Fort FrancesIce Accretion2055RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2055 | 11.1913 | 13.2592 | 15.906 | 17.9297 | 19.9546
Fort FrancesIce Accretion2060RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2060 | 11.3019 | 13.3962 | 16.074 | 18.1229 | 20.1701
Fort FrancesIce Accretion2065RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2065 | 11.4126 | 13.5331 | 16.242 | 18.3162 | 20.3855
Fort FrancesIce Accretion2070RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2070 | 11.5232 | 13.6701 | 16.41 | 18.5094 | 20.601
Fort FrancesIce Accretion2075RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2075 | 11.518 | 13.667 | 16.4025 | 18.5009 | 20.5963
Fort FrancesIce Accretion2080RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2080 | 11.5128 | 13.6639 | 16.395 | 18.4924 | 20.5915
Fort FrancesIce Accretion2085RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2085 | 11.5076 | 13.6608 | 16.3875 | 18.484 | 20.5868
Fort FrancesIce Accretion2090RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2090 | 11.4919 | 13.6452 | 16.365 | 18.4585 | 20.5632
Fort FrancesIce Accretion2095RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2095 | 11.4815 | 13.6327 | 16.35 | 18.4416 | 20.5443
Fort FrancesIce Accretion2100RCP6.0 | Fort Frances | Ice Accretion | RCP6.0 | 2100 | 11.471 | 13.6203 | 16.335 | 18.4246 | 20.5254
Fort FrancesIce Accretion2023RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2023 | 10.7717 | 12.7986 | 15.375 | 17.3398 | 19.3158
Fort FrancesIce Accretion2025RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2025 | 10.8378 | 12.8608 | 15.44 | 17.4076 | 19.3851
Fort FrancesIce Accretion2030RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2030 | 10.9039 | 12.9231 | 15.505 | 17.4754 | 19.4544
Fort FrancesIce Accretion2035RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2035 | 10.97 | 12.9853 | 15.57 | 17.5432 | 19.5237
Fort FrancesIce Accretion2040RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2040 | 11.1544 | 13.2136 | 15.85 | 17.8653 | 19.8828
Fort FrancesIce Accretion2045RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2045 | 11.3388 | 13.4418 | 16.13 | 18.1873 | 20.2419
Fort FrancesIce Accretion2050RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2050 | 11.5163 | 13.6659 | 16.4 | 18.4981 | 20.5947
Fort FrancesIce Accretion2055RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2055 | 11.5093 | 13.6618 | 16.39 | 18.4868 | 20.5884
Fort FrancesIce Accretion2060RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2060 | 11.4919 | 13.6452 | 16.365 | 18.4585 | 20.5632
Fort FrancesIce Accretion2065RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2065 | 11.4815 | 13.6327 | 16.35 | 18.4416 | 20.5443
Fort FrancesIce Accretion2070RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2070 | 11.311 | 13.4336 | 16.115 | 18.1761 | 20.2482
Fort FrancesIce Accretion2075RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2075 | 11.1509 | 13.2468 | 15.895 | 17.9274 | 19.971
Fort FrancesIce Accretion2080RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2080 | 10.9909 | 13.06 | 15.675 | 17.6788 | 19.6938
Fort FrancesIce Accretion2085RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2085 | 10.7508 | 12.7737 | 15.345 | 17.3144 | 19.2874
Fort FrancesIce Accretion2090RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2090 | 10.5108 | 12.4873 | 15.015 | 16.95 | 18.8811
Fort FrancesIce Accretion2095RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2095 | 10.5108 | 12.4873 | 15.015 | 16.95 | 18.8811
Fort FrancesIce Accretion2100RCP8.5 | Fort Frances | Ice Accretion | RCP8.5 | 2100 | 10.5108 | 12.4873 | 15.015 | 16.95 | 18.8811
Fort FrancesWind2023RCP4.5 | Fort Frances | Wind | RCP4.5 | 2023 | 72.3947 | 77.9872 | 83.8824 | 89.7721 | 95.6547
Fort FrancesWind2025RCP4.5 | Fort Frances | Wind | RCP4.5 | 2025 | 72.3802 | 77.9573 | 83.832 | 89.7047 | 95.5701
Fort FrancesWind2030RCP4.5 | Fort Frances | Wind | RCP4.5 | 2030 | 72.3657 | 77.9273 | 83.7816 | 89.6373 | 95.4855
Fort FrancesWind2035RCP4.5 | Fort Frances | Wind | RCP4.5 | 2035 | 72.3512 | 77.8974 | 83.7312 | 89.5699 | 95.4009
Fort FrancesWind2040RCP4.5 | Fort Frances | Wind | RCP4.5 | 2040 | 72.3367 | 77.8674 | 83.6808 | 89.5025 | 95.3163
Fort FrancesWind2045RCP4.5 | Fort Frances | Wind | RCP4.5 | 2045 | 72.3222 | 77.8375 | 83.6304 | 89.4351 | 95.2317
Fort FrancesWind2050RCP4.5 | Fort Frances | Wind | RCP4.5 | 2050 | 72.4672 | 78.0044 | 83.8236 | 89.6499 | 95.4708
Fort FrancesWind2055RCP4.5 | Fort Frances | Wind | RCP4.5 | 2055 | 72.6268 | 78.2012 | 84.0672 | 89.9321 | 95.7945
Fort FrancesWind2060RCP4.5 | Fort Frances | Wind | RCP4.5 | 2060 | 72.7864 | 78.3981 | 84.3108 | 90.2144 | 96.1181
Fort FrancesWind2065RCP4.5 | Fort Frances | Wind | RCP4.5 | 2065 | 72.946 | 78.595 | 84.5544 | 90.4966 | 96.4418
Fort FrancesWind2070RCP4.5 | Fort Frances | Wind | RCP4.5 | 2070 | 73.1055 | 78.7918 | 84.798 | 90.7788 | 96.7655
Fort FrancesWind2075RCP4.5 | Fort Frances | Wind | RCP4.5 | 2075 | 73.201 | 78.909 | 84.9408 | 90.9466 | 96.957
Fort FrancesWind2080RCP4.5 | Fort Frances | Wind | RCP4.5 | 2080 | 73.2965 | 79.0262 | 85.0836 | 91.1144 | 97.1485
Fort FrancesWind2085RCP4.5 | Fort Frances | Wind | RCP4.5 | 2085 | 73.392 | 79.1434 | 85.2264 | 91.2821 | 97.34
Fort FrancesWind2090RCP4.5 | Fort Frances | Wind | RCP4.5 | 2090 | 73.4875 | 79.2606 | 85.3692 | 91.4499 | 97.5316
Fort FrancesWind2095RCP4.5 | Fort Frances | Wind | RCP4.5 | 2095 | 73.583 | 79.3777 | 85.512 | 91.6177 | 97.7231
Fort FrancesWind2100RCP4.5 | Fort Frances | Wind | RCP4.5 | 2100 | 73.6785 | 79.4949 | 85.6548 | 91.7855 | 97.9146
Fort FrancesWind2023RCP6.0 | Fort Frances | Wind | RCP6.0 | 2023 | 72.3947 | 77.9872 | 83.8824 | 89.7721 | 95.6547
Fort FrancesWind2025RCP6.0 | Fort Frances | Wind | RCP6.0 | 2025 | 72.3802 | 77.9573 | 83.832 | 89.7047 | 95.5701
Fort FrancesWind2030RCP6.0 | Fort Frances | Wind | RCP6.0 | 2030 | 72.3657 | 77.9273 | 83.7816 | 89.6373 | 95.4855
Fort FrancesWind2035RCP6.0 | Fort Frances | Wind | RCP6.0 | 2035 | 72.3512 | 77.8974 | 83.7312 | 89.5699 | 95.4009
Fort FrancesWind2040RCP6.0 | Fort Frances | Wind | RCP6.0 | 2040 | 72.3367 | 77.8674 | 83.6808 | 89.5025 | 95.3163
Fort FrancesWind2045RCP6.0 | Fort Frances | Wind | RCP6.0 | 2045 | 72.3222 | 77.8375 | 83.6304 | 89.4351 | 95.2317
Fort FrancesWind2050RCP6.0 | Fort Frances | Wind | RCP6.0 | 2050 | 72.4672 | 78.0044 | 83.8236 | 89.6499 | 95.4708
Fort FrancesWind2055RCP6.0 | Fort Frances | Wind | RCP6.0 | 2055 | 72.6268 | 78.2012 | 84.0672 | 89.9321 | 95.7945
Fort FrancesWind2060RCP6.0 | Fort Frances | Wind | RCP6.0 | 2060 | 72.7864 | 78.3981 | 84.3108 | 90.2144 | 96.1181
Fort FrancesWind2065RCP6.0 | Fort Frances | Wind | RCP6.0 | 2065 | 72.946 | 78.595 | 84.5544 | 90.4966 | 96.4418
Fort FrancesWind2070RCP6.0 | Fort Frances | Wind | RCP6.0 | 2070 | 73.1055 | 78.7918 | 84.798 | 90.7788 | 96.7655
Fort FrancesWind2075RCP6.0 | Fort Frances | Wind | RCP6.0 | 2075 | 73.2488 | 78.9676 | 85.0122 | 91.0305 | 97.0528
Fort FrancesWind2080RCP6.0 | Fort Frances | Wind | RCP6.0 | 2080 | 73.392 | 79.1434 | 85.2264 | 91.2821 | 97.34
Fort FrancesWind2085RCP6.0 | Fort Frances | Wind | RCP6.0 | 2085 | 73.5353 | 79.3191 | 85.4406 | 91.5338 | 97.6273
Fort FrancesWind2090RCP6.0 | Fort Frances | Wind | RCP6.0 | 2090 | 73.9155 | 79.81 | 86.0664 | 92.2738 | 98.486
Fort FrancesWind2095RCP6.0 | Fort Frances | Wind | RCP6.0 | 2095 | 74.1524 | 80.1251 | 86.478 | 92.7622 | 99.0573
Fort FrancesWind2100RCP6.0 | Fort Frances | Wind | RCP6.0 | 2100 | 74.3894 | 80.4402 | 86.8896 | 93.2505 | 99.6287
Fort FrancesWind2023RCP8.5 | Fort Frances | Wind | RCP8.5 | 2023 | 72.3947 | 77.9872 | 83.8824 | 89.7721 | 95.6547
Fort FrancesWind2025RCP8.5 | Fort Frances | Wind | RCP8.5 | 2025 | 72.3657 | 77.9273 | 83.7816 | 89.6373 | 95.4855
Fort FrancesWind2030RCP8.5 | Fort Frances | Wind | RCP8.5 | 2030 | 72.3367 | 77.8674 | 83.6808 | 89.5025 | 95.3163
Fort FrancesWind2035RCP8.5 | Fort Frances | Wind | RCP8.5 | 2035 | 72.3077 | 77.8075 | 83.58 | 89.3677 | 95.1471
Fort FrancesWind2040RCP8.5 | Fort Frances | Wind | RCP8.5 | 2040 | 72.5736 | 78.1356 | 83.986 | 89.8381 | 95.6866
Fort FrancesWind2045RCP8.5 | Fort Frances | Wind | RCP8.5 | 2045 | 72.8396 | 78.4637 | 84.392 | 90.3084 | 96.226
Fort FrancesWind2050RCP8.5 | Fort Frances | Wind | RCP8.5 | 2050 | 73.2965 | 79.0262 | 85.0836 | 91.1144 | 97.1485
Fort FrancesWind2055RCP8.5 | Fort Frances | Wind | RCP8.5 | 2055 | 73.4875 | 79.2606 | 85.3692 | 91.4499 | 97.5316
Fort FrancesWind2060RCP8.5 | Fort Frances | Wind | RCP8.5 | 2060 | 73.9155 | 79.81 | 86.0664 | 92.2738 | 98.486
Fort FrancesWind2065RCP8.5 | Fort Frances | Wind | RCP8.5 | 2065 | 74.1524 | 80.1251 | 86.478 | 92.7622 | 99.0573
Fort FrancesWind2070RCP8.5 | Fort Frances | Wind | RCP8.5 | 2070 | 74.4885 | 80.5599 | 87.0324 | 93.4183 | 99.817
Fort FrancesWind2075RCP8.5 | Fort Frances | Wind | RCP8.5 | 2075 | 74.5876 | 80.6797 | 87.1752 | 93.5861 | 100.0054
Fort FrancesWind2080RCP8.5 | Fort Frances | Wind | RCP8.5 | 2080 | 74.6867 | 80.7995 | 87.318 | 93.7538 | 100.1937
Fort FrancesWind2085RCP8.5 | Fort Frances | Wind | RCP8.5 | 2085 | 74.879 | 81.0261 | 87.5868 | 94.0594 | 100.5384
Fort FrancesWind2090RCP8.5 | Fort Frances | Wind | RCP8.5 | 2090 | 75.0712 | 81.2526 | 87.8556 | 94.365 | 100.8832
Fort FrancesWind2095RCP8.5 | Fort Frances | Wind | RCP8.5 | 2095 | 75.0712 | 81.2526 | 87.8556 | 94.365 | 100.8832
Fort FrancesWind2100RCP8.5 | Fort Frances | Wind | RCP8.5 | 2100 | 75.0712 | 81.2526 | 87.8556 | 94.365 | 100.8832
GananoqueIce Accretion2023RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2023 | 20.8754 | 24.8751 | 29.97 | 33.8661 | 37.7244
GananoqueIce Accretion2025RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2025 | 20.9624 | 24.9954 | 30.13 | 34.0525 | 37.9449
GananoqueIce Accretion2030RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2030 | 21.0493 | 25.1158 | 30.29 | 34.239 | 38.1654
GananoqueIce Accretion2035RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2035 | 21.1363 | 25.2362 | 30.45 | 34.4254 | 38.3859
GananoqueIce Accretion2040RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2040 | 21.2233 | 25.3565 | 30.61 | 34.6119 | 38.6064
GananoqueIce Accretion2045RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2045 | 21.3103 | 25.4768 | 30.77 | 34.7983 | 38.8269
GananoqueIce Accretion2050RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2050 | 21.2804 | 25.4777 | 30.804 | 34.856 | 38.9189
GananoqueIce Accretion2055RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2055 | 21.1635 | 25.3582 | 30.678 | 34.7272 | 38.7904
GananoqueIce Accretion2060RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2060 | 21.0466 | 25.2386 | 30.552 | 34.5983 | 38.6618
GananoqueIce Accretion2065RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2065 | 20.9297 | 25.1191 | 30.426 | 34.4695 | 38.5333
GananoqueIce Accretion2070RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2070 | 20.8128 | 24.9996 | 30.3 | 34.3407 | 38.4048
GananoqueIce Accretion2075RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2075 | 20.8267 | 25.0452 | 30.38 | 34.448 | 38.5371
GananoqueIce Accretion2080RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2080 | 20.8406 | 25.0909 | 30.46 | 34.5554 | 38.6694
GananoqueIce Accretion2085RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2085 | 20.8545 | 25.1365 | 30.54 | 34.6628 | 38.8017
GananoqueIce Accretion2090RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2090 | 20.8684 | 25.1822 | 30.62 | 34.7701 | 38.934
GananoqueIce Accretion2095RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2095 | 20.8823 | 25.2278 | 30.7 | 34.8774 | 39.0663
GananoqueIce Accretion2100RCP4.5 | Gananoque | Ice Accretion | RCP4.5 | 2100 | 20.8963 | 25.2735 | 30.78 | 34.9848 | 39.1986
GananoqueIce Accretion2023RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2023 | 20.8754 | 24.8751 | 29.97 | 33.8661 | 37.7244
GananoqueIce Accretion2025RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2025 | 20.9624 | 24.9954 | 30.13 | 34.0525 | 37.9449
GananoqueIce Accretion2030RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2030 | 21.0493 | 25.1158 | 30.29 | 34.239 | 38.1654
GananoqueIce Accretion2035RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2035 | 21.1363 | 25.2362 | 30.45 | 34.4254 | 38.3859
GananoqueIce Accretion2040RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2040 | 21.2233 | 25.3565 | 30.61 | 34.6119 | 38.6064
GananoqueIce Accretion2045RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2045 | 21.3103 | 25.4768 | 30.77 | 34.7983 | 38.8269
GananoqueIce Accretion2050RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2050 | 21.2804 | 25.4777 | 30.804 | 34.856 | 38.9189
GananoqueIce Accretion2055RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2055 | 21.1635 | 25.3582 | 30.678 | 34.7272 | 38.7904
GananoqueIce Accretion2060RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2060 | 21.0466 | 25.2386 | 30.552 | 34.5983 | 38.6618
GananoqueIce Accretion2065RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2065 | 20.9297 | 25.1191 | 30.426 | 34.4695 | 38.5333
GananoqueIce Accretion2070RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2070 | 20.8128 | 24.9996 | 30.3 | 34.3407 | 38.4048
GananoqueIce Accretion2075RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2075 | 20.8336 | 25.0681 | 30.42 | 34.5017 | 38.6032
GananoqueIce Accretion2080RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2080 | 20.8545 | 25.1365 | 30.54 | 34.6628 | 38.8017
GananoqueIce Accretion2085RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2085 | 20.8754 | 25.205 | 30.66 | 34.8238 | 39.0001
GananoqueIce Accretion2090RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2090 | 20.5414 | 24.8751 | 30.34 | 34.4989 | 38.6694
GananoqueIce Accretion2095RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2095 | 20.1865 | 24.4767 | 29.9 | 34.013 | 38.1402
GananoqueIce Accretion2100RCP6.0 | Gananoque | Ice Accretion | RCP6.0 | 2100 | 19.8316 | 24.0783 | 29.46 | 33.5271 | 37.611
GananoqueIce Accretion2023RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2023 | 20.8754 | 24.8751 | 29.97 | 33.8661 | 37.7244
GananoqueIce Accretion2025RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2025 | 21.0493 | 25.1158 | 30.29 | 34.239 | 38.1654
GananoqueIce Accretion2030RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2030 | 21.2233 | 25.3565 | 30.61 | 34.6119 | 38.6064
GananoqueIce Accretion2035RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2035 | 21.3973 | 25.5972 | 30.93 | 34.9848 | 39.0474
GananoqueIce Accretion2040RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2040 | 21.2024 | 25.398 | 30.72 | 34.7701 | 38.8332
GananoqueIce Accretion2045RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2045 | 21.0076 | 25.1988 | 30.51 | 34.5554 | 38.619
GananoqueIce Accretion2050RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2050 | 20.8406 | 25.0909 | 30.46 | 34.5554 | 38.6694
GananoqueIce Accretion2055RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2055 | 20.8684 | 25.1822 | 30.62 | 34.7701 | 38.934
GananoqueIce Accretion2060RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2060 | 20.5414 | 24.8751 | 30.34 | 34.4989 | 38.6694
GananoqueIce Accretion2065RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2065 | 20.1865 | 24.4767 | 29.9 | 34.013 | 38.1402
GananoqueIce Accretion2070RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2070 | 19.5463 | 23.7795 | 29.13 | 33.1881 | 37.2456
GananoqueIce Accretion2075RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2075 | 19.261 | 23.4807 | 28.8 | 32.8491 | 36.8802
GananoqueIce Accretion2080RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2080 | 18.9757 | 23.1819 | 28.47 | 32.5101 | 36.5148
GananoqueIce Accretion2085RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2085 | 18.266 | 22.3477 | 27.48 | 31.3914 | 35.2674
GananoqueIce Accretion2090RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2090 | 17.5562 | 21.5136 | 26.49 | 30.2727 | 34.02
GananoqueIce Accretion2095RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2095 | 17.5562 | 21.5136 | 26.49 | 30.2727 | 34.02
GananoqueIce Accretion2100RCP8.5 | Gananoque | Ice Accretion | RCP8.5 | 2100 | 17.5562 | 21.5136 | 26.49 | 30.2727 | 34.02
GananoqueWind2023RCP4.5 | Gananoque | Wind | RCP4.5 | 2023 | 86.1755 | 92.721 | 99.6 | 106.4971 | 113.3958
GananoqueWind2025RCP4.5 | Gananoque | Wind | RCP4.5 | 2025 | 86.1597 | 92.6931 | 99.5533 | 106.4365 | 113.3198
GananoqueWind2030RCP4.5 | Gananoque | Wind | RCP4.5 | 2030 | 86.1439 | 92.6652 | 99.5067 | 106.3758 | 113.2438
GananoqueWind2035RCP4.5 | Gananoque | Wind | RCP4.5 | 2035 | 86.1281 | 92.6373 | 99.46 | 106.3152 | 113.1678
GananoqueWind2040RCP4.5 | Gananoque | Wind | RCP4.5 | 2040 | 86.1122 | 92.6094 | 99.4133 | 106.2546 | 113.0918
GananoqueWind2045RCP4.5 | Gananoque | Wind | RCP4.5 | 2045 | 86.0964 | 92.5815 | 99.3667 | 106.1939 | 113.0158
GananoqueWind2050RCP4.5 | Gananoque | Wind | RCP4.5 | 2050 | 86.1894 | 92.6857 | 99.482 | 106.3195 | 113.1518
GananoqueWind2055RCP4.5 | Gananoque | Wind | RCP4.5 | 2055 | 86.2982 | 92.8177 | 99.644 | 106.5057 | 113.3639
GananoqueWind2060RCP4.5 | Gananoque | Wind | RCP4.5 | 2060 | 86.407 | 92.9498 | 99.806 | 106.6918 | 113.5759
GananoqueWind2065RCP4.5 | Gananoque | Wind | RCP4.5 | 2065 | 86.5158 | 93.0818 | 99.968 | 106.878 | 113.788
GananoqueWind2070RCP4.5 | Gananoque | Wind | RCP4.5 | 2070 | 86.6246 | 93.2139 | 100.13 | 107.0642 | 114
GananoqueWind2075RCP4.5 | Gananoque | Wind | RCP4.5 | 2075 | 86.7426 | 93.3751 | 100.3433 | 107.321 | 114.3002
GananoqueWind2080RCP4.5 | Gananoque | Wind | RCP4.5 | 2080 | 86.8606 | 93.5363 | 100.5567 | 107.5778 | 114.6004
GananoqueWind2085RCP4.5 | Gananoque | Wind | RCP4.5 | 2085 | 86.9786 | 93.6975 | 100.77 | 107.8346 | 114.9006
GananoqueWind2090RCP4.5 | Gananoque | Wind | RCP4.5 | 2090 | 87.0966 | 93.8587 | 100.9833 | 108.0914 | 115.2008
GananoqueWind2095RCP4.5 | Gananoque | Wind | RCP4.5 | 2095 | 87.2146 | 94.0199 | 101.1967 | 108.3482 | 115.501
GananoqueWind2100RCP4.5 | Gananoque | Wind | RCP4.5 | 2100 | 87.3326 | 94.1811 | 101.41 | 108.605 | 115.8012
GananoqueWind2023RCP6.0 | Gananoque | Wind | RCP6.0 | 2023 | 86.1755 | 92.721 | 99.6 | 106.4971 | 113.3958
GananoqueWind2025RCP6.0 | Gananoque | Wind | RCP6.0 | 2025 | 86.1597 | 92.6931 | 99.5533 | 106.4365 | 113.3198
GananoqueWind2030RCP6.0 | Gananoque | Wind | RCP6.0 | 2030 | 86.1439 | 92.6652 | 99.5067 | 106.3758 | 113.2438
GananoqueWind2035RCP6.0 | Gananoque | Wind | RCP6.0 | 2035 | 86.1281 | 92.6373 | 99.46 | 106.3152 | 113.1678
GananoqueWind2040RCP6.0 | Gananoque | Wind | RCP6.0 | 2040 | 86.1122 | 92.6094 | 99.4133 | 106.2546 | 113.0918
GananoqueWind2045RCP6.0 | Gananoque | Wind | RCP6.0 | 2045 | 86.0964 | 92.5815 | 99.3667 | 106.1939 | 113.0158
GananoqueWind2050RCP6.0 | Gananoque | Wind | RCP6.0 | 2050 | 86.1894 | 92.6857 | 99.482 | 106.3195 | 113.1518
GananoqueWind2055RCP6.0 | Gananoque | Wind | RCP6.0 | 2055 | 86.2982 | 92.8177 | 99.644 | 106.5057 | 113.3639
GananoqueWind2060RCP6.0 | Gananoque | Wind | RCP6.0 | 2060 | 86.407 | 92.9498 | 99.806 | 106.6918 | 113.5759
GananoqueWind2065RCP6.0 | Gananoque | Wind | RCP6.0 | 2065 | 86.5158 | 93.0818 | 99.968 | 106.878 | 113.788
GananoqueWind2070RCP6.0 | Gananoque | Wind | RCP6.0 | 2070 | 86.6246 | 93.2139 | 100.13 | 107.0642 | 114
GananoqueWind2075RCP6.0 | Gananoque | Wind | RCP6.0 | 2075 | 86.8016 | 93.4557 | 100.45 | 107.4494 | 114.4503
GananoqueWind2080RCP6.0 | Gananoque | Wind | RCP6.0 | 2080 | 86.9786 | 93.6975 | 100.77 | 107.8346 | 114.9006
GananoqueWind2085RCP6.0 | Gananoque | Wind | RCP6.0 | 2085 | 87.1556 | 93.9393 | 101.09 | 108.2198 | 115.3509
GananoqueWind2090RCP6.0 | Gananoque | Wind | RCP6.0 | 2090 | 87.5312 | 94.4384 | 101.7433 | 109.0045 | 116.2648
GananoqueWind2095RCP6.0 | Gananoque | Wind | RCP6.0 | 2095 | 87.7298 | 94.6957 | 102.0767 | 109.4039 | 116.7284
GananoqueWind2100RCP6.0 | Gananoque | Wind | RCP6.0 | 2100 | 87.9284 | 94.953 | 102.41 | 109.8034 | 117.192
GananoqueWind2023RCP8.5 | Gananoque | Wind | RCP8.5 | 2023 | 86.1755 | 92.721 | 99.6 | 106.4971 | 113.3958
GananoqueWind2025RCP8.5 | Gananoque | Wind | RCP8.5 | 2025 | 86.1439 | 92.6652 | 99.5067 | 106.3758 | 113.2438
GananoqueWind2030RCP8.5 | Gananoque | Wind | RCP8.5 | 2030 | 86.1122 | 92.6094 | 99.4133 | 106.2546 | 113.0918
GananoqueWind2035RCP8.5 | Gananoque | Wind | RCP8.5 | 2035 | 86.0806 | 92.5536 | 99.32 | 106.1333 | 112.9398
GananoqueWind2040RCP8.5 | Gananoque | Wind | RCP8.5 | 2040 | 86.2619 | 92.7737 | 99.59 | 106.4436 | 113.2932
GananoqueWind2045RCP8.5 | Gananoque | Wind | RCP8.5 | 2045 | 86.4432 | 92.9938 | 99.86 | 106.7539 | 113.6466
GananoqueWind2050RCP8.5 | Gananoque | Wind | RCP8.5 | 2050 | 86.8606 | 93.5363 | 100.5567 | 107.5778 | 114.6004
GananoqueWind2055RCP8.5 | Gananoque | Wind | RCP8.5 | 2055 | 87.0966 | 93.8587 | 100.9833 | 108.0914 | 115.2008
GananoqueWind2060RCP8.5 | Gananoque | Wind | RCP8.5 | 2060 | 87.5312 | 94.4384 | 101.7433 | 109.0045 | 116.2648
GananoqueWind2065RCP8.5 | Gananoque | Wind | RCP8.5 | 2065 | 87.7298 | 94.6957 | 102.0767 | 109.4039 | 116.7284
GananoqueWind2070RCP8.5 | Gananoque | Wind | RCP8.5 | 2070 | 88.0004 | 95.0584 | 102.5567 | 109.9853 | 117.4086
GananoqueWind2075RCP8.5 | Gananoque | Wind | RCP8.5 | 2075 | 88.0723 | 95.1638 | 102.7033 | 110.1672 | 117.6252
GananoqueWind2080RCP8.5 | Gananoque | Wind | RCP8.5 | 2080 | 88.1443 | 95.2692 | 102.85 | 110.3491 | 117.8418
GananoqueWind2085RCP8.5 | Gananoque | Wind | RCP8.5 | 2085 | 88.3127 | 95.5017 | 103.165 | 110.7289 | 118.2978
GananoqueWind2090RCP8.5 | Gananoque | Wind | RCP8.5 | 2090 | 88.481 | 95.7342 | 103.48 | 111.1088 | 118.7538
GananoqueWind2095RCP8.5 | Gananoque | Wind | RCP8.5 | 2095 | 88.481 | 95.7342 | 103.48 | 111.1088 | 118.7538
GananoqueWind2100RCP8.5 | Gananoque | Wind | RCP8.5 | 2100 | 88.481 | 95.7342 | 103.48 | 111.1088 | 118.7538
GeraldtonIce Accretion2023RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2023 | 10.7091 | 12.7737 | 15.39 | 17.3907 | 19.3914
GeraldtonIce Accretion2025RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2025 | 10.7961 | 12.8774 | 15.5175 | 17.5348 | 19.552
GeraldtonIce Accretion2030RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2030 | 10.883 | 12.9812 | 15.645 | 17.6788 | 19.7127
GeraldtonIce Accretion2035RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2035 | 10.97 | 13.0849 | 15.7725 | 17.8229 | 19.8733
GeraldtonIce Accretion2040RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2040 | 11.057 | 13.1887 | 15.9 | 17.967 | 20.034
GeraldtonIce Accretion2045RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2045 | 11.144 | 13.2925 | 16.0275 | 18.1111 | 20.1946
GeraldtonIce Accretion2050RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2050 | 11.2748 | 13.4485 | 16.215 | 18.3229 | 20.4309
GeraldtonIce Accretion2055RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2055 | 11.3186 | 13.5008 | 16.275 | 18.3907 | 20.5065
GeraldtonIce Accretion2060RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2060 | 11.3625 | 13.5531 | 16.335 | 18.4585 | 20.5821
GeraldtonIce Accretion2065RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2065 | 11.4063 | 13.6054 | 16.395 | 18.5263 | 20.6577
GeraldtonIce Accretion2070RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2070 | 11.4501 | 13.6576 | 16.455 | 18.5941 | 20.7333
GeraldtonIce Accretion2075RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2075 | 11.4971 | 13.7178 | 16.53 | 18.6817 | 20.8309
GeraldtonIce Accretion2080RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2080 | 11.5441 | 13.778 | 16.605 | 18.7693 | 20.9286
GeraldtonIce Accretion2085RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2085 | 11.5911 | 13.8382 | 16.68 | 18.8569 | 21.0262
GeraldtonIce Accretion2090RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2090 | 11.638 | 13.8983 | 16.755 | 18.9444 | 21.1239
GeraldtonIce Accretion2095RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2095 | 11.685 | 13.9585 | 16.83 | 19.032 | 21.2216
GeraldtonIce Accretion2100RCP4.5 | Geraldton | Ice Accretion | RCP4.5 | 2100 | 11.732 | 14.0187 | 16.905 | 19.1196 | 21.3192
GeraldtonIce Accretion2023RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2023 | 10.7091 | 12.7737 | 15.39 | 17.3907 | 19.3914
GeraldtonIce Accretion2025RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2025 | 10.7961 | 12.8774 | 15.5175 | 17.5348 | 19.552
GeraldtonIce Accretion2030RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2030 | 10.883 | 12.9812 | 15.645 | 17.6788 | 19.7127
GeraldtonIce Accretion2035RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2035 | 10.97 | 13.0849 | 15.7725 | 17.8229 | 19.8733
GeraldtonIce Accretion2040RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2040 | 11.057 | 13.1887 | 15.9 | 17.967 | 20.034
GeraldtonIce Accretion2045RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2045 | 11.144 | 13.2925 | 16.0275 | 18.1111 | 20.1946
GeraldtonIce Accretion2050RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2050 | 11.2748 | 13.4485 | 16.215 | 18.3229 | 20.4309
GeraldtonIce Accretion2055RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2055 | 11.3186 | 13.5008 | 16.275 | 18.3907 | 20.5065
GeraldtonIce Accretion2060RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2060 | 11.3625 | 13.5531 | 16.335 | 18.4585 | 20.5821
GeraldtonIce Accretion2065RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2065 | 11.4063 | 13.6054 | 16.395 | 18.5263 | 20.6577
GeraldtonIce Accretion2070RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2070 | 11.4501 | 13.6576 | 16.455 | 18.5941 | 20.7333
GeraldtonIce Accretion2075RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2075 | 11.5206 | 13.7479 | 16.5675 | 18.7255 | 20.8798
GeraldtonIce Accretion2080RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2080 | 11.5911 | 13.8382 | 16.68 | 18.8569 | 21.0262
GeraldtonIce Accretion2085RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2085 | 11.6615 | 13.9284 | 16.7925 | 18.9882 | 21.1727
GeraldtonIce Accretion2090RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2090 | 11.6206 | 13.8776 | 16.73 | 18.9162 | 21.0924
GeraldtonIce Accretion2095RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2095 | 11.5093 | 13.7365 | 16.555 | 18.7128 | 20.8656
GeraldtonIce Accretion2100RCP6.0 | Geraldton | Ice Accretion | RCP6.0 | 2100 | 11.398 | 13.5954 | 16.38 | 18.5094 | 20.6388
GeraldtonIce Accretion2023RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2023 | 10.7091 | 12.7737 | 15.39 | 17.3907 | 19.3914
GeraldtonIce Accretion2025RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2025 | 10.883 | 12.9812 | 15.645 | 17.6788 | 19.7127
GeraldtonIce Accretion2030RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2030 | 11.057 | 13.1887 | 15.9 | 17.967 | 20.034
GeraldtonIce Accretion2035RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2035 | 11.231 | 13.3962 | 16.155 | 18.2551 | 20.3553
GeraldtonIce Accretion2040RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2040 | 11.304 | 13.4833 | 16.255 | 18.3681 | 20.4813
GeraldtonIce Accretion2045RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2045 | 11.3771 | 13.5705 | 16.355 | 18.4811 | 20.6073
GeraldtonIce Accretion2050RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2050 | 11.5441 | 13.778 | 16.605 | 18.7693 | 20.9286
GeraldtonIce Accretion2055RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2055 | 11.638 | 13.8983 | 16.755 | 18.9444 | 21.1239
GeraldtonIce Accretion2060RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2060 | 11.6206 | 13.8776 | 16.73 | 18.9162 | 21.0924
GeraldtonIce Accretion2065RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2065 | 11.5093 | 13.7365 | 16.555 | 18.7128 | 20.8656
GeraldtonIce Accretion2070RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2070 | 11.3701 | 13.5705 | 16.36 | 18.4924 | 20.6262
GeraldtonIce Accretion2075RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2075 | 11.3423 | 13.5456 | 16.34 | 18.4755 | 20.6136
GeraldtonIce Accretion2080RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2080 | 11.3145 | 13.5207 | 16.32 | 18.4585 | 20.601
GeraldtonIce Accretion2085RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2085 | 11.0587 | 13.2343 | 15.9825 | 18.0857 | 20.1852
GeraldtonIce Accretion2090RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2090 | 10.803 | 12.948 | 15.645 | 17.7127 | 19.7694
GeraldtonIce Accretion2095RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2095 | 10.803 | 12.948 | 15.645 | 17.7127 | 19.7694
GeraldtonIce Accretion2100RCP8.5 | Geraldton | Ice Accretion | RCP8.5 | 2100 | 10.803 | 12.948 | 15.645 | 17.7127 | 19.7694
GeraldtonWind2023RCP4.5 | Geraldton | Wind | RCP4.5 | 2023 | 73.6162 | 79.2634 | 85.204 | 91.141 | 97.0841
GeraldtonWind2025RCP4.5 | Geraldton | Wind | RCP4.5 | 2025 | 73.7324 | 79.3991 | 85.3641 | 91.3229 | 97.2876
GeraldtonWind2030RCP4.5 | Geraldton | Wind | RCP4.5 | 2030 | 73.8486 | 79.5348 | 85.5242 | 91.5048 | 97.4911
GeraldtonWind2035RCP4.5 | Geraldton | Wind | RCP4.5 | 2035 | 73.9648 | 79.6705 | 85.6842 | 91.6867 | 97.6946
GeraldtonWind2040RCP4.5 | Geraldton | Wind | RCP4.5 | 2040 | 74.081 | 79.8062 | 85.8443 | 91.8686 | 97.8981
GeraldtonWind2045RCP4.5 | Geraldton | Wind | RCP4.5 | 2045 | 74.1972 | 79.9419 | 86.0044 | 92.0505 | 98.1016
GeraldtonWind2050RCP4.5 | Geraldton | Wind | RCP4.5 | 2050 | 74.4588 | 80.2563 | 86.3838 | 92.4871 | 98.5957
GeraldtonWind2055RCP4.5 | Geraldton | Wind | RCP4.5 | 2055 | 74.6041 | 80.435 | 86.6031 | 92.7417 | 98.8864
GeraldtonWind2060RCP4.5 | Geraldton | Wind | RCP4.5 | 2060 | 74.7494 | 80.6136 | 86.8224 | 92.9964 | 99.1771
GeraldtonWind2065RCP4.5 | Geraldton | Wind | RCP4.5 | 2065 | 74.8948 | 80.7923 | 87.0417 | 93.251 | 99.4678
GeraldtonWind2070RCP4.5 | Geraldton | Wind | RCP4.5 | 2070 | 75.0401 | 80.9709 | 87.261 | 93.5057 | 99.7585
GeraldtonWind2075RCP4.5 | Geraldton | Wind | RCP4.5 | 2075 | 75.1049 | 81.0434 | 87.3403 | 93.5921 | 99.8522
GeraldtonWind2080RCP4.5 | Geraldton | Wind | RCP4.5 | 2080 | 75.1697 | 81.1158 | 87.4197 | 93.6785 | 99.9459
GeraldtonWind2085RCP4.5 | Geraldton | Wind | RCP4.5 | 2085 | 75.2346 | 81.1883 | 87.499 | 93.7649 | 100.0396
GeraldtonWind2090RCP4.5 | Geraldton | Wind | RCP4.5 | 2090 | 75.2994 | 81.2608 | 87.5783 | 93.8513 | 100.1332
GeraldtonWind2095RCP4.5 | Geraldton | Wind | RCP4.5 | 2095 | 75.3642 | 81.3332 | 87.6577 | 93.9377 | 100.2269
GeraldtonWind2100RCP4.5 | Geraldton | Wind | RCP4.5 | 2100 | 75.4291 | 81.4057 | 87.737 | 94.0241 | 100.3206
GeraldtonWind2023RCP6.0 | Geraldton | Wind | RCP6.0 | 2023 | 73.6162 | 79.2634 | 85.204 | 91.141 | 97.0841
GeraldtonWind2025RCP6.0 | Geraldton | Wind | RCP6.0 | 2025 | 73.7324 | 79.3991 | 85.3641 | 91.3229 | 97.2876
GeraldtonWind2030RCP6.0 | Geraldton | Wind | RCP6.0 | 2030 | 73.8486 | 79.5348 | 85.5242 | 91.5048 | 97.4911
GeraldtonWind2035RCP6.0 | Geraldton | Wind | RCP6.0 | 2035 | 73.9648 | 79.6705 | 85.6842 | 91.6867 | 97.6946
GeraldtonWind2040RCP6.0 | Geraldton | Wind | RCP6.0 | 2040 | 74.081 | 79.8062 | 85.8443 | 91.8686 | 97.8981
GeraldtonWind2045RCP6.0 | Geraldton | Wind | RCP6.0 | 2045 | 74.1972 | 79.9419 | 86.0044 | 92.0505 | 98.1016
GeraldtonWind2050RCP6.0 | Geraldton | Wind | RCP6.0 | 2050 | 74.4588 | 80.2563 | 86.3838 | 92.4871 | 98.5957
GeraldtonWind2055RCP6.0 | Geraldton | Wind | RCP6.0 | 2055 | 74.6041 | 80.435 | 86.6031 | 92.7417 | 98.8864
GeraldtonWind2060RCP6.0 | Geraldton | Wind | RCP6.0 | 2060 | 74.7494 | 80.6136 | 86.8224 | 92.9964 | 99.1771
GeraldtonWind2065RCP6.0 | Geraldton | Wind | RCP6.0 | 2065 | 74.8948 | 80.7923 | 87.0417 | 93.251 | 99.4678
GeraldtonWind2070RCP6.0 | Geraldton | Wind | RCP6.0 | 2070 | 75.0401 | 80.9709 | 87.261 | 93.5057 | 99.7585
GeraldtonWind2075RCP6.0 | Geraldton | Wind | RCP6.0 | 2075 | 75.1373 | 81.0796 | 87.38 | 93.6353 | 99.8991
GeraldtonWind2080RCP6.0 | Geraldton | Wind | RCP6.0 | 2080 | 75.2346 | 81.1883 | 87.499 | 93.7649 | 100.0396
GeraldtonWind2085RCP6.0 | Geraldton | Wind | RCP6.0 | 2085 | 75.3318 | 81.297 | 87.618 | 93.8945 | 100.1801
GeraldtonWind2090RCP6.0 | Geraldton | Wind | RCP6.0 | 2090 | 75.4878 | 81.4847 | 87.8447 | 94.1545 | 100.4724
GeraldtonWind2095RCP6.0 | Geraldton | Wind | RCP6.0 | 2095 | 75.5465 | 81.5638 | 87.9523 | 94.2848 | 100.6242
GeraldtonWind2100RCP6.0 | Geraldton | Wind | RCP6.0 | 2100 | 75.6052 | 81.6428 | 88.06 | 94.4152 | 100.776
GeraldtonWind2023RCP8.5 | Geraldton | Wind | RCP8.5 | 2023 | 73.6162 | 79.2634 | 85.204 | 91.141 | 97.0841
GeraldtonWind2025RCP8.5 | Geraldton | Wind | RCP8.5 | 2025 | 73.8486 | 79.5348 | 85.5242 | 91.5048 | 97.4911
GeraldtonWind2030RCP8.5 | Geraldton | Wind | RCP8.5 | 2030 | 74.081 | 79.8062 | 85.8443 | 91.8686 | 97.8981
GeraldtonWind2035RCP8.5 | Geraldton | Wind | RCP8.5 | 2035 | 74.3135 | 80.0776 | 86.1645 | 92.2324 | 98.305
GeraldtonWind2040RCP8.5 | Geraldton | Wind | RCP8.5 | 2040 | 74.5557 | 80.3754 | 86.53 | 92.6568 | 98.7895
GeraldtonWind2045RCP8.5 | Geraldton | Wind | RCP8.5 | 2045 | 74.7979 | 80.6732 | 86.8955 | 93.0813 | 99.2741
GeraldtonWind2050RCP8.5 | Geraldton | Wind | RCP8.5 | 2050 | 75.1697 | 81.1158 | 87.4197 | 93.6785 | 99.9459
GeraldtonWind2055RCP8.5 | Geraldton | Wind | RCP8.5 | 2055 | 75.2994 | 81.2608 | 87.5783 | 93.8513 | 100.1332
GeraldtonWind2060RCP8.5 | Geraldton | Wind | RCP8.5 | 2060 | 75.4878 | 81.4847 | 87.8447 | 94.1545 | 100.4724
GeraldtonWind2065RCP8.5 | Geraldton | Wind | RCP8.5 | 2065 | 75.5465 | 81.5638 | 87.9523 | 94.2848 | 100.6242
GeraldtonWind2070RCP8.5 | Geraldton | Wind | RCP8.5 | 2070 | 75.5857 | 81.6033 | 87.9948 | 94.3303 | 100.6726
GeraldtonWind2075RCP8.5 | Geraldton | Wind | RCP8.5 | 2075 | 75.5661 | 81.5638 | 87.9297 | 94.2454 | 100.5693
GeraldtonWind2080RCP8.5 | Geraldton | Wind | RCP8.5 | 2080 | 75.5465 | 81.5243 | 87.8645 | 94.1605 | 100.4659
GeraldtonWind2085RCP8.5 | Geraldton | Wind | RCP8.5 | 2085 | 75.8071 | 81.8681 | 88.315 | 94.6971 | 101.0909
GeraldtonWind2090RCP8.5 | Geraldton | Wind | RCP8.5 | 2090 | 76.0676 | 82.212 | 88.7655 | 95.2337 | 101.7159
GeraldtonWind2095RCP8.5 | Geraldton | Wind | RCP8.5 | 2095 | 76.0676 | 82.212 | 88.7655 | 95.2337 | 101.7159
GeraldtonWind2100RCP8.5 | Geraldton | Wind | RCP8.5 | 2100 | 76.0676 | 82.212 | 88.7655 | 95.2337 | 101.7159
GlencoeIce Accretion2023RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2023 | 17.4226 | 20.911 | 25.324 | 28.6749 | 32.0393
GlencoeIce Accretion2025RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2025 | 17.3532 | 20.8427 | 25.2547 | 28.6063 | 31.9683
GlencoeIce Accretion2030RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2030 | 17.2839 | 20.7743 | 25.1853 | 28.5378 | 31.8973
GlencoeIce Accretion2035RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2035 | 17.2145 | 20.706 | 25.116 | 28.4692 | 31.8263
GlencoeIce Accretion2040RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2040 | 17.1452 | 20.6377 | 25.0467 | 28.4007 | 31.7554
GlencoeIce Accretion2045RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2045 | 17.0758 | 20.5693 | 24.9773 | 28.3321 | 31.6844
GlencoeIce Accretion2050RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2050 | 16.6881 | 20.1471 | 24.5024 | 27.8229 | 31.1351
GlencoeIce Accretion2055RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2055 | 16.3696 | 19.7932 | 24.0968 | 27.3822 | 30.6568
GlencoeIce Accretion2060RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2060 | 16.0512 | 19.4393 | 23.6912 | 26.9415 | 30.1785
GlencoeIce Accretion2065RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2065 | 15.7328 | 19.0854 | 23.2856 | 26.5008 | 29.7002
GlencoeIce Accretion2070RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2070 | 15.4144 | 18.7314 | 22.88 | 26.0601 | 29.2219
GlencoeIce Accretion2075RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2075 | 15.2696 | 18.5804 | 22.724 | 25.8936 | 29.0472
GlencoeIce Accretion2080RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2080 | 15.1249 | 18.4293 | 22.568 | 25.7271 | 28.8725
GlencoeIce Accretion2085RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2085 | 14.9802 | 18.2783 | 22.412 | 25.5606 | 28.6978
GlencoeIce Accretion2090RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2090 | 14.8354 | 18.1272 | 22.256 | 25.3941 | 28.523
GlencoeIce Accretion2095RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2095 | 14.6907 | 17.9761 | 22.1 | 25.2276 | 28.3483
GlencoeIce Accretion2100RCP4.5 | Glencoe | Ice Accretion | RCP4.5 | 2100 | 14.546 | 17.8251 | 21.944 | 25.0611 | 28.1736
GlencoeIce Accretion2023RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2023 | 17.4226 | 20.911 | 25.324 | 28.6749 | 32.0393
GlencoeIce Accretion2025RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2025 | 17.3532 | 20.8427 | 25.2547 | 28.6063 | 31.9683
GlencoeIce Accretion2030RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2030 | 17.2839 | 20.7743 | 25.1853 | 28.5378 | 31.8973
GlencoeIce Accretion2035RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2035 | 17.2145 | 20.706 | 25.116 | 28.4692 | 31.8263
GlencoeIce Accretion2040RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2040 | 17.1452 | 20.6377 | 25.0467 | 28.4007 | 31.7554
GlencoeIce Accretion2045RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2045 | 17.0758 | 20.5693 | 24.9773 | 28.3321 | 31.6844
GlencoeIce Accretion2050RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2050 | 16.6881 | 20.1471 | 24.5024 | 27.8229 | 31.1351
GlencoeIce Accretion2055RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2055 | 16.3696 | 19.7932 | 24.0968 | 27.3822 | 30.6568
GlencoeIce Accretion2060RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2060 | 16.0512 | 19.4393 | 23.6912 | 26.9415 | 30.1785
GlencoeIce Accretion2065RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2065 | 15.7328 | 19.0854 | 23.2856 | 26.5008 | 29.7002
GlencoeIce Accretion2070RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2070 | 15.4144 | 18.7314 | 22.88 | 26.0601 | 29.2219
GlencoeIce Accretion2075RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2075 | 15.1973 | 18.5048 | 22.646 | 25.8103 | 28.9598
GlencoeIce Accretion2080RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2080 | 14.9802 | 18.2783 | 22.412 | 25.5606 | 28.6978
GlencoeIce Accretion2085RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2085 | 14.7631 | 18.0517 | 22.178 | 25.3109 | 28.4357
GlencoeIce Accretion2090RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2090 | 14.1057 | 17.3287 | 21.372 | 24.4246 | 27.4747
GlencoeIce Accretion2095RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2095 | 13.6655 | 16.8324 | 20.8 | 23.788 | 26.7758
GlencoeIce Accretion2100RCP6.0 | Glencoe | Ice Accretion | RCP6.0 | 2100 | 13.2253 | 16.3361 | 20.228 | 23.1514 | 26.077
GlencoeIce Accretion2023RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2023 | 17.4226 | 20.911 | 25.324 | 28.6749 | 32.0393
GlencoeIce Accretion2025RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2025 | 17.2839 | 20.7743 | 25.1853 | 28.5378 | 31.8973
GlencoeIce Accretion2030RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2030 | 17.1452 | 20.6377 | 25.0467 | 28.4007 | 31.7554
GlencoeIce Accretion2035RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2035 | 17.0065 | 20.501 | 24.908 | 28.2636 | 31.6134
GlencoeIce Accretion2040RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2040 | 16.4758 | 19.9111 | 24.232 | 27.5291 | 30.8162
GlencoeIce Accretion2045RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2045 | 15.9451 | 19.3213 | 23.556 | 26.7946 | 30.0191
GlencoeIce Accretion2050RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2050 | 15.1249 | 18.4293 | 22.568 | 25.7271 | 28.8725
GlencoeIce Accretion2055RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2055 | 14.8354 | 18.1272 | 22.256 | 25.3941 | 28.523
GlencoeIce Accretion2060RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2060 | 14.1057 | 17.3287 | 21.372 | 24.4246 | 27.4747
GlencoeIce Accretion2065RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2065 | 13.6655 | 16.8324 | 20.8 | 23.788 | 26.7758
GlencoeIce Accretion2070RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2070 | 12.8815 | 15.962 | 19.8033 | 22.7009 | 25.5856
GlencoeIce Accretion2075RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2075 | 12.5378 | 15.588 | 19.3787 | 22.2505 | 25.0942
GlencoeIce Accretion2080RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2080 | 12.194 | 15.2139 | 18.954 | 21.8 | 24.6028
GlencoeIce Accretion2085RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2085 | 11.3618 | 14.2212 | 17.771 | 20.4485 | 23.1122
GlencoeIce Accretion2090RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2090 | 10.5295 | 13.2285 | 16.588 | 19.097 | 21.6216
GlencoeIce Accretion2095RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2095 | 10.5295 | 13.2285 | 16.588 | 19.097 | 21.6216
GlencoeIce Accretion2100RCP8.5 | Glencoe | Ice Accretion | RCP8.5 | 2100 | 10.5295 | 13.2285 | 16.588 | 19.097 | 21.6216
GlencoeWind2023RCP4.5 | Glencoe | Wind | RCP4.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
GlencoeWind2025RCP4.5 | Glencoe | Wind | RCP4.5 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
GlencoeWind2030RCP4.5 | Glencoe | Wind | RCP4.5 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
GlencoeWind2035RCP4.5 | Glencoe | Wind | RCP4.5 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
GlencoeWind2040RCP4.5 | Glencoe | Wind | RCP4.5 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
GlencoeWind2045RCP4.5 | Glencoe | Wind | RCP4.5 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
GlencoeWind2050RCP4.5 | Glencoe | Wind | RCP4.5 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
GlencoeWind2055RCP4.5 | Glencoe | Wind | RCP4.5 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
GlencoeWind2060RCP4.5 | Glencoe | Wind | RCP4.5 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
GlencoeWind2065RCP4.5 | Glencoe | Wind | RCP4.5 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
GlencoeWind2070RCP4.5 | Glencoe | Wind | RCP4.5 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
GlencoeWind2075RCP4.5 | Glencoe | Wind | RCP4.5 | 2075 | 85.7411 | 92.542 | 99.746 | 106.9048 | 114.0736
GlencoeWind2080RCP4.5 | Glencoe | Wind | RCP4.5 | 2080 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
GlencoeWind2085RCP4.5 | Glencoe | Wind | RCP4.5 | 2085 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
GlencoeWind2090RCP4.5 | Glencoe | Wind | RCP4.5 | 2090 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
GlencoeWind2095RCP4.5 | Glencoe | Wind | RCP4.5 | 2095 | 86.3278 | 93.3015 | 100.7326 | 108.0792 | 115.444
GlencoeWind2100RCP4.5 | Glencoe | Wind | RCP4.5 | 2100 | 86.4745 | 93.4914 | 100.9792 | 108.3728 | 115.7866
GlencoeWind2023RCP6.0 | Glencoe | Wind | RCP6.0 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
GlencoeWind2025RCP6.0 | Glencoe | Wind | RCP6.0 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
GlencoeWind2030RCP6.0 | Glencoe | Wind | RCP6.0 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
GlencoeWind2035RCP6.0 | Glencoe | Wind | RCP6.0 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
GlencoeWind2040RCP6.0 | Glencoe | Wind | RCP6.0 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
GlencoeWind2045RCP6.0 | Glencoe | Wind | RCP6.0 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
GlencoeWind2050RCP6.0 | Glencoe | Wind | RCP6.0 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
GlencoeWind2055RCP6.0 | Glencoe | Wind | RCP6.0 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
GlencoeWind2060RCP6.0 | Glencoe | Wind | RCP6.0 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
GlencoeWind2065RCP6.0 | Glencoe | Wind | RCP6.0 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
GlencoeWind2070RCP6.0 | Glencoe | Wind | RCP6.0 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
GlencoeWind2075RCP6.0 | Glencoe | Wind | RCP6.0 | 2075 | 85.8144 | 92.637 | 99.8693 | 107.0516 | 114.2449
GlencoeWind2080RCP6.0 | Glencoe | Wind | RCP6.0 | 2080 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
GlencoeWind2085RCP6.0 | Glencoe | Wind | RCP6.0 | 2085 | 86.2545 | 93.2066 | 100.6093 | 107.9324 | 115.2727
GlencoeWind2090RCP6.0 | Glencoe | Wind | RCP6.0 | 2090 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
GlencoeWind2095RCP6.0 | Glencoe | Wind | RCP6.0 | 2095 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
GlencoeWind2100RCP6.0 | Glencoe | Wind | RCP6.0 | 2100 | 87.5746 | 94.8494 | 102.6452 | 110.3127 | 117.9987
GlencoeWind2023RCP8.5 | Glencoe | Wind | RCP8.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
GlencoeWind2025RCP8.5 | Glencoe | Wind | RCP8.5 | 2025 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
GlencoeWind2030RCP8.5 | Glencoe | Wind | RCP8.5 | 2030 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
GlencoeWind2035RCP8.5 | Glencoe | Wind | RCP8.5 | 2035 | 85.586 | 92.3248 | 99.4504 | 106.5378 | 113.6304
GlencoeWind2040RCP8.5 | Glencoe | Wind | RCP8.5 | 2040 | 85.5888 | 92.3339 | 99.4667 | 106.5622 | 113.6639
GlencoeWind2045RCP8.5 | Glencoe | Wind | RCP8.5 | 2045 | 85.5916 | 92.343 | 99.4831 | 106.5867 | 113.6974
GlencoeWind2050RCP8.5 | Glencoe | Wind | RCP8.5 | 2050 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
GlencoeWind2055RCP8.5 | Glencoe | Wind | RCP8.5 | 2055 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
GlencoeWind2060RCP8.5 | Glencoe | Wind | RCP8.5 | 2060 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
GlencoeWind2065RCP8.5 | Glencoe | Wind | RCP8.5 | 2065 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
GlencoeWind2070RCP8.5 | Glencoe | Wind | RCP8.5 | 2070 | 87.882 | 95.2383 | 103.1385 | 110.8929 | 118.669
GlencoeWind2075RCP8.5 | Glencoe | Wind | RCP8.5 | 2075 | 88.1895 | 95.6271 | 103.6317 | 111.4732 | 119.3393
GlencoeWind2080RCP8.5 | Glencoe | Wind | RCP8.5 | 2080 | 88.4969 | 96.016 | 104.125 | 112.0534 | 120.0096
GlencoeWind2085RCP8.5 | Glencoe | Wind | RCP8.5 | 2085 | 88.8396 | 96.4489 | 104.664 | 112.6826 | 120.7358
GlencoeWind2090RCP8.5 | Glencoe | Wind | RCP8.5 | 2090 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
GlencoeWind2095RCP8.5 | Glencoe | Wind | RCP8.5 | 2095 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
GlencoeWind2100RCP8.5 | Glencoe | Wind | RCP8.5 | 2100 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
GoderichIce Accretion2023RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2023 | 13.8195 | 16.5834 | 20.08 | 22.7582 | 25.4268
GoderichIce Accretion2025RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2025 | 13.9076 | 16.6996 | 20.23 | 22.9315 | 25.6242
GoderichIce Accretion2030RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2030 | 13.9958 | 16.8158 | 20.38 | 23.1047 | 25.8216
GoderichIce Accretion2035RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2035 | 14.0839 | 16.932 | 20.53 | 23.278 | 26.019
GoderichIce Accretion2040RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2040 | 14.1721 | 17.0482 | 20.68 | 23.4513 | 26.2164
GoderichIce Accretion2045RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2045 | 14.2602 | 17.1644 | 20.83 | 23.6245 | 26.4138
GoderichIce Accretion2050RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2050 | 14.3539 | 17.3072 | 21.036 | 23.8746 | 26.707
GoderichIce Accretion2055RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2055 | 14.3595 | 17.3337 | 21.092 | 23.9515 | 26.8027
GoderichIce Accretion2060RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2060 | 14.365 | 17.3603 | 21.148 | 24.0283 | 26.8985
GoderichIce Accretion2065RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2065 | 14.3706 | 17.3868 | 21.204 | 24.1052 | 26.9942
GoderichIce Accretion2070RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2070 | 14.3762 | 17.4134 | 21.26 | 24.182 | 27.09
GoderichIce Accretion2075RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2075 | 14.2788 | 17.3138 | 21.1533 | 24.0728 | 26.9766
GoderichIce Accretion2080RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2080 | 14.1813 | 17.2142 | 21.0467 | 23.9635 | 26.8632
GoderichIce Accretion2085RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2085 | 14.0839 | 17.1146 | 20.94 | 23.8543 | 26.7498
GoderichIce Accretion2090RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2090 | 13.9865 | 17.015 | 20.8333 | 23.7451 | 26.6364
GoderichIce Accretion2095RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2095 | 13.8891 | 16.9154 | 20.7267 | 23.6358 | 26.523
GoderichIce Accretion2100RCP4.5 | Goderich | Ice Accretion | RCP4.5 | 2100 | 13.7917 | 16.8158 | 20.62 | 23.5266 | 26.4096
GoderichIce Accretion2023RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2023 | 13.8195 | 16.5834 | 20.08 | 22.7582 | 25.4268
GoderichIce Accretion2025RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2025 | 13.9076 | 16.6996 | 20.23 | 22.9315 | 25.6242
GoderichIce Accretion2030RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2030 | 13.9958 | 16.8158 | 20.38 | 23.1047 | 25.8216
GoderichIce Accretion2035RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2035 | 14.0839 | 16.932 | 20.53 | 23.278 | 26.019
GoderichIce Accretion2040RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2040 | 14.1721 | 17.0482 | 20.68 | 23.4513 | 26.2164
GoderichIce Accretion2045RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2045 | 14.2602 | 17.1644 | 20.83 | 23.6245 | 26.4138
GoderichIce Accretion2050RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2050 | 14.3539 | 17.3072 | 21.036 | 23.8746 | 26.707
GoderichIce Accretion2055RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2055 | 14.3595 | 17.3337 | 21.092 | 23.9515 | 26.8027
GoderichIce Accretion2060RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2060 | 14.365 | 17.3603 | 21.148 | 24.0283 | 26.8985
GoderichIce Accretion2065RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2065 | 14.3706 | 17.3868 | 21.204 | 24.1052 | 26.9942
GoderichIce Accretion2070RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2070 | 14.3762 | 17.4134 | 21.26 | 24.182 | 27.09
GoderichIce Accretion2075RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2075 | 14.2301 | 17.264 | 21.1 | 24.0181 | 26.9199
GoderichIce Accretion2080RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2080 | 14.0839 | 17.1146 | 20.94 | 23.8543 | 26.7498
GoderichIce Accretion2085RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2085 | 13.9378 | 16.9652 | 20.78 | 23.6904 | 26.5797
GoderichIce Accretion2090RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2090 | 13.4716 | 16.4617 | 20.22 | 23.0897 | 25.9308
GoderichIce Accretion2095RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2095 | 13.1515 | 16.1075 | 19.82 | 22.6527 | 25.452
GoderichIce Accretion2100RCP6.0 | Goderich | Ice Accretion | RCP6.0 | 2100 | 12.8314 | 15.7534 | 19.42 | 22.2158 | 24.9732
GoderichIce Accretion2023RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2023 | 13.8195 | 16.5834 | 20.08 | 22.7582 | 25.4268
GoderichIce Accretion2025RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2025 | 13.9958 | 16.8158 | 20.38 | 23.1047 | 25.8216
GoderichIce Accretion2030RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2030 | 14.1721 | 17.0482 | 20.68 | 23.4513 | 26.2164
GoderichIce Accretion2035RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2035 | 14.3483 | 17.2806 | 20.98 | 23.7978 | 26.6112
GoderichIce Accretion2040RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2040 | 14.3576 | 17.3249 | 21.0733 | 23.9259 | 26.7708
GoderichIce Accretion2045RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2045 | 14.3669 | 17.3691 | 21.1667 | 24.0539 | 26.9304
GoderichIce Accretion2050RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2050 | 14.1813 | 17.2142 | 21.0467 | 23.9635 | 26.8632
GoderichIce Accretion2055RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2055 | 13.9865 | 17.015 | 20.8333 | 23.7451 | 26.6364
GoderichIce Accretion2060RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2060 | 13.4716 | 16.4617 | 20.22 | 23.0897 | 25.9308
GoderichIce Accretion2065RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2065 | 13.1515 | 16.1075 | 19.82 | 22.6527 | 25.452
GoderichIce Accretion2070RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2070 | 12.4 | 15.2665 | 18.8667 | 21.5981 | 24.3096
GoderichIce Accretion2075RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2075 | 11.9686 | 14.7795 | 18.3133 | 20.9803 | 23.646
GoderichIce Accretion2080RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2080 | 11.5371 | 14.2926 | 17.76 | 20.3626 | 22.9824
GoderichIce Accretion2085RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2085 | 10.9665 | 13.6286 | 16.97 | 19.4925 | 22.0122
GoderichIce Accretion2090RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2090 | 10.3959 | 12.9646 | 16.18 | 18.6224 | 21.042
GoderichIce Accretion2095RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2095 | 10.3959 | 12.9646 | 16.18 | 18.6224 | 21.042
GoderichIce Accretion2100RCP8.5 | Goderich | Ice Accretion | RCP8.5 | 2100 | 10.3959 | 12.9646 | 16.18 | 18.6224 | 21.042
GoderichWind2023RCP4.5 | Goderich | Wind | RCP4.5 | 2023 | 86.1344 | 92.8894 | 100.0296 | 107.1482 | 114.2595
GoderichWind2025RCP4.5 | Goderich | Wind | RCP4.5 | 2025 | 86.2014 | 92.9754 | 100.1402 | 107.2788 | 114.4137
GoderichWind2030RCP4.5 | Goderich | Wind | RCP4.5 | 2030 | 86.2684 | 93.0613 | 100.2507 | 107.4095 | 114.5679
GoderichWind2035RCP4.5 | Goderich | Wind | RCP4.5 | 2035 | 86.3353 | 93.1472 | 100.3612 | 107.5401 | 114.7222
GoderichWind2040RCP4.5 | Goderich | Wind | RCP4.5 | 2040 | 86.4023 | 93.2332 | 100.4718 | 107.6708 | 114.8764
GoderichWind2045RCP4.5 | Goderich | Wind | RCP4.5 | 2045 | 86.4693 | 93.3191 | 100.5823 | 107.8014 | 115.0307
GoderichWind2050RCP4.5 | Goderich | Wind | RCP4.5 | 2050 | 86.5567 | 93.4271 | 100.7167 | 107.9575 | 115.212
GoderichWind2055RCP4.5 | Goderich | Wind | RCP4.5 | 2055 | 86.5773 | 93.4492 | 100.7404 | 107.9829 | 115.2391
GoderichWind2060RCP4.5 | Goderich | Wind | RCP4.5 | 2060 | 86.5978 | 93.4713 | 100.7642 | 108.0083 | 115.2662
GoderichWind2065RCP4.5 | Goderich | Wind | RCP4.5 | 2065 | 86.6183 | 93.4934 | 100.7879 | 108.0338 | 115.2933
GoderichWind2070RCP4.5 | Goderich | Wind | RCP4.5 | 2070 | 86.6388 | 93.5155 | 100.8117 | 108.0592 | 115.3203
GoderichWind2075RCP4.5 | Goderich | Wind | RCP4.5 | 2075 | 86.7542 | 93.6674 | 101.0097 | 108.2958 | 115.5969
GoderichWind2080RCP4.5 | Goderich | Wind | RCP4.5 | 2080 | 86.8696 | 93.8193 | 101.2077 | 108.5323 | 115.8734
GoderichWind2085RCP4.5 | Goderich | Wind | RCP4.5 | 2085 | 86.985 | 93.9712 | 101.4057 | 108.7689 | 116.1499
GoderichWind2090RCP4.5 | Goderich | Wind | RCP4.5 | 2090 | 87.1004 | 94.1232 | 101.6037 | 109.0055 | 116.4264
GoderichWind2095RCP4.5 | Goderich | Wind | RCP4.5 | 2095 | 87.2158 | 94.2751 | 101.8017 | 109.2421 | 116.7029
GoderichWind2100RCP4.5 | Goderich | Wind | RCP4.5 | 2100 | 87.3312 | 94.427 | 101.9997 | 109.4787 | 116.9794
GoderichWind2023RCP6.0 | Goderich | Wind | RCP6.0 | 2023 | 86.1344 | 92.8894 | 100.0296 | 107.1482 | 114.2595
GoderichWind2025RCP6.0 | Goderich | Wind | RCP6.0 | 2025 | 86.2014 | 92.9754 | 100.1402 | 107.2788 | 114.4137
GoderichWind2030RCP6.0 | Goderich | Wind | RCP6.0 | 2030 | 86.2684 | 93.0613 | 100.2507 | 107.4095 | 114.5679
GoderichWind2035RCP6.0 | Goderich | Wind | RCP6.0 | 2035 | 86.3353 | 93.1472 | 100.3612 | 107.5401 | 114.7222
GoderichWind2040RCP6.0 | Goderich | Wind | RCP6.0 | 2040 | 86.4023 | 93.2332 | 100.4718 | 107.6708 | 114.8764
GoderichWind2045RCP6.0 | Goderich | Wind | RCP6.0 | 2045 | 86.4693 | 93.3191 | 100.5823 | 107.8014 | 115.0307
GoderichWind2050RCP6.0 | Goderich | Wind | RCP6.0 | 2050 | 86.5567 | 93.4271 | 100.7167 | 107.9575 | 115.212
GoderichWind2055RCP6.0 | Goderich | Wind | RCP6.0 | 2055 | 86.5773 | 93.4492 | 100.7404 | 107.9829 | 115.2391
GoderichWind2060RCP6.0 | Goderich | Wind | RCP6.0 | 2060 | 86.5978 | 93.4713 | 100.7642 | 108.0083 | 115.2662
GoderichWind2065RCP6.0 | Goderich | Wind | RCP6.0 | 2065 | 86.6183 | 93.4934 | 100.7879 | 108.0338 | 115.2933
GoderichWind2070RCP6.0 | Goderich | Wind | RCP6.0 | 2070 | 86.6388 | 93.5155 | 100.8117 | 108.0592 | 115.3203
GoderichWind2075RCP6.0 | Goderich | Wind | RCP6.0 | 2075 | 86.8119 | 93.7434 | 101.1087 | 108.4141 | 115.7351
GoderichWind2080RCP6.0 | Goderich | Wind | RCP6.0 | 2080 | 86.985 | 93.9712 | 101.4057 | 108.7689 | 116.1499
GoderichWind2085RCP6.0 | Goderich | Wind | RCP6.0 | 2085 | 87.1581 | 94.1991 | 101.7027 | 109.1238 | 116.5646
GoderichWind2090RCP6.0 | Goderich | Wind | RCP6.0 | 2090 | 87.7729 | 94.9794 | 102.6861 | 110.2837 | 117.9011
GoderichWind2095RCP6.0 | Goderich | Wind | RCP6.0 | 2095 | 88.2146 | 95.5318 | 103.3725 | 111.0888 | 118.8228
GoderichWind2100RCP6.0 | Goderich | Wind | RCP6.0 | 2100 | 88.6562 | 96.0843 | 104.0589 | 111.8939 | 119.7445
GoderichWind2023RCP8.5 | Goderich | Wind | RCP8.5 | 2023 | 86.1344 | 92.8894 | 100.0296 | 107.1482 | 114.2595
GoderichWind2025RCP8.5 | Goderich | Wind | RCP8.5 | 2025 | 86.2684 | 93.0613 | 100.2507 | 107.4095 | 114.5679
GoderichWind2030RCP8.5 | Goderich | Wind | RCP8.5 | 2030 | 86.4023 | 93.2332 | 100.4718 | 107.6708 | 114.8764
GoderichWind2035RCP8.5 | Goderich | Wind | RCP8.5 | 2035 | 86.5362 | 93.405 | 100.6929 | 107.9321 | 115.1849
GoderichWind2040RCP8.5 | Goderich | Wind | RCP8.5 | 2040 | 86.5704 | 93.4418 | 100.7325 | 107.9744 | 115.2301
GoderichWind2045RCP8.5 | Goderich | Wind | RCP8.5 | 2045 | 86.6046 | 93.4787 | 100.7721 | 108.0168 | 115.2752
GoderichWind2050RCP8.5 | Goderich | Wind | RCP8.5 | 2050 | 86.8696 | 93.8193 | 101.2077 | 108.5323 | 115.8734
GoderichWind2055RCP8.5 | Goderich | Wind | RCP8.5 | 2055 | 87.1004 | 94.1232 | 101.6037 | 109.0055 | 116.4264
GoderichWind2060RCP8.5 | Goderich | Wind | RCP8.5 | 2060 | 87.7729 | 94.9794 | 102.6861 | 110.2837 | 117.9011
GoderichWind2065RCP8.5 | Goderich | Wind | RCP8.5 | 2065 | 88.2146 | 95.5318 | 103.3725 | 111.0888 | 118.8228
GoderichWind2070RCP8.5 | Goderich | Wind | RCP8.5 | 2070 | 88.8643 | 96.339 | 104.3757 | 112.2576 | 120.162
GoderichWind2075RCP8.5 | Goderich | Wind | RCP8.5 | 2075 | 89.0723 | 96.5937 | 104.6925 | 112.6212 | 120.5796
GoderichWind2080RCP8.5 | Goderich | Wind | RCP8.5 | 2080 | 89.2803 | 96.8484 | 105.0093 | 112.9849 | 120.9972
GoderichWind2085RCP8.5 | Goderich | Wind | RCP8.5 | 2085 | 89.4171 | 97.0003 | 105.1776 | 113.1703 | 121.2004
GoderichWind2090RCP8.5 | Goderich | Wind | RCP8.5 | 2090 | 89.5538 | 97.1523 | 105.3459 | 113.3557 | 121.4035
GoderichWind2095RCP8.5 | Goderich | Wind | RCP8.5 | 2095 | 89.5538 | 97.1523 | 105.3459 | 113.3557 | 121.4035
GoderichWind2100RCP8.5 | Goderich | Wind | RCP8.5 | 2100 | 89.5538 | 97.1523 | 105.3459 | 113.3557 | 121.4035
Gore BayIce Accretion2023RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2023 | 15.6454 | 18.7165 | 22.594 | 25.5809 | 28.5516
Gore BayIce Accretion2025RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2025 | 15.6148 | 18.6952 | 22.5793 | 25.5727 | 28.547
Gore BayIce Accretion2030RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2030 | 15.5842 | 18.6739 | 22.5647 | 25.5644 | 28.5424
Gore BayIce Accretion2035RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2035 | 15.5536 | 18.6526 | 22.55 | 25.5561 | 28.5377
Gore BayIce Accretion2040RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2040 | 15.5229 | 18.6313 | 22.5353 | 25.5478 | 28.5331
Gore BayIce Accretion2045RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2045 | 15.4923 | 18.61 | 22.5207 | 25.5395 | 28.5285
Gore BayIce Accretion2050RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2050 | 15.5842 | 18.7494 | 22.7172 | 25.7798 | 28.8122
Gore BayIce Accretion2055RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2055 | 15.7066 | 18.9101 | 22.9284 | 26.0284 | 29.1005
Gore BayIce Accretion2060RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2060 | 15.8291 | 19.0707 | 23.1396 | 26.277 | 29.3887
Gore BayIce Accretion2065RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2065 | 15.9516 | 19.2314 | 23.3508 | 26.5256 | 29.677
Gore BayIce Accretion2070RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2070 | 16.074 | 19.3921 | 23.562 | 26.7742 | 29.9653
Gore BayIce Accretion2075RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2075 | 15.972 | 19.2795 | 23.4447 | 26.6416 | 29.8267
Gore BayIce Accretion2080RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2080 | 15.8699 | 19.1669 | 23.3273 | 26.509 | 29.6881
Gore BayIce Accretion2085RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2085 | 15.7679 | 19.0543 | 23.21 | 26.3765 | 29.5495
Gore BayIce Accretion2090RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2090 | 15.6658 | 18.9417 | 23.0927 | 26.2439 | 29.4109
Gore BayIce Accretion2095RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2095 | 15.5638 | 18.8291 | 22.9753 | 26.1113 | 29.2723
Gore BayIce Accretion2100RCP4.5 | Gore Bay | Ice Accretion | RCP4.5 | 2100 | 15.4617 | 18.7165 | 22.858 | 25.9787 | 29.1337
Gore BayIce Accretion2023RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2023 | 15.6454 | 18.7165 | 22.594 | 25.5809 | 28.5516
Gore BayIce Accretion2025RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2025 | 15.6148 | 18.6952 | 22.5793 | 25.5727 | 28.547
Gore BayIce Accretion2030RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2030 | 15.5842 | 18.6739 | 22.5647 | 25.5644 | 28.5424
Gore BayIce Accretion2035RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2035 | 15.5536 | 18.6526 | 22.55 | 25.5561 | 28.5377
Gore BayIce Accretion2040RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2040 | 15.5229 | 18.6313 | 22.5353 | 25.5478 | 28.5331
Gore BayIce Accretion2045RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2045 | 15.4923 | 18.61 | 22.5207 | 25.5395 | 28.5285
Gore BayIce Accretion2050RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2050 | 15.5842 | 18.7494 | 22.7172 | 25.7798 | 28.8122
Gore BayIce Accretion2055RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2055 | 15.7066 | 18.9101 | 22.9284 | 26.0284 | 29.1005
Gore BayIce Accretion2060RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2060 | 15.8291 | 19.0707 | 23.1396 | 26.277 | 29.3887
Gore BayIce Accretion2065RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2065 | 15.9516 | 19.2314 | 23.3508 | 26.5256 | 29.677
Gore BayIce Accretion2070RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2070 | 16.074 | 19.3921 | 23.562 | 26.7742 | 29.9653
Gore BayIce Accretion2075RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2075 | 15.921 | 19.2232 | 23.386 | 26.5753 | 29.7574
Gore BayIce Accretion2080RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2080 | 15.7679 | 19.0543 | 23.21 | 26.3765 | 29.5495
Gore BayIce Accretion2085RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2085 | 15.6148 | 18.8854 | 23.034 | 26.1776 | 29.3416
Gore BayIce Accretion2090RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2090 | 15.5025 | 18.7835 | 22.9533 | 26.103 | 29.2723
Gore BayIce Accretion2095RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2095 | 15.5433 | 18.8504 | 23.0487 | 26.2273 | 29.4109
Gore BayIce Accretion2100RCP6.0 | Gore Bay | Ice Accretion | RCP6.0 | 2100 | 15.5842 | 18.9174 | 23.144 | 26.3516 | 29.5495
Gore BayIce Accretion2023RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2023 | 15.6454 | 18.7165 | 22.594 | 25.5809 | 28.5516
Gore BayIce Accretion2025RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2025 | 15.5842 | 18.6739 | 22.5647 | 25.5644 | 28.5424
Gore BayIce Accretion2030RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2030 | 15.5229 | 18.6313 | 22.5353 | 25.5478 | 28.5331
Gore BayIce Accretion2035RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2035 | 15.4617 | 18.5887 | 22.506 | 25.5312 | 28.5239
Gore BayIce Accretion2040RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2040 | 15.6658 | 18.8565 | 22.858 | 25.9456 | 29.0044
Gore BayIce Accretion2045RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2045 | 15.8699 | 19.1243 | 23.21 | 26.3599 | 29.4848
Gore BayIce Accretion2050RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2050 | 15.8699 | 19.1669 | 23.3273 | 26.509 | 29.6881
Gore BayIce Accretion2055RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2055 | 15.6658 | 18.9417 | 23.0927 | 26.2439 | 29.4109
Gore BayIce Accretion2060RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2060 | 15.5025 | 18.7835 | 22.9533 | 26.103 | 29.2723
Gore BayIce Accretion2065RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2065 | 15.5433 | 18.8504 | 23.0487 | 26.2273 | 29.4109
Gore BayIce Accretion2070RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2070 | 15.0586 | 18.3087 | 22.418 | 25.5395 | 28.6532
Gore BayIce Accretion2075RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2075 | 14.533 | 17.7 | 21.692 | 24.7274 | 27.757
Gore BayIce Accretion2080RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2080 | 14.0074 | 17.0914 | 20.966 | 23.9153 | 26.8607
Gore BayIce Accretion2085RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2085 | 13.7012 | 16.7535 | 20.592 | 23.5051 | 26.4172
Gore BayIce Accretion2090RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2090 | 13.395 | 16.4157 | 20.218 | 23.0949 | 25.9736
Gore BayIce Accretion2095RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2095 | 13.395 | 16.4157 | 20.218 | 23.0949 | 25.9736
Gore BayIce Accretion2100RCP8.5 | Gore Bay | Ice Accretion | RCP8.5 | 2100 | 13.395 | 16.4157 | 20.218 | 23.0949 | 25.9736
Gore BayWind2023RCP4.5 | Gore Bay | Wind | RCP4.5 | 2023 | 82.605 | 88.9773 | 95.684 | 102.4022 | 109.1014
Gore BayWind2025RCP4.5 | Gore Bay | Wind | RCP4.5 | 2025 | 82.7062 | 89.0966 | 95.8249 | 102.5598 | 109.2801
Gore BayWind2030RCP4.5 | Gore Bay | Wind | RCP4.5 | 2030 | 82.8074 | 89.2158 | 95.9658 | 102.7173 | 109.4588
Gore BayWind2035RCP4.5 | Gore Bay | Wind | RCP4.5 | 2035 | 82.9086 | 89.3351 | 96.1068 | 102.8749 | 109.6375
Gore BayWind2040RCP4.5 | Gore Bay | Wind | RCP4.5 | 2040 | 83.0097 | 89.4544 | 96.2477 | 103.0324 | 109.8162
Gore BayWind2045RCP4.5 | Gore Bay | Wind | RCP4.5 | 2045 | 83.1109 | 89.5736 | 96.3886 | 103.19 | 109.9949
Gore BayWind2050RCP4.5 | Gore Bay | Wind | RCP4.5 | 2050 | 83.281 | 89.7777 | 96.6321 | 103.4675 | 110.3079
Gore BayWind2055RCP4.5 | Gore Bay | Wind | RCP4.5 | 2055 | 83.3499 | 89.8626 | 96.7347 | 103.5874 | 110.4422
Gore BayWind2060RCP4.5 | Gore Bay | Wind | RCP4.5 | 2060 | 83.4188 | 89.9474 | 96.8373 | 103.7074 | 110.5765
Gore BayWind2065RCP4.5 | Gore Bay | Wind | RCP4.5 | 2065 | 83.4877 | 90.0322 | 96.9399 | 103.8273 | 110.7108
Gore BayWind2070RCP4.5 | Gore Bay | Wind | RCP4.5 | 2070 | 83.5566 | 90.117 | 97.0425 | 103.9473 | 110.8451
Gore BayWind2075RCP4.5 | Gore Bay | Wind | RCP4.5 | 2075 | 83.6072 | 90.1877 | 97.1391 | 104.0642 | 110.984
Gore BayWind2080RCP4.5 | Gore Bay | Wind | RCP4.5 | 2080 | 83.6578 | 90.2584 | 97.2357 | 104.1811 | 111.123
Gore BayWind2085RCP4.5 | Gore Bay | Wind | RCP4.5 | 2085 | 83.7084 | 90.329 | 97.3323 | 104.298 | 111.262
Gore BayWind2090RCP4.5 | Gore Bay | Wind | RCP4.5 | 2090 | 83.7589 | 90.3997 | 97.4288 | 104.4149 | 111.401
Gore BayWind2095RCP4.5 | Gore Bay | Wind | RCP4.5 | 2095 | 83.8095 | 90.4704 | 97.5254 | 104.5318 | 111.54
Gore BayWind2100RCP4.5 | Gore Bay | Wind | RCP4.5 | 2100 | 83.8601 | 90.5411 | 97.622 | 104.6487 | 111.679
Gore BayWind2023RCP6.0 | Gore Bay | Wind | RCP6.0 | 2023 | 82.605 | 88.9773 | 95.684 | 102.4022 | 109.1014
Gore BayWind2025RCP6.0 | Gore Bay | Wind | RCP6.0 | 2025 | 82.7062 | 89.0966 | 95.8249 | 102.5598 | 109.2801
Gore BayWind2030RCP6.0 | Gore Bay | Wind | RCP6.0 | 2030 | 82.8074 | 89.2158 | 95.9658 | 102.7173 | 109.4588
Gore BayWind2035RCP6.0 | Gore Bay | Wind | RCP6.0 | 2035 | 82.9086 | 89.3351 | 96.1068 | 102.8749 | 109.6375
Gore BayWind2040RCP6.0 | Gore Bay | Wind | RCP6.0 | 2040 | 83.0097 | 89.4544 | 96.2477 | 103.0324 | 109.8162
Gore BayWind2045RCP6.0 | Gore Bay | Wind | RCP6.0 | 2045 | 83.1109 | 89.5736 | 96.3886 | 103.19 | 109.9949
Gore BayWind2050RCP6.0 | Gore Bay | Wind | RCP6.0 | 2050 | 83.281 | 89.7777 | 96.6321 | 103.4675 | 110.3079
Gore BayWind2055RCP6.0 | Gore Bay | Wind | RCP6.0 | 2055 | 83.3499 | 89.8626 | 96.7347 | 103.5874 | 110.4422
Gore BayWind2060RCP6.0 | Gore Bay | Wind | RCP6.0 | 2060 | 83.4188 | 89.9474 | 96.8373 | 103.7074 | 110.5765
Gore BayWind2065RCP6.0 | Gore Bay | Wind | RCP6.0 | 2065 | 83.4877 | 90.0322 | 96.9399 | 103.8273 | 110.7108
Gore BayWind2070RCP6.0 | Gore Bay | Wind | RCP6.0 | 2070 | 83.5566 | 90.117 | 97.0425 | 103.9473 | 110.8451
Gore BayWind2075RCP6.0 | Gore Bay | Wind | RCP6.0 | 2075 | 83.6325 | 90.223 | 97.1874 | 104.1226 | 111.0535
Gore BayWind2080RCP6.0 | Gore Bay | Wind | RCP6.0 | 2080 | 83.7084 | 90.329 | 97.3323 | 104.298 | 111.262
Gore BayWind2085RCP6.0 | Gore Bay | Wind | RCP6.0 | 2085 | 83.7842 | 90.4351 | 97.4771 | 104.4733 | 111.4705
Gore BayWind2090RCP6.0 | Gore Bay | Wind | RCP6.0 | 2090 | 84.0652 | 90.8032 | 97.9577 | 105.0451 | 112.141
Gore BayWind2095RCP6.0 | Gore Bay | Wind | RCP6.0 | 2095 | 84.2703 | 91.0653 | 98.2933 | 105.4415 | 112.6031
Gore BayWind2100RCP6.0 | Gore Bay | Wind | RCP6.0 | 2100 | 84.4753 | 91.3274 | 98.629 | 105.838 | 113.0652
Gore BayWind2023RCP8.5 | Gore Bay | Wind | RCP8.5 | 2023 | 82.605 | 88.9773 | 95.684 | 102.4022 | 109.1014
Gore BayWind2025RCP8.5 | Gore Bay | Wind | RCP8.5 | 2025 | 82.8074 | 89.2158 | 95.9658 | 102.7173 | 109.4588
Gore BayWind2030RCP8.5 | Gore Bay | Wind | RCP8.5 | 2030 | 83.0097 | 89.4544 | 96.2477 | 103.0324 | 109.8162
Gore BayWind2035RCP8.5 | Gore Bay | Wind | RCP8.5 | 2035 | 83.2121 | 89.6929 | 96.5295 | 103.3476 | 110.1736
Gore BayWind2040RCP8.5 | Gore Bay | Wind | RCP8.5 | 2040 | 83.3269 | 89.8343 | 96.7005 | 103.5475 | 110.3974
Gore BayWind2045RCP8.5 | Gore Bay | Wind | RCP8.5 | 2045 | 83.4418 | 89.9756 | 96.8715 | 103.7474 | 110.6212
Gore BayWind2050RCP8.5 | Gore Bay | Wind | RCP8.5 | 2050 | 83.6578 | 90.2584 | 97.2357 | 104.1811 | 111.123
Gore BayWind2055RCP8.5 | Gore Bay | Wind | RCP8.5 | 2055 | 83.7589 | 90.3997 | 97.4288 | 104.4149 | 111.401
Gore BayWind2060RCP8.5 | Gore Bay | Wind | RCP8.5 | 2060 | 84.0652 | 90.8032 | 97.9577 | 105.0451 | 112.141
Gore BayWind2065RCP8.5 | Gore Bay | Wind | RCP8.5 | 2065 | 84.2703 | 91.0653 | 98.2933 | 105.4415 | 112.6031
Gore BayWind2070RCP8.5 | Gore Bay | Wind | RCP8.5 | 2070 | 84.7324 | 91.6572 | 99.0438 | 106.3259 | 113.6284
Gore BayWind2075RCP8.5 | Gore Bay | Wind | RCP8.5 | 2075 | 84.9894 | 91.9871 | 99.4587 | 106.8138 | 114.1915
Gore BayWind2080RCP8.5 | Gore Bay | Wind | RCP8.5 | 2080 | 85.2464 | 92.3169 | 99.8735 | 107.3017 | 114.7547
Gore BayWind2085RCP8.5 | Gore Bay | Wind | RCP8.5 | 2085 | 85.5664 | 92.7233 | 100.3912 | 107.9116 | 115.4586
Gore BayWind2090RCP8.5 | Gore Bay | Wind | RCP8.5 | 2090 | 85.8863 | 93.1297 | 100.909 | 108.5215 | 116.1626
Gore BayWind2095RCP8.5 | Gore Bay | Wind | RCP8.5 | 2095 | 85.8863 | 93.1297 | 100.909 | 108.5215 | 116.1626
Gore BayWind2100RCP8.5 | Gore Bay | Wind | RCP8.5 | 2100 | 85.8863 | 93.1297 | 100.909 | 108.5215 | 116.1626
GrahamIce Accretion2023RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2023 | 10.6464 | 12.7114 | 15.33 | 17.3229 | 19.3347
GrahamIce Accretion2025RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2025 | 10.7195 | 12.8007 | 15.44 | 17.45 | 19.4764
GrahamIce Accretion2030RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2030 | 10.7926 | 12.8899 | 15.55 | 17.5771 | 19.6182
GrahamIce Accretion2035RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2035 | 10.8656 | 12.9791 | 15.66 | 17.7043 | 19.7599
GrahamIce Accretion2040RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2040 | 10.9387 | 13.0683 | 15.77 | 17.8314 | 19.9017
GrahamIce Accretion2045RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2045 | 11.0118 | 13.1576 | 15.88 | 17.9585 | 20.0434
GrahamIce Accretion2050RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2050 | 11.0473 | 13.1945 | 15.918 | 18.0009 | 20.0869
GrahamIce Accretion2055RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2055 | 11.0097 | 13.1422 | 15.846 | 17.9161 | 19.9886
GrahamIce Accretion2060RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2060 | 10.9721 | 13.0899 | 15.774 | 17.8314 | 19.8904
GrahamIce Accretion2065RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2065 | 10.9345 | 13.0376 | 15.702 | 17.7466 | 19.7921
GrahamIce Accretion2070RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2070 | 10.897 | 12.9853 | 15.63 | 17.6619 | 19.6938
GrahamIce Accretion2075RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2075 | 10.9561 | 13.058 | 15.72 | 17.7636 | 19.8072
GrahamIce Accretion2080RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2080 | 11.0152 | 13.1306 | 15.81 | 17.8653 | 19.9206
GrahamIce Accretion2085RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2085 | 11.0744 | 13.2032 | 15.9 | 17.967 | 20.034
GrahamIce Accretion2090RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2090 | 11.1335 | 13.2759 | 15.99 | 18.0687 | 20.1474
GrahamIce Accretion2095RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2095 | 11.1927 | 13.3485 | 16.08 | 18.1704 | 20.2608
GrahamIce Accretion2100RCP4.5 | Graham | Ice Accretion | RCP4.5 | 2100 | 11.2518 | 13.4211 | 16.17 | 18.2721 | 20.3742
GrahamIce Accretion2023RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2023 | 10.6464 | 12.7114 | 15.33 | 17.3229 | 19.3347
GrahamIce Accretion2025RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2025 | 10.7195 | 12.8007 | 15.44 | 17.45 | 19.4764
GrahamIce Accretion2030RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2030 | 10.7926 | 12.8899 | 15.55 | 17.5771 | 19.6182
GrahamIce Accretion2035RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2035 | 10.8656 | 12.9791 | 15.66 | 17.7043 | 19.7599
GrahamIce Accretion2040RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2040 | 10.9387 | 13.0683 | 15.77 | 17.8314 | 19.9017
GrahamIce Accretion2045RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2045 | 11.0118 | 13.1576 | 15.88 | 17.9585 | 20.0434
GrahamIce Accretion2050RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2050 | 11.0473 | 13.1945 | 15.918 | 18.0009 | 20.0869
GrahamIce Accretion2055RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2055 | 11.0097 | 13.1422 | 15.846 | 17.9161 | 19.9886
GrahamIce Accretion2060RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2060 | 10.9721 | 13.0899 | 15.774 | 17.8314 | 19.8904
GrahamIce Accretion2065RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2065 | 10.9345 | 13.0376 | 15.702 | 17.7466 | 19.7921
GrahamIce Accretion2070RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2070 | 10.897 | 12.9853 | 15.63 | 17.6619 | 19.6938
GrahamIce Accretion2075RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2075 | 10.9857 | 13.0943 | 15.765 | 17.8145 | 19.8639
GrahamIce Accretion2080RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2080 | 11.0744 | 13.2032 | 15.9 | 17.967 | 20.034
GrahamIce Accretion2085RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2085 | 11.1631 | 13.3122 | 16.035 | 18.1196 | 20.2041
GrahamIce Accretion2090RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2090 | 11.1857 | 13.3422 | 16.075 | 18.1648 | 20.2545
GrahamIce Accretion2095RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2095 | 11.1196 | 13.2634 | 15.98 | 18.0574 | 20.1348
GrahamIce Accretion2100RCP6.0 | Graham | Ice Accretion | RCP6.0 | 2100 | 11.0535 | 13.1845 | 15.885 | 17.95 | 20.0151
GrahamIce Accretion2023RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2023 | 10.6464 | 12.7114 | 15.33 | 17.3229 | 19.3347
GrahamIce Accretion2025RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2025 | 10.7926 | 12.8899 | 15.55 | 17.5771 | 19.6182
GrahamIce Accretion2030RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2030 | 10.9387 | 13.0683 | 15.77 | 17.8314 | 19.9017
GrahamIce Accretion2035RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2035 | 11.0848 | 13.2468 | 15.99 | 18.0856 | 20.1852
GrahamIce Accretion2040RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2040 | 11.0222 | 13.1596 | 15.87 | 17.9444 | 20.0214
GrahamIce Accretion2045RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2045 | 10.9596 | 13.0725 | 15.75 | 17.8031 | 19.8576
GrahamIce Accretion2050RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2050 | 11.0152 | 13.1306 | 15.81 | 17.8653 | 19.9206
GrahamIce Accretion2055RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2055 | 11.1335 | 13.2759 | 15.99 | 18.0687 | 20.1474
GrahamIce Accretion2060RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2060 | 11.1857 | 13.3422 | 16.075 | 18.1648 | 20.2545
GrahamIce Accretion2065RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2065 | 11.1196 | 13.2634 | 15.98 | 18.0574 | 20.1348
GrahamIce Accretion2070RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2070 | 11.0779 | 13.226 | 15.95 | 18.0291 | 20.1096
GrahamIce Accretion2075RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2075 | 11.1022 | 13.2675 | 16.015 | 18.1082 | 20.2041
GrahamIce Accretion2080RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2080 | 11.1266 | 13.309 | 16.08 | 18.1873 | 20.2986
GrahamIce Accretion2085RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2085 | 10.85 | 12.9916 | 15.705 | 17.7721 | 19.845
GrahamIce Accretion2090RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2090 | 10.5734 | 12.6741 | 15.33 | 17.3568 | 19.3914
GrahamIce Accretion2095RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2095 | 10.5734 | 12.6741 | 15.33 | 17.3568 | 19.3914
GrahamIce Accretion2100RCP8.5 | Graham | Ice Accretion | RCP8.5 | 2100 | 10.5734 | 12.6741 | 15.33 | 17.3568 | 19.3914
GrahamWind2023RCP4.5 | Graham | Wind | RCP4.5 | 2023 | 72.6486 | 78.2841 | 84.2184 | 90.1496 | 96.076
GrahamWind2025RCP4.5 | Graham | Wind | RCP4.5 | 2025 | 72.7163 | 78.3622 | 84.3122 | 90.2545 | 96.1941
GrahamWind2030RCP4.5 | Graham | Wind | RCP4.5 | 2030 | 72.784 | 78.4403 | 84.406 | 90.3594 | 96.3122
GrahamWind2035RCP4.5 | Graham | Wind | RCP4.5 | 2035 | 72.8517 | 78.5184 | 84.4998 | 90.4642 | 96.4303
GrahamWind2040RCP4.5 | Graham | Wind | RCP4.5 | 2040 | 72.9194 | 78.5965 | 84.5936 | 90.5691 | 96.5484
GrahamWind2045RCP4.5 | Graham | Wind | RCP4.5 | 2045 | 72.9871 | 78.6747 | 84.6874 | 90.6739 | 96.6665
GrahamWind2050RCP4.5 | Graham | Wind | RCP4.5 | 2050 | 73.1041 | 78.82 | 84.8669 | 90.8831 | 96.9072
GrahamWind2055RCP4.5 | Graham | Wind | RCP4.5 | 2055 | 73.1534 | 78.8871 | 84.9526 | 90.9873 | 97.0298
GrahamWind2060RCP4.5 | Graham | Wind | RCP4.5 | 2060 | 73.2027 | 78.9543 | 85.0382 | 91.0916 | 97.1524
GrahamWind2065RCP4.5 | Graham | Wind | RCP4.5 | 2065 | 73.252 | 79.0215 | 85.1239 | 91.1958 | 97.2749
GrahamWind2070RCP4.5 | Graham | Wind | RCP4.5 | 2070 | 73.3014 | 79.0887 | 85.2096 | 91.3001 | 97.3975
GrahamWind2075RCP4.5 | Graham | Wind | RCP4.5 | 2075 | 73.3981 | 79.2033 | 85.3454 | 91.4544 | 97.5699
GrahamWind2080RCP4.5 | Graham | Wind | RCP4.5 | 2080 | 73.4948 | 79.3178 | 85.4812 | 91.6087 | 97.7422
GrahamWind2085RCP4.5 | Graham | Wind | RCP4.5 | 2085 | 73.5915 | 79.4324 | 85.617 | 91.763 | 97.9146
GrahamWind2090RCP4.5 | Graham | Wind | RCP4.5 | 2090 | 73.6882 | 79.547 | 85.7528 | 91.9173 | 98.087
GrahamWind2095RCP4.5 | Graham | Wind | RCP4.5 | 2095 | 73.7849 | 79.6616 | 85.8886 | 92.0716 | 98.2593
GrahamWind2100RCP4.5 | Graham | Wind | RCP4.5 | 2100 | 73.8816 | 79.7761 | 86.0244 | 92.2259 | 98.4317
GrahamWind2023RCP6.0 | Graham | Wind | RCP6.0 | 2023 | 72.6486 | 78.2841 | 84.2184 | 90.1496 | 96.076
GrahamWind2025RCP6.0 | Graham | Wind | RCP6.0 | 2025 | 72.7163 | 78.3622 | 84.3122 | 90.2545 | 96.1941
GrahamWind2030RCP6.0 | Graham | Wind | RCP6.0 | 2030 | 72.784 | 78.4403 | 84.406 | 90.3594 | 96.3122
GrahamWind2035RCP6.0 | Graham | Wind | RCP6.0 | 2035 | 72.8517 | 78.5184 | 84.4998 | 90.4642 | 96.4303
GrahamWind2040RCP6.0 | Graham | Wind | RCP6.0 | 2040 | 72.9194 | 78.5965 | 84.5936 | 90.5691 | 96.5484
GrahamWind2045RCP6.0 | Graham | Wind | RCP6.0 | 2045 | 72.9871 | 78.6747 | 84.6874 | 90.6739 | 96.6665
GrahamWind2050RCP6.0 | Graham | Wind | RCP6.0 | 2050 | 73.1041 | 78.82 | 84.8669 | 90.8831 | 96.9072
GrahamWind2055RCP6.0 | Graham | Wind | RCP6.0 | 2055 | 73.1534 | 78.8871 | 84.9526 | 90.9873 | 97.0298
GrahamWind2060RCP6.0 | Graham | Wind | RCP6.0 | 2060 | 73.2027 | 78.9543 | 85.0382 | 91.0916 | 97.1524
GrahamWind2065RCP6.0 | Graham | Wind | RCP6.0 | 2065 | 73.252 | 79.0215 | 85.1239 | 91.1958 | 97.2749
GrahamWind2070RCP6.0 | Graham | Wind | RCP6.0 | 2070 | 73.3014 | 79.0887 | 85.2096 | 91.3001 | 97.3975
GrahamWind2075RCP6.0 | Graham | Wind | RCP6.0 | 2075 | 73.4464 | 79.2606 | 85.4133 | 91.5315 | 97.656
GrahamWind2080RCP6.0 | Graham | Wind | RCP6.0 | 2080 | 73.5915 | 79.4324 | 85.617 | 91.763 | 97.9146
GrahamWind2085RCP6.0 | Graham | Wind | RCP6.0 | 2085 | 73.7366 | 79.6043 | 85.8207 | 91.9944 | 98.1732
GrahamWind2090RCP6.0 | Graham | Wind | RCP6.0 | 2090 | 73.9783 | 79.9089 | 86.2064 | 92.4476 | 98.6934
GrahamWind2095RCP6.0 | Graham | Wind | RCP6.0 | 2095 | 74.075 | 80.0418 | 86.3884 | 92.6693 | 98.9552
GrahamWind2100RCP6.0 | Graham | Wind | RCP6.0 | 2100 | 74.1718 | 80.1746 | 86.5704 | 92.891 | 99.2169
GrahamWind2023RCP8.5 | Graham | Wind | RCP8.5 | 2023 | 72.6486 | 78.2841 | 84.2184 | 90.1496 | 96.076
GrahamWind2025RCP8.5 | Graham | Wind | RCP8.5 | 2025 | 72.784 | 78.4403 | 84.406 | 90.3594 | 96.3122
GrahamWind2030RCP8.5 | Graham | Wind | RCP8.5 | 2030 | 72.9194 | 78.5965 | 84.5936 | 90.5691 | 96.5484
GrahamWind2035RCP8.5 | Graham | Wind | RCP8.5 | 2035 | 73.0548 | 78.7528 | 84.7812 | 90.7788 | 96.7846
GrahamWind2040RCP8.5 | Graham | Wind | RCP8.5 | 2040 | 73.137 | 78.8647 | 84.924 | 90.9526 | 96.9889
GrahamWind2045RCP8.5 | Graham | Wind | RCP8.5 | 2045 | 73.2192 | 78.9767 | 85.0668 | 91.1263 | 97.1932
GrahamWind2050RCP8.5 | Graham | Wind | RCP8.5 | 2050 | 73.4948 | 79.3178 | 85.4812 | 91.6087 | 97.7422
GrahamWind2055RCP8.5 | Graham | Wind | RCP8.5 | 2055 | 73.6882 | 79.547 | 85.7528 | 91.9173 | 98.087
GrahamWind2060RCP8.5 | Graham | Wind | RCP8.5 | 2060 | 73.9783 | 79.9089 | 86.2064 | 92.4476 | 98.6934
GrahamWind2065RCP8.5 | Graham | Wind | RCP8.5 | 2065 | 74.075 | 80.0418 | 86.3884 | 92.6693 | 98.9552
GrahamWind2070RCP8.5 | Graham | Wind | RCP8.5 | 2070 | 74.3942 | 80.4324 | 86.87 | 93.2295 | 99.5936
GrahamWind2075RCP8.5 | Graham | Wind | RCP8.5 | 2075 | 74.6166 | 80.6901 | 87.1696 | 93.5681 | 99.9702
GrahamWind2080RCP8.5 | Graham | Wind | RCP8.5 | 2080 | 74.8391 | 80.9479 | 87.4692 | 93.9066 | 100.3469
GrahamWind2085RCP8.5 | Graham | Wind | RCP8.5 | 2085 | 74.8282 | 80.905 | 87.3894 | 93.7943 | 100.2081
GrahamWind2090RCP8.5 | Graham | Wind | RCP8.5 | 2090 | 74.8173 | 80.862 | 87.3096 | 93.6819 | 100.0692
GrahamWind2095RCP8.5 | Graham | Wind | RCP8.5 | 2095 | 74.8173 | 80.862 | 87.3096 | 93.6819 | 100.0692
GrahamWind2100RCP8.5 | Graham | Wind | RCP8.5 | 2100 | 74.8173 | 80.862 | 87.3096 | 93.6819 | 100.0692
Gravenhurst (Muskoka Airport)Ice Accretion2023RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2023 | 14.3351 | 17.0988 | 20.601 | 23.2791 | 25.9837
Gravenhurst (Muskoka Airport)Ice Accretion2025RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2025 | 14.3181 | 17.0872 | 20.594 | 23.2791 | 25.9837
Gravenhurst (Muskoka Airport)Ice Accretion2030RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2030 | 14.301 | 17.0756 | 20.587 | 23.2791 | 25.9837
Gravenhurst (Muskoka Airport)Ice Accretion2035RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2035 | 14.284 | 17.064 | 20.58 | 23.2791 | 25.9837
Gravenhurst (Muskoka Airport)Ice Accretion2040RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2040 | 14.2669 | 17.0524 | 20.573 | 23.2791 | 25.9837
Gravenhurst (Muskoka Airport)Ice Accretion2045RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2045 | 14.2499 | 17.0407 | 20.566 | 23.2791 | 25.9837
Gravenhurst (Muskoka Airport)Ice Accretion2050RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2050 | 14.2299 | 17.0396 | 20.5926 | 23.3218 | 26.0419
Gravenhurst (Muskoka Airport)Ice Accretion2055RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2055 | 14.227 | 17.05 | 20.6262 | 23.3646 | 26.1001
Gravenhurst (Muskoka Airport)Ice Accretion2060RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2060 | 14.2241 | 17.0605 | 20.6598 | 23.4073 | 26.1584
Gravenhurst (Muskoka Airport)Ice Accretion2065RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2065 | 14.2211 | 17.0709 | 20.6934 | 23.45 | 26.2166
Gravenhurst (Muskoka Airport)Ice Accretion2070RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2070 | 14.2182 | 17.0814 | 20.727 | 23.4927 | 26.2748
Gravenhurst (Muskoka Airport)Ice Accretion2075RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2075 | 14.2596 | 17.1482 | 20.8215 | 23.6074 | 26.4115
Gravenhurst (Muskoka Airport)Ice Accretion2080RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2080 | 14.301 | 17.215 | 20.916 | 23.7221 | 26.5482
Gravenhurst (Muskoka Airport)Ice Accretion2085RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2085 | 14.3424 | 17.2818 | 21.0105 | 23.8368 | 26.6849
Gravenhurst (Muskoka Airport)Ice Accretion2090RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2090 | 14.3838 | 17.3487 | 21.105 | 23.9515 | 26.8216
Gravenhurst (Muskoka Airport)Ice Accretion2095RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2095 | 14.4252 | 17.4155 | 21.1995 | 24.0662 | 26.9583
Gravenhurst (Muskoka Airport)Ice Accretion2100RCP4.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP4.5 | 2100 | 14.4666 | 17.4823 | 21.294 | 24.1809 | 27.095
Gravenhurst (Muskoka Airport)Ice Accretion2023RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2023 | 14.3351 | 17.0988 | 20.601 | 23.2791 | 25.9837
Gravenhurst (Muskoka Airport)Ice Accretion2025RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2025 | 14.3181 | 17.0872 | 20.594 | 23.2791 | 25.9837
Gravenhurst (Muskoka Airport)Ice Accretion2030RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2030 | 14.301 | 17.0756 | 20.587 | 23.2791 | 25.9837
Gravenhurst (Muskoka Airport)Ice Accretion2035RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2035 | 14.284 | 17.064 | 20.58 | 23.2791 | 25.9837
Gravenhurst (Muskoka Airport)Ice Accretion2040RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2040 | 14.2669 | 17.0524 | 20.573 | 23.2791 | 25.9837
Gravenhurst (Muskoka Airport)Ice Accretion2045RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2045 | 14.2499 | 17.0407 | 20.566 | 23.2791 | 25.9837
Gravenhurst (Muskoka Airport)Ice Accretion2050RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2050 | 14.2299 | 17.0396 | 20.5926 | 23.3218 | 26.0419
Gravenhurst (Muskoka Airport)Ice Accretion2055RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2055 | 14.227 | 17.05 | 20.6262 | 23.3646 | 26.1001
Gravenhurst (Muskoka Airport)Ice Accretion2060RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2060 | 14.2241 | 17.0605 | 20.6598 | 23.4073 | 26.1584
Gravenhurst (Muskoka Airport)Ice Accretion2065RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2065 | 14.2211 | 17.0709 | 20.6934 | 23.45 | 26.2166
Gravenhurst (Muskoka Airport)Ice Accretion2070RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2070 | 14.2182 | 17.0814 | 20.727 | 23.4927 | 26.2748
Gravenhurst (Muskoka Airport)Ice Accretion2075RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2075 | 14.2803 | 17.1816 | 20.8687 | 23.6647 | 26.4798
Gravenhurst (Muskoka Airport)Ice Accretion2080RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2080 | 14.3424 | 17.2818 | 21.0105 | 23.8368 | 26.6849
Gravenhurst (Muskoka Airport)Ice Accretion2085RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2085 | 14.4045 | 17.3821 | 21.1523 | 24.0088 | 26.89
Gravenhurst (Muskoka Airport)Ice Accretion2090RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2090 | 14.4423 | 17.4939 | 21.35 | 24.2758 | 27.2185
Gravenhurst (Muskoka Airport)Ice Accretion2095RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2095 | 14.4179 | 17.5055 | 21.406 | 24.3707 | 27.342
Gravenhurst (Muskoka Airport)Ice Accretion2100RCP6.0 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP6.0 | 2100 | 14.3936 | 17.5171 | 21.462 | 24.4656 | 27.4655
Gravenhurst (Muskoka Airport)Ice Accretion2023RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2023 | 14.3351 | 17.0988 | 20.601 | 23.2791 | 25.9837
Gravenhurst (Muskoka Airport)Ice Accretion2025RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2025 | 14.301 | 17.0756 | 20.587 | 23.2791 | 25.9837
Gravenhurst (Muskoka Airport)Ice Accretion2030RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2030 | 14.2669 | 17.0524 | 20.573 | 23.2791 | 25.9837
Gravenhurst (Muskoka Airport)Ice Accretion2035RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2035 | 14.2328 | 17.0291 | 20.559 | 23.2791 | 25.9837
Gravenhurst (Muskoka Airport)Ice Accretion2040RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2040 | 14.228 | 17.0465 | 20.615 | 23.3503 | 26.0807
Gravenhurst (Muskoka Airport)Ice Accretion2045RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2045 | 14.2231 | 17.064 | 20.671 | 23.4215 | 26.1778
Gravenhurst (Muskoka Airport)Ice Accretion2050RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2050 | 14.301 | 17.215 | 20.916 | 23.7221 | 26.5482
Gravenhurst (Muskoka Airport)Ice Accretion2055RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2055 | 14.3838 | 17.3487 | 21.105 | 23.9515 | 26.8216
Gravenhurst (Muskoka Airport)Ice Accretion2060RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2060 | 14.4423 | 17.4939 | 21.35 | 24.2758 | 27.2185
Gravenhurst (Muskoka Airport)Ice Accretion2065RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2065 | 14.4179 | 17.5055 | 21.406 | 24.3707 | 27.342
Gravenhurst (Muskoka Airport)Ice Accretion2070RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2070 | 14.1305 | 17.2383 | 21.161 | 24.1413 | 27.1215
Gravenhurst (Muskoka Airport)Ice Accretion2075RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2075 | 13.8675 | 16.9594 | 20.86 | 23.817 | 26.7775
Gravenhurst (Muskoka Airport)Ice Accretion2080RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2080 | 13.6045 | 16.6805 | 20.559 | 23.4927 | 26.4335
Gravenhurst (Muskoka Airport)Ice Accretion2085RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2085 | 13.0565 | 16.0617 | 19.845 | 22.7096 | 25.5736
Gravenhurst (Muskoka Airport)Ice Accretion2090RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2090 | 12.5085 | 15.443 | 19.131 | 21.9265 | 24.7136
Gravenhurst (Muskoka Airport)Ice Accretion2095RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2095 | 12.5085 | 15.443 | 19.131 | 21.9265 | 24.7136
Gravenhurst (Muskoka Airport)Ice Accretion2100RCP8.5 | Gravenhurst (Muskoka Airport) | Ice Accretion | RCP8.5 | 2100 | 12.5085 | 15.443 | 19.131 | 21.9265 | 24.7136
Gravenhurst (Muskoka Airport)Wind2023RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2023 | 77.3418 | 83.3328 | 89.6497 | 95.9537 | 102.2615
Gravenhurst (Muskoka Airport)Wind2025RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2025 | 77.4212 | 83.428 | 89.7624 | 96.0823 | 102.4053
Gravenhurst (Muskoka Airport)Wind2030RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2030 | 77.5006 | 83.5232 | 89.8752 | 96.2109 | 102.549
Gravenhurst (Muskoka Airport)Wind2035RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2035 | 77.58 | 83.6184 | 89.9879 | 96.3394 | 102.6927
Gravenhurst (Muskoka Airport)Wind2040RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2040 | 77.6594 | 83.7136 | 90.1006 | 96.468 | 102.8365
Gravenhurst (Muskoka Airport)Wind2045RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2045 | 77.7388 | 83.8088 | 90.2134 | 96.5966 | 102.9802
Gravenhurst (Muskoka Airport)Wind2050RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2050 | 77.9289 | 84.0364 | 90.4863 | 96.9099 | 103.335
Gravenhurst (Muskoka Airport)Wind2055RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2055 | 78.0396 | 84.1688 | 90.6465 | 97.0946 | 103.546
Gravenhurst (Muskoka Airport)Wind2060RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2060 | 78.1502 | 84.3012 | 90.8067 | 97.2793 | 103.7571
Gravenhurst (Muskoka Airport)Wind2065RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2065 | 78.2609 | 84.4337 | 90.9669 | 97.4641 | 103.9681
Gravenhurst (Muskoka Airport)Wind2070RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2070 | 78.3716 | 84.5661 | 91.1271 | 97.6488 | 104.1791
Gravenhurst (Muskoka Airport)Wind2075RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2075 | 78.4061 | 84.6158 | 91.1968 | 97.7345 | 104.2806
Gravenhurst (Muskoka Airport)Wind2080RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2080 | 78.4407 | 84.6654 | 91.2665 | 97.8203 | 104.382
Gravenhurst (Muskoka Airport)Wind2085RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2085 | 78.4753 | 84.7151 | 91.3363 | 97.906 | 104.4835
Gravenhurst (Muskoka Airport)Wind2090RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2090 | 78.5099 | 84.7648 | 91.406 | 97.9917 | 104.585
Gravenhurst (Muskoka Airport)Wind2095RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2095 | 78.5445 | 84.8144 | 91.4757 | 98.0774 | 104.6864
Gravenhurst (Muskoka Airport)Wind2100RCP4.5 | Gravenhurst (Muskoka Airport) | Wind | RCP4.5 | 2100 | 78.5791 | 84.8641 | 91.5454 | 98.1631 | 104.7879
Gravenhurst (Muskoka Airport)Wind2023RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2023 | 77.3418 | 83.3328 | 89.6497 | 95.9537 | 102.2615
Gravenhurst (Muskoka Airport)Wind2025RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2025 | 77.4212 | 83.428 | 89.7624 | 96.0823 | 102.4053
Gravenhurst (Muskoka Airport)Wind2030RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2030 | 77.5006 | 83.5232 | 89.8752 | 96.2109 | 102.549
Gravenhurst (Muskoka Airport)Wind2035RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2035 | 77.58 | 83.6184 | 89.9879 | 96.3394 | 102.6927
Gravenhurst (Muskoka Airport)Wind2040RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2040 | 77.6594 | 83.7136 | 90.1006 | 96.468 | 102.8365
Gravenhurst (Muskoka Airport)Wind2045RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2045 | 77.7388 | 83.8088 | 90.2134 | 96.5966 | 102.9802
Gravenhurst (Muskoka Airport)Wind2050RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2050 | 77.9289 | 84.0364 | 90.4863 | 96.9099 | 103.335
Gravenhurst (Muskoka Airport)Wind2055RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2055 | 78.0396 | 84.1688 | 90.6465 | 97.0946 | 103.546
Gravenhurst (Muskoka Airport)Wind2060RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2060 | 78.1502 | 84.3012 | 90.8067 | 97.2793 | 103.7571
Gravenhurst (Muskoka Airport)Wind2065RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2065 | 78.2609 | 84.4337 | 90.9669 | 97.4641 | 103.9681
Gravenhurst (Muskoka Airport)Wind2070RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2070 | 78.3716 | 84.5661 | 91.1271 | 97.6488 | 104.1791
Gravenhurst (Muskoka Airport)Wind2075RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2075 | 78.4234 | 84.6406 | 91.2317 | 97.7774 | 104.3313
Gravenhurst (Muskoka Airport)Wind2080RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2080 | 78.4753 | 84.7151 | 91.3363 | 97.906 | 104.4835
Gravenhurst (Muskoka Airport)Wind2085RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2085 | 78.5272 | 84.7896 | 91.4408 | 98.0345 | 104.6357
Gravenhurst (Muskoka Airport)Wind2090RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2090 | 78.6943 | 85.0186 | 91.7442 | 98.4012 | 105.0652
Gravenhurst (Muskoka Airport)Wind2095RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2095 | 78.8096 | 85.1731 | 91.9429 | 98.6392 | 105.3425
Gravenhurst (Muskoka Airport)Wind2100RCP6.0 | Gravenhurst (Muskoka Airport) | Wind | RCP6.0 | 2100 | 78.9249 | 85.3276 | 92.1417 | 98.8773 | 105.6199
Gravenhurst (Muskoka Airport)Wind2023RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2023 | 77.3418 | 83.3328 | 89.6497 | 95.9537 | 102.2615
Gravenhurst (Muskoka Airport)Wind2025RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2025 | 77.5006 | 83.5232 | 89.8752 | 96.2109 | 102.549
Gravenhurst (Muskoka Airport)Wind2030RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2030 | 77.6594 | 83.7136 | 90.1006 | 96.468 | 102.8365
Gravenhurst (Muskoka Airport)Wind2035RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2035 | 77.8182 | 83.9039 | 90.3261 | 96.7251 | 103.1239
Gravenhurst (Muskoka Airport)Wind2040RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2040 | 78.0027 | 84.1247 | 90.5931 | 97.033 | 103.4757
Gravenhurst (Muskoka Airport)Wind2045RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2045 | 78.1871 | 84.3454 | 90.8601 | 97.3409 | 103.8274
Gravenhurst (Muskoka Airport)Wind2050RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2050 | 78.4407 | 84.6654 | 91.2665 | 97.8203 | 104.382
Gravenhurst (Muskoka Airport)Wind2055RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2055 | 78.5099 | 84.7648 | 91.406 | 97.9917 | 104.585
Gravenhurst (Muskoka Airport)Wind2060RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2060 | 78.6943 | 85.0186 | 91.7442 | 98.4012 | 105.0652
Gravenhurst (Muskoka Airport)Wind2065RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2065 | 78.8096 | 85.1731 | 91.9429 | 98.6392 | 105.3425
Gravenhurst (Muskoka Airport)Wind2070RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2070 | 78.9121 | 85.3221 | 92.1476 | 98.89 | 105.6435
Gravenhurst (Muskoka Airport)Wind2075RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2075 | 78.8993 | 85.3166 | 92.1536 | 98.9027 | 105.6672
Gravenhurst (Muskoka Airport)Wind2080RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2080 | 78.8865 | 85.311 | 92.1595 | 98.9154 | 105.6909
Gravenhurst (Muskoka Airport)Wind2085RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2085 | 78.9864 | 85.4393 | 92.3286 | 99.1154 | 105.9242
Gravenhurst (Muskoka Airport)Wind2090RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2090 | 79.0863 | 85.5676 | 92.4977 | 99.3154 | 106.1576
Gravenhurst (Muskoka Airport)Wind2095RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2095 | 79.0863 | 85.5676 | 92.4977 | 99.3154 | 106.1576
Gravenhurst (Muskoka Airport)Wind2100RCP8.5 | Gravenhurst (Muskoka Airport) | Wind | RCP8.5 | 2100 | 79.0863 | 85.5676 | 92.4977 | 99.3154 | 106.1576
GrimsbyIce Accretion2023RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2023 | 20.6458 | 24.7755 | 30 | 34.0017 | 37.989
GrimsbyIce Accretion2025RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2025 | 20.5483 | 24.6676 | 29.885 | 33.8717 | 37.8504
GrimsbyIce Accretion2030RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2030 | 20.4509 | 24.5597 | 29.77 | 33.7418 | 37.7118
GrimsbyIce Accretion2035RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2035 | 20.3535 | 24.4518 | 29.655 | 33.6118 | 37.5732
GrimsbyIce Accretion2040RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2040 | 20.2561 | 24.3439 | 29.54 | 33.4819 | 37.4346
GrimsbyIce Accretion2045RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2045 | 20.1587 | 24.236 | 29.425 | 33.352 | 37.296
GrimsbyIce Accretion2050RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2050 | 19.6145 | 23.6251 | 28.722 | 32.5711 | 36.4468
GrimsbyIce Accretion2055RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2055 | 19.1678 | 23.1221 | 28.134 | 31.9202 | 35.7361
GrimsbyIce Accretion2060RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2060 | 18.721 | 22.6192 | 27.546 | 31.2694 | 35.0255
GrimsbyIce Accretion2065RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2065 | 18.2743 | 22.1162 | 26.958 | 30.6185 | 34.3148
GrimsbyIce Accretion2070RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2070 | 17.8276 | 21.6132 | 26.37 | 29.9676 | 33.6042
GrimsbyIce Accretion2075RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2075 | 17.6606 | 21.4389 | 26.185 | 29.7755 | 33.4026
GrimsbyIce Accretion2080RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2080 | 17.4936 | 21.2646 | 26 | 29.5834 | 33.201
GrimsbyIce Accretion2085RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2085 | 17.3266 | 21.0903 | 25.815 | 29.3913 | 32.9994
GrimsbyIce Accretion2090RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2090 | 17.1596 | 20.916 | 25.63 | 29.1992 | 32.7978
GrimsbyIce Accretion2095RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2095 | 16.9926 | 20.7417 | 25.445 | 29.0071 | 32.5962
GrimsbyIce Accretion2100RCP4.5 | Grimsby | Ice Accretion | RCP4.5 | 2100 | 16.8256 | 20.5674 | 25.26 | 28.815 | 32.3946
GrimsbyIce Accretion2023RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2023 | 20.6458 | 24.7755 | 30 | 34.0017 | 37.989
GrimsbyIce Accretion2025RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2025 | 20.5483 | 24.6676 | 29.885 | 33.8717 | 37.8504
GrimsbyIce Accretion2030RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2030 | 20.4509 | 24.5597 | 29.77 | 33.7418 | 37.7118
GrimsbyIce Accretion2035RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2035 | 20.3535 | 24.4518 | 29.655 | 33.6118 | 37.5732
GrimsbyIce Accretion2040RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2040 | 20.2561 | 24.3439 | 29.54 | 33.4819 | 37.4346
GrimsbyIce Accretion2045RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2045 | 20.1587 | 24.236 | 29.425 | 33.352 | 37.296
GrimsbyIce Accretion2050RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2050 | 19.6145 | 23.6251 | 28.722 | 32.5711 | 36.4468
GrimsbyIce Accretion2055RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2055 | 19.1678 | 23.1221 | 28.134 | 31.9202 | 35.7361
GrimsbyIce Accretion2060RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2060 | 18.721 | 22.6192 | 27.546 | 31.2694 | 35.0255
GrimsbyIce Accretion2065RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2065 | 18.2743 | 22.1162 | 26.958 | 30.6185 | 34.3148
GrimsbyIce Accretion2070RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2070 | 17.8276 | 21.6132 | 26.37 | 29.9676 | 33.6042
GrimsbyIce Accretion2075RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2075 | 17.5771 | 21.3517 | 26.0925 | 29.6794 | 33.3018
GrimsbyIce Accretion2080RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2080 | 17.3266 | 21.0903 | 25.815 | 29.3913 | 32.9994
GrimsbyIce Accretion2085RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2085 | 17.0761 | 20.8288 | 25.5375 | 29.1031 | 32.697
GrimsbyIce Accretion2090RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2090 | 16.1436 | 19.7872 | 24.35 | 27.8093 | 31.2732
GrimsbyIce Accretion2095RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2095 | 15.4617 | 19.007 | 23.44 | 26.8036 | 30.1518
GrimsbyIce Accretion2100RCP6.0 | Grimsby | Ice Accretion | RCP6.0 | 2100 | 14.7798 | 18.2268 | 22.53 | 25.7979 | 29.0304
GrimsbyIce Accretion2023RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2023 | 20.6458 | 24.7755 | 30 | 34.0017 | 37.989
GrimsbyIce Accretion2025RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2025 | 20.4509 | 24.5597 | 29.77 | 33.7418 | 37.7118
GrimsbyIce Accretion2030RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2030 | 20.2561 | 24.3439 | 29.54 | 33.4819 | 37.4346
GrimsbyIce Accretion2035RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2035 | 20.0612 | 24.1281 | 29.31 | 33.222 | 37.1574
GrimsbyIce Accretion2040RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2040 | 19.3167 | 23.2898 | 28.33 | 32.1372 | 35.973
GrimsbyIce Accretion2045RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2045 | 18.5721 | 22.4515 | 27.35 | 31.0524 | 34.7886
GrimsbyIce Accretion2050RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2050 | 17.4936 | 21.2646 | 26 | 29.5834 | 33.201
GrimsbyIce Accretion2055RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2055 | 17.1596 | 20.916 | 25.63 | 29.1992 | 32.7978
GrimsbyIce Accretion2060RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2060 | 16.1436 | 19.7872 | 24.35 | 27.8093 | 31.2732
GrimsbyIce Accretion2065RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2065 | 15.4617 | 19.007 | 23.44 | 26.8036 | 30.1518
GrimsbyIce Accretion2070RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2070 | 14.4388 | 17.8367 | 22.09 | 25.312 | 28.5012
GrimsbyIce Accretion2075RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2075 | 14.0978 | 17.4466 | 21.65 | 24.8261 | 27.972
GrimsbyIce Accretion2080RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2080 | 13.7569 | 17.0565 | 21.21 | 24.3402 | 27.4428
GrimsbyIce Accretion2085RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2085 | 12.9845 | 16.1476 | 20.115 | 23.1029 | 26.0631
GrimsbyIce Accretion2090RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2090 | 12.2121 | 15.2388 | 19.02 | 21.8655 | 24.6834
GrimsbyIce Accretion2095RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2095 | 12.2121 | 15.2388 | 19.02 | 21.8655 | 24.6834
GrimsbyIce Accretion2100RCP8.5 | Grimsby | Ice Accretion | RCP8.5 | 2100 | 12.2121 | 15.2388 | 19.02 | 21.8655 | 24.6834
GrimsbyWind2023RCP4.5 | Grimsby | Wind | RCP4.5 | 2023 | 87.2376 | 94.1811 | 101.55 | 108.8725 | 116.1888
GrimsbyWind2025RCP4.5 | Grimsby | Wind | RCP4.5 | 2025 | 87.2088 | 94.1517 | 101.5183 | 108.8386 | 116.1527
GrimsbyWind2030RCP4.5 | Grimsby | Wind | RCP4.5 | 2030 | 87.1801 | 94.1222 | 101.4867 | 108.8047 | 116.1166
GrimsbyWind2035RCP4.5 | Grimsby | Wind | RCP4.5 | 2035 | 87.1513 | 94.0927 | 101.455 | 108.7708 | 116.0805
GrimsbyWind2040RCP4.5 | Grimsby | Wind | RCP4.5 | 2040 | 87.1225 | 94.0633 | 101.4233 | 108.737 | 116.0444
GrimsbyWind2045RCP4.5 | Grimsby | Wind | RCP4.5 | 2045 | 87.0937 | 94.0338 | 101.3917 | 108.7031 | 116.0083
GrimsbyWind2050RCP4.5 | Grimsby | Wind | RCP4.5 | 2050 | 87.1219 | 94.0769 | 101.454 | 108.7783 | 116.0999
GrimsbyWind2055RCP4.5 | Grimsby | Wind | RCP4.5 | 2055 | 87.1789 | 94.1495 | 101.548 | 108.8875 | 116.2276
GrimsbyWind2060RCP4.5 | Grimsby | Wind | RCP4.5 | 2060 | 87.2359 | 94.222 | 101.642 | 108.9966 | 116.3552
GrimsbyWind2065RCP4.5 | Grimsby | Wind | RCP4.5 | 2065 | 87.2929 | 94.2946 | 101.736 | 109.1058 | 116.4829
GrimsbyWind2070RCP4.5 | Grimsby | Wind | RCP4.5 | 2070 | 87.3499 | 94.3671 | 101.83 | 109.2149 | 116.6106
GrimsbyWind2075RCP4.5 | Grimsby | Wind | RCP4.5 | 2075 | 87.4305 | 94.4802 | 101.985 | 109.4039 | 116.8367
GrimsbyWind2080RCP4.5 | Grimsby | Wind | RCP4.5 | 2080 | 87.5111 | 94.5934 | 102.14 | 109.593 | 117.0628
GrimsbyWind2085RCP4.5 | Grimsby | Wind | RCP4.5 | 2085 | 87.5917 | 94.7065 | 102.295 | 109.782 | 117.2889
GrimsbyWind2090RCP4.5 | Grimsby | Wind | RCP4.5 | 2090 | 87.6722 | 94.8197 | 102.45 | 109.971 | 117.515
GrimsbyWind2095RCP4.5 | Grimsby | Wind | RCP4.5 | 2095 | 87.7528 | 94.9329 | 102.605 | 110.1601 | 117.7411
GrimsbyWind2100RCP4.5 | Grimsby | Wind | RCP4.5 | 2100 | 87.8334 | 95.046 | 102.76 | 110.3491 | 117.9672
GrimsbyWind2023RCP6.0 | Grimsby | Wind | RCP6.0 | 2023 | 87.2376 | 94.1811 | 101.55 | 108.8725 | 116.1888
GrimsbyWind2025RCP6.0 | Grimsby | Wind | RCP6.0 | 2025 | 87.2088 | 94.1517 | 101.5183 | 108.8386 | 116.1527
GrimsbyWind2030RCP6.0 | Grimsby | Wind | RCP6.0 | 2030 | 87.1801 | 94.1222 | 101.4867 | 108.8047 | 116.1166
GrimsbyWind2035RCP6.0 | Grimsby | Wind | RCP6.0 | 2035 | 87.1513 | 94.0927 | 101.455 | 108.7708 | 116.0805
GrimsbyWind2040RCP6.0 | Grimsby | Wind | RCP6.0 | 2040 | 87.1225 | 94.0633 | 101.4233 | 108.737 | 116.0444
GrimsbyWind2045RCP6.0 | Grimsby | Wind | RCP6.0 | 2045 | 87.0937 | 94.0338 | 101.3917 | 108.7031 | 116.0083
GrimsbyWind2050RCP6.0 | Grimsby | Wind | RCP6.0 | 2050 | 87.1219 | 94.0769 | 101.454 | 108.7783 | 116.0999
GrimsbyWind2055RCP6.0 | Grimsby | Wind | RCP6.0 | 2055 | 87.1789 | 94.1495 | 101.548 | 108.8875 | 116.2276
GrimsbyWind2060RCP6.0 | Grimsby | Wind | RCP6.0 | 2060 | 87.2359 | 94.222 | 101.642 | 108.9966 | 116.3552
GrimsbyWind2065RCP6.0 | Grimsby | Wind | RCP6.0 | 2065 | 87.2929 | 94.2946 | 101.736 | 109.1058 | 116.4829
GrimsbyWind2070RCP6.0 | Grimsby | Wind | RCP6.0 | 2070 | 87.3499 | 94.3671 | 101.83 | 109.2149 | 116.6106
GrimsbyWind2075RCP6.0 | Grimsby | Wind | RCP6.0 | 2075 | 87.4708 | 94.5368 | 102.0625 | 109.4985 | 116.9497
GrimsbyWind2080RCP6.0 | Grimsby | Wind | RCP6.0 | 2080 | 87.5917 | 94.7065 | 102.295 | 109.782 | 117.2889
GrimsbyWind2085RCP6.0 | Grimsby | Wind | RCP6.0 | 2085 | 87.7125 | 94.8763 | 102.5275 | 110.0656 | 117.628
GrimsbyWind2090RCP6.0 | Grimsby | Wind | RCP6.0 | 2090 | 88.0176 | 95.2816 | 103.0567 | 110.7022 | 118.3776
GrimsbyWind2095RCP6.0 | Grimsby | Wind | RCP6.0 | 2095 | 88.2019 | 95.5172 | 103.3533 | 111.0553 | 118.788
GrimsbyWind2100RCP6.0 | Grimsby | Wind | RCP6.0 | 2100 | 88.3861 | 95.7528 | 103.65 | 111.4084 | 119.1984
GrimsbyWind2023RCP8.5 | Grimsby | Wind | RCP8.5 | 2023 | 87.2376 | 94.1811 | 101.55 | 108.8725 | 116.1888
GrimsbyWind2025RCP8.5 | Grimsby | Wind | RCP8.5 | 2025 | 87.1801 | 94.1222 | 101.4867 | 108.8047 | 116.1166
GrimsbyWind2030RCP8.5 | Grimsby | Wind | RCP8.5 | 2030 | 87.1225 | 94.0633 | 101.4233 | 108.737 | 116.0444
GrimsbyWind2035RCP8.5 | Grimsby | Wind | RCP8.5 | 2035 | 87.0649 | 94.0044 | 101.36 | 108.6692 | 115.9722
GrimsbyWind2040RCP8.5 | Grimsby | Wind | RCP8.5 | 2040 | 87.1599 | 94.1253 | 101.5167 | 108.8511 | 116.185
GrimsbyWind2045RCP8.5 | Grimsby | Wind | RCP8.5 | 2045 | 87.2549 | 94.2462 | 101.6733 | 109.033 | 116.3978
GrimsbyWind2050RCP8.5 | Grimsby | Wind | RCP8.5 | 2050 | 87.5111 | 94.5934 | 102.14 | 109.593 | 117.0628
GrimsbyWind2055RCP8.5 | Grimsby | Wind | RCP8.5 | 2055 | 87.6722 | 94.8197 | 102.45 | 109.971 | 117.515
GrimsbyWind2060RCP8.5 | Grimsby | Wind | RCP8.5 | 2060 | 88.0176 | 95.2816 | 103.0567 | 110.7022 | 118.3776
GrimsbyWind2065RCP8.5 | Grimsby | Wind | RCP8.5 | 2065 | 88.2019 | 95.5172 | 103.3533 | 111.0553 | 118.788
GrimsbyWind2070RCP8.5 | Grimsby | Wind | RCP8.5 | 2070 | 88.4465 | 95.8551 | 103.8133 | 111.6224 | 119.4568
GrimsbyWind2075RCP8.5 | Grimsby | Wind | RCP8.5 | 2075 | 88.5069 | 95.9574 | 103.9767 | 111.8364 | 119.7152
GrimsbyWind2080RCP8.5 | Grimsby | Wind | RCP8.5 | 2080 | 88.5674 | 96.0597 | 104.14 | 112.0504 | 119.9736
GrimsbyWind2085RCP8.5 | Grimsby | Wind | RCP8.5 | 2085 | 88.6322 | 96.1666 | 104.295 | 112.243 | 120.213
GrimsbyWind2090RCP8.5 | Grimsby | Wind | RCP8.5 | 2090 | 88.6969 | 96.2736 | 104.45 | 112.4356 | 120.4524
GrimsbyWind2095RCP8.5 | Grimsby | Wind | RCP8.5 | 2095 | 88.6969 | 96.2736 | 104.45 | 112.4356 | 120.4524
GrimsbyWind2100RCP8.5 | Grimsby | Wind | RCP8.5 | 2100 | 88.6969 | 96.2736 | 104.45 | 112.4356 | 120.4524
GuelphIce Accretion2023RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
GuelphIce Accretion2025RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2025 | 17.3208 | 20.7984 | 25.1958 | 28.5655 | 31.92
GuelphIce Accretion2030RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2030 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
GuelphIce Accretion2035RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2035 | 17.3788 | 20.8953 | 25.3375 | 28.7444 | 32.13
GuelphIce Accretion2040RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2040 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
GuelphIce Accretion2045RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2045 | 17.4367 | 20.9921 | 25.4792 | 28.9233 | 32.34
GuelphIce Accretion2050RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2050 | 17.4101 | 20.9907 | 25.51 | 28.9788 | 32.4198
GuelphIce Accretion2055RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2055 | 17.3544 | 20.9409 | 25.47 | 28.9449 | 32.3946
GuelphIce Accretion2060RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2060 | 17.2987 | 20.8911 | 25.43 | 28.911 | 32.3694
GuelphIce Accretion2065RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2065 | 17.2431 | 20.8413 | 25.39 | 28.8771 | 32.3442
GuelphIce Accretion2070RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2070 | 17.1874 | 20.7915 | 25.35 | 28.8432 | 32.319
GuelphIce Accretion2075RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2075 | 17.1555 | 20.7846 | 25.3708 | 28.8809 | 32.3768
GuelphIce Accretion2080RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2080 | 17.1236 | 20.7777 | 25.3917 | 28.9186 | 32.4345
GuelphIce Accretion2085RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2085 | 17.0917 | 20.7707 | 25.4125 | 28.9562 | 32.4922
GuelphIce Accretion2090RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2090 | 17.0598 | 20.7638 | 25.4333 | 28.9939 | 32.55
GuelphIce Accretion2095RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2095 | 17.0279 | 20.7569 | 25.4542 | 29.0316 | 32.6077
GuelphIce Accretion2100RCP4.5 | Guelph | Ice Accretion | RCP4.5 | 2100 | 16.996 | 20.75 | 25.475 | 29.0692 | 32.6655
GuelphIce Accretion2023RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
GuelphIce Accretion2025RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2025 | 17.3208 | 20.7984 | 25.1958 | 28.5655 | 31.92
GuelphIce Accretion2030RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2030 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
GuelphIce Accretion2035RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2035 | 17.3788 | 20.8953 | 25.3375 | 28.7444 | 32.13
GuelphIce Accretion2040RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2040 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
GuelphIce Accretion2045RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2045 | 17.4367 | 20.9921 | 25.4792 | 28.9233 | 32.34
GuelphIce Accretion2050RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2050 | 17.4101 | 20.9907 | 25.51 | 28.9788 | 32.4198
GuelphIce Accretion2055RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2055 | 17.3544 | 20.9409 | 25.47 | 28.9449 | 32.3946
GuelphIce Accretion2060RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2060 | 17.2987 | 20.8911 | 25.43 | 28.911 | 32.3694
GuelphIce Accretion2065RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2065 | 17.2431 | 20.8413 | 25.39 | 28.8771 | 32.3442
GuelphIce Accretion2070RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2070 | 17.1874 | 20.7915 | 25.35 | 28.8432 | 32.319
GuelphIce Accretion2075RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2075 | 17.1396 | 20.7811 | 25.3813 | 28.8997 | 32.4056
GuelphIce Accretion2080RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2080 | 17.0917 | 20.7707 | 25.4125 | 28.9562 | 32.4922
GuelphIce Accretion2085RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2085 | 17.0439 | 20.7604 | 25.4437 | 29.0127 | 32.5789
GuelphIce Accretion2090RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2090 | 16.6887 | 20.4249 | 25.1333 | 28.7114 | 32.298
GuelphIce Accretion2095RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2095 | 16.3814 | 20.0998 | 24.7917 | 28.3536 | 31.9305
GuelphIce Accretion2100RCP6.0 | Guelph | Ice Accretion | RCP6.0 | 2100 | 16.074 | 19.7747 | 24.45 | 27.9957 | 31.563
GuelphIce Accretion2023RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
GuelphIce Accretion2025RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2025 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
GuelphIce Accretion2030RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2030 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
GuelphIce Accretion2035RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2035 | 17.4657 | 21.0405 | 25.55 | 29.0127 | 32.445
GuelphIce Accretion2040RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2040 | 17.373 | 20.9575 | 25.4833 | 28.9562 | 32.403
GuelphIce Accretion2045RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2045 | 17.2802 | 20.8745 | 25.4167 | 28.8997 | 32.361
GuelphIce Accretion2050RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2050 | 17.1236 | 20.7777 | 25.3917 | 28.9186 | 32.4345
GuelphIce Accretion2055RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2055 | 17.0598 | 20.7638 | 25.4333 | 28.9939 | 32.55
GuelphIce Accretion2060RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2060 | 16.6887 | 20.4249 | 25.1333 | 28.7114 | 32.298
GuelphIce Accretion2065RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2065 | 16.3814 | 20.0998 | 24.7917 | 28.3536 | 31.9305
GuelphIce Accretion2070RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2070 | 15.6507 | 19.3182 | 23.95 | 27.4684 | 30.9855
GuelphIce Accretion2075RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2075 | 15.2274 | 18.8617 | 23.45 | 26.9411 | 30.408
GuelphIce Accretion2080RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2080 | 14.8041 | 18.4052 | 22.95 | 26.4137 | 29.8305
GuelphIce Accretion2085RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2085 | 13.9778 | 17.43 | 21.7875 | 25.086 | 28.3657
GuelphIce Accretion2090RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2090 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
GuelphIce Accretion2095RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2095 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
GuelphIce Accretion2100RCP8.5 | Guelph | Ice Accretion | RCP8.5 | 2100 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
GuelphWind2023RCP4.5 | Guelph | Wind | RCP4.5 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
GuelphWind2025RCP4.5 | Guelph | Wind | RCP4.5 | 2025 | 81.5488 | 87.8469 | 94.481 | 101.1097 | 107.7494
GuelphWind2030RCP4.5 | Guelph | Wind | RCP4.5 | 2030 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
GuelphWind2035RCP4.5 | Guelph | Wind | RCP4.5 | 2035 | 81.6625 | 88.0013 | 94.6909 | 101.3645 | 108.0494
GuelphWind2040RCP4.5 | Guelph | Wind | RCP4.5 | 2040 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
GuelphWind2045RCP4.5 | Guelph | Wind | RCP4.5 | 2045 | 81.7761 | 88.1558 | 94.9008 | 101.6193 | 108.3495
GuelphWind2050RCP4.5 | Guelph | Wind | RCP4.5 | 2050 | 81.8962 | 88.3099 | 95.096 | 101.8513 | 108.6174
GuelphWind2055RCP4.5 | Guelph | Wind | RCP4.5 | 2055 | 81.9595 | 88.3869 | 95.1863 | 101.9559 | 108.7353
GuelphWind2060RCP4.5 | Guelph | Wind | RCP4.5 | 2060 | 82.0229 | 88.4638 | 95.2765 | 102.0605 | 108.8531
GuelphWind2065RCP4.5 | Guelph | Wind | RCP4.5 | 2065 | 82.0862 | 88.5407 | 95.3668 | 102.1651 | 108.971
GuelphWind2070RCP4.5 | Guelph | Wind | RCP4.5 | 2070 | 82.1495 | 88.6177 | 95.457 | 102.2697 | 109.0889
GuelphWind2075RCP4.5 | Guelph | Wind | RCP4.5 | 2075 | 82.2185 | 88.7167 | 95.598 | 102.4424 | 109.2961
GuelphWind2080RCP4.5 | Guelph | Wind | RCP4.5 | 2080 | 82.2875 | 88.8158 | 95.739 | 102.6151 | 109.5032
GuelphWind2085RCP4.5 | Guelph | Wind | RCP4.5 | 2085 | 82.3564 | 88.9149 | 95.88 | 102.7877 | 109.7104
GuelphWind2090RCP4.5 | Guelph | Wind | RCP4.5 | 2090 | 82.4254 | 89.014 | 96.021 | 102.9604 | 109.9176
GuelphWind2095RCP4.5 | Guelph | Wind | RCP4.5 | 2095 | 82.4944 | 89.113 | 96.162 | 103.1331 | 110.1248
GuelphWind2100RCP4.5 | Guelph | Wind | RCP4.5 | 2100 | 82.5634 | 89.2121 | 96.303 | 103.3057 | 110.3319
GuelphWind2023RCP6.0 | Guelph | Wind | RCP6.0 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
GuelphWind2025RCP6.0 | Guelph | Wind | RCP6.0 | 2025 | 81.5488 | 87.8469 | 94.481 | 101.1097 | 107.7494
GuelphWind2030RCP6.0 | Guelph | Wind | RCP6.0 | 2030 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
GuelphWind2035RCP6.0 | Guelph | Wind | RCP6.0 | 2035 | 81.6625 | 88.0013 | 94.6909 | 101.3645 | 108.0494
GuelphWind2040RCP6.0 | Guelph | Wind | RCP6.0 | 2040 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
GuelphWind2045RCP6.0 | Guelph | Wind | RCP6.0 | 2045 | 81.7761 | 88.1558 | 94.9008 | 101.6193 | 108.3495
GuelphWind2050RCP6.0 | Guelph | Wind | RCP6.0 | 2050 | 81.8962 | 88.3099 | 95.096 | 101.8513 | 108.6174
GuelphWind2055RCP6.0 | Guelph | Wind | RCP6.0 | 2055 | 81.9595 | 88.3869 | 95.1863 | 101.9559 | 108.7353
GuelphWind2060RCP6.0 | Guelph | Wind | RCP6.0 | 2060 | 82.0229 | 88.4638 | 95.2765 | 102.0605 | 108.8531
GuelphWind2065RCP6.0 | Guelph | Wind | RCP6.0 | 2065 | 82.0862 | 88.5407 | 95.3668 | 102.1651 | 108.971
GuelphWind2070RCP6.0 | Guelph | Wind | RCP6.0 | 2070 | 82.1495 | 88.6177 | 95.457 | 102.2697 | 109.0889
GuelphWind2075RCP6.0 | Guelph | Wind | RCP6.0 | 2075 | 82.253 | 88.7663 | 95.6685 | 102.5287 | 109.3996
GuelphWind2080RCP6.0 | Guelph | Wind | RCP6.0 | 2080 | 82.3564 | 88.9149 | 95.88 | 102.7877 | 109.7104
GuelphWind2085RCP6.0 | Guelph | Wind | RCP6.0 | 2085 | 82.4599 | 89.0635 | 96.0915 | 103.0467 | 110.0212
GuelphWind2090RCP6.0 | Guelph | Wind | RCP6.0 | 2090 | 82.8421 | 89.5618 | 96.7385 | 103.8187 | 110.9213
GuelphWind2095RCP6.0 | Guelph | Wind | RCP6.0 | 2095 | 83.1208 | 89.9115 | 97.1741 | 104.3316 | 111.5107
GuelphWind2100RCP6.0 | Guelph | Wind | RCP6.0 | 2100 | 83.3995 | 90.2612 | 97.6096 | 104.8446 | 112.1001
GuelphWind2023RCP8.5 | Guelph | Wind | RCP8.5 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
GuelphWind2025RCP8.5 | Guelph | Wind | RCP8.5 | 2025 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
GuelphWind2030RCP8.5 | Guelph | Wind | RCP8.5 | 2030 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
GuelphWind2035RCP8.5 | Guelph | Wind | RCP8.5 | 2035 | 81.8329 | 88.233 | 95.0058 | 101.7467 | 108.4995
GuelphWind2040RCP8.5 | Guelph | Wind | RCP8.5 | 2040 | 81.9384 | 88.3612 | 95.1562 | 101.9211 | 108.696
GuelphWind2045RCP8.5 | Guelph | Wind | RCP8.5 | 2045 | 82.044 | 88.4894 | 95.3066 | 102.0954 | 108.8924
GuelphWind2050RCP8.5 | Guelph | Wind | RCP8.5 | 2050 | 82.2875 | 88.8158 | 95.739 | 102.6151 | 109.5032
GuelphWind2055RCP8.5 | Guelph | Wind | RCP8.5 | 2055 | 82.4254 | 89.014 | 96.021 | 102.9604 | 109.9176
GuelphWind2060RCP8.5 | Guelph | Wind | RCP8.5 | 2060 | 82.8421 | 89.5618 | 96.7385 | 103.8187 | 110.9213
GuelphWind2065RCP8.5 | Guelph | Wind | RCP8.5 | 2065 | 83.1208 | 89.9115 | 97.1741 | 104.3316 | 111.5107
GuelphWind2070RCP8.5 | Guelph | Wind | RCP8.5 | 2070 | 83.6457 | 90.5933 | 98.0451 | 105.371 | 112.718
GuelphWind2075RCP8.5 | Guelph | Wind | RCP8.5 | 2075 | 83.8919 | 90.9255 | 98.4807 | 105.8973 | 113.336
GuelphWind2080RCP8.5 | Guelph | Wind | RCP8.5 | 2080 | 84.1381 | 91.2577 | 98.9162 | 106.4237 | 113.9539
GuelphWind2085RCP8.5 | Guelph | Wind | RCP8.5 | 2085 | 84.3775 | 91.5768 | 99.3392 | 106.9266 | 114.5433
GuelphWind2090RCP8.5 | Guelph | Wind | RCP8.5 | 2090 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
GuelphWind2095RCP8.5 | Guelph | Wind | RCP8.5 | 2095 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
GuelphWind2100RCP8.5 | Guelph | Wind | RCP8.5 | 2100 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
GuthrieIce Accretion2023RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2023 | 15.6684 | 18.7464 | 22.632 | 25.6001 | 28.5453
GuthrieIce Accretion2025RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2025 | 15.663 | 18.7432 | 22.6358 | 25.6088 | 28.5646
GuthrieIce Accretion2030RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2030 | 15.6577 | 18.74 | 22.6397 | 25.6175 | 28.5839
GuthrieIce Accretion2035RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2035 | 15.6524 | 18.7368 | 22.6435 | 25.6261 | 28.6033
GuthrieIce Accretion2040RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2040 | 15.647 | 18.7337 | 22.6473 | 25.6348 | 28.6226
GuthrieIce Accretion2045RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2045 | 15.6417 | 18.7305 | 22.6512 | 25.6435 | 28.6419
GuthrieIce Accretion2050RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2050 | 15.5947 | 18.6967 | 22.6366 | 25.6417 | 28.6554
GuthrieIce Accretion2055RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2055 | 15.5531 | 18.6662 | 22.6182 | 25.6313 | 28.6496
GuthrieIce Accretion2060RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2060 | 15.5115 | 18.6357 | 22.5998 | 25.6209 | 28.6438
GuthrieIce Accretion2065RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2065 | 15.4699 | 18.6051 | 22.5814 | 25.6105 | 28.638
GuthrieIce Accretion2070RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2070 | 15.4283 | 18.5746 | 22.563 | 25.6001 | 28.6322
GuthrieIce Accretion2075RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2075 | 15.4283 | 18.5968 | 22.6128 | 25.6695 | 28.7192
GuthrieIce Accretion2080RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2080 | 15.4283 | 18.6191 | 22.6627 | 25.7388 | 28.8061
GuthrieIce Accretion2085RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2085 | 15.4283 | 18.6414 | 22.7125 | 25.8081 | 28.8931
GuthrieIce Accretion2090RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2090 | 15.4283 | 18.6637 | 22.7623 | 25.8774 | 28.98
GuthrieIce Accretion2095RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2095 | 15.4283 | 18.6859 | 22.8122 | 25.9467 | 29.0669
GuthrieIce Accretion2100RCP4.5 | Guthrie | Ice Accretion | RCP4.5 | 2100 | 15.4283 | 18.7082 | 22.862 | 26.016 | 29.1539
GuthrieIce Accretion2023RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2023 | 15.6684 | 18.7464 | 22.632 | 25.6001 | 28.5453
GuthrieIce Accretion2025RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2025 | 15.663 | 18.7432 | 22.6358 | 25.6088 | 28.5646
GuthrieIce Accretion2030RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2030 | 15.6577 | 18.74 | 22.6397 | 25.6175 | 28.5839
GuthrieIce Accretion2035RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2035 | 15.6524 | 18.7368 | 22.6435 | 25.6261 | 28.6033
GuthrieIce Accretion2040RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2040 | 15.647 | 18.7337 | 22.6473 | 25.6348 | 28.6226
GuthrieIce Accretion2045RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2045 | 15.6417 | 18.7305 | 22.6512 | 25.6435 | 28.6419
GuthrieIce Accretion2050RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2050 | 15.5947 | 18.6967 | 22.6366 | 25.6417 | 28.6554
GuthrieIce Accretion2055RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2055 | 15.5531 | 18.6662 | 22.6182 | 25.6313 | 28.6496
GuthrieIce Accretion2060RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2060 | 15.5115 | 18.6357 | 22.5998 | 25.6209 | 28.6438
GuthrieIce Accretion2065RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2065 | 15.4699 | 18.6051 | 22.5814 | 25.6105 | 28.638
GuthrieIce Accretion2070RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2070 | 15.4283 | 18.5746 | 22.563 | 25.6001 | 28.6322
GuthrieIce Accretion2075RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2075 | 15.4283 | 18.608 | 22.6377 | 25.7041 | 28.7627
GuthrieIce Accretion2080RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2080 | 15.4283 | 18.6414 | 22.7125 | 25.8081 | 28.8931
GuthrieIce Accretion2085RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2085 | 15.4283 | 18.6748 | 22.7873 | 25.912 | 29.0235
GuthrieIce Accretion2090RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2090 | 15.2523 | 18.53 | 22.6857 | 25.8341 | 28.98
GuthrieIce Accretion2095RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2095 | 15.0762 | 18.3519 | 22.5093 | 25.6521 | 28.8061
GuthrieIce Accretion2100RCP6.0 | Guthrie | Ice Accretion | RCP6.0 | 2100 | 14.9002 | 18.1737 | 22.333 | 25.4702 | 28.6322
GuthrieIce Accretion2023RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2023 | 15.6684 | 18.7464 | 22.632 | 25.6001 | 28.5453
GuthrieIce Accretion2025RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2025 | 15.6577 | 18.74 | 22.6397 | 25.6175 | 28.5839
GuthrieIce Accretion2030RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2030 | 15.647 | 18.7337 | 22.6473 | 25.6348 | 28.6226
GuthrieIce Accretion2035RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2035 | 15.6364 | 18.7273 | 22.655 | 25.6521 | 28.6612
GuthrieIce Accretion2040RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2040 | 15.567 | 18.6764 | 22.6243 | 25.6348 | 28.6516
GuthrieIce Accretion2045RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2045 | 15.4977 | 18.6255 | 22.5937 | 25.6175 | 28.6419
GuthrieIce Accretion2050RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2050 | 15.4283 | 18.6191 | 22.6627 | 25.7388 | 28.8061
GuthrieIce Accretion2055RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2055 | 15.4283 | 18.6637 | 22.7623 | 25.8774 | 28.98
GuthrieIce Accretion2060RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2060 | 15.2523 | 18.53 | 22.6857 | 25.8341 | 28.98
GuthrieIce Accretion2065RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2065 | 15.0762 | 18.3519 | 22.5093 | 25.6521 | 28.8061
GuthrieIce Accretion2070RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2070 | 14.6441 | 17.9191 | 22.0647 | 25.2016 | 28.3521
GuthrieIce Accretion2075RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2075 | 14.388 | 17.6646 | 21.7963 | 24.9331 | 28.072
GuthrieIce Accretion2080RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2080 | 14.1319 | 17.4101 | 21.528 | 24.6645 | 27.7918
GuthrieIce Accretion2085RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2085 | 13.4758 | 16.6465 | 20.6425 | 23.6769 | 26.6906
GuthrieIce Accretion2090RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2090 | 12.8196 | 15.8829 | 19.757 | 22.6893 | 25.5893
GuthrieIce Accretion2095RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2095 | 12.8196 | 15.8829 | 19.757 | 22.6893 | 25.5893
GuthrieIce Accretion2100RCP8.5 | Guthrie | Ice Accretion | RCP8.5 | 2100 | 12.8196 | 15.8829 | 19.757 | 22.6893 | 25.5893
GuthrieWind2023RCP4.5 | Guthrie | Wind | RCP4.5 | 2023 | 74.6382 | 80.4039 | 86.473 | 92.5445 | 98.6086
GuthrieWind2025RCP4.5 | Guthrie | Wind | RCP4.5 | 2025 | 74.6593 | 80.4306 | 86.5074 | 92.5844 | 98.656
GuthrieWind2030RCP4.5 | Guthrie | Wind | RCP4.5 | 2030 | 74.6803 | 80.4572 | 86.5418 | 92.6243 | 98.7034
GuthrieWind2035RCP4.5 | Guthrie | Wind | RCP4.5 | 2035 | 74.7013 | 80.4839 | 86.5762 | 92.6641 | 98.7508
GuthrieWind2040RCP4.5 | Guthrie | Wind | RCP4.5 | 2040 | 74.7224 | 80.5105 | 86.6106 | 92.704 | 98.7982
GuthrieWind2045RCP4.5 | Guthrie | Wind | RCP4.5 | 2045 | 74.7434 | 80.5372 | 86.645 | 92.7439 | 98.8456
GuthrieWind2050RCP4.5 | Guthrie | Wind | RCP4.5 | 2050 | 74.8818 | 80.6998 | 86.8359 | 92.9586 | 99.0871
GuthrieWind2055RCP4.5 | Guthrie | Wind | RCP4.5 | 2055 | 74.9991 | 80.8358 | 86.9924 | 93.1334 | 99.2812
GuthrieWind2060RCP4.5 | Guthrie | Wind | RCP4.5 | 2060 | 75.1164 | 80.9718 | 87.149 | 93.3083 | 99.4753
GuthrieWind2065RCP4.5 | Guthrie | Wind | RCP4.5 | 2065 | 75.2338 | 81.1077 | 87.3055 | 93.4831 | 99.6694
GuthrieWind2070RCP4.5 | Guthrie | Wind | RCP4.5 | 2070 | 75.3511 | 81.2437 | 87.462 | 93.658 | 99.8635
GuthrieWind2075RCP4.5 | Guthrie | Wind | RCP4.5 | 2075 | 75.408 | 81.3183 | 87.5595 | 93.7745 | 99.9975
GuthrieWind2080RCP4.5 | Guthrie | Wind | RCP4.5 | 2080 | 75.465 | 81.393 | 87.6569 | 93.8911 | 100.1315
GuthrieWind2085RCP4.5 | Guthrie | Wind | RCP4.5 | 2085 | 75.5219 | 81.4676 | 87.7544 | 94.0076 | 100.2655
GuthrieWind2090RCP4.5 | Guthrie | Wind | RCP4.5 | 2090 | 75.5788 | 81.5423 | 87.8519 | 94.1242 | 100.3995
GuthrieWind2095RCP4.5 | Guthrie | Wind | RCP4.5 | 2095 | 75.6358 | 81.6169 | 87.9493 | 94.2407 | 100.5335
GuthrieWind2100RCP4.5 | Guthrie | Wind | RCP4.5 | 2100 | 75.6927 | 81.6916 | 88.0468 | 94.3573 | 100.6675
GuthrieWind2023RCP6.0 | Guthrie | Wind | RCP6.0 | 2023 | 74.6382 | 80.4039 | 86.473 | 92.5445 | 98.6086
GuthrieWind2025RCP6.0 | Guthrie | Wind | RCP6.0 | 2025 | 74.6593 | 80.4306 | 86.5074 | 92.5844 | 98.656
GuthrieWind2030RCP6.0 | Guthrie | Wind | RCP6.0 | 2030 | 74.6803 | 80.4572 | 86.5418 | 92.6243 | 98.7034
GuthrieWind2035RCP6.0 | Guthrie | Wind | RCP6.0 | 2035 | 74.7013 | 80.4839 | 86.5762 | 92.6641 | 98.7508
GuthrieWind2040RCP6.0 | Guthrie | Wind | RCP6.0 | 2040 | 74.7224 | 80.5105 | 86.6106 | 92.704 | 98.7982
GuthrieWind2045RCP6.0 | Guthrie | Wind | RCP6.0 | 2045 | 74.7434 | 80.5372 | 86.645 | 92.7439 | 98.8456
GuthrieWind2050RCP6.0 | Guthrie | Wind | RCP6.0 | 2050 | 74.8818 | 80.6998 | 86.8359 | 92.9586 | 99.0871
GuthrieWind2055RCP6.0 | Guthrie | Wind | RCP6.0 | 2055 | 74.9991 | 80.8358 | 86.9924 | 93.1334 | 99.2812
GuthrieWind2060RCP6.0 | Guthrie | Wind | RCP6.0 | 2060 | 75.1164 | 80.9718 | 87.149 | 93.3083 | 99.4753
GuthrieWind2065RCP6.0 | Guthrie | Wind | RCP6.0 | 2065 | 75.2338 | 81.1077 | 87.3055 | 93.4831 | 99.6694
GuthrieWind2070RCP6.0 | Guthrie | Wind | RCP6.0 | 2070 | 75.3511 | 81.2437 | 87.462 | 93.658 | 99.8635
GuthrieWind2075RCP6.0 | Guthrie | Wind | RCP6.0 | 2075 | 75.4365 | 81.3557 | 87.6082 | 93.8328 | 100.0645
GuthrieWind2080RCP6.0 | Guthrie | Wind | RCP6.0 | 2080 | 75.5219 | 81.4676 | 87.7544 | 94.0076 | 100.2655
GuthrieWind2085RCP6.0 | Guthrie | Wind | RCP6.0 | 2085 | 75.6073 | 81.5796 | 87.9006 | 94.1825 | 100.4665
GuthrieWind2090RCP6.0 | Guthrie | Wind | RCP6.0 | 2090 | 75.9625 | 82.0168 | 88.4367 | 94.8051 | 101.1773
GuthrieWind2095RCP6.0 | Guthrie | Wind | RCP6.0 | 2095 | 76.2323 | 82.3421 | 88.8265 | 95.253 | 101.6871
GuthrieWind2100RCP6.0 | Guthrie | Wind | RCP6.0 | 2100 | 76.5021 | 82.6673 | 89.2164 | 95.7008 | 102.1969
GuthrieWind2023RCP8.5 | Guthrie | Wind | RCP8.5 | 2023 | 74.6382 | 80.4039 | 86.473 | 92.5445 | 98.6086
GuthrieWind2025RCP8.5 | Guthrie | Wind | RCP8.5 | 2025 | 74.6803 | 80.4572 | 86.5418 | 92.6243 | 98.7034
GuthrieWind2030RCP8.5 | Guthrie | Wind | RCP8.5 | 2030 | 74.7224 | 80.5105 | 86.6106 | 92.704 | 98.7982
GuthrieWind2035RCP8.5 | Guthrie | Wind | RCP8.5 | 2035 | 74.7645 | 80.5639 | 86.6794 | 92.7838 | 98.8929
GuthrieWind2040RCP8.5 | Guthrie | Wind | RCP8.5 | 2040 | 74.96 | 80.7905 | 86.9403 | 93.0752 | 99.2165
GuthrieWind2045RCP8.5 | Guthrie | Wind | RCP8.5 | 2045 | 75.1556 | 81.0171 | 87.2011 | 93.3666 | 99.54
GuthrieWind2050RCP8.5 | Guthrie | Wind | RCP8.5 | 2050 | 75.465 | 81.393 | 87.6569 | 93.8911 | 100.1315
GuthrieWind2055RCP8.5 | Guthrie | Wind | RCP8.5 | 2055 | 75.5788 | 81.5423 | 87.8519 | 94.1242 | 100.3995
GuthrieWind2060RCP8.5 | Guthrie | Wind | RCP8.5 | 2060 | 75.9625 | 82.0168 | 88.4367 | 94.8051 | 101.1773
GuthrieWind2065RCP8.5 | Guthrie | Wind | RCP8.5 | 2065 | 76.2323 | 82.3421 | 88.8265 | 95.253 | 101.6871
GuthrieWind2070RCP8.5 | Guthrie | Wind | RCP8.5 | 2070 | 76.6457 | 82.8406 | 89.4314 | 95.9493 | 102.4779
GuthrieWind2075RCP8.5 | Guthrie | Wind | RCP8.5 | 2075 | 76.7893 | 83.0139 | 89.6464 | 96.1977 | 102.759
GuthrieWind2080RCP8.5 | Guthrie | Wind | RCP8.5 | 2080 | 76.9328 | 83.1872 | 89.8614 | 96.4462 | 103.04
GuthrieWind2085RCP8.5 | Guthrie | Wind | RCP8.5 | 2085 | 76.9625 | 83.2192 | 89.8915 | 96.4784 | 103.0695
GuthrieWind2090RCP8.5 | Guthrie | Wind | RCP8.5 | 2090 | 76.9922 | 83.2512 | 89.9216 | 96.5106 | 103.0989
GuthrieWind2095RCP8.5 | Guthrie | Wind | RCP8.5 | 2095 | 76.9922 | 83.2512 | 89.9216 | 96.5106 | 103.0989
GuthrieWind2100RCP8.5 | Guthrie | Wind | RCP8.5 | 2100 | 76.9922 | 83.2512 | 89.9216 | 96.5106 | 103.0989
HaileyburyIce Accretion2023RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2023 | 14.7519 | 17.6458 | 21.32 | 24.1142 | 26.9136
HaileyburyIce Accretion2025RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2025 | 14.7311 | 17.6209 | 21.2867 | 24.0765 | 26.8716
HaileyburyIce Accretion2030RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2030 | 14.7102 | 17.596 | 21.2533 | 24.0389 | 26.8296
HaileyburyIce Accretion2035RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2035 | 14.6893 | 17.5711 | 21.22 | 24.0012 | 26.7876
HaileyburyIce Accretion2040RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2040 | 14.6684 | 17.5462 | 21.1867 | 23.9635 | 26.7456
HaileyburyIce Accretion2045RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2045 | 14.6476 | 17.5213 | 21.1533 | 23.9259 | 26.7036
HaileyburyIce Accretion2050RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2050 | 14.635 | 17.5064 | 21.128 | 23.8972 | 26.6717
HaileyburyIce Accretion2055RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2055 | 14.6434 | 17.5163 | 21.136 | 23.9063 | 26.6818
HaileyburyIce Accretion2060RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2060 | 14.6517 | 17.5263 | 21.144 | 23.9153 | 26.6918
HaileyburyIce Accretion2065RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2065 | 14.6601 | 17.5362 | 21.152 | 23.9244 | 26.7019
HaileyburyIce Accretion2070RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2070 | 14.6684 | 17.5462 | 21.16 | 23.9334 | 26.712
HaileyburyIce Accretion2075RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2075 | 14.7055 | 17.5988 | 21.2367 | 24.0276 | 26.8212
HaileyburyIce Accretion2080RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2080 | 14.7427 | 17.6513 | 21.3133 | 24.1217 | 26.9304
HaileyburyIce Accretion2085RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2085 | 14.7798 | 17.7039 | 21.39 | 24.2159 | 27.0396
HaileyburyIce Accretion2090RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2090 | 14.8169 | 17.7565 | 21.4667 | 24.3101 | 27.1488
HaileyburyIce Accretion2095RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2095 | 14.854 | 17.809 | 21.5433 | 24.4042 | 27.258
HaileyburyIce Accretion2100RCP4.5 | Haileybury | Ice Accretion | RCP4.5 | 2100 | 14.8911 | 17.8616 | 21.62 | 24.4984 | 27.3672
HaileyburyIce Accretion2023RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2023 | 14.7519 | 17.6458 | 21.32 | 24.1142 | 26.9136
HaileyburyIce Accretion2025RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2025 | 14.7311 | 17.6209 | 21.2867 | 24.0765 | 26.8716
HaileyburyIce Accretion2030RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2030 | 14.7102 | 17.596 | 21.2533 | 24.0389 | 26.8296
HaileyburyIce Accretion2035RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2035 | 14.6893 | 17.5711 | 21.22 | 24.0012 | 26.7876
HaileyburyIce Accretion2040RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2040 | 14.6684 | 17.5462 | 21.1867 | 23.9635 | 26.7456
HaileyburyIce Accretion2045RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2045 | 14.6476 | 17.5213 | 21.1533 | 23.9259 | 26.7036
HaileyburyIce Accretion2050RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2050 | 14.635 | 17.5064 | 21.128 | 23.8972 | 26.6717
HaileyburyIce Accretion2055RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2055 | 14.6434 | 17.5163 | 21.136 | 23.9063 | 26.6818
HaileyburyIce Accretion2060RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2060 | 14.6517 | 17.5263 | 21.144 | 23.9153 | 26.6918
HaileyburyIce Accretion2065RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2065 | 14.6601 | 17.5362 | 21.152 | 23.9244 | 26.7019
HaileyburyIce Accretion2070RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2070 | 14.6684 | 17.5462 | 21.16 | 23.9334 | 26.712
HaileyburyIce Accretion2075RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2075 | 14.7241 | 17.625 | 21.275 | 24.0746 | 26.8758
HaileyburyIce Accretion2080RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2080 | 14.7798 | 17.7039 | 21.39 | 24.2159 | 27.0396
HaileyburyIce Accretion2085RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2085 | 14.8354 | 17.7828 | 21.505 | 24.3571 | 27.2034
HaileyburyIce Accretion2090RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2090 | 14.9375 | 17.9225 | 21.7067 | 24.6039 | 27.4848
HaileyburyIce Accretion2095RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2095 | 14.9839 | 17.9833 | 21.7933 | 24.7093 | 27.6024
HaileyburyIce Accretion2100RCP6.0 | Haileybury | Ice Accretion | RCP6.0 | 2100 | 15.0303 | 18.0442 | 21.88 | 24.8148 | 27.72
HaileyburyIce Accretion2023RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2023 | 14.7519 | 17.6458 | 21.32 | 24.1142 | 26.9136
HaileyburyIce Accretion2025RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2025 | 14.7102 | 17.596 | 21.2533 | 24.0389 | 26.8296
HaileyburyIce Accretion2030RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2030 | 14.6684 | 17.5462 | 21.1867 | 23.9635 | 26.7456
HaileyburyIce Accretion2035RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2035 | 14.6267 | 17.4964 | 21.12 | 23.8882 | 26.6616
HaileyburyIce Accretion2040RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2040 | 14.6406 | 17.513 | 21.1333 | 23.9033 | 26.6784
HaileyburyIce Accretion2045RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2045 | 14.6545 | 17.5296 | 21.1467 | 23.9183 | 26.6952
HaileyburyIce Accretion2050RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2050 | 14.7427 | 17.6513 | 21.3133 | 24.1217 | 26.9304
HaileyburyIce Accretion2055RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2055 | 14.8169 | 17.7565 | 21.4667 | 24.3101 | 27.1488
HaileyburyIce Accretion2060RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2060 | 14.9375 | 17.9225 | 21.7067 | 24.6039 | 27.4848
HaileyburyIce Accretion2065RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2065 | 14.9839 | 17.9833 | 21.7933 | 24.7093 | 27.6024
HaileyburyIce Accretion2070RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2070 | 14.8633 | 17.8616 | 21.6667 | 24.5737 | 27.4596
HaileyburyIce Accretion2075RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2075 | 14.6963 | 17.679 | 21.4533 | 24.3327 | 27.1992
HaileyburyIce Accretion2080RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2080 | 14.5293 | 17.4964 | 21.24 | 24.0916 | 26.9388
HaileyburyIce Accretion2085RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2085 | 14.5641 | 17.5711 | 21.36 | 24.2611 | 27.1404
HaileyburyIce Accretion2090RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2090 | 14.5989 | 17.6458 | 21.48 | 24.4306 | 27.342
HaileyburyIce Accretion2095RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2095 | 14.5989 | 17.6458 | 21.48 | 24.4306 | 27.342
HaileyburyIce Accretion2100RCP8.5 | Haileybury | Ice Accretion | RCP8.5 | 2100 | 14.5989 | 17.6458 | 21.48 | 24.4306 | 27.342
HaileyburyWind2023RCP4.5 | Haileybury | Wind | RCP4.5 | 2023 | 76.1156 | 81.9218 | 88.0088 | 94.1129 | 100.2197
HaileyburyWind2025RCP4.5 | Haileybury | Wind | RCP4.5 | 2025 | 76.122 | 81.9259 | 88.0132 | 94.1176 | 100.223
HaileyburyWind2030RCP4.5 | Haileybury | Wind | RCP4.5 | 2030 | 76.1283 | 81.93 | 88.0176 | 94.1223 | 100.2264
HaileyburyWind2035RCP4.5 | Haileybury | Wind | RCP4.5 | 2035 | 76.1346 | 81.9341 | 88.022 | 94.127 | 100.2297
HaileyburyWind2040RCP4.5 | Haileybury | Wind | RCP4.5 | 2040 | 76.141 | 81.9382 | 88.0264 | 94.1318 | 100.2331
HaileyburyWind2045RCP4.5 | Haileybury | Wind | RCP4.5 | 2045 | 76.1473 | 81.9423 | 88.0308 | 94.1365 | 100.2364
HaileyburyWind2050RCP4.5 | Haileybury | Wind | RCP4.5 | 2050 | 76.1551 | 81.9448 | 88.0246 | 94.1261 | 100.2197
HaileyburyWind2055RCP4.5 | Haileybury | Wind | RCP4.5 | 2055 | 76.1567 | 81.9431 | 88.0141 | 94.111 | 100.1996
HaileyburyWind2060RCP4.5 | Haileybury | Wind | RCP4.5 | 2060 | 76.1582 | 81.9415 | 88.0035 | 94.096 | 100.1796
HaileyburyWind2065RCP4.5 | Haileybury | Wind | RCP4.5 | 2065 | 76.1597 | 81.9398 | 87.993 | 94.0809 | 100.1595
HaileyburyWind2070RCP4.5 | Haileybury | Wind | RCP4.5 | 2070 | 76.1612 | 81.9382 | 87.9824 | 94.0658 | 100.1394
HaileyburyWind2075RCP4.5 | Haileybury | Wind | RCP4.5 | 2075 | 76.2182 | 82.0078 | 88.0689 | 94.1647 | 100.2514
HaileyburyWind2080RCP4.5 | Haileybury | Wind | RCP4.5 | 2080 | 76.2752 | 82.0773 | 88.1555 | 94.2636 | 100.3635
HaileyburyWind2085RCP4.5 | Haileybury | Wind | RCP4.5 | 2085 | 76.3322 | 82.1469 | 88.242 | 94.3624 | 100.4755
HaileyburyWind2090RCP4.5 | Haileybury | Wind | RCP4.5 | 2090 | 76.3892 | 82.2165 | 88.3285 | 94.4613 | 100.5875
HaileyburyWind2095RCP4.5 | Haileybury | Wind | RCP4.5 | 2095 | 76.4462 | 82.286 | 88.4151 | 94.5602 | 100.6995
HaileyburyWind2100RCP4.5 | Haileybury | Wind | RCP4.5 | 2100 | 76.5032 | 82.3556 | 88.5016 | 94.659 | 100.8116
HaileyburyWind2023RCP6.0 | Haileybury | Wind | RCP6.0 | 2023 | 76.1156 | 81.9218 | 88.0088 | 94.1129 | 100.2197
HaileyburyWind2025RCP6.0 | Haileybury | Wind | RCP6.0 | 2025 | 76.122 | 81.9259 | 88.0132 | 94.1176 | 100.223
HaileyburyWind2030RCP6.0 | Haileybury | Wind | RCP6.0 | 2030 | 76.1283 | 81.93 | 88.0176 | 94.1223 | 100.2264
HaileyburyWind2035RCP6.0 | Haileybury | Wind | RCP6.0 | 2035 | 76.1346 | 81.9341 | 88.022 | 94.127 | 100.2297
HaileyburyWind2040RCP6.0 | Haileybury | Wind | RCP6.0 | 2040 | 76.141 | 81.9382 | 88.0264 | 94.1318 | 100.2331
HaileyburyWind2045RCP6.0 | Haileybury | Wind | RCP6.0 | 2045 | 76.1473 | 81.9423 | 88.0308 | 94.1365 | 100.2364
HaileyburyWind2050RCP6.0 | Haileybury | Wind | RCP6.0 | 2050 | 76.1551 | 81.9448 | 88.0246 | 94.1261 | 100.2197
HaileyburyWind2055RCP6.0 | Haileybury | Wind | RCP6.0 | 2055 | 76.1567 | 81.9431 | 88.0141 | 94.111 | 100.1996
HaileyburyWind2060RCP6.0 | Haileybury | Wind | RCP6.0 | 2060 | 76.1582 | 81.9415 | 88.0035 | 94.096 | 100.1796
HaileyburyWind2065RCP6.0 | Haileybury | Wind | RCP6.0 | 2065 | 76.1597 | 81.9398 | 87.993 | 94.0809 | 100.1595
HaileyburyWind2070RCP6.0 | Haileybury | Wind | RCP6.0 | 2070 | 76.1612 | 81.9382 | 87.9824 | 94.0658 | 100.1394
HaileyburyWind2075RCP6.0 | Haileybury | Wind | RCP6.0 | 2075 | 76.2467 | 82.0426 | 88.1122 | 94.2141 | 100.3075
HaileyburyWind2080RCP6.0 | Haileybury | Wind | RCP6.0 | 2080 | 76.3322 | 82.1469 | 88.242 | 94.3624 | 100.4755
HaileyburyWind2085RCP6.0 | Haileybury | Wind | RCP6.0 | 2085 | 76.4177 | 82.2512 | 88.3718 | 94.5107 | 100.6435
HaileyburyWind2090RCP6.0 | Haileybury | Wind | RCP6.0 | 2090 | 76.493 | 82.331 | 88.4576 | 94.6026 | 100.7413
HaileyburyWind2095RCP6.0 | Haileybury | Wind | RCP6.0 | 2095 | 76.4829 | 82.3065 | 88.4136 | 94.5461 | 100.6711
HaileyburyWind2100RCP6.0 | Haileybury | Wind | RCP6.0 | 2100 | 76.4728 | 82.2819 | 88.3696 | 94.4896 | 100.6009
HaileyburyWind2023RCP8.5 | Haileybury | Wind | RCP8.5 | 2023 | 76.1156 | 81.9218 | 88.0088 | 94.1129 | 100.2197
HaileyburyWind2025RCP8.5 | Haileybury | Wind | RCP8.5 | 2025 | 76.1283 | 81.93 | 88.0176 | 94.1223 | 100.2264
HaileyburyWind2030RCP8.5 | Haileybury | Wind | RCP8.5 | 2030 | 76.141 | 81.9382 | 88.0264 | 94.1318 | 100.2331
HaileyburyWind2035RCP8.5 | Haileybury | Wind | RCP8.5 | 2035 | 76.1536 | 81.9464 | 88.0352 | 94.1412 | 100.2397
HaileyburyWind2040RCP8.5 | Haileybury | Wind | RCP8.5 | 2040 | 76.1562 | 81.9437 | 88.0176 | 94.1161 | 100.2063
HaileyburyWind2045RCP8.5 | Haileybury | Wind | RCP8.5 | 2045 | 76.1587 | 81.9409 | 88 | 94.0909 | 100.1729
HaileyburyWind2050RCP8.5 | Haileybury | Wind | RCP8.5 | 2050 | 76.2752 | 82.0773 | 88.1555 | 94.2636 | 100.3635
HaileyburyWind2055RCP8.5 | Haileybury | Wind | RCP8.5 | 2055 | 76.3892 | 82.2165 | 88.3285 | 94.4613 | 100.5875
HaileyburyWind2060RCP8.5 | Haileybury | Wind | RCP8.5 | 2060 | 76.493 | 82.331 | 88.4576 | 94.6026 | 100.7413
HaileyburyWind2065RCP8.5 | Haileybury | Wind | RCP8.5 | 2065 | 76.4829 | 82.3065 | 88.4136 | 94.5461 | 100.6711
HaileyburyWind2070RCP8.5 | Haileybury | Wind | RCP8.5 | 2070 | 76.5488 | 82.3665 | 88.4635 | 94.59 | 100.7112
HaileyburyWind2075RCP8.5 | Haileybury | Wind | RCP8.5 | 2075 | 76.6247 | 82.4511 | 88.5573 | 94.6904 | 100.8216
HaileyburyWind2080RCP8.5 | Haileybury | Wind | RCP8.5 | 2080 | 76.7007 | 82.5356 | 88.6512 | 94.7909 | 100.932
HaileyburyWind2085RCP8.5 | Haileybury | Wind | RCP8.5 | 2085 | 76.8299 | 82.7075 | 88.8756 | 95.0592 | 101.248
HaileyburyWind2090RCP8.5 | Haileybury | Wind | RCP8.5 | 2090 | 76.9591 | 82.8794 | 89.1 | 95.3276 | 101.564
HaileyburyWind2095RCP8.5 | Haileybury | Wind | RCP8.5 | 2095 | 76.9591 | 82.8794 | 89.1 | 95.3276 | 101.564
HaileyburyWind2100RCP8.5 | Haileybury | Wind | RCP8.5 | 2100 | 76.9591 | 82.8794 | 89.1 | 95.3276 | 101.564
Haldimand (Caledonia)Ice Accretion2023RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2023 | 23.2802 | 27.9096 | 33.796 | 38.2663 | 42.7543
Haldimand (Caledonia)Ice Accretion2025RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2025 | 23.1619 | 27.7826 | 33.6543 | 38.119 | 42.5972
Haldimand (Caledonia)Ice Accretion2030RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2030 | 23.0436 | 27.6556 | 33.5127 | 37.9718 | 42.4402
Haldimand (Caledonia)Ice Accretion2035RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2035 | 22.9253 | 27.5286 | 33.371 | 37.8245 | 42.2831
Haldimand (Caledonia)Ice Accretion2040RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2040 | 22.8071 | 27.4016 | 33.2293 | 37.6772 | 42.126
Haldimand (Caledonia)Ice Accretion2045RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2045 | 22.6888 | 27.2746 | 33.0877 | 37.5299 | 41.9689
Haldimand (Caledonia)Ice Accretion2050RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2050 | 22.2534 | 26.8034 | 32.572 | 36.9754 | 41.3749
Haldimand (Caledonia)Ice Accretion2055RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2055 | 21.9364 | 26.4591 | 32.198 | 36.5682 | 40.9379
Haldimand (Caledonia)Ice Accretion2060RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2060 | 21.6194 | 26.1148 | 31.824 | 36.1609 | 40.5009
Haldimand (Caledonia)Ice Accretion2065RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2065 | 21.3024 | 25.7705 | 31.45 | 35.7537 | 40.064
Haldimand (Caledonia)Ice Accretion2070RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2070 | 20.9853 | 25.4262 | 31.076 | 35.3464 | 39.627
Haldimand (Caledonia)Ice Accretion2075RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2075 | 20.8828 | 25.3369 | 30.9967 | 35.276 | 39.5556
Haldimand (Caledonia)Ice Accretion2080RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2080 | 20.7803 | 25.2475 | 30.9173 | 35.2055 | 39.4842
Haldimand (Caledonia)Ice Accretion2085RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2085 | 20.6778 | 25.1581 | 30.838 | 35.1351 | 39.4128
Haldimand (Caledonia)Ice Accretion2090RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2090 | 20.5752 | 25.0688 | 30.7587 | 35.0647 | 39.3414
Haldimand (Caledonia)Ice Accretion2095RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2095 | 20.4727 | 24.9794 | 30.6793 | 34.9942 | 39.27
Haldimand (Caledonia)Ice Accretion2100RCP4.5 | Haldimand (Caledonia) | Ice Accretion | RCP4.5 | 2100 | 20.3702 | 24.89 | 30.6 | 34.9238 | 39.1986
Haldimand (Caledonia)Ice Accretion2023RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2023 | 23.2802 | 27.9096 | 33.796 | 38.2663 | 42.7543
Haldimand (Caledonia)Ice Accretion2025RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2025 | 23.1619 | 27.7826 | 33.6543 | 38.119 | 42.5972
Haldimand (Caledonia)Ice Accretion2030RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2030 | 23.0436 | 27.6556 | 33.5127 | 37.9718 | 42.4402
Haldimand (Caledonia)Ice Accretion2035RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2035 | 22.9253 | 27.5286 | 33.371 | 37.8245 | 42.2831
Haldimand (Caledonia)Ice Accretion2040RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2040 | 22.8071 | 27.4016 | 33.2293 | 37.6772 | 42.126
Haldimand (Caledonia)Ice Accretion2045RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2045 | 22.6888 | 27.2746 | 33.0877 | 37.5299 | 41.9689
Haldimand (Caledonia)Ice Accretion2050RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2050 | 22.2534 | 26.8034 | 32.572 | 36.9754 | 41.3749
Haldimand (Caledonia)Ice Accretion2055RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2055 | 21.9364 | 26.4591 | 32.198 | 36.5682 | 40.9379
Haldimand (Caledonia)Ice Accretion2060RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2060 | 21.6194 | 26.1148 | 31.824 | 36.1609 | 40.5009
Haldimand (Caledonia)Ice Accretion2065RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2065 | 21.3024 | 25.7705 | 31.45 | 35.7537 | 40.064
Haldimand (Caledonia)Ice Accretion2070RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2070 | 20.9853 | 25.4262 | 31.076 | 35.3464 | 39.627
Haldimand (Caledonia)Ice Accretion2075RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2075 | 20.8315 | 25.2922 | 30.957 | 35.2407 | 39.5199
Haldimand (Caledonia)Ice Accretion2080RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2080 | 20.6778 | 25.1581 | 30.838 | 35.1351 | 39.4128
Haldimand (Caledonia)Ice Accretion2085RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2085 | 20.524 | 25.0241 | 30.719 | 35.0294 | 39.3057
Haldimand (Caledonia)Ice Accretion2090RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2090 | 19.6999 | 24.1281 | 29.716 | 33.9505 | 38.1419
Haldimand (Caledonia)Ice Accretion2095RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2095 | 19.0295 | 23.3662 | 28.832 | 32.9772 | 37.0852
Haldimand (Caledonia)Ice Accretion2100RCP6.0 | Haldimand (Caledonia) | Ice Accretion | RCP6.0 | 2100 | 18.3592 | 22.6042 | 27.948 | 32.0039 | 36.0284
Haldimand (Caledonia)Ice Accretion2023RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2023 | 23.2802 | 27.9096 | 33.796 | 38.2663 | 42.7543
Haldimand (Caledonia)Ice Accretion2025RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2025 | 23.0436 | 27.6556 | 33.5127 | 37.9718 | 42.4402
Haldimand (Caledonia)Ice Accretion2030RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2030 | 22.8071 | 27.4016 | 33.2293 | 37.6772 | 42.126
Haldimand (Caledonia)Ice Accretion2035RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2035 | 22.5705 | 27.1476 | 32.946 | 37.3827 | 41.8118
Haldimand (Caledonia)Ice Accretion2040RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2040 | 22.0421 | 26.5738 | 32.3227 | 36.7039 | 41.0836
Haldimand (Caledonia)Ice Accretion2045RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2045 | 21.5137 | 26 | 31.6993 | 36.0252 | 40.3553
Haldimand (Caledonia)Ice Accretion2050RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2050 | 20.7803 | 25.2475 | 30.9173 | 35.2055 | 39.4842
Haldimand (Caledonia)Ice Accretion2055RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2055 | 20.5752 | 25.0688 | 30.7587 | 35.0647 | 39.3414
Haldimand (Caledonia)Ice Accretion2060RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2060 | 19.6999 | 24.1281 | 29.716 | 33.9505 | 38.1419
Haldimand (Caledonia)Ice Accretion2065RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2065 | 19.0295 | 23.3662 | 28.832 | 32.9772 | 37.0852
Haldimand (Caledonia)Ice Accretion2070RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2070 | 17.9255 | 22.1245 | 27.4153 | 31.4148 | 35.4001
Haldimand (Caledonia)Ice Accretion2075RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2075 | 17.4917 | 21.6447 | 26.8827 | 30.8256 | 34.7718
Haldimand (Caledonia)Ice Accretion2080RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2080 | 17.058 | 21.165 | 26.35 | 30.2365 | 34.1435
Haldimand (Caledonia)Ice Accretion2085RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2085 | 15.8987 | 19.8104 | 24.701 | 28.3924 | 32.0872
Haldimand (Caledonia)Ice Accretion2090RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2090 | 14.7394 | 18.4559 | 23.052 | 26.5482 | 30.0308
Haldimand (Caledonia)Ice Accretion2095RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2095 | 14.7394 | 18.4559 | 23.052 | 26.5482 | 30.0308
Haldimand (Caledonia)Ice Accretion2100RCP8.5 | Haldimand (Caledonia) | Ice Accretion | RCP8.5 | 2100 | 14.7394 | 18.4559 | 23.052 | 26.5482 | 30.0308
Haldimand (Caledonia)Wind2023RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2023 | 87.6216 | 94.4654 | 101.6969 | 108.9021 | 116.1072
Haldimand (Caledonia)Wind2025RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2025 | 87.6405 | 94.4983 | 101.7474 | 108.967 | 116.1878
Haldimand (Caledonia)Wind2030RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2030 | 87.6594 | 94.5312 | 101.7979 | 109.0318 | 116.2684
Haldimand (Caledonia)Wind2035RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2035 | 87.6783 | 94.564 | 101.8484 | 109.0967 | 116.349
Haldimand (Caledonia)Wind2040RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2040 | 87.6972 | 94.5969 | 101.8989 | 109.1615 | 116.4296
Haldimand (Caledonia)Wind2045RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2045 | 87.7161 | 94.6298 | 101.9494 | 109.2263 | 116.5102
Haldimand (Caledonia)Wind2050RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2050 | 87.8083 | 94.7585 | 102.1231 | 109.4403 | 116.7658
Haldimand (Caledonia)Wind2055RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2055 | 87.8815 | 94.8543 | 102.2463 | 109.5895 | 116.9408
Haldimand (Caledonia)Wind2060RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2060 | 87.9548 | 94.9501 | 102.3696 | 109.7386 | 117.1158
Haldimand (Caledonia)Wind2065RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2065 | 88.028 | 95.0459 | 102.4928 | 109.8877 | 117.2908
Haldimand (Caledonia)Wind2070RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2070 | 88.1013 | 95.1417 | 102.616 | 110.0369 | 117.4658
Haldimand (Caledonia)Wind2075RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2075 | 88.2103 | 95.2873 | 102.8062 | 110.2638 | 117.7326
Haldimand (Caledonia)Wind2080RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2080 | 88.3193 | 95.4329 | 102.9964 | 110.4908 | 117.9993
Haldimand (Caledonia)Wind2085RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2085 | 88.4283 | 95.5785 | 103.1867 | 110.7177 | 118.2661
Haldimand (Caledonia)Wind2090RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2090 | 88.5373 | 95.7241 | 103.3769 | 110.9447 | 118.5328
Haldimand (Caledonia)Wind2095RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2095 | 88.6464 | 95.8697 | 103.5671 | 111.1716 | 118.7995
Haldimand (Caledonia)Wind2100RCP4.5 | Haldimand (Caledonia) | Wind | RCP4.5 | 2100 | 88.7554 | 96.0152 | 103.7573 | 111.3986 | 119.0663
Haldimand (Caledonia)Wind2023RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2023 | 87.6216 | 94.4654 | 101.6969 | 108.9021 | 116.1072
Haldimand (Caledonia)Wind2025RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2025 | 87.6405 | 94.4983 | 101.7474 | 108.967 | 116.1878
Haldimand (Caledonia)Wind2030RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2030 | 87.6594 | 94.5312 | 101.7979 | 109.0318 | 116.2684
Haldimand (Caledonia)Wind2035RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2035 | 87.6783 | 94.564 | 101.8484 | 109.0967 | 116.349
Haldimand (Caledonia)Wind2040RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2040 | 87.6972 | 94.5969 | 101.8989 | 109.1615 | 116.4296
Haldimand (Caledonia)Wind2045RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2045 | 87.7161 | 94.6298 | 101.9494 | 109.2263 | 116.5102
Haldimand (Caledonia)Wind2050RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2050 | 87.8083 | 94.7585 | 102.1231 | 109.4403 | 116.7658
Haldimand (Caledonia)Wind2055RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2055 | 87.8815 | 94.8543 | 102.2463 | 109.5895 | 116.9408
Haldimand (Caledonia)Wind2060RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2060 | 87.9548 | 94.9501 | 102.3696 | 109.7386 | 117.1158
Haldimand (Caledonia)Wind2065RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2065 | 88.028 | 95.0459 | 102.4928 | 109.8877 | 117.2908
Haldimand (Caledonia)Wind2070RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2070 | 88.1013 | 95.1417 | 102.616 | 110.0369 | 117.4658
Haldimand (Caledonia)Wind2075RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2075 | 88.2648 | 95.3601 | 102.9013 | 110.3773 | 117.8659
Haldimand (Caledonia)Wind2080RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2080 | 88.4283 | 95.5785 | 103.1867 | 110.7177 | 118.2661
Haldimand (Caledonia)Wind2085RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2085 | 88.5919 | 95.7969 | 103.472 | 111.0581 | 118.6662
Haldimand (Caledonia)Wind2090RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2090 | 89.0781 | 96.4254 | 104.2825 | 112.0218 | 119.7878
Haldimand (Caledonia)Wind2095RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2095 | 89.4007 | 96.8356 | 104.8077 | 112.645 | 120.5094
Haldimand (Caledonia)Wind2100RCP6.0 | Haldimand (Caledonia) | Wind | RCP6.0 | 2100 | 89.7234 | 97.2457 | 105.3329 | 113.2682 | 121.2309
Haldimand (Caledonia)Wind2023RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2023 | 87.6216 | 94.4654 | 101.6969 | 108.9021 | 116.1072
Haldimand (Caledonia)Wind2025RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2025 | 87.6594 | 94.5312 | 101.7979 | 109.0318 | 116.2684
Haldimand (Caledonia)Wind2030RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2030 | 87.6972 | 94.5969 | 101.8989 | 109.1615 | 116.4296
Haldimand (Caledonia)Wind2035RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2035 | 87.735 | 94.6627 | 101.9999 | 109.2912 | 116.5908
Haldimand (Caledonia)Wind2040RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2040 | 87.8571 | 94.8223 | 102.2053 | 109.5398 | 116.8825
Haldimand (Caledonia)Wind2045RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2045 | 87.9792 | 94.982 | 102.4106 | 109.7883 | 117.1741
Haldimand (Caledonia)Wind2050RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2050 | 88.3193 | 95.4329 | 102.9964 | 110.4908 | 117.9993
Haldimand (Caledonia)Wind2055RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2055 | 88.5373 | 95.7241 | 103.3769 | 110.9447 | 118.5328
Haldimand (Caledonia)Wind2060RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2060 | 89.0781 | 96.4254 | 104.2825 | 112.0218 | 119.7878
Haldimand (Caledonia)Wind2065RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2065 | 89.4007 | 96.8356 | 104.8077 | 112.645 | 120.5094
Haldimand (Caledonia)Wind2070RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2070 | 89.9037 | 97.4962 | 105.6763 | 113.686 | 121.726
Haldimand (Caledonia)Wind2075RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2075 | 90.0839 | 97.7467 | 106.0197 | 114.1039 | 122.2211
Haldimand (Caledonia)Wind2080RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2080 | 90.2641 | 97.9972 | 106.3631 | 114.5218 | 122.7162
Haldimand (Caledonia)Wind2085RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2085 | 90.5389 | 98.3682 | 106.8479 | 115.1108 | 123.4071
Haldimand (Caledonia)Wind2090RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2090 | 90.8136 | 98.7392 | 107.3327 | 115.6997 | 124.0979
Haldimand (Caledonia)Wind2095RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2095 | 90.8136 | 98.7392 | 107.3327 | 115.6997 | 124.0979
Haldimand (Caledonia)Wind2100RCP8.5 | Haldimand (Caledonia) | Wind | RCP8.5 | 2100 | 90.8136 | 98.7392 | 107.3327 | 115.6997 | 124.0979
Haldimand (Hagersville)Ice Accretion2023RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2023 | 23.2802 | 27.9096 | 33.796 | 38.2663 | 42.7543
Haldimand (Hagersville)Ice Accretion2025RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2025 | 23.1619 | 27.7826 | 33.6543 | 38.119 | 42.5972
Haldimand (Hagersville)Ice Accretion2030RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2030 | 23.0436 | 27.6556 | 33.5127 | 37.9718 | 42.4402
Haldimand (Hagersville)Ice Accretion2035RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2035 | 22.9253 | 27.5286 | 33.371 | 37.8245 | 42.2831
Haldimand (Hagersville)Ice Accretion2040RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2040 | 22.8071 | 27.4016 | 33.2293 | 37.6772 | 42.126
Haldimand (Hagersville)Ice Accretion2045RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2045 | 22.6888 | 27.2746 | 33.0877 | 37.5299 | 41.9689
Haldimand (Hagersville)Ice Accretion2050RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2050 | 22.2534 | 26.8034 | 32.572 | 36.9754 | 41.3749
Haldimand (Hagersville)Ice Accretion2055RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2055 | 21.9364 | 26.4591 | 32.198 | 36.5682 | 40.9379
Haldimand (Hagersville)Ice Accretion2060RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2060 | 21.6194 | 26.1148 | 31.824 | 36.1609 | 40.5009
Haldimand (Hagersville)Ice Accretion2065RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2065 | 21.3024 | 25.7705 | 31.45 | 35.7537 | 40.064
Haldimand (Hagersville)Ice Accretion2070RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2070 | 20.9853 | 25.4262 | 31.076 | 35.3464 | 39.627
Haldimand (Hagersville)Ice Accretion2075RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2075 | 20.8828 | 25.3369 | 30.9967 | 35.276 | 39.5556
Haldimand (Hagersville)Ice Accretion2080RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2080 | 20.7803 | 25.2475 | 30.9173 | 35.2055 | 39.4842
Haldimand (Hagersville)Ice Accretion2085RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2085 | 20.6778 | 25.1581 | 30.838 | 35.1351 | 39.4128
Haldimand (Hagersville)Ice Accretion2090RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2090 | 20.5752 | 25.0688 | 30.7587 | 35.0647 | 39.3414
Haldimand (Hagersville)Ice Accretion2095RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2095 | 20.4727 | 24.9794 | 30.6793 | 34.9942 | 39.27
Haldimand (Hagersville)Ice Accretion2100RCP4.5 | Haldimand (Hagersville) | Ice Accretion | RCP4.5 | 2100 | 20.3702 | 24.89 | 30.6 | 34.9238 | 39.1986
Haldimand (Hagersville)Ice Accretion2023RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2023 | 23.2802 | 27.9096 | 33.796 | 38.2663 | 42.7543
Haldimand (Hagersville)Ice Accretion2025RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2025 | 23.1619 | 27.7826 | 33.6543 | 38.119 | 42.5972
Haldimand (Hagersville)Ice Accretion2030RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2030 | 23.0436 | 27.6556 | 33.5127 | 37.9718 | 42.4402
Haldimand (Hagersville)Ice Accretion2035RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2035 | 22.9253 | 27.5286 | 33.371 | 37.8245 | 42.2831
Haldimand (Hagersville)Ice Accretion2040RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2040 | 22.8071 | 27.4016 | 33.2293 | 37.6772 | 42.126
Haldimand (Hagersville)Ice Accretion2045RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2045 | 22.6888 | 27.2746 | 33.0877 | 37.5299 | 41.9689
Haldimand (Hagersville)Ice Accretion2050RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2050 | 22.2534 | 26.8034 | 32.572 | 36.9754 | 41.3749
Haldimand (Hagersville)Ice Accretion2055RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2055 | 21.9364 | 26.4591 | 32.198 | 36.5682 | 40.9379
Haldimand (Hagersville)Ice Accretion2060RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2060 | 21.6194 | 26.1148 | 31.824 | 36.1609 | 40.5009
Haldimand (Hagersville)Ice Accretion2065RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2065 | 21.3024 | 25.7705 | 31.45 | 35.7537 | 40.064
Haldimand (Hagersville)Ice Accretion2070RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2070 | 20.9853 | 25.4262 | 31.076 | 35.3464 | 39.627
Haldimand (Hagersville)Ice Accretion2075RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2075 | 20.8315 | 25.2922 | 30.957 | 35.2407 | 39.5199
Haldimand (Hagersville)Ice Accretion2080RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2080 | 20.6778 | 25.1581 | 30.838 | 35.1351 | 39.4128
Haldimand (Hagersville)Ice Accretion2085RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2085 | 20.524 | 25.0241 | 30.719 | 35.0294 | 39.3057
Haldimand (Hagersville)Ice Accretion2090RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2090 | 19.6999 | 24.1281 | 29.716 | 33.9505 | 38.1419
Haldimand (Hagersville)Ice Accretion2095RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2095 | 19.0295 | 23.3662 | 28.832 | 32.9772 | 37.0852
Haldimand (Hagersville)Ice Accretion2100RCP6.0 | Haldimand (Hagersville) | Ice Accretion | RCP6.0 | 2100 | 18.3592 | 22.6042 | 27.948 | 32.0039 | 36.0284
Haldimand (Hagersville)Ice Accretion2023RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2023 | 23.2802 | 27.9096 | 33.796 | 38.2663 | 42.7543
Haldimand (Hagersville)Ice Accretion2025RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2025 | 23.0436 | 27.6556 | 33.5127 | 37.9718 | 42.4402
Haldimand (Hagersville)Ice Accretion2030RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2030 | 22.8071 | 27.4016 | 33.2293 | 37.6772 | 42.126
Haldimand (Hagersville)Ice Accretion2035RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2035 | 22.5705 | 27.1476 | 32.946 | 37.3827 | 41.8118
Haldimand (Hagersville)Ice Accretion2040RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2040 | 22.0421 | 26.5738 | 32.3227 | 36.7039 | 41.0836
Haldimand (Hagersville)Ice Accretion2045RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2045 | 21.5137 | 26 | 31.6993 | 36.0252 | 40.3553
Haldimand (Hagersville)Ice Accretion2050RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2050 | 20.7803 | 25.2475 | 30.9173 | 35.2055 | 39.4842
Haldimand (Hagersville)Ice Accretion2055RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2055 | 20.5752 | 25.0688 | 30.7587 | 35.0647 | 39.3414
Haldimand (Hagersville)Ice Accretion2060RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2060 | 19.6999 | 24.1281 | 29.716 | 33.9505 | 38.1419
Haldimand (Hagersville)Ice Accretion2065RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2065 | 19.0295 | 23.3662 | 28.832 | 32.9772 | 37.0852
Haldimand (Hagersville)Ice Accretion2070RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2070 | 17.9255 | 22.1245 | 27.4153 | 31.4148 | 35.4001
Haldimand (Hagersville)Ice Accretion2075RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2075 | 17.4917 | 21.6447 | 26.8827 | 30.8256 | 34.7718
Haldimand (Hagersville)Ice Accretion2080RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2080 | 17.058 | 21.165 | 26.35 | 30.2365 | 34.1435
Haldimand (Hagersville)Ice Accretion2085RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2085 | 15.8987 | 19.8104 | 24.701 | 28.3924 | 32.0872
Haldimand (Hagersville)Ice Accretion2090RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2090 | 14.7394 | 18.4559 | 23.052 | 26.5482 | 30.0308
Haldimand (Hagersville)Ice Accretion2095RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2095 | 14.7394 | 18.4559 | 23.052 | 26.5482 | 30.0308
Haldimand (Hagersville)Ice Accretion2100RCP8.5 | Haldimand (Hagersville) | Ice Accretion | RCP8.5 | 2100 | 14.7394 | 18.4559 | 23.052 | 26.5482 | 30.0308
Haldimand (Hagersville)Wind2023RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2023 | 87.6216 | 94.4654 | 101.6969 | 108.9021 | 116.1072
Haldimand (Hagersville)Wind2025RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2025 | 87.6405 | 94.4983 | 101.7474 | 108.967 | 116.1878
Haldimand (Hagersville)Wind2030RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2030 | 87.6594 | 94.5312 | 101.7979 | 109.0318 | 116.2684
Haldimand (Hagersville)Wind2035RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2035 | 87.6783 | 94.564 | 101.8484 | 109.0967 | 116.349
Haldimand (Hagersville)Wind2040RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2040 | 87.6972 | 94.5969 | 101.8989 | 109.1615 | 116.4296
Haldimand (Hagersville)Wind2045RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2045 | 87.7161 | 94.6298 | 101.9494 | 109.2263 | 116.5102
Haldimand (Hagersville)Wind2050RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2050 | 87.8083 | 94.7585 | 102.1231 | 109.4403 | 116.7658
Haldimand (Hagersville)Wind2055RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2055 | 87.8815 | 94.8543 | 102.2463 | 109.5895 | 116.9408
Haldimand (Hagersville)Wind2060RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2060 | 87.9548 | 94.9501 | 102.3696 | 109.7386 | 117.1158
Haldimand (Hagersville)Wind2065RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2065 | 88.028 | 95.0459 | 102.4928 | 109.8877 | 117.2908
Haldimand (Hagersville)Wind2070RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2070 | 88.1013 | 95.1417 | 102.616 | 110.0369 | 117.4658
Haldimand (Hagersville)Wind2075RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2075 | 88.2103 | 95.2873 | 102.8062 | 110.2638 | 117.7326
Haldimand (Hagersville)Wind2080RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2080 | 88.3193 | 95.4329 | 102.9964 | 110.4908 | 117.9993
Haldimand (Hagersville)Wind2085RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2085 | 88.4283 | 95.5785 | 103.1867 | 110.7177 | 118.2661
Haldimand (Hagersville)Wind2090RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2090 | 88.5373 | 95.7241 | 103.3769 | 110.9447 | 118.5328
Haldimand (Hagersville)Wind2095RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2095 | 88.6464 | 95.8697 | 103.5671 | 111.1716 | 118.7995
Haldimand (Hagersville)Wind2100RCP4.5 | Haldimand (Hagersville) | Wind | RCP4.5 | 2100 | 88.7554 | 96.0152 | 103.7573 | 111.3986 | 119.0663
Haldimand (Hagersville)Wind2023RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2023 | 87.6216 | 94.4654 | 101.6969 | 108.9021 | 116.1072
Haldimand (Hagersville)Wind2025RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2025 | 87.6405 | 94.4983 | 101.7474 | 108.967 | 116.1878
Haldimand (Hagersville)Wind2030RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2030 | 87.6594 | 94.5312 | 101.7979 | 109.0318 | 116.2684
Haldimand (Hagersville)Wind2035RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2035 | 87.6783 | 94.564 | 101.8484 | 109.0967 | 116.349
Haldimand (Hagersville)Wind2040RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2040 | 87.6972 | 94.5969 | 101.8989 | 109.1615 | 116.4296
Haldimand (Hagersville)Wind2045RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2045 | 87.7161 | 94.6298 | 101.9494 | 109.2263 | 116.5102
Haldimand (Hagersville)Wind2050RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2050 | 87.8083 | 94.7585 | 102.1231 | 109.4403 | 116.7658
Haldimand (Hagersville)Wind2055RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2055 | 87.8815 | 94.8543 | 102.2463 | 109.5895 | 116.9408
Haldimand (Hagersville)Wind2060RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2060 | 87.9548 | 94.9501 | 102.3696 | 109.7386 | 117.1158
Haldimand (Hagersville)Wind2065RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2065 | 88.028 | 95.0459 | 102.4928 | 109.8877 | 117.2908
Haldimand (Hagersville)Wind2070RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2070 | 88.1013 | 95.1417 | 102.616 | 110.0369 | 117.4658
Haldimand (Hagersville)Wind2075RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2075 | 88.2648 | 95.3601 | 102.9013 | 110.3773 | 117.8659
Haldimand (Hagersville)Wind2080RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2080 | 88.4283 | 95.5785 | 103.1867 | 110.7177 | 118.2661
Haldimand (Hagersville)Wind2085RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2085 | 88.5919 | 95.7969 | 103.472 | 111.0581 | 118.6662
Haldimand (Hagersville)Wind2090RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2090 | 89.0781 | 96.4254 | 104.2825 | 112.0218 | 119.7878
Haldimand (Hagersville)Wind2095RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2095 | 89.4007 | 96.8356 | 104.8077 | 112.645 | 120.5094
Haldimand (Hagersville)Wind2100RCP6.0 | Haldimand (Hagersville) | Wind | RCP6.0 | 2100 | 89.7234 | 97.2457 | 105.3329 | 113.2682 | 121.2309
Haldimand (Hagersville)Wind2023RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2023 | 87.6216 | 94.4654 | 101.6969 | 108.9021 | 116.1072
Haldimand (Hagersville)Wind2025RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2025 | 87.6594 | 94.5312 | 101.7979 | 109.0318 | 116.2684
Haldimand (Hagersville)Wind2030RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2030 | 87.6972 | 94.5969 | 101.8989 | 109.1615 | 116.4296
Haldimand (Hagersville)Wind2035RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2035 | 87.735 | 94.6627 | 101.9999 | 109.2912 | 116.5908
Haldimand (Hagersville)Wind2040RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2040 | 87.8571 | 94.8223 | 102.2053 | 109.5398 | 116.8825
Haldimand (Hagersville)Wind2045RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2045 | 87.9792 | 94.982 | 102.4106 | 109.7883 | 117.1741
Haldimand (Hagersville)Wind2050RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2050 | 88.3193 | 95.4329 | 102.9964 | 110.4908 | 117.9993
Haldimand (Hagersville)Wind2055RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2055 | 88.5373 | 95.7241 | 103.3769 | 110.9447 | 118.5328
Haldimand (Hagersville)Wind2060RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2060 | 89.0781 | 96.4254 | 104.2825 | 112.0218 | 119.7878
Haldimand (Hagersville)Wind2065RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2065 | 89.4007 | 96.8356 | 104.8077 | 112.645 | 120.5094
Haldimand (Hagersville)Wind2070RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2070 | 89.9037 | 97.4962 | 105.6763 | 113.686 | 121.726
Haldimand (Hagersville)Wind2075RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2075 | 90.0839 | 97.7467 | 106.0197 | 114.1039 | 122.2211
Haldimand (Hagersville)Wind2080RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2080 | 90.2641 | 97.9972 | 106.3631 | 114.5218 | 122.7162
Haldimand (Hagersville)Wind2085RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2085 | 90.5389 | 98.3682 | 106.8479 | 115.1108 | 123.4071
Haldimand (Hagersville)Wind2090RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2090 | 90.8136 | 98.7392 | 107.3327 | 115.6997 | 124.0979
Haldimand (Hagersville)Wind2095RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2095 | 90.8136 | 98.7392 | 107.3327 | 115.6997 | 124.0979
Haldimand (Hagersville)Wind2100RCP8.5 | Haldimand (Hagersville) | Wind | RCP8.5 | 2100 | 90.8136 | 98.7392 | 107.3327 | 115.6997 | 124.0979
HaliburtonIce Accretion2023RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2023 | 16.8569 | 20.0652 | 24.125 | 27.233 | 30.366
HaliburtonIce Accretion2025RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2025 | 16.8395 | 20.041 | 24.0917 | 27.1953 | 30.3188
HaliburtonIce Accretion2030RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2030 | 16.8221 | 20.0168 | 24.0583 | 27.1577 | 30.2715
HaliburtonIce Accretion2035RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2035 | 16.8047 | 19.9926 | 24.025 | 27.12 | 30.2242
HaliburtonIce Accretion2040RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2040 | 16.7873 | 19.9684 | 23.9917 | 27.0823 | 30.177
HaliburtonIce Accretion2045RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2045 | 16.7699 | 19.9442 | 23.9583 | 27.0447 | 30.1298
HaliburtonIce Accretion2050RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2050 | 16.749 | 19.9324 | 23.965 | 27.0635 | 30.1581
HaliburtonIce Accretion2055RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2055 | 16.7455 | 19.9449 | 24.005 | 27.12 | 30.2337
HaliburtonIce Accretion2060RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2060 | 16.7421 | 19.9573 | 24.045 | 27.1765 | 30.3093
HaliburtonIce Accretion2065RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2065 | 16.7386 | 19.9698 | 24.085 | 27.233 | 30.3849
HaliburtonIce Accretion2070RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2070 | 16.7351 | 19.9823 | 24.125 | 27.2895 | 30.4605
HaliburtonIce Accretion2075RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2075 | 16.8134 | 20.0929 | 24.2708 | 27.4637 | 30.66
HaliburtonIce Accretion2080RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2080 | 16.8917 | 20.2036 | 24.4167 | 27.6379 | 30.8595
HaliburtonIce Accretion2085RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2085 | 16.9699 | 20.3143 | 24.5625 | 27.8121 | 31.059
HaliburtonIce Accretion2090RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2090 | 17.0482 | 20.4249 | 24.7083 | 27.9863 | 31.2585
HaliburtonIce Accretion2095RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2095 | 17.1265 | 20.5356 | 24.8542 | 28.1605 | 31.458
HaliburtonIce Accretion2100RCP4.5 | Haliburton | Ice Accretion | RCP4.5 | 2100 | 17.2048 | 20.6462 | 25 | 28.3347 | 31.6575
HaliburtonIce Accretion2023RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2023 | 16.8569 | 20.0652 | 24.125 | 27.233 | 30.366
HaliburtonIce Accretion2025RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2025 | 16.8395 | 20.041 | 24.0917 | 27.1953 | 30.3188
HaliburtonIce Accretion2030RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2030 | 16.8221 | 20.0168 | 24.0583 | 27.1577 | 30.2715
HaliburtonIce Accretion2035RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2035 | 16.8047 | 19.9926 | 24.025 | 27.12 | 30.2242
HaliburtonIce Accretion2040RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2040 | 16.7873 | 19.9684 | 23.9917 | 27.0823 | 30.177
HaliburtonIce Accretion2045RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2045 | 16.7699 | 19.9442 | 23.9583 | 27.0447 | 30.1298
HaliburtonIce Accretion2050RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2050 | 16.749 | 19.9324 | 23.965 | 27.0635 | 30.1581
HaliburtonIce Accretion2055RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2055 | 16.7455 | 19.9449 | 24.005 | 27.12 | 30.2337
HaliburtonIce Accretion2060RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2060 | 16.7421 | 19.9573 | 24.045 | 27.1765 | 30.3093
HaliburtonIce Accretion2065RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2065 | 16.7386 | 19.9698 | 24.085 | 27.233 | 30.3849
HaliburtonIce Accretion2070RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2070 | 16.7351 | 19.9823 | 24.125 | 27.2895 | 30.4605
HaliburtonIce Accretion2075RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2075 | 16.8525 | 20.1483 | 24.3438 | 27.5508 | 30.7597
HaliburtonIce Accretion2080RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2080 | 16.9699 | 20.3143 | 24.5625 | 27.8121 | 31.059
HaliburtonIce Accretion2085RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2085 | 17.0874 | 20.4802 | 24.7812 | 28.0734 | 31.3582
HaliburtonIce Accretion2090RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2090 | 17.3034 | 20.8053 | 25.2417 | 28.6361 | 32.0145
HaliburtonIce Accretion2095RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2095 | 17.402 | 20.9644 | 25.4833 | 28.9374 | 32.3715
HaliburtonIce Accretion2100RCP6.0 | Haliburton | Ice Accretion | RCP6.0 | 2100 | 17.5005 | 21.1235 | 25.725 | 29.2387 | 32.7285
HaliburtonIce Accretion2023RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2023 | 16.8569 | 20.0652 | 24.125 | 27.233 | 30.366
HaliburtonIce Accretion2025RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2025 | 16.8221 | 20.0168 | 24.0583 | 27.1577 | 30.2715
HaliburtonIce Accretion2030RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2030 | 16.7873 | 19.9684 | 23.9917 | 27.0823 | 30.177
HaliburtonIce Accretion2035RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2035 | 16.7525 | 19.92 | 23.925 | 27.007 | 30.0825
HaliburtonIce Accretion2040RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2040 | 16.7467 | 19.9407 | 23.9917 | 27.1012 | 30.2085
HaliburtonIce Accretion2045RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2045 | 16.7409 | 19.9615 | 24.0583 | 27.1953 | 30.3345
HaliburtonIce Accretion2050RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2050 | 16.8917 | 20.2036 | 24.4167 | 27.6379 | 30.8595
HaliburtonIce Accretion2055RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2055 | 17.0482 | 20.4249 | 24.7083 | 27.9863 | 31.2585
HaliburtonIce Accretion2060RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2060 | 17.3034 | 20.8053 | 25.2417 | 28.6361 | 32.0145
HaliburtonIce Accretion2065RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2065 | 17.402 | 20.9644 | 25.4833 | 28.9374 | 32.3715
HaliburtonIce Accretion2070RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2070 | 17.373 | 20.999 | 25.6 | 29.1163 | 32.613
HaliburtonIce Accretion2075RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2075 | 17.2454 | 20.8745 | 25.475 | 28.9939 | 32.4975
HaliburtonIce Accretion2080RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2080 | 17.1178 | 20.75 | 25.35 | 28.8715 | 32.382
HaliburtonIce Accretion2085RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2085 | 16.6916 | 20.2831 | 24.8375 | 28.3065 | 31.7677
HaliburtonIce Accretion2090RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2090 | 16.2654 | 19.8163 | 24.325 | 27.7415 | 31.1535
HaliburtonIce Accretion2095RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2095 | 16.2654 | 19.8163 | 24.325 | 27.7415 | 31.1535
HaliburtonIce Accretion2100RCP8.5 | Haliburton | Ice Accretion | RCP8.5 | 2100 | 16.2654 | 19.8163 | 24.325 | 27.7415 | 31.1535
HaliburtonWind2023RCP4.5 | Haliburton | Wind | RCP4.5 | 2023 | 69.5414 | 74.9134 | 80.576 | 86.2334 | 91.884
HaliburtonWind2025RCP4.5 | Haliburton | Wind | RCP4.5 | 2025 | 69.6266 | 75.0287 | 80.728 | 86.4161 | 92.0998
HaliburtonWind2030RCP4.5 | Haliburton | Wind | RCP4.5 | 2030 | 69.7118 | 75.144 | 80.88 | 86.5987 | 92.3157
HaliburtonWind2035RCP4.5 | Haliburton | Wind | RCP4.5 | 2035 | 69.797 | 75.2593 | 81.032 | 86.7813 | 92.5315
HaliburtonWind2040RCP4.5 | Haliburton | Wind | RCP4.5 | 2040 | 69.8822 | 75.3746 | 81.184 | 86.9639 | 92.7474
HaliburtonWind2045RCP4.5 | Haliburton | Wind | RCP4.5 | 2045 | 69.9674 | 75.49 | 81.336 | 87.1465 | 92.9632
HaliburtonWind2050RCP4.5 | Haliburton | Wind | RCP4.5 | 2050 | 70.0498 | 75.5949 | 81.4672 | 87.3 | 93.1407
HaliburtonWind2055RCP4.5 | Haliburton | Wind | RCP4.5 | 2055 | 70.0471 | 75.5844 | 81.4464 | 87.2709 | 93.1024
HaliburtonWind2060RCP4.5 | Haliburton | Wind | RCP4.5 | 2060 | 70.0443 | 75.574 | 81.4256 | 87.2418 | 93.0641
HaliburtonWind2065RCP4.5 | Haliburton | Wind | RCP4.5 | 2065 | 70.0415 | 75.5636 | 81.4048 | 87.2127 | 93.0258
HaliburtonWind2070RCP4.5 | Haliburton | Wind | RCP4.5 | 2070 | 70.0388 | 75.5532 | 81.384 | 87.1836 | 92.9875
HaliburtonWind2075RCP4.5 | Haliburton | Wind | RCP4.5 | 2075 | 69.9996 | 75.5024 | 81.32 | 87.1094 | 92.9009
HaliburtonWind2080RCP4.5 | Haliburton | Wind | RCP4.5 | 2080 | 69.9605 | 75.4515 | 81.256 | 87.0352 | 92.8142
HaliburtonWind2085RCP4.5 | Haliburton | Wind | RCP4.5 | 2085 | 69.9214 | 75.4007 | 81.192 | 86.961 | 92.7276
HaliburtonWind2090RCP4.5 | Haliburton | Wind | RCP4.5 | 2090 | 69.8822 | 75.3498 | 81.128 | 86.8869 | 92.641
HaliburtonWind2095RCP4.5 | Haliburton | Wind | RCP4.5 | 2095 | 69.8431 | 75.299 | 81.064 | 86.8127 | 92.5543
HaliburtonWind2100RCP4.5 | Haliburton | Wind | RCP4.5 | 2100 | 69.8039 | 75.2482 | 81 | 86.7385 | 92.4677
HaliburtonWind2023RCP6.0 | Haliburton | Wind | RCP6.0 | 2023 | 69.5414 | 74.9134 | 80.576 | 86.2334 | 91.884
HaliburtonWind2025RCP6.0 | Haliburton | Wind | RCP6.0 | 2025 | 69.6266 | 75.0287 | 80.728 | 86.4161 | 92.0998
HaliburtonWind2030RCP6.0 | Haliburton | Wind | RCP6.0 | 2030 | 69.7118 | 75.144 | 80.88 | 86.5987 | 92.3157
HaliburtonWind2035RCP6.0 | Haliburton | Wind | RCP6.0 | 2035 | 69.797 | 75.2593 | 81.032 | 86.7813 | 92.5315
HaliburtonWind2040RCP6.0 | Haliburton | Wind | RCP6.0 | 2040 | 69.8822 | 75.3746 | 81.184 | 86.9639 | 92.7474
HaliburtonWind2045RCP6.0 | Haliburton | Wind | RCP6.0 | 2045 | 69.9674 | 75.49 | 81.336 | 87.1465 | 92.9632
HaliburtonWind2050RCP6.0 | Haliburton | Wind | RCP6.0 | 2050 | 70.0498 | 75.5949 | 81.4672 | 87.3 | 93.1407
HaliburtonWind2055RCP6.0 | Haliburton | Wind | RCP6.0 | 2055 | 70.0471 | 75.5844 | 81.4464 | 87.2709 | 93.1024
HaliburtonWind2060RCP6.0 | Haliburton | Wind | RCP6.0 | 2060 | 70.0443 | 75.574 | 81.4256 | 87.2418 | 93.0641
HaliburtonWind2065RCP6.0 | Haliburton | Wind | RCP6.0 | 2065 | 70.0415 | 75.5636 | 81.4048 | 87.2127 | 93.0258
HaliburtonWind2070RCP6.0 | Haliburton | Wind | RCP6.0 | 2070 | 70.0388 | 75.5532 | 81.384 | 87.1836 | 92.9875
HaliburtonWind2075RCP6.0 | Haliburton | Wind | RCP6.0 | 2075 | 69.9801 | 75.4769 | 81.288 | 87.0723 | 92.8576
HaliburtonWind2080RCP6.0 | Haliburton | Wind | RCP6.0 | 2080 | 69.9214 | 75.4007 | 81.192 | 86.961 | 92.7276
HaliburtonWind2085RCP6.0 | Haliburton | Wind | RCP6.0 | 2085 | 69.8626 | 75.3244 | 81.096 | 86.8498 | 92.5976
HaliburtonWind2090RCP6.0 | Haliburton | Wind | RCP6.0 | 2090 | 69.7302 | 75.1465 | 80.8613 | 86.5673 | 92.267
HaliburtonWind2095RCP6.0 | Haliburton | Wind | RCP6.0 | 2095 | 69.6566 | 75.0448 | 80.7227 | 86.3961 | 92.0664
HaliburtonWind2100RCP6.0 | Haliburton | Wind | RCP6.0 | 2100 | 69.5829 | 74.9431 | 80.584 | 86.2249 | 91.8658
HaliburtonWind2023RCP8.5 | Haliburton | Wind | RCP8.5 | 2023 | 69.5414 | 74.9134 | 80.576 | 86.2334 | 91.884
HaliburtonWind2025RCP8.5 | Haliburton | Wind | RCP8.5 | 2025 | 69.7118 | 75.144 | 80.88 | 86.5987 | 92.3157
HaliburtonWind2030RCP8.5 | Haliburton | Wind | RCP8.5 | 2030 | 69.8822 | 75.3746 | 81.184 | 86.9639 | 92.7474
HaliburtonWind2035RCP8.5 | Haliburton | Wind | RCP8.5 | 2035 | 70.0526 | 75.6053 | 81.488 | 87.3291 | 93.179
HaliburtonWind2040RCP8.5 | Haliburton | Wind | RCP8.5 | 2040 | 70.048 | 75.5879 | 81.4533 | 87.2806 | 93.1152
HaliburtonWind2045RCP8.5 | Haliburton | Wind | RCP8.5 | 2045 | 70.0434 | 75.5706 | 81.4187 | 87.2321 | 93.0514
HaliburtonWind2050RCP8.5 | Haliburton | Wind | RCP8.5 | 2050 | 69.9605 | 75.4515 | 81.256 | 87.0352 | 92.8142
HaliburtonWind2055RCP8.5 | Haliburton | Wind | RCP8.5 | 2055 | 69.8822 | 75.3498 | 81.128 | 86.8869 | 92.641
HaliburtonWind2060RCP8.5 | Haliburton | Wind | RCP8.5 | 2060 | 69.7302 | 75.1465 | 80.8613 | 86.5673 | 92.267
HaliburtonWind2065RCP8.5 | Haliburton | Wind | RCP8.5 | 2065 | 69.6566 | 75.0448 | 80.7227 | 86.3961 | 92.0664
HaliburtonWind2070RCP8.5 | Haliburton | Wind | RCP8.5 | 2070 | 69.5944 | 74.9382 | 80.5547 | 86.1764 | 91.7989
HaliburtonWind2075RCP8.5 | Haliburton | Wind | RCP8.5 | 2075 | 69.6059 | 74.9332 | 80.5253 | 86.1279 | 91.732
HaliburtonWind2080RCP8.5 | Haliburton | Wind | RCP8.5 | 2080 | 69.6174 | 74.9282 | 80.496 | 86.0794 | 91.6651
HaliburtonWind2085RCP8.5 | Haliburton | Wind | RCP8.5 | 2085 | 69.8316 | 75.1961 | 80.832 | 86.4731 | 92.1166
HaliburtonWind2090RCP8.5 | Haliburton | Wind | RCP8.5 | 2090 | 70.0457 | 75.4639 | 81.168 | 86.8669 | 92.568
HaliburtonWind2095RCP8.5 | Haliburton | Wind | RCP8.5 | 2095 | 70.0457 | 75.4639 | 81.168 | 86.8669 | 92.568
HaliburtonWind2100RCP8.5 | Haliburton | Wind | RCP8.5 | 2100 | 70.0457 | 75.4639 | 81.168 | 86.8669 | 92.568
Halton Hills (Georgetown)Ice Accretion2023RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
Halton Hills (Georgetown)Ice Accretion2025RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
Halton Hills (Georgetown)Ice Accretion2030RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
Halton Hills (Georgetown)Ice Accretion2035RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
Halton Hills (Georgetown)Ice Accretion2040RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
Halton Hills (Georgetown)Ice Accretion2045RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
Halton Hills (Georgetown)Ice Accretion2050RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
Halton Hills (Georgetown)Ice Accretion2055RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
Halton Hills (Georgetown)Ice Accretion2060RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
Halton Hills (Georgetown)Ice Accretion2065RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
Halton Hills (Georgetown)Ice Accretion2070RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
Halton Hills (Georgetown)Ice Accretion2075RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2075 | 15.5377 | 18.8894 | 23.1125 | 26.329 | 29.5313
Halton Hills (Georgetown)Ice Accretion2080RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2080 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
Halton Hills (Georgetown)Ice Accretion2085RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2085 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
Halton Hills (Georgetown)Ice Accretion2090RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2090 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
Halton Hills (Georgetown)Ice Accretion2095RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2095 | 15.3405 | 18.7511 | 23.0625 | 26.329 | 29.5942
Halton Hills (Georgetown)Ice Accretion2100RCP4.5 | Halton Hills (Georgetown) | Ice Accretion | RCP4.5 | 2100 | 15.2912 | 18.7165 | 23.05 | 26.329 | 29.61
Halton Hills (Georgetown)Ice Accretion2023RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
Halton Hills (Georgetown)Ice Accretion2025RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
Halton Hills (Georgetown)Ice Accretion2030RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
Halton Hills (Georgetown)Ice Accretion2035RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
Halton Hills (Georgetown)Ice Accretion2040RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
Halton Hills (Georgetown)Ice Accretion2045RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
Halton Hills (Georgetown)Ice Accretion2050RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
Halton Hills (Georgetown)Ice Accretion2055RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
Halton Hills (Georgetown)Ice Accretion2060RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
Halton Hills (Georgetown)Ice Accretion2065RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
Halton Hills (Georgetown)Ice Accretion2070RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
Halton Hills (Georgetown)Ice Accretion2075RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2075 | 15.513 | 18.8721 | 23.1062 | 26.329 | 29.5391
Halton Hills (Georgetown)Ice Accretion2080RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2080 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
Halton Hills (Georgetown)Ice Accretion2085RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2085 | 15.3652 | 18.7684 | 23.0688 | 26.329 | 29.5864
Halton Hills (Georgetown)Ice Accretion2090RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2090 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
Halton Hills (Georgetown)Ice Accretion2095RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2095 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
Halton Hills (Georgetown)Ice Accretion2100RCP6.0 | Halton Hills (Georgetown) | Ice Accretion | RCP6.0 | 2100 | 14.2127 | 17.596 | 21.825 | 25.0577 | 28.2555
Halton Hills (Georgetown)Ice Accretion2023RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
Halton Hills (Georgetown)Ice Accretion2025RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2025 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
Halton Hills (Georgetown)Ice Accretion2030RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2030 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
Halton Hills (Georgetown)Ice Accretion2035RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2035 | 16.6133 | 20.0652 | 24.425 | 27.7415 | 31.059
Halton Hills (Georgetown)Ice Accretion2040RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2040 | 16.2712 | 19.6848 | 23.9917 | 27.2707 | 30.5445
Halton Hills (Georgetown)Ice Accretion2045RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2045 | 15.9291 | 19.3044 | 23.5583 | 26.7998 | 30.03
Halton Hills (Georgetown)Ice Accretion2050RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2050 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
Halton Hills (Georgetown)Ice Accretion2055RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2055 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
Halton Hills (Georgetown)Ice Accretion2060RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2060 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
Halton Hills (Georgetown)Ice Accretion2065RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2065 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
Halton Hills (Georgetown)Ice Accretion2070RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2070 | 13.8125 | 17.1464 | 21.325 | 24.5022 | 27.657
Halton Hills (Georgetown)Ice Accretion2075RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2075 | 13.4124 | 16.6968 | 20.825 | 23.9466 | 27.0585
Halton Hills (Georgetown)Ice Accretion2080RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2080 | 13.0123 | 16.2473 | 20.325 | 23.391 | 26.46
Halton Hills (Georgetown)Ice Accretion2085RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2085 | 12.1338 | 15.1994 | 19.0625 | 21.9785 | 24.885
Halton Hills (Georgetown)Ice Accretion2090RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2090 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
Halton Hills (Georgetown)Ice Accretion2095RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2095 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
Halton Hills (Georgetown)Ice Accretion2100RCP8.5 | Halton Hills (Georgetown) | Ice Accretion | RCP8.5 | 2100 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
Halton Hills (Georgetown)Wind2023RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2023 | 79.8296 | 86.0306 | 92.5704 | 99.0995 | 105.6246
Halton Hills (Georgetown)Wind2025RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2025 | 79.8588 | 86.0734 | 92.6317 | 99.1767 | 105.7173
Halton Hills (Georgetown)Wind2030RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2030 | 79.8879 | 86.1161 | 92.6931 | 99.2538 | 105.8099
Halton Hills (Georgetown)Wind2035RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2035 | 79.917 | 86.1589 | 92.7544 | 99.3309 | 105.9026
Halton Hills (Georgetown)Wind2040RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2040 | 79.9462 | 86.2017 | 92.8157 | 99.408 | 105.9952
Halton Hills (Georgetown)Wind2045RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2045 | 79.9753 | 86.2445 | 92.8771 | 99.4851 | 106.0879
Halton Hills (Georgetown)Wind2050RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2050 | 80.068 | 86.3643 | 93.0322 | 99.6705 | 106.3043
Halton Hills (Georgetown)Wind2055RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2055 | 80.1315 | 86.4413 | 93.1261 | 99.7788 | 106.428
Halton Hills (Georgetown)Wind2060RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2060 | 80.1951 | 86.5183 | 93.2199 | 99.8871 | 106.5518
Halton Hills (Georgetown)Wind2065RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2065 | 80.2586 | 86.5953 | 93.3138 | 99.9954 | 106.6755
Halton Hills (Georgetown)Wind2070RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2070 | 80.3222 | 86.6723 | 93.4076 | 100.1036 | 106.7993
Halton Hills (Georgetown)Wind2075RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2075 | 80.4096 | 86.7949 | 93.5747 | 100.3071 | 107.0405
Halton Hills (Georgetown)Wind2080RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2080 | 80.4969 | 86.9176 | 93.7419 | 100.5105 | 107.2818
Halton Hills (Georgetown)Wind2085RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2085 | 80.5843 | 87.0402 | 93.909 | 100.714 | 107.523
Halton Hills (Georgetown)Wind2090RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2090 | 80.6717 | 87.1628 | 94.0761 | 100.9174 | 107.7642
Halton Hills (Georgetown)Wind2095RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2095 | 80.7591 | 87.2855 | 94.2433 | 101.1208 | 108.0054
Halton Hills (Georgetown)Wind2100RCP4.5 | Halton Hills (Georgetown) | Wind | RCP4.5 | 2100 | 80.8465 | 87.4081 | 94.4104 | 101.3243 | 108.2466
Halton Hills (Georgetown)Wind2023RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2023 | 79.8296 | 86.0306 | 92.5704 | 99.0995 | 105.6246
Halton Hills (Georgetown)Wind2025RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2025 | 79.8588 | 86.0734 | 92.6317 | 99.1767 | 105.7173
Halton Hills (Georgetown)Wind2030RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2030 | 79.8879 | 86.1161 | 92.6931 | 99.2538 | 105.8099
Halton Hills (Georgetown)Wind2035RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2035 | 79.917 | 86.1589 | 92.7544 | 99.3309 | 105.9026
Halton Hills (Georgetown)Wind2040RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2040 | 79.9462 | 86.2017 | 92.8157 | 99.408 | 105.9952
Halton Hills (Georgetown)Wind2045RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2045 | 79.9753 | 86.2445 | 92.8771 | 99.4851 | 106.0879
Halton Hills (Georgetown)Wind2050RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2050 | 80.068 | 86.3643 | 93.0322 | 99.6705 | 106.3043
Halton Hills (Georgetown)Wind2055RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2055 | 80.1315 | 86.4413 | 93.1261 | 99.7788 | 106.428
Halton Hills (Georgetown)Wind2060RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2060 | 80.1951 | 86.5183 | 93.2199 | 99.8871 | 106.5518
Halton Hills (Georgetown)Wind2065RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2065 | 80.2586 | 86.5953 | 93.3138 | 99.9954 | 106.6755
Halton Hills (Georgetown)Wind2070RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2070 | 80.3222 | 86.6723 | 93.4076 | 100.1036 | 106.7993
Halton Hills (Georgetown)Wind2075RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2075 | 80.4532 | 86.8562 | 93.6583 | 100.4088 | 107.1611
Halton Hills (Georgetown)Wind2080RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2080 | 80.5843 | 87.0402 | 93.909 | 100.714 | 107.523
Halton Hills (Georgetown)Wind2085RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2085 | 80.7154 | 87.2241 | 94.1597 | 101.0191 | 107.8848
Halton Hills (Georgetown)Wind2090RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2090 | 81.1219 | 87.7617 | 94.8612 | 101.8591 | 108.8689
Halton Hills (Georgetown)Wind2095RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2095 | 81.3973 | 88.1154 | 95.312 | 102.394 | 109.4912
Halton Hills (Georgetown)Wind2100RCP6.0 | Halton Hills (Georgetown) | Wind | RCP6.0 | 2100 | 81.6727 | 88.469 | 95.7628 | 102.9289 | 110.1135
Halton Hills (Georgetown)Wind2023RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2023 | 79.8296 | 86.0306 | 92.5704 | 99.0995 | 105.6246
Halton Hills (Georgetown)Wind2025RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2025 | 79.8879 | 86.1161 | 92.6931 | 99.2538 | 105.8099
Halton Hills (Georgetown)Wind2030RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2030 | 79.9462 | 86.2017 | 92.8157 | 99.408 | 105.9952
Halton Hills (Georgetown)Wind2035RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2035 | 80.0044 | 86.2873 | 92.9384 | 99.5622 | 106.1805
Halton Hills (Georgetown)Wind2040RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2040 | 80.1103 | 86.4156 | 93.0948 | 99.7427 | 106.3868
Halton Hills (Georgetown)Wind2045RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2045 | 80.2163 | 86.5439 | 93.2512 | 99.9232 | 106.593
Halton Hills (Georgetown)Wind2050RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2050 | 80.4969 | 86.9176 | 93.7419 | 100.5105 | 107.2818
Halton Hills (Georgetown)Wind2055RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2055 | 80.6717 | 87.1628 | 94.0761 | 100.9174 | 107.7642
Halton Hills (Georgetown)Wind2060RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2060 | 81.1219 | 87.7617 | 94.8612 | 101.8591 | 108.8689
Halton Hills (Georgetown)Wind2065RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2065 | 81.3973 | 88.1154 | 95.312 | 102.394 | 109.4912
Halton Hills (Georgetown)Wind2070RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2070 | 81.8289 | 88.6943 | 96.0756 | 103.3128 | 110.5715
Halton Hills (Georgetown)Wind2075RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2075 | 81.9851 | 88.9197 | 96.3884 | 103.6967 | 111.0295
Halton Hills (Georgetown)Wind2080RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2080 | 82.1414 | 89.145 | 96.7012 | 104.0806 | 111.4874
Halton Hills (Georgetown)Wind2085RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2085 | 82.3916 | 89.4701 | 97.1198 | 104.5827 | 112.0748
Halton Hills (Georgetown)Wind2090RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2090 | 82.6418 | 89.7952 | 97.5384 | 105.0847 | 112.6621
Halton Hills (Georgetown)Wind2095RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2095 | 82.6418 | 89.7952 | 97.5384 | 105.0847 | 112.6621
Halton Hills (Georgetown)Wind2100RCP8.5 | Halton Hills (Georgetown) | Wind | RCP8.5 | 2100 | 82.6418 | 89.7952 | 97.5384 | 105.0847 | 112.6621
HamiltonIce Accretion2023RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2023 | 21.9108 | 26.2678 | 31.808 | 36.0154 | 40.2394
HamiltonIce Accretion2025RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2025 | 21.7995 | 26.1483 | 31.6747 | 35.8767 | 40.0915
HamiltonIce Accretion2030RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2030 | 21.6881 | 26.0288 | 31.5413 | 35.7381 | 39.9437
HamiltonIce Accretion2035RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2035 | 21.5768 | 25.9093 | 31.408 | 35.5995 | 39.7958
HamiltonIce Accretion2040RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2040 | 21.4655 | 25.7898 | 31.2747 | 35.4609 | 39.648
HamiltonIce Accretion2045RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2045 | 21.3541 | 25.6702 | 31.1413 | 35.3223 | 39.5002
HamiltonIce Accretion2050RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2050 | 20.9444 | 25.2267 | 30.656 | 34.8004 | 38.9411
HamiltonIce Accretion2055RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2055 | 20.646 | 24.9027 | 30.304 | 34.4171 | 38.5298
HamiltonIce Accretion2060RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2060 | 20.3477 | 24.5786 | 29.952 | 34.0338 | 38.1185
HamiltonIce Accretion2065RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2065 | 20.0493 | 24.2546 | 29.6 | 33.6505 | 37.7073
HamiltonIce Accretion2070RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2070 | 19.7509 | 23.9306 | 29.248 | 33.2672 | 37.296
HamiltonIce Accretion2075RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2075 | 19.6544 | 23.8465 | 29.1733 | 33.2009 | 37.2288
HamiltonIce Accretion2080RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2080 | 19.5579 | 23.7623 | 29.0987 | 33.1346 | 37.1616
HamiltonIce Accretion2085RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2085 | 19.4614 | 23.6782 | 29.024 | 33.0683 | 37.0944
HamiltonIce Accretion2090RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2090 | 19.3649 | 23.5941 | 28.9493 | 33.002 | 37.0272
HamiltonIce Accretion2095RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2095 | 19.2684 | 23.51 | 28.8747 | 32.9357 | 36.96
HamiltonIce Accretion2100RCP4.5 | Hamilton | Ice Accretion | RCP4.5 | 2100 | 19.172 | 23.4259 | 28.8 | 32.8694 | 36.8928
HamiltonIce Accretion2023RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2023 | 21.9108 | 26.2678 | 31.808 | 36.0154 | 40.2394
HamiltonIce Accretion2025RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2025 | 21.7995 | 26.1483 | 31.6747 | 35.8767 | 40.0915
HamiltonIce Accretion2030RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2030 | 21.6881 | 26.0288 | 31.5413 | 35.7381 | 39.9437
HamiltonIce Accretion2035RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2035 | 21.5768 | 25.9093 | 31.408 | 35.5995 | 39.7958
HamiltonIce Accretion2040RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2040 | 21.4655 | 25.7898 | 31.2747 | 35.4609 | 39.648
HamiltonIce Accretion2045RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2045 | 21.3541 | 25.6702 | 31.1413 | 35.3223 | 39.5002
HamiltonIce Accretion2050RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2050 | 20.9444 | 25.2267 | 30.656 | 34.8004 | 38.9411
HamiltonIce Accretion2055RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2055 | 20.646 | 24.9027 | 30.304 | 34.4171 | 38.5298
HamiltonIce Accretion2060RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2060 | 20.3477 | 24.5786 | 29.952 | 34.0338 | 38.1185
HamiltonIce Accretion2065RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2065 | 20.0493 | 24.2546 | 29.6 | 33.6505 | 37.7073
HamiltonIce Accretion2070RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2070 | 19.7509 | 23.9306 | 29.248 | 33.2672 | 37.296
HamiltonIce Accretion2075RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2075 | 19.6062 | 23.8044 | 29.136 | 33.1678 | 37.1952
HamiltonIce Accretion2080RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2080 | 19.4614 | 23.6782 | 29.024 | 33.0683 | 37.0944
HamiltonIce Accretion2085RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2085 | 19.3167 | 23.5521 | 28.912 | 32.9689 | 36.9936
HamiltonIce Accretion2090RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2090 | 18.5411 | 22.7088 | 27.968 | 31.9534 | 35.8982
HamiltonIce Accretion2095RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2095 | 17.9102 | 21.9917 | 27.136 | 31.0373 | 34.9037
HamiltonIce Accretion2100RCP6.0 | Hamilton | Ice Accretion | RCP6.0 | 2100 | 17.2793 | 21.2746 | 26.304 | 30.1213 | 33.9091
HamiltonIce Accretion2023RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2023 | 21.9108 | 26.2678 | 31.808 | 36.0154 | 40.2394
HamiltonIce Accretion2025RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2025 | 21.6881 | 26.0288 | 31.5413 | 35.7381 | 39.9437
HamiltonIce Accretion2030RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2030 | 21.4655 | 25.7898 | 31.2747 | 35.4609 | 39.648
HamiltonIce Accretion2035RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2035 | 21.2428 | 25.5507 | 31.008 | 35.1837 | 39.3523
HamiltonIce Accretion2040RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2040 | 20.7455 | 25.0107 | 30.4213 | 34.5449 | 38.6669
HamiltonIce Accretion2045RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2045 | 20.2482 | 24.4706 | 29.8347 | 33.906 | 37.9814
HamiltonIce Accretion2050RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2050 | 19.5579 | 23.7623 | 29.0987 | 33.1346 | 37.1616
HamiltonIce Accretion2055RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2055 | 19.3649 | 23.5941 | 28.9493 | 33.002 | 37.0272
HamiltonIce Accretion2060RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2060 | 18.5411 | 22.7088 | 27.968 | 31.9534 | 35.8982
HamiltonIce Accretion2065RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2065 | 17.9102 | 21.9917 | 27.136 | 31.0373 | 34.9037
HamiltonIce Accretion2070RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2070 | 16.871 | 20.823 | 25.8027 | 29.5668 | 33.3178
HamiltonIce Accretion2075RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2075 | 16.4628 | 20.3715 | 25.3013 | 29.0124 | 32.7264
HamiltonIce Accretion2080RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2080 | 16.0546 | 19.92 | 24.8 | 28.4579 | 32.135
HamiltonIce Accretion2085RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2085 | 14.9635 | 18.6451 | 23.248 | 26.7222 | 30.1997
HamiltonIce Accretion2090RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2090 | 13.8724 | 17.3702 | 21.696 | 24.9866 | 28.2643
HamiltonIce Accretion2095RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2095 | 13.8724 | 17.3702 | 21.696 | 24.9866 | 28.2643
HamiltonIce Accretion2100RCP8.5 | Hamilton | Ice Accretion | RCP8.5 | 2100 | 13.8724 | 17.3702 | 21.696 | 24.9866 | 28.2643
HamiltonWind2023RCP4.5 | Hamilton | Wind | RCP4.5 | 2023 | 83.2839 | 89.7889 | 96.6624 | 103.5109 | 110.3593
HamiltonWind2025RCP4.5 | Hamilton | Wind | RCP4.5 | 2025 | 83.3019 | 89.8201 | 96.7104 | 103.5726 | 110.4359
HamiltonWind2030RCP4.5 | Hamilton | Wind | RCP4.5 | 2030 | 83.3198 | 89.8514 | 96.7584 | 103.6342 | 110.5125
HamiltonWind2035RCP4.5 | Hamilton | Wind | RCP4.5 | 2035 | 83.3378 | 89.8826 | 96.8064 | 103.6958 | 110.5891
HamiltonWind2040RCP4.5 | Hamilton | Wind | RCP4.5 | 2040 | 83.3558 | 89.9139 | 96.8544 | 103.7575 | 110.6657
HamiltonWind2045RCP4.5 | Hamilton | Wind | RCP4.5 | 2045 | 83.3737 | 89.9451 | 96.9024 | 103.8191 | 110.7423
HamiltonWind2050RCP4.5 | Hamilton | Wind | RCP4.5 | 2050 | 83.4613 | 90.0674 | 97.0675 | 104.0225 | 110.9853
HamiltonWind2055RCP4.5 | Hamilton | Wind | RCP4.5 | 2055 | 83.5309 | 90.1585 | 97.1846 | 104.1642 | 111.1516
HamiltonWind2060RCP4.5 | Hamilton | Wind | RCP4.5 | 2060 | 83.6006 | 90.2496 | 97.3018 | 104.306 | 111.318
HamiltonWind2065RCP4.5 | Hamilton | Wind | RCP4.5 | 2065 | 83.6702 | 90.3406 | 97.4189 | 104.4478 | 111.4843
HamiltonWind2070RCP4.5 | Hamilton | Wind | RCP4.5 | 2070 | 83.7398 | 90.4317 | 97.536 | 104.5895 | 111.6507
HamiltonWind2075RCP4.5 | Hamilton | Wind | RCP4.5 | 2075 | 83.8435 | 90.5701 | 97.7168 | 104.8052 | 111.9042
HamiltonWind2080RCP4.5 | Hamilton | Wind | RCP4.5 | 2080 | 83.9471 | 90.7085 | 97.8976 | 105.0209 | 112.1578
HamiltonWind2085RCP4.5 | Hamilton | Wind | RCP4.5 | 2085 | 84.0507 | 90.8469 | 98.0784 | 105.2366 | 112.4113
HamiltonWind2090RCP4.5 | Hamilton | Wind | RCP4.5 | 2090 | 84.1543 | 90.9852 | 98.2592 | 105.4524 | 112.6648
HamiltonWind2095RCP4.5 | Hamilton | Wind | RCP4.5 | 2095 | 84.2579 | 91.1236 | 98.44 | 105.6681 | 112.9184
HamiltonWind2100RCP4.5 | Hamilton | Wind | RCP4.5 | 2100 | 84.3615 | 91.262 | 98.6208 | 105.8838 | 113.1719
HamiltonWind2023RCP6.0 | Hamilton | Wind | RCP6.0 | 2023 | 83.2839 | 89.7889 | 96.6624 | 103.5109 | 110.3593
HamiltonWind2025RCP6.0 | Hamilton | Wind | RCP6.0 | 2025 | 83.3019 | 89.8201 | 96.7104 | 103.5726 | 110.4359
HamiltonWind2030RCP6.0 | Hamilton | Wind | RCP6.0 | 2030 | 83.3198 | 89.8514 | 96.7584 | 103.6342 | 110.5125
HamiltonWind2035RCP6.0 | Hamilton | Wind | RCP6.0 | 2035 | 83.3378 | 89.8826 | 96.8064 | 103.6958 | 110.5891
HamiltonWind2040RCP6.0 | Hamilton | Wind | RCP6.0 | 2040 | 83.3558 | 89.9139 | 96.8544 | 103.7575 | 110.6657
HamiltonWind2045RCP6.0 | Hamilton | Wind | RCP6.0 | 2045 | 83.3737 | 89.9451 | 96.9024 | 103.8191 | 110.7423
HamiltonWind2050RCP6.0 | Hamilton | Wind | RCP6.0 | 2050 | 83.4613 | 90.0674 | 97.0675 | 104.0225 | 110.9853
HamiltonWind2055RCP6.0 | Hamilton | Wind | RCP6.0 | 2055 | 83.5309 | 90.1585 | 97.1846 | 104.1642 | 111.1516
HamiltonWind2060RCP6.0 | Hamilton | Wind | RCP6.0 | 2060 | 83.6006 | 90.2496 | 97.3018 | 104.306 | 111.318
HamiltonWind2065RCP6.0 | Hamilton | Wind | RCP6.0 | 2065 | 83.6702 | 90.3406 | 97.4189 | 104.4478 | 111.4843
HamiltonWind2070RCP6.0 | Hamilton | Wind | RCP6.0 | 2070 | 83.7398 | 90.4317 | 97.536 | 104.5895 | 111.6507
HamiltonWind2075RCP6.0 | Hamilton | Wind | RCP6.0 | 2075 | 83.8953 | 90.6393 | 97.8072 | 104.9131 | 112.031
HamiltonWind2080RCP6.0 | Hamilton | Wind | RCP6.0 | 2080 | 84.0507 | 90.8469 | 98.0784 | 105.2366 | 112.4113
HamiltonWind2085RCP6.0 | Hamilton | Wind | RCP6.0 | 2085 | 84.2061 | 91.0544 | 98.3496 | 105.5602 | 112.7916
HamiltonWind2090RCP6.0 | Hamilton | Wind | RCP6.0 | 2090 | 84.6683 | 91.6519 | 99.12 | 106.4761 | 113.8577
HamiltonWind2095RCP6.0 | Hamilton | Wind | RCP6.0 | 2095 | 84.975 | 92.0417 | 99.6192 | 107.0685 | 114.5436
HamiltonWind2100RCP6.0 | Hamilton | Wind | RCP6.0 | 2100 | 85.2817 | 92.4316 | 100.1184 | 107.6608 | 115.2294
HamiltonWind2023RCP8.5 | Hamilton | Wind | RCP8.5 | 2023 | 83.2839 | 89.7889 | 96.6624 | 103.5109 | 110.3593
HamiltonWind2025RCP8.5 | Hamilton | Wind | RCP8.5 | 2025 | 83.3198 | 89.8514 | 96.7584 | 103.6342 | 110.5125
HamiltonWind2030RCP8.5 | Hamilton | Wind | RCP8.5 | 2030 | 83.3558 | 89.9139 | 96.8544 | 103.7575 | 110.6657
HamiltonWind2035RCP8.5 | Hamilton | Wind | RCP8.5 | 2035 | 83.3917 | 89.9764 | 96.9504 | 103.8807 | 110.8189
HamiltonWind2040RCP8.5 | Hamilton | Wind | RCP8.5 | 2040 | 83.5077 | 90.1282 | 97.1456 | 104.117 | 111.0962
HamiltonWind2045RCP8.5 | Hamilton | Wind | RCP8.5 | 2045 | 83.6238 | 90.2799 | 97.3408 | 104.3532 | 111.3734
HamiltonWind2050RCP8.5 | Hamilton | Wind | RCP8.5 | 2050 | 83.9471 | 90.7085 | 97.8976 | 105.0209 | 112.1578
HamiltonWind2055RCP8.5 | Hamilton | Wind | RCP8.5 | 2055 | 84.1543 | 90.9852 | 98.2592 | 105.4524 | 112.6648
HamiltonWind2060RCP8.5 | Hamilton | Wind | RCP8.5 | 2060 | 84.6683 | 91.6519 | 99.12 | 106.4761 | 113.8577
HamiltonWind2065RCP8.5 | Hamilton | Wind | RCP8.5 | 2065 | 84.975 | 92.0417 | 99.6192 | 107.0685 | 114.5436
HamiltonWind2070RCP8.5 | Hamilton | Wind | RCP8.5 | 2070 | 85.453 | 92.6697 | 100.4448 | 108.058 | 115.7
HamiltonWind2075RCP8.5 | Hamilton | Wind | RCP8.5 | 2075 | 85.6243 | 92.9077 | 100.7712 | 108.4552 | 116.1706
HamiltonWind2080RCP8.5 | Hamilton | Wind | RCP8.5 | 2080 | 85.7956 | 93.1458 | 101.0976 | 108.8524 | 116.6412
HamiltonWind2085RCP8.5 | Hamilton | Wind | RCP8.5 | 2085 | 86.0567 | 93.4985 | 101.5584 | 109.4122 | 117.2978
HamiltonWind2090RCP8.5 | Hamilton | Wind | RCP8.5 | 2090 | 86.3178 | 93.8511 | 102.0192 | 109.972 | 117.9544
HamiltonWind2095RCP8.5 | Hamilton | Wind | RCP8.5 | 2095 | 86.3178 | 93.8511 | 102.0192 | 109.972 | 117.9544
HamiltonWind2100RCP8.5 | Hamilton | Wind | RCP8.5 | 2100 | 86.3178 | 93.8511 | 102.0192 | 109.972 | 117.9544
HanoverIce Accretion2023RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2023 | 15.2933 | 18.333 | 22.198 | 25.1335 | 28.0804
HanoverIce Accretion2025RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2025 | 15.2984 | 18.3543 | 22.231 | 25.179 | 28.1404
HanoverIce Accretion2030RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2030 | 15.3035 | 18.3756 | 22.264 | 25.2246 | 28.2005
HanoverIce Accretion2035RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2035 | 15.3086 | 18.3969 | 22.297 | 25.2702 | 28.2605
HanoverIce Accretion2040RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2040 | 15.3137 | 18.4183 | 22.33 | 25.3158 | 28.3206
HanoverIce Accretion2045RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2045 | 15.3188 | 18.4396 | 22.363 | 25.3613 | 28.3807
HanoverIce Accretion2050RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2050 | 15.3178 | 18.4718 | 22.4356 | 25.4666 | 28.5183
HanoverIce Accretion2055RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2055 | 15.3117 | 18.4828 | 22.4752 | 25.5262 | 28.596
HanoverIce Accretion2060RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2060 | 15.3056 | 18.4937 | 22.5148 | 25.5859 | 28.6736
HanoverIce Accretion2065RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2065 | 15.2994 | 18.5047 | 22.5544 | 25.6456 | 28.7512
HanoverIce Accretion2070RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2070 | 15.2933 | 18.5156 | 22.594 | 25.7052 | 28.8288
HanoverIce Accretion2075RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2075 | 15.227 | 18.4609 | 22.5573 | 25.6762 | 28.8103
HanoverIce Accretion2080RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2080 | 15.1606 | 18.4061 | 22.5207 | 25.6472 | 28.7918
HanoverIce Accretion2085RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2085 | 15.0943 | 18.3513 | 22.484 | 25.6182 | 28.7734
HanoverIce Accretion2090RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2090 | 15.028 | 18.2965 | 22.4473 | 25.5892 | 28.7549
HanoverIce Accretion2095RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2095 | 14.9616 | 18.2417 | 22.4107 | 25.5602 | 28.7364
HanoverIce Accretion2100RCP4.5 | Hanover | Ice Accretion | RCP4.5 | 2100 | 14.8953 | 18.187 | 22.374 | 25.5312 | 28.7179
HanoverIce Accretion2023RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2023 | 15.2933 | 18.333 | 22.198 | 25.1335 | 28.0804
HanoverIce Accretion2025RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2025 | 15.2984 | 18.3543 | 22.231 | 25.179 | 28.1404
HanoverIce Accretion2030RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2030 | 15.3035 | 18.3756 | 22.264 | 25.2246 | 28.2005
HanoverIce Accretion2035RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2035 | 15.3086 | 18.3969 | 22.297 | 25.2702 | 28.2605
HanoverIce Accretion2040RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2040 | 15.3137 | 18.4183 | 22.33 | 25.3158 | 28.3206
HanoverIce Accretion2045RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2045 | 15.3188 | 18.4396 | 22.363 | 25.3613 | 28.3807
HanoverIce Accretion2050RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2050 | 15.3178 | 18.4718 | 22.4356 | 25.4666 | 28.5183
HanoverIce Accretion2055RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2055 | 15.3117 | 18.4828 | 22.4752 | 25.5262 | 28.596
HanoverIce Accretion2060RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2060 | 15.3056 | 18.4937 | 22.5148 | 25.5859 | 28.6736
HanoverIce Accretion2065RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2065 | 15.2994 | 18.5047 | 22.5544 | 25.6456 | 28.7512
HanoverIce Accretion2070RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2070 | 15.2933 | 18.5156 | 22.594 | 25.7052 | 28.8288
HanoverIce Accretion2075RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2075 | 15.1938 | 18.4335 | 22.539 | 25.6617 | 28.8011
HanoverIce Accretion2080RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2080 | 15.0943 | 18.3513 | 22.484 | 25.6182 | 28.7734
HanoverIce Accretion2085RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2085 | 14.9948 | 18.2691 | 22.429 | 25.5747 | 28.7456
HanoverIce Accretion2090RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2090 | 14.6401 | 17.9191 | 22.0733 | 25.2163 | 28.376
HanoverIce Accretion2095RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2095 | 14.385 | 17.6513 | 21.7727 | 24.9014 | 28.0342
HanoverIce Accretion2100RCP6.0 | Hanover | Ice Accretion | RCP6.0 | 2100 | 14.1299 | 17.3835 | 21.472 | 24.5865 | 27.6923
HanoverIce Accretion2023RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2023 | 15.2933 | 18.333 | 22.198 | 25.1335 | 28.0804
HanoverIce Accretion2025RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2025 | 15.3035 | 18.3756 | 22.264 | 25.2246 | 28.2005
HanoverIce Accretion2030RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2030 | 15.3137 | 18.4183 | 22.33 | 25.3158 | 28.3206
HanoverIce Accretion2035RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2035 | 15.3239 | 18.4609 | 22.396 | 25.4069 | 28.4407
HanoverIce Accretion2040RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2040 | 15.3137 | 18.4791 | 22.462 | 25.5064 | 28.5701
HanoverIce Accretion2045RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2045 | 15.3035 | 18.4974 | 22.528 | 25.6058 | 28.6994
HanoverIce Accretion2050RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2050 | 15.1606 | 18.4061 | 22.5207 | 25.6472 | 28.7918
HanoverIce Accretion2055RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2055 | 15.028 | 18.2965 | 22.4473 | 25.5892 | 28.7549
HanoverIce Accretion2060RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2060 | 14.6401 | 17.9191 | 22.0733 | 25.2163 | 28.376
HanoverIce Accretion2065RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2065 | 14.385 | 17.6513 | 21.7727 | 24.9014 | 28.0342
HanoverIce Accretion2070RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2070 | 13.7114 | 16.9088 | 20.9367 | 23.9982 | 27.0547
HanoverIce Accretion2075RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2075 | 13.293 | 16.434 | 20.4013 | 23.4098 | 26.4172
HanoverIce Accretion2080RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2080 | 12.8745 | 15.9592 | 19.866 | 22.8215 | 25.7796
HanoverIce Accretion2085RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2085 | 12.4536 | 15.4936 | 19.338 | 22.2497 | 25.1698
HanoverIce Accretion2090RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2090 | 12.0326 | 15.028 | 18.81 | 21.6779 | 24.5599
HanoverIce Accretion2095RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2095 | 12.0326 | 15.028 | 18.81 | 21.6779 | 24.5599
HanoverIce Accretion2100RCP8.5 | Hanover | Ice Accretion | RCP8.5 | 2100 | 12.0326 | 15.028 | 18.81 | 21.6779 | 24.5599
HanoverWind2023RCP4.5 | Hanover | Wind | RCP4.5 | 2023 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2506
HanoverWind2025RCP4.5 | Hanover | Wind | RCP4.5 | 2025 | 85.4139 | 92.1425 | 99.2626 | 106.3385 | 113.42
HanoverWind2030RCP4.5 | Hanover | Wind | RCP4.5 | 2030 | 85.4957 | 92.2428 | 99.3883 | 106.4853 | 113.5894
HanoverWind2035RCP4.5 | Hanover | Wind | RCP4.5 | 2035 | 85.5775 | 92.343 | 99.5141 | 106.6321 | 113.7589
HanoverWind2040RCP4.5 | Hanover | Wind | RCP4.5 | 2040 | 85.6593 | 92.4433 | 99.6399 | 106.7789 | 113.9283
HanoverWind2045RCP4.5 | Hanover | Wind | RCP4.5 | 2045 | 85.7411 | 92.5436 | 99.7656 | 106.9257 | 114.0978
HanoverWind2050RCP4.5 | Hanover | Wind | RCP4.5 | 2050 | 85.8364 | 92.6566 | 99.9012 | 107.0809 | 114.2739
HanoverWind2055RCP4.5 | Hanover | Wind | RCP4.5 | 2055 | 85.85 | 92.6693 | 99.911 | 107.0893 | 114.2806
HanoverWind2060RCP4.5 | Hanover | Wind | RCP4.5 | 2060 | 85.8635 | 92.6821 | 99.9208 | 107.0977 | 114.2873
HanoverWind2065RCP4.5 | Hanover | Wind | RCP4.5 | 2065 | 85.8771 | 92.6948 | 99.9306 | 107.1061 | 114.294
HanoverWind2070RCP4.5 | Hanover | Wind | RCP4.5 | 2070 | 85.8906 | 92.7076 | 99.9404 | 107.1145 | 114.3007
HanoverWind2075RCP4.5 | Hanover | Wind | RCP4.5 | 2075 | 85.9738 | 92.8155 | 100.0792 | 107.2805 | 114.4925
HanoverWind2080RCP4.5 | Hanover | Wind | RCP4.5 | 2080 | 86.057 | 92.9233 | 100.2181 | 107.4465 | 114.6843
HanoverWind2085RCP4.5 | Hanover | Wind | RCP4.5 | 2085 | 86.1402 | 93.0312 | 100.3569 | 107.6126 | 114.8761
HanoverWind2090RCP4.5 | Hanover | Wind | RCP4.5 | 2090 | 86.2234 | 93.139 | 100.4957 | 107.7786 | 115.0679
HanoverWind2095RCP4.5 | Hanover | Wind | RCP4.5 | 2095 | 86.3067 | 93.2469 | 100.6346 | 107.9446 | 115.2597
HanoverWind2100RCP4.5 | Hanover | Wind | RCP4.5 | 2100 | 86.3899 | 93.3547 | 100.7734 | 108.1107 | 115.4514
HanoverWind2023RCP6.0 | Hanover | Wind | RCP6.0 | 2023 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2506
HanoverWind2025RCP6.0 | Hanover | Wind | RCP6.0 | 2025 | 85.4139 | 92.1425 | 99.2626 | 106.3385 | 113.42
HanoverWind2030RCP6.0 | Hanover | Wind | RCP6.0 | 2030 | 85.4957 | 92.2428 | 99.3883 | 106.4853 | 113.5894
HanoverWind2035RCP6.0 | Hanover | Wind | RCP6.0 | 2035 | 85.5775 | 92.343 | 99.5141 | 106.6321 | 113.7589
HanoverWind2040RCP6.0 | Hanover | Wind | RCP6.0 | 2040 | 85.6593 | 92.4433 | 99.6399 | 106.7789 | 113.9283
HanoverWind2045RCP6.0 | Hanover | Wind | RCP6.0 | 2045 | 85.7411 | 92.5436 | 99.7656 | 106.9257 | 114.0978
HanoverWind2050RCP6.0 | Hanover | Wind | RCP6.0 | 2050 | 85.8364 | 92.6566 | 99.9012 | 107.0809 | 114.2739
HanoverWind2055RCP6.0 | Hanover | Wind | RCP6.0 | 2055 | 85.85 | 92.6693 | 99.911 | 107.0893 | 114.2806
HanoverWind2060RCP6.0 | Hanover | Wind | RCP6.0 | 2060 | 85.8635 | 92.6821 | 99.9208 | 107.0977 | 114.2873
HanoverWind2065RCP6.0 | Hanover | Wind | RCP6.0 | 2065 | 85.8771 | 92.6948 | 99.9306 | 107.1061 | 114.294
HanoverWind2070RCP6.0 | Hanover | Wind | RCP6.0 | 2070 | 85.8906 | 92.7076 | 99.9404 | 107.1145 | 114.3007
HanoverWind2075RCP6.0 | Hanover | Wind | RCP6.0 | 2075 | 86.0154 | 92.8694 | 100.1487 | 107.3635 | 114.5884
HanoverWind2080RCP6.0 | Hanover | Wind | RCP6.0 | 2080 | 86.1402 | 93.0312 | 100.3569 | 107.6126 | 114.8761
HanoverWind2085RCP6.0 | Hanover | Wind | RCP6.0 | 2085 | 86.265 | 93.1929 | 100.5652 | 107.8616 | 115.1638
HanoverWind2090RCP6.0 | Hanover | Wind | RCP6.0 | 2090 | 86.8017 | 93.8712 | 101.4169 | 108.8657 | 116.3229
HanoverWind2095RCP6.0 | Hanover | Wind | RCP6.0 | 2095 | 87.2135 | 94.3876 | 102.0605 | 109.6206 | 117.1943
HanoverWind2100RCP6.0 | Hanover | Wind | RCP6.0 | 2100 | 87.6253 | 94.9041 | 102.704 | 110.3756 | 118.0657
HanoverWind2023RCP8.5 | Hanover | Wind | RCP8.5 | 2023 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2506
HanoverWind2025RCP8.5 | Hanover | Wind | RCP8.5 | 2025 | 85.4957 | 92.2428 | 99.3883 | 106.4853 | 113.5894
HanoverWind2030RCP8.5 | Hanover | Wind | RCP8.5 | 2030 | 85.6593 | 92.4433 | 99.6399 | 106.7789 | 113.9283
HanoverWind2035RCP8.5 | Hanover | Wind | RCP8.5 | 2035 | 85.8229 | 92.6438 | 99.8914 | 107.0725 | 114.2672
HanoverWind2040RCP8.5 | Hanover | Wind | RCP8.5 | 2040 | 85.8455 | 92.6651 | 99.9077 | 107.0865 | 114.2784
HanoverWind2045RCP8.5 | Hanover | Wind | RCP8.5 | 2045 | 85.868 | 92.6863 | 99.9241 | 107.1005 | 114.2896
HanoverWind2050RCP8.5 | Hanover | Wind | RCP8.5 | 2050 | 86.057 | 92.9233 | 100.2181 | 107.4465 | 114.6843
HanoverWind2055RCP8.5 | Hanover | Wind | RCP8.5 | 2055 | 86.2234 | 93.139 | 100.4957 | 107.7786 | 115.0679
HanoverWind2060RCP8.5 | Hanover | Wind | RCP8.5 | 2060 | 86.8017 | 93.8712 | 101.4169 | 108.8657 | 116.3229
HanoverWind2065RCP8.5 | Hanover | Wind | RCP8.5 | 2065 | 87.2135 | 94.3876 | 102.0605 | 109.6206 | 117.1943
HanoverWind2070RCP8.5 | Hanover | Wind | RCP8.5 | 2070 | 87.8397 | 95.1653 | 103.0241 | 110.7461 | 118.4865
HanoverWind2075RCP8.5 | Hanover | Wind | RCP8.5 | 2075 | 88.0541 | 95.4266 | 103.3443 | 111.1166 | 118.9073
HanoverWind2080RCP8.5 | Hanover | Wind | RCP8.5 | 2080 | 88.2685 | 95.6879 | 103.6644 | 111.4872 | 119.3281
HanoverWind2085RCP8.5 | Hanover | Wind | RCP8.5 | 2085 | 88.2896 | 95.697 | 103.6644 | 111.4714 | 119.3058
HanoverWind2090RCP8.5 | Hanover | Wind | RCP8.5 | 2090 | 88.3108 | 95.7061 | 103.6644 | 111.4557 | 119.2834
HanoverWind2095RCP8.5 | Hanover | Wind | RCP8.5 | 2095 | 88.3108 | 95.7061 | 103.6644 | 111.4557 | 119.2834
HanoverWind2100RCP8.5 | Hanover | Wind | RCP8.5 | 2100 | 88.3108 | 95.7061 | 103.6644 | 111.4557 | 119.2834
HastingsIce Accretion2023RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
HastingsIce Accretion2025RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
HastingsIce Accretion2030RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
HastingsIce Accretion2035RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
HastingsIce Accretion2040RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
HastingsIce Accretion2045RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
HastingsIce Accretion2050RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
HastingsIce Accretion2055RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
HastingsIce Accretion2060RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
HastingsIce Accretion2065RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
HastingsIce Accretion2070RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
HastingsIce Accretion2075RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2075 | 16.8859 | 20.3972 | 24.8292 | 28.2123 | 31.5682
HastingsIce Accretion2080RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2080 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
HastingsIce Accretion2085RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2085 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
HastingsIce Accretion2090RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2090 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
HastingsIce Accretion2095RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2095 | 16.7235 | 20.3142 | 24.8458 | 28.2877 | 31.7152
HastingsIce Accretion2100RCP4.5 | Hastings | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.2935 | 24.85 | 28.3065 | 31.752
HastingsIce Accretion2023RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
HastingsIce Accretion2025RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
HastingsIce Accretion2030RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
HastingsIce Accretion2035RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
HastingsIce Accretion2040RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
HastingsIce Accretion2045RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
HastingsIce Accretion2050RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
HastingsIce Accretion2055RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
HastingsIce Accretion2060RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
HastingsIce Accretion2065RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
HastingsIce Accretion2070RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
HastingsIce Accretion2075RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2075 | 16.8656 | 20.3869 | 24.8313 | 28.2217 | 31.5866
HastingsIce Accretion2080RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2080 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
HastingsIce Accretion2085RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2085 | 16.7438 | 20.3246 | 24.8438 | 28.2782 | 31.6969
HastingsIce Accretion2090RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2090 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
HastingsIce Accretion2095RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2095 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
HastingsIce Accretion2100RCP6.0 | Hastings | Ice Accretion | RCP6.0 | 2100 | 15.6565 | 19.173 | 23.6 | 26.9505 | 30.2715
HastingsIce Accretion2023RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
HastingsIce Accretion2025RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2025 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
HastingsIce Accretion2030RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2030 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
HastingsIce Accretion2035RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2035 | 17.6745 | 21.2272 | 25.725 | 29.154 | 32.571
HastingsIce Accretion2040RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2040 | 17.4251 | 20.9575 | 25.425 | 28.8338 | 32.2245
HastingsIce Accretion2045RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2045 | 17.1758 | 20.6877 | 25.125 | 28.5137 | 31.878
HastingsIce Accretion2050RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2050 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
HastingsIce Accretion2055RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2055 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
HastingsIce Accretion2060RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2060 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
HastingsIce Accretion2065RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2065 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
HastingsIce Accretion2070RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2070 | 15.2216 | 18.6888 | 23.05 | 26.3478 | 29.631
HastingsIce Accretion2075RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2075 | 14.7867 | 18.2047 | 22.5 | 25.7452 | 28.9905
HastingsIce Accretion2080RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2080 | 14.3518 | 17.7205 | 21.95 | 25.1425 | 28.35
HastingsIce Accretion2085RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2085 | 13.6908 | 16.9424 | 21.025 | 24.0972 | 27.1845
HastingsIce Accretion2090RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2090 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
HastingsIce Accretion2095RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2095 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
HastingsIce Accretion2100RCP8.5 | Hastings | Ice Accretion | RCP8.5 | 2100 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
HastingsWind2023RCP4.5 | Hastings | Wind | RCP4.5 | 2023 | 74.705 | 80.4759 | 86.5418 | 92.6089 | 98.6773
HastingsWind2025RCP4.5 | Hastings | Wind | RCP4.5 | 2025 | 74.6766 | 80.4452 | 86.5117 | 92.5767 | 98.6446
HastingsWind2030RCP4.5 | Hastings | Wind | RCP4.5 | 2030 | 74.6481 | 80.4146 | 86.4816 | 92.5445 | 98.6119
HastingsWind2035RCP4.5 | Hastings | Wind | RCP4.5 | 2035 | 74.6196 | 80.3839 | 86.4515 | 92.5123 | 98.5792
HastingsWind2040RCP4.5 | Hastings | Wind | RCP4.5 | 2040 | 74.5912 | 80.3532 | 86.4214 | 92.4801 | 98.5465
HastingsWind2045RCP4.5 | Hastings | Wind | RCP4.5 | 2045 | 74.5627 | 80.3226 | 86.3913 | 92.4479 | 98.5139
HastingsWind2050RCP4.5 | Hastings | Wind | RCP4.5 | 2050 | 74.6397 | 80.4327 | 86.5452 | 92.6365 | 98.74
HastingsWind2055RCP4.5 | Hastings | Wind | RCP4.5 | 2055 | 74.7451 | 80.5735 | 86.7293 | 92.8574 | 98.9988
HastingsWind2060RCP4.5 | Hastings | Wind | RCP4.5 | 2060 | 74.8506 | 80.7142 | 86.9133 | 93.0782 | 99.2577
HastingsWind2065RCP4.5 | Hastings | Wind | RCP4.5 | 2065 | 74.956 | 80.855 | 87.0974 | 93.2991 | 99.5165
HastingsWind2070RCP4.5 | Hastings | Wind | RCP4.5 | 2070 | 75.0615 | 80.9957 | 87.2814 | 93.5199 | 99.7753
HastingsWind2075RCP4.5 | Hastings | Wind | RCP4.5 | 2075 | 75.1147 | 81.0691 | 87.3789 | 93.638 | 99.9142
HastingsWind2080RCP4.5 | Hastings | Wind | RCP4.5 | 2080 | 75.1679 | 81.1424 | 87.4763 | 93.7561 | 100.0531
HastingsWind2085RCP4.5 | Hastings | Wind | RCP4.5 | 2085 | 75.2211 | 81.2157 | 87.5738 | 93.8742 | 100.192
HastingsWind2090RCP4.5 | Hastings | Wind | RCP4.5 | 2090 | 75.2744 | 81.289 | 87.6713 | 93.9923 | 100.3309
HastingsWind2095RCP4.5 | Hastings | Wind | RCP4.5 | 2095 | 75.3276 | 81.3623 | 87.7687 | 94.1104 | 100.4698
HastingsWind2100RCP4.5 | Hastings | Wind | RCP4.5 | 2100 | 75.3808 | 81.4356 | 87.8662 | 94.2285 | 100.6086
HastingsWind2023RCP6.0 | Hastings | Wind | RCP6.0 | 2023 | 74.705 | 80.4759 | 86.5418 | 92.6089 | 98.6773
HastingsWind2025RCP6.0 | Hastings | Wind | RCP6.0 | 2025 | 74.6766 | 80.4452 | 86.5117 | 92.5767 | 98.6446
HastingsWind2030RCP6.0 | Hastings | Wind | RCP6.0 | 2030 | 74.6481 | 80.4146 | 86.4816 | 92.5445 | 98.6119
HastingsWind2035RCP6.0 | Hastings | Wind | RCP6.0 | 2035 | 74.6196 | 80.3839 | 86.4515 | 92.5123 | 98.5792
HastingsWind2040RCP6.0 | Hastings | Wind | RCP6.0 | 2040 | 74.5912 | 80.3532 | 86.4214 | 92.4801 | 98.5465
HastingsWind2045RCP6.0 | Hastings | Wind | RCP6.0 | 2045 | 74.5627 | 80.3226 | 86.3913 | 92.4479 | 98.5139
HastingsWind2050RCP6.0 | Hastings | Wind | RCP6.0 | 2050 | 74.6397 | 80.4327 | 86.5452 | 92.6365 | 98.74
HastingsWind2055RCP6.0 | Hastings | Wind | RCP6.0 | 2055 | 74.7451 | 80.5735 | 86.7293 | 92.8574 | 98.9988
HastingsWind2060RCP6.0 | Hastings | Wind | RCP6.0 | 2060 | 74.8506 | 80.7142 | 86.9133 | 93.0782 | 99.2577
HastingsWind2065RCP6.0 | Hastings | Wind | RCP6.0 | 2065 | 74.956 | 80.855 | 87.0974 | 93.2991 | 99.5165
HastingsWind2070RCP6.0 | Hastings | Wind | RCP6.0 | 2070 | 75.0615 | 80.9957 | 87.2814 | 93.5199 | 99.7753
HastingsWind2075RCP6.0 | Hastings | Wind | RCP6.0 | 2075 | 75.1413 | 81.1057 | 87.4276 | 93.6971 | 99.9836
HastingsWind2080RCP6.0 | Hastings | Wind | RCP6.0 | 2080 | 75.2211 | 81.2157 | 87.5738 | 93.8742 | 100.192
HastingsWind2085RCP6.0 | Hastings | Wind | RCP6.0 | 2085 | 75.301 | 81.3257 | 87.72 | 94.0513 | 100.4003
HastingsWind2090RCP6.0 | Hastings | Wind | RCP6.0 | 2090 | 75.6358 | 81.7449 | 88.2446 | 94.6702 | 101.1087
HastingsWind2095RCP6.0 | Hastings | Wind | RCP6.0 | 2095 | 75.8907 | 82.0541 | 88.623 | 95.1119 | 101.6087
HastingsWind2100RCP6.0 | Hastings | Wind | RCP6.0 | 2100 | 76.1457 | 82.3634 | 89.0014 | 95.5536 | 102.1087
HastingsWind2023RCP8.5 | Hastings | Wind | RCP8.5 | 2023 | 74.705 | 80.4759 | 86.5418 | 92.6089 | 98.6773
HastingsWind2025RCP8.5 | Hastings | Wind | RCP8.5 | 2025 | 74.6481 | 80.4146 | 86.4816 | 92.5445 | 98.6119
HastingsWind2030RCP8.5 | Hastings | Wind | RCP8.5 | 2030 | 74.5912 | 80.3532 | 86.4214 | 92.4801 | 98.5465
HastingsWind2035RCP8.5 | Hastings | Wind | RCP8.5 | 2035 | 74.5342 | 80.2919 | 86.3612 | 92.4157 | 98.4812
HastingsWind2040RCP8.5 | Hastings | Wind | RCP8.5 | 2040 | 74.71 | 80.5265 | 86.6679 | 92.7838 | 98.9126
HastingsWind2045RCP8.5 | Hastings | Wind | RCP8.5 | 2045 | 74.8857 | 80.7611 | 86.9747 | 93.1518 | 99.3439
HastingsWind2050RCP8.5 | Hastings | Wind | RCP8.5 | 2050 | 75.1679 | 81.1424 | 87.4763 | 93.7561 | 100.0531
HastingsWind2055RCP8.5 | Hastings | Wind | RCP8.5 | 2055 | 75.2744 | 81.289 | 87.6713 | 93.9923 | 100.3309
HastingsWind2060RCP8.5 | Hastings | Wind | RCP8.5 | 2060 | 75.6358 | 81.7449 | 88.2446 | 94.6702 | 101.1087
HastingsWind2065RCP8.5 | Hastings | Wind | RCP8.5 | 2065 | 75.8907 | 82.0541 | 88.623 | 95.1119 | 101.6087
HastingsWind2070RCP8.5 | Hastings | Wind | RCP8.5 | 2070 | 76.0764 | 82.2861 | 88.9125 | 95.4554 | 102.0041
HastingsWind2075RCP8.5 | Hastings | Wind | RCP8.5 | 2075 | 76.0071 | 82.2088 | 88.8237 | 95.3573 | 101.8995
HastingsWind2080RCP8.5 | Hastings | Wind | RCP8.5 | 2080 | 75.9378 | 82.1315 | 88.7348 | 95.2591 | 101.7949
HastingsWind2085RCP8.5 | Hastings | Wind | RCP8.5 | 2085 | 76.1197 | 82.4074 | 89.1304 | 95.7514 | 102.3881
HastingsWind2090RCP8.5 | Hastings | Wind | RCP8.5 | 2090 | 76.3016 | 82.6833 | 89.526 | 96.2437 | 102.9812
HastingsWind2095RCP8.5 | Hastings | Wind | RCP8.5 | 2095 | 76.3016 | 82.6833 | 89.526 | 96.2437 | 102.9812
HastingsWind2100RCP8.5 | Hastings | Wind | RCP8.5 | 2100 | 76.3016 | 82.6833 | 89.526 | 96.2437 | 102.9812
HawkesburyIce Accretion2023RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2023 | 20.6666 | 24.6012 | 29.61 | 33.4254 | 37.233
HawkesburyIce Accretion2025RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2025 | 20.6736 | 24.6178 | 29.635 | 33.4593 | 37.2771
HawkesburyIce Accretion2030RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2030 | 20.6805 | 24.6344 | 29.66 | 33.4932 | 37.3212
HawkesburyIce Accretion2035RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2035 | 20.6875 | 24.651 | 29.685 | 33.5271 | 37.3653
HawkesburyIce Accretion2040RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2040 | 20.6945 | 24.6676 | 29.71 | 33.561 | 37.4094
HawkesburyIce Accretion2045RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2045 | 20.7014 | 24.6842 | 29.735 | 33.5949 | 37.4535
HawkesburyIce Accretion2050RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2050 | 20.6625 | 24.661 | 29.724 | 33.5949 | 37.4674
HawkesburyIce Accretion2055RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2055 | 20.6165 | 24.6211 | 29.688 | 33.561 | 37.4371
HawkesburyIce Accretion2060RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2060 | 20.5706 | 24.5813 | 29.652 | 33.5271 | 37.4069
HawkesburyIce Accretion2065RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2065 | 20.5247 | 24.5414 | 29.616 | 33.4932 | 37.3766
HawkesburyIce Accretion2070RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2070 | 20.4788 | 24.5016 | 29.58 | 33.4593 | 37.3464
HawkesburyIce Accretion2075RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2075 | 20.5588 | 24.6178 | 29.745 | 33.657 | 37.5795
HawkesburyIce Accretion2080RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2080 | 20.6388 | 24.734 | 29.91 | 33.8548 | 37.8126
HawkesburyIce Accretion2085RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2085 | 20.7188 | 24.8502 | 30.075 | 34.0525 | 38.0457
HawkesburyIce Accretion2090RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2090 | 20.7988 | 24.9664 | 30.24 | 34.2503 | 38.2788
HawkesburyIce Accretion2095RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2095 | 20.8789 | 25.0826 | 30.405 | 34.4481 | 38.5119
HawkesburyIce Accretion2100RCP4.5 | Hawkesbury | Ice Accretion | RCP4.5 | 2100 | 20.9589 | 25.1988 | 30.57 | 34.6458 | 38.745
HawkesburyIce Accretion2023RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2023 | 20.6666 | 24.6012 | 29.61 | 33.4254 | 37.233
HawkesburyIce Accretion2025RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2025 | 20.6736 | 24.6178 | 29.635 | 33.4593 | 37.2771
HawkesburyIce Accretion2030RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2030 | 20.6805 | 24.6344 | 29.66 | 33.4932 | 37.3212
HawkesburyIce Accretion2035RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2035 | 20.6875 | 24.651 | 29.685 | 33.5271 | 37.3653
HawkesburyIce Accretion2040RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2040 | 20.6945 | 24.6676 | 29.71 | 33.561 | 37.4094
HawkesburyIce Accretion2045RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2045 | 20.7014 | 24.6842 | 29.735 | 33.5949 | 37.4535
HawkesburyIce Accretion2050RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2050 | 20.6625 | 24.661 | 29.724 | 33.5949 | 37.4674
HawkesburyIce Accretion2055RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2055 | 20.6165 | 24.6211 | 29.688 | 33.561 | 37.4371
HawkesburyIce Accretion2060RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2060 | 20.5706 | 24.5813 | 29.652 | 33.5271 | 37.4069
HawkesburyIce Accretion2065RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2065 | 20.5247 | 24.5414 | 29.616 | 33.4932 | 37.3766
HawkesburyIce Accretion2070RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2070 | 20.4788 | 24.5016 | 29.58 | 33.4593 | 37.3464
HawkesburyIce Accretion2075RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2075 | 20.5988 | 24.6759 | 29.8275 | 33.7559 | 37.696
HawkesburyIce Accretion2080RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2080 | 20.7188 | 24.8502 | 30.075 | 34.0525 | 38.0457
HawkesburyIce Accretion2085RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2085 | 20.8389 | 25.0245 | 30.3225 | 34.3492 | 38.3953
HawkesburyIce Accretion2090RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2090 | 20.9728 | 25.2403 | 30.65 | 34.7588 | 38.8836
HawkesburyIce Accretion2095RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2095 | 20.9867 | 25.2818 | 30.73 | 34.8718 | 39.0222
HawkesburyIce Accretion2100RCP6.0 | Hawkesbury | Ice Accretion | RCP6.0 | 2100 | 21.0006 | 25.3233 | 30.81 | 34.9848 | 39.1608
HawkesburyIce Accretion2023RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2023 | 20.6666 | 24.6012 | 29.61 | 33.4254 | 37.233
HawkesburyIce Accretion2025RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2025 | 20.6805 | 24.6344 | 29.66 | 33.4932 | 37.3212
HawkesburyIce Accretion2030RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2030 | 20.6945 | 24.6676 | 29.71 | 33.561 | 37.4094
HawkesburyIce Accretion2035RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2035 | 20.7084 | 24.7008 | 29.76 | 33.6288 | 37.4976
HawkesburyIce Accretion2040RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2040 | 20.6318 | 24.6344 | 29.7 | 33.5723 | 37.4472
HawkesburyIce Accretion2045RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2045 | 20.5553 | 24.568 | 29.64 | 33.5158 | 37.3968
HawkesburyIce Accretion2050RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2050 | 20.6388 | 24.734 | 29.91 | 33.8548 | 37.8126
HawkesburyIce Accretion2055RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2055 | 20.7988 | 24.9664 | 30.24 | 34.2503 | 38.2788
HawkesburyIce Accretion2060RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2060 | 20.9728 | 25.2403 | 30.65 | 34.7588 | 38.8836
HawkesburyIce Accretion2065RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2065 | 20.9867 | 25.2818 | 30.73 | 34.8718 | 39.0222
HawkesburyIce Accretion2070RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2070 | 21.0006 | 25.3648 | 30.9 | 35.1204 | 39.3372
HawkesburyIce Accretion2075RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2075 | 21.0006 | 25.4063 | 30.99 | 35.256 | 39.5136
HawkesburyIce Accretion2080RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2080 | 21.0006 | 25.4478 | 31.08 | 35.3916 | 39.69
HawkesburyIce Accretion2085RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2085 | 20.5101 | 24.9124 | 30.495 | 34.7644 | 39.0096
HawkesburyIce Accretion2090RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2090 | 20.0195 | 24.3771 | 29.91 | 34.1373 | 38.3292
HawkesburyIce Accretion2095RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2095 | 20.0195 | 24.3771 | 29.91 | 34.1373 | 38.3292
HawkesburyIce Accretion2100RCP8.5 | Hawkesbury | Ice Accretion | RCP8.5 | 2100 | 20.0195 | 24.3771 | 29.91 | 34.1373 | 38.3292
HawkesburyWind2023RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2023 | 83.2922 | 89.7532 | 96.5664 | 103.3671 | 110.1623
HawkesburyWind2025RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2025 | 83.4055 | 89.8916 | 96.736 | 103.5623 | 110.3867
HawkesburyWind2030RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2030 | 83.5188 | 90.03 | 96.9056 | 103.7575 | 110.611
HawkesburyWind2035RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2035 | 83.6321 | 90.1683 | 97.0752 | 103.9526 | 110.8354
HawkesburyWind2040RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2040 | 83.7454 | 90.3067 | 97.2448 | 104.1478 | 111.0597
HawkesburyWind2045RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2045 | 83.8587 | 90.4451 | 97.4144 | 104.343 | 111.2841
HawkesburyWind2050RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2050 | 83.8658 | 90.4406 | 97.3939 | 104.3101 | 111.2392
HawkesburyWind2055RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2055 | 83.7597 | 90.2978 | 97.2038 | 104.0821 | 110.97
HawkesburyWind2060RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2060 | 83.6536 | 90.1549 | 97.0138 | 103.854 | 110.7007
HawkesburyWind2065RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2065 | 83.5475 | 90.0121 | 96.8237 | 103.626 | 110.4315
HawkesburyWind2070RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2070 | 83.4414 | 89.8692 | 96.6336 | 103.398 | 110.1623
HawkesburyWind2075RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2075 | 83.4538 | 89.8886 | 96.664 | 103.4356 | 110.2079
HawkesburyWind2080RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2080 | 83.4663 | 89.9079 | 96.6944 | 103.4733 | 110.2535
HawkesburyWind2085RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2085 | 83.4787 | 89.9273 | 96.7248 | 103.5109 | 110.2991
HawkesburyWind2090RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2090 | 83.4912 | 89.9466 | 96.7552 | 103.5486 | 110.3447
HawkesburyWind2095RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2095 | 83.5036 | 89.966 | 96.7856 | 103.5863 | 110.3903
HawkesburyWind2100RCP4.5 | Hawkesbury | Wind | RCP4.5 | 2100 | 83.516 | 89.9853 | 96.816 | 103.6239 | 110.4359
HawkesburyWind2023RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2023 | 83.2922 | 89.7532 | 96.5664 | 103.3671 | 110.1623
HawkesburyWind2025RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2025 | 83.4055 | 89.8916 | 96.736 | 103.5623 | 110.3867
HawkesburyWind2030RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2030 | 83.5188 | 90.03 | 96.9056 | 103.7575 | 110.611
HawkesburyWind2035RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2035 | 83.6321 | 90.1683 | 97.0752 | 103.9526 | 110.8354
HawkesburyWind2040RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2040 | 83.7454 | 90.3067 | 97.2448 | 104.1478 | 111.0597
HawkesburyWind2045RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2045 | 83.8587 | 90.4451 | 97.4144 | 104.343 | 111.2841
HawkesburyWind2050RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2050 | 83.8658 | 90.4406 | 97.3939 | 104.3101 | 111.2392
HawkesburyWind2055RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2055 | 83.7597 | 90.2978 | 97.2038 | 104.0821 | 110.97
HawkesburyWind2060RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2060 | 83.6536 | 90.1549 | 97.0138 | 103.854 | 110.7007
HawkesburyWind2065RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2065 | 83.5475 | 90.0121 | 96.8237 | 103.626 | 110.4315
HawkesburyWind2070RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2070 | 83.4414 | 89.8692 | 96.6336 | 103.398 | 110.1623
HawkesburyWind2075RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2075 | 83.4601 | 89.8983 | 96.6792 | 103.4544 | 110.2307
HawkesburyWind2080RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2080 | 83.4787 | 89.9273 | 96.7248 | 103.5109 | 110.2991
HawkesburyWind2085RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2085 | 83.4974 | 89.9563 | 96.7704 | 103.5674 | 110.3675
HawkesburyWind2090RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2090 | 83.4 | 89.8306 | 96.608 | 103.374 | 110.1441
HawkesburyWind2095RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2095 | 83.2839 | 89.6758 | 96.4 | 103.124 | 109.8522
HawkesburyWind2100RCP6.0 | Hawkesbury | Wind | RCP6.0 | 2100 | 83.1679 | 89.5211 | 96.192 | 102.8741 | 109.5604
HawkesburyWind2023RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2023 | 83.2922 | 89.7532 | 96.5664 | 103.3671 | 110.1623
HawkesburyWind2025RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2025 | 83.5188 | 90.03 | 96.9056 | 103.7575 | 110.611
HawkesburyWind2030RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2030 | 83.7454 | 90.3067 | 97.2448 | 104.1478 | 111.0597
HawkesburyWind2035RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2035 | 83.9719 | 90.5835 | 97.584 | 104.5381 | 111.5084
HawkesburyWind2040RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2040 | 83.7951 | 90.3454 | 97.2672 | 104.1581 | 111.0597
HawkesburyWind2045RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2045 | 83.6183 | 90.1073 | 96.9504 | 103.778 | 110.611
HawkesburyWind2050RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2050 | 83.4663 | 89.9079 | 96.6944 | 103.4733 | 110.2535
HawkesburyWind2055RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2055 | 83.4912 | 89.9466 | 96.7552 | 103.5486 | 110.3447
HawkesburyWind2060RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2060 | 83.4 | 89.8306 | 96.608 | 103.374 | 110.1441
HawkesburyWind2065RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2065 | 83.2839 | 89.6758 | 96.4 | 103.124 | 109.8522
HawkesburyWind2070RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2070 | 83.3337 | 89.7294 | 96.4576 | 103.1857 | 109.9215
HawkesburyWind2075RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2075 | 83.4994 | 89.9377 | 96.7232 | 103.4972 | 110.2827
HawkesburyWind2080RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2080 | 83.6652 | 90.146 | 96.9888 | 103.8088 | 110.6438
HawkesburyWind2085RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2085 | 83.574 | 90.021 | 96.8112 | 103.5931 | 110.3812
HawkesburyWind2090RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2090 | 83.4829 | 89.896 | 96.6336 | 103.3774 | 110.1185
HawkesburyWind2095RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2095 | 83.4829 | 89.896 | 96.6336 | 103.3774 | 110.1185
HawkesburyWind2100RCP8.5 | Hawkesbury | Wind | RCP8.5 | 2100 | 83.4829 | 89.896 | 96.6336 | 103.3774 | 110.1185
HearstIce Accretion2023RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2023 | 10.4377 | 12.4375 | 14.97 | 16.9161 | 18.8433
HearstIce Accretion2025RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2025 | 10.5247 | 12.5454 | 15.1025 | 17.0658 | 19.0134
HearstIce Accretion2030RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2030 | 10.6117 | 12.6533 | 15.235 | 17.2156 | 19.1835
HearstIce Accretion2035RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2035 | 10.6986 | 12.7613 | 15.3675 | 17.3653 | 19.3536
HearstIce Accretion2040RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2040 | 10.7856 | 12.8691 | 15.5 | 17.515 | 19.5237
HearstIce Accretion2045RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2045 | 10.8726 | 12.977 | 15.6325 | 17.6647 | 19.6938
HearstIce Accretion2050RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2050 | 10.9992 | 13.1298 | 15.819 | 17.8755 | 19.9319
HearstIce Accretion2055RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2055 | 11.0389 | 13.1746 | 15.873 | 17.9365 | 20
HearstIce Accretion2060RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2060 | 11.0786 | 13.2194 | 15.927 | 17.9975 | 20.068
HearstIce Accretion2065RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2065 | 11.1182 | 13.2642 | 15.981 | 18.0585 | 20.1361
HearstIce Accretion2070RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2070 | 11.1579 | 13.309 | 16.035 | 18.1195 | 20.2041
HearstIce Accretion2075RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2075 | 11.177 | 13.336 | 16.07 | 18.1619 | 20.2513
HearstIce Accretion2080RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2080 | 11.1962 | 13.363 | 16.105 | 18.2043 | 20.2986
HearstIce Accretion2085RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2085 | 11.2153 | 13.39 | 16.14 | 18.2467 | 20.3458
HearstIce Accretion2090RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2090 | 11.2344 | 13.4169 | 16.175 | 18.289 | 20.3931
HearstIce Accretion2095RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2095 | 11.2536 | 13.4439 | 16.21 | 18.3314 | 20.4403
HearstIce Accretion2100RCP4.5 | Hearst | Ice Accretion | RCP4.5 | 2100 | 11.2727 | 13.4709 | 16.245 | 18.3738 | 20.4876
HearstIce Accretion2023RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2023 | 10.4377 | 12.4375 | 14.97 | 16.9161 | 18.8433
HearstIce Accretion2025RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2025 | 10.5247 | 12.5454 | 15.1025 | 17.0658 | 19.0134
HearstIce Accretion2030RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2030 | 10.6117 | 12.6533 | 15.235 | 17.2156 | 19.1835
HearstIce Accretion2035RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2035 | 10.6986 | 12.7613 | 15.3675 | 17.3653 | 19.3536
HearstIce Accretion2040RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2040 | 10.7856 | 12.8691 | 15.5 | 17.515 | 19.5237
HearstIce Accretion2045RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2045 | 10.8726 | 12.977 | 15.6325 | 17.6647 | 19.6938
HearstIce Accretion2050RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2050 | 10.9992 | 13.1298 | 15.819 | 17.8755 | 19.9319
HearstIce Accretion2055RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2055 | 11.0389 | 13.1746 | 15.873 | 17.9365 | 20
HearstIce Accretion2060RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2060 | 11.0786 | 13.2194 | 15.927 | 17.9975 | 20.068
HearstIce Accretion2065RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2065 | 11.1182 | 13.2642 | 15.981 | 18.0585 | 20.1361
HearstIce Accretion2070RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2070 | 11.1579 | 13.309 | 16.035 | 18.1195 | 20.2041
HearstIce Accretion2075RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2075 | 11.1866 | 13.3495 | 16.0875 | 18.1831 | 20.275
HearstIce Accretion2080RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2080 | 11.2153 | 13.39 | 16.14 | 18.2467 | 20.3458
HearstIce Accretion2085RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2085 | 11.244 | 13.4304 | 16.1925 | 18.3102 | 20.4167
HearstIce Accretion2090RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2090 | 11.1788 | 13.3672 | 16.13 | 18.2438 | 20.349
HearstIce Accretion2095RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2095 | 11.0848 | 13.2634 | 16.015 | 18.1139 | 20.2104
HearstIce Accretion2100RCP6.0 | Hearst | Ice Accretion | RCP6.0 | 2100 | 10.9909 | 13.1596 | 15.9 | 17.9839 | 20.0718
HearstIce Accretion2023RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2023 | 10.4377 | 12.4375 | 14.97 | 16.9161 | 18.8433
HearstIce Accretion2025RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2025 | 10.6117 | 12.6533 | 15.235 | 17.2156 | 19.1835
HearstIce Accretion2030RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2030 | 10.7856 | 12.8691 | 15.5 | 17.515 | 19.5237
HearstIce Accretion2035RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2035 | 10.9596 | 13.0849 | 15.765 | 17.8144 | 19.8639
HearstIce Accretion2040RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2040 | 11.0257 | 13.1596 | 15.855 | 17.9161 | 19.9773
HearstIce Accretion2045RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2045 | 11.0918 | 13.2343 | 15.945 | 18.0178 | 20.0907
HearstIce Accretion2050RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2050 | 11.1962 | 13.363 | 16.105 | 18.2043 | 20.2986
HearstIce Accretion2055RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2055 | 11.2344 | 13.4169 | 16.175 | 18.289 | 20.3931
HearstIce Accretion2060RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2060 | 11.1788 | 13.3672 | 16.13 | 18.2438 | 20.349
HearstIce Accretion2065RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2065 | 11.0848 | 13.2634 | 16.015 | 18.1139 | 20.2104
HearstIce Accretion2070RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2070 | 10.9387 | 13.114 | 15.865 | 17.9613 | 20.0529
HearstIce Accretion2075RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2075 | 10.8865 | 13.0684 | 15.83 | 17.9387 | 20.034
HearstIce Accretion2080RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2080 | 10.8343 | 13.0227 | 15.795 | 17.9161 | 20.0151
HearstIce Accretion2085RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2085 | 10.6204 | 12.7986 | 15.5475 | 17.6534 | 19.741
HearstIce Accretion2090RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2090 | 10.4064 | 12.5745 | 15.3 | 17.3907 | 19.467
HearstIce Accretion2095RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2095 | 10.4064 | 12.5745 | 15.3 | 17.3907 | 19.467
HearstIce Accretion2100RCP8.5 | Hearst | Ice Accretion | RCP8.5 | 2100 | 10.4064 | 12.5745 | 15.3 | 17.3907 | 19.467
HearstWind2023RCP4.5 | Hearst | Wind | RCP4.5 | 2023 | 69.9352 | 75.3598 | 81.072 | 86.7813 | 92.4859
HearstWind2025RCP4.5 | Hearst | Wind | RCP4.5 | 2025 | 70.0146 | 75.4528 | 81.1813 | 86.904 | 92.6227
HearstWind2030RCP4.5 | Hearst | Wind | RCP4.5 | 2030 | 70.094 | 75.5458 | 81.2907 | 87.0267 | 92.7595
HearstWind2035RCP4.5 | Hearst | Wind | RCP4.5 | 2035 | 70.1735 | 75.6388 | 81.4 | 87.1494 | 92.8963
HearstWind2040RCP4.5 | Hearst | Wind | RCP4.5 | 2040 | 70.2529 | 75.7318 | 81.5093 | 87.2721 | 93.0331
HearstWind2045RCP4.5 | Hearst | Wind | RCP4.5 | 2045 | 70.3324 | 75.8248 | 81.6187 | 87.3947 | 93.1699
HearstWind2050RCP4.5 | Hearst | Wind | RCP4.5 | 2050 | 70.445 | 75.9431 | 81.744 | 87.526 | 93.3085
HearstWind2055RCP4.5 | Hearst | Wind | RCP4.5 | 2055 | 70.4781 | 75.9684 | 81.76 | 87.5346 | 93.3104
HearstWind2060RCP4.5 | Hearst | Wind | RCP4.5 | 2060 | 70.5113 | 75.9936 | 81.776 | 87.5431 | 93.3122
HearstWind2065RCP4.5 | Hearst | Wind | RCP4.5 | 2065 | 70.5444 | 76.0189 | 81.792 | 87.5517 | 93.314
HearstWind2070RCP4.5 | Hearst | Wind | RCP4.5 | 2070 | 70.5776 | 76.0442 | 81.808 | 87.5602 | 93.3158
HearstWind2075RCP4.5 | Hearst | Wind | RCP4.5 | 2075 | 70.5811 | 76.0393 | 81.7907 | 87.5346 | 93.2809
HearstWind2080RCP4.5 | Hearst | Wind | RCP4.5 | 2080 | 70.5845 | 76.0343 | 81.7733 | 87.5089 | 93.2459
HearstWind2085RCP4.5 | Hearst | Wind | RCP4.5 | 2085 | 70.588 | 76.0294 | 81.756 | 87.4832 | 93.211
HearstWind2090RCP4.5 | Hearst | Wind | RCP4.5 | 2090 | 70.5914 | 76.0244 | 81.7387 | 87.4575 | 93.176
HearstWind2095RCP4.5 | Hearst | Wind | RCP4.5 | 2095 | 70.5949 | 76.0194 | 81.7213 | 87.4318 | 93.141
HearstWind2100RCP4.5 | Hearst | Wind | RCP4.5 | 2100 | 70.5983 | 76.0145 | 81.704 | 87.4062 | 93.1061
HearstWind2023RCP6.0 | Hearst | Wind | RCP6.0 | 2023 | 69.9352 | 75.3598 | 81.072 | 86.7813 | 92.4859
HearstWind2025RCP6.0 | Hearst | Wind | RCP6.0 | 2025 | 70.0146 | 75.4528 | 81.1813 | 86.904 | 92.6227
HearstWind2030RCP6.0 | Hearst | Wind | RCP6.0 | 2030 | 70.094 | 75.5458 | 81.2907 | 87.0267 | 92.7595
HearstWind2035RCP6.0 | Hearst | Wind | RCP6.0 | 2035 | 70.1735 | 75.6388 | 81.4 | 87.1494 | 92.8963
HearstWind2040RCP6.0 | Hearst | Wind | RCP6.0 | 2040 | 70.2529 | 75.7318 | 81.5093 | 87.2721 | 93.0331
HearstWind2045RCP6.0 | Hearst | Wind | RCP6.0 | 2045 | 70.3324 | 75.8248 | 81.6187 | 87.3947 | 93.1699
HearstWind2050RCP6.0 | Hearst | Wind | RCP6.0 | 2050 | 70.445 | 75.9431 | 81.744 | 87.526 | 93.3085
HearstWind2055RCP6.0 | Hearst | Wind | RCP6.0 | 2055 | 70.4781 | 75.9684 | 81.76 | 87.5346 | 93.3104
HearstWind2060RCP6.0 | Hearst | Wind | RCP6.0 | 2060 | 70.5113 | 75.9936 | 81.776 | 87.5431 | 93.3122
HearstWind2065RCP6.0 | Hearst | Wind | RCP6.0 | 2065 | 70.5444 | 76.0189 | 81.792 | 87.5517 | 93.314
HearstWind2070RCP6.0 | Hearst | Wind | RCP6.0 | 2070 | 70.5776 | 76.0442 | 81.808 | 87.5602 | 93.3158
HearstWind2075RCP6.0 | Hearst | Wind | RCP6.0 | 2075 | 70.5828 | 76.0368 | 81.782 | 87.5217 | 93.2634
HearstWind2080RCP6.0 | Hearst | Wind | RCP6.0 | 2080 | 70.588 | 76.0294 | 81.756 | 87.4832 | 93.211
HearstWind2085RCP6.0 | Hearst | Wind | RCP6.0 | 2085 | 70.5931 | 76.0219 | 81.73 | 87.4447 | 93.1585
HearstWind2090RCP6.0 | Hearst | Wind | RCP6.0 | 2090 | 70.6167 | 76.0219 | 81.7013 | 87.3919 | 93.0787
HearstWind2095RCP6.0 | Hearst | Wind | RCP6.0 | 2095 | 70.6352 | 76.0294 | 81.6987 | 87.3776 | 93.0514
HearstWind2100RCP6.0 | Hearst | Wind | RCP6.0 | 2100 | 70.6536 | 76.0368 | 81.696 | 87.3634 | 93.024
HearstWind2023RCP8.5 | Hearst | Wind | RCP8.5 | 2023 | 69.9352 | 75.3598 | 81.072 | 86.7813 | 92.4859
HearstWind2025RCP8.5 | Hearst | Wind | RCP8.5 | 2025 | 70.094 | 75.5458 | 81.2907 | 87.0267 | 92.7595
HearstWind2030RCP8.5 | Hearst | Wind | RCP8.5 | 2030 | 70.2529 | 75.7318 | 81.5093 | 87.2721 | 93.0331
HearstWind2035RCP8.5 | Hearst | Wind | RCP8.5 | 2035 | 70.4118 | 75.9178 | 81.728 | 87.5174 | 93.3067
HearstWind2040RCP8.5 | Hearst | Wind | RCP8.5 | 2040 | 70.4671 | 75.9599 | 81.7547 | 87.5317 | 93.3098
HearstWind2045RCP8.5 | Hearst | Wind | RCP8.5 | 2045 | 70.5223 | 76.0021 | 81.7813 | 87.546 | 93.3128
HearstWind2050RCP8.5 | Hearst | Wind | RCP8.5 | 2050 | 70.5845 | 76.0343 | 81.7733 | 87.5089 | 93.2459
HearstWind2055RCP8.5 | Hearst | Wind | RCP8.5 | 2055 | 70.5914 | 76.0244 | 81.7387 | 87.4575 | 93.176
HearstWind2060RCP8.5 | Hearst | Wind | RCP8.5 | 2060 | 70.6167 | 76.0219 | 81.7013 | 87.3919 | 93.0787
HearstWind2065RCP8.5 | Hearst | Wind | RCP8.5 | 2065 | 70.6352 | 76.0294 | 81.6987 | 87.3776 | 93.0514
HearstWind2070RCP8.5 | Hearst | Wind | RCP8.5 | 2070 | 70.7987 | 76.2104 | 81.8987 | 87.5916 | 93.2824
HearstWind2075RCP8.5 | Hearst | Wind | RCP8.5 | 2075 | 70.9437 | 76.384 | 82.1013 | 87.8199 | 93.5408
HearstWind2080RCP8.5 | Hearst | Wind | RCP8.5 | 2080 | 71.0888 | 76.5576 | 82.304 | 88.0482 | 93.7992
HearstWind2085RCP8.5 | Hearst | Wind | RCP8.5 | 2085 | 71.2649 | 76.7845 | 82.592 | 88.3906 | 94.1959
HearstWind2090RCP8.5 | Hearst | Wind | RCP8.5 | 2090 | 71.4411 | 77.0114 | 82.88 | 88.733 | 94.5926
HearstWind2095RCP8.5 | Hearst | Wind | RCP8.5 | 2095 | 71.4411 | 77.0114 | 82.88 | 88.733 | 94.5926
HearstWind2100RCP8.5 | Hearst | Wind | RCP8.5 | 2100 | 71.4411 | 77.0114 | 82.88 | 88.733 | 94.5926
Honey HarbourIce Accretion2023RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2023 | 13.6525 | 16.2846 | 19.62 | 22.1706 | 24.7464
Honey HarbourIce Accretion2025RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2025 | 13.6363 | 16.2735 | 19.6133 | 22.1706 | 24.7464
Honey HarbourIce Accretion2030RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2030 | 13.62 | 16.2625 | 19.6067 | 22.1706 | 24.7464
Honey HarbourIce Accretion2035RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2035 | 13.6038 | 16.2514 | 19.6 | 22.1706 | 24.7464
Honey HarbourIce Accretion2040RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2040 | 13.5876 | 16.2403 | 19.5933 | 22.1706 | 24.7464
Honey HarbourIce Accretion2045RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2045 | 13.5713 | 16.2293 | 19.5867 | 22.1706 | 24.7464
Honey HarbourIce Accretion2050RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2050 | 13.5523 | 16.2282 | 19.612 | 22.2113 | 24.8018
Honey HarbourIce Accretion2055RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2055 | 13.5495 | 16.2381 | 19.644 | 22.252 | 24.8573
Honey HarbourIce Accretion2060RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2060 | 13.5467 | 16.2481 | 19.676 | 22.2926 | 24.9127
Honey HarbourIce Accretion2065RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2065 | 13.5439 | 16.258 | 19.708 | 22.3333 | 24.9682
Honey HarbourIce Accretion2070RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2070 | 13.5412 | 16.268 | 19.74 | 22.374 | 25.0236
Honey HarbourIce Accretion2075RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2075 | 13.5806 | 16.3316 | 19.83 | 22.4832 | 25.1538
Honey HarbourIce Accretion2080RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2080 | 13.62 | 16.3953 | 19.92 | 22.5925 | 25.284
Honey HarbourIce Accretion2085RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2085 | 13.6595 | 16.4589 | 20.01 | 22.7017 | 25.4142
Honey HarbourIce Accretion2090RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2090 | 13.6989 | 16.5225 | 20.1 | 22.8109 | 25.5444
Honey HarbourIce Accretion2095RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2095 | 13.7383 | 16.5862 | 20.19 | 22.9202 | 25.6746
Honey HarbourIce Accretion2100RCP4.5 | Honey Harbour | Ice Accretion | RCP4.5 | 2100 | 13.7778 | 16.6498 | 20.28 | 23.0294 | 25.8048
Honey HarbourIce Accretion2023RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2023 | 13.6525 | 16.2846 | 19.62 | 22.1706 | 24.7464
Honey HarbourIce Accretion2025RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2025 | 13.6363 | 16.2735 | 19.6133 | 22.1706 | 24.7464
Honey HarbourIce Accretion2030RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2030 | 13.62 | 16.2625 | 19.6067 | 22.1706 | 24.7464
Honey HarbourIce Accretion2035RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2035 | 13.6038 | 16.2514 | 19.6 | 22.1706 | 24.7464
Honey HarbourIce Accretion2040RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2040 | 13.5876 | 16.2403 | 19.5933 | 22.1706 | 24.7464
Honey HarbourIce Accretion2045RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2045 | 13.5713 | 16.2293 | 19.5867 | 22.1706 | 24.7464
Honey HarbourIce Accretion2050RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2050 | 13.5523 | 16.2282 | 19.612 | 22.2113 | 24.8018
Honey HarbourIce Accretion2055RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2055 | 13.5495 | 16.2381 | 19.644 | 22.252 | 24.8573
Honey HarbourIce Accretion2060RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2060 | 13.5467 | 16.2481 | 19.676 | 22.2926 | 24.9127
Honey HarbourIce Accretion2065RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2065 | 13.5439 | 16.258 | 19.708 | 22.3333 | 24.9682
Honey HarbourIce Accretion2070RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2070 | 13.5412 | 16.268 | 19.74 | 22.374 | 25.0236
Honey HarbourIce Accretion2075RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2075 | 13.6003 | 16.3634 | 19.875 | 22.5378 | 25.2189
Honey HarbourIce Accretion2080RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2080 | 13.6595 | 16.4589 | 20.01 | 22.7017 | 25.4142
Honey HarbourIce Accretion2085RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2085 | 13.7186 | 16.5543 | 20.145 | 22.8655 | 25.6095
Honey HarbourIce Accretion2090RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2090 | 13.7546 | 16.6609 | 20.3333 | 23.1198 | 25.9224
Honey HarbourIce Accretion2095RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2095 | 13.7314 | 16.6719 | 20.3867 | 23.2102 | 26.04
Honey HarbourIce Accretion2100RCP6.0 | Honey Harbour | Ice Accretion | RCP6.0 | 2100 | 13.7082 | 16.683 | 20.44 | 23.3006 | 26.1576
Honey HarbourIce Accretion2023RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2023 | 13.6525 | 16.2846 | 19.62 | 22.1706 | 24.7464
Honey HarbourIce Accretion2025RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2025 | 13.62 | 16.2625 | 19.6067 | 22.1706 | 24.7464
Honey HarbourIce Accretion2030RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2030 | 13.5876 | 16.2403 | 19.5933 | 22.1706 | 24.7464
Honey HarbourIce Accretion2035RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2035 | 13.5551 | 16.2182 | 19.58 | 22.1706 | 24.7464
Honey HarbourIce Accretion2040RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2040 | 13.5504 | 16.2348 | 19.6333 | 22.2384 | 24.8388
Honey HarbourIce Accretion2045RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2045 | 13.5458 | 16.2514 | 19.6867 | 22.3062 | 24.9312
Honey HarbourIce Accretion2050RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2050 | 13.62 | 16.3953 | 19.92 | 22.5925 | 25.284
Honey HarbourIce Accretion2055RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2055 | 13.6989 | 16.5225 | 20.1 | 22.8109 | 25.5444
Honey HarbourIce Accretion2060RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2060 | 13.7546 | 16.6609 | 20.3333 | 23.1198 | 25.9224
Honey HarbourIce Accretion2065RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2065 | 13.7314 | 16.6719 | 20.3867 | 23.2102 | 26.04
Honey HarbourIce Accretion2070RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2070 | 13.4577 | 16.4174 | 20.1533 | 22.9917 | 25.83
Honey HarbourIce Accretion2075RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2075 | 13.2072 | 16.1518 | 19.8667 | 22.6829 | 25.5024
Honey HarbourIce Accretion2080RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2080 | 12.9567 | 15.8862 | 19.58 | 22.374 | 25.1748
Honey HarbourIce Accretion2085RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2085 | 12.4348 | 15.2969 | 18.9 | 21.6282 | 24.3558
Honey HarbourIce Accretion2090RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2090 | 11.9129 | 14.7076 | 18.22 | 20.8824 | 23.5368
Honey HarbourIce Accretion2095RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2095 | 11.9129 | 14.7076 | 18.22 | 20.8824 | 23.5368
Honey HarbourIce Accretion2100RCP8.5 | Honey Harbour | Ice Accretion | RCP8.5 | 2100 | 11.9129 | 14.7076 | 18.22 | 20.8824 | 23.5368
Honey HarbourWind2023RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2023 | 76.4728 | 82.3965 | 88.6424 | 94.8756 | 101.1125
Honey HarbourWind2025RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2025 | 76.5513 | 82.4906 | 88.7539 | 95.0027 | 101.2546
Honey HarbourWind2030RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2030 | 76.6298 | 82.5847 | 88.8653 | 95.1298 | 101.3968
Honey HarbourWind2035RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2035 | 76.7083 | 82.6789 | 88.9768 | 95.257 | 101.5389
Honey HarbourWind2040RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2040 | 76.7868 | 82.773 | 89.0883 | 95.3841 | 101.681
Honey HarbourWind2045RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2045 | 76.8654 | 82.8671 | 89.1997 | 95.5112 | 101.8231
Honey HarbourWind2050RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2050 | 77.0533 | 83.0922 | 89.4696 | 95.821 | 102.1739
Honey HarbourWind2055RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2055 | 77.1627 | 83.2231 | 89.628 | 96.0037 | 102.3826
Honey HarbourWind2060RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2060 | 77.2721 | 83.354 | 89.7864 | 96.1863 | 102.5912
Honey HarbourWind2065RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2065 | 77.3816 | 83.485 | 89.9448 | 96.369 | 102.7999
Honey HarbourWind2070RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2070 | 77.491 | 83.6159 | 90.1032 | 96.5517 | 103.0086
Honey HarbourWind2075RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2075 | 77.5252 | 83.665 | 90.1721 | 96.6364 | 103.1089
Honey HarbourWind2080RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2080 | 77.5594 | 83.7141 | 90.2411 | 96.7212 | 103.2092
Honey HarbourWind2085RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2085 | 77.5936 | 83.7632 | 90.31 | 96.8059 | 103.3095
Honey HarbourWind2090RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2090 | 77.6278 | 83.8123 | 90.3789 | 96.8906 | 103.4099
Honey HarbourWind2095RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2095 | 77.662 | 83.8614 | 90.4479 | 96.9754 | 103.5102
Honey HarbourWind2100RCP4.5 | Honey Harbour | Wind | RCP4.5 | 2100 | 77.6961 | 83.9106 | 90.5168 | 97.0601 | 103.6105
Honey HarbourWind2023RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2023 | 76.4728 | 82.3965 | 88.6424 | 94.8756 | 101.1125
Honey HarbourWind2025RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2025 | 76.5513 | 82.4906 | 88.7539 | 95.0027 | 101.2546
Honey HarbourWind2030RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2030 | 76.6298 | 82.5847 | 88.8653 | 95.1298 | 101.3968
Honey HarbourWind2035RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2035 | 76.7083 | 82.6789 | 88.9768 | 95.257 | 101.5389
Honey HarbourWind2040RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2040 | 76.7868 | 82.773 | 89.0883 | 95.3841 | 101.681
Honey HarbourWind2045RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2045 | 76.8654 | 82.8671 | 89.1997 | 95.5112 | 101.8231
Honey HarbourWind2050RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2050 | 77.0533 | 83.0922 | 89.4696 | 95.821 | 102.1739
Honey HarbourWind2055RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2055 | 77.1627 | 83.2231 | 89.628 | 96.0037 | 102.3826
Honey HarbourWind2060RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2060 | 77.2721 | 83.354 | 89.7864 | 96.1863 | 102.5912
Honey HarbourWind2065RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2065 | 77.3816 | 83.485 | 89.9448 | 96.369 | 102.7999
Honey HarbourWind2070RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2070 | 77.491 | 83.6159 | 90.1032 | 96.5517 | 103.0086
Honey HarbourWind2075RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2075 | 77.5423 | 83.6896 | 90.2066 | 96.6788 | 103.1591
Honey HarbourWind2080RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2080 | 77.5936 | 83.7632 | 90.31 | 96.8059 | 103.3095
Honey HarbourWind2085RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2085 | 77.6449 | 83.8369 | 90.4134 | 96.933 | 103.46
Honey HarbourWind2090RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2090 | 77.8101 | 84.0633 | 90.7133 | 97.2955 | 103.8847
Honey HarbourWind2095RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2095 | 77.9241 | 84.2161 | 90.9099 | 97.5309 | 104.1589
Honey HarbourWind2100RCP6.0 | Honey Harbour | Wind | RCP6.0 | 2100 | 78.0381 | 84.3689 | 91.1064 | 97.7663 | 104.4331
Honey HarbourWind2023RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2023 | 76.4728 | 82.3965 | 88.6424 | 94.8756 | 101.1125
Honey HarbourWind2025RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2025 | 76.6298 | 82.5847 | 88.8653 | 95.1298 | 101.3968
Honey HarbourWind2030RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2030 | 76.7868 | 82.773 | 89.0883 | 95.3841 | 101.681
Honey HarbourWind2035RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2035 | 76.9439 | 82.9612 | 89.3112 | 95.6383 | 101.9652
Honey HarbourWind2040RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2040 | 77.1263 | 83.1794 | 89.5752 | 95.9428 | 102.313
Honey HarbourWind2045RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2045 | 77.3086 | 83.3977 | 89.8392 | 96.2472 | 102.6608
Honey HarbourWind2050RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2050 | 77.5594 | 83.7141 | 90.2411 | 96.7212 | 103.2092
Honey HarbourWind2055RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2055 | 77.6278 | 83.8123 | 90.3789 | 96.8906 | 103.4099
Honey HarbourWind2060RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2060 | 77.8101 | 84.0633 | 90.7133 | 97.2955 | 103.8847
Honey HarbourWind2065RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2065 | 77.9241 | 84.2161 | 90.9099 | 97.5309 | 104.1589
Honey HarbourWind2070RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2070 | 78.0254 | 84.3634 | 91.1123 | 97.7789 | 104.4565
Honey HarbourWind2075RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2075 | 78.0128 | 84.3579 | 91.1181 | 97.7914 | 104.4799
Honey HarbourWind2080RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2080 | 78.0001 | 84.3525 | 91.124 | 97.804 | 104.5033
Honey HarbourWind2085RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2085 | 78.0989 | 84.4793 | 91.2912 | 98.0017 | 104.7341
Honey HarbourWind2090RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2090 | 78.1977 | 84.6062 | 91.4584 | 98.1995 | 104.9648
Honey HarbourWind2095RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2095 | 78.1977 | 84.6062 | 91.4584 | 98.1995 | 104.9648
Honey HarbourWind2100RCP8.5 | Honey Harbour | Wind | RCP8.5 | 2100 | 78.1977 | 84.6062 | 91.4584 | 98.1995 | 104.9648
HornepayneIce Accretion2023RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2023 | 10.5316 | 12.5496 | 15.105 | 17.0686 | 19.0323
HornepayneIce Accretion2025RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2025 | 10.603 | 12.6388 | 15.22 | 17.1986 | 19.1803
HornepayneIce Accretion2030RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2030 | 10.6743 | 12.728 | 15.335 | 17.3285 | 19.3284
HornepayneIce Accretion2035RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2035 | 10.7456 | 12.8173 | 15.45 | 17.4585 | 19.4764
HornepayneIce Accretion2040RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2040 | 10.8169 | 12.9065 | 15.565 | 17.5884 | 19.6245
HornepayneIce Accretion2045RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2045 | 10.8883 | 12.9957 | 15.68 | 17.7184 | 19.7725
HornepayneIce Accretion2050RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2050 | 10.9742 | 13.0974 | 15.804 | 17.8585 | 19.9282
HornepayneIce Accretion2055RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2055 | 10.9888 | 13.1098 | 15.813 | 17.8687 | 19.9357
HornepayneIce Accretion2060RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2060 | 11.0034 | 13.1223 | 15.822 | 17.8789 | 19.9433
HornepayneIce Accretion2065RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2065 | 11.018 | 13.1348 | 15.831 | 17.889 | 19.9508
HornepayneIce Accretion2070RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2070 | 11.0326 | 13.1472 | 15.84 | 17.8992 | 19.9584
HornepayneIce Accretion2075RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2075 | 11.057 | 13.1825 | 15.8875 | 17.9557 | 20.0214
HornepayneIce Accretion2080RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2080 | 11.0813 | 13.2177 | 15.935 | 18.0122 | 20.0844
HornepayneIce Accretion2085RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2085 | 11.1057 | 13.253 | 15.9825 | 18.0687 | 20.1474
HornepayneIce Accretion2090RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2090 | 11.1301 | 13.2883 | 16.03 | 18.1252 | 20.2104
HornepayneIce Accretion2095RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2095 | 11.1544 | 13.3236 | 16.0775 | 18.1817 | 20.2734
HornepayneIce Accretion2100RCP4.5 | Hornepayne | Ice Accretion | RCP4.5 | 2100 | 11.1788 | 13.3588 | 16.125 | 18.2382 | 20.3364
HornepayneIce Accretion2023RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2023 | 10.5316 | 12.5496 | 15.105 | 17.0686 | 19.0323
HornepayneIce Accretion2025RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2025 | 10.603 | 12.6388 | 15.22 | 17.1986 | 19.1803
HornepayneIce Accretion2030RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2030 | 10.6743 | 12.728 | 15.335 | 17.3285 | 19.3284
HornepayneIce Accretion2035RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2035 | 10.7456 | 12.8173 | 15.45 | 17.4585 | 19.4764
HornepayneIce Accretion2040RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2040 | 10.8169 | 12.9065 | 15.565 | 17.5884 | 19.6245
HornepayneIce Accretion2045RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2045 | 10.8883 | 12.9957 | 15.68 | 17.7184 | 19.7725
HornepayneIce Accretion2050RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2050 | 10.9742 | 13.0974 | 15.804 | 17.8585 | 19.9282
HornepayneIce Accretion2055RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2055 | 10.9888 | 13.1098 | 15.813 | 17.8687 | 19.9357
HornepayneIce Accretion2060RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2060 | 11.0034 | 13.1223 | 15.822 | 17.8789 | 19.9433
HornepayneIce Accretion2065RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2065 | 11.018 | 13.1348 | 15.831 | 17.889 | 19.9508
HornepayneIce Accretion2070RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2070 | 11.0326 | 13.1472 | 15.84 | 17.8992 | 19.9584
HornepayneIce Accretion2075RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2075 | 11.0692 | 13.2001 | 15.9112 | 17.984 | 20.0529
HornepayneIce Accretion2080RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2080 | 11.1057 | 13.253 | 15.9825 | 18.0687 | 20.1474
HornepayneIce Accretion2085RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2085 | 11.1422 | 13.3059 | 16.0538 | 18.1534 | 20.2419
HornepayneIce Accretion2090RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2090 | 11.0744 | 13.2426 | 15.985 | 18.0856 | 20.1726
HornepayneIce Accretion2095RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2095 | 10.97 | 13.1264 | 15.845 | 17.9331 | 20.0088
HornepayneIce Accretion2100RCP6.0 | Hornepayne | Ice Accretion | RCP6.0 | 2100 | 10.8656 | 13.0102 | 15.705 | 17.7805 | 19.845
HornepayneIce Accretion2023RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2023 | 10.5316 | 12.5496 | 15.105 | 17.0686 | 19.0323
HornepayneIce Accretion2025RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2025 | 10.6743 | 12.728 | 15.335 | 17.3285 | 19.3284
HornepayneIce Accretion2030RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2030 | 10.8169 | 12.9065 | 15.565 | 17.5884 | 19.6245
HornepayneIce Accretion2035RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2035 | 10.9596 | 13.0849 | 15.795 | 17.8483 | 19.9206
HornepayneIce Accretion2040RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2040 | 10.9839 | 13.1057 | 15.81 | 17.8653 | 19.9332
HornepayneIce Accretion2045RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2045 | 11.0083 | 13.1265 | 15.825 | 17.8822 | 19.9458
HornepayneIce Accretion2050RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2050 | 11.0813 | 13.2177 | 15.935 | 18.0122 | 20.0844
HornepayneIce Accretion2055RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2055 | 11.1301 | 13.2883 | 16.03 | 18.1252 | 20.2104
HornepayneIce Accretion2060RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2060 | 11.0744 | 13.2426 | 15.985 | 18.0856 | 20.1726
HornepayneIce Accretion2065RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2065 | 10.97 | 13.1264 | 15.845 | 17.9331 | 20.0088
HornepayneIce Accretion2070RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2070 | 10.7856 | 12.9231 | 15.615 | 17.6845 | 19.7442
HornepayneIce Accretion2075RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2075 | 10.7056 | 12.8359 | 15.525 | 17.5884 | 19.6434
HornepayneIce Accretion2080RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2080 | 10.6256 | 12.7488 | 15.435 | 17.4924 | 19.5426
HornepayneIce Accretion2085RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2085 | 10.4533 | 12.5558 | 15.21 | 17.2466 | 19.2685
HornepayneIce Accretion2090RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2090 | 10.2811 | 12.3628 | 14.985 | 17.0008 | 18.9945
HornepayneIce Accretion2095RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2095 | 10.2811 | 12.3628 | 14.985 | 17.0008 | 18.9945
HornepayneIce Accretion2100RCP8.5 | Hornepayne | Ice Accretion | RCP8.5 | 2100 | 10.2811 | 12.3628 | 14.985 | 17.0008 | 18.9945
HornepayneWind2023RCP4.5 | Hornepayne | Wind | RCP4.5 | 2023 | 69.9697 | 75.4342 | 81.208 | 86.9525 | 92.7048
HornepayneWind2025RCP4.5 | Hornepayne | Wind | RCP4.5 | 2025 | 70.0699 | 75.5582 | 81.3613 | 87.1322 | 92.91
HornepayneWind2030RCP4.5 | Hornepayne | Wind | RCP4.5 | 2030 | 70.17 | 75.6822 | 81.5147 | 87.312 | 93.1152
HornepayneWind2035RCP4.5 | Hornepayne | Wind | RCP4.5 | 2035 | 70.2702 | 75.8062 | 81.668 | 87.4918 | 93.3204
HornepayneWind2040RCP4.5 | Hornepayne | Wind | RCP4.5 | 2040 | 70.3704 | 75.9302 | 81.8213 | 87.6715 | 93.5256
HornepayneWind2045RCP4.5 | Hornepayne | Wind | RCP4.5 | 2045 | 70.4705 | 76.0542 | 81.9747 | 87.8513 | 93.7308
HornepayneWind2050RCP4.5 | Hornepayne | Wind | RCP4.5 | 2050 | 70.6633 | 76.2927 | 82.2672 | 88.192 | 94.1202
HornepayneWind2055RCP4.5 | Hornepayne | Wind | RCP4.5 | 2055 | 70.7558 | 76.4073 | 82.4064 | 88.3529 | 94.3044
HornepayneWind2060RCP4.5 | Hornepayne | Wind | RCP4.5 | 2060 | 70.8484 | 76.5219 | 82.5456 | 88.5138 | 94.4887
HornepayneWind2065RCP4.5 | Hornepayne | Wind | RCP4.5 | 2065 | 70.941 | 76.6365 | 82.6848 | 88.6748 | 94.6729
HornepayneWind2070RCP4.5 | Hornepayne | Wind | RCP4.5 | 2070 | 71.0335 | 76.751 | 82.824 | 88.8357 | 94.8571
HornepayneWind2075RCP4.5 | Hornepayne | Wind | RCP4.5 | 2075 | 71.0232 | 76.7262 | 82.7813 | 88.7786 | 94.7842
HornepayneWind2080RCP4.5 | Hornepayne | Wind | RCP4.5 | 2080 | 71.0128 | 76.7014 | 82.7387 | 88.7215 | 94.7112
HornepayneWind2085RCP4.5 | Hornepayne | Wind | RCP4.5 | 2085 | 71.0024 | 76.6766 | 82.696 | 88.6645 | 94.6382
HornepayneWind2090RCP4.5 | Hornepayne | Wind | RCP4.5 | 2090 | 70.9921 | 76.6518 | 82.6533 | 88.6074 | 94.5653
HornepayneWind2095RCP4.5 | Hornepayne | Wind | RCP4.5 | 2095 | 70.9817 | 76.627 | 82.6107 | 88.5503 | 94.4923
HornepayneWind2100RCP4.5 | Hornepayne | Wind | RCP4.5 | 2100 | 70.9713 | 76.6022 | 82.568 | 88.4933 | 94.4194
HornepayneWind2023RCP6.0 | Hornepayne | Wind | RCP6.0 | 2023 | 69.9697 | 75.4342 | 81.208 | 86.9525 | 92.7048
HornepayneWind2025RCP6.0 | Hornepayne | Wind | RCP6.0 | 2025 | 70.0699 | 75.5582 | 81.3613 | 87.1322 | 92.91
HornepayneWind2030RCP6.0 | Hornepayne | Wind | RCP6.0 | 2030 | 70.17 | 75.6822 | 81.5147 | 87.312 | 93.1152
HornepayneWind2035RCP6.0 | Hornepayne | Wind | RCP6.0 | 2035 | 70.2702 | 75.8062 | 81.668 | 87.4918 | 93.3204
HornepayneWind2040RCP6.0 | Hornepayne | Wind | RCP6.0 | 2040 | 70.3704 | 75.9302 | 81.8213 | 87.6715 | 93.5256
HornepayneWind2045RCP6.0 | Hornepayne | Wind | RCP6.0 | 2045 | 70.4705 | 76.0542 | 81.9747 | 87.8513 | 93.7308
HornepayneWind2050RCP6.0 | Hornepayne | Wind | RCP6.0 | 2050 | 70.6633 | 76.2927 | 82.2672 | 88.192 | 94.1202
HornepayneWind2055RCP6.0 | Hornepayne | Wind | RCP6.0 | 2055 | 70.7558 | 76.4073 | 82.4064 | 88.3529 | 94.3044
HornepayneWind2060RCP6.0 | Hornepayne | Wind | RCP6.0 | 2060 | 70.8484 | 76.5219 | 82.5456 | 88.5138 | 94.4887
HornepayneWind2065RCP6.0 | Hornepayne | Wind | RCP6.0 | 2065 | 70.941 | 76.6365 | 82.6848 | 88.6748 | 94.6729
HornepayneWind2070RCP6.0 | Hornepayne | Wind | RCP6.0 | 2070 | 71.0335 | 76.751 | 82.824 | 88.8357 | 94.8571
HornepayneWind2075RCP6.0 | Hornepayne | Wind | RCP6.0 | 2075 | 71.018 | 76.7138 | 82.76 | 88.7501 | 94.7477
HornepayneWind2080RCP6.0 | Hornepayne | Wind | RCP6.0 | 2080 | 71.0024 | 76.6766 | 82.696 | 88.6645 | 94.6382
HornepayneWind2085RCP6.0 | Hornepayne | Wind | RCP6.0 | 2085 | 70.9869 | 76.6394 | 82.632 | 88.5789 | 94.5288
HornepayneWind2090RCP6.0 | Hornepayne | Wind | RCP6.0 | 2090 | 71.121 | 76.7659 | 82.7467 | 88.6873 | 94.6291
HornepayneWind2095RCP6.0 | Hornepayne | Wind | RCP6.0 | 2095 | 71.2707 | 76.9296 | 82.9253 | 88.8813 | 94.8389
HornepayneWind2100RCP6.0 | Hornepayne | Wind | RCP6.0 | 2100 | 71.4204 | 77.0933 | 83.104 | 89.0754 | 95.0486
HornepayneWind2023RCP8.5 | Hornepayne | Wind | RCP8.5 | 2023 | 69.9697 | 75.4342 | 81.208 | 86.9525 | 92.7048
HornepayneWind2025RCP8.5 | Hornepayne | Wind | RCP8.5 | 2025 | 70.17 | 75.6822 | 81.5147 | 87.312 | 93.1152
HornepayneWind2030RCP8.5 | Hornepayne | Wind | RCP8.5 | 2030 | 70.3704 | 75.9302 | 81.8213 | 87.6715 | 93.5256
HornepayneWind2035RCP8.5 | Hornepayne | Wind | RCP8.5 | 2035 | 70.5707 | 76.1782 | 82.128 | 88.031 | 93.936
HornepayneWind2040RCP8.5 | Hornepayne | Wind | RCP8.5 | 2040 | 70.725 | 76.3691 | 82.36 | 88.2993 | 94.243
HornepayneWind2045RCP8.5 | Hornepayne | Wind | RCP8.5 | 2045 | 70.8792 | 76.5601 | 82.592 | 88.5675 | 94.5501
HornepayneWind2050RCP8.5 | Hornepayne | Wind | RCP8.5 | 2050 | 71.0128 | 76.7014 | 82.7387 | 88.7215 | 94.7112
HornepayneWind2055RCP8.5 | Hornepayne | Wind | RCP8.5 | 2055 | 70.9921 | 76.6518 | 82.6533 | 88.6074 | 94.5653
HornepayneWind2060RCP8.5 | Hornepayne | Wind | RCP8.5 | 2060 | 71.121 | 76.7659 | 82.7467 | 88.6873 | 94.6291
HornepayneWind2065RCP8.5 | Hornepayne | Wind | RCP8.5 | 2065 | 71.2707 | 76.9296 | 82.9253 | 88.8813 | 94.8389
HornepayneWind2070RCP8.5 | Hornepayne | Wind | RCP8.5 | 2070 | 71.4687 | 77.133 | 83.1307 | 89.0896 | 95.0517
HornepayneWind2075RCP8.5 | Hornepayne | Wind | RCP8.5 | 2075 | 71.5171 | 77.1726 | 83.1573 | 89.1039 | 95.0547
HornepayneWind2080RCP8.5 | Hornepayne | Wind | RCP8.5 | 2080 | 71.5654 | 77.2123 | 83.184 | 89.1182 | 95.0578
HornepayneWind2085RCP8.5 | Hornepayne | Wind | RCP8.5 | 2085 | 71.7692 | 77.4578 | 83.48 | 89.4606 | 95.4454
HornepayneWind2090RCP8.5 | Hornepayne | Wind | RCP8.5 | 2090 | 71.973 | 77.7034 | 83.776 | 89.803 | 95.833
HornepayneWind2095RCP8.5 | Hornepayne | Wind | RCP8.5 | 2095 | 71.973 | 77.7034 | 83.776 | 89.803 | 95.833
HornepayneWind2100RCP8.5 | Hornepayne | Wind | RCP8.5 | 2100 | 71.973 | 77.7034 | 83.776 | 89.803 | 95.833
HuntsvilleIce Accretion2023RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2023 | 15.2627 | 18.2235 | 21.978 | 24.8351 | 27.6923
HuntsvilleIce Accretion2025RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2025 | 15.2601 | 18.2265 | 21.989 | 24.8517 | 27.7154
HuntsvilleIce Accretion2030RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2030 | 15.2576 | 18.2296 | 22 | 24.8683 | 27.7385
HuntsvilleIce Accretion2035RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2035 | 15.255 | 18.2326 | 22.011 | 24.8849 | 27.7616
HuntsvilleIce Accretion2040RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2040 | 15.2525 | 18.2357 | 22.022 | 24.9014 | 27.7847
HuntsvilleIce Accretion2045RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2045 | 15.2499 | 18.2387 | 22.033 | 24.918 | 27.8078
HuntsvilleIce Accretion2050RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2050 | 15.2382 | 18.249 | 22.066 | 24.9744 | 27.8863
HuntsvilleIce Accretion2055RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2055 | 15.229 | 18.2563 | 22.088 | 25.0141 | 27.9418
HuntsvilleIce Accretion2060RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2060 | 15.2198 | 18.2637 | 22.11 | 25.0539 | 27.9972
HuntsvilleIce Accretion2065RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2065 | 15.2106 | 18.271 | 22.132 | 25.0937 | 28.0526
HuntsvilleIce Accretion2070RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2070 | 15.2015 | 18.2783 | 22.154 | 25.1335 | 28.1081
HuntsvilleIce Accretion2075RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2075 | 15.2346 | 18.33 | 22.2347 | 25.2288 | 28.2236
HuntsvilleIce Accretion2080RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2080 | 15.2678 | 18.3817 | 22.3153 | 25.3241 | 28.3391
HuntsvilleIce Accretion2085RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2085 | 15.301 | 18.4335 | 22.396 | 25.4193 | 28.4546
HuntsvilleIce Accretion2090RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2090 | 15.3341 | 18.4852 | 22.4767 | 25.5146 | 28.5701
HuntsvilleIce Accretion2095RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2095 | 15.3673 | 18.5369 | 22.5573 | 25.6099 | 28.6856
HuntsvilleIce Accretion2100RCP4.5 | Huntsville | Ice Accretion | RCP4.5 | 2100 | 15.4005 | 18.5887 | 22.638 | 25.7052 | 28.8011
HuntsvilleIce Accretion2023RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2023 | 15.2627 | 18.2235 | 21.978 | 24.8351 | 27.6923
HuntsvilleIce Accretion2025RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2025 | 15.2601 | 18.2265 | 21.989 | 24.8517 | 27.7154
HuntsvilleIce Accretion2030RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2030 | 15.2576 | 18.2296 | 22 | 24.8683 | 27.7385
HuntsvilleIce Accretion2035RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2035 | 15.255 | 18.2326 | 22.011 | 24.8849 | 27.7616
HuntsvilleIce Accretion2040RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2040 | 15.2525 | 18.2357 | 22.022 | 24.9014 | 27.7847
HuntsvilleIce Accretion2045RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2045 | 15.2499 | 18.2387 | 22.033 | 24.918 | 27.8078
HuntsvilleIce Accretion2050RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2050 | 15.2382 | 18.249 | 22.066 | 24.9744 | 27.8863
HuntsvilleIce Accretion2055RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2055 | 15.229 | 18.2563 | 22.088 | 25.0141 | 27.9418
HuntsvilleIce Accretion2060RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2060 | 15.2198 | 18.2637 | 22.11 | 25.0539 | 27.9972
HuntsvilleIce Accretion2065RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2065 | 15.2106 | 18.271 | 22.132 | 25.0937 | 28.0526
HuntsvilleIce Accretion2070RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2070 | 15.2015 | 18.2783 | 22.154 | 25.1335 | 28.1081
HuntsvilleIce Accretion2075RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2075 | 15.2512 | 18.3559 | 22.275 | 25.2764 | 28.2813
HuntsvilleIce Accretion2080RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2080 | 15.301 | 18.4335 | 22.396 | 25.4193 | 28.4546
HuntsvilleIce Accretion2085RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2085 | 15.3507 | 18.5111 | 22.517 | 25.5623 | 28.6278
HuntsvilleIce Accretion2090RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2090 | 15.4362 | 18.6739 | 22.7847 | 25.8958 | 29.0321
HuntsvilleIce Accretion2095RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2095 | 15.4719 | 18.7591 | 22.9313 | 26.0864 | 29.2631
HuntsvilleIce Accretion2100RCP6.0 | Huntsville | Ice Accretion | RCP6.0 | 2100 | 15.5076 | 18.8443 | 23.078 | 26.277 | 29.4941
HuntsvilleIce Accretion2023RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2023 | 15.2627 | 18.2235 | 21.978 | 24.8351 | 27.6923
HuntsvilleIce Accretion2025RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2025 | 15.2576 | 18.2296 | 22 | 24.8683 | 27.7385
HuntsvilleIce Accretion2030RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2030 | 15.2525 | 18.2357 | 22.022 | 24.9014 | 27.7847
HuntsvilleIce Accretion2035RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2035 | 15.2474 | 18.2417 | 22.044 | 24.9346 | 27.8309
HuntsvilleIce Accretion2040RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2040 | 15.2321 | 18.2539 | 22.0807 | 25.0009 | 27.9233
HuntsvilleIce Accretion2045RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2045 | 15.2168 | 18.2661 | 22.1173 | 25.0672 | 28.0157
HuntsvilleIce Accretion2050RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2050 | 15.2678 | 18.3817 | 22.3153 | 25.3241 | 28.3391
HuntsvilleIce Accretion2055RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2055 | 15.3341 | 18.4852 | 22.4767 | 25.5146 | 28.5701
HuntsvilleIce Accretion2060RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2060 | 15.4362 | 18.6739 | 22.7847 | 25.8958 | 29.0321
HuntsvilleIce Accretion2065RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2065 | 15.4719 | 18.7591 | 22.9313 | 26.0864 | 29.2631
HuntsvilleIce Accretion2070RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2070 | 15.2984 | 18.613 | 22.814 | 26.0036 | 29.1984
HuntsvilleIce Accretion2075RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2075 | 15.0892 | 18.3817 | 22.55 | 25.7301 | 28.9027
HuntsvilleIce Accretion2080RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2080 | 14.88 | 18.1504 | 22.286 | 25.4566 | 28.607
HuntsvilleIce Accretion2085RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2085 | 14.3518 | 17.557 | 21.604 | 24.6984 | 27.7754
HuntsvilleIce Accretion2090RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2090 | 13.8237 | 16.9635 | 20.922 | 23.9402 | 26.9438
HuntsvilleIce Accretion2095RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2095 | 13.8237 | 16.9635 | 20.922 | 23.9402 | 26.9438
HuntsvilleIce Accretion2100RCP8.5 | Huntsville | Ice Accretion | RCP8.5 | 2100 | 13.8237 | 16.9635 | 20.922 | 23.9402 | 26.9438
HuntsvilleWind2023RCP4.5 | Huntsville | Wind | RCP4.5 | 2023 | 69.1684 | 74.4595 | 80.024 | 85.5914 | 91.1635
HuntsvilleWind2025RCP4.5 | Huntsville | Wind | RCP4.5 | 2025 | 69.2778 | 74.5996 | 80.2 | 85.7983 | 91.4006
HuntsvilleWind2030RCP4.5 | Huntsville | Wind | RCP4.5 | 2030 | 69.3871 | 74.7398 | 80.376 | 86.0052 | 91.6378
HuntsvilleWind2035RCP4.5 | Huntsville | Wind | RCP4.5 | 2035 | 69.4965 | 74.8799 | 80.552 | 86.212 | 91.8749
HuntsvilleWind2040RCP4.5 | Huntsville | Wind | RCP4.5 | 2040 | 69.6059 | 75.02 | 80.728 | 86.4189 | 92.112
HuntsvilleWind2045RCP4.5 | Huntsville | Wind | RCP4.5 | 2045 | 69.7153 | 75.1601 | 80.904 | 86.6258 | 92.3491
HuntsvilleWind2050RCP4.5 | Huntsville | Wind | RCP4.5 | 2050 | 69.8274 | 75.2839 | 81.04 | 86.7727 | 92.5078
HuntsvilleWind2055RCP4.5 | Huntsville | Wind | RCP4.5 | 2055 | 69.8302 | 75.2675 | 81 | 86.7128 | 92.4294
HuntsvilleWind2060RCP4.5 | Huntsville | Wind | RCP4.5 | 2060 | 69.8329 | 75.2511 | 80.96 | 86.6529 | 92.3509
HuntsvilleWind2065RCP4.5 | Huntsville | Wind | RCP4.5 | 2065 | 69.8357 | 75.2348 | 80.92 | 86.593 | 92.2725
HuntsvilleWind2070RCP4.5 | Huntsville | Wind | RCP4.5 | 2070 | 69.8385 | 75.2184 | 80.88 | 86.533 | 92.1941
HuntsvilleWind2075RCP4.5 | Huntsville | Wind | RCP4.5 | 2075 | 69.8626 | 75.2444 | 80.908 | 86.5644 | 92.2275
HuntsvilleWind2080RCP4.5 | Huntsville | Wind | RCP4.5 | 2080 | 69.8868 | 75.2705 | 80.936 | 86.5958 | 92.261
HuntsvilleWind2085RCP4.5 | Huntsville | Wind | RCP4.5 | 2085 | 69.911 | 75.2965 | 80.964 | 86.6272 | 92.2944
HuntsvilleWind2090RCP4.5 | Huntsville | Wind | RCP4.5 | 2090 | 69.9352 | 75.3226 | 80.992 | 86.6586 | 92.3278
HuntsvilleWind2095RCP4.5 | Huntsville | Wind | RCP4.5 | 2095 | 69.9593 | 75.3486 | 81.02 | 86.69 | 92.3613
HuntsvilleWind2100RCP4.5 | Huntsville | Wind | RCP4.5 | 2100 | 69.9835 | 75.3746 | 81.048 | 86.7214 | 92.3947
HuntsvilleWind2023RCP6.0 | Huntsville | Wind | RCP6.0 | 2023 | 69.1684 | 74.4595 | 80.024 | 85.5914 | 91.1635
HuntsvilleWind2025RCP6.0 | Huntsville | Wind | RCP6.0 | 2025 | 69.2778 | 74.5996 | 80.2 | 85.7983 | 91.4006
HuntsvilleWind2030RCP6.0 | Huntsville | Wind | RCP6.0 | 2030 | 69.3871 | 74.7398 | 80.376 | 86.0052 | 91.6378
HuntsvilleWind2035RCP6.0 | Huntsville | Wind | RCP6.0 | 2035 | 69.4965 | 74.8799 | 80.552 | 86.212 | 91.8749
HuntsvilleWind2040RCP6.0 | Huntsville | Wind | RCP6.0 | 2040 | 69.6059 | 75.02 | 80.728 | 86.4189 | 92.112
HuntsvilleWind2045RCP6.0 | Huntsville | Wind | RCP6.0 | 2045 | 69.7153 | 75.1601 | 80.904 | 86.6258 | 92.3491
HuntsvilleWind2050RCP6.0 | Huntsville | Wind | RCP6.0 | 2050 | 69.8274 | 75.2839 | 81.04 | 86.7727 | 92.5078
HuntsvilleWind2055RCP6.0 | Huntsville | Wind | RCP6.0 | 2055 | 69.8302 | 75.2675 | 81 | 86.7128 | 92.4294
HuntsvilleWind2060RCP6.0 | Huntsville | Wind | RCP6.0 | 2060 | 69.8329 | 75.2511 | 80.96 | 86.6529 | 92.3509
HuntsvilleWind2065RCP6.0 | Huntsville | Wind | RCP6.0 | 2065 | 69.8357 | 75.2348 | 80.92 | 86.593 | 92.2725
HuntsvilleWind2070RCP6.0 | Huntsville | Wind | RCP6.0 | 2070 | 69.8385 | 75.2184 | 80.88 | 86.533 | 92.1941
HuntsvilleWind2075RCP6.0 | Huntsville | Wind | RCP6.0 | 2075 | 69.8747 | 75.2575 | 80.922 | 86.5801 | 92.2442
HuntsvilleWind2080RCP6.0 | Huntsville | Wind | RCP6.0 | 2080 | 69.911 | 75.2965 | 80.964 | 86.6272 | 92.2944
HuntsvilleWind2085RCP6.0 | Huntsville | Wind | RCP6.0 | 2085 | 69.9473 | 75.3356 | 81.006 | 86.6743 | 92.3446
HuntsvilleWind2090RCP6.0 | Huntsville | Wind | RCP6.0 | 2090 | 69.9121 | 75.273 | 80.9093 | 86.553 | 92.1971
HuntsvilleWind2095RCP6.0 | Huntsville | Wind | RCP6.0 | 2095 | 69.8408 | 75.1713 | 80.7707 | 86.3847 | 91.9995
HuntsvilleWind2100RCP6.0 | Huntsville | Wind | RCP6.0 | 2100 | 69.7694 | 75.0696 | 80.632 | 86.2163 | 91.8019
HuntsvilleWind2023RCP8.5 | Huntsville | Wind | RCP8.5 | 2023 | 69.1684 | 74.4595 | 80.024 | 85.5914 | 91.1635
HuntsvilleWind2025RCP8.5 | Huntsville | Wind | RCP8.5 | 2025 | 69.3871 | 74.7398 | 80.376 | 86.0052 | 91.6378
HuntsvilleWind2030RCP8.5 | Huntsville | Wind | RCP8.5 | 2030 | 69.6059 | 75.02 | 80.728 | 86.4189 | 92.112
HuntsvilleWind2035RCP8.5 | Huntsville | Wind | RCP8.5 | 2035 | 69.8246 | 75.3002 | 81.08 | 86.8326 | 92.5862
HuntsvilleWind2040RCP8.5 | Huntsville | Wind | RCP8.5 | 2040 | 69.8292 | 75.273 | 81.0133 | 86.7328 | 92.4555
HuntsvilleWind2045RCP8.5 | Huntsville | Wind | RCP8.5 | 2045 | 69.8339 | 75.2457 | 80.9467 | 86.6329 | 92.3248
HuntsvilleWind2050RCP8.5 | Huntsville | Wind | RCP8.5 | 2050 | 69.8868 | 75.2705 | 80.936 | 86.5958 | 92.261
HuntsvilleWind2055RCP8.5 | Huntsville | Wind | RCP8.5 | 2055 | 69.9352 | 75.3226 | 80.992 | 86.6586 | 92.3278
HuntsvilleWind2060RCP8.5 | Huntsville | Wind | RCP8.5 | 2060 | 69.9121 | 75.273 | 80.9093 | 86.553 | 92.1971
HuntsvilleWind2065RCP8.5 | Huntsville | Wind | RCP8.5 | 2065 | 69.8408 | 75.1713 | 80.7707 | 86.3847 | 91.9995
HuntsvilleWind2070RCP8.5 | Huntsville | Wind | RCP8.5 | 2070 | 69.8615 | 75.1787 | 80.7627 | 86.3618 | 91.9661
HuntsvilleWind2075RCP8.5 | Huntsville | Wind | RCP8.5 | 2075 | 69.9536 | 75.2878 | 80.8933 | 86.5074 | 92.1302
HuntsvilleWind2080RCP8.5 | Huntsville | Wind | RCP8.5 | 2080 | 70.0457 | 75.397 | 81.024 | 86.6529 | 92.2944
HuntsvilleWind2085RCP8.5 | Huntsville | Wind | RCP8.5 | 2085 | 70.3393 | 75.7615 | 81.468 | 87.1708 | 92.8826
HuntsvilleWind2090RCP8.5 | Huntsville | Wind | RCP8.5 | 2090 | 70.6329 | 76.1261 | 81.912 | 87.6886 | 93.4709
HuntsvilleWind2095RCP8.5 | Huntsville | Wind | RCP8.5 | 2095 | 70.6329 | 76.1261 | 81.912 | 87.6886 | 93.4709
HuntsvilleWind2100RCP8.5 | Huntsville | Wind | RCP8.5 | 2100 | 70.6329 | 76.1261 | 81.912 | 87.6886 | 93.4709
IngersollIce Accretion2023RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2023 | 21.1182 | 25.3183 | 30.628 | 34.6797 | 38.7475
IngersollIce Accretion2025RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2025 | 21.0751 | 25.2797 | 30.5918 | 34.6505 | 38.715
IngersollIce Accretion2030RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2030 | 21.0319 | 25.2411 | 30.5557 | 34.6213 | 38.6824
IngersollIce Accretion2035RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2035 | 20.9888 | 25.2025 | 30.5195 | 34.5921 | 38.6499
IngersollIce Accretion2040RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2040 | 20.9457 | 25.1639 | 30.4833 | 34.5629 | 38.6173
IngersollIce Accretion2045RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2045 | 20.9025 | 25.1253 | 30.4472 | 34.5337 | 38.5848
IngersollIce Accretion2050RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2050 | 20.7256 | 24.9581 | 30.2932 | 34.3854 | 38.4429
IngersollIce Accretion2055RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2055 | 20.5919 | 24.8294 | 30.1754 | 34.2663 | 38.3335
IngersollIce Accretion2060RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2060 | 20.4582 | 24.7008 | 30.0576 | 34.1472 | 38.2241
IngersollIce Accretion2065RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2065 | 20.3244 | 24.5722 | 29.9398 | 34.0281 | 38.1147
IngersollIce Accretion2070RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2070 | 20.1907 | 24.4435 | 29.822 | 33.909 | 38.0054
IngersollIce Accretion2075RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2075 | 20.1331 | 24.4006 | 29.8013 | 33.9032 | 38.0119
IngersollIce Accretion2080RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2080 | 20.0756 | 24.3577 | 29.7807 | 33.8974 | 38.0184
IngersollIce Accretion2085RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2085 | 20.0181 | 24.3148 | 29.76 | 33.8915 | 38.0249
IngersollIce Accretion2090RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2090 | 19.9606 | 24.272 | 29.7393 | 33.8857 | 38.0314
IngersollIce Accretion2095RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2095 | 19.9031 | 24.2291 | 29.7187 | 33.8798 | 38.0379
IngersollIce Accretion2100RCP4.5 | Ingersoll | Ice Accretion | RCP4.5 | 2100 | 19.8455 | 24.1862 | 29.698 | 33.874 | 38.0444
IngersollIce Accretion2023RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2023 | 21.1182 | 25.3183 | 30.628 | 34.6797 | 38.7475
IngersollIce Accretion2025RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2025 | 21.0751 | 25.2797 | 30.5918 | 34.6505 | 38.715
IngersollIce Accretion2030RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2030 | 21.0319 | 25.2411 | 30.5557 | 34.6213 | 38.6824
IngersollIce Accretion2035RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2035 | 20.9888 | 25.2025 | 30.5195 | 34.5921 | 38.6499
IngersollIce Accretion2040RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2040 | 20.9457 | 25.1639 | 30.4833 | 34.5629 | 38.6173
IngersollIce Accretion2045RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2045 | 20.9025 | 25.1253 | 30.4472 | 34.5337 | 38.5848
IngersollIce Accretion2050RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2050 | 20.7256 | 24.9581 | 30.2932 | 34.3854 | 38.4429
IngersollIce Accretion2055RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2055 | 20.5919 | 24.8294 | 30.1754 | 34.2663 | 38.3335
IngersollIce Accretion2060RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2060 | 20.4582 | 24.7008 | 30.0576 | 34.1472 | 38.2241
IngersollIce Accretion2065RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2065 | 20.3244 | 24.5722 | 29.9398 | 34.0281 | 38.1147
IngersollIce Accretion2070RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2070 | 20.1907 | 24.4435 | 29.822 | 33.909 | 38.0054
IngersollIce Accretion2075RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2075 | 20.1044 | 24.3792 | 29.791 | 33.9003 | 38.0151
IngersollIce Accretion2080RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2080 | 20.0181 | 24.3148 | 29.76 | 33.8915 | 38.0249
IngersollIce Accretion2085RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2085 | 19.9318 | 24.2505 | 29.729 | 33.8828 | 38.0347
IngersollIce Accretion2090RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2090 | 19.3997 | 23.7059 | 29.1503 | 33.2902 | 37.4065
IngersollIce Accretion2095RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2095 | 18.9539 | 23.2256 | 28.6027 | 32.7063 | 36.7685
IngersollIce Accretion2100RCP6.0 | Ingersoll | Ice Accretion | RCP6.0 | 2100 | 18.5081 | 22.7453 | 28.055 | 32.1225 | 36.1305
IngersollIce Accretion2023RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2023 | 21.1182 | 25.3183 | 30.628 | 34.6797 | 38.7475
IngersollIce Accretion2025RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2025 | 21.0319 | 25.2411 | 30.5557 | 34.6213 | 38.6824
IngersollIce Accretion2030RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2030 | 20.9457 | 25.1639 | 30.4833 | 34.5629 | 38.6173
IngersollIce Accretion2035RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2035 | 20.8594 | 25.0867 | 30.411 | 34.5045 | 38.5522
IngersollIce Accretion2040RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2040 | 20.6365 | 24.8723 | 30.2147 | 34.306 | 38.3699
IngersollIce Accretion2045RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2045 | 20.4136 | 24.6579 | 30.0183 | 34.1075 | 38.1877
IngersollIce Accretion2050RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2050 | 20.0756 | 24.3577 | 29.7807 | 33.8974 | 38.0184
IngersollIce Accretion2055RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2055 | 19.9606 | 24.272 | 29.7393 | 33.8857 | 38.0314
IngersollIce Accretion2060RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2060 | 19.3997 | 23.7059 | 29.1503 | 33.2902 | 37.4065
IngersollIce Accretion2065RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2065 | 18.9539 | 23.2256 | 28.6027 | 32.7063 | 36.7685
IngersollIce Accretion2070RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2070 | 18.1198 | 22.3251 | 27.6003 | 31.6321 | 35.6097
IngersollIce Accretion2075RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2075 | 17.7316 | 21.9048 | 27.1457 | 31.1417 | 35.0889
IngersollIce Accretion2080RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2080 | 17.3433 | 21.4845 | 26.691 | 30.6512 | 34.5681
IngersollIce Accretion2085RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2085 | 16.3833 | 20.3782 | 25.389 | 29.18 | 32.9666
IngersollIce Accretion2090RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2090 | 15.4234 | 19.2718 | 24.087 | 27.7087 | 31.3652
IngersollIce Accretion2095RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2095 | 15.4234 | 19.2718 | 24.087 | 27.7087 | 31.3652
IngersollIce Accretion2100RCP8.5 | Ingersoll | Ice Accretion | RCP8.5 | 2100 | 15.4234 | 19.2718 | 24.087 | 27.7087 | 31.3652
IngersollWind2023RCP4.5 | Ingersoll | Wind | RCP4.5 | 2023 | 88.8679 | 95.875 | 103.2954 | 110.6789 | 118.0707
IngersollWind2025RCP4.5 | Ingersoll | Wind | RCP4.5 | 2025 | 88.9501 | 95.9841 | 103.4365 | 110.848 | 118.2684
IngersollWind2030RCP4.5 | Ingersoll | Wind | RCP4.5 | 2030 | 89.0323 | 96.0932 | 103.5776 | 111.0172 | 118.4661
IngersollWind2035RCP4.5 | Ingersoll | Wind | RCP4.5 | 2035 | 89.1145 | 96.2023 | 103.7187 | 111.1864 | 118.6637
IngersollWind2040RCP4.5 | Ingersoll | Wind | RCP4.5 | 2040 | 89.1967 | 96.3114 | 103.8598 | 111.3555 | 118.8614
IngersollWind2045RCP4.5 | Ingersoll | Wind | RCP4.5 | 2045 | 89.2789 | 96.4204 | 104.0009 | 111.5247 | 119.0591
IngersollWind2050RCP4.5 | Ingersoll | Wind | RCP4.5 | 2050 | 89.4316 | 96.6149 | 104.2501 | 111.8183 | 119.3986
IngersollWind2055RCP4.5 | Ingersoll | Wind | RCP4.5 | 2055 | 89.502 | 96.7003 | 104.3582 | 111.9427 | 119.5405
IngersollWind2060RCP4.5 | Ingersoll | Wind | RCP4.5 | 2060 | 89.5725 | 96.7857 | 104.4664 | 112.0671 | 119.6824
IngersollWind2065RCP4.5 | Ingersoll | Wind | RCP4.5 | 2065 | 89.6429 | 96.871 | 104.5745 | 112.1916 | 119.8242
IngersollWind2070RCP4.5 | Ingersoll | Wind | RCP4.5 | 2070 | 89.7134 | 96.9564 | 104.6826 | 112.316 | 119.9661
IngersollWind2075RCP4.5 | Ingersoll | Wind | RCP4.5 | 2075 | 89.8015 | 97.0781 | 104.8475 | 112.5179 | 120.2064
IngersollWind2080RCP4.5 | Ingersoll | Wind | RCP4.5 | 2080 | 89.8896 | 97.1999 | 105.0124 | 112.7198 | 120.4467
IngersollWind2085RCP4.5 | Ingersoll | Wind | RCP4.5 | 2085 | 89.9776 | 97.3216 | 105.1773 | 112.9217 | 120.687
IngersollWind2090RCP4.5 | Ingersoll | Wind | RCP4.5 | 2090 | 90.0657 | 97.4434 | 105.3422 | 113.1236 | 120.9273
IngersollWind2095RCP4.5 | Ingersoll | Wind | RCP4.5 | 2095 | 90.1538 | 97.5651 | 105.5071 | 113.3255 | 121.1676
IngersollWind2100RCP4.5 | Ingersoll | Wind | RCP4.5 | 2100 | 90.2419 | 97.6868 | 105.672 | 113.5274 | 121.4079
IngersollWind2023RCP6.0 | Ingersoll | Wind | RCP6.0 | 2023 | 88.8679 | 95.875 | 103.2954 | 110.6789 | 118.0707
IngersollWind2025RCP6.0 | Ingersoll | Wind | RCP6.0 | 2025 | 88.9501 | 95.9841 | 103.4365 | 110.848 | 118.2684
IngersollWind2030RCP6.0 | Ingersoll | Wind | RCP6.0 | 2030 | 89.0323 | 96.0932 | 103.5776 | 111.0172 | 118.4661
IngersollWind2035RCP6.0 | Ingersoll | Wind | RCP6.0 | 2035 | 89.1145 | 96.2023 | 103.7187 | 111.1864 | 118.6637
IngersollWind2040RCP6.0 | Ingersoll | Wind | RCP6.0 | 2040 | 89.1967 | 96.3114 | 103.8598 | 111.3555 | 118.8614
IngersollWind2045RCP6.0 | Ingersoll | Wind | RCP6.0 | 2045 | 89.2789 | 96.4204 | 104.0009 | 111.5247 | 119.0591
IngersollWind2050RCP6.0 | Ingersoll | Wind | RCP6.0 | 2050 | 89.4316 | 96.6149 | 104.2501 | 111.8183 | 119.3986
IngersollWind2055RCP6.0 | Ingersoll | Wind | RCP6.0 | 2055 | 89.502 | 96.7003 | 104.3582 | 111.9427 | 119.5405
IngersollWind2060RCP6.0 | Ingersoll | Wind | RCP6.0 | 2060 | 89.5725 | 96.7857 | 104.4664 | 112.0671 | 119.6824
IngersollWind2065RCP6.0 | Ingersoll | Wind | RCP6.0 | 2065 | 89.6429 | 96.871 | 104.5745 | 112.1916 | 119.8242
IngersollWind2070RCP6.0 | Ingersoll | Wind | RCP6.0 | 2070 | 89.7134 | 96.9564 | 104.6826 | 112.316 | 119.9661
IngersollWind2075RCP6.0 | Ingersoll | Wind | RCP6.0 | 2075 | 89.8455 | 97.139 | 104.9299 | 112.6188 | 120.3265
IngersollWind2080RCP6.0 | Ingersoll | Wind | RCP6.0 | 2080 | 89.9776 | 97.3216 | 105.1773 | 112.9217 | 120.687
IngersollWind2085RCP6.0 | Ingersoll | Wind | RCP6.0 | 2085 | 90.1097 | 97.5042 | 105.4246 | 113.2246 | 121.0475
IngersollWind2090RCP6.0 | Ingersoll | Wind | RCP6.0 | 2090 | 90.603 | 98.1516 | 106.2636 | 114.2259 | 122.218
IngersollWind2095RCP6.0 | Ingersoll | Wind | RCP6.0 | 2095 | 90.9641 | 98.6165 | 106.8552 | 114.9244 | 123.0281
IngersollWind2100RCP6.0 | Ingersoll | Wind | RCP6.0 | 2100 | 91.3252 | 99.0813 | 107.4468 | 115.6229 | 123.8382
IngersollWind2023RCP8.5 | Ingersoll | Wind | RCP8.5 | 2023 | 88.8679 | 95.875 | 103.2954 | 110.6789 | 118.0707
IngersollWind2025RCP8.5 | Ingersoll | Wind | RCP8.5 | 2025 | 89.0323 | 96.0932 | 103.5776 | 111.0172 | 118.4661
IngersollWind2030RCP8.5 | Ingersoll | Wind | RCP8.5 | 2030 | 89.1967 | 96.3114 | 103.8598 | 111.3555 | 118.8614
IngersollWind2035RCP8.5 | Ingersoll | Wind | RCP8.5 | 2035 | 89.3611 | 96.5295 | 104.142 | 111.6939 | 119.2568
IngersollWind2040RCP8.5 | Ingersoll | Wind | RCP8.5 | 2040 | 89.4785 | 96.6718 | 104.3222 | 111.9012 | 119.4932
IngersollWind2045RCP8.5 | Ingersoll | Wind | RCP8.5 | 2045 | 89.596 | 96.8141 | 104.5024 | 112.1086 | 119.7296
IngersollWind2050RCP8.5 | Ingersoll | Wind | RCP8.5 | 2050 | 89.8896 | 97.1999 | 105.0124 | 112.7198 | 120.4467
IngersollWind2055RCP8.5 | Ingersoll | Wind | RCP8.5 | 2055 | 90.0657 | 97.4434 | 105.3422 | 113.1236 | 120.9273
IngersollWind2060RCP8.5 | Ingersoll | Wind | RCP8.5 | 2060 | 90.603 | 98.1516 | 106.2636 | 114.2259 | 122.218
IngersollWind2065RCP8.5 | Ingersoll | Wind | RCP8.5 | 2065 | 90.9641 | 98.6165 | 106.8552 | 114.9244 | 123.0281
IngersollWind2070RCP8.5 | Ingersoll | Wind | RCP8.5 | 2070 | 91.5542 | 99.388 | 107.8514 | 116.1104 | 124.4118
IngersollWind2075RCP8.5 | Ingersoll | Wind | RCP8.5 | 2075 | 91.7832 | 99.6947 | 108.256 | 116.5979 | 124.9855
IngersollWind2080RCP8.5 | Ingersoll | Wind | RCP8.5 | 2080 | 92.0122 | 100.0014 | 108.6606 | 117.0854 | 125.5591
IngersollWind2085RCP8.5 | Ingersoll | Wind | RCP8.5 | 2085 | 92.4614 | 100.5895 | 109.4307 | 118.0076 | 126.6347
IngersollWind2090RCP8.5 | Ingersoll | Wind | RCP8.5 | 2090 | 92.9105 | 101.1777 | 110.2008 | 118.9299 | 127.7103
IngersollWind2095RCP8.5 | Ingersoll | Wind | RCP8.5 | 2095 | 92.9105 | 101.1777 | 110.2008 | 118.9299 | 127.7103
IngersollWind2100RCP8.5 | Ingersoll | Wind | RCP8.5 | 2100 | 92.9105 | 101.1777 | 110.2008 | 118.9299 | 127.7103
Iroquois FallsIce Accretion2023RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2023 | 12.4751 | 14.8354 | 17.838 | 20.1366 | 22.4305
Iroquois FallsIce Accretion2025RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2025 | 12.5231 | 14.8952 | 17.913 | 20.2213 | 22.525
Iroquois FallsIce Accretion2030RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2030 | 12.5712 | 14.9549 | 17.988 | 20.3061 | 22.6195
Iroquois FallsIce Accretion2035RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2035 | 12.6192 | 15.0147 | 18.063 | 20.3908 | 22.714
Iroquois FallsIce Accretion2040RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2040 | 12.6672 | 15.0745 | 18.138 | 20.4756 | 22.8085
Iroquois FallsIce Accretion2045RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2045 | 12.7152 | 15.1342 | 18.213 | 20.5603 | 22.903
Iroquois FallsIce Accretion2050RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2050 | 12.8384 | 15.2926 | 18.414 | 20.7956 | 23.1699
Iroquois FallsIce Accretion2055RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2055 | 12.9135 | 15.3912 | 18.54 | 20.9461 | 23.3423
Iroquois FallsIce Accretion2060RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2060 | 12.9887 | 15.4898 | 18.666 | 21.0966 | 23.5146
Iroquois FallsIce Accretion2065RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2065 | 13.0638 | 15.5884 | 18.792 | 21.2472 | 23.687
Iroquois FallsIce Accretion2070RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2070 | 13.139 | 15.687 | 18.918 | 21.3977 | 23.8594
Iroquois FallsIce Accretion2075RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2075 | 13.1223 | 15.6721 | 18.903 | 21.3841 | 23.8442
Iroquois FallsIce Accretion2080RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2080 | 13.1056 | 15.6571 | 18.888 | 21.3706 | 23.8291
Iroquois FallsIce Accretion2085RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2085 | 13.0889 | 15.6422 | 18.873 | 21.357 | 23.814
Iroquois FallsIce Accretion2090RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2090 | 13.0722 | 15.6272 | 18.858 | 21.3434 | 23.7989
Iroquois FallsIce Accretion2095RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2095 | 13.0555 | 15.6123 | 18.843 | 21.3299 | 23.7838
Iroquois FallsIce Accretion2100RCP4.5 | Iroquois Falls | Ice Accretion | RCP4.5 | 2100 | 13.0388 | 15.5974 | 18.828 | 21.3163 | 23.7686
Iroquois FallsIce Accretion2023RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2023 | 12.4751 | 14.8354 | 17.838 | 20.1366 | 22.4305
Iroquois FallsIce Accretion2025RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2025 | 12.5231 | 14.8952 | 17.913 | 20.2213 | 22.525
Iroquois FallsIce Accretion2030RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2030 | 12.5712 | 14.9549 | 17.988 | 20.3061 | 22.6195
Iroquois FallsIce Accretion2035RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2035 | 12.6192 | 15.0147 | 18.063 | 20.3908 | 22.714
Iroquois FallsIce Accretion2040RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2040 | 12.6672 | 15.0745 | 18.138 | 20.4756 | 22.8085
Iroquois FallsIce Accretion2045RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2045 | 12.7152 | 15.1342 | 18.213 | 20.5603 | 22.903
Iroquois FallsIce Accretion2050RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2050 | 12.8384 | 15.2926 | 18.414 | 20.7956 | 23.1699
Iroquois FallsIce Accretion2055RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2055 | 12.9135 | 15.3912 | 18.54 | 20.9461 | 23.3423
Iroquois FallsIce Accretion2060RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2060 | 12.9887 | 15.4898 | 18.666 | 21.0966 | 23.5146
Iroquois FallsIce Accretion2065RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2065 | 13.0638 | 15.5884 | 18.792 | 21.2472 | 23.687
Iroquois FallsIce Accretion2070RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2070 | 13.139 | 15.687 | 18.918 | 21.3977 | 23.8594
Iroquois FallsIce Accretion2075RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2075 | 13.1139 | 15.6646 | 18.8955 | 21.3773 | 23.8367
Iroquois FallsIce Accretion2080RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2080 | 13.0889 | 15.6422 | 18.873 | 21.357 | 23.814
Iroquois FallsIce Accretion2085RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2085 | 13.0638 | 15.6198 | 18.8505 | 21.3367 | 23.7913
Iroquois FallsIce Accretion2090RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2090 | 12.926 | 15.4729 | 18.696 | 21.1672 | 23.6174
Iroquois FallsIce Accretion2095RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2095 | 12.8133 | 15.3484 | 18.564 | 21.018 | 23.4662
Iroquois FallsIce Accretion2100RCP6.0 | Iroquois Falls | Ice Accretion | RCP6.0 | 2100 | 12.7006 | 15.2239 | 18.432 | 20.8688 | 23.315
Iroquois FallsIce Accretion2023RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2023 | 12.4751 | 14.8354 | 17.838 | 20.1366 | 22.4305
Iroquois FallsIce Accretion2025RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2025 | 12.5712 | 14.9549 | 17.988 | 20.3061 | 22.6195
Iroquois FallsIce Accretion2030RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2030 | 12.6672 | 15.0745 | 18.138 | 20.4756 | 22.8085
Iroquois FallsIce Accretion2035RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2035 | 12.7632 | 15.194 | 18.288 | 20.6451 | 22.9975
Iroquois FallsIce Accretion2040RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2040 | 12.8885 | 15.3583 | 18.498 | 20.896 | 23.2848
Iroquois FallsIce Accretion2045RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2045 | 13.0137 | 15.5227 | 18.708 | 21.1468 | 23.5721
Iroquois FallsIce Accretion2050RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2050 | 13.1056 | 15.6571 | 18.888 | 21.3706 | 23.8291
Iroquois FallsIce Accretion2055RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2055 | 13.0722 | 15.6272 | 18.858 | 21.3434 | 23.7989
Iroquois FallsIce Accretion2060RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2060 | 12.926 | 15.4729 | 18.696 | 21.1672 | 23.6174
Iroquois FallsIce Accretion2065RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2065 | 12.8133 | 15.3484 | 18.564 | 21.018 | 23.4662
Iroquois FallsIce Accretion2070RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2070 | 12.6254 | 15.1492 | 18.354 | 20.7943 | 23.2319
Iroquois FallsIce Accretion2075RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2075 | 12.5503 | 15.0745 | 18.276 | 20.7197 | 23.1487
Iroquois FallsIce Accretion2080RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2080 | 12.4751 | 14.9998 | 18.198 | 20.6451 | 23.0656
Iroquois FallsIce Accretion2085RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2085 | 12.3374 | 14.8728 | 18.072 | 20.5231 | 22.9522
Iroquois FallsIce Accretion2090RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2090 | 12.1996 | 14.7458 | 17.946 | 20.401 | 22.8388
Iroquois FallsIce Accretion2095RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2095 | 12.1996 | 14.7458 | 17.946 | 20.401 | 22.8388
Iroquois FallsIce Accretion2100RCP8.5 | Iroquois Falls | Ice Accretion | RCP8.5 | 2100 | 12.1996 | 14.7458 | 17.946 | 20.401 | 22.8388
Iroquois FallsWind2023RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2023 | 75.0392 | 80.8598 | 86.9976 | 93.1242 | 99.2557
Iroquois FallsWind2025RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2025 | 75.0305 | 80.8331 | 86.946 | 93.0537 | 99.1642
Iroquois FallsWind2030RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2030 | 75.0219 | 80.8065 | 86.8944 | 92.9831 | 99.0727
Iroquois FallsWind2035RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2035 | 75.0132 | 80.7798 | 86.8428 | 92.9126 | 98.9812
Iroquois FallsWind2040RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2040 | 75.0046 | 80.7531 | 86.7912 | 92.842 | 98.8897
Iroquois FallsWind2045RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2045 | 74.9959 | 80.7265 | 86.7396 | 92.7715 | 98.7982
Iroquois FallsWind2050RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2050 | 75.0199 | 80.7478 | 86.7534 | 92.7819 | 98.8028
Iroquois FallsWind2055RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2055 | 75.0526 | 80.7958 | 86.8187 | 92.8629 | 98.8988
Iroquois FallsWind2060RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2060 | 75.0853 | 80.8438 | 86.8841 | 92.9439 | 98.9949
Iroquois FallsWind2065RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2065 | 75.1179 | 80.8918 | 86.9494 | 93.0249 | 99.091
Iroquois FallsWind2070RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2070 | 75.1506 | 80.9398 | 87.0148 | 93.1058 | 99.1871
Iroquois FallsWind2075RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2075 | 75.1803 | 80.9584 | 87.0234 | 93.1043 | 99.1773
Iroquois FallsWind2080RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2080 | 75.21 | 80.9771 | 87.032 | 93.1028 | 99.1675
Iroquois FallsWind2085RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2085 | 75.2397 | 80.9957 | 87.0406 | 93.1012 | 99.1577
Iroquois FallsWind2090RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2090 | 75.2694 | 81.0144 | 87.0492 | 93.0997 | 99.1479
Iroquois FallsWind2095RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2095 | 75.2991 | 81.0331 | 87.0578 | 93.0982 | 99.138
Iroquois FallsWind2100RCP4.5 | Iroquois Falls | Wind | RCP4.5 | 2100 | 75.3288 | 81.0517 | 87.0664 | 93.0966 | 99.1282
Iroquois FallsWind2023RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2023 | 75.0392 | 80.8598 | 86.9976 | 93.1242 | 99.2557
Iroquois FallsWind2025RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2025 | 75.0305 | 80.8331 | 86.946 | 93.0537 | 99.1642
Iroquois FallsWind2030RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2030 | 75.0219 | 80.8065 | 86.8944 | 92.9831 | 99.0727
Iroquois FallsWind2035RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2035 | 75.0132 | 80.7798 | 86.8428 | 92.9126 | 98.9812
Iroquois FallsWind2040RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2040 | 75.0046 | 80.7531 | 86.7912 | 92.842 | 98.8897
Iroquois FallsWind2045RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2045 | 74.9959 | 80.7265 | 86.7396 | 92.7715 | 98.7982
Iroquois FallsWind2050RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2050 | 75.0199 | 80.7478 | 86.7534 | 92.7819 | 98.8028
Iroquois FallsWind2055RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2055 | 75.0526 | 80.7958 | 86.8187 | 92.8629 | 98.8988
Iroquois FallsWind2060RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2060 | 75.0853 | 80.8438 | 86.8841 | 92.9439 | 98.9949
Iroquois FallsWind2065RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2065 | 75.1179 | 80.8918 | 86.9494 | 93.0249 | 99.091
Iroquois FallsWind2070RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2070 | 75.1506 | 80.9398 | 87.0148 | 93.1058 | 99.1871
Iroquois FallsWind2075RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2075 | 75.1952 | 80.9678 | 87.0277 | 93.1035 | 99.1724
Iroquois FallsWind2080RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2080 | 75.2397 | 80.9957 | 87.0406 | 93.1012 | 99.1577
Iroquois FallsWind2085RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2085 | 75.2843 | 81.0237 | 87.0535 | 93.0989 | 99.143
Iroquois FallsWind2090RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2090 | 75.5863 | 81.3743 | 87.4649 | 93.5598 | 99.6577
Iroquois FallsWind2095RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2095 | 75.8437 | 81.6969 | 87.8633 | 94.023 | 100.1871
Iroquois FallsWind2100RCP6.0 | Iroquois Falls | Wind | RCP6.0 | 2100 | 76.1011 | 82.0195 | 88.2618 | 94.4861 | 100.7165
Iroquois FallsWind2023RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2023 | 75.0392 | 80.8598 | 86.9976 | 93.1242 | 99.2557
Iroquois FallsWind2025RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2025 | 75.0219 | 80.8065 | 86.8944 | 92.9831 | 99.0727
Iroquois FallsWind2030RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2030 | 75.0046 | 80.7531 | 86.7912 | 92.842 | 98.8897
Iroquois FallsWind2035RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2035 | 74.9872 | 80.6998 | 86.688 | 92.7009 | 98.7067
Iroquois FallsWind2040RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2040 | 75.0417 | 80.7798 | 86.7969 | 92.8359 | 98.8668
Iroquois FallsWind2045RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2045 | 75.0961 | 80.8598 | 86.9059 | 92.9709 | 99.0269
Iroquois FallsWind2050RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2050 | 75.21 | 80.9771 | 87.032 | 93.1028 | 99.1675
Iroquois FallsWind2055RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2055 | 75.2694 | 81.0144 | 87.0492 | 93.0997 | 99.1479
Iroquois FallsWind2060RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2060 | 75.5863 | 81.3743 | 87.4649 | 93.5598 | 99.6577
Iroquois FallsWind2065RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2065 | 75.8437 | 81.6969 | 87.8633 | 94.023 | 100.1871
Iroquois FallsWind2070RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2070 | 76.2868 | 82.2114 | 88.4625 | 94.6947 | 100.9354
Iroquois FallsWind2075RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2075 | 76.4724 | 82.4034 | 88.6631 | 94.9033 | 101.1544
Iroquois FallsWind2080RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2080 | 76.6581 | 82.5953 | 88.8638 | 95.1119 | 101.3734
Iroquois FallsWind2085RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2085 | 76.7917 | 82.7873 | 89.1175 | 95.4247 | 101.741
Iroquois FallsWind2090RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2090 | 76.9254 | 82.9793 | 89.3712 | 95.7376 | 102.1087
Iroquois FallsWind2095RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2095 | 76.9254 | 82.9793 | 89.3712 | 95.7376 | 102.1087
Iroquois FallsWind2100RCP8.5 | Iroquois Falls | Wind | RCP8.5 | 2100 | 76.9254 | 82.9793 | 89.3712 | 95.7376 | 102.1087
JellicoeIce Accretion2023RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2023 | 9.9269 | 11.8175 | 14.224 | 16.0573 | 17.887
JellicoeIce Accretion2025RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2025 | 10.0049 | 11.9105 | 14.3337 | 16.1839 | 18.0281
JellicoeIce Accretion2030RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2030 | 10.0828 | 12.0035 | 14.4433 | 16.3104 | 18.1692
JellicoeIce Accretion2035RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2035 | 10.1607 | 12.0964 | 14.553 | 16.437 | 18.3103
JellicoeIce Accretion2040RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2040 | 10.2387 | 12.1894 | 14.6627 | 16.5635 | 18.4514
JellicoeIce Accretion2045RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2045 | 10.3166 | 12.2823 | 14.7723 | 16.6901 | 18.5926
JellicoeIce Accretion2050RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2050 | 10.4355 | 12.4195 | 14.9352 | 16.8736 | 18.7972
JellicoeIce Accretion2055RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2055 | 10.4764 | 12.4636 | 14.9884 | 16.9306 | 18.8607
JellicoeIce Accretion2060RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2060 | 10.5173 | 12.5078 | 15.0416 | 16.9875 | 18.9242
JellicoeIce Accretion2065RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2065 | 10.5582 | 12.5519 | 15.0948 | 17.0445 | 18.9877
JellicoeIce Accretion2070RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2070 | 10.5991 | 12.5961 | 15.148 | 17.1014 | 19.0512
JellicoeIce Accretion2075RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2075 | 10.6219 | 12.6251 | 15.1807 | 17.1383 | 19.0924
JellicoeIce Accretion2080RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2080 | 10.6446 | 12.6542 | 15.2133 | 17.1752 | 19.1335
JellicoeIce Accretion2085RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2085 | 10.6673 | 12.6832 | 15.246 | 17.2122 | 19.1747
JellicoeIce Accretion2090RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2090 | 10.6901 | 12.7123 | 15.2787 | 17.2491 | 19.2158
JellicoeIce Accretion2095RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2095 | 10.7128 | 12.7413 | 15.3113 | 17.286 | 19.257
JellicoeIce Accretion2100RCP4.5 | Jellicoe | Ice Accretion | RCP4.5 | 2100 | 10.7355 | 12.7704 | 15.344 | 17.3229 | 19.2982
JellicoeIce Accretion2023RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2023 | 9.9269 | 11.8175 | 14.224 | 16.0573 | 17.887
JellicoeIce Accretion2025RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2025 | 10.0049 | 11.9105 | 14.3337 | 16.1839 | 18.0281
JellicoeIce Accretion2030RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2030 | 10.0828 | 12.0035 | 14.4433 | 16.3104 | 18.1692
JellicoeIce Accretion2035RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2035 | 10.1607 | 12.0964 | 14.553 | 16.437 | 18.3103
JellicoeIce Accretion2040RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2040 | 10.2387 | 12.1894 | 14.6627 | 16.5635 | 18.4514
JellicoeIce Accretion2045RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2045 | 10.3166 | 12.2823 | 14.7723 | 16.6901 | 18.5926
JellicoeIce Accretion2050RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2050 | 10.4355 | 12.4195 | 14.9352 | 16.8736 | 18.7972
JellicoeIce Accretion2055RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2055 | 10.4764 | 12.4636 | 14.9884 | 16.9306 | 18.8607
JellicoeIce Accretion2060RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2060 | 10.5173 | 12.5078 | 15.0416 | 16.9875 | 18.9242
JellicoeIce Accretion2065RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2065 | 10.5582 | 12.5519 | 15.0948 | 17.0445 | 18.9877
JellicoeIce Accretion2070RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2070 | 10.5991 | 12.5961 | 15.148 | 17.1014 | 19.0512
JellicoeIce Accretion2075RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2075 | 10.6332 | 12.6397 | 15.197 | 17.1568 | 19.1129
JellicoeIce Accretion2080RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2080 | 10.6673 | 12.6832 | 15.246 | 17.2122 | 19.1747
JellicoeIce Accretion2085RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2085 | 10.7014 | 12.7268 | 15.295 | 17.2675 | 19.2364
JellicoeIce Accretion2090RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2090 | 10.6868 | 12.7045 | 15.26 | 17.228 | 19.1864
JellicoeIce Accretion2095RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2095 | 10.6381 | 12.6387 | 15.176 | 17.1331 | 19.0747
JellicoeIce Accretion2100RCP6.0 | Jellicoe | Ice Accretion | RCP6.0 | 2100 | 10.5894 | 12.5728 | 15.092 | 17.0381 | 18.963
JellicoeIce Accretion2023RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2023 | 9.9269 | 11.8175 | 14.224 | 16.0573 | 17.887
JellicoeIce Accretion2025RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2025 | 10.0828 | 12.0035 | 14.4433 | 16.3104 | 18.1692
JellicoeIce Accretion2030RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2030 | 10.2387 | 12.1894 | 14.6627 | 16.5635 | 18.4514
JellicoeIce Accretion2035RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2035 | 10.3945 | 12.3753 | 14.882 | 16.8167 | 18.7337
JellicoeIce Accretion2040RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2040 | 10.4627 | 12.4489 | 14.9707 | 16.9116 | 18.8395
JellicoeIce Accretion2045RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2045 | 10.5309 | 12.5225 | 15.0593 | 17.0065 | 18.9454
JellicoeIce Accretion2050RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2050 | 10.6446 | 12.6542 | 15.2133 | 17.1752 | 19.1335
JellicoeIce Accretion2055RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2055 | 10.6901 | 12.7123 | 15.2787 | 17.2491 | 19.2158
JellicoeIce Accretion2060RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2060 | 10.6868 | 12.7045 | 15.26 | 17.228 | 19.1864
JellicoeIce Accretion2065RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2065 | 10.6381 | 12.6387 | 15.176 | 17.1331 | 19.0747
JellicoeIce Accretion2070RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2070 | 10.6056 | 12.6077 | 15.1527 | 17.1067 | 19.0512
JellicoeIce Accretion2075RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2075 | 10.6219 | 12.6426 | 15.2133 | 17.1752 | 19.1394
JellicoeIce Accretion2080RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2080 | 10.6381 | 12.6774 | 15.274 | 17.2438 | 19.2276
JellicoeIce Accretion2085RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2085 | 10.5017 | 12.5322 | 15.113 | 17.0777 | 19.0512
JellicoeIce Accretion2090RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2090 | 10.3653 | 12.3869 | 14.952 | 16.9116 | 18.8748
JellicoeIce Accretion2095RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2095 | 10.3653 | 12.3869 | 14.952 | 16.9116 | 18.8748
JellicoeIce Accretion2100RCP8.5 | Jellicoe | Ice Accretion | RCP8.5 | 2100 | 10.3653 | 12.3869 | 14.952 | 16.9116 | 18.8748
JellicoeWind2023RCP4.5 | Jellicoe | Wind | RCP4.5 | 2023 | 73.6382 | 79.2951 | 85.2465 | 91.2047 | 97.1616
JellicoeWind2025RCP4.5 | Jellicoe | Wind | RCP4.5 | 2025 | 73.7397 | 79.4163 | 85.391 | 91.3699 | 97.3474
JellicoeWind2030RCP4.5 | Jellicoe | Wind | RCP4.5 | 2030 | 73.8413 | 79.5375 | 85.5355 | 91.5351 | 97.5331
JellicoeWind2035RCP4.5 | Jellicoe | Wind | RCP4.5 | 2035 | 73.9428 | 79.6587 | 85.68 | 91.7003 | 97.7188
JellicoeWind2040RCP4.5 | Jellicoe | Wind | RCP4.5 | 2040 | 74.0443 | 79.7799 | 85.8245 | 91.8656 | 97.9045
JellicoeWind2045RCP4.5 | Jellicoe | Wind | RCP4.5 | 2045 | 74.1459 | 79.9011 | 85.969 | 92.0308 | 98.0903
JellicoeWind2050RCP4.5 | Jellicoe | Wind | RCP4.5 | 2050 | 74.3795 | 80.1757 | 86.2937 | 92.3979 | 98.5008
JellicoeWind2055RCP4.5 | Jellicoe | Wind | RCP4.5 | 2055 | 74.5116 | 80.329 | 86.4739 | 92.5998 | 98.7256
JellicoeWind2060RCP4.5 | Jellicoe | Wind | RCP4.5 | 2060 | 74.6437 | 80.4824 | 86.6541 | 92.8017 | 98.9504
JellicoeWind2065RCP4.5 | Jellicoe | Wind | RCP4.5 | 2065 | 74.7759 | 80.6357 | 86.8343 | 93.0037 | 99.1752
JellicoeWind2070RCP4.5 | Jellicoe | Wind | RCP4.5 | 2070 | 74.908 | 80.7891 | 87.0145 | 93.2056 | 99.4
JellicoeWind2075RCP4.5 | Jellicoe | Wind | RCP4.5 | 2075 | 74.9471 | 80.8339 | 87.0641 | 93.2601 | 99.4614
JellicoeWind2080RCP4.5 | Jellicoe | Wind | RCP4.5 | 2080 | 74.9863 | 80.8787 | 87.1137 | 93.3147 | 99.5228
JellicoeWind2085RCP4.5 | Jellicoe | Wind | RCP4.5 | 2085 | 75.0254 | 80.9235 | 87.1633 | 93.3693 | 99.5841
JellicoeWind2090RCP4.5 | Jellicoe | Wind | RCP4.5 | 2090 | 75.0645 | 80.9683 | 87.2128 | 93.4238 | 99.6455
JellicoeWind2095RCP4.5 | Jellicoe | Wind | RCP4.5 | 2095 | 75.1037 | 81.0131 | 87.2624 | 93.4784 | 99.7069
JellicoeWind2100RCP4.5 | Jellicoe | Wind | RCP4.5 | 2100 | 75.1428 | 81.0579 | 87.312 | 93.533 | 99.7682
JellicoeWind2023RCP6.0 | Jellicoe | Wind | RCP6.0 | 2023 | 73.6382 | 79.2951 | 85.2465 | 91.2047 | 97.1616
JellicoeWind2025RCP6.0 | Jellicoe | Wind | RCP6.0 | 2025 | 73.7397 | 79.4163 | 85.391 | 91.3699 | 97.3474
JellicoeWind2030RCP6.0 | Jellicoe | Wind | RCP6.0 | 2030 | 73.8413 | 79.5375 | 85.5355 | 91.5351 | 97.5331
JellicoeWind2035RCP6.0 | Jellicoe | Wind | RCP6.0 | 2035 | 73.9428 | 79.6587 | 85.68 | 91.7003 | 97.7188
JellicoeWind2040RCP6.0 | Jellicoe | Wind | RCP6.0 | 2040 | 74.0443 | 79.7799 | 85.8245 | 91.8656 | 97.9045
JellicoeWind2045RCP6.0 | Jellicoe | Wind | RCP6.0 | 2045 | 74.1459 | 79.9011 | 85.969 | 92.0308 | 98.0903
JellicoeWind2050RCP6.0 | Jellicoe | Wind | RCP6.0 | 2050 | 74.3795 | 80.1757 | 86.2937 | 92.3979 | 98.5008
JellicoeWind2055RCP6.0 | Jellicoe | Wind | RCP6.0 | 2055 | 74.5116 | 80.329 | 86.4739 | 92.5998 | 98.7256
JellicoeWind2060RCP6.0 | Jellicoe | Wind | RCP6.0 | 2060 | 74.6437 | 80.4824 | 86.6541 | 92.8017 | 98.9504
JellicoeWind2065RCP6.0 | Jellicoe | Wind | RCP6.0 | 2065 | 74.7759 | 80.6357 | 86.8343 | 93.0037 | 99.1752
JellicoeWind2070RCP6.0 | Jellicoe | Wind | RCP6.0 | 2070 | 74.908 | 80.7891 | 87.0145 | 93.2056 | 99.4
JellicoeWind2075RCP6.0 | Jellicoe | Wind | RCP6.0 | 2075 | 74.9667 | 80.8563 | 87.0889 | 93.2874 | 99.4921
JellicoeWind2080RCP6.0 | Jellicoe | Wind | RCP6.0 | 2080 | 75.0254 | 80.9235 | 87.1633 | 93.3693 | 99.5841
JellicoeWind2085RCP6.0 | Jellicoe | Wind | RCP6.0 | 2085 | 75.0841 | 80.9907 | 87.2376 | 93.4511 | 99.6762
JellicoeWind2090RCP6.0 | Jellicoe | Wind | RCP6.0 | 2090 | 75.1918 | 81.1237 | 87.397 | 93.6361 | 99.8877
JellicoeWind2095RCP6.0 | Jellicoe | Wind | RCP6.0 | 2095 | 75.2407 | 81.1896 | 87.482 | 93.7391 | 100.0073
JellicoeWind2100RCP6.0 | Jellicoe | Wind | RCP6.0 | 2100 | 75.2896 | 81.2555 | 87.567 | 93.8422 | 100.1268
JellicoeWind2023RCP8.5 | Jellicoe | Wind | RCP8.5 | 2023 | 73.6382 | 79.2951 | 85.2465 | 91.2047 | 97.1616
JellicoeWind2025RCP8.5 | Jellicoe | Wind | RCP8.5 | 2025 | 73.8413 | 79.5375 | 85.5355 | 91.5351 | 97.5331
JellicoeWind2030RCP8.5 | Jellicoe | Wind | RCP8.5 | 2030 | 74.0443 | 79.7799 | 85.8245 | 91.8656 | 97.9045
JellicoeWind2035RCP8.5 | Jellicoe | Wind | RCP8.5 | 2035 | 74.2474 | 80.0223 | 86.1135 | 92.196 | 98.276
JellicoeWind2040RCP8.5 | Jellicoe | Wind | RCP8.5 | 2040 | 74.4676 | 80.2779 | 86.4138 | 92.5325 | 98.6507
JellicoeWind2045RCP8.5 | Jellicoe | Wind | RCP8.5 | 2045 | 74.6878 | 80.5335 | 86.7142 | 92.869 | 99.0253
JellicoeWind2050RCP8.5 | Jellicoe | Wind | RCP8.5 | 2050 | 74.9863 | 80.8787 | 87.1137 | 93.3147 | 99.5228
JellicoeWind2055RCP8.5 | Jellicoe | Wind | RCP8.5 | 2055 | 75.0645 | 80.9683 | 87.2128 | 93.4238 | 99.6455
JellicoeWind2060RCP8.5 | Jellicoe | Wind | RCP8.5 | 2060 | 75.1918 | 81.1237 | 87.397 | 93.6361 | 99.8877
JellicoeWind2065RCP8.5 | Jellicoe | Wind | RCP8.5 | 2065 | 75.2407 | 81.1896 | 87.482 | 93.7391 | 100.0073
JellicoeWind2070RCP8.5 | Jellicoe | Wind | RCP8.5 | 2070 | 75.3288 | 81.3029 | 87.6265 | 93.9119 | 100.2043
JellicoeWind2075RCP8.5 | Jellicoe | Wind | RCP8.5 | 2075 | 75.3679 | 81.3504 | 87.686 | 93.9817 | 100.2818
JellicoeWind2080RCP8.5 | Jellicoe | Wind | RCP8.5 | 2080 | 75.4071 | 81.3978 | 87.7455 | 94.0514 | 100.3593
JellicoeWind2085RCP8.5 | Jellicoe | Wind | RCP8.5 | 2085 | 75.5979 | 81.6389 | 88.0472 | 94.4061 | 100.7663
JellicoeWind2090RCP8.5 | Jellicoe | Wind | RCP8.5 | 2090 | 75.7887 | 81.88 | 88.349 | 94.7608 | 101.1733
JellicoeWind2095RCP8.5 | Jellicoe | Wind | RCP8.5 | 2095 | 75.7887 | 81.88 | 88.349 | 94.7608 | 101.1733
JellicoeWind2100RCP8.5 | Jellicoe | Wind | RCP8.5 | 2100 | 75.7887 | 81.88 | 88.349 | 94.7608 | 101.1733
KapuskasingIce Accretion2023RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2023 | 10.7195 | 12.7737 | 15.375 | 17.3568 | 19.3536
KapuskasingIce Accretion2025RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2025 | 10.77 | 12.8401 | 15.465 | 17.4642 | 19.4764
KapuskasingIce Accretion2030RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2030 | 10.8204 | 12.9065 | 15.555 | 17.5715 | 19.5993
KapuskasingIce Accretion2035RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2035 | 10.8709 | 12.9729 | 15.645 | 17.6789 | 19.7221
KapuskasingIce Accretion2040RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2040 | 10.9213 | 13.0393 | 15.735 | 17.7862 | 19.845
KapuskasingIce Accretion2045RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2045 | 10.9718 | 13.1057 | 15.825 | 17.8936 | 19.9678
KapuskasingIce Accretion2050RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2050 | 11.0723 | 13.2244 | 15.966 | 18.0551 | 20.1474
KapuskasingIce Accretion2055RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2055 | 11.1224 | 13.2767 | 16.017 | 18.1094 | 20.2041
KapuskasingIce Accretion2060RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2060 | 11.1725 | 13.329 | 16.068 | 18.1636 | 20.2608
KapuskasingIce Accretion2065RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2065 | 11.2226 | 13.3813 | 16.119 | 18.2179 | 20.3175
KapuskasingIce Accretion2070RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2070 | 11.2727 | 13.4335 | 16.17 | 18.2721 | 20.3742
KapuskasingIce Accretion2075RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2075 | 11.3058 | 13.4792 | 16.23 | 18.3427 | 20.4561
KapuskasingIce Accretion2080RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2080 | 11.3388 | 13.5248 | 16.29 | 18.4134 | 20.538
KapuskasingIce Accretion2085RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2085 | 11.3719 | 13.5705 | 16.35 | 18.484 | 20.6199
KapuskasingIce Accretion2090RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2090 | 11.4049 | 13.6161 | 16.41 | 18.5546 | 20.7018
KapuskasingIce Accretion2095RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2095 | 11.438 | 13.6618 | 16.47 | 18.6252 | 20.7837
KapuskasingIce Accretion2100RCP4.5 | Kapuskasing | Ice Accretion | RCP4.5 | 2100 | 11.471 | 13.7074 | 16.53 | 18.6959 | 20.8656
KapuskasingIce Accretion2023RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2023 | 10.7195 | 12.7737 | 15.375 | 17.3568 | 19.3536
KapuskasingIce Accretion2025RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2025 | 10.77 | 12.8401 | 15.465 | 17.4642 | 19.4764
KapuskasingIce Accretion2030RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2030 | 10.8204 | 12.9065 | 15.555 | 17.5715 | 19.5993
KapuskasingIce Accretion2035RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2035 | 10.8709 | 12.9729 | 15.645 | 17.6789 | 19.7221
KapuskasingIce Accretion2040RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2040 | 10.9213 | 13.0393 | 15.735 | 17.7862 | 19.845
KapuskasingIce Accretion2045RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2045 | 10.9718 | 13.1057 | 15.825 | 17.8936 | 19.9678
KapuskasingIce Accretion2050RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2050 | 11.0723 | 13.2244 | 15.966 | 18.0551 | 20.1474
KapuskasingIce Accretion2055RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2055 | 11.1224 | 13.2767 | 16.017 | 18.1094 | 20.2041
KapuskasingIce Accretion2060RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2060 | 11.1725 | 13.329 | 16.068 | 18.1636 | 20.2608
KapuskasingIce Accretion2065RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2065 | 11.2226 | 13.3813 | 16.119 | 18.2179 | 20.3175
KapuskasingIce Accretion2070RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2070 | 11.2727 | 13.4335 | 16.17 | 18.2721 | 20.3742
KapuskasingIce Accretion2075RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2075 | 11.3223 | 13.502 | 16.26 | 18.378 | 20.497
KapuskasingIce Accretion2080RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2080 | 11.3719 | 13.5705 | 16.35 | 18.484 | 20.6199
KapuskasingIce Accretion2085RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2085 | 11.4214 | 13.639 | 16.44 | 18.5899 | 20.7428
KapuskasingIce Accretion2090RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2090 | 11.4536 | 13.7033 | 16.55 | 18.7297 | 20.9097
KapuskasingIce Accretion2095RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2095 | 11.4362 | 13.6991 | 16.57 | 18.7636 | 20.9538
KapuskasingIce Accretion2100RCP6.0 | Kapuskasing | Ice Accretion | RCP6.0 | 2100 | 11.4188 | 13.695 | 16.59 | 18.7975 | 20.9979
KapuskasingIce Accretion2023RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2023 | 10.7195 | 12.7737 | 15.375 | 17.3568 | 19.3536
KapuskasingIce Accretion2025RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2025 | 10.8204 | 12.9065 | 15.555 | 17.5715 | 19.5993
KapuskasingIce Accretion2030RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2030 | 10.9213 | 13.0393 | 15.735 | 17.7862 | 19.845
KapuskasingIce Accretion2035RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2035 | 11.0222 | 13.1721 | 15.915 | 18.0009 | 20.0907
KapuskasingIce Accretion2040RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2040 | 11.1057 | 13.2592 | 16 | 18.0913 | 20.1852
KapuskasingIce Accretion2045RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2045 | 11.1892 | 13.3464 | 16.085 | 18.1817 | 20.2797
KapuskasingIce Accretion2050RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2050 | 11.3388 | 13.5248 | 16.29 | 18.4134 | 20.538
KapuskasingIce Accretion2055RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2055 | 11.4049 | 13.6161 | 16.41 | 18.5546 | 20.7018
KapuskasingIce Accretion2060RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2060 | 11.4536 | 13.7033 | 16.55 | 18.7297 | 20.9097
KapuskasingIce Accretion2065RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2065 | 11.4362 | 13.6991 | 16.57 | 18.7636 | 20.9538
KapuskasingIce Accretion2070RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2070 | 11.4188 | 13.7157 | 16.63 | 18.8484 | 21.0672
KapuskasingIce Accretion2075RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2075 | 11.4188 | 13.7365 | 16.67 | 18.8993 | 21.1365
KapuskasingIce Accretion2080RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2080 | 11.4188 | 13.7572 | 16.71 | 18.9501 | 21.2058
KapuskasingIce Accretion2085RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2085 | 11.2623 | 13.5954 | 16.545 | 18.7806 | 21.0357
KapuskasingIce Accretion2090RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2090 | 11.1057 | 13.4335 | 16.38 | 18.6111 | 20.8656
KapuskasingIce Accretion2095RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2095 | 11.1057 | 13.4335 | 16.38 | 18.6111 | 20.8656
KapuskasingIce Accretion2100RCP8.5 | Kapuskasing | Ice Accretion | RCP8.5 | 2100 | 11.1057 | 13.4335 | 16.38 | 18.6111 | 20.8656
KapuskasingWind2023RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2023 | 74.4382 | 80.2357 | 86.3515 | 92.4507 | 98.5473
KapuskasingWind2025RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2025 | 74.5948 | 80.4215 | 86.5739 | 92.7038 | 98.8315
KapuskasingWind2030RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2030 | 74.7514 | 80.6073 | 86.7963 | 92.957 | 99.1158
KapuskasingWind2035RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2035 | 74.908 | 80.7931 | 87.0188 | 93.2101 | 99.4
KapuskasingWind2040RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2040 | 75.0645 | 80.9788 | 87.2412 | 93.4633 | 99.6843
KapuskasingWind2045RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2045 | 75.2211 | 81.1646 | 87.4636 | 93.7164 | 99.9685
KapuskasingWind2050RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2050 | 75.385 | 81.3519 | 87.6775 | 93.955 | 100.2314
KapuskasingWind2055RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2055 | 75.3924 | 81.3535 | 87.669 | 93.9404 | 100.2101
KapuskasingWind2060RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2060 | 75.3997 | 81.3551 | 87.6605 | 93.9259 | 100.1888
KapuskasingWind2065RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2065 | 75.4071 | 81.3567 | 87.652 | 93.9113 | 100.1675
KapuskasingWind2070RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2070 | 75.4144 | 81.3583 | 87.6435 | 93.8968 | 100.1462
KapuskasingWind2075RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2075 | 75.4217 | 81.3543 | 87.6265 | 93.8695 | 100.109
KapuskasingWind2080RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2080 | 75.4291 | 81.3504 | 87.6095 | 93.8422 | 100.0719
KapuskasingWind2085RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2085 | 75.4364 | 81.3464 | 87.5925 | 93.8149 | 100.0347
KapuskasingWind2090RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2090 | 75.4438 | 81.3424 | 87.5755 | 93.7876 | 99.9976
KapuskasingWind2095RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2095 | 75.4511 | 81.3385 | 87.5585 | 93.7604 | 99.9604
KapuskasingWind2100RCP4.5 | Kapuskasing | Wind | RCP4.5 | 2100 | 75.4584 | 81.3345 | 87.5415 | 93.7331 | 99.9233
KapuskasingWind2023RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2023 | 74.4382 | 80.2357 | 86.3515 | 92.4507 | 98.5473
KapuskasingWind2025RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2025 | 74.5948 | 80.4215 | 86.5739 | 92.7038 | 98.8315
KapuskasingWind2030RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2030 | 74.7514 | 80.6073 | 86.7963 | 92.957 | 99.1158
KapuskasingWind2035RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2035 | 74.908 | 80.7931 | 87.0188 | 93.2101 | 99.4
KapuskasingWind2040RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2040 | 75.0645 | 80.9788 | 87.2412 | 93.4633 | 99.6843
KapuskasingWind2045RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2045 | 75.2211 | 81.1646 | 87.4636 | 93.7164 | 99.9685
KapuskasingWind2050RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2050 | 75.385 | 81.3519 | 87.6775 | 93.955 | 100.2314
KapuskasingWind2055RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2055 | 75.3924 | 81.3535 | 87.669 | 93.9404 | 100.2101
KapuskasingWind2060RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2060 | 75.3997 | 81.3551 | 87.6605 | 93.9259 | 100.1888
KapuskasingWind2065RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2065 | 75.4071 | 81.3567 | 87.652 | 93.9113 | 100.1675
KapuskasingWind2070RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2070 | 75.4144 | 81.3583 | 87.6435 | 93.8968 | 100.1462
KapuskasingWind2075RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2075 | 75.4254 | 81.3523 | 87.618 | 93.8559 | 100.0904
KapuskasingWind2080RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2080 | 75.4364 | 81.3464 | 87.5925 | 93.8149 | 100.0347
KapuskasingWind2085RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2085 | 75.4474 | 81.3405 | 87.567 | 93.774 | 99.979
KapuskasingWind2090RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2090 | 75.4878 | 81.3556 | 87.5472 | 93.727 | 99.9071
KapuskasingWind2095RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2095 | 75.5172 | 81.3767 | 87.5528 | 93.7209 | 99.891
KapuskasingWind2100RCP6.0 | Kapuskasing | Wind | RCP6.0 | 2100 | 75.5465 | 81.3978 | 87.5585 | 93.7149 | 99.8748
KapuskasingWind2023RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2023 | 74.4382 | 80.2357 | 86.3515 | 92.4507 | 98.5473
KapuskasingWind2025RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2025 | 74.7514 | 80.6073 | 86.7963 | 92.957 | 99.1158
KapuskasingWind2030RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2030 | 75.0645 | 80.9788 | 87.2412 | 93.4633 | 99.6843
KapuskasingWind2035RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2035 | 75.3777 | 81.3504 | 87.686 | 93.9695 | 100.2527
KapuskasingWind2040RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2040 | 75.3899 | 81.353 | 87.6718 | 93.9453 | 100.2172
KapuskasingWind2045RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2045 | 75.4022 | 81.3556 | 87.6577 | 93.921 | 100.1817
KapuskasingWind2050RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2050 | 75.4291 | 81.3504 | 87.6095 | 93.8422 | 100.0719
KapuskasingWind2055RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2055 | 75.4438 | 81.3424 | 87.5755 | 93.7876 | 99.9976
KapuskasingWind2060RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2060 | 75.4878 | 81.3556 | 87.5472 | 93.727 | 99.9071
KapuskasingWind2065RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2065 | 75.5172 | 81.3767 | 87.5528 | 93.7209 | 99.891
KapuskasingWind2070RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2070 | 75.7227 | 81.5849 | 87.7597 | 93.9271 | 100.1009
KapuskasingWind2075RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2075 | 75.8988 | 81.772 | 87.9608 | 94.1393 | 100.327
KapuskasingWind2080RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2080 | 76.075 | 81.959 | 88.162 | 94.3515 | 100.5531
KapuskasingWind2085RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2085 | 76.1851 | 82.0974 | 88.3277 | 94.5471 | 100.7712
KapuskasingWind2090RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2090 | 76.2951 | 82.2357 | 88.4935 | 94.7426 | 100.9892
KapuskasingWind2095RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2095 | 76.2951 | 82.2357 | 88.4935 | 94.7426 | 100.9892
KapuskasingWind2100RCP8.5 | Kapuskasing | Wind | RCP8.5 | 2100 | 76.2951 | 82.2357 | 88.4935 | 94.7426 | 100.9892
KemptvilleIce Accretion2023RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2023 | 20.5623 | 24.4518 | 29.4 | 33.1542 | 36.9306
KemptvilleIce Accretion2025RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2025 | 20.5588 | 24.4601 | 29.42 | 33.1881 | 36.9747
KemptvilleIce Accretion2030RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2030 | 20.5553 | 24.4684 | 29.44 | 33.222 | 37.0188
KemptvilleIce Accretion2035RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2035 | 20.5518 | 24.4767 | 29.46 | 33.2559 | 37.0629
KemptvilleIce Accretion2040RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2040 | 20.5483 | 24.485 | 29.48 | 33.2898 | 37.107
KemptvilleIce Accretion2045RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2045 | 20.5449 | 24.4933 | 29.5 | 33.3237 | 37.1511
KemptvilleIce Accretion2050RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2050 | 20.5623 | 24.5414 | 29.586 | 33.439 | 37.2935
KemptvilleIce Accretion2055RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2055 | 20.5831 | 24.5813 | 29.652 | 33.5203 | 37.3918
KemptvilleIce Accretion2060RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2060 | 20.604 | 24.6211 | 29.718 | 33.6017 | 37.49
KemptvilleIce Accretion2065RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2065 | 20.6249 | 24.661 | 29.784 | 33.683 | 37.5883
KemptvilleIce Accretion2070RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2070 | 20.6458 | 24.7008 | 29.85 | 33.7644 | 37.6866
KemptvilleIce Accretion2075RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2075 | 20.7188 | 24.817 | 30.015 | 33.9678 | 37.9323
KemptvilleIce Accretion2080RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2080 | 20.7919 | 24.9332 | 30.18 | 34.1712 | 38.178
KemptvilleIce Accretion2085RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2085 | 20.8649 | 25.0494 | 30.345 | 34.3746 | 38.4237
KemptvilleIce Accretion2090RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2090 | 20.938 | 25.1656 | 30.51 | 34.578 | 38.6694
KemptvilleIce Accretion2095RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2095 | 21.0111 | 25.2818 | 30.675 | 34.7814 | 38.9151
KemptvilleIce Accretion2100RCP4.5 | Kemptville | Ice Accretion | RCP4.5 | 2100 | 21.0841 | 25.398 | 30.84 | 34.9848 | 39.1608
KemptvilleIce Accretion2023RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2023 | 20.5623 | 24.4518 | 29.4 | 33.1542 | 36.9306
KemptvilleIce Accretion2025RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2025 | 20.5588 | 24.4601 | 29.42 | 33.1881 | 36.9747
KemptvilleIce Accretion2030RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2030 | 20.5553 | 24.4684 | 29.44 | 33.222 | 37.0188
KemptvilleIce Accretion2035RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2035 | 20.5518 | 24.4767 | 29.46 | 33.2559 | 37.0629
KemptvilleIce Accretion2040RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2040 | 20.5483 | 24.485 | 29.48 | 33.2898 | 37.107
KemptvilleIce Accretion2045RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2045 | 20.5449 | 24.4933 | 29.5 | 33.3237 | 37.1511
KemptvilleIce Accretion2050RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2050 | 20.5623 | 24.5414 | 29.586 | 33.439 | 37.2935
KemptvilleIce Accretion2055RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2055 | 20.5831 | 24.5813 | 29.652 | 33.5203 | 37.3918
KemptvilleIce Accretion2060RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2060 | 20.604 | 24.6211 | 29.718 | 33.6017 | 37.49
KemptvilleIce Accretion2065RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2065 | 20.6249 | 24.661 | 29.784 | 33.683 | 37.5883
KemptvilleIce Accretion2070RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2070 | 20.6458 | 24.7008 | 29.85 | 33.7644 | 37.6866
KemptvilleIce Accretion2075RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2075 | 20.7554 | 24.8751 | 30.0975 | 34.0695 | 38.0551
KemptvilleIce Accretion2080RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2080 | 20.8649 | 25.0494 | 30.345 | 34.3746 | 38.4237
KemptvilleIce Accretion2085RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2085 | 20.9745 | 25.2237 | 30.5925 | 34.6797 | 38.7922
KemptvilleIce Accretion2090RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2090 | 21.0911 | 25.4561 | 30.97 | 35.1656 | 39.3876
KemptvilleIce Accretion2095RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2095 | 21.0981 | 25.5142 | 31.1 | 35.3464 | 39.6144
KemptvilleIce Accretion2100RCP6.0 | Kemptville | Ice Accretion | RCP6.0 | 2100 | 21.105 | 25.5723 | 31.23 | 35.5272 | 39.8412
KemptvilleIce Accretion2023RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2023 | 20.5623 | 24.4518 | 29.4 | 33.1542 | 36.9306
KemptvilleIce Accretion2025RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2025 | 20.5553 | 24.4684 | 29.44 | 33.222 | 37.0188
KemptvilleIce Accretion2030RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2030 | 20.5483 | 24.485 | 29.48 | 33.2898 | 37.107
KemptvilleIce Accretion2035RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2035 | 20.5414 | 24.5016 | 29.52 | 33.3576 | 37.1952
KemptvilleIce Accretion2040RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2040 | 20.5762 | 24.568 | 29.63 | 33.4932 | 37.359
KemptvilleIce Accretion2045RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2045 | 20.611 | 24.6344 | 29.74 | 33.6288 | 37.5228
KemptvilleIce Accretion2050RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2050 | 20.7919 | 24.9332 | 30.18 | 34.1712 | 38.178
KemptvilleIce Accretion2055RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2055 | 20.938 | 25.1656 | 30.51 | 34.578 | 38.6694
KemptvilleIce Accretion2060RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2060 | 21.0911 | 25.4561 | 30.97 | 35.1656 | 39.3876
KemptvilleIce Accretion2065RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2065 | 21.0981 | 25.5142 | 31.1 | 35.3464 | 39.6144
KemptvilleIce Accretion2070RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2070 | 20.764 | 25.1905 | 30.8 | 35.0639 | 39.3246
KemptvilleIce Accretion2075RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2075 | 20.4231 | 24.8087 | 30.37 | 34.6006 | 38.808
KemptvilleIce Accretion2080RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2080 | 20.0821 | 24.4269 | 29.94 | 34.1373 | 38.2914
KemptvilleIce Accretion2085RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2085 | 19.2158 | 23.4433 | 28.8 | 32.866 | 36.9117
KemptvilleIce Accretion2090RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2090 | 18.3495 | 22.4598 | 27.66 | 31.5948 | 35.532
KemptvilleIce Accretion2095RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2095 | 18.3495 | 22.4598 | 27.66 | 31.5948 | 35.532
KemptvilleIce Accretion2100RCP8.5 | Kemptville | Ice Accretion | RCP8.5 | 2100 | 18.3495 | 22.4598 | 27.66 | 31.5948 | 35.532
KemptvilleWind2023RCP4.5 | Kemptville | Wind | RCP4.5 | 2023 | 75.9789 | 81.8236 | 87.9736 | 94.1223 | 100.2698
KemptvilleWind2025RCP4.5 | Kemptville | Wind | RCP4.5 | 2025 | 75.9852 | 81.825 | 87.9707 | 94.1145 | 100.2581
KemptvilleWind2030RCP4.5 | Kemptville | Wind | RCP4.5 | 2030 | 75.9915 | 81.8264 | 87.9677 | 94.1066 | 100.2464
KemptvilleWind2035RCP4.5 | Kemptville | Wind | RCP4.5 | 2035 | 75.9979 | 81.8277 | 87.9648 | 94.0988 | 100.2347
KemptvilleWind2040RCP4.5 | Kemptville | Wind | RCP4.5 | 2040 | 76.0042 | 81.8291 | 87.9619 | 94.0909 | 100.223
KemptvilleWind2045RCP4.5 | Kemptville | Wind | RCP4.5 | 2045 | 76.0105 | 81.8305 | 87.9589 | 94.0831 | 100.2113
KemptvilleWind2050RCP4.5 | Kemptville | Wind | RCP4.5 | 2050 | 76.0032 | 81.8204 | 87.9454 | 94.0677 | 100.1936
KemptvilleWind2055RCP4.5 | Kemptville | Wind | RCP4.5 | 2055 | 75.9895 | 81.8089 | 87.9349 | 94.0602 | 100.1876
KemptvilleWind2060RCP4.5 | Kemptville | Wind | RCP4.5 | 2060 | 75.9758 | 81.7974 | 87.9243 | 94.0527 | 100.1816
KemptvilleWind2065RCP4.5 | Kemptville | Wind | RCP4.5 | 2065 | 75.9621 | 81.786 | 87.9138 | 94.0451 | 100.1755
KemptvilleWind2070RCP4.5 | Kemptville | Wind | RCP4.5 | 2070 | 75.9485 | 81.7745 | 87.9032 | 94.0376 | 100.1695
KemptvilleWind2075RCP4.5 | Kemptville | Wind | RCP4.5 | 2075 | 75.9181 | 81.7445 | 87.8739 | 94.0093 | 100.1411
KemptvilleWind2080RCP4.5 | Kemptville | Wind | RCP4.5 | 2080 | 75.8877 | 81.7145 | 87.8445 | 93.9811 | 100.1127
KemptvilleWind2085RCP4.5 | Kemptville | Wind | RCP4.5 | 2085 | 75.8573 | 81.6845 | 87.8152 | 93.9528 | 100.0842
KemptvilleWind2090RCP4.5 | Kemptville | Wind | RCP4.5 | 2090 | 75.8269 | 81.6545 | 87.7859 | 93.9246 | 100.0558
KemptvilleWind2095RCP4.5 | Kemptville | Wind | RCP4.5 | 2095 | 75.7965 | 81.6245 | 87.7565 | 93.8964 | 100.0274
KemptvilleWind2100RCP4.5 | Kemptville | Wind | RCP4.5 | 2100 | 75.7661 | 81.5945 | 87.7272 | 93.8681 | 99.999
KemptvilleWind2023RCP6.0 | Kemptville | Wind | RCP6.0 | 2023 | 75.9789 | 81.8236 | 87.9736 | 94.1223 | 100.2698
KemptvilleWind2025RCP6.0 | Kemptville | Wind | RCP6.0 | 2025 | 75.9852 | 81.825 | 87.9707 | 94.1145 | 100.2581
KemptvilleWind2030RCP6.0 | Kemptville | Wind | RCP6.0 | 2030 | 75.9915 | 81.8264 | 87.9677 | 94.1066 | 100.2464
KemptvilleWind2035RCP6.0 | Kemptville | Wind | RCP6.0 | 2035 | 75.9979 | 81.8277 | 87.9648 | 94.0988 | 100.2347
KemptvilleWind2040RCP6.0 | Kemptville | Wind | RCP6.0 | 2040 | 76.0042 | 81.8291 | 87.9619 | 94.0909 | 100.223
KemptvilleWind2045RCP6.0 | Kemptville | Wind | RCP6.0 | 2045 | 76.0105 | 81.8305 | 87.9589 | 94.0831 | 100.2113
KemptvilleWind2050RCP6.0 | Kemptville | Wind | RCP6.0 | 2050 | 76.0032 | 81.8204 | 87.9454 | 94.0677 | 100.1936
KemptvilleWind2055RCP6.0 | Kemptville | Wind | RCP6.0 | 2055 | 75.9895 | 81.8089 | 87.9349 | 94.0602 | 100.1876
KemptvilleWind2060RCP6.0 | Kemptville | Wind | RCP6.0 | 2060 | 75.9758 | 81.7974 | 87.9243 | 94.0527 | 100.1816
KemptvilleWind2065RCP6.0 | Kemptville | Wind | RCP6.0 | 2065 | 75.9621 | 81.786 | 87.9138 | 94.0451 | 100.1755
KemptvilleWind2070RCP6.0 | Kemptville | Wind | RCP6.0 | 2070 | 75.9485 | 81.7745 | 87.9032 | 94.0376 | 100.1695
KemptvilleWind2075RCP6.0 | Kemptville | Wind | RCP6.0 | 2075 | 75.9029 | 81.7295 | 87.8592 | 93.9952 | 100.1269
KemptvilleWind2080RCP6.0 | Kemptville | Wind | RCP6.0 | 2080 | 75.8573 | 81.6845 | 87.8152 | 93.9528 | 100.0842
KemptvilleWind2085RCP6.0 | Kemptville | Wind | RCP6.0 | 2085 | 75.8117 | 81.6395 | 87.7712 | 93.9105 | 100.0416
KemptvilleWind2090RCP6.0 | Kemptville | Wind | RCP6.0 | 2090 | 75.7332 | 81.5508 | 87.6744 | 93.8053 | 99.9254
KemptvilleWind2095RCP6.0 | Kemptville | Wind | RCP6.0 | 2095 | 75.7002 | 81.5072 | 87.6216 | 93.7426 | 99.8518
KemptvilleWind2100RCP6.0 | Kemptville | Wind | RCP6.0 | 2100 | 75.6673 | 81.4635 | 87.5688 | 93.6798 | 99.7783
KemptvilleWind2023RCP8.5 | Kemptville | Wind | RCP8.5 | 2023 | 75.9789 | 81.8236 | 87.9736 | 94.1223 | 100.2698
KemptvilleWind2025RCP8.5 | Kemptville | Wind | RCP8.5 | 2025 | 75.9915 | 81.8264 | 87.9677 | 94.1066 | 100.2464
KemptvilleWind2030RCP8.5 | Kemptville | Wind | RCP8.5 | 2030 | 76.0042 | 81.8291 | 87.9619 | 94.0909 | 100.223
KemptvilleWind2035RCP8.5 | Kemptville | Wind | RCP8.5 | 2035 | 76.0168 | 81.8318 | 87.956 | 94.0753 | 100.1996
KemptvilleWind2040RCP8.5 | Kemptville | Wind | RCP8.5 | 2040 | 75.9941 | 81.8127 | 87.9384 | 94.0627 | 100.1896
KemptvilleWind2045RCP8.5 | Kemptville | Wind | RCP8.5 | 2045 | 75.9713 | 81.7936 | 87.9208 | 94.0501 | 100.1796
KemptvilleWind2050RCP8.5 | Kemptville | Wind | RCP8.5 | 2050 | 75.8877 | 81.7145 | 87.8445 | 93.9811 | 100.1127
KemptvilleWind2055RCP8.5 | Kemptville | Wind | RCP8.5 | 2055 | 75.8269 | 81.6545 | 87.7859 | 93.9246 | 100.0558
KemptvilleWind2060RCP8.5 | Kemptville | Wind | RCP8.5 | 2060 | 75.7332 | 81.5508 | 87.6744 | 93.8053 | 99.9254
KemptvilleWind2065RCP8.5 | Kemptville | Wind | RCP8.5 | 2065 | 75.7002 | 81.5072 | 87.6216 | 93.7426 | 99.8518
KemptvilleWind2070RCP8.5 | Kemptville | Wind | RCP8.5 | 2070 | 75.7104 | 81.5154 | 87.6275 | 93.7457 | 99.8552
KemptvilleWind2075RCP8.5 | Kemptville | Wind | RCP8.5 | 2075 | 75.7534 | 81.5672 | 87.6861 | 93.8116 | 99.9321
KemptvilleWind2080RCP8.5 | Kemptville | Wind | RCP8.5 | 2080 | 75.7965 | 81.619 | 87.7448 | 93.8775 | 100.009
KemptvilleWind2085RCP8.5 | Kemptville | Wind | RCP8.5 | 2085 | 75.7357 | 81.5617 | 87.692 | 93.8304 | 99.9639
KemptvilleWind2090RCP8.5 | Kemptville | Wind | RCP8.5 | 2090 | 75.6749 | 81.5045 | 87.6392 | 93.7834 | 99.9187
KemptvilleWind2095RCP8.5 | Kemptville | Wind | RCP8.5 | 2095 | 75.6749 | 81.5045 | 87.6392 | 93.7834 | 99.9187
KemptvilleWind2100RCP8.5 | Kemptville | Wind | RCP8.5 | 2100 | 75.6749 | 81.5045 | 87.6392 | 93.7834 | 99.9187
KenoraIce Accretion2023RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2023 | 9.4531 | 11.2432 | 13.52 | 15.2776 | 17.0188
KenoraIce Accretion2025RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2025 | 9.4923 | 11.2863 | 13.5677 | 15.3266 | 17.0734
KenoraIce Accretion2030RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2030 | 9.5315 | 11.3295 | 13.6153 | 15.3755 | 17.128
KenoraIce Accretion2035RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2035 | 9.5707 | 11.3727 | 13.663 | 15.4245 | 17.1826
KenoraIce Accretion2040RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2040 | 9.6099 | 11.4158 | 13.7107 | 15.4735 | 17.2372
KenoraIce Accretion2045RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2045 | 9.6491 | 11.459 | 13.7583 | 15.5224 | 17.2918
KenoraIce Accretion2050RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2050 | 9.6684 | 11.4762 | 13.7748 | 15.5361 | 17.3038
KenoraIce Accretion2055RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2055 | 9.6485 | 11.4503 | 13.7436 | 15.5009 | 17.2612
KenoraIce Accretion2060RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2060 | 9.6286 | 11.4245 | 13.7124 | 15.4656 | 17.2187
KenoraIce Accretion2065RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2065 | 9.6087 | 11.3986 | 13.6812 | 15.4304 | 17.1761
KenoraIce Accretion2070RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2070 | 9.5888 | 11.3727 | 13.65 | 15.3951 | 17.1335
KenoraIce Accretion2075RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2075 | 9.6445 | 11.4428 | 13.7367 | 15.4955 | 17.2454
KenoraIce Accretion2080RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2080 | 9.7003 | 11.5129 | 13.8233 | 15.5959 | 17.3573
KenoraIce Accretion2085RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2085 | 9.7561 | 11.5831 | 13.91 | 15.6963 | 17.4693
KenoraIce Accretion2090RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2090 | 9.8119 | 11.6532 | 13.9967 | 15.7966 | 17.5812
KenoraIce Accretion2095RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2095 | 9.8677 | 11.7233 | 14.0833 | 15.897 | 17.6931
KenoraIce Accretion2100RCP4.5 | Kenora | Ice Accretion | RCP4.5 | 2100 | 9.9235 | 11.7935 | 14.17 | 15.9974 | 17.8051
KenoraIce Accretion2023RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2023 | 9.4531 | 11.2432 | 13.52 | 15.2776 | 17.0188
KenoraIce Accretion2025RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2025 | 9.4923 | 11.2863 | 13.5677 | 15.3266 | 17.0734
KenoraIce Accretion2030RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2030 | 9.5315 | 11.3295 | 13.6153 | 15.3755 | 17.128
KenoraIce Accretion2035RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2035 | 9.5707 | 11.3727 | 13.663 | 15.4245 | 17.1826
KenoraIce Accretion2040RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2040 | 9.6099 | 11.4158 | 13.7107 | 15.4735 | 17.2372
KenoraIce Accretion2045RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2045 | 9.6491 | 11.459 | 13.7583 | 15.5224 | 17.2918
KenoraIce Accretion2050RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2050 | 9.6684 | 11.4762 | 13.7748 | 15.5361 | 17.3038
KenoraIce Accretion2055RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2055 | 9.6485 | 11.4503 | 13.7436 | 15.5009 | 17.2612
KenoraIce Accretion2060RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2060 | 9.6286 | 11.4245 | 13.7124 | 15.4656 | 17.2187
KenoraIce Accretion2065RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2065 | 9.6087 | 11.3986 | 13.6812 | 15.4304 | 17.1761
KenoraIce Accretion2070RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2070 | 9.5888 | 11.3727 | 13.65 | 15.3951 | 17.1335
KenoraIce Accretion2075RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2075 | 9.6724 | 11.4779 | 13.78 | 15.5457 | 17.3014
KenoraIce Accretion2080RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2080 | 9.7561 | 11.5831 | 13.91 | 15.6963 | 17.4693
KenoraIce Accretion2085RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2085 | 9.8398 | 11.6883 | 14.04 | 15.8468 | 17.6372
KenoraIce Accretion2090RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2090 | 9.9235 | 11.7935 | 14.17 | 15.9925 | 17.8051
KenoraIce Accretion2095RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2095 | 9.9235 | 11.7935 | 14.17 | 15.9876 | 17.8051
KenoraIce Accretion2100RCP6.0 | Kenora | Ice Accretion | RCP6.0 | 2100 | 9.9235 | 11.7935 | 14.17 | 15.9827 | 17.8051
KenoraIce Accretion2023RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2023 | 9.4531 | 11.2432 | 13.52 | 15.2776 | 17.0188
KenoraIce Accretion2025RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2025 | 9.5315 | 11.3295 | 13.6153 | 15.3755 | 17.128
KenoraIce Accretion2030RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2030 | 9.6099 | 11.4158 | 13.7107 | 15.4735 | 17.2372
KenoraIce Accretion2035RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2035 | 9.6883 | 11.5021 | 13.806 | 15.5714 | 17.3464
KenoraIce Accretion2040RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2040 | 9.6551 | 11.459 | 13.754 | 15.5126 | 17.2754
KenoraIce Accretion2045RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2045 | 9.6219 | 11.4158 | 13.702 | 15.4539 | 17.2045
KenoraIce Accretion2050RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2050 | 9.7003 | 11.5129 | 13.8233 | 15.5959 | 17.3573
KenoraIce Accretion2055RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2055 | 9.8119 | 11.6532 | 13.9967 | 15.7966 | 17.5812
KenoraIce Accretion2060RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2060 | 9.9235 | 11.7935 | 14.17 | 15.9925 | 17.8051
KenoraIce Accretion2065RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2065 | 9.9235 | 11.7935 | 14.17 | 15.9876 | 17.8051
KenoraIce Accretion2070RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2070 | 9.9657 | 11.851 | 14.248 | 16.0758 | 17.9088
KenoraIce Accretion2075RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2075 | 10.0079 | 11.9086 | 14.326 | 16.1688 | 18.0125
KenoraIce Accretion2080RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2080 | 10.0501 | 11.9661 | 14.404 | 16.2618 | 18.1163
KenoraIce Accretion2085RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2085 | 9.7878 | 11.6532 | 14.0205 | 15.8285 | 17.6331
KenoraIce Accretion2090RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2090 | 9.5254 | 11.3403 | 13.637 | 15.3951 | 17.1499
KenoraIce Accretion2095RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2095 | 9.5254 | 11.3403 | 13.637 | 15.3951 | 17.1499
KenoraIce Accretion2100RCP8.5 | Kenora | Ice Accretion | RCP8.5 | 2100 | 9.5254 | 11.3403 | 13.637 | 15.3951 | 17.1499
KenoraWind2023RCP4.5 | Kenora | Wind | RCP4.5 | 2023 | 75.0838 | 81.0837 | 87.462 | 93.7776 | 100.0988
KenoraWind2025RCP4.5 | Kenora | Wind | RCP4.5 | 2025 | 75.09 | 81.0757 | 87.4333 | 93.7331 | 100.0384
KenoraWind2030RCP4.5 | Kenora | Wind | RCP4.5 | 2030 | 75.0961 | 81.0677 | 87.4047 | 93.6886 | 99.9779
KenoraWind2035RCP4.5 | Kenora | Wind | RCP4.5 | 2035 | 75.1023 | 81.0597 | 87.376 | 93.6442 | 99.9175
KenoraWind2040RCP4.5 | Kenora | Wind | RCP4.5 | 2040 | 75.1085 | 81.0517 | 87.3473 | 93.5997 | 99.857
KenoraWind2045RCP4.5 | Kenora | Wind | RCP4.5 | 2045 | 75.1147 | 81.0437 | 87.3187 | 93.5552 | 99.7965
KenoraWind2050RCP4.5 | Kenora | Wind | RCP4.5 | 2050 | 75.2174 | 81.1573 | 87.4431 | 93.6911 | 99.9459
KenoraWind2055RCP4.5 | Kenora | Wind | RCP4.5 | 2055 | 75.314 | 81.2789 | 87.5962 | 93.8714 | 100.1557
KenoraWind2060RCP4.5 | Kenora | Wind | RCP4.5 | 2060 | 75.4105 | 81.4004 | 87.7492 | 94.0518 | 100.3655
KenoraWind2065RCP4.5 | Kenora | Wind | RCP4.5 | 2065 | 75.507 | 81.522 | 87.9023 | 94.2322 | 100.5753
KenoraWind2070RCP4.5 | Kenora | Wind | RCP4.5 | 2070 | 75.6036 | 81.6436 | 88.0554 | 94.4125 | 100.7851
KenoraWind2075RCP4.5 | Kenora | Wind | RCP4.5 | 2075 | 75.6679 | 81.7209 | 88.15 | 94.5214 | 100.9077
KenoraWind2080RCP4.5 | Kenora | Wind | RCP4.5 | 2080 | 75.7323 | 81.7982 | 88.2446 | 94.6303 | 101.0302
KenoraWind2085RCP4.5 | Kenora | Wind | RCP4.5 | 2085 | 75.7967 | 81.8755 | 88.3392 | 94.7392 | 101.1528
KenoraWind2090RCP4.5 | Kenora | Wind | RCP4.5 | 2090 | 75.861 | 81.9528 | 88.4338 | 94.8481 | 101.2753
KenoraWind2095RCP4.5 | Kenora | Wind | RCP4.5 | 2095 | 75.9254 | 82.0302 | 88.5284 | 94.957 | 101.3979
KenoraWind2100RCP4.5 | Kenora | Wind | RCP4.5 | 2100 | 75.9897 | 82.1075 | 88.623 | 95.0659 | 101.5204
KenoraWind2023RCP6.0 | Kenora | Wind | RCP6.0 | 2023 | 75.0838 | 81.0837 | 87.462 | 93.7776 | 100.0988
KenoraWind2025RCP6.0 | Kenora | Wind | RCP6.0 | 2025 | 75.09 | 81.0757 | 87.4333 | 93.7331 | 100.0384
KenoraWind2030RCP6.0 | Kenora | Wind | RCP6.0 | 2030 | 75.0961 | 81.0677 | 87.4047 | 93.6886 | 99.9779
KenoraWind2035RCP6.0 | Kenora | Wind | RCP6.0 | 2035 | 75.1023 | 81.0597 | 87.376 | 93.6442 | 99.9175
KenoraWind2040RCP6.0 | Kenora | Wind | RCP6.0 | 2040 | 75.1085 | 81.0517 | 87.3473 | 93.5997 | 99.857
KenoraWind2045RCP6.0 | Kenora | Wind | RCP6.0 | 2045 | 75.1147 | 81.0437 | 87.3187 | 93.5552 | 99.7965
KenoraWind2050RCP6.0 | Kenora | Wind | RCP6.0 | 2050 | 75.2174 | 81.1573 | 87.4431 | 93.6911 | 99.9459
KenoraWind2055RCP6.0 | Kenora | Wind | RCP6.0 | 2055 | 75.314 | 81.2789 | 87.5962 | 93.8714 | 100.1557
KenoraWind2060RCP6.0 | Kenora | Wind | RCP6.0 | 2060 | 75.4105 | 81.4004 | 87.7492 | 94.0518 | 100.3655
KenoraWind2065RCP6.0 | Kenora | Wind | RCP6.0 | 2065 | 75.507 | 81.522 | 87.9023 | 94.2322 | 100.5753
KenoraWind2070RCP6.0 | Kenora | Wind | RCP6.0 | 2070 | 75.6036 | 81.6436 | 88.0554 | 94.4125 | 100.7851
KenoraWind2075RCP6.0 | Kenora | Wind | RCP6.0 | 2075 | 75.7001 | 81.7596 | 88.1973 | 94.5759 | 100.9689
KenoraWind2080RCP6.0 | Kenora | Wind | RCP6.0 | 2080 | 75.7967 | 81.8755 | 88.3392 | 94.7392 | 101.1528
KenoraWind2085RCP6.0 | Kenora | Wind | RCP6.0 | 2085 | 75.8932 | 81.9915 | 88.4811 | 94.9025 | 101.3366
KenoraWind2090RCP6.0 | Kenora | Wind | RCP6.0 | 2090 | 76.2472 | 82.4514 | 89.0731 | 95.6057 | 102.1544
KenoraWind2095RCP6.0 | Kenora | Wind | RCP6.0 | 2095 | 76.5046 | 82.7953 | 89.5231 | 96.1456 | 102.7884
KenoraWind2100RCP6.0 | Kenora | Wind | RCP6.0 | 2100 | 76.762 | 83.1392 | 89.9732 | 96.6854 | 103.4224
KenoraWind2023RCP8.5 | Kenora | Wind | RCP8.5 | 2023 | 75.0838 | 81.0837 | 87.462 | 93.7776 | 100.0988
KenoraWind2025RCP8.5 | Kenora | Wind | RCP8.5 | 2025 | 75.0961 | 81.0677 | 87.4047 | 93.6886 | 99.9779
KenoraWind2030RCP8.5 | Kenora | Wind | RCP8.5 | 2030 | 75.1085 | 81.0517 | 87.3473 | 93.5997 | 99.857
KenoraWind2035RCP8.5 | Kenora | Wind | RCP8.5 | 2035 | 75.1209 | 81.0357 | 87.29 | 93.5107 | 99.7361
KenoraWind2040RCP8.5 | Kenora | Wind | RCP8.5 | 2040 | 75.2818 | 81.2384 | 87.5451 | 93.8113 | 100.0858
KenoraWind2045RCP8.5 | Kenora | Wind | RCP8.5 | 2045 | 75.4427 | 81.441 | 87.8003 | 94.1119 | 100.4354
KenoraWind2050RCP8.5 | Kenora | Wind | RCP8.5 | 2050 | 75.7323 | 81.7982 | 88.2446 | 94.6303 | 101.0302
KenoraWind2055RCP8.5 | Kenora | Wind | RCP8.5 | 2055 | 75.861 | 81.9528 | 88.4338 | 94.8481 | 101.2753
KenoraWind2060RCP8.5 | Kenora | Wind | RCP8.5 | 2060 | 76.2472 | 82.4514 | 89.0731 | 95.6057 | 102.1544
KenoraWind2065RCP8.5 | Kenora | Wind | RCP8.5 | 2065 | 76.5046 | 82.7953 | 89.5231 | 96.1456 | 102.7884
KenoraWind2070RCP8.5 | Kenora | Wind | RCP8.5 | 2070 | 76.9724 | 83.3925 | 90.2799 | 97.0382 | 103.8178
KenoraWind2075RCP8.5 | Kenora | Wind | RCP8.5 | 2075 | 77.1828 | 83.6457 | 90.5867 | 97.3909 | 104.2133
KenoraWind2080RCP8.5 | Kenora | Wind | RCP8.5 | 2080 | 77.3932 | 83.899 | 90.8934 | 97.7436 | 104.6087
KenoraWind2085RCP8.5 | Kenora | Wind | RCP8.5 | 2085 | 77.4341 | 83.959 | 90.9751 | 97.8449 | 104.7312
KenoraWind2090RCP8.5 | Kenora | Wind | RCP8.5 | 2090 | 77.4749 | 84.019 | 91.0568 | 97.9461 | 104.8538
KenoraWind2095RCP8.5 | Kenora | Wind | RCP8.5 | 2095 | 77.4749 | 84.019 | 91.0568 | 97.9461 | 104.8538
KenoraWind2100RCP8.5 | Kenora | Wind | RCP8.5 | 2100 | 77.4749 | 84.019 | 91.0568 | 97.9461 | 104.8538
KillaloeIce Accretion2023RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2023 | 13.8613 | 16.4838 | 19.8 | 22.3288 | 24.8724
KillaloeIce Accretion2025RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2025 | 13.9517 | 16.5972 | 19.94 | 22.4908 | 25.0572
KillaloeIce Accretion2030RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2030 | 14.0422 | 16.7107 | 20.08 | 22.6527 | 25.242
KillaloeIce Accretion2035RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2035 | 14.1326 | 16.8241 | 20.22 | 22.8147 | 25.4268
KillaloeIce Accretion2040RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2040 | 14.2231 | 16.9375 | 20.36 | 22.9767 | 25.6116
KillaloeIce Accretion2045RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2045 | 14.3136 | 17.051 | 20.5 | 23.1386 | 25.7964
KillaloeIce Accretion2050RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2050 | 14.4068 | 17.181 | 20.676 | 23.3503 | 26.0417
KillaloeIce Accretion2055RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2055 | 14.4096 | 17.1976 | 20.712 | 23.4 | 26.1022
KillaloeIce Accretion2060RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2060 | 14.4124 | 17.2142 | 20.748 | 23.4498 | 26.1626
KillaloeIce Accretion2065RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2065 | 14.4151 | 17.2308 | 20.784 | 23.4995 | 26.2231
KillaloeIce Accretion2070RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2070 | 14.4179 | 17.2474 | 20.82 | 23.5492 | 26.2836
KillaloeIce Accretion2075RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2075 | 14.4574 | 17.3027 | 20.9 | 23.6471 | 26.397
KillaloeIce Accretion2080RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2080 | 14.4968 | 17.3581 | 20.98 | 23.7451 | 26.5104
KillaloeIce Accretion2085RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2085 | 14.5362 | 17.4134 | 21.06 | 23.843 | 26.6238
KillaloeIce Accretion2090RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2090 | 14.5757 | 17.4687 | 21.14 | 23.9409 | 26.7372
KillaloeIce Accretion2095RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2095 | 14.6151 | 17.5241 | 21.22 | 24.0389 | 26.8506
KillaloeIce Accretion2100RCP4.5 | Killaloe | Ice Accretion | RCP4.5 | 2100 | 14.6545 | 17.5794 | 21.3 | 24.1368 | 26.964
KillaloeIce Accretion2023RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2023 | 13.8613 | 16.4838 | 19.8 | 22.3288 | 24.8724
KillaloeIce Accretion2025RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2025 | 13.9517 | 16.5972 | 19.94 | 22.4908 | 25.0572
KillaloeIce Accretion2030RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2030 | 14.0422 | 16.7107 | 20.08 | 22.6527 | 25.242
KillaloeIce Accretion2035RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2035 | 14.1326 | 16.8241 | 20.22 | 22.8147 | 25.4268
KillaloeIce Accretion2040RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2040 | 14.2231 | 16.9375 | 20.36 | 22.9767 | 25.6116
KillaloeIce Accretion2045RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2045 | 14.3136 | 17.051 | 20.5 | 23.1386 | 25.7964
KillaloeIce Accretion2050RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2050 | 14.4068 | 17.181 | 20.676 | 23.3503 | 26.0417
KillaloeIce Accretion2055RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2055 | 14.4096 | 17.1976 | 20.712 | 23.4 | 26.1022
KillaloeIce Accretion2060RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2060 | 14.4124 | 17.2142 | 20.748 | 23.4498 | 26.1626
KillaloeIce Accretion2065RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2065 | 14.4151 | 17.2308 | 20.784 | 23.4995 | 26.2231
KillaloeIce Accretion2070RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2070 | 14.4179 | 17.2474 | 20.82 | 23.5492 | 26.2836
KillaloeIce Accretion2075RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2075 | 14.4771 | 17.3304 | 20.94 | 23.6961 | 26.4537
KillaloeIce Accretion2080RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2080 | 14.5362 | 17.4134 | 21.06 | 23.843 | 26.6238
KillaloeIce Accretion2085RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2085 | 14.5954 | 17.4964 | 21.18 | 23.9899 | 26.7939
KillaloeIce Accretion2090RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2090 | 14.5525 | 17.4687 | 21.18 | 24.0087 | 26.8296
KillaloeIce Accretion2095RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2095 | 14.4504 | 17.3581 | 21.06 | 23.8807 | 26.6952
KillaloeIce Accretion2100RCP6.0 | Killaloe | Ice Accretion | RCP6.0 | 2100 | 14.3483 | 17.2474 | 20.94 | 23.7526 | 26.5608
KillaloeIce Accretion2023RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2023 | 13.8613 | 16.4838 | 19.8 | 22.3288 | 24.8724
KillaloeIce Accretion2025RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2025 | 14.0422 | 16.7107 | 20.08 | 22.6527 | 25.242
KillaloeIce Accretion2030RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2030 | 14.2231 | 16.9375 | 20.36 | 22.9767 | 25.6116
KillaloeIce Accretion2035RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2035 | 14.404 | 17.1644 | 20.64 | 23.3006 | 25.9812
KillaloeIce Accretion2040RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2040 | 14.4087 | 17.1921 | 20.7 | 23.3835 | 26.082
KillaloeIce Accretion2045RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2045 | 14.4133 | 17.2197 | 20.76 | 23.4663 | 26.1828
KillaloeIce Accretion2050RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2050 | 14.4968 | 17.3581 | 20.98 | 23.7451 | 26.5104
KillaloeIce Accretion2055RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2055 | 14.5757 | 17.4687 | 21.14 | 23.9409 | 26.7372
KillaloeIce Accretion2060RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2060 | 14.5525 | 17.4687 | 21.18 | 24.0087 | 26.8296
KillaloeIce Accretion2065RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2065 | 14.4504 | 17.3581 | 21.06 | 23.8807 | 26.6952
KillaloeIce Accretion2070RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2070 | 14.302 | 17.2253 | 20.9333 | 23.7601 | 26.586
KillaloeIce Accretion2075RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2075 | 14.2556 | 17.2031 | 20.9267 | 23.7677 | 26.6112
KillaloeIce Accretion2080RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2080 | 14.2092 | 17.181 | 20.92 | 23.7752 | 26.6364
KillaloeIce Accretion2085RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2085 | 13.9448 | 16.9071 | 20.64 | 23.4927 | 26.334
KillaloeIce Accretion2090RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2090 | 13.6803 | 16.6332 | 20.36 | 23.2102 | 26.0316
KillaloeIce Accretion2095RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2095 | 13.6803 | 16.6332 | 20.36 | 23.2102 | 26.0316
KillaloeIce Accretion2100RCP8.5 | Killaloe | Ice Accretion | RCP8.5 | 2100 | 13.6803 | 16.6332 | 20.36 | 23.2102 | 26.0316
KillaloeWind2023RCP4.5 | Killaloe | Wind | RCP4.5 | 2023 | 69.4033 | 74.7869 | 80.464 | 86.1307 | 91.7928
KillaloeWind2025RCP4.5 | Killaloe | Wind | RCP4.5 | 2025 | 69.4965 | 74.9047 | 80.612 | 86.3048 | 91.995
KillaloeWind2030RCP4.5 | Killaloe | Wind | RCP4.5 | 2030 | 69.5898 | 75.0225 | 80.76 | 86.4788 | 92.1971
KillaloeWind2035RCP4.5 | Killaloe | Wind | RCP4.5 | 2035 | 69.683 | 75.1403 | 80.908 | 86.6529 | 92.3993
KillaloeWind2040RCP4.5 | Killaloe | Wind | RCP4.5 | 2040 | 69.7763 | 75.2581 | 81.056 | 86.8269 | 92.6014
KillaloeWind2045RCP4.5 | Killaloe | Wind | RCP4.5 | 2045 | 69.8695 | 75.3759 | 81.204 | 87.001 | 92.8036
KillaloeWind2050RCP4.5 | Killaloe | Wind | RCP4.5 | 2050 | 69.9835 | 75.519 | 81.384 | 87.211 | 93.0441
KillaloeWind2055RCP4.5 | Killaloe | Wind | RCP4.5 | 2055 | 70.0042 | 75.5443 | 81.416 | 87.2469 | 93.0824
KillaloeWind2060RCP4.5 | Killaloe | Wind | RCP4.5 | 2060 | 70.025 | 75.5696 | 81.448 | 87.2829 | 93.1207
KillaloeWind2065RCP4.5 | Killaloe | Wind | RCP4.5 | 2065 | 70.0457 | 75.5949 | 81.48 | 87.3188 | 93.159
KillaloeWind2070RCP4.5 | Killaloe | Wind | RCP4.5 | 2070 | 70.0664 | 75.6202 | 81.512 | 87.3548 | 93.1973
KillaloeWind2075RCP4.5 | Killaloe | Wind | RCP4.5 | 2075 | 70.0894 | 75.6549 | 81.5587 | 87.4133 | 93.2687
KillaloeWind2080RCP4.5 | Killaloe | Wind | RCP4.5 | 2080 | 70.1125 | 75.6896 | 81.6053 | 87.4718 | 93.3402
KillaloeWind2085RCP4.5 | Killaloe | Wind | RCP4.5 | 2085 | 70.1355 | 75.7243 | 81.652 | 87.5303 | 93.4116
KillaloeWind2090RCP4.5 | Killaloe | Wind | RCP4.5 | 2090 | 70.1585 | 75.759 | 81.6987 | 87.5888 | 93.483
KillaloeWind2095RCP4.5 | Killaloe | Wind | RCP4.5 | 2095 | 70.1815 | 75.7938 | 81.7453 | 87.6473 | 93.5545
KillaloeWind2100RCP4.5 | Killaloe | Wind | RCP4.5 | 2100 | 70.2046 | 75.8285 | 81.792 | 87.7058 | 93.6259
KillaloeWind2023RCP6.0 | Killaloe | Wind | RCP6.0 | 2023 | 69.4033 | 74.7869 | 80.464 | 86.1307 | 91.7928
KillaloeWind2025RCP6.0 | Killaloe | Wind | RCP6.0 | 2025 | 69.4965 | 74.9047 | 80.612 | 86.3048 | 91.995
KillaloeWind2030RCP6.0 | Killaloe | Wind | RCP6.0 | 2030 | 69.5898 | 75.0225 | 80.76 | 86.4788 | 92.1971
KillaloeWind2035RCP6.0 | Killaloe | Wind | RCP6.0 | 2035 | 69.683 | 75.1403 | 80.908 | 86.6529 | 92.3993
KillaloeWind2040RCP6.0 | Killaloe | Wind | RCP6.0 | 2040 | 69.7763 | 75.2581 | 81.056 | 86.8269 | 92.6014
KillaloeWind2045RCP6.0 | Killaloe | Wind | RCP6.0 | 2045 | 69.8695 | 75.3759 | 81.204 | 87.001 | 92.8036
KillaloeWind2050RCP6.0 | Killaloe | Wind | RCP6.0 | 2050 | 69.9835 | 75.519 | 81.384 | 87.211 | 93.0441
KillaloeWind2055RCP6.0 | Killaloe | Wind | RCP6.0 | 2055 | 70.0042 | 75.5443 | 81.416 | 87.2469 | 93.0824
KillaloeWind2060RCP6.0 | Killaloe | Wind | RCP6.0 | 2060 | 70.025 | 75.5696 | 81.448 | 87.2829 | 93.1207
KillaloeWind2065RCP6.0 | Killaloe | Wind | RCP6.0 | 2065 | 70.0457 | 75.5949 | 81.48 | 87.3188 | 93.159
KillaloeWind2070RCP6.0 | Killaloe | Wind | RCP6.0 | 2070 | 70.0664 | 75.6202 | 81.512 | 87.3548 | 93.1973
KillaloeWind2075RCP6.0 | Killaloe | Wind | RCP6.0 | 2075 | 70.101 | 75.6722 | 81.582 | 87.4425 | 93.3044
KillaloeWind2080RCP6.0 | Killaloe | Wind | RCP6.0 | 2080 | 70.1355 | 75.7243 | 81.652 | 87.5303 | 93.4116
KillaloeWind2085RCP6.0 | Killaloe | Wind | RCP6.0 | 2085 | 70.17 | 75.7764 | 81.722 | 87.618 | 93.5188
KillaloeWind2090RCP6.0 | Killaloe | Wind | RCP6.0 | 2090 | 70.2161 | 75.826 | 81.776 | 87.6744 | 93.5834
KillaloeWind2095RCP6.0 | Killaloe | Wind | RCP6.0 | 2095 | 70.2276 | 75.8235 | 81.76 | 87.643 | 93.5408
KillaloeWind2100RCP6.0 | Killaloe | Wind | RCP6.0 | 2100 | 70.2391 | 75.821 | 81.744 | 87.6116 | 93.4982
KillaloeWind2023RCP8.5 | Killaloe | Wind | RCP8.5 | 2023 | 69.4033 | 74.7869 | 80.464 | 86.1307 | 91.7928
KillaloeWind2025RCP8.5 | Killaloe | Wind | RCP8.5 | 2025 | 69.5898 | 75.0225 | 80.76 | 86.4788 | 92.1971
KillaloeWind2030RCP8.5 | Killaloe | Wind | RCP8.5 | 2030 | 69.7763 | 75.2581 | 81.056 | 86.8269 | 92.6014
KillaloeWind2035RCP8.5 | Killaloe | Wind | RCP8.5 | 2035 | 69.9628 | 75.4937 | 81.352 | 87.175 | 93.0058
KillaloeWind2040RCP8.5 | Killaloe | Wind | RCP8.5 | 2040 | 69.9973 | 75.5358 | 81.4053 | 87.235 | 93.0696
KillaloeWind2045RCP8.5 | Killaloe | Wind | RCP8.5 | 2045 | 70.0319 | 75.578 | 81.4587 | 87.2949 | 93.1334
KillaloeWind2050RCP8.5 | Killaloe | Wind | RCP8.5 | 2050 | 70.1125 | 75.6896 | 81.6053 | 87.4718 | 93.3402
KillaloeWind2055RCP8.5 | Killaloe | Wind | RCP8.5 | 2055 | 70.1585 | 75.759 | 81.6987 | 87.5888 | 93.483
KillaloeWind2060RCP8.5 | Killaloe | Wind | RCP8.5 | 2060 | 70.2161 | 75.826 | 81.776 | 87.6744 | 93.5834
KillaloeWind2065RCP8.5 | Killaloe | Wind | RCP8.5 | 2065 | 70.2276 | 75.8235 | 81.76 | 87.643 | 93.5408
KillaloeWind2070RCP8.5 | Killaloe | Wind | RCP8.5 | 2070 | 70.2345 | 75.7789 | 81.6533 | 87.4861 | 93.331
KillaloeWind2075RCP8.5 | Killaloe | Wind | RCP8.5 | 2075 | 70.2299 | 75.7367 | 81.5627 | 87.3605 | 93.1638
KillaloeWind2080RCP8.5 | Killaloe | Wind | RCP8.5 | 2080 | 70.2253 | 75.6946 | 81.472 | 87.235 | 92.9966
KillaloeWind2085RCP8.5 | Killaloe | Wind | RCP8.5 | 2085 | 70.2564 | 75.7206 | 81.492 | 87.2478 | 93.0012
KillaloeWind2090RCP8.5 | Killaloe | Wind | RCP8.5 | 2090 | 70.2875 | 75.7466 | 81.512 | 87.2606 | 93.0058
KillaloeWind2095RCP8.5 | Killaloe | Wind | RCP8.5 | 2095 | 70.2875 | 75.7466 | 81.512 | 87.2606 | 93.0058
KillaloeWind2100RCP8.5 | Killaloe | Wind | RCP8.5 | 2100 | 70.2875 | 75.7466 | 81.512 | 87.2606 | 93.0058
KincardineIce Accretion2023RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2023 | 14.0283 | 16.8324 | 20.36 | 23.0746 | 25.7544
KincardineIce Accretion2025RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2025 | 14.0561 | 16.8767 | 20.4267 | 23.1537 | 25.851
KincardineIce Accretion2030RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2030 | 14.0839 | 16.9209 | 20.4933 | 23.2328 | 25.9476
KincardineIce Accretion2035RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2035 | 14.1118 | 16.9652 | 20.56 | 23.3119 | 26.0442
KincardineIce Accretion2040RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2040 | 14.1396 | 17.0095 | 20.6267 | 23.391 | 26.1408
KincardineIce Accretion2045RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2045 | 14.1674 | 17.0537 | 20.6933 | 23.4701 | 26.2374
KincardineIce Accretion2050RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2050 | 14.1006 | 17.005 | 20.672 | 23.4633 | 26.2534
KincardineIce Accretion2055RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2055 | 14.006 | 16.9121 | 20.584 | 23.3774 | 26.1727
KincardineIce Accretion2060RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2060 | 13.9114 | 16.8191 | 20.496 | 23.2916 | 26.0921
KincardineIce Accretion2065RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2065 | 13.8167 | 16.7262 | 20.408 | 23.2057 | 26.0114
KincardineIce Accretion2070RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2070 | 13.7221 | 16.6332 | 20.32 | 23.1198 | 25.9308
KincardineIce Accretion2075RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2075 | 13.6131 | 16.5198 | 20.2 | 22.9955 | 25.8006
KincardineIce Accretion2080RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2080 | 13.5041 | 16.4063 | 20.08 | 22.8712 | 25.6704
KincardineIce Accretion2085RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2085 | 13.395 | 16.2929 | 19.96 | 22.7469 | 25.5402
KincardineIce Accretion2090RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2090 | 13.286 | 16.1795 | 19.84 | 22.6226 | 25.41
KincardineIce Accretion2095RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2095 | 13.177 | 16.066 | 19.72 | 22.4983 | 25.2798
KincardineIce Accretion2100RCP4.5 | Kincardine | Ice Accretion | RCP4.5 | 2100 | 13.068 | 15.9526 | 19.6 | 22.374 | 25.1496
KincardineIce Accretion2023RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2023 | 14.0283 | 16.8324 | 20.36 | 23.0746 | 25.7544
KincardineIce Accretion2025RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2025 | 14.0561 | 16.8767 | 20.4267 | 23.1537 | 25.851
KincardineIce Accretion2030RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2030 | 14.0839 | 16.9209 | 20.4933 | 23.2328 | 25.9476
KincardineIce Accretion2035RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2035 | 14.1118 | 16.9652 | 20.56 | 23.3119 | 26.0442
KincardineIce Accretion2040RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2040 | 14.1396 | 17.0095 | 20.6267 | 23.391 | 26.1408
KincardineIce Accretion2045RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2045 | 14.1674 | 17.0537 | 20.6933 | 23.4701 | 26.2374
KincardineIce Accretion2050RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2050 | 14.1006 | 17.005 | 20.672 | 23.4633 | 26.2534
KincardineIce Accretion2055RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2055 | 14.006 | 16.9121 | 20.584 | 23.3774 | 26.1727
KincardineIce Accretion2060RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2060 | 13.9114 | 16.8191 | 20.496 | 23.2916 | 26.0921
KincardineIce Accretion2065RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2065 | 13.8167 | 16.7262 | 20.408 | 23.2057 | 26.0114
KincardineIce Accretion2070RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2070 | 13.7221 | 16.6332 | 20.32 | 23.1198 | 25.9308
KincardineIce Accretion2075RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2075 | 13.5586 | 16.463 | 20.14 | 22.9333 | 25.7355
KincardineIce Accretion2080RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2080 | 13.395 | 16.2929 | 19.96 | 22.7469 | 25.5402
KincardineIce Accretion2085RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2085 | 13.2315 | 16.1227 | 19.78 | 22.5604 | 25.3449
KincardineIce Accretion2090RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2090 | 12.6412 | 15.4657 | 19.0267 | 21.7412 | 24.444
KincardineIce Accretion2095RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2095 | 12.2144 | 14.9787 | 18.4533 | 21.1084 | 23.7384
KincardineIce Accretion2100RCP6.0 | Kincardine | Ice Accretion | RCP6.0 | 2100 | 11.7876 | 14.4918 | 17.88 | 20.4756 | 23.0328
KincardineIce Accretion2023RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2023 | 14.0283 | 16.8324 | 20.36 | 23.0746 | 25.7544
KincardineIce Accretion2025RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2025 | 14.0839 | 16.9209 | 20.4933 | 23.2328 | 25.9476
KincardineIce Accretion2030RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2030 | 14.1396 | 17.0095 | 20.6267 | 23.391 | 26.1408
KincardineIce Accretion2035RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2035 | 14.1953 | 17.098 | 20.76 | 23.5492 | 26.334
KincardineIce Accretion2040RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2040 | 14.0375 | 16.9431 | 20.6133 | 23.4061 | 26.1996
KincardineIce Accretion2045RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2045 | 13.8798 | 16.7881 | 20.4667 | 23.2629 | 26.0652
KincardineIce Accretion2050RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2050 | 13.5041 | 16.4063 | 20.08 | 22.8712 | 25.6704
KincardineIce Accretion2055RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2055 | 13.286 | 16.1795 | 19.84 | 22.6226 | 25.41
KincardineIce Accretion2060RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2060 | 12.6412 | 15.4657 | 19.0267 | 21.7412 | 24.444
KincardineIce Accretion2065RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2065 | 12.2144 | 14.9787 | 18.4533 | 21.1084 | 23.7384
KincardineIce Accretion2070RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2070 | 11.333 | 13.9717 | 17.28 | 19.8051 | 22.302
KincardineIce Accretion2075RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2075 | 10.8784 | 13.4515 | 16.68 | 19.1347 | 21.5712
KincardineIce Accretion2080RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2080 | 10.4238 | 12.9314 | 16.08 | 18.4642 | 20.8404
KincardineIce Accretion2085RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2085 | 9.9019 | 12.3255 | 15.36 | 17.6619 | 19.9584
KincardineIce Accretion2090RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2090 | 9.38 | 11.7196 | 14.64 | 16.8596 | 19.0764
KincardineIce Accretion2095RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2095 | 9.38 | 11.7196 | 14.64 | 16.8596 | 19.0764
KincardineIce Accretion2100RCP8.5 | Kincardine | Ice Accretion | RCP8.5 | 2100 | 9.38 | 11.7196 | 14.64 | 16.8596 | 19.0764
KincardineWind2023RCP4.5 | Kincardine | Wind | RCP4.5 | 2023 | 86.3225 | 93.1196 | 100.3167 | 107.4766 | 114.6432
KincardineWind2025RCP4.5 | Kincardine | Wind | RCP4.5 | 2025 | 86.4422 | 93.2608 | 100.485 | 107.669 | 114.8595
KincardineWind2030RCP4.5 | Kincardine | Wind | RCP4.5 | 2030 | 86.5619 | 93.4019 | 100.6533 | 107.8615 | 115.0758
KincardineWind2035RCP4.5 | Kincardine | Wind | RCP4.5 | 2035 | 86.6815 | 93.5431 | 100.8216 | 108.0539 | 115.2921
KincardineWind2040RCP4.5 | Kincardine | Wind | RCP4.5 | 2040 | 86.8012 | 93.6843 | 100.9899 | 108.2463 | 115.5084
KincardineWind2045RCP4.5 | Kincardine | Wind | RCP4.5 | 2045 | 86.9209 | 93.8255 | 101.1582 | 108.4388 | 115.7248
KincardineWind2050RCP4.5 | Kincardine | Wind | RCP4.5 | 2050 | 87.0611 | 93.9832 | 101.3344 | 108.6312 | 115.9366
KincardineWind2055RCP4.5 | Kincardine | Wind | RCP4.5 | 2055 | 87.0816 | 93.9998 | 101.3423 | 108.6312 | 115.932
KincardineWind2060RCP4.5 | Kincardine | Wind | RCP4.5 | 2060 | 87.1021 | 94.0164 | 101.3503 | 108.6312 | 115.9275
KincardineWind2065RCP4.5 | Kincardine | Wind | RCP4.5 | 2065 | 87.1226 | 94.0329 | 101.3582 | 108.6312 | 115.923
KincardineWind2070RCP4.5 | Kincardine | Wind | RCP4.5 | 2070 | 87.1432 | 94.0495 | 101.3661 | 108.6312 | 115.9185
KincardineWind2075RCP4.5 | Kincardine | Wind | RCP4.5 | 2075 | 87.2557 | 94.1968 | 101.5559 | 108.859 | 116.1818
KincardineWind2080RCP4.5 | Kincardine | Wind | RCP4.5 | 2080 | 87.3683 | 94.3441 | 101.7456 | 109.0867 | 116.4452
KincardineWind2085RCP4.5 | Kincardine | Wind | RCP4.5 | 2085 | 87.4808 | 94.4914 | 101.9353 | 109.3145 | 116.7085
KincardineWind2090RCP4.5 | Kincardine | Wind | RCP4.5 | 2090 | 87.5934 | 94.6388 | 102.1251 | 109.5422 | 116.9719
KincardineWind2095RCP4.5 | Kincardine | Wind | RCP4.5 | 2095 | 87.7059 | 94.7861 | 102.3149 | 109.77 | 117.2352
KincardineWind2100RCP4.5 | Kincardine | Wind | RCP4.5 | 2100 | 87.8185 | 94.9334 | 102.5046 | 109.9977 | 117.4985
KincardineWind2023RCP6.0 | Kincardine | Wind | RCP6.0 | 2023 | 86.3225 | 93.1196 | 100.3167 | 107.4766 | 114.6432
KincardineWind2025RCP6.0 | Kincardine | Wind | RCP6.0 | 2025 | 86.4422 | 93.2608 | 100.485 | 107.669 | 114.8595
KincardineWind2030RCP6.0 | Kincardine | Wind | RCP6.0 | 2030 | 86.5619 | 93.4019 | 100.6533 | 107.8615 | 115.0758
KincardineWind2035RCP6.0 | Kincardine | Wind | RCP6.0 | 2035 | 86.6815 | 93.5431 | 100.8216 | 108.0539 | 115.2921
KincardineWind2040RCP6.0 | Kincardine | Wind | RCP6.0 | 2040 | 86.8012 | 93.6843 | 100.9899 | 108.2463 | 115.5084
KincardineWind2045RCP6.0 | Kincardine | Wind | RCP6.0 | 2045 | 86.9209 | 93.8255 | 101.1582 | 108.4388 | 115.7248
KincardineWind2050RCP6.0 | Kincardine | Wind | RCP6.0 | 2050 | 87.0611 | 93.9832 | 101.3344 | 108.6312 | 115.9366
KincardineWind2055RCP6.0 | Kincardine | Wind | RCP6.0 | 2055 | 87.0816 | 93.9998 | 101.3423 | 108.6312 | 115.932
KincardineWind2060RCP6.0 | Kincardine | Wind | RCP6.0 | 2060 | 87.1021 | 94.0164 | 101.3503 | 108.6312 | 115.9275
KincardineWind2065RCP6.0 | Kincardine | Wind | RCP6.0 | 2065 | 87.1226 | 94.0329 | 101.3582 | 108.6312 | 115.923
KincardineWind2070RCP6.0 | Kincardine | Wind | RCP6.0 | 2070 | 87.1432 | 94.0495 | 101.3661 | 108.6312 | 115.9185
KincardineWind2075RCP6.0 | Kincardine | Wind | RCP6.0 | 2075 | 87.312 | 94.2705 | 101.6507 | 108.9728 | 116.3135
KincardineWind2080RCP6.0 | Kincardine | Wind | RCP6.0 | 2080 | 87.4808 | 94.4914 | 101.9353 | 109.3145 | 116.7085
KincardineWind2085RCP6.0 | Kincardine | Wind | RCP6.0 | 2085 | 87.6497 | 94.7124 | 102.22 | 109.6561 | 117.1035
KincardineWind2090RCP6.0 | Kincardine | Wind | RCP6.0 | 2090 | 88.1376 | 95.3231 | 102.9864 | 110.5591 | 118.1381
KincardineWind2095RCP6.0 | Kincardine | Wind | RCP6.0 | 2095 | 88.4568 | 95.7129 | 103.4682 | 111.1206 | 118.7776
KincardineWind2100RCP6.0 | Kincardine | Wind | RCP6.0 | 2100 | 88.7759 | 96.1027 | 103.95 | 111.682 | 119.4172
KincardineWind2023RCP8.5 | Kincardine | Wind | RCP8.5 | 2023 | 86.3225 | 93.1196 | 100.3167 | 107.4766 | 114.6432
KincardineWind2025RCP8.5 | Kincardine | Wind | RCP8.5 | 2025 | 86.5619 | 93.4019 | 100.6533 | 107.8615 | 115.0758
KincardineWind2030RCP8.5 | Kincardine | Wind | RCP8.5 | 2030 | 86.8012 | 93.6843 | 100.9899 | 108.2463 | 115.5084
KincardineWind2035RCP8.5 | Kincardine | Wind | RCP8.5 | 2035 | 87.0406 | 93.9666 | 101.3265 | 108.6312 | 115.9411
KincardineWind2040RCP8.5 | Kincardine | Wind | RCP8.5 | 2040 | 87.0748 | 93.9943 | 101.3397 | 108.6312 | 115.9336
KincardineWind2045RCP8.5 | Kincardine | Wind | RCP8.5 | 2045 | 87.109 | 94.0219 | 101.3529 | 108.6312 | 115.926
KincardineWind2050RCP8.5 | Kincardine | Wind | RCP8.5 | 2050 | 87.3683 | 94.3441 | 101.7456 | 109.0867 | 116.4452
KincardineWind2055RCP8.5 | Kincardine | Wind | RCP8.5 | 2055 | 87.5934 | 94.6388 | 102.1251 | 109.5422 | 116.9719
KincardineWind2060RCP8.5 | Kincardine | Wind | RCP8.5 | 2060 | 88.1376 | 95.3231 | 102.9864 | 110.5591 | 118.1381
KincardineWind2065RCP8.5 | Kincardine | Wind | RCP8.5 | 2065 | 88.4568 | 95.7129 | 103.4682 | 111.1206 | 118.7776
KincardineWind2070RCP8.5 | Kincardine | Wind | RCP8.5 | 2070 | 88.9326 | 96.2868 | 104.1645 | 111.9186 | 119.6843
KincardineWind2075RCP8.5 | Kincardine | Wind | RCP8.5 | 2075 | 89.0894 | 96.4709 | 104.379 | 112.1552 | 119.9514
KincardineWind2080RCP8.5 | Kincardine | Wind | RCP8.5 | 2080 | 89.2461 | 96.6551 | 104.5935 | 112.3917 | 120.2185
KincardineWind2085RCP8.5 | Kincardine | Wind | RCP8.5 | 2085 | 89.4513 | 96.8991 | 104.8855 | 112.7307 | 120.5966
KincardineWind2090RCP8.5 | Kincardine | Wind | RCP8.5 | 2090 | 89.6564 | 97.1431 | 105.1776 | 113.0697 | 120.9746
KincardineWind2095RCP8.5 | Kincardine | Wind | RCP8.5 | 2095 | 89.6564 | 97.1431 | 105.1776 | 113.0697 | 120.9746
KincardineWind2100RCP8.5 | Kincardine | Wind | RCP8.5 | 2100 | 89.6564 | 97.1431 | 105.1776 | 113.0697 | 120.9746
KingstonIce Accretion2023RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2023 | 19.4837 | 23.2168 | 27.972 | 31.6084 | 35.2094
KingstonIce Accretion2025RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2025 | 19.5649 | 23.3291 | 28.1213 | 31.7824 | 35.4152
KingstonIce Accretion2030RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2030 | 19.6461 | 23.4414 | 28.2707 | 31.9564 | 35.621
KingstonIce Accretion2035RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2035 | 19.7272 | 23.5537 | 28.42 | 32.1304 | 35.8268
KingstonIce Accretion2040RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2040 | 19.8084 | 23.6661 | 28.5693 | 32.3044 | 36.0326
KingstonIce Accretion2045RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2045 | 19.8896 | 23.7784 | 28.7187 | 32.4785 | 36.2384
KingstonIce Accretion2050RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2050 | 19.8617 | 23.7792 | 28.7504 | 32.5322 | 36.3243
KingstonIce Accretion2055RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2055 | 19.7526 | 23.6676 | 28.6328 | 32.412 | 36.2043
KingstonIce Accretion2060RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2060 | 19.6435 | 23.5561 | 28.5152 | 32.2918 | 36.0844
KingstonIce Accretion2065RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2065 | 19.5343 | 23.4445 | 28.3976 | 32.1716 | 35.9644
KingstonIce Accretion2070RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2070 | 19.4252 | 23.333 | 28.28 | 32.0513 | 35.8445
KingstonIce Accretion2075RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2075 | 19.4382 | 23.3756 | 28.3547 | 32.1515 | 35.968
KingstonIce Accretion2080RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2080 | 19.4512 | 23.4182 | 28.4293 | 32.2517 | 36.0914
KingstonIce Accretion2085RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2085 | 19.4642 | 23.4608 | 28.504 | 32.3519 | 36.2149
KingstonIce Accretion2090RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2090 | 19.4772 | 23.5034 | 28.5787 | 32.4521 | 36.3384
KingstonIce Accretion2095RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2095 | 19.4902 | 23.546 | 28.6533 | 32.5523 | 36.4619
KingstonIce Accretion2100RCP4.5 | Kingston | Ice Accretion | RCP4.5 | 2100 | 19.5032 | 23.5886 | 28.728 | 32.6525 | 36.5854
KingstonIce Accretion2023RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2023 | 19.4837 | 23.2168 | 27.972 | 31.6084 | 35.2094
KingstonIce Accretion2025RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2025 | 19.5649 | 23.3291 | 28.1213 | 31.7824 | 35.4152
KingstonIce Accretion2030RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2030 | 19.6461 | 23.4414 | 28.2707 | 31.9564 | 35.621
KingstonIce Accretion2035RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2035 | 19.7272 | 23.5537 | 28.42 | 32.1304 | 35.8268
KingstonIce Accretion2040RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2040 | 19.8084 | 23.6661 | 28.5693 | 32.3044 | 36.0326
KingstonIce Accretion2045RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2045 | 19.8896 | 23.7784 | 28.7187 | 32.4785 | 36.2384
KingstonIce Accretion2050RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2050 | 19.8617 | 23.7792 | 28.7504 | 32.5322 | 36.3243
KingstonIce Accretion2055RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2055 | 19.7526 | 23.6676 | 28.6328 | 32.412 | 36.2043
KingstonIce Accretion2060RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2060 | 19.6435 | 23.5561 | 28.5152 | 32.2918 | 36.0844
KingstonIce Accretion2065RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2065 | 19.5343 | 23.4445 | 28.3976 | 32.1716 | 35.9644
KingstonIce Accretion2070RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2070 | 19.4252 | 23.333 | 28.28 | 32.0513 | 35.8445
KingstonIce Accretion2075RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2075 | 19.4447 | 23.3969 | 28.392 | 32.2016 | 36.0297
KingstonIce Accretion2080RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2080 | 19.4642 | 23.4608 | 28.504 | 32.3519 | 36.2149
KingstonIce Accretion2085RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2085 | 19.4837 | 23.5247 | 28.616 | 32.5022 | 36.4001
KingstonIce Accretion2090RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2090 | 19.172 | 23.2168 | 28.3173 | 32.199 | 36.0914
KingstonIce Accretion2095RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2095 | 18.8407 | 22.8449 | 27.9067 | 31.7455 | 35.5975
KingstonIce Accretion2100RCP6.0 | Kingston | Ice Accretion | RCP6.0 | 2100 | 18.5095 | 22.4731 | 27.496 | 31.292 | 35.1036
KingstonIce Accretion2023RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2023 | 19.4837 | 23.2168 | 27.972 | 31.6084 | 35.2094
KingstonIce Accretion2025RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2025 | 19.6461 | 23.4414 | 28.2707 | 31.9564 | 35.621
KingstonIce Accretion2030RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2030 | 19.8084 | 23.6661 | 28.5693 | 32.3044 | 36.0326
KingstonIce Accretion2035RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2035 | 19.9708 | 23.8907 | 28.868 | 32.6525 | 36.4442
KingstonIce Accretion2040RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2040 | 19.7889 | 23.7048 | 28.672 | 32.4521 | 36.2443
KingstonIce Accretion2045RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2045 | 19.6071 | 23.5189 | 28.476 | 32.2517 | 36.0444
KingstonIce Accretion2050RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2050 | 19.4512 | 23.4182 | 28.4293 | 32.2517 | 36.0914
KingstonIce Accretion2055RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2055 | 19.4772 | 23.5034 | 28.5787 | 32.4521 | 36.3384
KingstonIce Accretion2060RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2060 | 19.172 | 23.2168 | 28.3173 | 32.199 | 36.0914
KingstonIce Accretion2065RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2065 | 18.8407 | 22.8449 | 27.9067 | 31.7455 | 35.5975
KingstonIce Accretion2070RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2070 | 18.2432 | 22.1942 | 27.188 | 30.9756 | 34.7626
KingstonIce Accretion2075RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2075 | 17.977 | 21.9153 | 26.88 | 30.6592 | 34.4215
KingstonIce Accretion2080RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2080 | 17.7107 | 21.6364 | 26.572 | 30.3428 | 34.0805
KingstonIce Accretion2085RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2085 | 17.0482 | 20.8579 | 25.648 | 29.2986 | 32.9162
KingstonIce Accretion2090RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2090 | 16.3858 | 20.0794 | 24.724 | 28.2545 | 31.752
KingstonIce Accretion2095RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2095 | 16.3858 | 20.0794 | 24.724 | 28.2545 | 31.752
KingstonIce Accretion2100RCP8.5 | Kingston | Ice Accretion | RCP8.5 | 2100 | 16.3858 | 20.0794 | 24.724 | 28.2545 | 31.752
KingstonWind2023RCP4.5 | Kingston | Wind | RCP4.5 | 2023 | 87.8991 | 94.5754 | 101.592 | 108.627 | 115.6637
KingstonWind2025RCP4.5 | Kingston | Wind | RCP4.5 | 2025 | 87.8829 | 94.547 | 101.5444 | 108.5652 | 115.5862
KingstonWind2030RCP4.5 | Kingston | Wind | RCP4.5 | 2030 | 87.8668 | 94.5185 | 101.4968 | 108.5033 | 115.5087
KingstonWind2035RCP4.5 | Kingston | Wind | RCP4.5 | 2035 | 87.8506 | 94.49 | 101.4492 | 108.4415 | 115.4312
KingstonWind2040RCP4.5 | Kingston | Wind | RCP4.5 | 2040 | 87.8345 | 94.4616 | 101.4016 | 108.3797 | 115.3536
KingstonWind2045RCP4.5 | Kingston | Wind | RCP4.5 | 2045 | 87.8183 | 94.4331 | 101.354 | 108.3178 | 115.2761
KingstonWind2050RCP4.5 | Kingston | Wind | RCP4.5 | 2050 | 87.9131 | 94.5394 | 101.4716 | 108.4459 | 115.4149
KingstonWind2055RCP4.5 | Kingston | Wind | RCP4.5 | 2055 | 88.0241 | 94.6741 | 101.6369 | 108.6358 | 115.6312
KingstonWind2060RCP4.5 | Kingston | Wind | RCP4.5 | 2060 | 88.1351 | 94.8088 | 101.8021 | 108.8257 | 115.8474
KingstonWind2065RCP4.5 | Kingston | Wind | RCP4.5 | 2065 | 88.2461 | 94.9435 | 101.9674 | 109.0156 | 116.0637
KingstonWind2070RCP4.5 | Kingston | Wind | RCP4.5 | 2070 | 88.357 | 95.0782 | 102.1326 | 109.2055 | 116.28
KingstonWind2075RCP4.5 | Kingston | Wind | RCP4.5 | 2075 | 88.4774 | 95.2426 | 102.3502 | 109.4674 | 116.5862
KingstonWind2080RCP4.5 | Kingston | Wind | RCP4.5 | 2080 | 88.5978 | 95.407 | 102.5678 | 109.7294 | 116.8924
KingstonWind2085RCP4.5 | Kingston | Wind | RCP4.5 | 2085 | 88.7182 | 95.5714 | 102.7854 | 109.9913 | 117.1986
KingstonWind2090RCP4.5 | Kingston | Wind | RCP4.5 | 2090 | 88.8385 | 95.7359 | 103.003 | 110.2532 | 117.5048
KingstonWind2095RCP4.5 | Kingston | Wind | RCP4.5 | 2095 | 88.9589 | 95.9003 | 103.2206 | 110.5152 | 117.811
KingstonWind2100RCP4.5 | Kingston | Wind | RCP4.5 | 2100 | 89.0793 | 96.0647 | 103.4382 | 110.7771 | 118.1172
KingstonWind2023RCP6.0 | Kingston | Wind | RCP6.0 | 2023 | 87.8991 | 94.5754 | 101.592 | 108.627 | 115.6637
KingstonWind2025RCP6.0 | Kingston | Wind | RCP6.0 | 2025 | 87.8829 | 94.547 | 101.5444 | 108.5652 | 115.5862
KingstonWind2030RCP6.0 | Kingston | Wind | RCP6.0 | 2030 | 87.8668 | 94.5185 | 101.4968 | 108.5033 | 115.5087
KingstonWind2035RCP6.0 | Kingston | Wind | RCP6.0 | 2035 | 87.8506 | 94.49 | 101.4492 | 108.4415 | 115.4312
KingstonWind2040RCP6.0 | Kingston | Wind | RCP6.0 | 2040 | 87.8345 | 94.4616 | 101.4016 | 108.3797 | 115.3536
KingstonWind2045RCP6.0 | Kingston | Wind | RCP6.0 | 2045 | 87.8183 | 94.4331 | 101.354 | 108.3178 | 115.2761
KingstonWind2050RCP6.0 | Kingston | Wind | RCP6.0 | 2050 | 87.9131 | 94.5394 | 101.4716 | 108.4459 | 115.4149
KingstonWind2055RCP6.0 | Kingston | Wind | RCP6.0 | 2055 | 88.0241 | 94.6741 | 101.6369 | 108.6358 | 115.6312
KingstonWind2060RCP6.0 | Kingston | Wind | RCP6.0 | 2060 | 88.1351 | 94.8088 | 101.8021 | 108.8257 | 115.8474
KingstonWind2065RCP6.0 | Kingston | Wind | RCP6.0 | 2065 | 88.2461 | 94.9435 | 101.9674 | 109.0156 | 116.0637
KingstonWind2070RCP6.0 | Kingston | Wind | RCP6.0 | 2070 | 88.357 | 95.0782 | 102.1326 | 109.2055 | 116.28
KingstonWind2075RCP6.0 | Kingston | Wind | RCP6.0 | 2075 | 88.5376 | 95.3248 | 102.459 | 109.5984 | 116.7393
KingstonWind2080RCP6.0 | Kingston | Wind | RCP6.0 | 2080 | 88.7182 | 95.5714 | 102.7854 | 109.9913 | 117.1986
KingstonWind2085RCP6.0 | Kingston | Wind | RCP6.0 | 2085 | 88.8987 | 95.8181 | 103.1118 | 110.3842 | 117.6579
KingstonWind2090RCP6.0 | Kingston | Wind | RCP6.0 | 2090 | 89.2818 | 96.3272 | 103.7782 | 111.1846 | 118.5901
KingstonWind2095RCP6.0 | Kingston | Wind | RCP6.0 | 2095 | 89.4844 | 96.5896 | 104.1182 | 111.592 | 119.063
KingstonWind2100RCP6.0 | Kingston | Wind | RCP6.0 | 2100 | 89.687 | 96.8521 | 104.4582 | 111.9995 | 119.5358
KingstonWind2023RCP8.5 | Kingston | Wind | RCP8.5 | 2023 | 87.8991 | 94.5754 | 101.592 | 108.627 | 115.6637
KingstonWind2025RCP8.5 | Kingston | Wind | RCP8.5 | 2025 | 87.8668 | 94.5185 | 101.4968 | 108.5033 | 115.5087
KingstonWind2030RCP8.5 | Kingston | Wind | RCP8.5 | 2030 | 87.8345 | 94.4616 | 101.4016 | 108.3797 | 115.3536
KingstonWind2035RCP8.5 | Kingston | Wind | RCP8.5 | 2035 | 87.8022 | 94.4047 | 101.3064 | 108.256 | 115.1986
KingstonWind2040RCP8.5 | Kingston | Wind | RCP8.5 | 2040 | 87.9871 | 94.6292 | 101.5818 | 108.5725 | 115.5591
KingstonWind2045RCP8.5 | Kingston | Wind | RCP8.5 | 2045 | 88.1721 | 94.8537 | 101.8572 | 108.889 | 115.9195
KingstonWind2050RCP8.5 | Kingston | Wind | RCP8.5 | 2050 | 88.5978 | 95.407 | 102.5678 | 109.7294 | 116.8924
KingstonWind2055RCP8.5 | Kingston | Wind | RCP8.5 | 2055 | 88.8385 | 95.7359 | 103.003 | 110.2532 | 117.5048
KingstonWind2060RCP8.5 | Kingston | Wind | RCP8.5 | 2060 | 89.2818 | 96.3272 | 103.7782 | 111.1846 | 118.5901
KingstonWind2065RCP8.5 | Kingston | Wind | RCP8.5 | 2065 | 89.4844 | 96.5896 | 104.1182 | 111.592 | 119.063
KingstonWind2070RCP8.5 | Kingston | Wind | RCP8.5 | 2070 | 89.7604 | 96.9596 | 104.6078 | 112.185 | 119.7568
KingstonWind2075RCP8.5 | Kingston | Wind | RCP8.5 | 2075 | 89.8338 | 97.0671 | 104.7574 | 112.3705 | 119.9777
KingstonWind2080RCP8.5 | Kingston | Wind | RCP8.5 | 2080 | 89.9072 | 97.1746 | 104.907 | 112.5561 | 120.1986
KingstonWind2085RCP8.5 | Kingston | Wind | RCP8.5 | 2085 | 90.0789 | 97.4117 | 105.2283 | 112.9435 | 120.6638
KingstonWind2090RCP8.5 | Kingston | Wind | RCP8.5 | 2090 | 90.2507 | 97.6489 | 105.5496 | 113.331 | 121.1289
KingstonWind2095RCP8.5 | Kingston | Wind | RCP8.5 | 2095 | 90.2507 | 97.6489 | 105.5496 | 113.331 | 121.1289
KingstonWind2100RCP8.5 | Kingston | Wind | RCP8.5 | 2100 | 90.2507 | 97.6489 | 105.5496 | 113.331 | 121.1289
KinmountIce Accretion2023RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2023 | 17.2396 | 20.584 | 24.825 | 28.0522 | 31.311
KinmountIce Accretion2025RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2025 | 17.2251 | 20.5771 | 24.825 | 28.057 | 31.3215
KinmountIce Accretion2030RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2030 | 17.2106 | 20.5702 | 24.825 | 28.0617 | 31.332
KinmountIce Accretion2035RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2035 | 17.1961 | 20.5633 | 24.825 | 28.0664 | 31.3425
KinmountIce Accretion2040RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2040 | 17.1816 | 20.5563 | 24.825 | 28.0711 | 31.353
KinmountIce Accretion2045RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2045 | 17.1671 | 20.5494 | 24.825 | 28.0758 | 31.3635
KinmountIce Accretion2050RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2050 | 17.1109 | 20.5134 | 24.81 | 28.0748 | 31.374
KinmountIce Accretion2055RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2055 | 17.0691 | 20.4844 | 24.795 | 28.0692 | 31.374
KinmountIce Accretion2060RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2060 | 17.0274 | 20.4553 | 24.78 | 28.0635 | 31.374
KinmountIce Accretion2065RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2065 | 16.9856 | 20.4263 | 24.765 | 28.0579 | 31.374
KinmountIce Accretion2070RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2070 | 16.9439 | 20.3972 | 24.75 | 28.0522 | 31.374
KinmountIce Accretion2075RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2075 | 17.0134 | 20.4975 | 24.8875 | 28.2217 | 31.5735
KinmountIce Accretion2080RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2080 | 17.083 | 20.5978 | 25.025 | 28.3912 | 31.773
KinmountIce Accretion2085RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2085 | 17.1526 | 20.6981 | 25.1625 | 28.5607 | 31.9725
KinmountIce Accretion2090RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2090 | 17.2222 | 20.7984 | 25.3 | 28.7302 | 32.172
KinmountIce Accretion2095RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2095 | 17.2918 | 20.8987 | 25.4375 | 28.8997 | 32.3715
KinmountIce Accretion2100RCP4.5 | Kinmount | Ice Accretion | RCP4.5 | 2100 | 17.3614 | 20.999 | 25.575 | 29.0692 | 32.571
KinmountIce Accretion2023RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2023 | 17.2396 | 20.584 | 24.825 | 28.0522 | 31.311
KinmountIce Accretion2025RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2025 | 17.2251 | 20.5771 | 24.825 | 28.057 | 31.3215
KinmountIce Accretion2030RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2030 | 17.2106 | 20.5702 | 24.825 | 28.0617 | 31.332
KinmountIce Accretion2035RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2035 | 17.1961 | 20.5633 | 24.825 | 28.0664 | 31.3425
KinmountIce Accretion2040RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2040 | 17.1816 | 20.5563 | 24.825 | 28.0711 | 31.353
KinmountIce Accretion2045RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2045 | 17.1671 | 20.5494 | 24.825 | 28.0758 | 31.3635
KinmountIce Accretion2050RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2050 | 17.1109 | 20.5134 | 24.81 | 28.0748 | 31.374
KinmountIce Accretion2055RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2055 | 17.0691 | 20.4844 | 24.795 | 28.0692 | 31.374
KinmountIce Accretion2060RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2060 | 17.0274 | 20.4553 | 24.78 | 28.0635 | 31.374
KinmountIce Accretion2065RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2065 | 16.9856 | 20.4263 | 24.765 | 28.0579 | 31.374
KinmountIce Accretion2070RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2070 | 16.9439 | 20.3972 | 24.75 | 28.0522 | 31.374
KinmountIce Accretion2075RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2075 | 17.0482 | 20.5477 | 24.9563 | 28.3065 | 31.6732
KinmountIce Accretion2080RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2080 | 17.1526 | 20.6981 | 25.1625 | 28.5607 | 31.9725
KinmountIce Accretion2085RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2085 | 17.257 | 20.8486 | 25.3687 | 28.815 | 32.2717
KinmountIce Accretion2090RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2090 | 17.2512 | 20.916 | 25.5333 | 29.0504 | 32.5815
KinmountIce Accretion2095RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2095 | 17.141 | 20.833 | 25.4917 | 29.0316 | 32.592
KinmountIce Accretion2100RCP6.0 | Kinmount | Ice Accretion | RCP6.0 | 2100 | 17.0308 | 20.75 | 25.45 | 29.0127 | 32.6025
KinmountIce Accretion2023RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2023 | 17.2396 | 20.584 | 24.825 | 28.0522 | 31.311
KinmountIce Accretion2025RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2025 | 17.2106 | 20.5702 | 24.825 | 28.0617 | 31.332
KinmountIce Accretion2030RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2030 | 17.1816 | 20.5563 | 24.825 | 28.0711 | 31.353
KinmountIce Accretion2035RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2035 | 17.1526 | 20.5425 | 24.825 | 28.0805 | 31.374
KinmountIce Accretion2040RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2040 | 17.083 | 20.4941 | 24.8 | 28.0711 | 31.374
KinmountIce Accretion2045RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2045 | 17.0134 | 20.4457 | 24.775 | 28.0617 | 31.374
KinmountIce Accretion2050RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2050 | 17.083 | 20.5978 | 25.025 | 28.3912 | 31.773
KinmountIce Accretion2055RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2055 | 17.2222 | 20.7984 | 25.3 | 28.7302 | 32.172
KinmountIce Accretion2060RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2060 | 17.2512 | 20.916 | 25.5333 | 29.0504 | 32.5815
KinmountIce Accretion2065RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2065 | 17.141 | 20.833 | 25.4917 | 29.0316 | 32.592
KinmountIce Accretion2070RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2070 | 16.8105 | 20.5218 | 25.2167 | 28.7773 | 32.3505
KinmountIce Accretion2075RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2075 | 16.5901 | 20.2935 | 24.9833 | 28.5419 | 32.0985
KinmountIce Accretion2080RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2080 | 16.3698 | 20.0652 | 24.75 | 28.3065 | 31.8465
KinmountIce Accretion2085RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2085 | 15.6826 | 19.2871 | 23.85 | 27.3177 | 30.7597
KinmountIce Accretion2090RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2090 | 14.9955 | 18.509 | 22.95 | 26.329 | 29.673
KinmountIce Accretion2095RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2095 | 14.9955 | 18.509 | 22.95 | 26.329 | 29.673
KinmountIce Accretion2100RCP8.5 | Kinmount | Ice Accretion | RCP8.5 | 2100 | 14.9955 | 18.509 | 22.95 | 26.329 | 29.673
KinmountWind2023RCP4.5 | Kinmount | Wind | RCP4.5 | 2023 | 69.3273 | 74.6381 | 80.224 | 85.814 | 91.4006
KinmountWind2025RCP4.5 | Kinmount | Wind | RCP4.5 | 2025 | 69.3802 | 74.7001 | 80.2973 | 85.8967 | 91.4934
KinmountWind2030RCP4.5 | Kinmount | Wind | RCP4.5 | 2030 | 69.4332 | 74.7621 | 80.3707 | 85.9795 | 91.5861
KinmountWind2035RCP4.5 | Kinmount | Wind | RCP4.5 | 2035 | 69.4862 | 74.8241 | 80.444 | 86.0622 | 91.6788
KinmountWind2040RCP4.5 | Kinmount | Wind | RCP4.5 | 2040 | 69.5391 | 74.8861 | 80.5173 | 86.145 | 91.7715
KinmountWind2045RCP4.5 | Kinmount | Wind | RCP4.5 | 2045 | 69.5921 | 74.9481 | 80.5907 | 86.2277 | 91.8642
KinmountWind2050RCP4.5 | Kinmount | Wind | RCP4.5 | 2050 | 69.7155 | 75.0889 | 80.7504 | 86.4046 | 92.0591
KinmountWind2055RCP4.5 | Kinmount | Wind | RCP4.5 | 2055 | 69.786 | 75.1678 | 80.8368 | 86.4988 | 92.1612
KinmountWind2060RCP4.5 | Kinmount | Wind | RCP4.5 | 2060 | 69.8564 | 75.2467 | 80.9232 | 86.593 | 92.2634
KinmountWind2065RCP4.5 | Kinmount | Wind | RCP4.5 | 2065 | 69.9269 | 75.3255 | 81.0096 | 86.6871 | 92.3655
KinmountWind2070RCP4.5 | Kinmount | Wind | RCP4.5 | 2070 | 69.9973 | 75.4044 | 81.096 | 86.7813 | 92.4677
KinmountWind2075RCP4.5 | Kinmount | Wind | RCP4.5 | 2075 | 69.9755 | 75.3821 | 81.072 | 86.757 | 92.4434
KinmountWind2080RCP4.5 | Kinmount | Wind | RCP4.5 | 2080 | 69.9536 | 75.3598 | 81.048 | 86.7328 | 92.419
KinmountWind2085RCP4.5 | Kinmount | Wind | RCP4.5 | 2085 | 69.9317 | 75.3374 | 81.024 | 86.7085 | 92.3947
KinmountWind2090RCP4.5 | Kinmount | Wind | RCP4.5 | 2090 | 69.9098 | 75.3151 | 81 | 86.6843 | 92.3704
KinmountWind2095RCP4.5 | Kinmount | Wind | RCP4.5 | 2095 | 69.888 | 75.2928 | 80.976 | 86.66 | 92.3461
KinmountWind2100RCP4.5 | Kinmount | Wind | RCP4.5 | 2100 | 69.8661 | 75.2705 | 80.952 | 86.6358 | 92.3218
KinmountWind2023RCP6.0 | Kinmount | Wind | RCP6.0 | 2023 | 69.3273 | 74.6381 | 80.224 | 85.814 | 91.4006
KinmountWind2025RCP6.0 | Kinmount | Wind | RCP6.0 | 2025 | 69.3802 | 74.7001 | 80.2973 | 85.8967 | 91.4934
KinmountWind2030RCP6.0 | Kinmount | Wind | RCP6.0 | 2030 | 69.4332 | 74.7621 | 80.3707 | 85.9795 | 91.5861
KinmountWind2035RCP6.0 | Kinmount | Wind | RCP6.0 | 2035 | 69.4862 | 74.8241 | 80.444 | 86.0622 | 91.6788
KinmountWind2040RCP6.0 | Kinmount | Wind | RCP6.0 | 2040 | 69.5391 | 74.8861 | 80.5173 | 86.145 | 91.7715
KinmountWind2045RCP6.0 | Kinmount | Wind | RCP6.0 | 2045 | 69.5921 | 74.9481 | 80.5907 | 86.2277 | 91.8642
KinmountWind2050RCP6.0 | Kinmount | Wind | RCP6.0 | 2050 | 69.7155 | 75.0889 | 80.7504 | 86.4046 | 92.0591
KinmountWind2055RCP6.0 | Kinmount | Wind | RCP6.0 | 2055 | 69.786 | 75.1678 | 80.8368 | 86.4988 | 92.1612
KinmountWind2060RCP6.0 | Kinmount | Wind | RCP6.0 | 2060 | 69.8564 | 75.2467 | 80.9232 | 86.593 | 92.2634
KinmountWind2065RCP6.0 | Kinmount | Wind | RCP6.0 | 2065 | 69.9269 | 75.3255 | 81.0096 | 86.6871 | 92.3655
KinmountWind2070RCP6.0 | Kinmount | Wind | RCP6.0 | 2070 | 69.9973 | 75.4044 | 81.096 | 86.7813 | 92.4677
KinmountWind2075RCP6.0 | Kinmount | Wind | RCP6.0 | 2075 | 69.9645 | 75.3709 | 81.06 | 86.7449 | 92.4312
KinmountWind2080RCP6.0 | Kinmount | Wind | RCP6.0 | 2080 | 69.9317 | 75.3374 | 81.024 | 86.7085 | 92.3947
KinmountWind2085RCP6.0 | Kinmount | Wind | RCP6.0 | 2085 | 69.8989 | 75.304 | 80.988 | 86.6721 | 92.3582
KinmountWind2090RCP6.0 | Kinmount | Wind | RCP6.0 | 2090 | 69.9167 | 75.3275 | 81.0187 | 86.7099 | 92.4038
KinmountWind2095RCP6.0 | Kinmount | Wind | RCP6.0 | 2095 | 69.9674 | 75.3846 | 81.0853 | 86.7841 | 92.4859
KinmountWind2100RCP6.0 | Kinmount | Wind | RCP6.0 | 2100 | 70.0181 | 75.4416 | 81.152 | 86.8583 | 92.568
KinmountWind2023RCP8.5 | Kinmount | Wind | RCP8.5 | 2023 | 69.3273 | 74.6381 | 80.224 | 85.814 | 91.4006
KinmountWind2025RCP8.5 | Kinmount | Wind | RCP8.5 | 2025 | 69.4332 | 74.7621 | 80.3707 | 85.9795 | 91.5861
KinmountWind2030RCP8.5 | Kinmount | Wind | RCP8.5 | 2030 | 69.5391 | 74.8861 | 80.5173 | 86.145 | 91.7715
KinmountWind2035RCP8.5 | Kinmount | Wind | RCP8.5 | 2035 | 69.645 | 75.0101 | 80.664 | 86.3105 | 91.957
KinmountWind2040RCP8.5 | Kinmount | Wind | RCP8.5 | 2040 | 69.7625 | 75.1415 | 80.808 | 86.4674 | 92.1272
KinmountWind2045RCP8.5 | Kinmount | Wind | RCP8.5 | 2045 | 69.8799 | 75.273 | 80.952 | 86.6243 | 92.2974
KinmountWind2050RCP8.5 | Kinmount | Wind | RCP8.5 | 2050 | 69.9536 | 75.3598 | 81.048 | 86.7328 | 92.419
KinmountWind2055RCP8.5 | Kinmount | Wind | RCP8.5 | 2055 | 69.9098 | 75.3151 | 81 | 86.6843 | 92.3704
KinmountWind2060RCP8.5 | Kinmount | Wind | RCP8.5 | 2060 | 69.9167 | 75.3275 | 81.0187 | 86.7099 | 92.4038
KinmountWind2065RCP8.5 | Kinmount | Wind | RCP8.5 | 2065 | 69.9674 | 75.3846 | 81.0853 | 86.7841 | 92.4859
KinmountWind2070RCP8.5 | Kinmount | Wind | RCP8.5 | 2070 | 70.0342 | 75.454 | 81.1627 | 86.8669 | 92.5741
KinmountWind2075RCP8.5 | Kinmount | Wind | RCP8.5 | 2075 | 70.0503 | 75.4664 | 81.1733 | 86.8754 | 92.5802
KinmountWind2080RCP8.5 | Kinmount | Wind | RCP8.5 | 2080 | 70.0664 | 75.4788 | 81.184 | 86.884 | 92.5862
KinmountWind2085RCP8.5 | Kinmount | Wind | RCP8.5 | 2085 | 70.1666 | 75.5904 | 81.304 | 87.0124 | 92.723
KinmountWind2090RCP8.5 | Kinmount | Wind | RCP8.5 | 2090 | 70.2667 | 75.702 | 81.424 | 87.1408 | 92.8598
KinmountWind2095RCP8.5 | Kinmount | Wind | RCP8.5 | 2095 | 70.2667 | 75.702 | 81.424 | 87.1408 | 92.8598
KinmountWind2100RCP8.5 | Kinmount | Wind | RCP8.5 | 2100 | 70.2667 | 75.702 | 81.424 | 87.1408 | 92.8598
Kirkland LakeIce Accretion2023RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2023 | 14.6545 | 17.5296 | 21.16 | 23.9334 | 26.712
Kirkland LakeIce Accretion2025RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2025 | 14.6638 | 17.5407 | 21.1733 | 23.9522 | 26.733
Kirkland LakeIce Accretion2030RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2030 | 14.6731 | 17.5517 | 21.1867 | 23.9711 | 26.754
Kirkland LakeIce Accretion2035RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2035 | 14.6824 | 17.5628 | 21.2 | 23.9899 | 26.775
Kirkland LakeIce Accretion2040RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2040 | 14.6916 | 17.5739 | 21.2133 | 24.0087 | 26.796
Kirkland LakeIce Accretion2045RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2045 | 14.7009 | 17.5849 | 21.2267 | 24.0276 | 26.817
Kirkland LakeIce Accretion2050RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2050 | 14.816 | 17.7321 | 21.416 | 24.2498 | 27.0698
Kirkland LakeIce Accretion2055RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2055 | 14.9217 | 17.8682 | 21.592 | 24.4532 | 27.3017
Kirkland LakeIce Accretion2060RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2060 | 15.0275 | 18.0044 | 21.768 | 24.6566 | 27.5335
Kirkland LakeIce Accretion2065RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2065 | 15.1333 | 18.1405 | 21.944 | 24.86 | 27.7654
Kirkland LakeIce Accretion2070RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2070 | 15.239 | 18.2766 | 22.12 | 25.0634 | 27.9972
Kirkland LakeIce Accretion2075RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2075 | 15.3249 | 18.39 | 22.2667 | 25.2367 | 28.1988
Kirkland LakeIce Accretion2080RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2080 | 15.4107 | 18.5035 | 22.4133 | 25.4099 | 28.4004
Kirkland LakeIce Accretion2085RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2085 | 15.4965 | 18.6169 | 22.56 | 25.5832 | 28.602
Kirkland LakeIce Accretion2090RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2090 | 15.5823 | 18.7303 | 22.7067 | 25.7565 | 28.8036
Kirkland LakeIce Accretion2095RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2095 | 15.6681 | 18.8438 | 22.8533 | 25.9297 | 29.0052
Kirkland LakeIce Accretion2100RCP4.5 | Kirkland Lake | Ice Accretion | RCP4.5 | 2100 | 15.754 | 18.9572 | 23 | 26.103 | 29.2068
Kirkland LakeIce Accretion2023RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2023 | 14.6545 | 17.5296 | 21.16 | 23.9334 | 26.712
Kirkland LakeIce Accretion2025RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2025 | 14.6638 | 17.5407 | 21.1733 | 23.9522 | 26.733
Kirkland LakeIce Accretion2030RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2030 | 14.6731 | 17.5517 | 21.1867 | 23.9711 | 26.754
Kirkland LakeIce Accretion2035RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2035 | 14.6824 | 17.5628 | 21.2 | 23.9899 | 26.775
Kirkland LakeIce Accretion2040RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2040 | 14.6916 | 17.5739 | 21.2133 | 24.0087 | 26.796
Kirkland LakeIce Accretion2045RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2045 | 14.7009 | 17.5849 | 21.2267 | 24.0276 | 26.817
Kirkland LakeIce Accretion2050RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2050 | 14.816 | 17.7321 | 21.416 | 24.2498 | 27.0698
Kirkland LakeIce Accretion2055RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2055 | 14.9217 | 17.8682 | 21.592 | 24.4532 | 27.3017
Kirkland LakeIce Accretion2060RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2060 | 15.0275 | 18.0044 | 21.768 | 24.6566 | 27.5335
Kirkland LakeIce Accretion2065RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2065 | 15.1333 | 18.1405 | 21.944 | 24.86 | 27.7654
Kirkland LakeIce Accretion2070RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2070 | 15.239 | 18.2766 | 22.12 | 25.0634 | 27.9972
Kirkland LakeIce Accretion2075RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2075 | 15.3678 | 18.4467 | 22.34 | 25.3233 | 28.2996
Kirkland LakeIce Accretion2080RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2080 | 15.4965 | 18.6169 | 22.56 | 25.5832 | 28.602
Kirkland LakeIce Accretion2085RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2085 | 15.6252 | 18.787 | 22.78 | 25.8431 | 28.9044
Kirkland LakeIce Accretion2090RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2090 | 15.7586 | 18.9793 | 23.0467 | 26.1633 | 29.274
Kirkland LakeIce Accretion2095RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2095 | 15.7632 | 19.0015 | 23.0933 | 26.2235 | 29.3412
Kirkland LakeIce Accretion2100RCP6.0 | Kirkland Lake | Ice Accretion | RCP6.0 | 2100 | 15.7679 | 19.0236 | 23.14 | 26.2838 | 29.4084
Kirkland LakeIce Accretion2023RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2023 | 14.6545 | 17.5296 | 21.16 | 23.9334 | 26.712
Kirkland LakeIce Accretion2025RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2025 | 14.6731 | 17.5517 | 21.1867 | 23.9711 | 26.754
Kirkland LakeIce Accretion2030RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2030 | 14.6916 | 17.5739 | 21.2133 | 24.0087 | 26.796
Kirkland LakeIce Accretion2035RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2035 | 14.7102 | 17.596 | 21.24 | 24.0464 | 26.838
Kirkland LakeIce Accretion2040RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2040 | 14.8865 | 17.8229 | 21.5333 | 24.3854 | 27.2244
Kirkland LakeIce Accretion2045RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2045 | 15.0627 | 18.0497 | 21.8267 | 24.7244 | 27.6108
Kirkland LakeIce Accretion2050RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2050 | 15.4107 | 18.5035 | 22.4133 | 25.4099 | 28.4004
Kirkland LakeIce Accretion2055RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2055 | 15.5823 | 18.7303 | 22.7067 | 25.7565 | 28.8036
Kirkland LakeIce Accretion2060RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2060 | 15.7586 | 18.9793 | 23.0467 | 26.1633 | 29.274
Kirkland LakeIce Accretion2065RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2065 | 15.7632 | 19.0015 | 23.0933 | 26.2235 | 29.3412
Kirkland LakeIce Accretion2070RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2070 | 15.5359 | 18.7469 | 22.8067 | 25.9071 | 28.9968
Kirkland LakeIce Accretion2075RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2075 | 15.304 | 18.4703 | 22.4733 | 25.5305 | 28.5852
Kirkland LakeIce Accretion2080RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2080 | 15.072 | 18.1936 | 22.14 | 25.1538 | 28.1736
Kirkland LakeIce Accretion2085RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2085 | 14.8841 | 18.0027 | 21.94 | 24.9391 | 27.9468
Kirkland LakeIce Accretion2090RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2090 | 14.6963 | 17.8118 | 21.74 | 24.7244 | 27.72
Kirkland LakeIce Accretion2095RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2095 | 14.6963 | 17.8118 | 21.74 | 24.7244 | 27.72
Kirkland LakeIce Accretion2100RCP8.5 | Kirkland Lake | Ice Accretion | RCP8.5 | 2100 | 14.6963 | 17.8118 | 21.74 | 24.7244 | 27.72
Kirkland LakeWind2023RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2023 | 74.7422 | 80.4759 | 86.4902 | 92.5169 | 98.5498
Kirkland LakeWind2025RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2025 | 74.8065 | 80.5439 | 86.5662 | 92.5982 | 98.6364
Kirkland LakeWind2030RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2030 | 74.8709 | 80.6118 | 86.6421 | 92.6795 | 98.723
Kirkland LakeWind2035RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2035 | 74.9353 | 80.6798 | 86.7181 | 92.7608 | 98.8096
Kirkland LakeWind2040RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2040 | 74.9996 | 80.7478 | 86.7941 | 92.842 | 98.8962
Kirkland LakeWind2045RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2045 | 75.064 | 80.8158 | 86.87 | 92.9233 | 98.9828
Kirkland LakeWind2050RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2050 | 75.1476 | 80.8982 | 86.9512 | 93.0046 | 99.0616
Kirkland LakeWind2055RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2055 | 75.1669 | 80.9126 | 86.9563 | 93.0046 | 99.0537
Kirkland LakeWind2060RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2060 | 75.1862 | 80.927 | 86.9615 | 93.0046 | 99.0459
Kirkland LakeWind2065RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2065 | 75.2056 | 80.9414 | 86.9666 | 93.0046 | 99.038
Kirkland LakeWind2070RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2070 | 75.2249 | 80.9558 | 86.9718 | 93.0046 | 99.0302
Kirkland LakeWind2075RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2075 | 75.2669 | 81.0064 | 87.032 | 93.0736 | 99.1086
Kirkland LakeWind2080RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2080 | 75.309 | 81.0571 | 87.0922 | 93.1426 | 99.1871
Kirkland LakeWind2085RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2085 | 75.3511 | 81.1077 | 87.1524 | 93.2117 | 99.2655
Kirkland LakeWind2090RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2090 | 75.3932 | 81.1584 | 87.2126 | 93.2807 | 99.3439
Kirkland LakeWind2095RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2095 | 75.4353 | 81.209 | 87.2728 | 93.3497 | 99.4224
Kirkland LakeWind2100RCP4.5 | Kirkland Lake | Wind | RCP4.5 | 2100 | 75.4773 | 81.2597 | 87.333 | 93.4187 | 99.5008
Kirkland LakeWind2023RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2023 | 74.7422 | 80.4759 | 86.4902 | 92.5169 | 98.5498
Kirkland LakeWind2025RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2025 | 74.8065 | 80.5439 | 86.5662 | 92.5982 | 98.6364
Kirkland LakeWind2030RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2030 | 74.8709 | 80.6118 | 86.6421 | 92.6795 | 98.723
Kirkland LakeWind2035RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2035 | 74.9353 | 80.6798 | 86.7181 | 92.7608 | 98.8096
Kirkland LakeWind2040RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2040 | 74.9996 | 80.7478 | 86.7941 | 92.842 | 98.8962
Kirkland LakeWind2045RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2045 | 75.064 | 80.8158 | 86.87 | 92.9233 | 98.9828
Kirkland LakeWind2050RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2050 | 75.1476 | 80.8982 | 86.9512 | 93.0046 | 99.0616
Kirkland LakeWind2055RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2055 | 75.1669 | 80.9126 | 86.9563 | 93.0046 | 99.0537
Kirkland LakeWind2060RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2060 | 75.1862 | 80.927 | 86.9615 | 93.0046 | 99.0459
Kirkland LakeWind2065RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2065 | 75.2056 | 80.9414 | 86.9666 | 93.0046 | 99.038
Kirkland LakeWind2070RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2070 | 75.2249 | 80.9558 | 86.9718 | 93.0046 | 99.0302
Kirkland LakeWind2075RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2075 | 75.288 | 81.0317 | 87.0621 | 93.1081 | 99.1479
Kirkland LakeWind2080RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2080 | 75.3511 | 81.1077 | 87.1524 | 93.2117 | 99.2655
Kirkland LakeWind2085RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2085 | 75.4142 | 81.1837 | 87.2427 | 93.3152 | 99.3831
Kirkland LakeWind2090RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2090 | 75.5194 | 81.2997 | 87.3731 | 93.4586 | 99.5433
Kirkland LakeWind2095RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2095 | 75.5615 | 81.3397 | 87.4133 | 93.4985 | 99.5858
Kirkland LakeWind2100RCP6.0 | Kirkland Lake | Wind | RCP6.0 | 2100 | 75.6036 | 81.3797 | 87.4534 | 93.5383 | 99.6282
Kirkland LakeWind2023RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2023 | 74.7422 | 80.4759 | 86.4902 | 92.5169 | 98.5498
Kirkland LakeWind2025RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2025 | 74.8709 | 80.6118 | 86.6421 | 92.6795 | 98.723
Kirkland LakeWind2030RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2030 | 74.9996 | 80.7478 | 86.7941 | 92.842 | 98.8962
Kirkland LakeWind2035RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2035 | 75.1283 | 80.8838 | 86.946 | 93.0046 | 99.0694
Kirkland LakeWind2040RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2040 | 75.1605 | 80.9078 | 86.9546 | 93.0046 | 99.0563
Kirkland LakeWind2045RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2045 | 75.1927 | 80.9318 | 86.9632 | 93.0046 | 99.0433
Kirkland LakeWind2050RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2050 | 75.309 | 81.0571 | 87.0922 | 93.1426 | 99.1871
Kirkland LakeWind2055RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2055 | 75.3932 | 81.1584 | 87.2126 | 93.2807 | 99.3439
Kirkland LakeWind2060RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2060 | 75.5194 | 81.2997 | 87.3731 | 93.4586 | 99.5433
Kirkland LakeWind2065RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2065 | 75.5615 | 81.3397 | 87.4133 | 93.4985 | 99.5858
Kirkland LakeWind2070RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2070 | 75.7199 | 81.497 | 87.5709 | 93.658 | 99.7459
Kirkland LakeWind2075RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2075 | 75.8363 | 81.6143 | 87.6885 | 93.7776 | 99.8635
Kirkland LakeWind2080RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2080 | 75.9526 | 81.7316 | 87.806 | 93.8972 | 99.9812
Kirkland LakeWind2085RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2085 | 75.9526 | 81.7436 | 87.8318 | 93.934 | 100.0302
Kirkland LakeWind2090RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2090 | 75.9526 | 81.7556 | 87.8576 | 93.9708 | 100.0792
Kirkland LakeWind2095RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2095 | 75.9526 | 81.7556 | 87.8576 | 93.9708 | 100.0792
Kirkland LakeWind2100RCP8.5 | Kirkland Lake | Wind | RCP8.5 | 2100 | 75.9526 | 81.7556 | 87.8576 | 93.9708 | 100.0792
KitchenerIce Accretion2023RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
KitchenerIce Accretion2025RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2025 | 17.3208 | 20.7984 | 25.1958 | 28.5655 | 31.92
KitchenerIce Accretion2030RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2030 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
KitchenerIce Accretion2035RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2035 | 17.3788 | 20.8953 | 25.3375 | 28.7444 | 32.13
KitchenerIce Accretion2040RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2040 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
KitchenerIce Accretion2045RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2045 | 17.4367 | 20.9921 | 25.4792 | 28.9233 | 32.34
KitchenerIce Accretion2050RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2050 | 17.4101 | 20.9907 | 25.51 | 28.9788 | 32.4198
KitchenerIce Accretion2055RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2055 | 17.3544 | 20.9409 | 25.47 | 28.9449 | 32.3946
KitchenerIce Accretion2060RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2060 | 17.2987 | 20.8911 | 25.43 | 28.911 | 32.3694
KitchenerIce Accretion2065RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2065 | 17.2431 | 20.8413 | 25.39 | 28.8771 | 32.3442
KitchenerIce Accretion2070RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2070 | 17.1874 | 20.7915 | 25.35 | 28.8432 | 32.319
KitchenerIce Accretion2075RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2075 | 17.1555 | 20.7846 | 25.3708 | 28.8809 | 32.3768
KitchenerIce Accretion2080RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2080 | 17.1236 | 20.7777 | 25.3917 | 28.9186 | 32.4345
KitchenerIce Accretion2085RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2085 | 17.0917 | 20.7707 | 25.4125 | 28.9562 | 32.4922
KitchenerIce Accretion2090RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2090 | 17.0598 | 20.7638 | 25.4333 | 28.9939 | 32.55
KitchenerIce Accretion2095RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2095 | 17.0279 | 20.7569 | 25.4542 | 29.0316 | 32.6077
KitchenerIce Accretion2100RCP4.5 | Kitchener | Ice Accretion | RCP4.5 | 2100 | 16.996 | 20.75 | 25.475 | 29.0692 | 32.6655
KitchenerIce Accretion2023RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
KitchenerIce Accretion2025RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2025 | 17.3208 | 20.7984 | 25.1958 | 28.5655 | 31.92
KitchenerIce Accretion2030RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2030 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
KitchenerIce Accretion2035RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2035 | 17.3788 | 20.8953 | 25.3375 | 28.7444 | 32.13
KitchenerIce Accretion2040RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2040 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
KitchenerIce Accretion2045RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2045 | 17.4367 | 20.9921 | 25.4792 | 28.9233 | 32.34
KitchenerIce Accretion2050RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2050 | 17.4101 | 20.9907 | 25.51 | 28.9788 | 32.4198
KitchenerIce Accretion2055RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2055 | 17.3544 | 20.9409 | 25.47 | 28.9449 | 32.3946
KitchenerIce Accretion2060RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2060 | 17.2987 | 20.8911 | 25.43 | 28.911 | 32.3694
KitchenerIce Accretion2065RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2065 | 17.2431 | 20.8413 | 25.39 | 28.8771 | 32.3442
KitchenerIce Accretion2070RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2070 | 17.1874 | 20.7915 | 25.35 | 28.8432 | 32.319
KitchenerIce Accretion2075RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2075 | 17.1396 | 20.7811 | 25.3813 | 28.8997 | 32.4056
KitchenerIce Accretion2080RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2080 | 17.0917 | 20.7707 | 25.4125 | 28.9562 | 32.4922
KitchenerIce Accretion2085RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2085 | 17.0439 | 20.7604 | 25.4437 | 29.0127 | 32.5789
KitchenerIce Accretion2090RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2090 | 16.6887 | 20.4249 | 25.1333 | 28.7114 | 32.298
KitchenerIce Accretion2095RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2095 | 16.3814 | 20.0998 | 24.7917 | 28.3536 | 31.9305
KitchenerIce Accretion2100RCP6.0 | Kitchener | Ice Accretion | RCP6.0 | 2100 | 16.074 | 19.7747 | 24.45 | 27.9957 | 31.563
KitchenerIce Accretion2023RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
KitchenerIce Accretion2025RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2025 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
KitchenerIce Accretion2030RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2030 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
KitchenerIce Accretion2035RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2035 | 17.4657 | 21.0405 | 25.55 | 29.0127 | 32.445
KitchenerIce Accretion2040RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2040 | 17.373 | 20.9575 | 25.4833 | 28.9562 | 32.403
KitchenerIce Accretion2045RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2045 | 17.2802 | 20.8745 | 25.4167 | 28.8997 | 32.361
KitchenerIce Accretion2050RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2050 | 17.1236 | 20.7777 | 25.3917 | 28.9186 | 32.4345
KitchenerIce Accretion2055RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2055 | 17.0598 | 20.7638 | 25.4333 | 28.9939 | 32.55
KitchenerIce Accretion2060RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2060 | 16.6887 | 20.4249 | 25.1333 | 28.7114 | 32.298
KitchenerIce Accretion2065RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2065 | 16.3814 | 20.0998 | 24.7917 | 28.3536 | 31.9305
KitchenerIce Accretion2070RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2070 | 15.6507 | 19.3182 | 23.95 | 27.4684 | 30.9855
KitchenerIce Accretion2075RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2075 | 15.2274 | 18.8617 | 23.45 | 26.9411 | 30.408
KitchenerIce Accretion2080RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2080 | 14.8041 | 18.4052 | 22.95 | 26.4137 | 29.8305
KitchenerIce Accretion2085RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2085 | 13.9778 | 17.43 | 21.7875 | 25.086 | 28.3657
KitchenerIce Accretion2090RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2090 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
KitchenerIce Accretion2095RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2095 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
KitchenerIce Accretion2100RCP8.5 | Kitchener | Ice Accretion | RCP8.5 | 2100 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
KitchenerWind2023RCP4.5 | Kitchener | Wind | RCP4.5 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
KitchenerWind2025RCP4.5 | Kitchener | Wind | RCP4.5 | 2025 | 81.5488 | 87.8469 | 94.481 | 101.1097 | 107.7494
KitchenerWind2030RCP4.5 | Kitchener | Wind | RCP4.5 | 2030 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
KitchenerWind2035RCP4.5 | Kitchener | Wind | RCP4.5 | 2035 | 81.6625 | 88.0013 | 94.6909 | 101.3645 | 108.0494
KitchenerWind2040RCP4.5 | Kitchener | Wind | RCP4.5 | 2040 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
KitchenerWind2045RCP4.5 | Kitchener | Wind | RCP4.5 | 2045 | 81.7761 | 88.1558 | 94.9008 | 101.6193 | 108.3495
KitchenerWind2050RCP4.5 | Kitchener | Wind | RCP4.5 | 2050 | 81.8962 | 88.3099 | 95.096 | 101.8513 | 108.6174
KitchenerWind2055RCP4.5 | Kitchener | Wind | RCP4.5 | 2055 | 81.9595 | 88.3869 | 95.1863 | 101.9559 | 108.7353
KitchenerWind2060RCP4.5 | Kitchener | Wind | RCP4.5 | 2060 | 82.0229 | 88.4638 | 95.2765 | 102.0605 | 108.8531
KitchenerWind2065RCP4.5 | Kitchener | Wind | RCP4.5 | 2065 | 82.0862 | 88.5407 | 95.3668 | 102.1651 | 108.971
KitchenerWind2070RCP4.5 | Kitchener | Wind | RCP4.5 | 2070 | 82.1495 | 88.6177 | 95.457 | 102.2697 | 109.0889
KitchenerWind2075RCP4.5 | Kitchener | Wind | RCP4.5 | 2075 | 82.2185 | 88.7167 | 95.598 | 102.4424 | 109.2961
KitchenerWind2080RCP4.5 | Kitchener | Wind | RCP4.5 | 2080 | 82.2875 | 88.8158 | 95.739 | 102.6151 | 109.5032
KitchenerWind2085RCP4.5 | Kitchener | Wind | RCP4.5 | 2085 | 82.3564 | 88.9149 | 95.88 | 102.7877 | 109.7104
KitchenerWind2090RCP4.5 | Kitchener | Wind | RCP4.5 | 2090 | 82.4254 | 89.014 | 96.021 | 102.9604 | 109.9176
KitchenerWind2095RCP4.5 | Kitchener | Wind | RCP4.5 | 2095 | 82.4944 | 89.113 | 96.162 | 103.1331 | 110.1248
KitchenerWind2100RCP4.5 | Kitchener | Wind | RCP4.5 | 2100 | 82.5634 | 89.2121 | 96.303 | 103.3057 | 110.3319
KitchenerWind2023RCP6.0 | Kitchener | Wind | RCP6.0 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
KitchenerWind2025RCP6.0 | Kitchener | Wind | RCP6.0 | 2025 | 81.5488 | 87.8469 | 94.481 | 101.1097 | 107.7494
KitchenerWind2030RCP6.0 | Kitchener | Wind | RCP6.0 | 2030 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
KitchenerWind2035RCP6.0 | Kitchener | Wind | RCP6.0 | 2035 | 81.6625 | 88.0013 | 94.6909 | 101.3645 | 108.0494
KitchenerWind2040RCP6.0 | Kitchener | Wind | RCP6.0 | 2040 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
KitchenerWind2045RCP6.0 | Kitchener | Wind | RCP6.0 | 2045 | 81.7761 | 88.1558 | 94.9008 | 101.6193 | 108.3495
KitchenerWind2050RCP6.0 | Kitchener | Wind | RCP6.0 | 2050 | 81.8962 | 88.3099 | 95.096 | 101.8513 | 108.6174
KitchenerWind2055RCP6.0 | Kitchener | Wind | RCP6.0 | 2055 | 81.9595 | 88.3869 | 95.1863 | 101.9559 | 108.7353
KitchenerWind2060RCP6.0 | Kitchener | Wind | RCP6.0 | 2060 | 82.0229 | 88.4638 | 95.2765 | 102.0605 | 108.8531
KitchenerWind2065RCP6.0 | Kitchener | Wind | RCP6.0 | 2065 | 82.0862 | 88.5407 | 95.3668 | 102.1651 | 108.971
KitchenerWind2070RCP6.0 | Kitchener | Wind | RCP6.0 | 2070 | 82.1495 | 88.6177 | 95.457 | 102.2697 | 109.0889
KitchenerWind2075RCP6.0 | Kitchener | Wind | RCP6.0 | 2075 | 82.253 | 88.7663 | 95.6685 | 102.5287 | 109.3996
KitchenerWind2080RCP6.0 | Kitchener | Wind | RCP6.0 | 2080 | 82.3564 | 88.9149 | 95.88 | 102.7877 | 109.7104
KitchenerWind2085RCP6.0 | Kitchener | Wind | RCP6.0 | 2085 | 82.4599 | 89.0635 | 96.0915 | 103.0467 | 110.0212
KitchenerWind2090RCP6.0 | Kitchener | Wind | RCP6.0 | 2090 | 82.8421 | 89.5618 | 96.7385 | 103.8187 | 110.9213
KitchenerWind2095RCP6.0 | Kitchener | Wind | RCP6.0 | 2095 | 83.1208 | 89.9115 | 97.1741 | 104.3316 | 111.5107
KitchenerWind2100RCP6.0 | Kitchener | Wind | RCP6.0 | 2100 | 83.3995 | 90.2612 | 97.6096 | 104.8446 | 112.1001
KitchenerWind2023RCP8.5 | Kitchener | Wind | RCP8.5 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
KitchenerWind2025RCP8.5 | Kitchener | Wind | RCP8.5 | 2025 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
KitchenerWind2030RCP8.5 | Kitchener | Wind | RCP8.5 | 2030 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
KitchenerWind2035RCP8.5 | Kitchener | Wind | RCP8.5 | 2035 | 81.8329 | 88.233 | 95.0058 | 101.7467 | 108.4995
KitchenerWind2040RCP8.5 | Kitchener | Wind | RCP8.5 | 2040 | 81.9384 | 88.3612 | 95.1562 | 101.9211 | 108.696
KitchenerWind2045RCP8.5 | Kitchener | Wind | RCP8.5 | 2045 | 82.044 | 88.4894 | 95.3066 | 102.0954 | 108.8924
KitchenerWind2050RCP8.5 | Kitchener | Wind | RCP8.5 | 2050 | 82.2875 | 88.8158 | 95.739 | 102.6151 | 109.5032
KitchenerWind2055RCP8.5 | Kitchener | Wind | RCP8.5 | 2055 | 82.4254 | 89.014 | 96.021 | 102.9604 | 109.9176
KitchenerWind2060RCP8.5 | Kitchener | Wind | RCP8.5 | 2060 | 82.8421 | 89.5618 | 96.7385 | 103.8187 | 110.9213
KitchenerWind2065RCP8.5 | Kitchener | Wind | RCP8.5 | 2065 | 83.1208 | 89.9115 | 97.1741 | 104.3316 | 111.5107
KitchenerWind2070RCP8.5 | Kitchener | Wind | RCP8.5 | 2070 | 83.6457 | 90.5933 | 98.0451 | 105.371 | 112.718
KitchenerWind2075RCP8.5 | Kitchener | Wind | RCP8.5 | 2075 | 83.8919 | 90.9255 | 98.4807 | 105.8973 | 113.336
KitchenerWind2080RCP8.5 | Kitchener | Wind | RCP8.5 | 2080 | 84.1381 | 91.2577 | 98.9162 | 106.4237 | 113.9539
KitchenerWind2085RCP8.5 | Kitchener | Wind | RCP8.5 | 2085 | 84.3775 | 91.5768 | 99.3392 | 106.9266 | 114.5433
KitchenerWind2090RCP8.5 | Kitchener | Wind | RCP8.5 | 2090 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
KitchenerWind2095RCP8.5 | Kitchener | Wind | RCP8.5 | 2095 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
KitchenerWind2100RCP8.5 | Kitchener | Wind | RCP8.5 | 2100 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
KitchenuhmaykoosibIce Accretion2023RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2023 | 12.8634 | 15.3583 | 18.504 | 20.9299 | 23.3377
KitchenuhmaykoosibIce Accretion2025RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2025 | 13.0116 | 15.5326 | 18.714 | 21.1672 | 23.6023
KitchenuhmaykoosibIce Accretion2030RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2030 | 13.1598 | 15.7069 | 18.924 | 21.4045 | 23.8669
KitchenuhmaykoosibIce Accretion2035RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2035 | 13.3081 | 15.8812 | 19.134 | 21.6418 | 24.1315
KitchenuhmaykoosibIce Accretion2040RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2040 | 13.4563 | 16.0555 | 19.344 | 21.8791 | 24.3961
KitchenuhmaykoosibIce Accretion2045RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2045 | 13.6045 | 16.2298 | 19.554 | 22.1164 | 24.6607
KitchenuhmaykoosibIce Accretion2050RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2050 | 13.7402 | 16.3772 | 19.7208 | 22.2967 | 24.8573
KitchenuhmaykoosibIce Accretion2055RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2055 | 13.7277 | 16.3503 | 19.6776 | 22.2398 | 24.7892
KitchenuhmaykoosibIce Accretion2060RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2060 | 13.7151 | 16.3234 | 19.6344 | 22.1828 | 24.7212
KitchenuhmaykoosibIce Accretion2065RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2065 | 13.7026 | 16.2966 | 19.5912 | 22.1259 | 24.6532
KitchenuhmaykoosibIce Accretion2070RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2070 | 13.6901 | 16.2697 | 19.548 | 22.0689 | 24.5851
KitchenuhmaykoosibIce Accretion2075RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2075 | 13.7318 | 16.3294 | 19.626 | 22.1604 | 24.691
KitchenuhmaykoosibIce Accretion2080RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2080 | 13.7736 | 16.3892 | 19.704 | 22.252 | 24.7968
KitchenuhmaykoosibIce Accretion2085RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2085 | 13.8153 | 16.4489 | 19.782 | 22.3435 | 24.9026
KitchenuhmaykoosibIce Accretion2090RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2090 | 13.8571 | 16.5087 | 19.86 | 22.435 | 25.0085
KitchenuhmaykoosibIce Accretion2095RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2095 | 13.8988 | 16.5685 | 19.938 | 22.5266 | 25.1143
KitchenuhmaykoosibIce Accretion2100RCP4.5 | Kitchenuhmaykoosib | Ice Accretion | RCP4.5 | 2100 | 13.9406 | 16.6282 | 20.016 | 22.6181 | 25.2202
KitchenuhmaykoosibIce Accretion2023RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2023 | 12.8634 | 15.3583 | 18.504 | 20.9299 | 23.3377
KitchenuhmaykoosibIce Accretion2025RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2025 | 13.0116 | 15.5326 | 18.714 | 21.1672 | 23.6023
KitchenuhmaykoosibIce Accretion2030RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2030 | 13.1598 | 15.7069 | 18.924 | 21.4045 | 23.8669
KitchenuhmaykoosibIce Accretion2035RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2035 | 13.3081 | 15.8812 | 19.134 | 21.6418 | 24.1315
KitchenuhmaykoosibIce Accretion2040RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2040 | 13.4563 | 16.0555 | 19.344 | 21.8791 | 24.3961
KitchenuhmaykoosibIce Accretion2045RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2045 | 13.6045 | 16.2298 | 19.554 | 22.1164 | 24.6607
KitchenuhmaykoosibIce Accretion2050RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2050 | 13.7402 | 16.3772 | 19.7208 | 22.2967 | 24.8573
KitchenuhmaykoosibIce Accretion2055RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2055 | 13.7277 | 16.3503 | 19.6776 | 22.2398 | 24.7892
KitchenuhmaykoosibIce Accretion2060RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2060 | 13.7151 | 16.3234 | 19.6344 | 22.1828 | 24.7212
KitchenuhmaykoosibIce Accretion2065RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2065 | 13.7026 | 16.2966 | 19.5912 | 22.1259 | 24.6532
KitchenuhmaykoosibIce Accretion2070RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2070 | 13.6901 | 16.2697 | 19.548 | 22.0689 | 24.5851
KitchenuhmaykoosibIce Accretion2075RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2075 | 13.7527 | 16.3593 | 19.665 | 22.2062 | 24.7439
KitchenuhmaykoosibIce Accretion2080RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2080 | 13.8153 | 16.4489 | 19.782 | 22.3435 | 24.9026
KitchenuhmaykoosibIce Accretion2085RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2085 | 13.878 | 16.5386 | 19.899 | 22.4808 | 25.0614
KitchenuhmaykoosibIce Accretion2090RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2090 | 13.8153 | 16.4539 | 19.782 | 22.3401 | 24.8951
KitchenuhmaykoosibIce Accretion2095RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2095 | 13.6901 | 16.2796 | 19.548 | 22.0621 | 24.57
KitchenuhmaykoosibIce Accretion2100RCP6.0 | Kitchenuhmaykoosib | Ice Accretion | RCP6.0 | 2100 | 13.5648 | 16.1053 | 19.314 | 21.7841 | 24.2449
KitchenuhmaykoosibIce Accretion2023RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2023 | 12.8634 | 15.3583 | 18.504 | 20.9299 | 23.3377
KitchenuhmaykoosibIce Accretion2025RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2025 | 13.1598 | 15.7069 | 18.924 | 21.4045 | 23.8669
KitchenuhmaykoosibIce Accretion2030RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2030 | 13.4563 | 16.0555 | 19.344 | 21.8791 | 24.3961
KitchenuhmaykoosibIce Accretion2035RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2035 | 13.7527 | 16.4041 | 19.764 | 22.3537 | 24.9253
KitchenuhmaykoosibIce Accretion2040RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2040 | 13.7318 | 16.3593 | 19.692 | 22.2587 | 24.8119
KitchenuhmaykoosibIce Accretion2045RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2045 | 13.711 | 16.3145 | 19.62 | 22.1638 | 24.6985
KitchenuhmaykoosibIce Accretion2050RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2050 | 13.7736 | 16.3892 | 19.704 | 22.252 | 24.7968
KitchenuhmaykoosibIce Accretion2055RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2055 | 13.8571 | 16.5087 | 19.86 | 22.435 | 25.0085
KitchenuhmaykoosibIce Accretion2060RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2060 | 13.8153 | 16.4539 | 19.782 | 22.3401 | 24.8951
KitchenuhmaykoosibIce Accretion2065RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2065 | 13.6901 | 16.2796 | 19.548 | 22.0621 | 24.57
KitchenuhmaykoosibIce Accretion2070RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2070 | 13.5272 | 16.0705 | 19.29 | 21.7638 | 24.2298
KitchenuhmaykoosibIce Accretion2075RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2075 | 13.4897 | 16.0356 | 19.266 | 21.7435 | 24.2147
KitchenuhmaykoosibIce Accretion2080RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2080 | 13.4521 | 16.0007 | 19.242 | 21.7231 | 24.1996
KitchenuhmaykoosibIce Accretion2085RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2085 | 13.5147 | 16.068 | 19.314 | 21.8045 | 24.2903
KitchenuhmaykoosibIce Accretion2090RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2090 | 13.5773 | 16.1352 | 19.386 | 21.8858 | 24.381
KitchenuhmaykoosibIce Accretion2095RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2095 | 13.5773 | 16.1352 | 19.386 | 21.8858 | 24.381
KitchenuhmaykoosibIce Accretion2100RCP8.5 | Kitchenuhmaykoosib | Ice Accretion | RCP8.5 | 2100 | 13.5773 | 16.1352 | 19.386 | 21.8858 | 24.381
KitchenuhmaykoosibWind2023RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2023 | 80.0839 | 86.2787 | 92.8096 | 99.3358 | 105.8554
KitchenuhmaykoosibWind2025RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2025 | 80.1673 | 86.3814 | 92.9353 | 99.4818 | 106.0232
KitchenuhmaykoosibWind2030RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2030 | 80.2507 | 86.484 | 93.0611 | 99.6278 | 106.191
KitchenuhmaykoosibWind2035RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2035 | 80.3341 | 86.5867 | 93.1868 | 99.7739 | 106.3588
KitchenuhmaykoosibWind2040RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2040 | 80.4175 | 86.6894 | 93.3125 | 99.9199 | 106.5266
KitchenuhmaykoosibWind2045RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2045 | 80.5009 | 86.7921 | 93.4383 | 100.0659 | 106.6944
KitchenuhmaykoosibWind2050RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2050 | 80.7527 | 87.0932 | 93.7977 | 100.4757 | 107.1559
KitchenuhmaykoosibWind2055RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2055 | 80.9212 | 87.2917 | 94.0314 | 100.7396 | 107.4496
KitchenuhmaykoosibWind2060RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2060 | 81.0896 | 87.4902 | 94.265 | 101.0034 | 107.7432
KitchenuhmaykoosibWind2065RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2065 | 81.258 | 87.6887 | 94.4987 | 101.2672 | 108.0369
KitchenuhmaykoosibWind2070RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2070 | 81.4264 | 87.8872 | 94.7324 | 101.531 | 108.3306
KitchenuhmaykoosibWind2075RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2075 | 81.4198 | 87.8587 | 94.6757 | 101.4506 | 108.2274
KitchenuhmaykoosibWind2080RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2080 | 81.4132 | 87.8302 | 94.6189 | 101.3702 | 108.1243
KitchenuhmaykoosibWind2085RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2085 | 81.4065 | 87.8017 | 94.5622 | 101.2898 | 108.0212
KitchenuhmaykoosibWind2090RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2090 | 81.3999 | 87.7732 | 94.5055 | 101.2094 | 107.918
KitchenuhmaykoosibWind2095RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2095 | 81.3933 | 87.7446 | 94.4487 | 101.1291 | 107.8149
KitchenuhmaykoosibWind2100RCP4.5 | Kitchenuhmaykoosib | Wind | RCP4.5 | 2100 | 81.3867 | 87.7161 | 94.392 | 101.0487 | 107.7118
KitchenuhmaykoosibWind2023RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2023 | 80.0839 | 86.2787 | 92.8096 | 99.3358 | 105.8554
KitchenuhmaykoosibWind2025RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2025 | 80.1673 | 86.3814 | 92.9353 | 99.4818 | 106.0232
KitchenuhmaykoosibWind2030RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2030 | 80.2507 | 86.484 | 93.0611 | 99.6278 | 106.191
KitchenuhmaykoosibWind2035RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2035 | 80.3341 | 86.5867 | 93.1868 | 99.7739 | 106.3588
KitchenuhmaykoosibWind2040RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2040 | 80.4175 | 86.6894 | 93.3125 | 99.9199 | 106.5266
KitchenuhmaykoosibWind2045RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2045 | 80.5009 | 86.7921 | 93.4383 | 100.0659 | 106.6944
KitchenuhmaykoosibWind2050RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2050 | 80.7527 | 87.0932 | 93.7977 | 100.4757 | 107.1559
KitchenuhmaykoosibWind2055RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2055 | 80.9212 | 87.2917 | 94.0314 | 100.7396 | 107.4496
KitchenuhmaykoosibWind2060RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2060 | 81.0896 | 87.4902 | 94.265 | 101.0034 | 107.7432
KitchenuhmaykoosibWind2065RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2065 | 81.258 | 87.6887 | 94.4987 | 101.2672 | 108.0369
KitchenuhmaykoosibWind2070RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2070 | 81.4264 | 87.8872 | 94.7324 | 101.531 | 108.3306
KitchenuhmaykoosibWind2075RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2075 | 81.4165 | 87.8445 | 94.6473 | 101.4104 | 108.1759
KitchenuhmaykoosibWind2080RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2080 | 81.4065 | 87.8017 | 94.5622 | 101.2898 | 108.0212
KitchenuhmaykoosibWind2085RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2085 | 81.3966 | 87.7589 | 94.4771 | 101.1692 | 107.8665
KitchenuhmaykoosibWind2090RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2090 | 81.4317 | 87.7503 | 94.4073 | 101.0487 | 107.6978
KitchenuhmaykoosibWind2095RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2095 | 81.4767 | 87.7846 | 94.4227 | 101.0487 | 107.6838
KitchenuhmaykoosibWind2100RCP6.0 | Kitchenuhmaykoosib | Wind | RCP6.0 | 2100 | 81.5217 | 87.8188 | 94.438 | 101.0487 | 107.6698
KitchenuhmaykoosibWind2023RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2023 | 80.0839 | 86.2787 | 92.8096 | 99.3358 | 105.8554
KitchenuhmaykoosibWind2025RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2025 | 80.2507 | 86.484 | 93.0611 | 99.6278 | 106.191
KitchenuhmaykoosibWind2030RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2030 | 80.4175 | 86.6894 | 93.3125 | 99.9199 | 106.5266
KitchenuhmaykoosibWind2035RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2035 | 80.5843 | 86.8947 | 93.564 | 100.2119 | 106.8622
KitchenuhmaykoosibWind2040RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2040 | 80.865 | 87.2256 | 93.9535 | 100.6516 | 107.3517
KitchenuhmaykoosibWind2045RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2045 | 81.1457 | 87.5564 | 94.3429 | 101.0913 | 107.8411
KitchenuhmaykoosibWind2050RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2050 | 81.4132 | 87.8302 | 94.6189 | 101.3702 | 108.1243
KitchenuhmaykoosibWind2055RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2055 | 81.3999 | 87.7732 | 94.5055 | 101.2094 | 107.918
KitchenuhmaykoosibWind2060RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2060 | 81.4317 | 87.7503 | 94.4073 | 101.0487 | 107.6978
KitchenuhmaykoosibWind2065RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2065 | 81.4767 | 87.7846 | 94.4227 | 101.0487 | 107.6838
KitchenuhmaykoosibWind2070RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2070 | 81.5191 | 87.7903 | 94.3797 | 100.9666 | 107.5614
KitchenuhmaykoosibWind2075RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2075 | 81.5164 | 87.7617 | 94.3215 | 100.8846 | 107.4531
KitchenuhmaykoosibWind2080RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2080 | 81.5138 | 87.7332 | 94.2632 | 100.8026 | 107.3447
KitchenuhmaykoosibWind2085RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2085 | 81.6568 | 87.8958 | 94.4518 | 101.0142 | 107.5807
KitchenuhmaykoosibWind2090RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2090 | 81.7998 | 88.0584 | 94.6404 | 101.2259 | 107.8166
KitchenuhmaykoosibWind2095RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2095 | 81.7998 | 88.0584 | 94.6404 | 101.2259 | 107.8166
KitchenuhmaykoosibWind2100RCP8.5 | Kitchenuhmaykoosib | Wind | RCP8.5 | 2100 | 81.7998 | 88.0584 | 94.6404 | 101.2259 | 107.8166
LakefieldIce Accretion2023RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2023 | 17.1526 | 20.4387 | 24.625 | 27.8262 | 30.996
LakefieldIce Accretion2025RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2025 | 17.1468 | 20.4422 | 24.6333 | 27.8404 | 31.017
LakefieldIce Accretion2030RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2030 | 17.141 | 20.4457 | 24.6417 | 27.8545 | 31.038
LakefieldIce Accretion2035RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2035 | 17.1352 | 20.4491 | 24.65 | 27.8686 | 31.059
LakefieldIce Accretion2040RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2040 | 17.1294 | 20.4526 | 24.6583 | 27.8827 | 31.08
LakefieldIce Accretion2045RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2045 | 17.1236 | 20.456 | 24.6667 | 27.8969 | 31.101
LakefieldIce Accretion2050RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2050 | 17.0795 | 20.4305 | 24.66 | 27.9053 | 31.1283
LakefieldIce Accretion2055RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2055 | 17.0413 | 20.4014 | 24.645 | 27.8997 | 31.1346
LakefieldIce Accretion2060RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2060 | 17.003 | 20.3724 | 24.63 | 27.894 | 31.1409
LakefieldIce Accretion2065RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2065 | 16.9647 | 20.3433 | 24.615 | 27.8884 | 31.1472
LakefieldIce Accretion2070RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2070 | 16.9265 | 20.3143 | 24.6 | 27.8827 | 31.1535
LakefieldIce Accretion2075RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2075 | 16.996 | 20.418 | 24.7417 | 28.0522 | 31.353
LakefieldIce Accretion2080RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2080 | 17.0656 | 20.5218 | 24.8833 | 28.2217 | 31.5525
LakefieldIce Accretion2085RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2085 | 17.1352 | 20.6255 | 25.025 | 28.3912 | 31.752
LakefieldIce Accretion2090RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2090 | 17.2048 | 20.7292 | 25.1667 | 28.5607 | 31.9515
LakefieldIce Accretion2095RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2095 | 17.2744 | 20.833 | 25.3083 | 28.7302 | 32.151
LakefieldIce Accretion2100RCP4.5 | Lakefield | Ice Accretion | RCP4.5 | 2100 | 17.344 | 20.9367 | 25.45 | 28.8997 | 32.3505
LakefieldIce Accretion2023RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2023 | 17.1526 | 20.4387 | 24.625 | 27.8262 | 30.996
LakefieldIce Accretion2025RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2025 | 17.1468 | 20.4422 | 24.6333 | 27.8404 | 31.017
LakefieldIce Accretion2030RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2030 | 17.141 | 20.4457 | 24.6417 | 27.8545 | 31.038
LakefieldIce Accretion2035RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2035 | 17.1352 | 20.4491 | 24.65 | 27.8686 | 31.059
LakefieldIce Accretion2040RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2040 | 17.1294 | 20.4526 | 24.6583 | 27.8827 | 31.08
LakefieldIce Accretion2045RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2045 | 17.1236 | 20.456 | 24.6667 | 27.8969 | 31.101
LakefieldIce Accretion2050RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2050 | 17.0795 | 20.4305 | 24.66 | 27.9053 | 31.1283
LakefieldIce Accretion2055RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2055 | 17.0413 | 20.4014 | 24.645 | 27.8997 | 31.1346
LakefieldIce Accretion2060RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2060 | 17.003 | 20.3724 | 24.63 | 27.894 | 31.1409
LakefieldIce Accretion2065RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2065 | 16.9647 | 20.3433 | 24.615 | 27.8884 | 31.1472
LakefieldIce Accretion2070RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2070 | 16.9265 | 20.3143 | 24.6 | 27.8827 | 31.1535
LakefieldIce Accretion2075RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2075 | 17.0308 | 20.4699 | 24.8125 | 28.137 | 31.4528
LakefieldIce Accretion2080RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2080 | 17.1352 | 20.6255 | 25.025 | 28.3912 | 31.752
LakefieldIce Accretion2085RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2085 | 17.2396 | 20.7811 | 25.2375 | 28.6455 | 32.0512
LakefieldIce Accretion2090RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2090 | 17.2048 | 20.8122 | 25.35 | 28.815 | 32.277
LakefieldIce Accretion2095RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2095 | 17.0656 | 20.6877 | 25.25 | 28.7302 | 32.2035
LakefieldIce Accretion2100RCP6.0 | Lakefield | Ice Accretion | RCP6.0 | 2100 | 16.9265 | 20.5633 | 25.15 | 28.6455 | 32.13
LakefieldIce Accretion2023RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2023 | 17.1526 | 20.4387 | 24.625 | 27.8262 | 30.996
LakefieldIce Accretion2025RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2025 | 17.141 | 20.4457 | 24.6417 | 27.8545 | 31.038
LakefieldIce Accretion2030RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2030 | 17.1294 | 20.4526 | 24.6583 | 27.8827 | 31.08
LakefieldIce Accretion2035RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2035 | 17.1178 | 20.4595 | 24.675 | 27.911 | 31.122
LakefieldIce Accretion2040RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2040 | 17.054 | 20.4111 | 24.65 | 27.9016 | 31.1325
LakefieldIce Accretion2045RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2045 | 16.9902 | 20.3627 | 24.625 | 27.8922 | 31.143
LakefieldIce Accretion2050RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2050 | 17.0656 | 20.5218 | 24.8833 | 28.2217 | 31.5525
LakefieldIce Accretion2055RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2055 | 17.2048 | 20.7292 | 25.1667 | 28.5607 | 31.9515
LakefieldIce Accretion2060RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2060 | 17.2048 | 20.8122 | 25.35 | 28.815 | 32.277
LakefieldIce Accretion2065RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2065 | 17.0656 | 20.6877 | 25.25 | 28.7302 | 32.2035
LakefieldIce Accretion2070RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2070 | 16.6887 | 20.3143 | 24.8917 | 28.3724 | 31.8465
LakefieldIce Accretion2075RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2075 | 16.451 | 20.0652 | 24.6333 | 28.0993 | 31.563
LakefieldIce Accretion2080RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2080 | 16.2132 | 19.8163 | 24.375 | 27.8262 | 31.2795
LakefieldIce Accretion2085RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2085 | 15.8131 | 19.3909 | 23.9125 | 27.346 | 30.7755
LakefieldIce Accretion2090RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2090 | 15.413 | 18.9655 | 23.45 | 26.8657 | 30.2715
LakefieldIce Accretion2095RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2095 | 15.413 | 18.9655 | 23.45 | 26.8657 | 30.2715
LakefieldIce Accretion2100RCP8.5 | Lakefield | Ice Accretion | RCP8.5 | 2100 | 15.413 | 18.9655 | 23.45 | 26.8657 | 30.2715
LakefieldWind2023RCP4.5 | Lakefield | Wind | RCP4.5 | 2023 | 74.705 | 80.5079 | 86.6364 | 92.7562 | 98.8635
LakefieldWind2025RCP4.5 | Lakefield | Wind | RCP4.5 | 2025 | 74.788 | 80.6132 | 86.7683 | 92.9111 | 99.0416
LakefieldWind2030RCP4.5 | Lakefield | Wind | RCP4.5 | 2030 | 74.8709 | 80.7185 | 86.9001 | 93.066 | 99.2197
LakefieldWind2035RCP4.5 | Lakefield | Wind | RCP4.5 | 2035 | 74.9538 | 80.8238 | 87.032 | 93.2209 | 99.3979
LakefieldWind2040RCP4.5 | Lakefield | Wind | RCP4.5 | 2040 | 75.0367 | 80.9291 | 87.1639 | 93.3758 | 99.576
LakefieldWind2045RCP4.5 | Lakefield | Wind | RCP4.5 | 2045 | 75.1197 | 81.0344 | 87.2957 | 93.5307 | 99.7541
LakefieldWind2050RCP4.5 | Lakefield | Wind | RCP4.5 | 2050 | 75.2056 | 81.1285 | 87.3966 | 93.6377 | 99.8694
LakefieldWind2055RCP4.5 | Lakefield | Wind | RCP4.5 | 2055 | 75.2085 | 81.1173 | 87.3657 | 93.5899 | 99.8067
LakefieldWind2060RCP4.5 | Lakefield | Wind | RCP4.5 | 2060 | 75.2115 | 81.1061 | 87.3347 | 93.542 | 99.7439
LakefieldWind2065RCP4.5 | Lakefield | Wind | RCP4.5 | 2065 | 75.2145 | 81.0949 | 87.3038 | 93.4942 | 99.6812
LakefieldWind2070RCP4.5 | Lakefield | Wind | RCP4.5 | 2070 | 75.2174 | 81.0837 | 87.2728 | 93.4463 | 99.6184
LakefieldWind2075RCP4.5 | Lakefield | Wind | RCP4.5 | 2075 | 75.2224 | 81.0944 | 87.2914 | 93.4708 | 99.6495
LakefieldWind2080RCP4.5 | Lakefield | Wind | RCP4.5 | 2080 | 75.2273 | 81.1051 | 87.3101 | 93.4954 | 99.6805
LakefieldWind2085RCP4.5 | Lakefield | Wind | RCP4.5 | 2085 | 75.2323 | 81.1157 | 87.3287 | 93.5199 | 99.7116
LakefieldWind2090RCP4.5 | Lakefield | Wind | RCP4.5 | 2090 | 75.2372 | 81.1264 | 87.3473 | 93.5445 | 99.7426
LakefieldWind2095RCP4.5 | Lakefield | Wind | RCP4.5 | 2095 | 75.2422 | 81.137 | 87.366 | 93.569 | 99.7737
LakefieldWind2100RCP4.5 | Lakefield | Wind | RCP4.5 | 2100 | 75.2471 | 81.1477 | 87.3846 | 93.5935 | 99.8047
LakefieldWind2023RCP6.0 | Lakefield | Wind | RCP6.0 | 2023 | 74.705 | 80.5079 | 86.6364 | 92.7562 | 98.8635
LakefieldWind2025RCP6.0 | Lakefield | Wind | RCP6.0 | 2025 | 74.788 | 80.6132 | 86.7683 | 92.9111 | 99.0416
LakefieldWind2030RCP6.0 | Lakefield | Wind | RCP6.0 | 2030 | 74.8709 | 80.7185 | 86.9001 | 93.066 | 99.2197
LakefieldWind2035RCP6.0 | Lakefield | Wind | RCP6.0 | 2035 | 74.9538 | 80.8238 | 87.032 | 93.2209 | 99.3979
LakefieldWind2040RCP6.0 | Lakefield | Wind | RCP6.0 | 2040 | 75.0367 | 80.9291 | 87.1639 | 93.3758 | 99.576
LakefieldWind2045RCP6.0 | Lakefield | Wind | RCP6.0 | 2045 | 75.1197 | 81.0344 | 87.2957 | 93.5307 | 99.7541
LakefieldWind2050RCP6.0 | Lakefield | Wind | RCP6.0 | 2050 | 75.2056 | 81.1285 | 87.3966 | 93.6377 | 99.8694
LakefieldWind2055RCP6.0 | Lakefield | Wind | RCP6.0 | 2055 | 75.2085 | 81.1173 | 87.3657 | 93.5899 | 99.8067
LakefieldWind2060RCP6.0 | Lakefield | Wind | RCP6.0 | 2060 | 75.2115 | 81.1061 | 87.3347 | 93.542 | 99.7439
LakefieldWind2065RCP6.0 | Lakefield | Wind | RCP6.0 | 2065 | 75.2145 | 81.0949 | 87.3038 | 93.4942 | 99.6812
LakefieldWind2070RCP6.0 | Lakefield | Wind | RCP6.0 | 2070 | 75.2174 | 81.0837 | 87.2728 | 93.4463 | 99.6184
LakefieldWind2075RCP6.0 | Lakefield | Wind | RCP6.0 | 2075 | 75.2249 | 81.0997 | 87.3007 | 93.4831 | 99.665
LakefieldWind2080RCP6.0 | Lakefield | Wind | RCP6.0 | 2080 | 75.2323 | 81.1157 | 87.3287 | 93.5199 | 99.7116
LakefieldWind2085RCP6.0 | Lakefield | Wind | RCP6.0 | 2085 | 75.2397 | 81.1317 | 87.3567 | 93.5567 | 99.7582
LakefieldWind2090RCP6.0 | Lakefield | Wind | RCP6.0 | 2090 | 75.3412 | 81.2543 | 87.505 | 93.7254 | 99.9485
LakefieldWind2095RCP6.0 | Lakefield | Wind | RCP6.0 | 2095 | 75.4353 | 81.361 | 87.6254 | 93.8573 | 100.0923
LakefieldWind2100RCP6.0 | Lakefield | Wind | RCP6.0 | 2100 | 75.5293 | 81.4676 | 87.7458 | 93.9892 | 100.2361
LakefieldWind2023RCP8.5 | Lakefield | Wind | RCP8.5 | 2023 | 74.705 | 80.5079 | 86.6364 | 92.7562 | 98.8635
LakefieldWind2025RCP8.5 | Lakefield | Wind | RCP8.5 | 2025 | 74.8709 | 80.7185 | 86.9001 | 93.066 | 99.2197
LakefieldWind2030RCP8.5 | Lakefield | Wind | RCP8.5 | 2030 | 75.0367 | 80.9291 | 87.1639 | 93.3758 | 99.576
LakefieldWind2035RCP8.5 | Lakefield | Wind | RCP8.5 | 2035 | 75.2026 | 81.1397 | 87.4276 | 93.6856 | 99.9322
LakefieldWind2040RCP8.5 | Lakefield | Wind | RCP8.5 | 2040 | 75.2075 | 81.121 | 87.376 | 93.6058 | 99.8276
LakefieldWind2045RCP8.5 | Lakefield | Wind | RCP8.5 | 2045 | 75.2125 | 81.1024 | 87.3244 | 93.5261 | 99.723
LakefieldWind2050RCP8.5 | Lakefield | Wind | RCP8.5 | 2050 | 75.2273 | 81.1051 | 87.3101 | 93.4954 | 99.6805
LakefieldWind2055RCP8.5 | Lakefield | Wind | RCP8.5 | 2055 | 75.2372 | 81.1264 | 87.3473 | 93.5445 | 99.7426
LakefieldWind2060RCP8.5 | Lakefield | Wind | RCP8.5 | 2060 | 75.3412 | 81.2543 | 87.505 | 93.7254 | 99.9485
LakefieldWind2065RCP8.5 | Lakefield | Wind | RCP8.5 | 2065 | 75.4353 | 81.361 | 87.6254 | 93.8573 | 100.0923
LakefieldWind2070RCP8.5 | Lakefield | Wind | RCP8.5 | 2070 | 75.6135 | 81.5769 | 87.8863 | 94.161 | 100.4354
LakefieldWind2075RCP8.5 | Lakefield | Wind | RCP8.5 | 2075 | 75.6976 | 81.6862 | 88.0267 | 94.3328 | 100.6348
LakefieldWind2080RCP8.5 | Lakefield | Wind | RCP8.5 | 2080 | 75.7818 | 81.7955 | 88.1672 | 94.5045 | 100.8341
LakefieldWind2085RCP8.5 | Lakefield | Wind | RCP8.5 | 2085 | 75.8858 | 81.9275 | 88.3349 | 94.7024 | 101.0645
LakefieldWind2090RCP8.5 | Lakefield | Wind | RCP8.5 | 2090 | 75.9897 | 82.0595 | 88.5026 | 94.9002 | 101.2949
LakefieldWind2095RCP8.5 | Lakefield | Wind | RCP8.5 | 2095 | 75.9897 | 82.0595 | 88.5026 | 94.9002 | 101.2949
LakefieldWind2100RCP8.5 | Lakefield | Wind | RCP8.5 | 2100 | 75.9897 | 82.0595 | 88.5026 | 94.9002 | 101.2949
Lansdowne HouseIce Accretion2023RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2023 | 10.3438 | 12.3255 | 14.835 | 16.7466 | 18.6732
Lansdowne HouseIce Accretion2025RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2025 | 10.4655 | 12.4666 | 15.0025 | 16.9359 | 18.8811
Lansdowne HouseIce Accretion2030RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2030 | 10.5873 | 12.6077 | 15.17 | 17.1252 | 19.089
Lansdowne HouseIce Accretion2035RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2035 | 10.7091 | 12.7488 | 15.3375 | 17.3144 | 19.2969
Lansdowne HouseIce Accretion2040RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2040 | 10.8308 | 12.8899 | 15.505 | 17.5037 | 19.5048
Lansdowne HouseIce Accretion2045RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2045 | 10.9526 | 13.031 | 15.6725 | 17.693 | 19.7127
Lansdowne HouseIce Accretion2050RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2050 | 11.0786 | 13.1696 | 15.831 | 17.8653 | 19.8979
Lansdowne HouseIce Accretion2055RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2055 | 11.0827 | 13.1671 | 15.822 | 17.8483 | 19.8752
Lansdowne HouseIce Accretion2060RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2060 | 11.0869 | 13.1646 | 15.813 | 17.8314 | 19.8526
Lansdowne HouseIce Accretion2065RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2065 | 11.0911 | 13.1621 | 15.804 | 17.8145 | 19.8299
Lansdowne HouseIce Accretion2070RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2070 | 11.0953 | 13.1596 | 15.795 | 17.7975 | 19.8072
Lansdowne HouseIce Accretion2075RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2075 | 11.1109 | 13.1804 | 15.8175 | 17.8257 | 19.8387
Lansdowne HouseIce Accretion2080RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2080 | 11.1266 | 13.2011 | 15.84 | 17.854 | 19.8702
Lansdowne HouseIce Accretion2085RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2085 | 11.1422 | 13.2219 | 15.8625 | 17.8822 | 19.9017
Lansdowne HouseIce Accretion2090RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2090 | 11.1579 | 13.2426 | 15.885 | 17.9105 | 19.9332
Lansdowne HouseIce Accretion2095RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2095 | 11.1735 | 13.2634 | 15.9075 | 17.9387 | 19.9647
Lansdowne HouseIce Accretion2100RCP4.5 | Lansdowne House | Ice Accretion | RCP4.5 | 2100 | 11.1892 | 13.2841 | 15.93 | 17.967 | 19.9962
Lansdowne HouseIce Accretion2023RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2023 | 10.3438 | 12.3255 | 14.835 | 16.7466 | 18.6732
Lansdowne HouseIce Accretion2025RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2025 | 10.4655 | 12.4666 | 15.0025 | 16.9359 | 18.8811
Lansdowne HouseIce Accretion2030RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2030 | 10.5873 | 12.6077 | 15.17 | 17.1252 | 19.089
Lansdowne HouseIce Accretion2035RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2035 | 10.7091 | 12.7488 | 15.3375 | 17.3144 | 19.2969
Lansdowne HouseIce Accretion2040RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2040 | 10.8308 | 12.8899 | 15.505 | 17.5037 | 19.5048
Lansdowne HouseIce Accretion2045RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2045 | 10.9526 | 13.031 | 15.6725 | 17.693 | 19.7127
Lansdowne HouseIce Accretion2050RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2050 | 11.0786 | 13.1696 | 15.831 | 17.8653 | 19.8979
Lansdowne HouseIce Accretion2055RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2055 | 11.0827 | 13.1671 | 15.822 | 17.8483 | 19.8752
Lansdowne HouseIce Accretion2060RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2060 | 11.0869 | 13.1646 | 15.813 | 17.8314 | 19.8526
Lansdowne HouseIce Accretion2065RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2065 | 11.0911 | 13.1621 | 15.804 | 17.8145 | 19.8299
Lansdowne HouseIce Accretion2070RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2070 | 11.0953 | 13.1596 | 15.795 | 17.7975 | 19.8072
Lansdowne HouseIce Accretion2075RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2075 | 11.1188 | 13.1908 | 15.8287 | 17.8399 | 19.8544
Lansdowne HouseIce Accretion2080RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2080 | 11.1422 | 13.2219 | 15.8625 | 17.8822 | 19.9017
Lansdowne HouseIce Accretion2085RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2085 | 11.1657 | 13.253 | 15.8963 | 17.9246 | 19.9489
Lansdowne HouseIce Accretion2090RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2090 | 11.0257 | 13.0891 | 15.695 | 17.7014 | 19.7001
Lansdowne HouseIce Accretion2095RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2095 | 10.8622 | 12.8941 | 15.46 | 17.4359 | 19.404
Lansdowne HouseIce Accretion2100RCP6.0 | Lansdowne House | Ice Accretion | RCP6.0 | 2100 | 10.6986 | 12.699 | 15.225 | 17.1703 | 19.1079
Lansdowne HouseIce Accretion2023RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2023 | 10.3438 | 12.3255 | 14.835 | 16.7466 | 18.6732
Lansdowne HouseIce Accretion2025RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2025 | 10.5873 | 12.6077 | 15.17 | 17.1252 | 19.089
Lansdowne HouseIce Accretion2030RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2030 | 10.8308 | 12.8899 | 15.505 | 17.5037 | 19.5048
Lansdowne HouseIce Accretion2035RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2035 | 11.0744 | 13.1721 | 15.84 | 17.8822 | 19.9206
Lansdowne HouseIce Accretion2040RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2040 | 11.0813 | 13.1679 | 15.825 | 17.854 | 19.8828
Lansdowne HouseIce Accretion2045RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2045 | 11.0883 | 13.1638 | 15.81 | 17.8257 | 19.845
Lansdowne HouseIce Accretion2050RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2050 | 11.1266 | 13.2011 | 15.84 | 17.854 | 19.8702
Lansdowne HouseIce Accretion2055RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2055 | 11.1579 | 13.2426 | 15.885 | 17.9105 | 19.9332
Lansdowne HouseIce Accretion2060RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2060 | 11.0257 | 13.0891 | 15.695 | 17.7014 | 19.7001
Lansdowne HouseIce Accretion2065RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2065 | 10.8622 | 12.8941 | 15.46 | 17.4359 | 19.404
Lansdowne HouseIce Accretion2070RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2070 | 10.7299 | 12.7405 | 15.28 | 17.2325 | 19.1835
Lansdowne HouseIce Accretion2075RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2075 | 10.7613 | 12.782 | 15.335 | 17.2947 | 19.2591
Lansdowne HouseIce Accretion2080RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2080 | 10.7926 | 12.8235 | 15.39 | 17.3568 | 19.3347
Lansdowne HouseIce Accretion2085RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2085 | 10.6308 | 12.6367 | 15.1725 | 17.1195 | 19.0701
Lansdowne HouseIce Accretion2090RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2090 | 10.469 | 12.45 | 14.955 | 16.8822 | 18.8055
Lansdowne HouseIce Accretion2095RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2095 | 10.469 | 12.45 | 14.955 | 16.8822 | 18.8055
Lansdowne HouseIce Accretion2100RCP8.5 | Lansdowne House | Ice Accretion | RCP8.5 | 2100 | 10.469 | 12.45 | 14.955 | 16.8822 | 18.8055
Lansdowne HouseWind2023RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2023 | 73.6089 | 79.3188 | 85.34 | 91.3593 | 97.3651
Lansdowne HouseWind2025RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2025 | 73.7018 | 79.4268 | 85.4647 | 91.4972 | 97.5202
Lansdowne HouseWind2030RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2030 | 73.7948 | 79.5348 | 85.5893 | 91.6352 | 97.6752
Lansdowne HouseWind2035RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2035 | 73.8878 | 79.6429 | 85.714 | 91.7731 | 97.8302
Lansdowne HouseWind2040RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2040 | 73.9807 | 79.7509 | 85.8387 | 91.911 | 97.9853
Lansdowne HouseWind2045RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2045 | 74.0737 | 79.8589 | 85.9633 | 92.049 | 98.1403
Lansdowne HouseWind2050RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2050 | 74.2401 | 80.046 | 86.1747 | 92.2815 | 98.3961
Lansdowne HouseWind2055RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2055 | 74.3135 | 80.1251 | 86.2614 | 92.3761 | 98.4969
Lansdowne HouseWind2060RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2060 | 74.3869 | 80.2041 | 86.3481 | 92.4707 | 98.5977
Lansdowne HouseWind2065RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2065 | 74.4602 | 80.2832 | 86.4348 | 92.5653 | 98.6985
Lansdowne HouseWind2070RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2070 | 74.5336 | 80.3622 | 86.5215 | 92.6599 | 98.7992
Lansdowne HouseWind2075RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2075 | 74.6168 | 80.4558 | 86.6263 | 92.7751 | 98.9236
Lansdowne HouseWind2080RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2080 | 74.7 | 80.5493 | 86.7312 | 92.8903 | 99.048
Lansdowne HouseWind2085RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2085 | 74.7832 | 80.6429 | 86.836 | 93.0055 | 99.1723
Lansdowne HouseWind2090RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2090 | 74.8664 | 80.7364 | 86.9408 | 93.1207 | 99.2967
Lansdowne HouseWind2095RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2095 | 74.9496 | 80.8299 | 87.0457 | 93.2359 | 99.421
Lansdowne HouseWind2100RCP4.5 | Lansdowne House | Wind | RCP4.5 | 2100 | 75.0327 | 80.9235 | 87.1505 | 93.3511 | 99.5454
Lansdowne HouseWind2023RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2023 | 73.6089 | 79.3188 | 85.34 | 91.3593 | 97.3651
Lansdowne HouseWind2025RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2025 | 73.7018 | 79.4268 | 85.4647 | 91.4972 | 97.5202
Lansdowne HouseWind2030RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2030 | 73.7948 | 79.5348 | 85.5893 | 91.6352 | 97.6752
Lansdowne HouseWind2035RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2035 | 73.8878 | 79.6429 | 85.714 | 91.7731 | 97.8302
Lansdowne HouseWind2040RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2040 | 73.9807 | 79.7509 | 85.8387 | 91.911 | 97.9853
Lansdowne HouseWind2045RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2045 | 74.0737 | 79.8589 | 85.9633 | 92.049 | 98.1403
Lansdowne HouseWind2050RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2050 | 74.2401 | 80.046 | 86.1747 | 92.2815 | 98.3961
Lansdowne HouseWind2055RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2055 | 74.3135 | 80.1251 | 86.2614 | 92.3761 | 98.4969
Lansdowne HouseWind2060RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2060 | 74.3869 | 80.2041 | 86.3481 | 92.4707 | 98.5977
Lansdowne HouseWind2065RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2065 | 74.4602 | 80.2832 | 86.4348 | 92.5653 | 98.6985
Lansdowne HouseWind2070RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2070 | 74.5336 | 80.3622 | 86.5215 | 92.6599 | 98.7992
Lansdowne HouseWind2075RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2075 | 74.6584 | 80.5025 | 86.6788 | 92.8327 | 98.9858
Lansdowne HouseWind2080RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2080 | 74.7832 | 80.6429 | 86.836 | 93.0055 | 99.1723
Lansdowne HouseWind2085RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2085 | 74.908 | 80.7832 | 86.9933 | 93.1783 | 99.3588
Lansdowne HouseWind2090RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2090 | 74.9716 | 80.8102 | 86.9692 | 93.1146 | 99.2547
Lansdowne HouseWind2095RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2095 | 74.9104 | 80.6969 | 86.7878 | 92.8781 | 98.964
Lansdowne HouseWind2100RCP6.0 | Lansdowne House | Wind | RCP6.0 | 2100 | 74.8492 | 80.5836 | 86.6065 | 92.6417 | 98.6733
Lansdowne HouseWind2023RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2023 | 73.6089 | 79.3188 | 85.34 | 91.3593 | 97.3651
Lansdowne HouseWind2025RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2025 | 73.7948 | 79.5348 | 85.5893 | 91.6352 | 97.6752
Lansdowne HouseWind2030RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2030 | 73.9807 | 79.7509 | 85.8387 | 91.911 | 97.9853
Lansdowne HouseWind2035RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2035 | 74.1667 | 79.967 | 86.088 | 92.1869 | 98.2954
Lansdowne HouseWind2040RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2040 | 74.289 | 80.0987 | 86.2325 | 92.3446 | 98.4633
Lansdowne HouseWind2045RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2045 | 74.4113 | 80.2305 | 86.377 | 92.5022 | 98.6313
Lansdowne HouseWind2050RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2050 | 74.7 | 80.5493 | 86.7312 | 92.8903 | 99.048
Lansdowne HouseWind2055RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2055 | 74.8664 | 80.7364 | 86.9408 | 93.1207 | 99.2967
Lansdowne HouseWind2060RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2060 | 74.9716 | 80.8102 | 86.9692 | 93.1146 | 99.2547
Lansdowne HouseWind2065RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2065 | 74.9104 | 80.6969 | 86.7878 | 92.8781 | 98.964
Lansdowne HouseWind2070RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2070 | 75.0548 | 80.8234 | 86.8898 | 92.963 | 99.0318
Lansdowne HouseWind2075RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2075 | 75.2603 | 81.0631 | 87.1732 | 93.2844 | 99.3903
Lansdowne HouseWind2080RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2080 | 75.4658 | 81.3029 | 87.4565 | 93.6057 | 99.7489
Lansdowne HouseWind2085RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2085 | 75.5942 | 81.4729 | 87.6732 | 93.8649 | 100.0493
Lansdowne HouseWind2090RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2090 | 75.7227 | 81.6428 | 87.89 | 94.1242 | 100.3496
Lansdowne HouseWind2095RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2095 | 75.7227 | 81.6428 | 87.89 | 94.1242 | 100.3496
Lansdowne HouseWind2100RCP8.5 | Lansdowne House | Wind | RCP8.5 | 2100 | 75.7227 | 81.6428 | 87.89 | 94.1242 | 100.3496
LeamingtonIce Accretion2023RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2023 | 18.3536 | 22.0083 | 26.628 | 30.1529 | 33.6924
LeamingtonIce Accretion2025RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2025 | 18.253 | 21.9153 | 26.5393 | 30.0685 | 33.6042
LeamingtonIce Accretion2030RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2030 | 18.1523 | 21.8224 | 26.4507 | 29.9842 | 33.516
LeamingtonIce Accretion2035RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2035 | 18.0516 | 21.7294 | 26.362 | 29.8998 | 33.4278
LeamingtonIce Accretion2040RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2040 | 17.951 | 21.6364 | 26.2733 | 29.8154 | 33.3396
LeamingtonIce Accretion2045RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2045 | 17.8503 | 21.5435 | 26.1847 | 29.7311 | 33.2514
LeamingtonIce Accretion2050RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2050 | 17.2275 | 20.8602 | 25.4184 | 28.8936 | 32.3376
LeamingtonIce Accretion2055RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2055 | 16.7053 | 20.2699 | 24.7408 | 28.1406 | 31.5121
LeamingtonIce Accretion2060RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2060 | 16.1832 | 19.6796 | 24.0632 | 27.3876 | 30.6865
LeamingtonIce Accretion2065RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2065 | 15.661 | 19.0893 | 23.3856 | 26.6346 | 29.861
LeamingtonIce Accretion2070RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2070 | 15.1388 | 18.499 | 22.708 | 25.8815 | 29.0354
LeamingtonIce Accretion2075RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2075 | 14.7849 | 18.0846 | 22.2133 | 25.3278 | 28.4239
LeamingtonIce Accretion2080RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2080 | 14.4309 | 17.6701 | 21.7187 | 24.7741 | 27.8124
LeamingtonIce Accretion2085RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2085 | 14.077 | 17.2557 | 21.224 | 24.2204 | 27.2009
LeamingtonIce Accretion2090RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2090 | 13.723 | 16.8413 | 20.7293 | 23.6667 | 26.5894
LeamingtonIce Accretion2095RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2095 | 13.3691 | 16.4268 | 20.2347 | 23.113 | 25.9778
LeamingtonIce Accretion2100RCP4.5 | Leamington | Ice Accretion | RCP4.5 | 2100 | 13.0151 | 16.0124 | 19.74 | 22.5593 | 25.3663
LeamingtonIce Accretion2023RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2023 | 18.3536 | 22.0083 | 26.628 | 30.1529 | 33.6924
LeamingtonIce Accretion2025RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2025 | 18.253 | 21.9153 | 26.5393 | 30.0685 | 33.6042
LeamingtonIce Accretion2030RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2030 | 18.1523 | 21.8224 | 26.4507 | 29.9842 | 33.516
LeamingtonIce Accretion2035RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2035 | 18.0516 | 21.7294 | 26.362 | 29.8998 | 33.4278
LeamingtonIce Accretion2040RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2040 | 17.951 | 21.6364 | 26.2733 | 29.8154 | 33.3396
LeamingtonIce Accretion2045RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2045 | 17.8503 | 21.5435 | 26.1847 | 29.7311 | 33.2514
LeamingtonIce Accretion2050RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2050 | 17.2275 | 20.8602 | 25.4184 | 28.8936 | 32.3376
LeamingtonIce Accretion2055RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2055 | 16.7053 | 20.2699 | 24.7408 | 28.1406 | 31.5121
LeamingtonIce Accretion2060RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2060 | 16.1832 | 19.6796 | 24.0632 | 27.3876 | 30.6865
LeamingtonIce Accretion2065RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2065 | 15.661 | 19.0893 | 23.3856 | 26.6346 | 29.861
LeamingtonIce Accretion2070RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2070 | 15.1388 | 18.499 | 22.708 | 25.8815 | 29.0354
LeamingtonIce Accretion2075RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2075 | 14.6079 | 17.8774 | 21.966 | 25.051 | 28.1182
LeamingtonIce Accretion2080RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2080 | 14.077 | 17.2557 | 21.224 | 24.2204 | 27.2009
LeamingtonIce Accretion2085RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2085 | 13.546 | 16.634 | 20.482 | 23.3899 | 26.2836
LeamingtonIce Accretion2090RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2090 | 11.8656 | 14.618 | 18.0413 | 20.6293 | 23.2142
LeamingtonIce Accretion2095RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2095 | 10.716 | 13.2236 | 16.3427 | 18.6992 | 21.0622
LeamingtonIce Accretion2100RCP6.0 | Leamington | Ice Accretion | RCP6.0 | 2100 | 9.5665 | 11.8292 | 14.644 | 16.7692 | 18.9101
LeamingtonIce Accretion2023RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2023 | 18.3536 | 22.0083 | 26.628 | 30.1529 | 33.6924
LeamingtonIce Accretion2025RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2025 | 18.1523 | 21.8224 | 26.4507 | 29.9842 | 33.516
LeamingtonIce Accretion2030RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2030 | 17.951 | 21.6364 | 26.2733 | 29.8154 | 33.3396
LeamingtonIce Accretion2035RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2035 | 17.7496 | 21.4505 | 26.096 | 29.6467 | 33.1632
LeamingtonIce Accretion2040RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2040 | 16.8794 | 20.4667 | 24.9667 | 28.3916 | 31.7873
LeamingtonIce Accretion2045RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2045 | 16.0091 | 19.4829 | 23.8373 | 27.1366 | 30.4114
LeamingtonIce Accretion2050RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2050 | 14.4309 | 17.6701 | 21.7187 | 24.7741 | 27.8124
LeamingtonIce Accretion2055RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2055 | 13.723 | 16.8413 | 20.7293 | 23.6667 | 26.5894
LeamingtonIce Accretion2060RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2060 | 11.8656 | 14.618 | 18.0413 | 20.6293 | 23.2142
LeamingtonIce Accretion2065RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2065 | 10.716 | 13.2236 | 16.3427 | 18.6992 | 21.0622
LeamingtonIce Accretion2070RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2070 | 9.0469 | 11.2094 | 13.888 | 15.9149 | 17.9458
LeamingtonIce Accretion2075RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2075 | 8.5274 | 10.5897 | 13.132 | 15.0606 | 16.9814
LeamingtonIce Accretion2080RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2080 | 8.0078 | 9.97 | 12.376 | 14.2064 | 16.0171
LeamingtonIce Accretion2085RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2085 | 7.2577 | 9.0636 | 11.284 | 12.9724 | 14.6412
LeamingtonIce Accretion2090RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2090 | 6.5076 | 8.1572 | 10.192 | 11.7384 | 13.2653
LeamingtonIce Accretion2095RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2095 | 6.5076 | 8.1572 | 10.192 | 11.7384 | 13.2653
LeamingtonIce Accretion2100RCP8.5 | Leamington | Ice Accretion | RCP8.5 | 2100 | 6.5076 | 8.1572 | 10.192 | 11.7384 | 13.2653
LeamingtonWind2023RCP4.5 | Leamington | Wind | RCP4.5 | 2023 | 85.0782 | 91.6686 | 98.6174 | 105.5521 | 112.4909
LeamingtonWind2025RCP4.5 | Leamington | Wind | RCP4.5 | 2025 | 85.1784 | 91.7977 | 98.7824 | 105.7461 | 112.7162
LeamingtonWind2030RCP4.5 | Leamington | Wind | RCP4.5 | 2030 | 85.2785 | 91.9268 | 98.9473 | 105.9401 | 112.9415
LeamingtonWind2035RCP4.5 | Leamington | Wind | RCP4.5 | 2035 | 85.3786 | 92.056 | 99.1123 | 106.134 | 113.1668
LeamingtonWind2040RCP4.5 | Leamington | Wind | RCP4.5 | 2040 | 85.4788 | 92.1851 | 99.2773 | 106.328 | 113.3921
LeamingtonWind2045RCP4.5 | Leamington | Wind | RCP4.5 | 2045 | 85.5789 | 92.3142 | 99.4422 | 106.522 | 113.6174
LeamingtonWind2050RCP4.5 | Leamington | Wind | RCP4.5 | 2050 | 85.7298 | 92.5071 | 99.6876 | 106.8104 | 113.9522
LeamingtonWind2055RCP4.5 | Leamington | Wind | RCP4.5 | 2055 | 85.7806 | 92.5709 | 99.7679 | 106.9048 | 114.0617
LeamingtonWind2060RCP4.5 | Leamington | Wind | RCP4.5 | 2060 | 85.8314 | 92.6347 | 99.8483 | 106.9991 | 114.1711
LeamingtonWind2065RCP4.5 | Leamington | Wind | RCP4.5 | 2065 | 85.8821 | 92.6985 | 99.9286 | 107.0935 | 114.2806
LeamingtonWind2070RCP4.5 | Leamington | Wind | RCP4.5 | 2070 | 85.9329 | 92.7623 | 100.009 | 107.1879 | 114.3901
LeamingtonWind2075RCP4.5 | Leamington | Wind | RCP4.5 | 2075 | 86.136 | 93.0296 | 100.3569 | 107.6073 | 114.878
LeamingtonWind2080RCP4.5 | Leamington | Wind | RCP4.5 | 2080 | 86.3391 | 93.297 | 100.7048 | 108.0268 | 115.3658
LeamingtonWind2085RCP4.5 | Leamington | Wind | RCP4.5 | 2085 | 86.5422 | 93.5643 | 101.0527 | 108.4462 | 115.8536
LeamingtonWind2090RCP4.5 | Leamington | Wind | RCP4.5 | 2090 | 86.7453 | 93.8317 | 101.4006 | 108.8657 | 116.3415
LeamingtonWind2095RCP4.5 | Leamington | Wind | RCP4.5 | 2095 | 86.9484 | 94.099 | 101.7485 | 109.2851 | 116.8293
LeamingtonWind2100RCP4.5 | Leamington | Wind | RCP4.5 | 2100 | 87.1515 | 94.3664 | 102.0964 | 109.7045 | 117.3172
LeamingtonWind2023RCP6.0 | Leamington | Wind | RCP6.0 | 2023 | 85.0782 | 91.6686 | 98.6174 | 105.5521 | 112.4909
LeamingtonWind2025RCP6.0 | Leamington | Wind | RCP6.0 | 2025 | 85.1784 | 91.7977 | 98.7824 | 105.7461 | 112.7162
LeamingtonWind2030RCP6.0 | Leamington | Wind | RCP6.0 | 2030 | 85.2785 | 91.9268 | 98.9473 | 105.9401 | 112.9415
LeamingtonWind2035RCP6.0 | Leamington | Wind | RCP6.0 | 2035 | 85.3786 | 92.056 | 99.1123 | 106.134 | 113.1668
LeamingtonWind2040RCP6.0 | Leamington | Wind | RCP6.0 | 2040 | 85.4788 | 92.1851 | 99.2773 | 106.328 | 113.3921
LeamingtonWind2045RCP6.0 | Leamington | Wind | RCP6.0 | 2045 | 85.5789 | 92.3142 | 99.4422 | 106.522 | 113.6174
LeamingtonWind2050RCP6.0 | Leamington | Wind | RCP6.0 | 2050 | 85.7298 | 92.5071 | 99.6876 | 106.8104 | 113.9522
LeamingtonWind2055RCP6.0 | Leamington | Wind | RCP6.0 | 2055 | 85.7806 | 92.5709 | 99.7679 | 106.9048 | 114.0617
LeamingtonWind2060RCP6.0 | Leamington | Wind | RCP6.0 | 2060 | 85.8314 | 92.6347 | 99.8483 | 106.9991 | 114.1711
LeamingtonWind2065RCP6.0 | Leamington | Wind | RCP6.0 | 2065 | 85.8821 | 92.6985 | 99.9286 | 107.0935 | 114.2806
LeamingtonWind2070RCP6.0 | Leamington | Wind | RCP6.0 | 2070 | 85.9329 | 92.7623 | 100.009 | 107.1879 | 114.3901
LeamingtonWind2075RCP6.0 | Leamington | Wind | RCP6.0 | 2075 | 86.2375 | 93.1633 | 100.5309 | 107.8171 | 115.1219
LeamingtonWind2080RCP6.0 | Leamington | Wind | RCP6.0 | 2080 | 86.5422 | 93.5643 | 101.0527 | 108.4462 | 115.8536
LeamingtonWind2085RCP6.0 | Leamington | Wind | RCP6.0 | 2085 | 86.8468 | 93.9653 | 101.5746 | 109.0754 | 116.5854
LeamingtonWind2090RCP6.0 | Leamington | Wind | RCP6.0 | 2090 | 87.5379 | 94.8433 | 102.6844 | 110.3861 | 118.0992
LeamingtonWind2095RCP6.0 | Leamington | Wind | RCP6.0 | 2095 | 87.9243 | 95.3203 | 103.2724 | 111.0677 | 118.8813
LeamingtonWind2100RCP6.0 | Leamington | Wind | RCP6.0 | 2100 | 88.3108 | 95.7973 | 103.8604 | 111.7493 | 119.6633
LeamingtonWind2023RCP8.5 | Leamington | Wind | RCP8.5 | 2023 | 85.0782 | 91.6686 | 98.6174 | 105.5521 | 112.4909
LeamingtonWind2025RCP8.5 | Leamington | Wind | RCP8.5 | 2025 | 85.2785 | 91.9268 | 98.9473 | 105.9401 | 112.9415
LeamingtonWind2030RCP8.5 | Leamington | Wind | RCP8.5 | 2030 | 85.4788 | 92.1851 | 99.2773 | 106.328 | 113.3921
LeamingtonWind2035RCP8.5 | Leamington | Wind | RCP8.5 | 2035 | 85.679 | 92.4433 | 99.6072 | 106.716 | 113.8427
LeamingtonWind2040RCP8.5 | Leamington | Wind | RCP8.5 | 2040 | 85.7637 | 92.5496 | 99.7411 | 106.8733 | 114.0252
LeamingtonWind2045RCP8.5 | Leamington | Wind | RCP8.5 | 2045 | 85.8483 | 92.656 | 99.8751 | 107.0306 | 114.2076
LeamingtonWind2050RCP8.5 | Leamington | Wind | RCP8.5 | 2050 | 86.3391 | 93.297 | 100.7048 | 108.0268 | 115.3658
LeamingtonWind2055RCP8.5 | Leamington | Wind | RCP8.5 | 2055 | 86.7453 | 93.8317 | 101.4006 | 108.8657 | 116.3415
LeamingtonWind2060RCP8.5 | Leamington | Wind | RCP8.5 | 2060 | 87.5379 | 94.8433 | 102.6844 | 110.3861 | 118.0992
LeamingtonWind2065RCP8.5 | Leamington | Wind | RCP8.5 | 2065 | 87.9243 | 95.3203 | 103.2724 | 111.0677 | 118.8813
LeamingtonWind2070RCP8.5 | Leamington | Wind | RCP8.5 | 2070 | 88.4292 | 95.937 | 104.0205 | 111.9311 | 119.8644
LeamingtonWind2075RCP8.5 | Leamington | Wind | RCP8.5 | 2075 | 88.5477 | 96.0768 | 104.1805 | 112.1128 | 120.0655
LeamingtonWind2080RCP8.5 | Leamington | Wind | RCP8.5 | 2080 | 88.6662 | 96.2165 | 104.3406 | 112.2946 | 120.2666
LeamingtonWind2085RCP8.5 | Leamington | Wind | RCP8.5 | 2085 | 89.1527 | 96.8044 | 105.0658 | 113.1335 | 121.2218
LeamingtonWind2090RCP8.5 | Leamington | Wind | RCP8.5 | 2090 | 89.6393 | 97.3922 | 105.791 | 113.9723 | 122.177
LeamingtonWind2095RCP8.5 | Leamington | Wind | RCP8.5 | 2095 | 89.6393 | 97.3922 | 105.791 | 113.9723 | 122.177
LeamingtonWind2100RCP8.5 | Leamington | Wind | RCP8.5 | 2100 | 89.6393 | 97.3922 | 105.791 | 113.9723 | 122.177
LindsayIce Accretion2023RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
LindsayIce Accretion2025RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
LindsayIce Accretion2030RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
LindsayIce Accretion2035RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
LindsayIce Accretion2040RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
LindsayIce Accretion2045RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
LindsayIce Accretion2050RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
LindsayIce Accretion2055RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
LindsayIce Accretion2060RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
LindsayIce Accretion2065RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
LindsayIce Accretion2070RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
LindsayIce Accretion2075RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2075 | 17.2744 | 20.8814 | 25.4167 | 28.8762 | 32.34
LindsayIce Accretion2080RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2080 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
LindsayIce Accretion2085RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2085 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
LindsayIce Accretion2090RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2090 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
LindsayIce Accretion2095RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2095 | 17.2048 | 20.9091 | 25.5833 | 29.121 | 32.676
LindsayIce Accretion2100RCP4.5 | Lindsay | Ice Accretion | RCP4.5 | 2100 | 17.1874 | 20.916 | 25.625 | 29.1822 | 32.76
LindsayIce Accretion2023RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
LindsayIce Accretion2025RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
LindsayIce Accretion2030RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
LindsayIce Accretion2035RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
LindsayIce Accretion2040RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
LindsayIce Accretion2045RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
LindsayIce Accretion2050RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
LindsayIce Accretion2055RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
LindsayIce Accretion2060RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
LindsayIce Accretion2065RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
LindsayIce Accretion2070RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
LindsayIce Accretion2075RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2075 | 17.2657 | 20.8849 | 25.4375 | 28.9068 | 32.382
LindsayIce Accretion2080RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2080 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
LindsayIce Accretion2085RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2085 | 17.2135 | 20.9056 | 25.5625 | 29.0904 | 32.634
LindsayIce Accretion2090RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2090 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
LindsayIce Accretion2095RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2095 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
LindsayIce Accretion2100RCP6.0 | Lindsay | Ice Accretion | RCP6.0 | 2100 | 16.2654 | 19.8992 | 24.5 | 27.9957 | 31.4685
LindsayIce Accretion2023RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
LindsayIce Accretion2025RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2025 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
LindsayIce Accretion2030RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2030 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
LindsayIce Accretion2035RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2035 | 17.6919 | 21.2272 | 25.725 | 29.154 | 32.6025
LindsayIce Accretion2040RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2040 | 17.5585 | 21.1097 | 25.6083 | 29.041 | 32.487
LindsayIce Accretion2045RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2045 | 17.4251 | 20.9921 | 25.4917 | 28.928 | 32.3715
LindsayIce Accretion2050RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2050 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
LindsayIce Accretion2055RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2055 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
LindsayIce Accretion2060RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2060 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
LindsayIce Accretion2065RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2065 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
LindsayIce Accretion2070RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2070 | 15.9987 | 19.6226 | 24.2083 | 27.685 | 31.143
LindsayIce Accretion2075RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2075 | 15.7319 | 19.3459 | 23.9167 | 27.3742 | 30.8175
LindsayIce Accretion2080RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2080 | 15.4652 | 19.0693 | 23.625 | 27.0635 | 30.492
LindsayIce Accretion2085RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2085 | 14.8911 | 18.426 | 22.8875 | 26.2584 | 29.6258
LindsayIce Accretion2090RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2090 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
LindsayIce Accretion2095RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2095 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
LindsayIce Accretion2100RCP8.5 | Lindsay | Ice Accretion | RCP8.5 | 2100 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
LindsayWind2023RCP4.5 | Lindsay | Wind | RCP4.5 | 2023 | 74.7496 | 80.5159 | 86.5762 | 92.6365 | 98.7067
LindsayWind2025RCP4.5 | Lindsay | Wind | RCP4.5 | 2025 | 74.783 | 80.5599 | 86.635 | 92.7086 | 98.79
LindsayWind2030RCP4.5 | Lindsay | Wind | RCP4.5 | 2030 | 74.8164 | 80.6038 | 86.6937 | 92.7807 | 98.8733
LindsayWind2035RCP4.5 | Lindsay | Wind | RCP4.5 | 2035 | 74.8499 | 80.6478 | 86.7525 | 92.8528 | 98.9567
LindsayWind2040RCP4.5 | Lindsay | Wind | RCP4.5 | 2040 | 74.8833 | 80.6918 | 86.8113 | 92.9249 | 99.04
LindsayWind2045RCP4.5 | Lindsay | Wind | RCP4.5 | 2045 | 74.9167 | 80.7358 | 86.87 | 92.9969 | 99.1233
LindsayWind2050RCP4.5 | Lindsay | Wind | RCP4.5 | 2050 | 75.0169 | 80.8582 | 87.02 | 93.1703 | 99.3204
LindsayWind2055RCP4.5 | Lindsay | Wind | RCP4.5 | 2055 | 75.0838 | 80.9366 | 87.1111 | 93.2715 | 99.4341
LindsayWind2060RCP4.5 | Lindsay | Wind | RCP4.5 | 2060 | 75.1506 | 81.0149 | 87.2023 | 93.3727 | 99.5479
LindsayWind2065RCP4.5 | Lindsay | Wind | RCP4.5 | 2065 | 75.2174 | 81.0933 | 87.2934 | 93.4739 | 99.6616
LindsayWind2070RCP4.5 | Lindsay | Wind | RCP4.5 | 2070 | 75.2843 | 81.1717 | 87.3846 | 93.5751 | 99.7753
LindsayWind2075RCP4.5 | Lindsay | Wind | RCP4.5 | 2075 | 75.3573 | 81.2623 | 87.4964 | 93.707 | 99.9256
LindsayWind2080RCP4.5 | Lindsay | Wind | RCP4.5 | 2080 | 75.4303 | 81.353 | 87.6082 | 93.8389 | 100.076
LindsayWind2085RCP4.5 | Lindsay | Wind | RCP4.5 | 2085 | 75.5033 | 81.4436 | 87.72 | 93.9708 | 100.2263
LindsayWind2090RCP4.5 | Lindsay | Wind | RCP4.5 | 2090 | 75.5764 | 81.5343 | 87.8318 | 94.1027 | 100.3766
LindsayWind2095RCP4.5 | Lindsay | Wind | RCP4.5 | 2095 | 75.6494 | 81.6249 | 87.9436 | 94.2346 | 100.5269
LindsayWind2100RCP4.5 | Lindsay | Wind | RCP4.5 | 2100 | 75.7224 | 81.7156 | 88.0554 | 94.3665 | 100.6773
LindsayWind2023RCP6.0 | Lindsay | Wind | RCP6.0 | 2023 | 74.7496 | 80.5159 | 86.5762 | 92.6365 | 98.7067
LindsayWind2025RCP6.0 | Lindsay | Wind | RCP6.0 | 2025 | 74.783 | 80.5599 | 86.635 | 92.7086 | 98.79
LindsayWind2030RCP6.0 | Lindsay | Wind | RCP6.0 | 2030 | 74.8164 | 80.6038 | 86.6937 | 92.7807 | 98.8733
LindsayWind2035RCP6.0 | Lindsay | Wind | RCP6.0 | 2035 | 74.8499 | 80.6478 | 86.7525 | 92.8528 | 98.9567
LindsayWind2040RCP6.0 | Lindsay | Wind | RCP6.0 | 2040 | 74.8833 | 80.6918 | 86.8113 | 92.9249 | 99.04
LindsayWind2045RCP6.0 | Lindsay | Wind | RCP6.0 | 2045 | 74.9167 | 80.7358 | 86.87 | 92.9969 | 99.1233
LindsayWind2050RCP6.0 | Lindsay | Wind | RCP6.0 | 2050 | 75.0169 | 80.8582 | 87.02 | 93.1703 | 99.3204
LindsayWind2055RCP6.0 | Lindsay | Wind | RCP6.0 | 2055 | 75.0838 | 80.9366 | 87.1111 | 93.2715 | 99.4341
LindsayWind2060RCP6.0 | Lindsay | Wind | RCP6.0 | 2060 | 75.1506 | 81.0149 | 87.2023 | 93.3727 | 99.5479
LindsayWind2065RCP6.0 | Lindsay | Wind | RCP6.0 | 2065 | 75.2174 | 81.0933 | 87.2934 | 93.4739 | 99.6616
LindsayWind2070RCP6.0 | Lindsay | Wind | RCP6.0 | 2070 | 75.2843 | 81.1717 | 87.3846 | 93.5751 | 99.7753
LindsayWind2075RCP6.0 | Lindsay | Wind | RCP6.0 | 2075 | 75.3938 | 81.3077 | 87.5523 | 93.773 | 100.0008
LindsayWind2080RCP6.0 | Lindsay | Wind | RCP6.0 | 2080 | 75.5033 | 81.4436 | 87.72 | 93.9708 | 100.2263
LindsayWind2085RCP6.0 | Lindsay | Wind | RCP6.0 | 2085 | 75.6129 | 81.5796 | 87.8877 | 94.1687 | 100.4518
LindsayWind2090RCP6.0 | Lindsay | Wind | RCP6.0 | 2090 | 75.9625 | 81.9902 | 88.3765 | 94.7223 | 101.0727
LindsayWind2095RCP6.0 | Lindsay | Wind | RCP6.0 | 2095 | 76.2026 | 82.2648 | 88.6975 | 95.0781 | 101.4681
LindsayWind2100RCP6.0 | Lindsay | Wind | RCP6.0 | 2100 | 76.4427 | 82.5394 | 89.0186 | 95.4339 | 101.8636
LindsayWind2023RCP8.5 | Lindsay | Wind | RCP8.5 | 2023 | 74.7496 | 80.5159 | 86.5762 | 92.6365 | 98.7067
LindsayWind2025RCP8.5 | Lindsay | Wind | RCP8.5 | 2025 | 74.8164 | 80.6038 | 86.6937 | 92.7807 | 98.8733
LindsayWind2030RCP8.5 | Lindsay | Wind | RCP8.5 | 2030 | 74.8833 | 80.6918 | 86.8113 | 92.9249 | 99.04
LindsayWind2035RCP8.5 | Lindsay | Wind | RCP8.5 | 2035 | 74.9501 | 80.7798 | 86.9288 | 93.069 | 99.2067
LindsayWind2040RCP8.5 | Lindsay | Wind | RCP8.5 | 2040 | 75.0615 | 80.9104 | 87.0807 | 93.2377 | 99.3962
LindsayWind2045RCP8.5 | Lindsay | Wind | RCP8.5 | 2045 | 75.1729 | 81.0411 | 87.2327 | 93.4064 | 99.5858
LindsayWind2050RCP8.5 | Lindsay | Wind | RCP8.5 | 2050 | 75.4303 | 81.353 | 87.6082 | 93.8389 | 100.076
LindsayWind2055RCP8.5 | Lindsay | Wind | RCP8.5 | 2055 | 75.5764 | 81.5343 | 87.8318 | 94.1027 | 100.3766
LindsayWind2060RCP8.5 | Lindsay | Wind | RCP8.5 | 2060 | 75.9625 | 81.9902 | 88.3765 | 94.7223 | 101.0727
LindsayWind2065RCP8.5 | Lindsay | Wind | RCP8.5 | 2065 | 76.2026 | 82.2648 | 88.6975 | 95.0781 | 101.4681
LindsayWind2070RCP8.5 | Lindsay | Wind | RCP8.5 | 2070 | 76.5269 | 82.6487 | 89.1533 | 95.5934 | 102.0498
LindsayWind2075RCP8.5 | Lindsay | Wind | RCP8.5 | 2075 | 76.611 | 82.758 | 89.2881 | 95.7529 | 102.2361
LindsayWind2080RCP8.5 | Lindsay | Wind | RCP8.5 | 2080 | 76.6952 | 82.8673 | 89.4228 | 95.9124 | 102.4224
LindsayWind2085RCP8.5 | Lindsay | Wind | RCP8.5 | 2085 | 76.892 | 83.1432 | 89.8098 | 96.3863 | 102.9861
LindsayWind2090RCP8.5 | Lindsay | Wind | RCP8.5 | 2090 | 77.0888 | 83.4191 | 90.1968 | 96.8603 | 103.5498
LindsayWind2095RCP8.5 | Lindsay | Wind | RCP8.5 | 2095 | 77.0888 | 83.4191 | 90.1968 | 96.8603 | 103.5498
LindsayWind2100RCP8.5 | Lindsay | Wind | RCP8.5 | 2100 | 77.0888 | 83.4191 | 90.1968 | 96.8603 | 103.5498
Lion's HeadIce Accretion2023RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2023 | 14.0283 | 16.8324 | 20.36 | 23.0746 | 25.7544
Lion's HeadIce Accretion2025RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2025 | 14.0561 | 16.8767 | 20.4267 | 23.1537 | 25.851
Lion's HeadIce Accretion2030RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2030 | 14.0839 | 16.9209 | 20.4933 | 23.2328 | 25.9476
Lion's HeadIce Accretion2035RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2035 | 14.1118 | 16.9652 | 20.56 | 23.3119 | 26.0442
Lion's HeadIce Accretion2040RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2040 | 14.1396 | 17.0095 | 20.6267 | 23.391 | 26.1408
Lion's HeadIce Accretion2045RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2045 | 14.1674 | 17.0537 | 20.6933 | 23.4701 | 26.2374
Lion's HeadIce Accretion2050RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2050 | 14.1006 | 17.005 | 20.672 | 23.4633 | 26.2534
Lion's HeadIce Accretion2055RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2055 | 14.006 | 16.9121 | 20.584 | 23.3774 | 26.1727
Lion's HeadIce Accretion2060RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2060 | 13.9114 | 16.8191 | 20.496 | 23.2916 | 26.0921
Lion's HeadIce Accretion2065RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2065 | 13.8167 | 16.7262 | 20.408 | 23.2057 | 26.0114
Lion's HeadIce Accretion2070RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2070 | 13.7221 | 16.6332 | 20.32 | 23.1198 | 25.9308
Lion's HeadIce Accretion2075RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2075 | 13.6131 | 16.5198 | 20.2 | 22.9955 | 25.8006
Lion's HeadIce Accretion2080RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2080 | 13.5041 | 16.4063 | 20.08 | 22.8712 | 25.6704
Lion's HeadIce Accretion2085RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2085 | 13.395 | 16.2929 | 19.96 | 22.7469 | 25.5402
Lion's HeadIce Accretion2090RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2090 | 13.286 | 16.1795 | 19.84 | 22.6226 | 25.41
Lion's HeadIce Accretion2095RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2095 | 13.177 | 16.066 | 19.72 | 22.4983 | 25.2798
Lion's HeadIce Accretion2100RCP4.5 | Lion's Head | Ice Accretion | RCP4.5 | 2100 | 13.068 | 15.9526 | 19.6 | 22.374 | 25.1496
Lion's HeadIce Accretion2023RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2023 | 14.0283 | 16.8324 | 20.36 | 23.0746 | 25.7544
Lion's HeadIce Accretion2025RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2025 | 14.0561 | 16.8767 | 20.4267 | 23.1537 | 25.851
Lion's HeadIce Accretion2030RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2030 | 14.0839 | 16.9209 | 20.4933 | 23.2328 | 25.9476
Lion's HeadIce Accretion2035RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2035 | 14.1118 | 16.9652 | 20.56 | 23.3119 | 26.0442
Lion's HeadIce Accretion2040RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2040 | 14.1396 | 17.0095 | 20.6267 | 23.391 | 26.1408
Lion's HeadIce Accretion2045RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2045 | 14.1674 | 17.0537 | 20.6933 | 23.4701 | 26.2374
Lion's HeadIce Accretion2050RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2050 | 14.1006 | 17.005 | 20.672 | 23.4633 | 26.2534
Lion's HeadIce Accretion2055RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2055 | 14.006 | 16.9121 | 20.584 | 23.3774 | 26.1727
Lion's HeadIce Accretion2060RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2060 | 13.9114 | 16.8191 | 20.496 | 23.2916 | 26.0921
Lion's HeadIce Accretion2065RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2065 | 13.8167 | 16.7262 | 20.408 | 23.2057 | 26.0114
Lion's HeadIce Accretion2070RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2070 | 13.7221 | 16.6332 | 20.32 | 23.1198 | 25.9308
Lion's HeadIce Accretion2075RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2075 | 13.5586 | 16.463 | 20.14 | 22.9333 | 25.7355
Lion's HeadIce Accretion2080RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2080 | 13.395 | 16.2929 | 19.96 | 22.7469 | 25.5402
Lion's HeadIce Accretion2085RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2085 | 13.2315 | 16.1227 | 19.78 | 22.5604 | 25.3449
Lion's HeadIce Accretion2090RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2090 | 12.6412 | 15.4657 | 19.0267 | 21.7412 | 24.444
Lion's HeadIce Accretion2095RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2095 | 12.2144 | 14.9787 | 18.4533 | 21.1084 | 23.7384
Lion's HeadIce Accretion2100RCP6.0 | Lion's Head | Ice Accretion | RCP6.0 | 2100 | 11.7876 | 14.4918 | 17.88 | 20.4756 | 23.0328
Lion's HeadIce Accretion2023RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2023 | 14.0283 | 16.8324 | 20.36 | 23.0746 | 25.7544
Lion's HeadIce Accretion2025RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2025 | 14.0839 | 16.9209 | 20.4933 | 23.2328 | 25.9476
Lion's HeadIce Accretion2030RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2030 | 14.1396 | 17.0095 | 20.6267 | 23.391 | 26.1408
Lion's HeadIce Accretion2035RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2035 | 14.1953 | 17.098 | 20.76 | 23.5492 | 26.334
Lion's HeadIce Accretion2040RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2040 | 14.0375 | 16.9431 | 20.6133 | 23.4061 | 26.1996
Lion's HeadIce Accretion2045RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2045 | 13.8798 | 16.7881 | 20.4667 | 23.2629 | 26.0652
Lion's HeadIce Accretion2050RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2050 | 13.5041 | 16.4063 | 20.08 | 22.8712 | 25.6704
Lion's HeadIce Accretion2055RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2055 | 13.286 | 16.1795 | 19.84 | 22.6226 | 25.41
Lion's HeadIce Accretion2060RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2060 | 12.6412 | 15.4657 | 19.0267 | 21.7412 | 24.444
Lion's HeadIce Accretion2065RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2065 | 12.2144 | 14.9787 | 18.4533 | 21.1084 | 23.7384
Lion's HeadIce Accretion2070RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2070 | 11.333 | 13.9717 | 17.28 | 19.8051 | 22.302
Lion's HeadIce Accretion2075RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2075 | 10.8784 | 13.4515 | 16.68 | 19.1347 | 21.5712
Lion's HeadIce Accretion2080RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2080 | 10.4238 | 12.9314 | 16.08 | 18.4642 | 20.8404
Lion's HeadIce Accretion2085RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2085 | 9.9019 | 12.3255 | 15.36 | 17.6619 | 19.9584
Lion's HeadIce Accretion2090RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2090 | 9.38 | 11.7196 | 14.64 | 16.8596 | 19.0764
Lion's HeadIce Accretion2095RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2095 | 9.38 | 11.7196 | 14.64 | 16.8596 | 19.0764
Lion's HeadIce Accretion2100RCP8.5 | Lion's Head | Ice Accretion | RCP8.5 | 2100 | 9.38 | 11.7196 | 14.64 | 16.8596 | 19.0764
Lion's HeadWind2023RCP4.5 | Lion's Head | Wind | RCP4.5 | 2023 | 83.7067 | 90.2978 | 97.2768 | 104.2197 | 111.1692
Lion's HeadWind2025RCP4.5 | Lion's Head | Wind | RCP4.5 | 2025 | 83.8227 | 90.4347 | 97.44 | 104.4063 | 111.3789
Lion's HeadWind2030RCP4.5 | Lion's Head | Wind | RCP4.5 | 2030 | 83.9388 | 90.5716 | 97.6032 | 104.5929 | 111.5887
Lion's HeadWind2035RCP4.5 | Lion's Head | Wind | RCP4.5 | 2035 | 84.0548 | 90.7085 | 97.7664 | 104.7795 | 111.7984
Lion's HeadWind2040RCP4.5 | Lion's Head | Wind | RCP4.5 | 2040 | 84.1709 | 90.8454 | 97.9296 | 104.9661 | 112.0082
Lion's HeadWind2045RCP4.5 | Lion's Head | Wind | RCP4.5 | 2045 | 84.2869 | 90.9823 | 98.0928 | 105.1528 | 112.218
Lion's HeadWind2050RCP4.5 | Lion's Head | Wind | RCP4.5 | 2050 | 84.4229 | 91.1352 | 98.2637 | 105.3394 | 112.4233
Lion's HeadWind2055RCP4.5 | Lion's Head | Wind | RCP4.5 | 2055 | 84.4428 | 91.1513 | 98.2714 | 105.3394 | 112.419
Lion's HeadWind2060RCP4.5 | Lion's Head | Wind | RCP4.5 | 2060 | 84.4627 | 91.1674 | 98.279 | 105.3394 | 112.4146
Lion's HeadWind2065RCP4.5 | Lion's Head | Wind | RCP4.5 | 2065 | 84.4826 | 91.1834 | 98.2867 | 105.3394 | 112.4102
Lion's HeadWind2070RCP4.5 | Lion's Head | Wind | RCP4.5 | 2070 | 84.5025 | 91.1995 | 98.2944 | 105.3394 | 112.4058
Lion's HeadWind2075RCP4.5 | Lion's Head | Wind | RCP4.5 | 2075 | 84.6116 | 91.3424 | 98.4784 | 105.5602 | 112.6612
Lion's HeadWind2080RCP4.5 | Lion's Head | Wind | RCP4.5 | 2080 | 84.7208 | 91.4852 | 98.6624 | 105.7811 | 112.9165
Lion's HeadWind2085RCP4.5 | Lion's Head | Wind | RCP4.5 | 2085 | 84.8299 | 91.6281 | 98.8464 | 106.0019 | 113.1719
Lion's HeadWind2090RCP4.5 | Lion's Head | Wind | RCP4.5 | 2090 | 84.939 | 91.7709 | 99.0304 | 106.2228 | 113.4273
Lion's HeadWind2095RCP4.5 | Lion's Head | Wind | RCP4.5 | 2095 | 85.0482 | 91.9138 | 99.2144 | 106.4436 | 113.6826
Lion's HeadWind2100RCP4.5 | Lion's Head | Wind | RCP4.5 | 2100 | 85.1573 | 92.0566 | 99.3984 | 106.6644 | 113.938
Lion's HeadWind2023RCP6.0 | Lion's Head | Wind | RCP6.0 | 2023 | 83.7067 | 90.2978 | 97.2768 | 104.2197 | 111.1692
Lion's HeadWind2025RCP6.0 | Lion's Head | Wind | RCP6.0 | 2025 | 83.8227 | 90.4347 | 97.44 | 104.4063 | 111.3789
Lion's HeadWind2030RCP6.0 | Lion's Head | Wind | RCP6.0 | 2030 | 83.9388 | 90.5716 | 97.6032 | 104.5929 | 111.5887
Lion's HeadWind2035RCP6.0 | Lion's Head | Wind | RCP6.0 | 2035 | 84.0548 | 90.7085 | 97.7664 | 104.7795 | 111.7984
Lion's HeadWind2040RCP6.0 | Lion's Head | Wind | RCP6.0 | 2040 | 84.1709 | 90.8454 | 97.9296 | 104.9661 | 112.0082
Lion's HeadWind2045RCP6.0 | Lion's Head | Wind | RCP6.0 | 2045 | 84.2869 | 90.9823 | 98.0928 | 105.1528 | 112.218
Lion's HeadWind2050RCP6.0 | Lion's Head | Wind | RCP6.0 | 2050 | 84.4229 | 91.1352 | 98.2637 | 105.3394 | 112.4233
Lion's HeadWind2055RCP6.0 | Lion's Head | Wind | RCP6.0 | 2055 | 84.4428 | 91.1513 | 98.2714 | 105.3394 | 112.419
Lion's HeadWind2060RCP6.0 | Lion's Head | Wind | RCP6.0 | 2060 | 84.4627 | 91.1674 | 98.279 | 105.3394 | 112.4146
Lion's HeadWind2065RCP6.0 | Lion's Head | Wind | RCP6.0 | 2065 | 84.4826 | 91.1834 | 98.2867 | 105.3394 | 112.4102
Lion's HeadWind2070RCP6.0 | Lion's Head | Wind | RCP6.0 | 2070 | 84.5025 | 91.1995 | 98.2944 | 105.3394 | 112.4058
Lion's HeadWind2075RCP6.0 | Lion's Head | Wind | RCP6.0 | 2075 | 84.6662 | 91.4138 | 98.5704 | 105.6706 | 112.7889
Lion's HeadWind2080RCP6.0 | Lion's Head | Wind | RCP6.0 | 2080 | 84.8299 | 91.6281 | 98.8464 | 106.0019 | 113.1719
Lion's HeadWind2085RCP6.0 | Lion's Head | Wind | RCP6.0 | 2085 | 84.9936 | 91.8423 | 99.1224 | 106.3332 | 113.5549
Lion's HeadWind2090RCP6.0 | Lion's Head | Wind | RCP6.0 | 2090 | 85.4668 | 92.4346 | 99.8656 | 107.2089 | 114.5581
Lion's HeadWind2095RCP6.0 | Lion's Head | Wind | RCP6.0 | 2095 | 85.7763 | 92.8125 | 100.3328 | 107.7533 | 115.1783
Lion's HeadWind2100RCP6.0 | Lion's Head | Wind | RCP6.0 | 2100 | 86.0857 | 93.1905 | 100.8 | 108.2977 | 115.7985
Lion's HeadWind2023RCP8.5 | Lion's Head | Wind | RCP8.5 | 2023 | 83.7067 | 90.2978 | 97.2768 | 104.2197 | 111.1692
Lion's HeadWind2025RCP8.5 | Lion's Head | Wind | RCP8.5 | 2025 | 83.9388 | 90.5716 | 97.6032 | 104.5929 | 111.5887
Lion's HeadWind2030RCP8.5 | Lion's Head | Wind | RCP8.5 | 2030 | 84.1709 | 90.8454 | 97.9296 | 104.9661 | 112.0082
Lion's HeadWind2035RCP8.5 | Lion's Head | Wind | RCP8.5 | 2035 | 84.403 | 91.1192 | 98.256 | 105.3394 | 112.4277
Lion's HeadWind2040RCP8.5 | Lion's Head | Wind | RCP8.5 | 2040 | 84.4361 | 91.146 | 98.2688 | 105.3394 | 112.4204
Lion's HeadWind2045RCP8.5 | Lion's Head | Wind | RCP8.5 | 2045 | 84.4693 | 91.1727 | 98.2816 | 105.3394 | 112.4131
Lion's HeadWind2050RCP8.5 | Lion's Head | Wind | RCP8.5 | 2050 | 84.7208 | 91.4852 | 98.6624 | 105.7811 | 112.9165
Lion's HeadWind2055RCP8.5 | Lion's Head | Wind | RCP8.5 | 2055 | 84.939 | 91.7709 | 99.0304 | 106.2228 | 113.4273
Lion's HeadWind2060RCP8.5 | Lion's Head | Wind | RCP8.5 | 2060 | 85.4668 | 92.4346 | 99.8656 | 107.2089 | 114.5581
Lion's HeadWind2065RCP8.5 | Lion's Head | Wind | RCP8.5 | 2065 | 85.7763 | 92.8125 | 100.3328 | 107.7533 | 115.1783
Lion's HeadWind2070RCP8.5 | Lion's Head | Wind | RCP8.5 | 2070 | 86.2377 | 93.369 | 101.008 | 108.5271 | 116.0575
Lion's HeadWind2075RCP8.5 | Lion's Head | Wind | RCP8.5 | 2075 | 86.3897 | 93.5476 | 101.216 | 108.7565 | 116.3165
Lion's HeadWind2080RCP8.5 | Lion's Head | Wind | RCP8.5 | 2080 | 86.5417 | 93.7261 | 101.424 | 108.9859 | 116.5755
Lion's HeadWind2085RCP8.5 | Lion's Head | Wind | RCP8.5 | 2085 | 86.7406 | 93.9627 | 101.7072 | 109.3146 | 116.9421
Lion's HeadWind2090RCP8.5 | Lion's Head | Wind | RCP8.5 | 2090 | 86.9396 | 94.1993 | 101.9904 | 109.6433 | 117.3087
Lion's HeadWind2095RCP8.5 | Lion's Head | Wind | RCP8.5 | 2095 | 86.9396 | 94.1993 | 101.9904 | 109.6433 | 117.3087
Lion's HeadWind2100RCP8.5 | Lion's Head | Wind | RCP8.5 | 2100 | 86.9396 | 94.1993 | 101.9904 | 109.6433 | 117.3087
ListowelIce Accretion2023RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2023 | 15.9725 | 19.1854 | 23.253 | 26.3539 | 29.4437
ListowelIce Accretion2025RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2025 | 16.0498 | 19.2841 | 23.3795 | 26.5055 | 29.6176
ListowelIce Accretion2030RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2030 | 16.1272 | 19.3827 | 23.506 | 26.6571 | 29.7914
ListowelIce Accretion2035RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2035 | 16.2045 | 19.4813 | 23.6325 | 26.8087 | 29.9653
ListowelIce Accretion2040RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2040 | 16.2819 | 19.58 | 23.759 | 26.9603 | 30.1392
ListowelIce Accretion2045RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2045 | 16.3592 | 19.6786 | 23.8855 | 27.1119 | 30.3131
ListowelIce Accretion2050RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2050 | 16.443 | 19.8078 | 24.0764 | 27.3415 | 30.5913
ListowelIce Accretion2055RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2055 | 16.4494 | 19.8383 | 24.1408 | 27.4194 | 30.6956
ListowelIce Accretion2060RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2060 | 16.4558 | 19.8689 | 24.2052 | 27.4974 | 30.7999
ListowelIce Accretion2065RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2065 | 16.4622 | 19.8994 | 24.2696 | 27.5754 | 30.9043
ListowelIce Accretion2070RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2070 | 16.4686 | 19.93 | 24.334 | 27.6534 | 31.0086
ListowelIce Accretion2075RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2075 | 16.4179 | 19.8981 | 24.3187 | 27.6577 | 31.0231
ListowelIce Accretion2080RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2080 | 16.3672 | 19.8663 | 24.3033 | 27.662 | 31.0376
ListowelIce Accretion2085RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2085 | 16.3165 | 19.8345 | 24.288 | 27.6664 | 31.0521
ListowelIce Accretion2090RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2090 | 16.2659 | 19.8027 | 24.2727 | 27.6707 | 31.0666
ListowelIce Accretion2095RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2095 | 16.2152 | 19.7709 | 24.2573 | 27.675 | 31.0811
ListowelIce Accretion2100RCP4.5 | Listowel | Ice Accretion | RCP4.5 | 2100 | 16.1645 | 19.7391 | 24.242 | 27.6793 | 31.0955
ListowelIce Accretion2023RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2023 | 15.9725 | 19.1854 | 23.253 | 26.3539 | 29.4437
ListowelIce Accretion2025RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2025 | 16.0498 | 19.2841 | 23.3795 | 26.5055 | 29.6176
ListowelIce Accretion2030RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2030 | 16.1272 | 19.3827 | 23.506 | 26.6571 | 29.7914
ListowelIce Accretion2035RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2035 | 16.2045 | 19.4813 | 23.6325 | 26.8087 | 29.9653
ListowelIce Accretion2040RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2040 | 16.2819 | 19.58 | 23.759 | 26.9603 | 30.1392
ListowelIce Accretion2045RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2045 | 16.3592 | 19.6786 | 23.8855 | 27.1119 | 30.3131
ListowelIce Accretion2050RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2050 | 16.443 | 19.8078 | 24.0764 | 27.3415 | 30.5913
ListowelIce Accretion2055RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2055 | 16.4494 | 19.8383 | 24.1408 | 27.4194 | 30.6956
ListowelIce Accretion2060RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2060 | 16.4558 | 19.8689 | 24.2052 | 27.4974 | 30.7999
ListowelIce Accretion2065RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2065 | 16.4622 | 19.8994 | 24.2696 | 27.5754 | 30.9043
ListowelIce Accretion2070RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2070 | 16.4686 | 19.93 | 24.334 | 27.6534 | 31.0086
ListowelIce Accretion2075RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2075 | 16.3926 | 19.8822 | 24.311 | 27.6599 | 31.0303
ListowelIce Accretion2080RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2080 | 16.3165 | 19.8345 | 24.288 | 27.6664 | 31.0521
ListowelIce Accretion2085RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2085 | 16.2405 | 19.7868 | 24.265 | 27.6729 | 31.0738
ListowelIce Accretion2090RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2090 | 15.8978 | 19.4654 | 23.9583 | 27.3761 | 30.7864
ListowelIce Accretion2095RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2095 | 15.631 | 19.1918 | 23.6747 | 27.0729 | 30.4773
ListowelIce Accretion2100RCP6.0 | Listowel | Ice Accretion | RCP6.0 | 2100 | 15.3643 | 18.9182 | 23.391 | 26.7697 | 30.1682
ListowelIce Accretion2023RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2023 | 15.9725 | 19.1854 | 23.253 | 26.3539 | 29.4437
ListowelIce Accretion2025RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2025 | 16.1272 | 19.3827 | 23.506 | 26.6571 | 29.7914
ListowelIce Accretion2030RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2030 | 16.2819 | 19.58 | 23.759 | 26.9603 | 30.1392
ListowelIce Accretion2035RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2035 | 16.4366 | 19.7772 | 24.012 | 27.2635 | 30.487
ListowelIce Accretion2040RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2040 | 16.4473 | 19.8281 | 24.1193 | 27.3935 | 30.6608
ListowelIce Accretion2045RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2045 | 16.4579 | 19.8791 | 24.2267 | 27.5234 | 30.8347
ListowelIce Accretion2050RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2050 | 16.3672 | 19.8663 | 24.3033 | 27.662 | 31.0376
ListowelIce Accretion2055RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2055 | 16.2659 | 19.8027 | 24.2727 | 27.6707 | 31.0666
ListowelIce Accretion2060RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2060 | 15.8978 | 19.4654 | 23.9583 | 27.3761 | 30.7864
ListowelIce Accretion2065RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2065 | 15.631 | 19.1918 | 23.6747 | 27.0729 | 30.4773
ListowelIce Accretion2070RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2070 | 14.8735 | 18.3646 | 22.7623 | 26.0853 | 29.4147
ListowelIce Accretion2075RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2075 | 14.3827 | 17.811 | 22.1337 | 25.4009 | 28.6612
ListowelIce Accretion2080RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2080 | 13.8919 | 17.2574 | 21.505 | 24.7165 | 27.9077
ListowelIce Accretion2085RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2085 | 13.1717 | 16.4079 | 20.493 | 23.5729 | 26.6471
ListowelIce Accretion2090RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2090 | 12.4515 | 15.5583 | 19.481 | 22.4294 | 25.3865
ListowelIce Accretion2095RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2095 | 12.4515 | 15.5583 | 19.481 | 22.4294 | 25.3865
ListowelIce Accretion2100RCP8.5 | Listowel | Ice Accretion | RCP8.5 | 2100 | 12.4515 | 15.5583 | 19.481 | 22.4294 | 25.3865
ListowelWind2023RCP4.5 | Listowel | Wind | RCP4.5 | 2023 | 84.3441 | 90.9317 | 97.8827 | 104.8175 | 111.7521
ListowelWind2025RCP4.5 | Listowel | Wind | RCP4.5 | 2025 | 84.3888 | 90.9843 | 97.9458 | 104.8884 | 111.8332
ListowelWind2030RCP4.5 | Listowel | Wind | RCP4.5 | 2030 | 84.4334 | 91.0369 | 98.0088 | 104.9594 | 111.9143
ListowelWind2035RCP4.5 | Listowel | Wind | RCP4.5 | 2035 | 84.4781 | 91.0895 | 98.0719 | 105.0303 | 111.9954
ListowelWind2040RCP4.5 | Listowel | Wind | RCP4.5 | 2040 | 84.5228 | 91.1422 | 98.1349 | 105.1012 | 112.0765
ListowelWind2045RCP4.5 | Listowel | Wind | RCP4.5 | 2045 | 84.5675 | 91.1948 | 98.1979 | 105.1721 | 112.1576
ListowelWind2050RCP4.5 | Listowel | Wind | RCP4.5 | 2050 | 84.6205 | 91.2528 | 98.261 | 105.241 | 112.2299
ListowelWind2055RCP4.5 | Listowel | Wind | RCP4.5 | 2055 | 84.6289 | 91.2582 | 98.261 | 105.2389 | 112.221
ListowelWind2060RCP4.5 | Listowel | Wind | RCP4.5 | 2060 | 84.6373 | 91.2637 | 98.261 | 105.2368 | 112.2122
ListowelWind2065RCP4.5 | Listowel | Wind | RCP4.5 | 2065 | 84.6456 | 91.2691 | 98.261 | 105.2348 | 112.2033
ListowelWind2070RCP4.5 | Listowel | Wind | RCP4.5 | 2070 | 84.654 | 91.2745 | 98.261 | 105.2327 | 112.1945
ListowelWind2075RCP4.5 | Listowel | Wind | RCP4.5 | 2075 | 84.7475 | 91.4023 | 98.434 | 105.4437 | 112.4451
ListowelWind2080RCP4.5 | Listowel | Wind | RCP4.5 | 2080 | 84.8411 | 91.5301 | 98.607 | 105.6548 | 112.6958
ListowelWind2085RCP4.5 | Listowel | Wind | RCP4.5 | 2085 | 84.9346 | 91.6579 | 98.7799 | 105.8658 | 112.9464
ListowelWind2090RCP4.5 | Listowel | Wind | RCP4.5 | 2090 | 85.0281 | 91.7857 | 98.9529 | 106.0768 | 113.1971
ListowelWind2095RCP4.5 | Listowel | Wind | RCP4.5 | 2095 | 85.1217 | 91.9135 | 99.1259 | 106.2879 | 113.4477
ListowelWind2100RCP4.5 | Listowel | Wind | RCP4.5 | 2100 | 85.2152 | 92.0413 | 99.2989 | 106.4989 | 113.6984
ListowelWind2023RCP6.0 | Listowel | Wind | RCP6.0 | 2023 | 84.3441 | 90.9317 | 97.8827 | 104.8175 | 111.7521
ListowelWind2025RCP6.0 | Listowel | Wind | RCP6.0 | 2025 | 84.3888 | 90.9843 | 97.9458 | 104.8884 | 111.8332
ListowelWind2030RCP6.0 | Listowel | Wind | RCP6.0 | 2030 | 84.4334 | 91.0369 | 98.0088 | 104.9594 | 111.9143
ListowelWind2035RCP6.0 | Listowel | Wind | RCP6.0 | 2035 | 84.4781 | 91.0895 | 98.0719 | 105.0303 | 111.9954
ListowelWind2040RCP6.0 | Listowel | Wind | RCP6.0 | 2040 | 84.5228 | 91.1422 | 98.1349 | 105.1012 | 112.0765
ListowelWind2045RCP6.0 | Listowel | Wind | RCP6.0 | 2045 | 84.5675 | 91.1948 | 98.1979 | 105.1721 | 112.1576
ListowelWind2050RCP6.0 | Listowel | Wind | RCP6.0 | 2050 | 84.6205 | 91.2528 | 98.261 | 105.241 | 112.2299
ListowelWind2055RCP6.0 | Listowel | Wind | RCP6.0 | 2055 | 84.6289 | 91.2582 | 98.261 | 105.2389 | 112.221
ListowelWind2060RCP6.0 | Listowel | Wind | RCP6.0 | 2060 | 84.6373 | 91.2637 | 98.261 | 105.2368 | 112.2122
ListowelWind2065RCP6.0 | Listowel | Wind | RCP6.0 | 2065 | 84.6456 | 91.2691 | 98.261 | 105.2348 | 112.2033
ListowelWind2070RCP6.0 | Listowel | Wind | RCP6.0 | 2070 | 84.654 | 91.2745 | 98.261 | 105.2327 | 112.1945
ListowelWind2075RCP6.0 | Listowel | Wind | RCP6.0 | 2075 | 84.7943 | 91.4662 | 98.5205 | 105.5492 | 112.5704
ListowelWind2080RCP6.0 | Listowel | Wind | RCP6.0 | 2080 | 84.9346 | 91.6579 | 98.7799 | 105.8658 | 112.9464
ListowelWind2085RCP6.0 | Listowel | Wind | RCP6.0 | 2085 | 85.0749 | 91.8496 | 99.0394 | 106.1824 | 113.3224
ListowelWind2090RCP6.0 | Listowel | Wind | RCP6.0 | 2090 | 85.5865 | 92.4983 | 99.8583 | 107.1459 | 114.4392
ListowelWind2095RCP6.0 | Listowel | Wind | RCP6.0 | 2095 | 85.9578 | 92.9554 | 100.4176 | 107.7928 | 115.1801
ListowelWind2100RCP6.0 | Listowel | Wind | RCP6.0 | 2100 | 86.3292 | 93.4125 | 100.977 | 108.4398 | 115.921
ListowelWind2023RCP8.5 | Listowel | Wind | RCP8.5 | 2023 | 84.3441 | 90.9317 | 97.8827 | 104.8175 | 111.7521
ListowelWind2025RCP8.5 | Listowel | Wind | RCP8.5 | 2025 | 84.4334 | 91.0369 | 98.0088 | 104.9594 | 111.9143
ListowelWind2030RCP8.5 | Listowel | Wind | RCP8.5 | 2030 | 84.5228 | 91.1422 | 98.1349 | 105.1012 | 112.0765
ListowelWind2035RCP8.5 | Listowel | Wind | RCP8.5 | 2035 | 84.6121 | 91.2474 | 98.261 | 105.2431 | 112.2387
ListowelWind2040RCP8.5 | Listowel | Wind | RCP8.5 | 2040 | 84.6261 | 91.2564 | 98.261 | 105.2396 | 112.224
ListowelWind2045RCP8.5 | Listowel | Wind | RCP8.5 | 2045 | 84.64 | 91.2655 | 98.261 | 105.2361 | 112.2092
ListowelWind2050RCP8.5 | Listowel | Wind | RCP8.5 | 2050 | 84.8411 | 91.5301 | 98.607 | 105.6548 | 112.6958
ListowelWind2055RCP8.5 | Listowel | Wind | RCP8.5 | 2055 | 85.0281 | 91.7857 | 98.9529 | 106.0768 | 113.1971
ListowelWind2060RCP8.5 | Listowel | Wind | RCP8.5 | 2060 | 85.5865 | 92.4983 | 99.8583 | 107.1459 | 114.4392
ListowelWind2065RCP8.5 | Listowel | Wind | RCP8.5 | 2065 | 85.9578 | 92.9554 | 100.4176 | 107.7928 | 115.1801
ListowelWind2070RCP8.5 | Listowel | Wind | RCP8.5 | 2070 | 86.6028 | 93.7703 | 101.4458 | 109.0003 | 116.5771
ListowelWind2075RCP8.5 | Listowel | Wind | RCP8.5 | 2075 | 86.8764 | 94.1281 | 101.9147 | 109.5607 | 117.2332
ListowelWind2080RCP8.5 | Listowel | Wind | RCP8.5 | 2080 | 87.15 | 94.486 | 102.3835 | 110.1212 | 117.8893
ListowelWind2085RCP8.5 | Listowel | Wind | RCP8.5 | 2085 | 87.3636 | 94.7701 | 102.757 | 110.5675 | 118.4091
ListowelWind2090RCP8.5 | Listowel | Wind | RCP8.5 | 2090 | 87.5772 | 95.0543 | 103.1304 | 111.0138 | 118.9288
ListowelWind2095RCP8.5 | Listowel | Wind | RCP8.5 | 2095 | 87.5772 | 95.0543 | 103.1304 | 111.0138 | 118.9288
ListowelWind2100RCP8.5 | Listowel | Wind | RCP8.5 | 2100 | 87.5772 | 95.0543 | 103.1304 | 111.0138 | 118.9288
LondonIce Accretion2023RCP4.5 | London | Ice Accretion | RCP4.5 | 2023 | 21.9553 | 26.3475 | 31.904 | 36.1238 | 40.3603
LondonIce Accretion2025RCP4.5 | London | Ice Accretion | RCP4.5 | 2025 | 21.8254 | 26.2059 | 31.7493 | 35.9611 | 40.1856
LondonIce Accretion2030RCP4.5 | London | Ice Accretion | RCP4.5 | 2030 | 21.6956 | 26.0642 | 31.5947 | 35.7984 | 40.0109
LondonIce Accretion2035RCP4.5 | London | Ice Accretion | RCP4.5 | 2035 | 21.5657 | 25.9226 | 31.44 | 35.6357 | 39.8362
LondonIce Accretion2040RCP4.5 | London | Ice Accretion | RCP4.5 | 2040 | 21.4358 | 25.7809 | 31.2853 | 35.473 | 39.6614
LondonIce Accretion2045RCP4.5 | London | Ice Accretion | RCP4.5 | 2045 | 21.3059 | 25.6393 | 31.1307 | 35.3102 | 39.4867
LondonIce Accretion2050RCP4.5 | London | Ice Accretion | RCP4.5 | 2050 | 20.7618 | 25.0408 | 30.4576 | 34.5834 | 38.6991
LondonIce Accretion2055RCP4.5 | London | Ice Accretion | RCP4.5 | 2055 | 20.3477 | 24.5839 | 29.9392 | 34.0193 | 38.0863
LondonIce Accretion2060RCP4.5 | London | Ice Accretion | RCP4.5 | 2060 | 19.9335 | 24.1271 | 29.4208 | 33.4552 | 37.4734
LondonIce Accretion2065RCP4.5 | London | Ice Accretion | RCP4.5 | 2065 | 19.5193 | 23.6703 | 28.9024 | 32.8911 | 36.8605
LondonIce Accretion2070RCP4.5 | London | Ice Accretion | RCP4.5 | 2070 | 19.1052 | 23.2134 | 28.384 | 32.327 | 36.2477
LondonIce Accretion2075RCP4.5 | London | Ice Accretion | RCP4.5 | 2075 | 18.9604 | 23.0674 | 28.2347 | 32.1703 | 36.0864
LondonIce Accretion2080RCP4.5 | London | Ice Accretion | RCP4.5 | 2080 | 18.8157 | 22.9213 | 28.0853 | 32.0137 | 35.9251
LondonIce Accretion2085RCP4.5 | London | Ice Accretion | RCP4.5 | 2085 | 18.6709 | 22.7752 | 27.936 | 31.857 | 35.7638
LondonIce Accretion2090RCP4.5 | London | Ice Accretion | RCP4.5 | 2090 | 18.5262 | 22.6291 | 27.7867 | 31.7003 | 35.6026
LondonIce Accretion2095RCP4.5 | London | Ice Accretion | RCP4.5 | 2095 | 18.3815 | 22.483 | 27.6373 | 31.5436 | 35.4413
LondonIce Accretion2100RCP4.5 | London | Ice Accretion | RCP4.5 | 2100 | 18.2367 | 22.337 | 27.488 | 31.3869 | 35.28
LondonIce Accretion2023RCP6.0 | London | Ice Accretion | RCP6.0 | 2023 | 21.9553 | 26.3475 | 31.904 | 36.1238 | 40.3603
LondonIce Accretion2025RCP6.0 | London | Ice Accretion | RCP6.0 | 2025 | 21.8254 | 26.2059 | 31.7493 | 35.9611 | 40.1856
LondonIce Accretion2030RCP6.0 | London | Ice Accretion | RCP6.0 | 2030 | 21.6956 | 26.0642 | 31.5947 | 35.7984 | 40.0109
LondonIce Accretion2035RCP6.0 | London | Ice Accretion | RCP6.0 | 2035 | 21.5657 | 25.9226 | 31.44 | 35.6357 | 39.8362
LondonIce Accretion2040RCP6.0 | London | Ice Accretion | RCP6.0 | 2040 | 21.4358 | 25.7809 | 31.2853 | 35.473 | 39.6614
LondonIce Accretion2045RCP6.0 | London | Ice Accretion | RCP6.0 | 2045 | 21.3059 | 25.6393 | 31.1307 | 35.3102 | 39.4867
LondonIce Accretion2050RCP6.0 | London | Ice Accretion | RCP6.0 | 2050 | 20.7618 | 25.0408 | 30.4576 | 34.5834 | 38.6991
LondonIce Accretion2055RCP6.0 | London | Ice Accretion | RCP6.0 | 2055 | 20.3477 | 24.5839 | 29.9392 | 34.0193 | 38.0863
LondonIce Accretion2060RCP6.0 | London | Ice Accretion | RCP6.0 | 2060 | 19.9335 | 24.1271 | 29.4208 | 33.4552 | 37.4734
LondonIce Accretion2065RCP6.0 | London | Ice Accretion | RCP6.0 | 2065 | 19.5193 | 23.6703 | 28.9024 | 32.8911 | 36.8605
LondonIce Accretion2070RCP6.0 | London | Ice Accretion | RCP6.0 | 2070 | 19.1052 | 23.2134 | 28.384 | 32.327 | 36.2477
LondonIce Accretion2075RCP6.0 | London | Ice Accretion | RCP6.0 | 2075 | 18.888 | 22.9943 | 28.16 | 32.092 | 36.0058
LondonIce Accretion2080RCP6.0 | London | Ice Accretion | RCP6.0 | 2080 | 18.6709 | 22.7752 | 27.936 | 31.857 | 35.7638
LondonIce Accretion2085RCP6.0 | London | Ice Accretion | RCP6.0 | 2085 | 18.4538 | 22.5561 | 27.712 | 31.6219 | 35.5219
LondonIce Accretion2090RCP6.0 | London | Ice Accretion | RCP6.0 | 2090 | 17.7172 | 21.7526 | 26.8267 | 30.6637 | 34.487
LondonIce Accretion2095RCP6.0 | London | Ice Accretion | RCP6.0 | 2095 | 17.1976 | 21.1683 | 26.1653 | 29.9405 | 33.6941
LondonIce Accretion2100RCP6.0 | London | Ice Accretion | RCP6.0 | 2100 | 16.678 | 20.584 | 25.504 | 29.2173 | 32.9011
LondonIce Accretion2023RCP8.5 | London | Ice Accretion | RCP8.5 | 2023 | 21.9553 | 26.3475 | 31.904 | 36.1238 | 40.3603
LondonIce Accretion2025RCP8.5 | London | Ice Accretion | RCP8.5 | 2025 | 21.6956 | 26.0642 | 31.5947 | 35.7984 | 40.0109
LondonIce Accretion2030RCP8.5 | London | Ice Accretion | RCP8.5 | 2030 | 21.4358 | 25.7809 | 31.2853 | 35.473 | 39.6614
LondonIce Accretion2035RCP8.5 | London | Ice Accretion | RCP8.5 | 2035 | 21.176 | 25.4976 | 30.976 | 35.1475 | 39.312
LondonIce Accretion2040RCP8.5 | London | Ice Accretion | RCP8.5 | 2040 | 20.4857 | 24.7362 | 30.112 | 34.2074 | 38.2906
LondonIce Accretion2045RCP8.5 | London | Ice Accretion | RCP8.5 | 2045 | 19.7954 | 23.9748 | 29.248 | 33.2672 | 37.2691
LondonIce Accretion2050RCP8.5 | London | Ice Accretion | RCP8.5 | 2050 | 18.8157 | 22.9213 | 28.0853 | 32.0137 | 35.9251
LondonIce Accretion2055RCP8.5 | London | Ice Accretion | RCP8.5 | 2055 | 18.5262 | 22.6291 | 27.7867 | 31.7003 | 35.6026
LondonIce Accretion2060RCP8.5 | London | Ice Accretion | RCP8.5 | 2060 | 17.7172 | 21.7526 | 26.8267 | 30.6637 | 34.487
LondonIce Accretion2065RCP8.5 | London | Ice Accretion | RCP8.5 | 2065 | 17.1976 | 21.1683 | 26.1653 | 29.9405 | 33.6941
LondonIce Accretion2070RCP8.5 | London | Ice Accretion | RCP8.5 | 2070 | 16.344 | 20.2299 | 25.12 | 28.7954 | 32.4576
LondonIce Accretion2075RCP8.5 | London | Ice Accretion | RCP8.5 | 2075 | 16.01 | 19.8757 | 24.736 | 28.3735 | 32.0141
LondonIce Accretion2080RCP8.5 | London | Ice Accretion | RCP8.5 | 2080 | 15.676 | 19.5216 | 24.352 | 27.9517 | 31.5706
LondonIce Accretion2085RCP8.5 | London | Ice Accretion | RCP8.5 | 2085 | 14.6851 | 18.353 | 22.944 | 26.3787 | 29.8166
LondonIce Accretion2090RCP8.5 | London | Ice Accretion | RCP8.5 | 2090 | 13.6943 | 17.1843 | 21.536 | 24.8058 | 28.0627
LondonIce Accretion2095RCP8.5 | London | Ice Accretion | RCP8.5 | 2095 | 13.6943 | 17.1843 | 21.536 | 24.8058 | 28.0627
LondonIce Accretion2100RCP8.5 | London | Ice Accretion | RCP8.5 | 2100 | 13.6943 | 17.1843 | 21.536 | 24.8058 | 28.0627
LondonWind2023RCP4.5 | London | Wind | RCP4.5 | 2023 | 87.0563 | 93.9114 | 101.17 | 108.391 | 115.6188
LondonWind2025RCP4.5 | London | Wind | RCP4.5 | 2025 | 87.1657 | 94.0571 | 101.3617 | 108.621 | 115.8886
LondonWind2030RCP4.5 | London | Wind | RCP4.5 | 2030 | 87.275 | 94.2028 | 101.5533 | 108.8511 | 116.1584
LondonWind2035RCP4.5 | London | Wind | RCP4.5 | 2035 | 87.3844 | 94.3485 | 101.745 | 109.0811 | 116.4282
LondonWind2040RCP4.5 | London | Wind | RCP4.5 | 2040 | 87.4938 | 94.4942 | 101.9367 | 109.3112 | 116.698
LondonWind2045RCP4.5 | London | Wind | RCP4.5 | 2045 | 87.6032 | 94.6399 | 102.1283 | 109.5412 | 116.9678
LondonWind2050RCP4.5 | London | Wind | RCP4.5 | 2050 | 87.7644 | 94.8581 | 102.42 | 109.8954 | 117.3858
LondonWind2055RCP4.5 | London | Wind | RCP4.5 | 2055 | 87.8162 | 94.9307 | 102.52 | 110.0195 | 117.534
LondonWind2060RCP4.5 | London | Wind | RCP4.5 | 2060 | 87.868 | 95.0032 | 102.62 | 110.1437 | 117.6822
LondonWind2065RCP4.5 | London | Wind | RCP4.5 | 2065 | 87.9198 | 95.0758 | 102.72 | 110.2678 | 117.8304
LondonWind2070RCP4.5 | London | Wind | RCP4.5 | 2070 | 87.9716 | 95.1483 | 102.82 | 110.3919 | 117.9786
LondonWind2075RCP4.5 | London | Wind | RCP4.5 | 2075 | 88.1241 | 95.3467 | 103.0767 | 110.6969 | 118.3339
LondonWind2080RCP4.5 | London | Wind | RCP4.5 | 2080 | 88.2767 | 95.5451 | 103.3333 | 111.0018 | 118.6892
LondonWind2085RCP4.5 | London | Wind | RCP4.5 | 2085 | 88.4292 | 95.7435 | 103.59 | 111.3067 | 119.0445
LondonWind2090RCP4.5 | London | Wind | RCP4.5 | 2090 | 88.5818 | 95.9419 | 103.8467 | 111.6117 | 119.3998
LondonWind2095RCP4.5 | London | Wind | RCP4.5 | 2095 | 88.7343 | 96.1403 | 104.1033 | 111.9167 | 119.7551
LondonWind2100RCP4.5 | London | Wind | RCP4.5 | 2100 | 88.8869 | 96.3387 | 104.36 | 112.2216 | 120.1104
LondonWind2023RCP6.0 | London | Wind | RCP6.0 | 2023 | 87.0563 | 93.9114 | 101.17 | 108.391 | 115.6188
LondonWind2025RCP6.0 | London | Wind | RCP6.0 | 2025 | 87.1657 | 94.0571 | 101.3617 | 108.621 | 115.8886
LondonWind2030RCP6.0 | London | Wind | RCP6.0 | 2030 | 87.275 | 94.2028 | 101.5533 | 108.8511 | 116.1584
LondonWind2035RCP6.0 | London | Wind | RCP6.0 | 2035 | 87.3844 | 94.3485 | 101.745 | 109.0811 | 116.4282
LondonWind2040RCP6.0 | London | Wind | RCP6.0 | 2040 | 87.4938 | 94.4942 | 101.9367 | 109.3112 | 116.698
LondonWind2045RCP6.0 | London | Wind | RCP6.0 | 2045 | 87.6032 | 94.6399 | 102.1283 | 109.5412 | 116.9678
LondonWind2050RCP6.0 | London | Wind | RCP6.0 | 2050 | 87.7644 | 94.8581 | 102.42 | 109.8954 | 117.3858
LondonWind2055RCP6.0 | London | Wind | RCP6.0 | 2055 | 87.8162 | 94.9307 | 102.52 | 110.0195 | 117.534
LondonWind2060RCP6.0 | London | Wind | RCP6.0 | 2060 | 87.868 | 95.0032 | 102.62 | 110.1437 | 117.6822
LondonWind2065RCP6.0 | London | Wind | RCP6.0 | 2065 | 87.9198 | 95.0758 | 102.72 | 110.2678 | 117.8304
LondonWind2070RCP6.0 | London | Wind | RCP6.0 | 2070 | 87.9716 | 95.1483 | 102.82 | 110.3919 | 117.9786
LondonWind2075RCP6.0 | London | Wind | RCP6.0 | 2075 | 88.2004 | 95.4459 | 103.205 | 110.8493 | 118.5115
LondonWind2080RCP6.0 | London | Wind | RCP6.0 | 2080 | 88.4292 | 95.7435 | 103.59 | 111.3067 | 119.0445
LondonWind2085RCP6.0 | London | Wind | RCP6.0 | 2085 | 88.6581 | 96.0411 | 103.975 | 111.7642 | 119.5774
LondonWind2090RCP6.0 | London | Wind | RCP6.0 | 2090 | 89.2639 | 96.8192 | 104.9633 | 112.9314 | 120.9312
LondonWind2095RCP6.0 | London | Wind | RCP6.0 | 2095 | 89.641 | 97.2997 | 105.5667 | 113.6411 | 121.752
LondonWind2100RCP6.0 | London | Wind | RCP6.0 | 2100 | 90.018 | 97.7802 | 106.17 | 114.3509 | 122.5728
LondonWind2023RCP8.5 | London | Wind | RCP8.5 | 2023 | 87.0563 | 93.9114 | 101.17 | 108.391 | 115.6188
LondonWind2025RCP8.5 | London | Wind | RCP8.5 | 2025 | 87.275 | 94.2028 | 101.5533 | 108.8511 | 116.1584
LondonWind2030RCP8.5 | London | Wind | RCP8.5 | 2030 | 87.4938 | 94.4942 | 101.9367 | 109.3112 | 116.698
LondonWind2035RCP8.5 | London | Wind | RCP8.5 | 2035 | 87.7125 | 94.7856 | 102.32 | 109.7713 | 117.2376
LondonWind2040RCP8.5 | London | Wind | RCP8.5 | 2040 | 87.7989 | 94.9065 | 102.4867 | 109.9782 | 117.4846
LondonWind2045RCP8.5 | London | Wind | RCP8.5 | 2045 | 87.8852 | 95.0274 | 102.6533 | 110.185 | 117.7316
LondonWind2050RCP8.5 | London | Wind | RCP8.5 | 2050 | 88.2767 | 95.5451 | 103.3333 | 111.0018 | 118.6892
LondonWind2055RCP8.5 | London | Wind | RCP8.5 | 2055 | 88.5818 | 95.9419 | 103.8467 | 111.6117 | 119.3998
LondonWind2060RCP8.5 | London | Wind | RCP8.5 | 2060 | 89.2639 | 96.8192 | 104.9633 | 112.9314 | 120.9312
LondonWind2065RCP8.5 | London | Wind | RCP8.5 | 2065 | 89.641 | 97.2997 | 105.5667 | 113.6411 | 121.752
LondonWind2070RCP8.5 | London | Wind | RCP8.5 | 2070 | 90.2512 | 98.0716 | 106.54 | 114.7896 | 123.0782
LondonWind2075RCP8.5 | London | Wind | RCP8.5 | 2075 | 90.4843 | 98.363 | 106.91 | 115.2283 | 123.5836
LondonWind2080RCP8.5 | London | Wind | RCP8.5 | 2080 | 90.7175 | 98.6544 | 107.28 | 115.667 | 124.089
LondonWind2085RCP8.5 | London | Wind | RCP8.5 | 2085 | 91.1147 | 99.1799 | 107.97 | 116.4909 | 125.058
LondonWind2090RCP8.5 | London | Wind | RCP8.5 | 2090 | 91.5119 | 99.7053 | 108.66 | 117.3148 | 126.027
LondonWind2095RCP8.5 | London | Wind | RCP8.5 | 2095 | 91.5119 | 99.7053 | 108.66 | 117.3148 | 126.027
LondonWind2100RCP8.5 | London | Wind | RCP8.5 | 2100 | 91.5119 | 99.7053 | 108.66 | 117.3148 | 126.027
LucanIce Accretion2023RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425
LucanIce Accretion2025RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2025 | 17.1352 | 20.5563 | 24.8625 | 28.1605 | 31.4423
LucanIce Accretion2030RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2030 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542
LucanIce Accretion2035RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2035 | 17.17 | 20.6255 | 24.9875 | 28.3206 | 31.6418
LucanIce Accretion2040RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2040 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415
LucanIce Accretion2045RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2045 | 17.2048 | 20.6947 | 25.1125 | 28.4807 | 31.8412
LucanIce Accretion2050RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2050 | 17.1526 | 20.6794 | 25.145 | 28.5438 | 31.941
LucanIce Accretion2055RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2055 | 17.083 | 20.6296 | 25.115 | 28.5268 | 31.941
LucanIce Accretion2060RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2060 | 17.0134 | 20.5799 | 25.085 | 28.5099 | 31.941
LucanIce Accretion2065RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2065 | 16.9439 | 20.53 | 25.055 | 28.4929 | 31.941
LucanIce Accretion2070RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2070 | 16.8743 | 20.4802 | 25.025 | 28.476 | 31.941
LucanIce Accretion2075RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2075 | 16.8424 | 20.4664 | 25.0375 | 28.5042 | 31.9883
LucanIce Accretion2080RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2080 | 16.8105 | 20.4526 | 25.05 | 28.5325 | 32.0355
LucanIce Accretion2085RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2085 | 16.7786 | 20.4387 | 25.0625 | 28.5607 | 32.0827
LucanIce Accretion2090RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2090 | 16.7467 | 20.4249 | 25.075 | 28.589 | 32.13
LucanIce Accretion2095RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2095 | 16.7148 | 20.4111 | 25.0875 | 28.6172 | 32.1773
LucanIce Accretion2100RCP4.5 | Lucan | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.3972 | 25.1 | 28.6455 | 32.2245
LucanIce Accretion2023RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425
LucanIce Accretion2025RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2025 | 17.1352 | 20.5563 | 24.8625 | 28.1605 | 31.4423
LucanIce Accretion2030RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2030 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542
LucanIce Accretion2035RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2035 | 17.17 | 20.6255 | 24.9875 | 28.3206 | 31.6418
LucanIce Accretion2040RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2040 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415
LucanIce Accretion2045RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2045 | 17.2048 | 20.6947 | 25.1125 | 28.4807 | 31.8412
LucanIce Accretion2050RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2050 | 17.1526 | 20.6794 | 25.145 | 28.5438 | 31.941
LucanIce Accretion2055RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2055 | 17.083 | 20.6296 | 25.115 | 28.5268 | 31.941
LucanIce Accretion2060RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2060 | 17.0134 | 20.5799 | 25.085 | 28.5099 | 31.941
LucanIce Accretion2065RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2065 | 16.9439 | 20.53 | 25.055 | 28.4929 | 31.941
LucanIce Accretion2070RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2070 | 16.8743 | 20.4802 | 25.025 | 28.476 | 31.941
LucanIce Accretion2075RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2075 | 16.8264 | 20.4595 | 25.0437 | 28.5184 | 32.0119
LucanIce Accretion2080RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2080 | 16.7786 | 20.4387 | 25.0625 | 28.5607 | 32.0827
LucanIce Accretion2085RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2085 | 16.7308 | 20.418 | 25.0813 | 28.6031 | 32.1536
LucanIce Accretion2090RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2090 | 16.4742 | 20.1898 | 24.8833 | 28.4289 | 31.9935
LucanIce Accretion2095RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2095 | 16.2654 | 19.9822 | 24.6667 | 28.2123 | 31.7625
LucanIce Accretion2100RCP6.0 | Lucan | Ice Accretion | RCP6.0 | 2100 | 16.0566 | 19.7747 | 24.45 | 27.9957 | 31.5315
LucanIce Accretion2023RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425
LucanIce Accretion2025RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2025 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542
LucanIce Accretion2030RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2030 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415
LucanIce Accretion2035RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2035 | 17.2222 | 20.7293 | 25.175 | 28.5607 | 31.941
LucanIce Accretion2040RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2040 | 17.1062 | 20.6462 | 25.125 | 28.5325 | 31.941
LucanIce Accretion2045RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2045 | 16.9902 | 20.5633 | 25.075 | 28.5042 | 31.941
LucanIce Accretion2050RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2050 | 16.8105 | 20.4526 | 25.05 | 28.5325 | 32.0355
LucanIce Accretion2055RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2055 | 16.7467 | 20.4249 | 25.075 | 28.589 | 32.13
LucanIce Accretion2060RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2060 | 16.4742 | 20.1898 | 24.8833 | 28.4289 | 31.9935
LucanIce Accretion2065RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2065 | 16.2654 | 19.9822 | 24.6667 | 28.2123 | 31.7625
LucanIce Accretion2070RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2070 | 15.6797 | 19.3528 | 23.975 | 27.4778 | 30.9645
LucanIce Accretion2075RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2075 | 15.3028 | 18.9309 | 23.5 | 26.9599 | 30.3975
LucanIce Accretion2080RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2080 | 14.9259 | 18.509 | 23.025 | 26.442 | 29.8305
LucanIce Accretion2085RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2085 | 14.1431 | 17.5856 | 21.925 | 25.2131 | 28.476
LucanIce Accretion2090RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2090 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215
LucanIce Accretion2095RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2095 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215
LucanIce Accretion2100RCP8.5 | Lucan | Ice Accretion | RCP8.5 | 2100 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215
LucanWind2023RCP4.5 | Lucan | Wind | RCP4.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
LucanWind2025RCP4.5 | Lucan | Wind | RCP4.5 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
LucanWind2030RCP4.5 | Lucan | Wind | RCP4.5 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
LucanWind2035RCP4.5 | Lucan | Wind | RCP4.5 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
LucanWind2040RCP4.5 | Lucan | Wind | RCP4.5 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
LucanWind2045RCP4.5 | Lucan | Wind | RCP4.5 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
LucanWind2050RCP4.5 | Lucan | Wind | RCP4.5 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
LucanWind2055RCP4.5 | Lucan | Wind | RCP4.5 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
LucanWind2060RCP4.5 | Lucan | Wind | RCP4.5 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
LucanWind2065RCP4.5 | Lucan | Wind | RCP4.5 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
LucanWind2070RCP4.5 | Lucan | Wind | RCP4.5 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
LucanWind2075RCP4.5 | Lucan | Wind | RCP4.5 | 2075 | 86.3504 | 93.3577 | 100.8387 | 108.226 | 115.6228
LucanWind2080RCP4.5 | Lucan | Wind | RCP4.5 | 2080 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
LucanWind2085RCP4.5 | Lucan | Wind | RCP4.5 | 2085 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
LucanWind2090RCP4.5 | Lucan | Wind | RCP4.5 | 2090 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
LucanWind2095RCP4.5 | Lucan | Wind | RCP4.5 | 2095 | 86.7678 | 93.9167 | 101.5705 | 109.1068 | 116.6655
LucanWind2100RCP4.5 | Lucan | Wind | RCP4.5 | 2100 | 86.8722 | 94.0565 | 101.7534 | 109.327 | 116.9262
LucanWind2023RCP6.0 | Lucan | Wind | RCP6.0 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
LucanWind2025RCP6.0 | Lucan | Wind | RCP6.0 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
LucanWind2030RCP6.0 | Lucan | Wind | RCP6.0 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
LucanWind2035RCP6.0 | Lucan | Wind | RCP6.0 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
LucanWind2040RCP6.0 | Lucan | Wind | RCP6.0 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
LucanWind2045RCP6.0 | Lucan | Wind | RCP6.0 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
LucanWind2050RCP6.0 | Lucan | Wind | RCP6.0 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
LucanWind2055RCP6.0 | Lucan | Wind | RCP6.0 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
LucanWind2060RCP6.0 | Lucan | Wind | RCP6.0 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
LucanWind2065RCP6.0 | Lucan | Wind | RCP6.0 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
LucanWind2070RCP6.0 | Lucan | Wind | RCP6.0 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
LucanWind2075RCP6.0 | Lucan | Wind | RCP6.0 | 2075 | 86.4026 | 93.4276 | 100.9302 | 108.3361 | 115.7531
LucanWind2080RCP6.0 | Lucan | Wind | RCP6.0 | 2080 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
LucanWind2085RCP6.0 | Lucan | Wind | RCP6.0 | 2085 | 86.7157 | 93.8469 | 101.479 | 108.9967 | 116.5351
LucanWind2090RCP6.0 | Lucan | Wind | RCP6.0 | 2090 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
LucanWind2095RCP6.0 | Lucan | Wind | RCP6.0 | 2095 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
LucanWind2100RCP6.0 | Lucan | Wind | RCP6.0 | 2100 | 87.7861 | 95.1502 | 103.0568 | 110.8265 | 118.6131
LucanWind2023RCP8.5 | Lucan | Wind | RCP8.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
LucanWind2025RCP8.5 | Lucan | Wind | RCP8.5 | 2025 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
LucanWind2030RCP8.5 | Lucan | Wind | RCP8.5 | 2030 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
LucanWind2035RCP8.5 | Lucan | Wind | RCP8.5 | 2035 | 86.0768 | 93.0084 | 100.3912 | 107.7017 | 115.0269
LucanWind2040RCP8.5 | Lucan | Wind | RCP8.5 | 2040 | 86.1332 | 93.0782 | 100.4794 | 107.8031 | 115.1386
LucanWind2045RCP8.5 | Lucan | Wind | RCP8.5 | 2045 | 86.1896 | 93.1481 | 100.5676 | 107.9044 | 115.2504
LucanWind2050RCP8.5 | Lucan | Wind | RCP8.5 | 2050 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
LucanWind2055RCP8.5 | Lucan | Wind | RCP8.5 | 2055 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
LucanWind2060RCP8.5 | Lucan | Wind | RCP8.5 | 2060 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
LucanWind2065RCP8.5 | Lucan | Wind | RCP8.5 | 2065 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
LucanWind2070RCP8.5 | Lucan | Wind | RCP8.5 | 2070 | 88.0541 | 95.5026 | 103.5207 | 111.3788 | 119.2611
LucanWind2075RCP8.5 | Lucan | Wind | RCP8.5 | 2075 | 88.322 | 95.855 | 103.9845 | 111.9311 | 119.9091
LucanWind2080RCP8.5 | Lucan | Wind | RCP8.5 | 2080 | 88.59 | 96.2074 | 104.4484 | 112.4833 | 120.5571
LucanWind2085RCP8.5 | Lucan | Wind | RCP8.5 | 2085 | 88.9454 | 96.6585 | 105.0217 | 113.1649 | 121.3447
LucanWind2090RCP8.5 | Lucan | Wind | RCP8.5 | 2090 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
LucanWind2095RCP8.5 | Lucan | Wind | RCP8.5 | 2095 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
LucanWind2100RCP8.5 | Lucan | Wind | RCP8.5 | 2100 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
MaitlandIce Accretion2023RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2023 | 20.6249 | 24.5763 | 29.61 | 33.4593 | 37.3086
MaitlandIce Accretion2025RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2025 | 20.6945 | 24.6801 | 29.755 | 33.6345 | 37.5102
MaitlandIce Accretion2030RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2030 | 20.764 | 24.7838 | 29.9 | 33.8096 | 37.7118
MaitlandIce Accretion2035RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2035 | 20.8336 | 24.8875 | 30.045 | 33.9847 | 37.9134
MaitlandIce Accretion2040RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2040 | 20.9032 | 24.9913 | 30.19 | 34.1599 | 38.115
MaitlandIce Accretion2045RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2045 | 20.9728 | 25.0951 | 30.335 | 34.335 | 38.3166
MaitlandIce Accretion2050RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2050 | 20.9046 | 25.0544 | 30.318 | 34.3339 | 38.3368
MaitlandIce Accretion2055RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2055 | 20.7668 | 24.91 | 30.156 | 34.1576 | 38.1553
MaitlandIce Accretion2060RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2060 | 20.6291 | 24.7655 | 29.994 | 33.9814 | 37.9739
MaitlandIce Accretion2065RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2065 | 20.4913 | 24.6211 | 29.832 | 33.8051 | 37.7924
MaitlandIce Accretion2070RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2070 | 20.3535 | 24.4767 | 29.67 | 33.6288 | 37.611
MaitlandIce Accretion2075RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2075 | 20.4231 | 24.5846 | 29.825 | 33.8209 | 37.8378
MaitlandIce Accretion2080RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2080 | 20.4927 | 24.6925 | 29.98 | 34.013 | 38.0646
MaitlandIce Accretion2085RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2085 | 20.5623 | 24.8004 | 30.135 | 34.2051 | 38.2914
MaitlandIce Accretion2090RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2090 | 20.6318 | 24.9083 | 30.29 | 34.3972 | 38.5182
MaitlandIce Accretion2095RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2095 | 20.7014 | 25.0162 | 30.445 | 34.5893 | 38.745
MaitlandIce Accretion2100RCP4.5 | Maitland | Ice Accretion | RCP4.5 | 2100 | 20.771 | 25.1241 | 30.6 | 34.7814 | 38.9718
MaitlandIce Accretion2023RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2023 | 20.6249 | 24.5763 | 29.61 | 33.4593 | 37.3086
MaitlandIce Accretion2025RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2025 | 20.6945 | 24.6801 | 29.755 | 33.6345 | 37.5102
MaitlandIce Accretion2030RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2030 | 20.764 | 24.7838 | 29.9 | 33.8096 | 37.7118
MaitlandIce Accretion2035RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2035 | 20.8336 | 24.8875 | 30.045 | 33.9847 | 37.9134
MaitlandIce Accretion2040RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2040 | 20.9032 | 24.9913 | 30.19 | 34.1599 | 38.115
MaitlandIce Accretion2045RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2045 | 20.9728 | 25.0951 | 30.335 | 34.335 | 38.3166
MaitlandIce Accretion2050RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2050 | 20.9046 | 25.0544 | 30.318 | 34.3339 | 38.3368
MaitlandIce Accretion2055RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2055 | 20.7668 | 24.91 | 30.156 | 34.1576 | 38.1553
MaitlandIce Accretion2060RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2060 | 20.6291 | 24.7655 | 29.994 | 33.9814 | 37.9739
MaitlandIce Accretion2065RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2065 | 20.4913 | 24.6211 | 29.832 | 33.8051 | 37.7924
MaitlandIce Accretion2070RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2070 | 20.3535 | 24.4767 | 29.67 | 33.6288 | 37.611
MaitlandIce Accretion2075RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2075 | 20.4579 | 24.6385 | 29.9025 | 33.9169 | 37.9512
MaitlandIce Accretion2080RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2080 | 20.5623 | 24.8004 | 30.135 | 34.2051 | 38.2914
MaitlandIce Accretion2085RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2085 | 20.6666 | 24.9622 | 30.3675 | 34.4932 | 38.6316
MaitlandIce Accretion2090RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2090 | 20.6249 | 24.9913 | 30.49 | 34.6797 | 38.8836
MaitlandIce Accretion2095RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2095 | 20.4788 | 24.8585 | 30.38 | 34.578 | 38.7954
MaitlandIce Accretion2100RCP6.0 | Maitland | Ice Accretion | RCP6.0 | 2100 | 20.3326 | 24.7257 | 30.27 | 34.4763 | 38.7072
MaitlandIce Accretion2023RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2023 | 20.6249 | 24.5763 | 29.61 | 33.4593 | 37.3086
MaitlandIce Accretion2025RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2025 | 20.764 | 24.7838 | 29.9 | 33.8096 | 37.7118
MaitlandIce Accretion2030RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2030 | 20.9032 | 24.9913 | 30.19 | 34.1599 | 38.115
MaitlandIce Accretion2035RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2035 | 21.0424 | 25.1988 | 30.48 | 34.5102 | 38.5182
MaitlandIce Accretion2040RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2040 | 20.8128 | 24.9581 | 30.21 | 34.2164 | 38.2158
MaitlandIce Accretion2045RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2045 | 20.5831 | 24.7174 | 29.94 | 33.9226 | 37.9134
MaitlandIce Accretion2050RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2050 | 20.4927 | 24.6925 | 29.98 | 34.013 | 38.0646
MaitlandIce Accretion2055RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2055 | 20.6318 | 24.9083 | 30.29 | 34.3972 | 38.5182
MaitlandIce Accretion2060RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2060 | 20.6249 | 24.9913 | 30.49 | 34.6797 | 38.8836
MaitlandIce Accretion2065RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2065 | 20.4788 | 24.8585 | 30.38 | 34.578 | 38.7954
MaitlandIce Accretion2070RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2070 | 20.0473 | 24.4103 | 29.91 | 34.0808 | 38.2662
MaitlandIce Accretion2075RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2075 | 19.762 | 24.0949 | 29.55 | 33.6853 | 37.8252
MaitlandIce Accretion2080RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2080 | 19.4767 | 23.7795 | 29.19 | 33.2898 | 37.3842
MaitlandIce Accretion2085RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2085 | 18.7148 | 22.8831 | 28.14 | 32.1202 | 36.0801
MaitlandIce Accretion2090RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2090 | 17.9528 | 21.9867 | 27.09 | 30.9507 | 34.776
MaitlandIce Accretion2095RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2095 | 17.9528 | 21.9867 | 27.09 | 30.9507 | 34.776
MaitlandIce Accretion2100RCP8.5 | Maitland | Ice Accretion | RCP8.5 | 2100 | 17.9528 | 21.9867 | 27.09 | 30.9507 | 34.776
MaitlandWind2023RCP4.5 | Maitland | Wind | RCP4.5 | 2023 | 81.0025 | 87.3376 | 94.0323 | 100.7041 | 107.3771
MaitlandWind2025RCP4.5 | Maitland | Wind | RCP4.5 | 2025 | 81.0065 | 87.3333 | 94.0153 | 100.6759 | 107.3399
MaitlandWind2030RCP4.5 | Maitland | Wind | RCP4.5 | 2030 | 81.0105 | 87.329 | 93.9982 | 100.6477 | 107.3028
MaitlandWind2035RCP4.5 | Maitland | Wind | RCP4.5 | 2035 | 81.0146 | 87.3246 | 93.9812 | 100.6195 | 107.2657
MaitlandWind2040RCP4.5 | Maitland | Wind | RCP4.5 | 2040 | 81.0186 | 87.3203 | 93.9641 | 100.5913 | 107.2286
MaitlandWind2045RCP4.5 | Maitland | Wind | RCP4.5 | 2045 | 81.0226 | 87.316 | 93.9471 | 100.5631 | 107.1915
MaitlandWind2050RCP4.5 | Maitland | Wind | RCP4.5 | 2050 | 80.9447 | 87.1871 | 93.7514 | 100.314 | 106.8851
MaitlandWind2055RCP4.5 | Maitland | Wind | RCP4.5 | 2055 | 80.8628 | 87.0626 | 93.5729 | 100.0931 | 106.6158
MaitlandWind2060RCP4.5 | Maitland | Wind | RCP4.5 | 2060 | 80.7809 | 86.938 | 93.3943 | 99.8722 | 106.3465
MaitlandWind2065RCP4.5 | Maitland | Wind | RCP4.5 | 2065 | 80.699 | 86.8135 | 93.2158 | 99.6513 | 106.0773
MaitlandWind2070RCP4.5 | Maitland | Wind | RCP4.5 | 2070 | 80.6171 | 86.6889 | 93.0372 | 99.4304 | 105.808
MaitlandWind2075RCP4.5 | Maitland | Wind | RCP4.5 | 2075 | 80.5836 | 86.6457 | 92.9845 | 99.369 | 105.739
MaitlandWind2080RCP4.5 | Maitland | Wind | RCP4.5 | 2080 | 80.5501 | 86.6024 | 92.9318 | 99.3077 | 105.6701
MaitlandWind2085RCP4.5 | Maitland | Wind | RCP4.5 | 2085 | 80.5167 | 86.5592 | 92.8791 | 99.2463 | 105.6012
MaitlandWind2090RCP4.5 | Maitland | Wind | RCP4.5 | 2090 | 80.4832 | 86.5159 | 92.8264 | 99.1849 | 105.5323
MaitlandWind2095RCP4.5 | Maitland | Wind | RCP4.5 | 2095 | 80.4498 | 86.4727 | 92.7737 | 99.1236 | 105.4634
MaitlandWind2100RCP4.5 | Maitland | Wind | RCP4.5 | 2100 | 80.4163 | 86.4295 | 92.721 | 99.0622 | 105.3945
MaitlandWind2023RCP6.0 | Maitland | Wind | RCP6.0 | 2023 | 81.0025 | 87.3376 | 94.0323 | 100.7041 | 107.3771
MaitlandWind2025RCP6.0 | Maitland | Wind | RCP6.0 | 2025 | 81.0065 | 87.3333 | 94.0153 | 100.6759 | 107.3399
MaitlandWind2030RCP6.0 | Maitland | Wind | RCP6.0 | 2030 | 81.0105 | 87.329 | 93.9982 | 100.6477 | 107.3028
MaitlandWind2035RCP6.0 | Maitland | Wind | RCP6.0 | 2035 | 81.0146 | 87.3246 | 93.9812 | 100.6195 | 107.2657
MaitlandWind2040RCP6.0 | Maitland | Wind | RCP6.0 | 2040 | 81.0186 | 87.3203 | 93.9641 | 100.5913 | 107.2286
MaitlandWind2045RCP6.0 | Maitland | Wind | RCP6.0 | 2045 | 81.0226 | 87.316 | 93.9471 | 100.5631 | 107.1915
MaitlandWind2050RCP6.0 | Maitland | Wind | RCP6.0 | 2050 | 80.9447 | 87.1871 | 93.7514 | 100.314 | 106.8851
MaitlandWind2055RCP6.0 | Maitland | Wind | RCP6.0 | 2055 | 80.8628 | 87.0626 | 93.5729 | 100.0931 | 106.6158
MaitlandWind2060RCP6.0 | Maitland | Wind | RCP6.0 | 2060 | 80.7809 | 86.938 | 93.3943 | 99.8722 | 106.3465
MaitlandWind2065RCP6.0 | Maitland | Wind | RCP6.0 | 2065 | 80.699 | 86.8135 | 93.2158 | 99.6513 | 106.0773
MaitlandWind2070RCP6.0 | Maitland | Wind | RCP6.0 | 2070 | 80.6171 | 86.6889 | 93.0372 | 99.4304 | 105.808
MaitlandWind2075RCP6.0 | Maitland | Wind | RCP6.0 | 2075 | 80.5669 | 86.6241 | 92.9582 | 99.3383 | 105.7046
MaitlandWind2080RCP6.0 | Maitland | Wind | RCP6.0 | 2080 | 80.5167 | 86.5592 | 92.8791 | 99.2463 | 105.6012
MaitlandWind2085RCP6.0 | Maitland | Wind | RCP6.0 | 2085 | 80.4665 | 86.4943 | 92.8 | 99.1543 | 105.4979
MaitlandWind2090RCP6.0 | Maitland | Wind | RCP6.0 | 2090 | 80.3467 | 86.3343 | 92.5877 | 98.8964 | 105.193
MaitlandWind2095RCP6.0 | Maitland | Wind | RCP6.0 | 2095 | 80.2771 | 86.2392 | 92.4544 | 98.7305 | 104.9916
MaitlandWind2100RCP6.0 | Maitland | Wind | RCP6.0 | 2100 | 80.2075 | 86.144 | 92.3211 | 98.5647 | 104.7902
MaitlandWind2023RCP8.5 | Maitland | Wind | RCP8.5 | 2023 | 81.0025 | 87.3376 | 94.0323 | 100.7041 | 107.3771
MaitlandWind2025RCP8.5 | Maitland | Wind | RCP8.5 | 2025 | 81.0105 | 87.329 | 93.9982 | 100.6477 | 107.3028
MaitlandWind2030RCP8.5 | Maitland | Wind | RCP8.5 | 2030 | 81.0186 | 87.3203 | 93.9641 | 100.5913 | 107.2286
MaitlandWind2035RCP8.5 | Maitland | Wind | RCP8.5 | 2035 | 81.0266 | 87.3117 | 93.93 | 100.535 | 107.1544
MaitlandWind2040RCP8.5 | Maitland | Wind | RCP8.5 | 2040 | 80.8901 | 87.1041 | 93.6324 | 100.1668 | 106.7056
MaitlandWind2045RCP8.5 | Maitland | Wind | RCP8.5 | 2045 | 80.7536 | 86.8965 | 93.3348 | 99.7986 | 106.2568
MaitlandWind2050RCP8.5 | Maitland | Wind | RCP8.5 | 2050 | 80.5501 | 86.6024 | 92.9318 | 99.3077 | 105.6701
MaitlandWind2055RCP8.5 | Maitland | Wind | RCP8.5 | 2055 | 80.4832 | 86.5159 | 92.8264 | 99.1849 | 105.5323
MaitlandWind2060RCP8.5 | Maitland | Wind | RCP8.5 | 2060 | 80.3467 | 86.3343 | 92.5877 | 98.8964 | 105.193
MaitlandWind2065RCP8.5 | Maitland | Wind | RCP8.5 | 2065 | 80.2771 | 86.2392 | 92.4544 | 98.7305 | 104.9916
MaitlandWind2070RCP8.5 | Maitland | Wind | RCP8.5 | 2070 | 80.336 | 86.3141 | 92.5443 | 98.8333 | 105.1118
MaitlandWind2075RCP8.5 | Maitland | Wind | RCP8.5 | 2075 | 80.4645 | 86.4842 | 92.7675 | 99.102 | 105.4334
MaitlandWind2080RCP8.5 | Maitland | Wind | RCP8.5 | 2080 | 80.593 | 86.6543 | 92.9907 | 99.3707 | 105.755
MaitlandWind2085RCP8.5 | Maitland | Wind | RCP8.5 | 2085 | 80.5769 | 86.6543 | 93.0093 | 99.4055 | 105.8027
MaitlandWind2090RCP8.5 | Maitland | Wind | RCP8.5 | 2090 | 80.5608 | 86.6543 | 93.0279 | 99.4403 | 105.8504
MaitlandWind2095RCP8.5 | Maitland | Wind | RCP8.5 | 2095 | 80.5608 | 86.6543 | 93.0279 | 99.4403 | 105.8504
MaitlandWind2100RCP8.5 | Maitland | Wind | RCP8.5 | 2100 | 80.5608 | 86.6543 | 93.0279 | 99.4403 | 105.8504
MarkdaleIce Accretion2023RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2023 | 15.3852 | 18.3878 | 22.198 | 25.1335 | 28.0249
MarkdaleIce Accretion2025RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2025 | 15.3954 | 18.4122 | 22.2383 | 25.1832 | 28.0896
MarkdaleIce Accretion2030RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2030 | 15.4056 | 18.4365 | 22.2787 | 25.2329 | 28.1543
MarkdaleIce Accretion2035RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2035 | 15.4158 | 18.4609 | 22.319 | 25.2826 | 28.219
MarkdaleIce Accretion2040RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2040 | 15.426 | 18.4852 | 22.3593 | 25.3323 | 28.2836
MarkdaleIce Accretion2045RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2045 | 15.4362 | 18.5096 | 22.3997 | 25.3821 | 28.3483
MarkdaleIce Accretion2050RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2050 | 15.3913 | 18.4828 | 22.396 | 25.392 | 28.3742
MarkdaleIce Accretion2055RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2055 | 15.3362 | 18.4316 | 22.352 | 25.3522 | 28.3354
MarkdaleIce Accretion2060RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2060 | 15.2811 | 18.3805 | 22.308 | 25.3125 | 28.2966
MarkdaleIce Accretion2065RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2065 | 15.2259 | 18.3294 | 22.264 | 25.2727 | 28.2578
MarkdaleIce Accretion2070RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2070 | 15.1708 | 18.2783 | 22.22 | 25.2329 | 28.219
MarkdaleIce Accretion2075RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2075 | 15.1147 | 18.2387 | 22.198 | 25.2205 | 28.219
MarkdaleIce Accretion2080RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2080 | 15.0586 | 18.1991 | 22.176 | 25.208 | 28.219
MarkdaleIce Accretion2085RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2085 | 15.0024 | 18.1596 | 22.154 | 25.1956 | 28.219
MarkdaleIce Accretion2090RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2090 | 14.9463 | 18.12 | 22.132 | 25.1832 | 28.219
MarkdaleIce Accretion2095RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2095 | 14.8902 | 18.0804 | 22.11 | 25.1707 | 28.219
MarkdaleIce Accretion2100RCP4.5 | Markdale | Ice Accretion | RCP4.5 | 2100 | 14.834 | 18.0409 | 22.088 | 25.1583 | 28.219
MarkdaleIce Accretion2023RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2023 | 15.3852 | 18.3878 | 22.198 | 25.1335 | 28.0249
MarkdaleIce Accretion2025RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2025 | 15.3954 | 18.4122 | 22.2383 | 25.1832 | 28.0896
MarkdaleIce Accretion2030RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2030 | 15.4056 | 18.4365 | 22.2787 | 25.2329 | 28.1543
MarkdaleIce Accretion2035RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2035 | 15.4158 | 18.4609 | 22.319 | 25.2826 | 28.219
MarkdaleIce Accretion2040RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2040 | 15.426 | 18.4852 | 22.3593 | 25.3323 | 28.2836
MarkdaleIce Accretion2045RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2045 | 15.4362 | 18.5096 | 22.3997 | 25.3821 | 28.3483
MarkdaleIce Accretion2050RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2050 | 15.3913 | 18.4828 | 22.396 | 25.392 | 28.3742
MarkdaleIce Accretion2055RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2055 | 15.3362 | 18.4316 | 22.352 | 25.3522 | 28.3354
MarkdaleIce Accretion2060RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2060 | 15.2811 | 18.3805 | 22.308 | 25.3125 | 28.2966
MarkdaleIce Accretion2065RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2065 | 15.2259 | 18.3294 | 22.264 | 25.2727 | 28.2578
MarkdaleIce Accretion2070RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2070 | 15.1708 | 18.2783 | 22.22 | 25.2329 | 28.219
MarkdaleIce Accretion2075RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2075 | 15.0866 | 18.2189 | 22.187 | 25.2143 | 28.219
MarkdaleIce Accretion2080RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2080 | 15.0024 | 18.1596 | 22.154 | 25.1956 | 28.219
MarkdaleIce Accretion2085RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2085 | 14.9182 | 18.1002 | 22.121 | 25.177 | 28.219
MarkdaleIce Accretion2090RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2090 | 14.5738 | 17.767 | 21.7873 | 24.8434 | 27.8863
MarkdaleIce Accretion2095RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2095 | 14.3136 | 17.4931 | 21.4867 | 24.5285 | 27.5537
MarkdaleIce Accretion2100RCP6.0 | Markdale | Ice Accretion | RCP6.0 | 2100 | 14.0533 | 17.2192 | 21.186 | 24.2136 | 27.221
MarkdaleIce Accretion2023RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2023 | 15.3852 | 18.3878 | 22.198 | 25.1335 | 28.0249
MarkdaleIce Accretion2025RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2025 | 15.4056 | 18.4365 | 22.2787 | 25.2329 | 28.1543
MarkdaleIce Accretion2030RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2030 | 15.426 | 18.4852 | 22.3593 | 25.3323 | 28.2836
MarkdaleIce Accretion2035RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2035 | 15.4464 | 18.5339 | 22.44 | 25.4318 | 28.413
MarkdaleIce Accretion2040RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2040 | 15.3545 | 18.4487 | 22.3667 | 25.3655 | 28.3483
MarkdaleIce Accretion2045RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2045 | 15.2627 | 18.3635 | 22.2933 | 25.2992 | 28.2836
MarkdaleIce Accretion2050RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2050 | 15.0586 | 18.1991 | 22.176 | 25.208 | 28.219
MarkdaleIce Accretion2055RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2055 | 14.9463 | 18.12 | 22.132 | 25.1832 | 28.219
MarkdaleIce Accretion2060RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2060 | 14.5738 | 17.767 | 21.7873 | 24.8434 | 27.8863
MarkdaleIce Accretion2065RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2065 | 14.3136 | 17.4931 | 21.4867 | 24.5285 | 27.5537
MarkdaleIce Accretion2070RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2070 | 13.6655 | 16.787 | 20.702 | 23.6916 | 26.6574
MarkdaleIce Accretion2075RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2075 | 13.2777 | 16.3549 | 20.218 | 23.1695 | 26.0938
MarkdaleIce Accretion2080RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2080 | 12.8899 | 15.9227 | 19.734 | 22.6475 | 25.5301
MarkdaleIce Accretion2085RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2085 | 12.2316 | 15.1649 | 18.843 | 21.6406 | 24.4213
MarkdaleIce Accretion2090RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2090 | 11.5733 | 14.4071 | 17.952 | 20.6338 | 23.3125
MarkdaleIce Accretion2095RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2095 | 11.5733 | 14.4071 | 17.952 | 20.6338 | 23.3125
MarkdaleIce Accretion2100RCP8.5 | Markdale | Ice Accretion | RCP8.5 | 2100 | 11.5733 | 14.4071 | 17.952 | 20.6338 | 23.3125
MarkdaleWind2023RCP4.5 | Markdale | Wind | RCP4.5 | 2023 | 82.8943 | 89.1818 | 95.7696 | 102.3913 | 109.0022
MarkdaleWind2025RCP4.5 | Markdale | Wind | RCP4.5 | 2025 | 82.9703 | 89.2755 | 95.888 | 102.5283 | 109.1609
MarkdaleWind2030RCP4.5 | Markdale | Wind | RCP4.5 | 2030 | 83.0463 | 89.3693 | 96.0064 | 102.6652 | 109.3196
MarkdaleWind2035RCP4.5 | Markdale | Wind | RCP4.5 | 2035 | 83.1223 | 89.463 | 96.1248 | 102.8022 | 109.4783
MarkdaleWind2040RCP4.5 | Markdale | Wind | RCP4.5 | 2040 | 83.1983 | 89.5568 | 96.2432 | 102.9391 | 109.637
MarkdaleWind2045RCP4.5 | Markdale | Wind | RCP4.5 | 2045 | 83.2742 | 89.6505 | 96.3616 | 103.0761 | 109.7957
MarkdaleWind2050RCP4.5 | Markdale | Wind | RCP4.5 | 2050 | 83.3469 | 89.7353 | 96.4608 | 103.1884 | 109.9215
MarkdaleWind2055RCP4.5 | Markdale | Wind | RCP4.5 | 2055 | 83.3436 | 89.7264 | 96.4416 | 103.1638 | 109.8887
MarkdaleWind2060RCP4.5 | Markdale | Wind | RCP4.5 | 2060 | 83.3403 | 89.7175 | 96.4224 | 103.1391 | 109.8559
MarkdaleWind2065RCP4.5 | Markdale | Wind | RCP4.5 | 2065 | 83.337 | 89.7085 | 96.4032 | 103.1144 | 109.823
MarkdaleWind2070RCP4.5 | Markdale | Wind | RCP4.5 | 2070 | 83.3337 | 89.6996 | 96.384 | 103.0898 | 109.7902
MarkdaleWind2075RCP4.5 | Markdale | Wind | RCP4.5 | 2075 | 83.3516 | 89.719 | 96.4048 | 103.112 | 109.8139
MarkdaleWind2080RCP4.5 | Markdale | Wind | RCP4.5 | 2080 | 83.3696 | 89.7383 | 96.4256 | 103.1343 | 109.8376
MarkdaleWind2085RCP4.5 | Markdale | Wind | RCP4.5 | 2085 | 83.3875 | 89.7576 | 96.4464 | 103.1566 | 109.8613
MarkdaleWind2090RCP4.5 | Markdale | Wind | RCP4.5 | 2090 | 83.4055 | 89.777 | 96.4672 | 103.1788 | 109.8851
MarkdaleWind2095RCP4.5 | Markdale | Wind | RCP4.5 | 2095 | 83.4235 | 89.7963 | 96.488 | 103.2011 | 109.9088
MarkdaleWind2100RCP4.5 | Markdale | Wind | RCP4.5 | 2100 | 83.4414 | 89.8157 | 96.5088 | 103.2233 | 109.9325
MarkdaleWind2023RCP6.0 | Markdale | Wind | RCP6.0 | 2023 | 82.8943 | 89.1818 | 95.7696 | 102.3913 | 109.0022
MarkdaleWind2025RCP6.0 | Markdale | Wind | RCP6.0 | 2025 | 82.9703 | 89.2755 | 95.888 | 102.5283 | 109.1609
MarkdaleWind2030RCP6.0 | Markdale | Wind | RCP6.0 | 2030 | 83.0463 | 89.3693 | 96.0064 | 102.6652 | 109.3196
MarkdaleWind2035RCP6.0 | Markdale | Wind | RCP6.0 | 2035 | 83.1223 | 89.463 | 96.1248 | 102.8022 | 109.4783
MarkdaleWind2040RCP6.0 | Markdale | Wind | RCP6.0 | 2040 | 83.1983 | 89.5568 | 96.2432 | 102.9391 | 109.637
MarkdaleWind2045RCP6.0 | Markdale | Wind | RCP6.0 | 2045 | 83.2742 | 89.6505 | 96.3616 | 103.0761 | 109.7957
MarkdaleWind2050RCP6.0 | Markdale | Wind | RCP6.0 | 2050 | 83.3469 | 89.7353 | 96.4608 | 103.1884 | 109.9215
MarkdaleWind2055RCP6.0 | Markdale | Wind | RCP6.0 | 2055 | 83.3436 | 89.7264 | 96.4416 | 103.1638 | 109.8887
MarkdaleWind2060RCP6.0 | Markdale | Wind | RCP6.0 | 2060 | 83.3403 | 89.7175 | 96.4224 | 103.1391 | 109.8559
MarkdaleWind2065RCP6.0 | Markdale | Wind | RCP6.0 | 2065 | 83.337 | 89.7085 | 96.4032 | 103.1144 | 109.823
MarkdaleWind2070RCP6.0 | Markdale | Wind | RCP6.0 | 2070 | 83.3337 | 89.6996 | 96.384 | 103.0898 | 109.7902
MarkdaleWind2075RCP6.0 | Markdale | Wind | RCP6.0 | 2075 | 83.3606 | 89.7286 | 96.4152 | 103.1232 | 109.8258
MarkdaleWind2080RCP6.0 | Markdale | Wind | RCP6.0 | 2080 | 83.3875 | 89.7576 | 96.4464 | 103.1566 | 109.8613
MarkdaleWind2085RCP6.0 | Markdale | Wind | RCP6.0 | 2085 | 83.4145 | 89.7867 | 96.4776 | 103.1899 | 109.8969
MarkdaleWind2090RCP6.0 | Markdale | Wind | RCP6.0 | 2090 | 83.574 | 89.9764 | 96.704 | 103.4459 | 110.1805
MarkdaleWind2095RCP6.0 | Markdale | Wind | RCP6.0 | 2095 | 83.7067 | 90.1371 | 96.8992 | 103.6684 | 110.4286
MarkdaleWind2100RCP6.0 | Markdale | Wind | RCP6.0 | 2100 | 83.8393 | 90.2978 | 97.0944 | 103.891 | 110.6767
MarkdaleWind2023RCP8.5 | Markdale | Wind | RCP8.5 | 2023 | 82.8943 | 89.1818 | 95.7696 | 102.3913 | 109.0022
MarkdaleWind2025RCP8.5 | Markdale | Wind | RCP8.5 | 2025 | 83.0463 | 89.3693 | 96.0064 | 102.6652 | 109.3196
MarkdaleWind2030RCP8.5 | Markdale | Wind | RCP8.5 | 2030 | 83.1983 | 89.5568 | 96.2432 | 102.9391 | 109.637
MarkdaleWind2035RCP8.5 | Markdale | Wind | RCP8.5 | 2035 | 83.3502 | 89.7443 | 96.48 | 103.2131 | 109.9544
MarkdaleWind2040RCP8.5 | Markdale | Wind | RCP8.5 | 2040 | 83.3447 | 89.7294 | 96.448 | 103.172 | 109.8996
MarkdaleWind2045RCP8.5 | Markdale | Wind | RCP8.5 | 2045 | 83.3392 | 89.7145 | 96.416 | 103.1309 | 109.8449
MarkdaleWind2050RCP8.5 | Markdale | Wind | RCP8.5 | 2050 | 83.3696 | 89.7383 | 96.4256 | 103.1343 | 109.8376
MarkdaleWind2055RCP8.5 | Markdale | Wind | RCP8.5 | 2055 | 83.4055 | 89.777 | 96.4672 | 103.1788 | 109.8851
MarkdaleWind2060RCP8.5 | Markdale | Wind | RCP8.5 | 2060 | 83.574 | 89.9764 | 96.704 | 103.4459 | 110.1805
MarkdaleWind2065RCP8.5 | Markdale | Wind | RCP8.5 | 2065 | 83.7067 | 90.1371 | 96.8992 | 103.6684 | 110.4286
MarkdaleWind2070RCP8.5 | Markdale | Wind | RCP8.5 | 2070 | 83.9084 | 90.3811 | 97.1904 | 104.0006 | 110.8044
MarkdaleWind2075RCP8.5 | Markdale | Wind | RCP8.5 | 2075 | 83.9775 | 90.4644 | 97.2864 | 104.1101 | 110.932
MarkdaleWind2080RCP8.5 | Markdale | Wind | RCP8.5 | 2080 | 84.0465 | 90.5478 | 97.3824 | 104.2197 | 111.0597
MarkdaleWind2085RCP8.5 | Markdale | Wind | RCP8.5 | 2085 | 84.3657 | 90.9763 | 97.9536 | 104.9079 | 111.8641
MarkdaleWind2090RCP8.5 | Markdale | Wind | RCP8.5 | 2090 | 84.6848 | 91.4049 | 98.5248 | 105.5962 | 112.6685
MarkdaleWind2095RCP8.5 | Markdale | Wind | RCP8.5 | 2095 | 84.6848 | 91.4049 | 98.5248 | 105.5962 | 112.6685
MarkdaleWind2100RCP8.5 | Markdale | Wind | RCP8.5 | 2100 | 84.6848 | 91.4049 | 98.5248 | 105.5962 | 112.6685
MarkhamIce Accretion2023RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
MarkhamIce Accretion2025RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
MarkhamIce Accretion2030RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
MarkhamIce Accretion2035RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
MarkhamIce Accretion2040RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
MarkhamIce Accretion2045RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
MarkhamIce Accretion2050RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
MarkhamIce Accretion2055RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
MarkhamIce Accretion2060RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
MarkhamIce Accretion2065RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
MarkhamIce Accretion2070RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
MarkhamIce Accretion2075RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
MarkhamIce Accretion2080RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
MarkhamIce Accretion2085RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
MarkhamIce Accretion2090RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
MarkhamIce Accretion2095RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
MarkhamIce Accretion2100RCP4.5 | Markham | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
MarkhamIce Accretion2023RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
MarkhamIce Accretion2025RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
MarkhamIce Accretion2030RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
MarkhamIce Accretion2035RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
MarkhamIce Accretion2040RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
MarkhamIce Accretion2045RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
MarkhamIce Accretion2050RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
MarkhamIce Accretion2055RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
MarkhamIce Accretion2060RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
MarkhamIce Accretion2065RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
MarkhamIce Accretion2070RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
MarkhamIce Accretion2075RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
MarkhamIce Accretion2080RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
MarkhamIce Accretion2085RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
MarkhamIce Accretion2090RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
MarkhamIce Accretion2095RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
MarkhamIce Accretion2100RCP6.0 | Markham | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
MarkhamIce Accretion2023RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
MarkhamIce Accretion2025RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
MarkhamIce Accretion2030RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
MarkhamIce Accretion2035RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
MarkhamIce Accretion2040RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
MarkhamIce Accretion2045RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
MarkhamIce Accretion2050RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
MarkhamIce Accretion2055RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
MarkhamIce Accretion2060RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
MarkhamIce Accretion2065RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
MarkhamIce Accretion2070RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
MarkhamIce Accretion2075RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
MarkhamIce Accretion2080RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
MarkhamIce Accretion2085RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
MarkhamIce Accretion2090RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
MarkhamIce Accretion2095RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
MarkhamIce Accretion2100RCP8.5 | Markham | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
MarkhamWind2023RCP4.5 | Markham | Wind | RCP4.5 | 2023 | 82.2277 | 88.5267 | 95.152 | 101.7821 | 108.4083
MarkhamWind2025RCP4.5 | Markham | Wind | RCP4.5 | 2025 | 82.2427 | 88.5591 | 95.2043 | 101.8516 | 108.4949
MarkhamWind2030RCP4.5 | Markham | Wind | RCP4.5 | 2030 | 82.2578 | 88.5915 | 95.2565 | 101.9211 | 108.5816
MarkhamWind2035RCP4.5 | Markham | Wind | RCP4.5 | 2035 | 82.2728 | 88.6239 | 95.3088 | 101.9905 | 108.6682
MarkhamWind2040RCP4.5 | Markham | Wind | RCP4.5 | 2040 | 82.2879 | 88.6563 | 95.361 | 102.06 | 108.7549
MarkhamWind2045RCP4.5 | Markham | Wind | RCP4.5 | 2045 | 82.3029 | 88.6887 | 95.4132 | 102.1294 | 108.8415
MarkhamWind2050RCP4.5 | Markham | Wind | RCP4.5 | 2050 | 82.3983 | 88.8218 | 95.5928 | 102.3473 | 109.1014
MarkhamWind2055RCP4.5 | Markham | Wind | RCP4.5 | 2055 | 82.4787 | 88.9225 | 95.7201 | 102.4957 | 109.2747
MarkhamWind2060RCP4.5 | Markham | Wind | RCP4.5 | 2060 | 82.5591 | 89.0232 | 95.8474 | 102.6441 | 109.448
MarkhamWind2065RCP4.5 | Markham | Wind | RCP4.5 | 2065 | 82.6395 | 89.1239 | 95.9747 | 102.7925 | 109.6213
MarkhamWind2070RCP4.5 | Markham | Wind | RCP4.5 | 2070 | 82.7199 | 89.2247 | 96.102 | 102.941 | 109.7945
MarkhamWind2075RCP4.5 | Markham | Wind | RCP4.5 | 2075 | 82.8593 | 89.4043 | 96.3316 | 103.2137 | 110.1104
MarkhamWind2080RCP4.5 | Markham | Wind | RCP4.5 | 2080 | 82.9988 | 89.584 | 96.5612 | 103.4865 | 110.4263
MarkhamWind2085RCP4.5 | Markham | Wind | RCP4.5 | 2085 | 83.1382 | 89.7636 | 96.7908 | 103.7592 | 110.7422
MarkhamWind2090RCP4.5 | Markham | Wind | RCP4.5 | 2090 | 83.2777 | 89.9432 | 97.0203 | 104.032 | 111.058
MarkhamWind2095RCP4.5 | Markham | Wind | RCP4.5 | 2095 | 83.4172 | 90.1229 | 97.2499 | 104.3048 | 111.3739
MarkhamWind2100RCP4.5 | Markham | Wind | RCP4.5 | 2100 | 83.5566 | 90.3025 | 97.4795 | 104.5775 | 111.6898
MarkhamWind2023RCP6.0 | Markham | Wind | RCP6.0 | 2023 | 82.2277 | 88.5267 | 95.152 | 101.7821 | 108.4083
MarkhamWind2025RCP6.0 | Markham | Wind | RCP6.0 | 2025 | 82.2427 | 88.5591 | 95.2043 | 101.8516 | 108.4949
MarkhamWind2030RCP6.0 | Markham | Wind | RCP6.0 | 2030 | 82.2578 | 88.5915 | 95.2565 | 101.9211 | 108.5816
MarkhamWind2035RCP6.0 | Markham | Wind | RCP6.0 | 2035 | 82.2728 | 88.6239 | 95.3088 | 101.9905 | 108.6682
MarkhamWind2040RCP6.0 | Markham | Wind | RCP6.0 | 2040 | 82.2879 | 88.6563 | 95.361 | 102.06 | 108.7549
MarkhamWind2045RCP6.0 | Markham | Wind | RCP6.0 | 2045 | 82.3029 | 88.6887 | 95.4132 | 102.1294 | 108.8415
MarkhamWind2050RCP6.0 | Markham | Wind | RCP6.0 | 2050 | 82.3983 | 88.8218 | 95.5928 | 102.3473 | 109.1014
MarkhamWind2055RCP6.0 | Markham | Wind | RCP6.0 | 2055 | 82.4787 | 88.9225 | 95.7201 | 102.4957 | 109.2747
MarkhamWind2060RCP6.0 | Markham | Wind | RCP6.0 | 2060 | 82.5591 | 89.0232 | 95.8474 | 102.6441 | 109.448
MarkhamWind2065RCP6.0 | Markham | Wind | RCP6.0 | 2065 | 82.6395 | 89.1239 | 95.9747 | 102.7925 | 109.6213
MarkhamWind2070RCP6.0 | Markham | Wind | RCP6.0 | 2070 | 82.7199 | 89.2247 | 96.102 | 102.941 | 109.7945
MarkhamWind2075RCP6.0 | Markham | Wind | RCP6.0 | 2075 | 82.9291 | 89.4941 | 96.4464 | 103.3501 | 110.2684
MarkhamWind2080RCP6.0 | Markham | Wind | RCP6.0 | 2080 | 83.1382 | 89.7636 | 96.7908 | 103.7592 | 110.7422
MarkhamWind2085RCP6.0 | Markham | Wind | RCP6.0 | 2085 | 83.3474 | 90.0331 | 97.1351 | 104.1684 | 111.216
MarkhamWind2090RCP6.0 | Markham | Wind | RCP6.0 | 2090 | 83.9886 | 90.8326 | 98.135 | 105.3399 | 112.5634
MarkhamWind2095RCP6.0 | Markham | Wind | RCP6.0 | 2095 | 84.4207 | 91.3627 | 98.7905 | 106.1023 | 113.437
MarkhamWind2100RCP6.0 | Markham | Wind | RCP6.0 | 2100 | 84.8527 | 91.8928 | 99.446 | 106.8646 | 114.3107
MarkhamWind2023RCP8.5 | Markham | Wind | RCP8.5 | 2023 | 82.2277 | 88.5267 | 95.152 | 101.7821 | 108.4083
MarkhamWind2025RCP8.5 | Markham | Wind | RCP8.5 | 2025 | 82.2578 | 88.5915 | 95.2565 | 101.9211 | 108.5816
MarkhamWind2030RCP8.5 | Markham | Wind | RCP8.5 | 2030 | 82.2879 | 88.6563 | 95.361 | 102.06 | 108.7549
MarkhamWind2035RCP8.5 | Markham | Wind | RCP8.5 | 2035 | 82.3179 | 88.7211 | 95.4655 | 102.1989 | 108.9281
MarkhamWind2040RCP8.5 | Markham | Wind | RCP8.5 | 2040 | 82.4519 | 88.8889 | 95.6777 | 102.4463 | 109.2169
MarkhamWind2045RCP8.5 | Markham | Wind | RCP8.5 | 2045 | 82.5859 | 89.0568 | 95.8898 | 102.6936 | 109.5057
MarkhamWind2050RCP8.5 | Markham | Wind | RCP8.5 | 2050 | 82.9988 | 89.584 | 96.5612 | 103.4865 | 110.4263
MarkhamWind2055RCP8.5 | Markham | Wind | RCP8.5 | 2055 | 83.2777 | 89.9432 | 97.0203 | 104.032 | 111.058
MarkhamWind2060RCP8.5 | Markham | Wind | RCP8.5 | 2060 | 83.9886 | 90.8326 | 98.135 | 105.3399 | 112.5634
MarkhamWind2065RCP8.5 | Markham | Wind | RCP8.5 | 2065 | 84.4207 | 91.3627 | 98.7905 | 106.1023 | 113.437
MarkhamWind2070RCP8.5 | Markham | Wind | RCP8.5 | 2070 | 84.9812 | 92.0666 | 99.6772 | 107.1493 | 114.6428
MarkhamWind2075RCP8.5 | Markham | Wind | RCP8.5 | 2075 | 85.1097 | 92.2403 | 99.9083 | 107.4339 | 114.9749
MarkhamWind2080RCP8.5 | Markham | Wind | RCP8.5 | 2080 | 85.2382 | 92.4141 | 100.1395 | 107.7185 | 115.307
MarkhamWind2085RCP8.5 | Markham | Wind | RCP8.5 | 2085 | 85.513 | 92.8028 | 100.6715 | 108.3691 | 116.0814
MarkhamWind2090RCP8.5 | Markham | Wind | RCP8.5 | 2090 | 85.7878 | 93.1916 | 101.2035 | 109.0196 | 116.8557
MarkhamWind2095RCP8.5 | Markham | Wind | RCP8.5 | 2095 | 85.7878 | 93.1916 | 101.2035 | 109.0196 | 116.8557
MarkhamWind2100RCP8.5 | Markham | Wind | RCP8.5 | 2100 | 85.7878 | 93.1916 | 101.2035 | 109.0196 | 116.8557
MartinIce Accretion2023RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2023 | 10.5421 | 12.5745 | 15.15 | 17.1195 | 19.089
MartinIce Accretion2025RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2025 | 10.6482 | 12.7052 | 15.3125 | 17.3059 | 19.3
MartinIce Accretion2030RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2030 | 10.7543 | 12.8359 | 15.475 | 17.4924 | 19.5111
MartinIce Accretion2035RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2035 | 10.8604 | 12.9667 | 15.6375 | 17.6788 | 19.7221
MartinIce Accretion2040RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2040 | 10.9665 | 13.0974 | 15.8 | 17.8653 | 19.9332
MartinIce Accretion2045RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2045 | 11.0727 | 13.2281 | 15.9625 | 18.0517 | 20.1442
MartinIce Accretion2050RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2050 | 11.1475 | 13.319 | 16.071 | 18.1738 | 20.2797
MartinIce Accretion2055RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2055 | 11.1161 | 13.2792 | 16.017 | 18.1094 | 20.2041
MartinIce Accretion2060RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2060 | 11.0848 | 13.2393 | 15.963 | 18.045 | 20.1285
MartinIce Accretion2065RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2065 | 11.0535 | 13.1995 | 15.909 | 17.9806 | 20.0529
MartinIce Accretion2070RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2070 | 11.0222 | 13.1596 | 15.855 | 17.9161 | 19.9773
MartinIce Accretion2075RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2075 | 11.0553 | 13.197 | 15.9 | 17.967 | 20.034
MartinIce Accretion2080RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2080 | 11.0883 | 13.2343 | 15.945 | 18.0178 | 20.0907
MartinIce Accretion2085RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2085 | 11.1214 | 13.2717 | 15.99 | 18.0687 | 20.1474
MartinIce Accretion2090RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2090 | 11.1544 | 13.309 | 16.035 | 18.1195 | 20.2041
MartinIce Accretion2095RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2095 | 11.1875 | 13.3464 | 16.08 | 18.1704 | 20.2608
MartinIce Accretion2100RCP4.5 | Martin | Ice Accretion | RCP4.5 | 2100 | 11.2205 | 13.3837 | 16.125 | 18.2212 | 20.3175
MartinIce Accretion2023RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2023 | 10.5421 | 12.5745 | 15.15 | 17.1195 | 19.089
MartinIce Accretion2025RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2025 | 10.6482 | 12.7052 | 15.3125 | 17.3059 | 19.3
MartinIce Accretion2030RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2030 | 10.7543 | 12.8359 | 15.475 | 17.4924 | 19.5111
MartinIce Accretion2035RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2035 | 10.8604 | 12.9667 | 15.6375 | 17.6788 | 19.7221
MartinIce Accretion2040RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2040 | 10.9665 | 13.0974 | 15.8 | 17.8653 | 19.9332
MartinIce Accretion2045RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2045 | 11.0727 | 13.2281 | 15.9625 | 18.0517 | 20.1442
MartinIce Accretion2050RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2050 | 11.1475 | 13.319 | 16.071 | 18.1738 | 20.2797
MartinIce Accretion2055RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2055 | 11.1161 | 13.2792 | 16.017 | 18.1094 | 20.2041
MartinIce Accretion2060RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2060 | 11.0848 | 13.2393 | 15.963 | 18.045 | 20.1285
MartinIce Accretion2065RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2065 | 11.0535 | 13.1995 | 15.909 | 17.9806 | 20.0529
MartinIce Accretion2070RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2070 | 11.0222 | 13.1596 | 15.855 | 17.9161 | 19.9773
MartinIce Accretion2075RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2075 | 11.0718 | 13.2157 | 15.9225 | 17.9924 | 20.0623
MartinIce Accretion2080RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2080 | 11.1214 | 13.2717 | 15.99 | 18.0687 | 20.1474
MartinIce Accretion2085RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2085 | 11.1709 | 13.3277 | 16.0575 | 18.145 | 20.2325
MartinIce Accretion2090RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2090 | 11.1475 | 13.2924 | 16.015 | 18.0969 | 20.1789
MartinIce Accretion2095RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2095 | 11.0744 | 13.2011 | 15.905 | 17.9726 | 20.0403
MartinIce Accretion2100RCP6.0 | Martin | Ice Accretion | RCP6.0 | 2100 | 11.0013 | 13.1098 | 15.795 | 17.8483 | 19.9017
MartinIce Accretion2023RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2023 | 10.5421 | 12.5745 | 15.15 | 17.1195 | 19.089
MartinIce Accretion2025RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2025 | 10.7543 | 12.8359 | 15.475 | 17.4924 | 19.5111
MartinIce Accretion2030RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2030 | 10.9665 | 13.0974 | 15.8 | 17.8653 | 19.9332
MartinIce Accretion2035RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2035 | 11.1788 | 13.3588 | 16.125 | 18.2382 | 20.3553
MartinIce Accretion2040RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2040 | 11.1266 | 13.2924 | 16.035 | 18.1308 | 20.2293
MartinIce Accretion2045RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2045 | 11.0744 | 13.226 | 15.945 | 18.0235 | 20.1033
MartinIce Accretion2050RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2050 | 11.0883 | 13.2343 | 15.945 | 18.0178 | 20.0907
MartinIce Accretion2055RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2055 | 11.1544 | 13.309 | 16.035 | 18.1195 | 20.2041
MartinIce Accretion2060RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2060 | 11.1475 | 13.2924 | 16.015 | 18.0969 | 20.1789
MartinIce Accretion2065RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2065 | 11.0744 | 13.2011 | 15.905 | 17.9726 | 20.0403
MartinIce Accretion2070RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2070 | 11.0083 | 13.1306 | 15.835 | 17.8992 | 19.9647
MartinIce Accretion2075RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2075 | 11.0152 | 13.1513 | 15.875 | 17.9501 | 20.0277
MartinIce Accretion2080RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2080 | 11.0222 | 13.1721 | 15.915 | 18.0009 | 20.0907
MartinIce Accretion2085RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2085 | 10.7613 | 12.8795 | 15.5625 | 17.611 | 19.6654
MartinIce Accretion2090RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2090 | 10.5003 | 12.5869 | 15.21 | 17.2212 | 19.2402
MartinIce Accretion2095RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2095 | 10.5003 | 12.5869 | 15.21 | 17.2212 | 19.2402
MartinIce Accretion2100RCP8.5 | Martin | Ice Accretion | RCP8.5 | 2100 | 10.5003 | 12.5869 | 15.21 | 17.2212 | 19.2402
MartinWind2023RCP4.5 | Martin | Wind | RCP4.5 | 2023 | 72.4382 | 77.9794 | 83.7984 | 89.6373 | 95.4631
MartinWind2025RCP4.5 | Martin | Wind | RCP4.5 | 2025 | 72.5313 | 78.0927 | 83.9356 | 89.7946 | 95.6419
MartinWind2030RCP4.5 | Martin | Wind | RCP4.5 | 2030 | 72.6244 | 78.2059 | 84.0728 | 89.9519 | 95.8206
MartinWind2035RCP4.5 | Martin | Wind | RCP4.5 | 2035 | 72.7175 | 78.3192 | 84.21 | 90.1092 | 95.9994
MartinWind2040RCP4.5 | Martin | Wind | RCP4.5 | 2040 | 72.8106 | 78.4325 | 84.3472 | 90.2665 | 96.1782
MartinWind2045RCP4.5 | Martin | Wind | RCP4.5 | 2045 | 72.9036 | 78.5458 | 84.4844 | 90.4238 | 96.3569
MartinWind2050RCP4.5 | Martin | Wind | RCP4.5 | 2050 | 73.0591 | 78.7434 | 84.7325 | 90.7141 | 96.6927
MartinWind2055RCP4.5 | Martin | Wind | RCP4.5 | 2055 | 73.1215 | 78.8278 | 84.8434 | 90.8471 | 96.8497
MartinWind2060RCP4.5 | Martin | Wind | RCP4.5 | 2060 | 73.1839 | 78.9121 | 84.9542 | 90.9801 | 97.0068
MartinWind2065RCP4.5 | Martin | Wind | RCP4.5 | 2065 | 73.2462 | 78.9965 | 85.0651 | 91.1132 | 97.1638
MartinWind2070RCP4.5 | Martin | Wind | RCP4.5 | 2070 | 73.3086 | 79.0809 | 85.176 | 91.2462 | 97.3209
MartinWind2075RCP4.5 | Martin | Wind | RCP4.5 | 2075 | 73.467 | 79.2788 | 85.4238 | 91.5368 | 97.6545
MartinWind2080RCP4.5 | Martin | Wind | RCP4.5 | 2080 | 73.6253 | 79.4767 | 85.6716 | 91.8274 | 97.988
MartinWind2085RCP4.5 | Martin | Wind | RCP4.5 | 2085 | 73.7837 | 79.6746 | 85.9194 | 92.118 | 98.3216
MartinWind2090RCP4.5 | Martin | Wind | RCP4.5 | 2090 | 73.9421 | 79.8725 | 86.1672 | 92.4086 | 98.6551
MartinWind2095RCP4.5 | Martin | Wind | RCP4.5 | 2095 | 74.1004 | 80.0704 | 86.415 | 92.6992 | 98.9887
MartinWind2100RCP4.5 | Martin | Wind | RCP4.5 | 2100 | 74.2588 | 80.2683 | 86.6628 | 92.9898 | 99.3223
MartinWind2023RCP6.0 | Martin | Wind | RCP6.0 | 2023 | 72.4382 | 77.9794 | 83.7984 | 89.6373 | 95.4631
MartinWind2025RCP6.0 | Martin | Wind | RCP6.0 | 2025 | 72.5313 | 78.0927 | 83.9356 | 89.7946 | 95.6419
MartinWind2030RCP6.0 | Martin | Wind | RCP6.0 | 2030 | 72.6244 | 78.2059 | 84.0728 | 89.9519 | 95.8206
MartinWind2035RCP6.0 | Martin | Wind | RCP6.0 | 2035 | 72.7175 | 78.3192 | 84.21 | 90.1092 | 95.9994
MartinWind2040RCP6.0 | Martin | Wind | RCP6.0 | 2040 | 72.8106 | 78.4325 | 84.3472 | 90.2665 | 96.1782
MartinWind2045RCP6.0 | Martin | Wind | RCP6.0 | 2045 | 72.9036 | 78.5458 | 84.4844 | 90.4238 | 96.3569
MartinWind2050RCP6.0 | Martin | Wind | RCP6.0 | 2050 | 73.0591 | 78.7434 | 84.7325 | 90.7141 | 96.6927
MartinWind2055RCP6.0 | Martin | Wind | RCP6.0 | 2055 | 73.1215 | 78.8278 | 84.8434 | 90.8471 | 96.8497
MartinWind2060RCP6.0 | Martin | Wind | RCP6.0 | 2060 | 73.1839 | 78.9121 | 84.9542 | 90.9801 | 97.0068
MartinWind2065RCP6.0 | Martin | Wind | RCP6.0 | 2065 | 73.2462 | 78.9965 | 85.0651 | 91.1132 | 97.1638
MartinWind2070RCP6.0 | Martin | Wind | RCP6.0 | 2070 | 73.3086 | 79.0809 | 85.176 | 91.2462 | 97.3209
MartinWind2075RCP6.0 | Martin | Wind | RCP6.0 | 2075 | 73.5462 | 79.3777 | 85.5477 | 91.6821 | 97.8212
MartinWind2080RCP6.0 | Martin | Wind | RCP6.0 | 2080 | 73.7837 | 79.6746 | 85.9194 | 92.118 | 98.3216
MartinWind2085RCP6.0 | Martin | Wind | RCP6.0 | 2085 | 74.0213 | 79.9714 | 86.2911 | 92.5539 | 98.8219
MartinWind2090RCP6.0 | Martin | Wind | RCP6.0 | 2090 | 74.4836 | 80.5599 | 87.038 | 93.4333 | 99.8394
MartinWind2095RCP6.0 | Martin | Wind | RCP6.0 | 2095 | 74.7085 | 80.8516 | 87.4132 | 93.8767 | 100.3565
MartinWind2100RCP6.0 | Martin | Wind | RCP6.0 | 2100 | 74.9334 | 81.1432 | 87.7884 | 94.3201 | 100.8736
MartinWind2023RCP8.5 | Martin | Wind | RCP8.5 | 2023 | 72.4382 | 77.9794 | 83.7984 | 89.6373 | 95.4631
MartinWind2025RCP8.5 | Martin | Wind | RCP8.5 | 2025 | 72.6244 | 78.2059 | 84.0728 | 89.9519 | 95.8206
MartinWind2030RCP8.5 | Martin | Wind | RCP8.5 | 2030 | 72.8106 | 78.4325 | 84.3472 | 90.2665 | 96.1782
MartinWind2035RCP8.5 | Martin | Wind | RCP8.5 | 2035 | 72.9967 | 78.659 | 84.6216 | 90.5811 | 96.5357
MartinWind2040RCP8.5 | Martin | Wind | RCP8.5 | 2040 | 73.1007 | 78.7996 | 84.8064 | 90.8028 | 96.7974
MartinWind2045RCP8.5 | Martin | Wind | RCP8.5 | 2045 | 73.2047 | 78.9403 | 84.9912 | 91.0245 | 97.0591
MartinWind2050RCP8.5 | Martin | Wind | RCP8.5 | 2050 | 73.6253 | 79.4767 | 85.6716 | 91.8274 | 97.988
MartinWind2055RCP8.5 | Martin | Wind | RCP8.5 | 2055 | 73.9421 | 79.8725 | 86.1672 | 92.4086 | 98.6551
MartinWind2060RCP8.5 | Martin | Wind | RCP8.5 | 2060 | 74.4836 | 80.5599 | 87.038 | 93.4333 | 99.8394
MartinWind2065RCP8.5 | Martin | Wind | RCP8.5 | 2065 | 74.7085 | 80.8516 | 87.4132 | 93.8767 | 100.3565
MartinWind2070RCP8.5 | Martin | Wind | RCP8.5 | 2070 | 75.1195 | 81.3464 | 88.0152 | 94.5657 | 101.1385
MartinWind2075RCP8.5 | Martin | Wind | RCP8.5 | 2075 | 75.3057 | 81.5495 | 88.242 | 94.8114 | 101.4035
MartinWind2080RCP8.5 | Martin | Wind | RCP8.5 | 2080 | 75.4919 | 81.7526 | 88.4688 | 95.0571 | 101.6684
MartinWind2085RCP8.5 | Martin | Wind | RCP8.5 | 2085 | 75.4556 | 81.6901 | 88.3722 | 94.9358 | 101.5152
MartinWind2090RCP8.5 | Martin | Wind | RCP8.5 | 2090 | 75.4193 | 81.6276 | 88.2756 | 94.8144 | 101.362
MartinWind2095RCP8.5 | Martin | Wind | RCP8.5 | 2095 | 75.4193 | 81.6276 | 88.2756 | 94.8144 | 101.362
MartinWind2100RCP8.5 | Martin | Wind | RCP8.5 | 2100 | 75.4193 | 81.6276 | 88.2756 | 94.8144 | 101.362
MathesonIce Accretion2023RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2023 | 13.2475 | 15.77 | 18.962 | 21.4056 | 23.8682
MathesonIce Accretion2025RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2025 | 13.2563 | 15.7805 | 18.9747 | 21.4199 | 23.8841
MathesonIce Accretion2030RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2030 | 13.2651 | 15.791 | 18.9873 | 21.4342 | 23.9001
MathesonIce Accretion2035RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2035 | 13.274 | 15.8015 | 19 | 21.4485 | 23.9161
MathesonIce Accretion2040RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2040 | 13.2828 | 15.8121 | 19.0127 | 21.4628 | 23.932
MathesonIce Accretion2045RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2045 | 13.2916 | 15.8226 | 19.0253 | 21.4772 | 23.948
MathesonIce Accretion2050RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2050 | 13.4405 | 16.0065 | 19.2584 | 21.7448 | 24.2512
MathesonIce Accretion2055RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2055 | 13.5807 | 16.18 | 19.4788 | 21.9982 | 24.5385
MathesonIce Accretion2060RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2060 | 13.7208 | 16.3535 | 19.6992 | 22.2515 | 24.8258
MathesonIce Accretion2065RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2065 | 13.861 | 16.527 | 19.9196 | 22.5049 | 25.1131
MathesonIce Accretion2070RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2070 | 14.0011 | 16.7004 | 20.14 | 22.7582 | 25.4003
MathesonIce Accretion2075RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2075 | 14.0232 | 16.7346 | 20.1875 | 22.8155 | 25.4642
MathesonIce Accretion2080RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2080 | 14.0452 | 16.7688 | 20.235 | 22.8727 | 25.528
MathesonIce Accretion2085RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2085 | 14.0672 | 16.8029 | 20.2825 | 22.93 | 25.5919
MathesonIce Accretion2090RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2090 | 14.0893 | 16.8371 | 20.33 | 22.9872 | 25.6557
MathesonIce Accretion2095RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2095 | 14.1113 | 16.8713 | 20.3775 | 23.0445 | 25.7195
MathesonIce Accretion2100RCP4.5 | Matheson | Ice Accretion | RCP4.5 | 2100 | 14.1333 | 16.9054 | 20.425 | 23.1017 | 25.7834
MathesonIce Accretion2023RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2023 | 13.2475 | 15.77 | 18.962 | 21.4056 | 23.8682
MathesonIce Accretion2025RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2025 | 13.2563 | 15.7805 | 18.9747 | 21.4199 | 23.8841
MathesonIce Accretion2030RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2030 | 13.2651 | 15.791 | 18.9873 | 21.4342 | 23.9001
MathesonIce Accretion2035RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2035 | 13.274 | 15.8015 | 19 | 21.4485 | 23.9161
MathesonIce Accretion2040RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2040 | 13.2828 | 15.8121 | 19.0127 | 21.4628 | 23.932
MathesonIce Accretion2045RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2045 | 13.2916 | 15.8226 | 19.0253 | 21.4772 | 23.948
MathesonIce Accretion2050RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2050 | 13.4405 | 16.0065 | 19.2584 | 21.7448 | 24.2512
MathesonIce Accretion2055RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2055 | 13.5807 | 16.18 | 19.4788 | 21.9982 | 24.5385
MathesonIce Accretion2060RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2060 | 13.7208 | 16.3535 | 19.6992 | 22.2515 | 24.8258
MathesonIce Accretion2065RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2065 | 13.861 | 16.527 | 19.9196 | 22.5049 | 25.1131
MathesonIce Accretion2070RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2070 | 14.0011 | 16.7004 | 20.14 | 22.7582 | 25.4003
MathesonIce Accretion2075RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2075 | 14.0342 | 16.7517 | 20.2112 | 22.8441 | 25.4961
MathesonIce Accretion2080RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2080 | 14.0672 | 16.8029 | 20.2825 | 22.93 | 25.5919
MathesonIce Accretion2085RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2085 | 14.1003 | 16.8542 | 20.3538 | 23.0158 | 25.6876
MathesonIce Accretion2090RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2090 | 14.0452 | 16.8213 | 20.3427 | 23.023 | 25.7036
MathesonIce Accretion2095RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2095 | 13.957 | 16.7372 | 20.2603 | 22.9443 | 25.6238
MathesonIce Accretion2100RCP6.0 | Matheson | Ice Accretion | RCP6.0 | 2100 | 13.8689 | 16.6531 | 20.178 | 22.8655 | 25.544
MathesonIce Accretion2023RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2023 | 13.2475 | 15.77 | 18.962 | 21.4056 | 23.8682
MathesonIce Accretion2025RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2025 | 13.2651 | 15.791 | 18.9873 | 21.4342 | 23.9001
MathesonIce Accretion2030RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2030 | 13.2828 | 15.8121 | 19.0127 | 21.4628 | 23.932
MathesonIce Accretion2035RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2035 | 13.3004 | 15.8331 | 19.038 | 21.4915 | 23.9639
MathesonIce Accretion2040RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2040 | 13.534 | 16.1222 | 19.4053 | 21.9137 | 24.4427
MathesonIce Accretion2045RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2045 | 13.7675 | 16.4113 | 19.7727 | 22.336 | 24.9215
MathesonIce Accretion2050RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2050 | 14.0452 | 16.7688 | 20.235 | 22.8727 | 25.528
MathesonIce Accretion2055RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2055 | 14.0893 | 16.8371 | 20.33 | 22.9872 | 25.6557
MathesonIce Accretion2060RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2060 | 14.0452 | 16.8213 | 20.3427 | 23.023 | 25.7036
MathesonIce Accretion2065RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2065 | 13.957 | 16.7372 | 20.2603 | 22.9443 | 25.6238
MathesonIce Accretion2070RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2070 | 13.7147 | 16.4849 | 19.988 | 22.6652 | 25.3285
MathesonIce Accretion2075RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2075 | 13.5604 | 16.3167 | 19.798 | 22.4648 | 25.1131
MathesonIce Accretion2080RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2080 | 13.4062 | 16.1485 | 19.608 | 22.2644 | 24.8976
MathesonIce Accretion2085RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2085 | 13.1153 | 15.8252 | 19.247 | 21.8672 | 24.4667
MathesonIce Accretion2090RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2090 | 12.8244 | 15.5019 | 18.886 | 21.47 | 24.0358
MathesonIce Accretion2095RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2095 | 12.8244 | 15.5019 | 18.886 | 21.47 | 24.0358
MathesonIce Accretion2100RCP8.5 | Matheson | Ice Accretion | RCP8.5 | 2100 | 12.8244 | 15.5019 | 18.886 | 21.47 | 24.0358
MathesonWind2023RCP4.5 | Matheson | Wind | RCP4.5 | 2023 | 74.8016 | 80.5479 | 86.5848 | 92.6273 | 98.6773
MathesonWind2025RCP4.5 | Matheson | Wind | RCP4.5 | 2025 | 74.8288 | 80.5652 | 86.5891 | 92.6212 | 98.6609
MathesonWind2030RCP4.5 | Matheson | Wind | RCP4.5 | 2030 | 74.856 | 80.5825 | 86.5934 | 92.6151 | 98.6446
MathesonWind2035RCP4.5 | Matheson | Wind | RCP4.5 | 2035 | 74.8833 | 80.5998 | 86.5977 | 92.6089 | 98.6282
MathesonWind2040RCP4.5 | Matheson | Wind | RCP4.5 | 2040 | 74.9105 | 80.6172 | 86.602 | 92.6028 | 98.6119
MathesonWind2045RCP4.5 | Matheson | Wind | RCP4.5 | 2045 | 74.9377 | 80.6345 | 86.6063 | 92.5967 | 98.5956
MathesonWind2050RCP4.5 | Matheson | Wind | RCP4.5 | 2050 | 75.0258 | 80.727 | 86.7035 | 92.6991 | 98.7008
MathesonWind2055RCP4.5 | Matheson | Wind | RCP4.5 | 2055 | 75.0867 | 80.8022 | 86.7964 | 92.8077 | 98.8224
MathesonWind2060RCP4.5 | Matheson | Wind | RCP4.5 | 2060 | 75.1476 | 80.8774 | 86.8892 | 92.9163 | 98.9439
MathesonWind2065RCP4.5 | Matheson | Wind | RCP4.5 | 2065 | 75.2085 | 80.9526 | 86.9821 | 93.0249 | 99.0655
MathesonWind2070RCP4.5 | Matheson | Wind | RCP4.5 | 2070 | 75.2694 | 81.0277 | 87.075 | 93.1334 | 99.1871
MathesonWind2075RCP4.5 | Matheson | Wind | RCP4.5 | 2075 | 75.3152 | 81.0757 | 87.1252 | 93.1856 | 99.2426
MathesonWind2080RCP4.5 | Matheson | Wind | RCP4.5 | 2080 | 75.361 | 81.1237 | 87.1753 | 93.2377 | 99.2982
MathesonWind2085RCP4.5 | Matheson | Wind | RCP4.5 | 2085 | 75.4068 | 81.1717 | 87.2255 | 93.2899 | 99.3537
MathesonWind2090RCP4.5 | Matheson | Wind | RCP4.5 | 2090 | 75.4526 | 81.2197 | 87.2757 | 93.342 | 99.4093
MathesonWind2095RCP4.5 | Matheson | Wind | RCP4.5 | 2095 | 75.4984 | 81.2677 | 87.3258 | 93.3942 | 99.4648
MathesonWind2100RCP4.5 | Matheson | Wind | RCP4.5 | 2100 | 75.5442 | 81.3157 | 87.376 | 93.4463 | 99.5204
MathesonWind2023RCP6.0 | Matheson | Wind | RCP6.0 | 2023 | 74.8016 | 80.5479 | 86.5848 | 92.6273 | 98.6773
MathesonWind2025RCP6.0 | Matheson | Wind | RCP6.0 | 2025 | 74.8288 | 80.5652 | 86.5891 | 92.6212 | 98.6609
MathesonWind2030RCP6.0 | Matheson | Wind | RCP6.0 | 2030 | 74.856 | 80.5825 | 86.5934 | 92.6151 | 98.6446
MathesonWind2035RCP6.0 | Matheson | Wind | RCP6.0 | 2035 | 74.8833 | 80.5998 | 86.5977 | 92.6089 | 98.6282
MathesonWind2040RCP6.0 | Matheson | Wind | RCP6.0 | 2040 | 74.9105 | 80.6172 | 86.602 | 92.6028 | 98.6119
MathesonWind2045RCP6.0 | Matheson | Wind | RCP6.0 | 2045 | 74.9377 | 80.6345 | 86.6063 | 92.5967 | 98.5956
MathesonWind2050RCP6.0 | Matheson | Wind | RCP6.0 | 2050 | 75.0258 | 80.727 | 86.7035 | 92.6991 | 98.7008
MathesonWind2055RCP6.0 | Matheson | Wind | RCP6.0 | 2055 | 75.0867 | 80.8022 | 86.7964 | 92.8077 | 98.8224
MathesonWind2060RCP6.0 | Matheson | Wind | RCP6.0 | 2060 | 75.1476 | 80.8774 | 86.8892 | 92.9163 | 98.9439
MathesonWind2065RCP6.0 | Matheson | Wind | RCP6.0 | 2065 | 75.2085 | 80.9526 | 86.9821 | 93.0249 | 99.0655
MathesonWind2070RCP6.0 | Matheson | Wind | RCP6.0 | 2070 | 75.2694 | 81.0277 | 87.075 | 93.1334 | 99.1871
MathesonWind2075RCP6.0 | Matheson | Wind | RCP6.0 | 2075 | 75.3381 | 81.0997 | 87.1502 | 93.2117 | 99.2704
MathesonWind2080RCP6.0 | Matheson | Wind | RCP6.0 | 2080 | 75.4068 | 81.1717 | 87.2255 | 93.2899 | 99.3537
MathesonWind2085RCP6.0 | Matheson | Wind | RCP6.0 | 2085 | 75.4755 | 81.2437 | 87.3008 | 93.3681 | 99.4371
MathesonWind2090RCP6.0 | Matheson | Wind | RCP6.0 | 2090 | 75.7447 | 81.5449 | 87.6397 | 93.7438 | 99.8472
MathesonWind2095RCP6.0 | Matheson | Wind | RCP6.0 | 2095 | 75.9452 | 81.7742 | 87.9035 | 94.0414 | 100.174
MathesonWind2100RCP6.0 | Matheson | Wind | RCP6.0 | 2100 | 76.1457 | 82.0035 | 88.1672 | 94.3389 | 100.5008
MathesonWind2023RCP8.5 | Matheson | Wind | RCP8.5 | 2023 | 74.8016 | 80.5479 | 86.5848 | 92.6273 | 98.6773
MathesonWind2025RCP8.5 | Matheson | Wind | RCP8.5 | 2025 | 74.856 | 80.5825 | 86.5934 | 92.6151 | 98.6446
MathesonWind2030RCP8.5 | Matheson | Wind | RCP8.5 | 2030 | 74.9105 | 80.6172 | 86.602 | 92.6028 | 98.6119
MathesonWind2035RCP8.5 | Matheson | Wind | RCP8.5 | 2035 | 74.965 | 80.6518 | 86.6106 | 92.5905 | 98.5792
MathesonWind2040RCP8.5 | Matheson | Wind | RCP8.5 | 2040 | 75.0664 | 80.7771 | 86.7654 | 92.7715 | 98.7818
MathesonWind2045RCP8.5 | Matheson | Wind | RCP8.5 | 2045 | 75.1679 | 80.9024 | 86.9202 | 92.9525 | 98.9845
MathesonWind2050RCP8.5 | Matheson | Wind | RCP8.5 | 2050 | 75.361 | 81.1237 | 87.1753 | 93.2377 | 99.2982
MathesonWind2055RCP8.5 | Matheson | Wind | RCP8.5 | 2055 | 75.4526 | 81.2197 | 87.2757 | 93.342 | 99.4093
MathesonWind2060RCP8.5 | Matheson | Wind | RCP8.5 | 2060 | 75.7447 | 81.5449 | 87.6397 | 93.7438 | 99.8472
MathesonWind2065RCP8.5 | Matheson | Wind | RCP8.5 | 2065 | 75.9452 | 81.7742 | 87.9035 | 94.0414 | 100.174
MathesonWind2070RCP8.5 | Matheson | Wind | RCP8.5 | 2070 | 76.2521 | 82.1101 | 88.2704 | 94.4371 | 100.5988
MathesonWind2075RCP8.5 | Matheson | Wind | RCP8.5 | 2075 | 76.3586 | 82.2168 | 88.3736 | 94.5352 | 100.6969
MathesonWind2080RCP8.5 | Matheson | Wind | RCP8.5 | 2080 | 76.465 | 82.3234 | 88.4768 | 94.6334 | 100.7949
MathesonWind2085RCP8.5 | Matheson | Wind | RCP8.5 | 2085 | 76.5504 | 82.4274 | 88.6015 | 94.776 | 100.9567
MathesonWind2090RCP8.5 | Matheson | Wind | RCP8.5 | 2090 | 76.6358 | 82.5314 | 88.7262 | 94.9186 | 101.1185
MathesonWind2095RCP8.5 | Matheson | Wind | RCP8.5 | 2095 | 76.6358 | 82.5314 | 88.7262 | 94.9186 | 101.1185
MathesonWind2100RCP8.5 | Matheson | Wind | RCP8.5 | 2100 | 76.6358 | 82.5314 | 88.7262 | 94.9186 | 101.1185
MattawaIce Accretion2023RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2023 | 15.4165 | 18.4409 | 22.26 | 25.2013 | 28.127
MattawaIce Accretion2025RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2025 | 15.509 | 18.56 | 22.414 | 25.3792 | 28.3298
MattawaIce Accretion2030RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2030 | 15.6016 | 18.6791 | 22.568 | 25.5572 | 28.5327
MattawaIce Accretion2035RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2035 | 15.6941 | 18.7983 | 22.722 | 25.7352 | 28.7356
MattawaIce Accretion2040RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2040 | 15.7867 | 18.9174 | 22.876 | 25.9132 | 28.9384
MattawaIce Accretion2045RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2045 | 15.8792 | 19.0365 | 23.03 | 26.0911 | 29.1413
MattawaIce Accretion2050RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2050 | 16.0565 | 19.2741 | 23.3436 | 26.4589 | 29.5611
MattawaIce Accretion2055RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2055 | 16.1413 | 19.3926 | 23.5032 | 26.6488 | 29.7781
MattawaIce Accretion2060RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2060 | 16.226 | 19.5111 | 23.6628 | 26.8386 | 29.9951
MattawaIce Accretion2065RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2065 | 16.3108 | 19.6297 | 23.8224 | 27.0285 | 30.212
MattawaIce Accretion2070RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2070 | 16.3955 | 19.7482 | 23.982 | 27.2183 | 30.429
MattawaIce Accretion2075RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2075 | 16.3712 | 19.7249 | 23.9645 | 27.2025 | 30.4202
MattawaIce Accretion2080RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2080 | 16.3468 | 19.7017 | 23.947 | 27.1867 | 30.4114
MattawaIce Accretion2085RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2085 | 16.3225 | 19.6785 | 23.9295 | 27.1708 | 30.4025
MattawaIce Accretion2090RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2090 | 16.2981 | 19.6552 | 23.912 | 27.155 | 30.3937
MattawaIce Accretion2095RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2095 | 16.2738 | 19.632 | 23.8945 | 27.1392 | 30.3849
MattawaIce Accretion2100RCP4.5 | Mattawa | Ice Accretion | RCP4.5 | 2100 | 16.2494 | 19.6088 | 23.877 | 27.1234 | 30.3761
MattawaIce Accretion2023RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2023 | 15.4165 | 18.4409 | 22.26 | 25.2013 | 28.127
MattawaIce Accretion2025RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2025 | 15.509 | 18.56 | 22.414 | 25.3792 | 28.3298
MattawaIce Accretion2030RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2030 | 15.6016 | 18.6791 | 22.568 | 25.5572 | 28.5327
MattawaIce Accretion2035RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2035 | 15.6941 | 18.7983 | 22.722 | 25.7352 | 28.7356
MattawaIce Accretion2040RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2040 | 15.7867 | 18.9174 | 22.876 | 25.9132 | 28.9384
MattawaIce Accretion2045RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2045 | 15.8792 | 19.0365 | 23.03 | 26.0911 | 29.1413
MattawaIce Accretion2050RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2050 | 16.0565 | 19.2741 | 23.3436 | 26.4589 | 29.5611
MattawaIce Accretion2055RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2055 | 16.1413 | 19.3926 | 23.5032 | 26.6488 | 29.7781
MattawaIce Accretion2060RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2060 | 16.226 | 19.5111 | 23.6628 | 26.8386 | 29.9951
MattawaIce Accretion2065RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2065 | 16.3108 | 19.6297 | 23.8224 | 27.0285 | 30.212
MattawaIce Accretion2070RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2070 | 16.3955 | 19.7482 | 23.982 | 27.2183 | 30.429
MattawaIce Accretion2075RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2075 | 16.359 | 19.7133 | 23.9557 | 27.1946 | 30.4158
MattawaIce Accretion2080RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2080 | 16.3225 | 19.6785 | 23.9295 | 27.1708 | 30.4025
MattawaIce Accretion2085RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2085 | 16.2859 | 19.6436 | 23.9032 | 27.1471 | 30.3893
MattawaIce Accretion2090RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2090 | 16.2348 | 19.6146 | 23.898 | 27.1629 | 30.429
MattawaIce Accretion2095RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2095 | 16.2202 | 19.6204 | 23.919 | 27.2025 | 30.4819
MattawaIce Accretion2100RCP6.0 | Mattawa | Ice Accretion | RCP6.0 | 2100 | 16.2056 | 19.6262 | 23.94 | 27.242 | 30.5348
MattawaIce Accretion2023RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2023 | 15.4165 | 18.4409 | 22.26 | 25.2013 | 28.127
MattawaIce Accretion2025RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2025 | 15.6016 | 18.6791 | 22.568 | 25.5572 | 28.5327
MattawaIce Accretion2030RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2030 | 15.7867 | 18.9174 | 22.876 | 25.9132 | 28.9384
MattawaIce Accretion2035RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2035 | 15.9718 | 19.1556 | 23.184 | 26.2691 | 29.3441
MattawaIce Accretion2040RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2040 | 16.113 | 19.3531 | 23.45 | 26.5855 | 29.7058
MattawaIce Accretion2045RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2045 | 16.2543 | 19.5507 | 23.716 | 26.9019 | 30.0674
MattawaIce Accretion2050RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2050 | 16.3468 | 19.7017 | 23.947 | 27.1867 | 30.4114
MattawaIce Accretion2055RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2055 | 16.2981 | 19.6552 | 23.912 | 27.155 | 30.3937
MattawaIce Accretion2060RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2060 | 16.2348 | 19.6146 | 23.898 | 27.1629 | 30.429
MattawaIce Accretion2065RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2065 | 16.2202 | 19.6204 | 23.919 | 27.2025 | 30.4819
MattawaIce Accretion2070RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2070 | 15.9328 | 19.3008 | 23.555 | 26.8149 | 30.0586
MattawaIce Accretion2075RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2075 | 15.66 | 18.9755 | 23.17 | 26.3878 | 29.5823
MattawaIce Accretion2080RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2080 | 15.3872 | 18.6501 | 22.785 | 25.9606 | 29.106
MattawaIce Accretion2085RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2085 | 15.2192 | 18.4932 | 22.638 | 25.8064 | 28.9605
MattawaIce Accretion2090RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2090 | 15.0512 | 18.3364 | 22.491 | 25.6521 | 28.8149
MattawaIce Accretion2095RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2095 | 15.0512 | 18.3364 | 22.491 | 25.6521 | 28.8149
MattawaIce Accretion2100RCP8.5 | Mattawa | Ice Accretion | RCP8.5 | 2100 | 15.0512 | 18.3364 | 22.491 | 25.6521 | 28.8149
MattawaWind2023RCP4.5 | Mattawa | Wind | RCP4.5 | 2023 | 75.1729 | 81.0037 | 87.161 | 93.2991 | 99.442
MattawaWind2025RCP4.5 | Mattawa | Wind | RCP4.5 | 2025 | 75.2088 | 81.0437 | 87.2011 | 93.342 | 99.4877
MattawaWind2030RCP4.5 | Mattawa | Wind | RCP4.5 | 2030 | 75.2447 | 81.0837 | 87.2413 | 93.385 | 99.5335
MattawaWind2035RCP4.5 | Mattawa | Wind | RCP4.5 | 2035 | 75.2806 | 81.1237 | 87.2814 | 93.4279 | 99.5792
MattawaWind2040RCP4.5 | Mattawa | Wind | RCP4.5 | 2040 | 75.3164 | 81.1637 | 87.3215 | 93.4708 | 99.625
MattawaWind2045RCP4.5 | Mattawa | Wind | RCP4.5 | 2045 | 75.3523 | 81.2037 | 87.3617 | 93.5138 | 99.6707
MattawaWind2050RCP4.5 | Mattawa | Wind | RCP4.5 | 2050 | 75.3422 | 81.1813 | 87.321 | 93.461 | 99.6028
MattawaWind2055RCP4.5 | Mattawa | Wind | RCP4.5 | 2055 | 75.2962 | 81.1189 | 87.2401 | 93.3653 | 99.489
MattawaWind2060RCP4.5 | Mattawa | Wind | RCP4.5 | 2060 | 75.2501 | 81.0565 | 87.1593 | 93.2696 | 99.3753
MattawaWind2065RCP4.5 | Mattawa | Wind | RCP4.5 | 2065 | 75.2041 | 80.9941 | 87.0784 | 93.1739 | 99.2616
MattawaWind2070RCP4.5 | Mattawa | Wind | RCP4.5 | 2070 | 75.158 | 80.9318 | 86.9976 | 93.0782 | 99.1479
MattawaWind2075RCP4.5 | Mattawa | Wind | RCP4.5 | 2075 | 75.2385 | 81.0304 | 87.118 | 93.2163 | 99.3047
MattawaWind2080RCP4.5 | Mattawa | Wind | RCP4.5 | 2080 | 75.3189 | 81.129 | 87.2384 | 93.3543 | 99.4616
MattawaWind2085RCP4.5 | Mattawa | Wind | RCP4.5 | 2085 | 75.3994 | 81.2277 | 87.3588 | 93.4923 | 99.6184
MattawaWind2090RCP4.5 | Mattawa | Wind | RCP4.5 | 2090 | 75.4798 | 81.3263 | 87.4792 | 93.6304 | 99.7753
MattawaWind2095RCP4.5 | Mattawa | Wind | RCP4.5 | 2095 | 75.5603 | 81.425 | 87.5996 | 93.7684 | 99.9322
MattawaWind2100RCP4.5 | Mattawa | Wind | RCP4.5 | 2100 | 75.6407 | 81.5236 | 87.72 | 93.9064 | 100.089
MattawaWind2023RCP6.0 | Mattawa | Wind | RCP6.0 | 2023 | 75.1729 | 81.0037 | 87.161 | 93.2991 | 99.442
MattawaWind2025RCP6.0 | Mattawa | Wind | RCP6.0 | 2025 | 75.2088 | 81.0437 | 87.2011 | 93.342 | 99.4877
MattawaWind2030RCP6.0 | Mattawa | Wind | RCP6.0 | 2030 | 75.2447 | 81.0837 | 87.2413 | 93.385 | 99.5335
MattawaWind2035RCP6.0 | Mattawa | Wind | RCP6.0 | 2035 | 75.2806 | 81.1237 | 87.2814 | 93.4279 | 99.5792
MattawaWind2040RCP6.0 | Mattawa | Wind | RCP6.0 | 2040 | 75.3164 | 81.1637 | 87.3215 | 93.4708 | 99.625
MattawaWind2045RCP6.0 | Mattawa | Wind | RCP6.0 | 2045 | 75.3523 | 81.2037 | 87.3617 | 93.5138 | 99.6707
MattawaWind2050RCP6.0 | Mattawa | Wind | RCP6.0 | 2050 | 75.3422 | 81.1813 | 87.321 | 93.461 | 99.6028
MattawaWind2055RCP6.0 | Mattawa | Wind | RCP6.0 | 2055 | 75.2962 | 81.1189 | 87.2401 | 93.3653 | 99.489
MattawaWind2060RCP6.0 | Mattawa | Wind | RCP6.0 | 2060 | 75.2501 | 81.0565 | 87.1593 | 93.2696 | 99.3753
MattawaWind2065RCP6.0 | Mattawa | Wind | RCP6.0 | 2065 | 75.2041 | 80.9941 | 87.0784 | 93.1739 | 99.2616
MattawaWind2070RCP6.0 | Mattawa | Wind | RCP6.0 | 2070 | 75.158 | 80.9318 | 86.9976 | 93.0782 | 99.1479
MattawaWind2075RCP6.0 | Mattawa | Wind | RCP6.0 | 2075 | 75.2787 | 81.0797 | 87.1782 | 93.2853 | 99.3831
MattawaWind2080RCP6.0 | Mattawa | Wind | RCP6.0 | 2080 | 75.3994 | 81.2277 | 87.3588 | 93.4923 | 99.6184
MattawaWind2085RCP6.0 | Mattawa | Wind | RCP6.0 | 2085 | 75.52 | 81.3757 | 87.5394 | 93.6994 | 99.8537
MattawaWind2090RCP6.0 | Mattawa | Wind | RCP6.0 | 2090 | 75.6135 | 81.4943 | 87.6913 | 93.8788 | 100.0629
MattawaWind2095RCP6.0 | Mattawa | Wind | RCP6.0 | 2095 | 75.5863 | 81.465 | 87.6627 | 93.8512 | 100.0367
MattawaWind2100RCP6.0 | Mattawa | Wind | RCP6.0 | 2100 | 75.559 | 81.4356 | 87.634 | 93.8236 | 100.0106
MattawaWind2023RCP8.5 | Mattawa | Wind | RCP8.5 | 2023 | 75.1729 | 81.0037 | 87.161 | 93.2991 | 99.442
MattawaWind2025RCP8.5 | Mattawa | Wind | RCP8.5 | 2025 | 75.2447 | 81.0837 | 87.2413 | 93.385 | 99.5335
MattawaWind2030RCP8.5 | Mattawa | Wind | RCP8.5 | 2030 | 75.3164 | 81.1637 | 87.3215 | 93.4708 | 99.625
MattawaWind2035RCP8.5 | Mattawa | Wind | RCP8.5 | 2035 | 75.3882 | 81.2437 | 87.4018 | 93.5567 | 99.7165
MattawaWind2040RCP8.5 | Mattawa | Wind | RCP8.5 | 2040 | 75.3115 | 81.1397 | 87.2671 | 93.3972 | 99.5269
MattawaWind2045RCP8.5 | Mattawa | Wind | RCP8.5 | 2045 | 75.2348 | 81.0357 | 87.1323 | 93.2377 | 99.3374
MattawaWind2050RCP8.5 | Mattawa | Wind | RCP8.5 | 2050 | 75.3189 | 81.129 | 87.2384 | 93.3543 | 99.4616
MattawaWind2055RCP8.5 | Mattawa | Wind | RCP8.5 | 2055 | 75.4798 | 81.3263 | 87.4792 | 93.6304 | 99.7753
MattawaWind2060RCP8.5 | Mattawa | Wind | RCP8.5 | 2060 | 75.6135 | 81.4943 | 87.6913 | 93.8788 | 100.0629
MattawaWind2065RCP8.5 | Mattawa | Wind | RCP8.5 | 2065 | 75.5863 | 81.465 | 87.6627 | 93.8512 | 100.0367
MattawaWind2070RCP8.5 | Mattawa | Wind | RCP8.5 | 2070 | 75.7595 | 81.6676 | 87.8977 | 94.115 | 100.3341
MattawaWind2075RCP8.5 | Mattawa | Wind | RCP8.5 | 2075 | 75.96 | 81.8995 | 88.1615 | 94.4064 | 100.6577
MattawaWind2080RCP8.5 | Mattawa | Wind | RCP8.5 | 2080 | 76.1605 | 82.1315 | 88.4252 | 94.6978 | 100.9812
MattawaWind2085RCP8.5 | Mattawa | Wind | RCP8.5 | 2085 | 76.1828 | 82.1395 | 88.4166 | 94.6748 | 100.942
MattawaWind2090RCP8.5 | Mattawa | Wind | RCP8.5 | 2090 | 76.2051 | 82.1475 | 88.408 | 94.6518 | 100.9028
MattawaWind2095RCP8.5 | Mattawa | Wind | RCP8.5 | 2095 | 76.2051 | 82.1475 | 88.408 | 94.6518 | 100.9028
MattawaWind2100RCP8.5 | Mattawa | Wind | RCP8.5 | 2100 | 76.2051 | 82.1475 | 88.408 | 94.6518 | 100.9028
MidlandIce Accretion2023RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2023 | 13.6525 | 16.2846 | 19.62 | 22.1706 | 24.7464
MidlandIce Accretion2025RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2025 | 13.6363 | 16.2735 | 19.6133 | 22.1706 | 24.7464
MidlandIce Accretion2030RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2030 | 13.62 | 16.2625 | 19.6067 | 22.1706 | 24.7464
MidlandIce Accretion2035RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2035 | 13.6038 | 16.2514 | 19.6 | 22.1706 | 24.7464
MidlandIce Accretion2040RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2040 | 13.5876 | 16.2403 | 19.5933 | 22.1706 | 24.7464
MidlandIce Accretion2045RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2045 | 13.5713 | 16.2293 | 19.5867 | 22.1706 | 24.7464
MidlandIce Accretion2050RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2050 | 13.5523 | 16.2282 | 19.612 | 22.2113 | 24.8018
MidlandIce Accretion2055RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2055 | 13.5495 | 16.2381 | 19.644 | 22.252 | 24.8573
MidlandIce Accretion2060RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2060 | 13.5467 | 16.2481 | 19.676 | 22.2926 | 24.9127
MidlandIce Accretion2065RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2065 | 13.5439 | 16.258 | 19.708 | 22.3333 | 24.9682
MidlandIce Accretion2070RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2070 | 13.5412 | 16.268 | 19.74 | 22.374 | 25.0236
MidlandIce Accretion2075RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2075 | 13.5806 | 16.3316 | 19.83 | 22.4832 | 25.1538
MidlandIce Accretion2080RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2080 | 13.62 | 16.3953 | 19.92 | 22.5925 | 25.284
MidlandIce Accretion2085RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2085 | 13.6595 | 16.4589 | 20.01 | 22.7017 | 25.4142
MidlandIce Accretion2090RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2090 | 13.6989 | 16.5225 | 20.1 | 22.8109 | 25.5444
MidlandIce Accretion2095RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2095 | 13.7383 | 16.5862 | 20.19 | 22.9202 | 25.6746
MidlandIce Accretion2100RCP4.5 | Midland | Ice Accretion | RCP4.5 | 2100 | 13.7778 | 16.6498 | 20.28 | 23.0294 | 25.8048
MidlandIce Accretion2023RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2023 | 13.6525 | 16.2846 | 19.62 | 22.1706 | 24.7464
MidlandIce Accretion2025RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2025 | 13.6363 | 16.2735 | 19.6133 | 22.1706 | 24.7464
MidlandIce Accretion2030RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2030 | 13.62 | 16.2625 | 19.6067 | 22.1706 | 24.7464
MidlandIce Accretion2035RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2035 | 13.6038 | 16.2514 | 19.6 | 22.1706 | 24.7464
MidlandIce Accretion2040RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2040 | 13.5876 | 16.2403 | 19.5933 | 22.1706 | 24.7464
MidlandIce Accretion2045RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2045 | 13.5713 | 16.2293 | 19.5867 | 22.1706 | 24.7464
MidlandIce Accretion2050RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2050 | 13.5523 | 16.2282 | 19.612 | 22.2113 | 24.8018
MidlandIce Accretion2055RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2055 | 13.5495 | 16.2381 | 19.644 | 22.252 | 24.8573
MidlandIce Accretion2060RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2060 | 13.5467 | 16.2481 | 19.676 | 22.2926 | 24.9127
MidlandIce Accretion2065RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2065 | 13.5439 | 16.258 | 19.708 | 22.3333 | 24.9682
MidlandIce Accretion2070RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2070 | 13.5412 | 16.268 | 19.74 | 22.374 | 25.0236
MidlandIce Accretion2075RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2075 | 13.6003 | 16.3634 | 19.875 | 22.5378 | 25.2189
MidlandIce Accretion2080RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2080 | 13.6595 | 16.4589 | 20.01 | 22.7017 | 25.4142
MidlandIce Accretion2085RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2085 | 13.7186 | 16.5543 | 20.145 | 22.8655 | 25.6095
MidlandIce Accretion2090RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2090 | 13.7546 | 16.6609 | 20.3333 | 23.1198 | 25.9224
MidlandIce Accretion2095RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2095 | 13.7314 | 16.6719 | 20.3867 | 23.2102 | 26.04
MidlandIce Accretion2100RCP6.0 | Midland | Ice Accretion | RCP6.0 | 2100 | 13.7082 | 16.683 | 20.44 | 23.3006 | 26.1576
MidlandIce Accretion2023RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2023 | 13.6525 | 16.2846 | 19.62 | 22.1706 | 24.7464
MidlandIce Accretion2025RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2025 | 13.62 | 16.2625 | 19.6067 | 22.1706 | 24.7464
MidlandIce Accretion2030RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2030 | 13.5876 | 16.2403 | 19.5933 | 22.1706 | 24.7464
MidlandIce Accretion2035RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2035 | 13.5551 | 16.2182 | 19.58 | 22.1706 | 24.7464
MidlandIce Accretion2040RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2040 | 13.5504 | 16.2348 | 19.6333 | 22.2384 | 24.8388
MidlandIce Accretion2045RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2045 | 13.5458 | 16.2514 | 19.6867 | 22.3062 | 24.9312
MidlandIce Accretion2050RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2050 | 13.62 | 16.3953 | 19.92 | 22.5925 | 25.284
MidlandIce Accretion2055RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2055 | 13.6989 | 16.5225 | 20.1 | 22.8109 | 25.5444
MidlandIce Accretion2060RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2060 | 13.7546 | 16.6609 | 20.3333 | 23.1198 | 25.9224
MidlandIce Accretion2065RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2065 | 13.7314 | 16.6719 | 20.3867 | 23.2102 | 26.04
MidlandIce Accretion2070RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2070 | 13.4577 | 16.4174 | 20.1533 | 22.9917 | 25.83
MidlandIce Accretion2075RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2075 | 13.2072 | 16.1518 | 19.8667 | 22.6829 | 25.5024
MidlandIce Accretion2080RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2080 | 12.9567 | 15.8862 | 19.58 | 22.374 | 25.1748
MidlandIce Accretion2085RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2085 | 12.4348 | 15.2969 | 18.9 | 21.6282 | 24.3558
MidlandIce Accretion2090RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2090 | 11.9129 | 14.7076 | 18.22 | 20.8824 | 23.5368
MidlandIce Accretion2095RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2095 | 11.9129 | 14.7076 | 18.22 | 20.8824 | 23.5368
MidlandIce Accretion2100RCP8.5 | Midland | Ice Accretion | RCP8.5 | 2100 | 11.9129 | 14.7076 | 18.22 | 20.8824 | 23.5368
MidlandWind2023RCP4.5 | Midland | Wind | RCP4.5 | 2023 | 78.2108 | 84.2692 | 90.657 | 97.0319 | 103.4105
MidlandWind2025RCP4.5 | Midland | Wind | RCP4.5 | 2025 | 78.2911 | 84.3654 | 90.771 | 97.1619 | 103.5559
MidlandWind2030RCP4.5 | Midland | Wind | RCP4.5 | 2030 | 78.3714 | 84.4617 | 90.885 | 97.2919 | 103.7012
MidlandWind2035RCP4.5 | Midland | Wind | RCP4.5 | 2035 | 78.4517 | 84.5579 | 90.999 | 97.4219 | 103.8466
MidlandWind2040RCP4.5 | Midland | Wind | RCP4.5 | 2040 | 78.532 | 84.6542 | 91.113 | 97.5519 | 103.9919
MidlandWind2045RCP4.5 | Midland | Wind | RCP4.5 | 2045 | 78.6123 | 84.7504 | 91.227 | 97.6819 | 104.1373
MidlandWind2050RCP4.5 | Midland | Wind | RCP4.5 | 2050 | 78.8045 | 84.9806 | 91.503 | 97.9987 | 104.496
MidlandWind2055RCP4.5 | Midland | Wind | RCP4.5 | 2055 | 78.9164 | 85.1145 | 91.665 | 98.1856 | 104.7095
MidlandWind2060RCP4.5 | Midland | Wind | RCP4.5 | 2060 | 79.0283 | 85.2485 | 91.827 | 98.3724 | 104.9229
MidlandWind2065RCP4.5 | Midland | Wind | RCP4.5 | 2065 | 79.1402 | 85.3824 | 91.989 | 98.5592 | 105.1363
MidlandWind2070RCP4.5 | Midland | Wind | RCP4.5 | 2070 | 79.2521 | 85.5163 | 92.151 | 98.746 | 105.3497
MidlandWind2075RCP4.5 | Midland | Wind | RCP4.5 | 2075 | 79.2871 | 85.5665 | 92.2215 | 98.8327 | 105.4523
MidlandWind2080RCP4.5 | Midland | Wind | RCP4.5 | 2080 | 79.3221 | 85.6167 | 92.292 | 98.9194 | 105.5549
MidlandWind2085RCP4.5 | Midland | Wind | RCP4.5 | 2085 | 79.3571 | 85.667 | 92.3625 | 99.006 | 105.6575
MidlandWind2090RCP4.5 | Midland | Wind | RCP4.5 | 2090 | 79.392 | 85.7172 | 92.433 | 99.0927 | 105.7601
MidlandWind2095RCP4.5 | Midland | Wind | RCP4.5 | 2095 | 79.427 | 85.7674 | 92.5035 | 99.1794 | 105.8627
MidlandWind2100RCP4.5 | Midland | Wind | RCP4.5 | 2100 | 79.462 | 85.8176 | 92.574 | 99.266 | 105.9653
MidlandWind2023RCP6.0 | Midland | Wind | RCP6.0 | 2023 | 78.2108 | 84.2692 | 90.657 | 97.0319 | 103.4105
MidlandWind2025RCP6.0 | Midland | Wind | RCP6.0 | 2025 | 78.2911 | 84.3654 | 90.771 | 97.1619 | 103.5559
MidlandWind2030RCP6.0 | Midland | Wind | RCP6.0 | 2030 | 78.3714 | 84.4617 | 90.885 | 97.2919 | 103.7012
MidlandWind2035RCP6.0 | Midland | Wind | RCP6.0 | 2035 | 78.4517 | 84.5579 | 90.999 | 97.4219 | 103.8466
MidlandWind2040RCP6.0 | Midland | Wind | RCP6.0 | 2040 | 78.532 | 84.6542 | 91.113 | 97.5519 | 103.9919
MidlandWind2045RCP6.0 | Midland | Wind | RCP6.0 | 2045 | 78.6123 | 84.7504 | 91.227 | 97.6819 | 104.1373
MidlandWind2050RCP6.0 | Midland | Wind | RCP6.0 | 2050 | 78.8045 | 84.9806 | 91.503 | 97.9987 | 104.496
MidlandWind2055RCP6.0 | Midland | Wind | RCP6.0 | 2055 | 78.9164 | 85.1145 | 91.665 | 98.1856 | 104.7095
MidlandWind2060RCP6.0 | Midland | Wind | RCP6.0 | 2060 | 79.0283 | 85.2485 | 91.827 | 98.3724 | 104.9229
MidlandWind2065RCP6.0 | Midland | Wind | RCP6.0 | 2065 | 79.1402 | 85.3824 | 91.989 | 98.5592 | 105.1363
MidlandWind2070RCP6.0 | Midland | Wind | RCP6.0 | 2070 | 79.2521 | 85.5163 | 92.151 | 98.746 | 105.3497
MidlandWind2075RCP6.0 | Midland | Wind | RCP6.0 | 2075 | 79.3046 | 85.5916 | 92.2567 | 98.876 | 105.5036
MidlandWind2080RCP6.0 | Midland | Wind | RCP6.0 | 2080 | 79.3571 | 85.667 | 92.3625 | 99.006 | 105.6575
MidlandWind2085RCP6.0 | Midland | Wind | RCP6.0 | 2085 | 79.4095 | 85.7423 | 92.4682 | 99.136 | 105.8114
MidlandWind2090RCP6.0 | Midland | Wind | RCP6.0 | 2090 | 79.5785 | 85.9739 | 92.775 | 99.5068 | 106.2457
MidlandWind2095RCP6.0 | Midland | Wind | RCP6.0 | 2095 | 79.6951 | 86.1301 | 92.976 | 99.7475 | 106.5262
MidlandWind2100RCP6.0 | Midland | Wind | RCP6.0 | 2100 | 79.8117 | 86.2863 | 93.177 | 99.9883 | 106.8066
MidlandWind2023RCP8.5 | Midland | Wind | RCP8.5 | 2023 | 78.2108 | 84.2692 | 90.657 | 97.0319 | 103.4105
MidlandWind2025RCP8.5 | Midland | Wind | RCP8.5 | 2025 | 78.3714 | 84.4617 | 90.885 | 97.2919 | 103.7012
MidlandWind2030RCP8.5 | Midland | Wind | RCP8.5 | 2030 | 78.532 | 84.6542 | 91.113 | 97.5519 | 103.9919
MidlandWind2035RCP8.5 | Midland | Wind | RCP8.5 | 2035 | 78.6926 | 84.8467 | 91.341 | 97.8119 | 104.2826
MidlandWind2040RCP8.5 | Midland | Wind | RCP8.5 | 2040 | 78.8791 | 85.0699 | 91.611 | 98.1233 | 104.6383
MidlandWind2045RCP8.5 | Midland | Wind | RCP8.5 | 2045 | 79.0656 | 85.2931 | 91.881 | 98.4347 | 104.994
MidlandWind2050RCP8.5 | Midland | Wind | RCP8.5 | 2050 | 79.3221 | 85.6167 | 92.292 | 98.9194 | 105.5549
MidlandWind2055RCP8.5 | Midland | Wind | RCP8.5 | 2055 | 79.392 | 85.7172 | 92.433 | 99.0927 | 105.7601
MidlandWind2060RCP8.5 | Midland | Wind | RCP8.5 | 2060 | 79.5785 | 85.9739 | 92.775 | 99.5068 | 106.2457
MidlandWind2065RCP8.5 | Midland | Wind | RCP8.5 | 2065 | 79.6951 | 86.1301 | 92.976 | 99.7475 | 106.5262
MidlandWind2070RCP8.5 | Midland | Wind | RCP8.5 | 2070 | 79.7987 | 86.2807 | 93.183 | 100.0011 | 106.8305
MidlandWind2075RCP8.5 | Midland | Wind | RCP8.5 | 2075 | 79.7858 | 86.2752 | 93.189 | 100.014 | 106.8545
MidlandWind2080RCP8.5 | Midland | Wind | RCP8.5 | 2080 | 79.7728 | 86.2696 | 93.195 | 100.0268 | 106.8784
MidlandWind2085RCP8.5 | Midland | Wind | RCP8.5 | 2085 | 79.8739 | 86.3993 | 93.366 | 100.229 | 107.1144
MidlandWind2090RCP8.5 | Midland | Wind | RCP8.5 | 2090 | 79.9749 | 86.5291 | 93.537 | 100.4313 | 107.3504
MidlandWind2095RCP8.5 | Midland | Wind | RCP8.5 | 2095 | 79.9749 | 86.5291 | 93.537 | 100.4313 | 107.3504
MidlandWind2100RCP8.5 | Midland | Wind | RCP8.5 | 2100 | 79.9749 | 86.5291 | 93.537 | 100.4313 | 107.3504
MiltonIce Accretion2023RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
MiltonIce Accretion2025RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
MiltonIce Accretion2030RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
MiltonIce Accretion2035RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
MiltonIce Accretion2040RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
MiltonIce Accretion2045RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
MiltonIce Accretion2050RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
MiltonIce Accretion2055RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
MiltonIce Accretion2060RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
MiltonIce Accretion2065RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
MiltonIce Accretion2070RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
MiltonIce Accretion2075RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2075 | 15.5377 | 18.8894 | 23.1125 | 26.329 | 29.5313
MiltonIce Accretion2080RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2080 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
MiltonIce Accretion2085RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2085 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
MiltonIce Accretion2090RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2090 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
MiltonIce Accretion2095RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2095 | 15.3405 | 18.7511 | 23.0625 | 26.329 | 29.5942
MiltonIce Accretion2100RCP4.5 | Milton | Ice Accretion | RCP4.5 | 2100 | 15.2912 | 18.7165 | 23.05 | 26.329 | 29.61
MiltonIce Accretion2023RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
MiltonIce Accretion2025RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
MiltonIce Accretion2030RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
MiltonIce Accretion2035RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
MiltonIce Accretion2040RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
MiltonIce Accretion2045RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
MiltonIce Accretion2050RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
MiltonIce Accretion2055RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
MiltonIce Accretion2060RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
MiltonIce Accretion2065RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
MiltonIce Accretion2070RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
MiltonIce Accretion2075RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2075 | 15.513 | 18.8721 | 23.1062 | 26.329 | 29.5391
MiltonIce Accretion2080RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2080 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
MiltonIce Accretion2085RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2085 | 15.3652 | 18.7684 | 23.0688 | 26.329 | 29.5864
MiltonIce Accretion2090RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2090 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
MiltonIce Accretion2095RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2095 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
MiltonIce Accretion2100RCP6.0 | Milton | Ice Accretion | RCP6.0 | 2100 | 14.2127 | 17.596 | 21.825 | 25.0577 | 28.2555
MiltonIce Accretion2023RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
MiltonIce Accretion2025RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2025 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
MiltonIce Accretion2030RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2030 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
MiltonIce Accretion2035RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2035 | 16.6133 | 20.0652 | 24.425 | 27.7415 | 31.059
MiltonIce Accretion2040RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2040 | 16.2712 | 19.6848 | 23.9917 | 27.2707 | 30.5445
MiltonIce Accretion2045RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2045 | 15.9291 | 19.3044 | 23.5583 | 26.7998 | 30.03
MiltonIce Accretion2050RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2050 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
MiltonIce Accretion2055RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2055 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
MiltonIce Accretion2060RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2060 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
MiltonIce Accretion2065RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2065 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
MiltonIce Accretion2070RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2070 | 13.8125 | 17.1464 | 21.325 | 24.5022 | 27.657
MiltonIce Accretion2075RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2075 | 13.4124 | 16.6968 | 20.825 | 23.9466 | 27.0585
MiltonIce Accretion2080RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2080 | 13.0123 | 16.2473 | 20.325 | 23.391 | 26.46
MiltonIce Accretion2085RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2085 | 12.1338 | 15.1994 | 19.0625 | 21.9785 | 24.885
MiltonIce Accretion2090RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2090 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
MiltonIce Accretion2095RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2095 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
MiltonIce Accretion2100RCP8.5 | Milton | Ice Accretion | RCP8.5 | 2100 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
MiltonWind2023RCP4.5 | Milton | Wind | RCP4.5 | 2023 | 82.4328 | 88.8359 | 95.589 | 102.3311 | 109.0689
MiltonWind2025RCP4.5 | Milton | Wind | RCP4.5 | 2025 | 82.4629 | 88.8801 | 95.6523 | 102.4107 | 109.1646
MiltonWind2030RCP4.5 | Milton | Wind | RCP4.5 | 2030 | 82.4929 | 88.9243 | 95.7157 | 102.4903 | 109.2603
MiltonWind2035RCP4.5 | Milton | Wind | RCP4.5 | 2035 | 82.523 | 88.9685 | 95.779 | 102.5699 | 109.3559
MiltonWind2040RCP4.5 | Milton | Wind | RCP4.5 | 2040 | 82.5531 | 89.0126 | 95.8423 | 102.6496 | 109.4516
MiltonWind2045RCP4.5 | Milton | Wind | RCP4.5 | 2045 | 82.5832 | 89.0568 | 95.9057 | 102.7292 | 109.5473
MiltonWind2050RCP4.5 | Milton | Wind | RCP4.5 | 2050 | 82.6789 | 89.1805 | 96.0659 | 102.9206 | 109.7707
MiltonWind2055RCP4.5 | Milton | Wind | RCP4.5 | 2055 | 82.7445 | 89.26 | 96.1628 | 103.0324 | 109.8985
MiltonWind2060RCP4.5 | Milton | Wind | RCP4.5 | 2060 | 82.8101 | 89.3395 | 96.2597 | 103.1443 | 110.0263
MiltonWind2065RCP4.5 | Milton | Wind | RCP4.5 | 2065 | 82.8757 | 89.419 | 96.3566 | 103.2561 | 110.1541
MiltonWind2070RCP4.5 | Milton | Wind | RCP4.5 | 2070 | 82.9414 | 89.4985 | 96.4535 | 103.3679 | 110.2819
MiltonWind2075RCP4.5 | Milton | Wind | RCP4.5 | 2075 | 83.0316 | 89.6252 | 96.6261 | 103.578 | 110.531
MiltonWind2080RCP4.5 | Milton | Wind | RCP4.5 | 2080 | 83.1218 | 89.7518 | 96.7987 | 103.788 | 110.7801
MiltonWind2085RCP4.5 | Milton | Wind | RCP4.5 | 2085 | 83.2121 | 89.8785 | 96.9712 | 103.9981 | 111.0292
MiltonWind2090RCP4.5 | Milton | Wind | RCP4.5 | 2090 | 83.3023 | 90.0051 | 97.1438 | 104.2082 | 111.2782
MiltonWind2095RCP4.5 | Milton | Wind | RCP4.5 | 2095 | 83.3925 | 90.1317 | 97.3164 | 104.4183 | 111.5273
MiltonWind2100RCP4.5 | Milton | Wind | RCP4.5 | 2100 | 83.4828 | 90.2584 | 97.489 | 104.6283 | 111.7764
MiltonWind2023RCP6.0 | Milton | Wind | RCP6.0 | 2023 | 82.4328 | 88.8359 | 95.589 | 102.3311 | 109.0689
MiltonWind2025RCP6.0 | Milton | Wind | RCP6.0 | 2025 | 82.4629 | 88.8801 | 95.6523 | 102.4107 | 109.1646
MiltonWind2030RCP6.0 | Milton | Wind | RCP6.0 | 2030 | 82.4929 | 88.9243 | 95.7157 | 102.4903 | 109.2603
MiltonWind2035RCP6.0 | Milton | Wind | RCP6.0 | 2035 | 82.523 | 88.9685 | 95.779 | 102.5699 | 109.3559
MiltonWind2040RCP6.0 | Milton | Wind | RCP6.0 | 2040 | 82.5531 | 89.0126 | 95.8423 | 102.6496 | 109.4516
MiltonWind2045RCP6.0 | Milton | Wind | RCP6.0 | 2045 | 82.5832 | 89.0568 | 95.9057 | 102.7292 | 109.5473
MiltonWind2050RCP6.0 | Milton | Wind | RCP6.0 | 2050 | 82.6789 | 89.1805 | 96.0659 | 102.9206 | 109.7707
MiltonWind2055RCP6.0 | Milton | Wind | RCP6.0 | 2055 | 82.7445 | 89.26 | 96.1628 | 103.0324 | 109.8985
MiltonWind2060RCP6.0 | Milton | Wind | RCP6.0 | 2060 | 82.8101 | 89.3395 | 96.2597 | 103.1443 | 110.0263
MiltonWind2065RCP6.0 | Milton | Wind | RCP6.0 | 2065 | 82.8757 | 89.419 | 96.3566 | 103.2561 | 110.1541
MiltonWind2070RCP6.0 | Milton | Wind | RCP6.0 | 2070 | 82.9414 | 89.4985 | 96.4535 | 103.3679 | 110.2819
MiltonWind2075RCP6.0 | Milton | Wind | RCP6.0 | 2075 | 83.0767 | 89.6885 | 96.7124 | 103.683 | 110.6555
MiltonWind2080RCP6.0 | Milton | Wind | RCP6.0 | 2080 | 83.2121 | 89.8785 | 96.9712 | 103.9981 | 111.0292
MiltonWind2085RCP6.0 | Milton | Wind | RCP6.0 | 2085 | 83.3474 | 90.0684 | 97.2301 | 104.3132 | 111.4028
MiltonWind2090RCP6.0 | Milton | Wind | RCP6.0 | 2090 | 83.7671 | 90.6235 | 97.9545 | 105.1806 | 112.419
MiltonWind2095RCP6.0 | Milton | Wind | RCP6.0 | 2095 | 84.0515 | 90.9887 | 98.42 | 105.7329 | 113.0616
MiltonWind2100RCP6.0 | Milton | Wind | RCP6.0 | 2100 | 84.3359 | 91.3539 | 98.8855 | 106.2852 | 113.7042
MiltonWind2023RCP8.5 | Milton | Wind | RCP8.5 | 2023 | 82.4328 | 88.8359 | 95.589 | 102.3311 | 109.0689
MiltonWind2025RCP8.5 | Milton | Wind | RCP8.5 | 2025 | 82.4929 | 88.9243 | 95.7157 | 102.4903 | 109.2603
MiltonWind2030RCP8.5 | Milton | Wind | RCP8.5 | 2030 | 82.5531 | 89.0126 | 95.8423 | 102.6496 | 109.4516
MiltonWind2035RCP8.5 | Milton | Wind | RCP8.5 | 2035 | 82.6132 | 89.101 | 95.969 | 102.8088 | 109.6429
MiltonWind2040RCP8.5 | Milton | Wind | RCP8.5 | 2040 | 82.7226 | 89.2335 | 96.1305 | 102.9952 | 109.8559
MiltonWind2045RCP8.5 | Milton | Wind | RCP8.5 | 2045 | 82.832 | 89.366 | 96.292 | 103.1815 | 110.0689
MiltonWind2050RCP8.5 | Milton | Wind | RCP8.5 | 2050 | 83.1218 | 89.7518 | 96.7987 | 103.788 | 110.7801
MiltonWind2055RCP8.5 | Milton | Wind | RCP8.5 | 2055 | 83.3023 | 90.0051 | 97.1438 | 104.2082 | 111.2782
MiltonWind2060RCP8.5 | Milton | Wind | RCP8.5 | 2060 | 83.7671 | 90.6235 | 97.9545 | 105.1806 | 112.419
MiltonWind2065RCP8.5 | Milton | Wind | RCP8.5 | 2065 | 84.0515 | 90.9887 | 98.42 | 105.7329 | 113.0616
MiltonWind2070RCP8.5 | Milton | Wind | RCP8.5 | 2070 | 84.4972 | 91.5866 | 99.2085 | 106.6817 | 114.1771
MiltonWind2075RCP8.5 | Milton | Wind | RCP8.5 | 2075 | 84.6586 | 91.8192 | 99.5315 | 107.0781 | 114.65
MiltonWind2080RCP8.5 | Milton | Wind | RCP8.5 | 2080 | 84.8199 | 92.0519 | 99.8545 | 107.4745 | 115.1229
MiltonWind2085RCP8.5 | Milton | Wind | RCP8.5 | 2085 | 85.0783 | 92.3876 | 100.2867 | 107.993 | 115.7294
MiltonWind2090RCP8.5 | Milton | Wind | RCP8.5 | 2090 | 85.3367 | 92.7233 | 100.719 | 108.5114 | 116.3359
MiltonWind2095RCP8.5 | Milton | Wind | RCP8.5 | 2095 | 85.3367 | 92.7233 | 100.719 | 108.5114 | 116.3359
MiltonWind2100RCP8.5 | Milton | Wind | RCP8.5 | 2100 | 85.3367 | 92.7233 | 100.719 | 108.5114 | 116.3359
MilvertonIce Accretion2023RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2023 | 15.9725 | 19.1854 | 23.253 | 26.3539 | 29.4437
MilvertonIce Accretion2025RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2025 | 16.0498 | 19.2841 | 23.3795 | 26.5055 | 29.6176
MilvertonIce Accretion2030RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2030 | 16.1272 | 19.3827 | 23.506 | 26.6571 | 29.7914
MilvertonIce Accretion2035RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2035 | 16.2045 | 19.4813 | 23.6325 | 26.8087 | 29.9653
MilvertonIce Accretion2040RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2040 | 16.2819 | 19.58 | 23.759 | 26.9603 | 30.1392
MilvertonIce Accretion2045RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2045 | 16.3592 | 19.6786 | 23.8855 | 27.1119 | 30.3131
MilvertonIce Accretion2050RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2050 | 16.443 | 19.8078 | 24.0764 | 27.3415 | 30.5913
MilvertonIce Accretion2055RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2055 | 16.4494 | 19.8383 | 24.1408 | 27.4194 | 30.6956
MilvertonIce Accretion2060RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2060 | 16.4558 | 19.8689 | 24.2052 | 27.4974 | 30.7999
MilvertonIce Accretion2065RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2065 | 16.4622 | 19.8994 | 24.2696 | 27.5754 | 30.9043
MilvertonIce Accretion2070RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2070 | 16.4686 | 19.93 | 24.334 | 27.6534 | 31.0086
MilvertonIce Accretion2075RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2075 | 16.4179 | 19.8981 | 24.3187 | 27.6577 | 31.0231
MilvertonIce Accretion2080RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2080 | 16.3672 | 19.8663 | 24.3033 | 27.662 | 31.0376
MilvertonIce Accretion2085RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2085 | 16.3165 | 19.8345 | 24.288 | 27.6664 | 31.0521
MilvertonIce Accretion2090RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2090 | 16.2659 | 19.8027 | 24.2727 | 27.6707 | 31.0666
MilvertonIce Accretion2095RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2095 | 16.2152 | 19.7709 | 24.2573 | 27.675 | 31.0811
MilvertonIce Accretion2100RCP4.5 | Milverton | Ice Accretion | RCP4.5 | 2100 | 16.1645 | 19.7391 | 24.242 | 27.6793 | 31.0955
MilvertonIce Accretion2023RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2023 | 15.9725 | 19.1854 | 23.253 | 26.3539 | 29.4437
MilvertonIce Accretion2025RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2025 | 16.0498 | 19.2841 | 23.3795 | 26.5055 | 29.6176
MilvertonIce Accretion2030RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2030 | 16.1272 | 19.3827 | 23.506 | 26.6571 | 29.7914
MilvertonIce Accretion2035RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2035 | 16.2045 | 19.4813 | 23.6325 | 26.8087 | 29.9653
MilvertonIce Accretion2040RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2040 | 16.2819 | 19.58 | 23.759 | 26.9603 | 30.1392
MilvertonIce Accretion2045RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2045 | 16.3592 | 19.6786 | 23.8855 | 27.1119 | 30.3131
MilvertonIce Accretion2050RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2050 | 16.443 | 19.8078 | 24.0764 | 27.3415 | 30.5913
MilvertonIce Accretion2055RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2055 | 16.4494 | 19.8383 | 24.1408 | 27.4194 | 30.6956
MilvertonIce Accretion2060RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2060 | 16.4558 | 19.8689 | 24.2052 | 27.4974 | 30.7999
MilvertonIce Accretion2065RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2065 | 16.4622 | 19.8994 | 24.2696 | 27.5754 | 30.9043
MilvertonIce Accretion2070RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2070 | 16.4686 | 19.93 | 24.334 | 27.6534 | 31.0086
MilvertonIce Accretion2075RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2075 | 16.3926 | 19.8822 | 24.311 | 27.6599 | 31.0303
MilvertonIce Accretion2080RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2080 | 16.3165 | 19.8345 | 24.288 | 27.6664 | 31.0521
MilvertonIce Accretion2085RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2085 | 16.2405 | 19.7868 | 24.265 | 27.6729 | 31.0738
MilvertonIce Accretion2090RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2090 | 15.8978 | 19.4654 | 23.9583 | 27.3761 | 30.7864
MilvertonIce Accretion2095RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2095 | 15.631 | 19.1918 | 23.6747 | 27.0729 | 30.4773
MilvertonIce Accretion2100RCP6.0 | Milverton | Ice Accretion | RCP6.0 | 2100 | 15.3643 | 18.9182 | 23.391 | 26.7697 | 30.1682
MilvertonIce Accretion2023RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2023 | 15.9725 | 19.1854 | 23.253 | 26.3539 | 29.4437
MilvertonIce Accretion2025RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2025 | 16.1272 | 19.3827 | 23.506 | 26.6571 | 29.7914
MilvertonIce Accretion2030RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2030 | 16.2819 | 19.58 | 23.759 | 26.9603 | 30.1392
MilvertonIce Accretion2035RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2035 | 16.4366 | 19.7772 | 24.012 | 27.2635 | 30.487
MilvertonIce Accretion2040RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2040 | 16.4473 | 19.8281 | 24.1193 | 27.3935 | 30.6608
MilvertonIce Accretion2045RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2045 | 16.4579 | 19.8791 | 24.2267 | 27.5234 | 30.8347
MilvertonIce Accretion2050RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2050 | 16.3672 | 19.8663 | 24.3033 | 27.662 | 31.0376
MilvertonIce Accretion2055RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2055 | 16.2659 | 19.8027 | 24.2727 | 27.6707 | 31.0666
MilvertonIce Accretion2060RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2060 | 15.8978 | 19.4654 | 23.9583 | 27.3761 | 30.7864
MilvertonIce Accretion2065RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2065 | 15.631 | 19.1918 | 23.6747 | 27.0729 | 30.4773
MilvertonIce Accretion2070RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2070 | 14.8735 | 18.3646 | 22.7623 | 26.0853 | 29.4147
MilvertonIce Accretion2075RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2075 | 14.3827 | 17.811 | 22.1337 | 25.4009 | 28.6612
MilvertonIce Accretion2080RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2080 | 13.8919 | 17.2574 | 21.505 | 24.7165 | 27.9077
MilvertonIce Accretion2085RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2085 | 13.1717 | 16.4079 | 20.493 | 23.5729 | 26.6471
MilvertonIce Accretion2090RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2090 | 12.4515 | 15.5583 | 19.481 | 22.4294 | 25.3865
MilvertonIce Accretion2095RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2095 | 12.4515 | 15.5583 | 19.481 | 22.4294 | 25.3865
MilvertonIce Accretion2100RCP8.5 | Milverton | Ice Accretion | RCP8.5 | 2100 | 12.4515 | 15.5583 | 19.481 | 22.4294 | 25.3865
MilvertonWind2023RCP4.5 | Milverton | Wind | RCP4.5 | 2023 | 85.2136 | 91.8691 | 98.8918 | 105.8981 | 112.9042
MilvertonWind2025RCP4.5 | Milverton | Wind | RCP4.5 | 2025 | 85.2588 | 91.9223 | 98.9555 | 105.9698 | 112.9862
MilvertonWind2030RCP4.5 | Milverton | Wind | RCP4.5 | 2030 | 85.3039 | 91.9754 | 99.0192 | 106.0414 | 113.0681
MilvertonWind2035RCP4.5 | Milverton | Wind | RCP4.5 | 2035 | 85.349 | 92.0286 | 99.0829 | 106.1131 | 113.15
MilvertonWind2040RCP4.5 | Milverton | Wind | RCP4.5 | 2040 | 85.3942 | 92.0818 | 99.1466 | 106.1847 | 113.2319
MilvertonWind2045RCP4.5 | Milverton | Wind | RCP4.5 | 2045 | 85.4393 | 92.1349 | 99.2103 | 106.2564 | 113.3139
MilvertonWind2050RCP4.5 | Milverton | Wind | RCP4.5 | 2050 | 85.4929 | 92.1936 | 99.274 | 106.3259 | 113.3869
MilvertonWind2055RCP4.5 | Milverton | Wind | RCP4.5 | 2055 | 85.5013 | 92.199 | 99.274 | 106.3238 | 113.3779
MilvertonWind2060RCP4.5 | Milverton | Wind | RCP4.5 | 2060 | 85.5098 | 92.2045 | 99.274 | 106.3217 | 113.369
MilvertonWind2065RCP4.5 | Milverton | Wind | RCP4.5 | 2065 | 85.5183 | 92.21 | 99.274 | 106.3197 | 113.36
MilvertonWind2070RCP4.5 | Milverton | Wind | RCP4.5 | 2070 | 85.5267 | 92.2155 | 99.274 | 106.3176 | 113.3511
MilvertonWind2075RCP4.5 | Milverton | Wind | RCP4.5 | 2075 | 85.6212 | 92.3446 | 99.4488 | 106.5308 | 113.6043
MilvertonWind2080RCP4.5 | Milverton | Wind | RCP4.5 | 2080 | 85.7157 | 92.4737 | 99.6235 | 106.744 | 113.8576
MilvertonWind2085RCP4.5 | Milverton | Wind | RCP4.5 | 2085 | 85.8102 | 92.6028 | 99.7983 | 106.9572 | 114.1108
MilvertonWind2090RCP4.5 | Milverton | Wind | RCP4.5 | 2090 | 85.9047 | 92.7319 | 99.9731 | 107.1704 | 114.364
MilvertonWind2095RCP4.5 | Milverton | Wind | RCP4.5 | 2095 | 85.9992 | 92.861 | 100.1478 | 107.3836 | 114.6173
MilvertonWind2100RCP4.5 | Milverton | Wind | RCP4.5 | 2100 | 86.0937 | 92.9901 | 100.3226 | 107.5968 | 114.8705
MilvertonWind2023RCP6.0 | Milverton | Wind | RCP6.0 | 2023 | 85.2136 | 91.8691 | 98.8918 | 105.8981 | 112.9042
MilvertonWind2025RCP6.0 | Milverton | Wind | RCP6.0 | 2025 | 85.2588 | 91.9223 | 98.9555 | 105.9698 | 112.9862
MilvertonWind2030RCP6.0 | Milverton | Wind | RCP6.0 | 2030 | 85.3039 | 91.9754 | 99.0192 | 106.0414 | 113.0681
MilvertonWind2035RCP6.0 | Milverton | Wind | RCP6.0 | 2035 | 85.349 | 92.0286 | 99.0829 | 106.1131 | 113.15
MilvertonWind2040RCP6.0 | Milverton | Wind | RCP6.0 | 2040 | 85.3942 | 92.0818 | 99.1466 | 106.1847 | 113.2319
MilvertonWind2045RCP6.0 | Milverton | Wind | RCP6.0 | 2045 | 85.4393 | 92.1349 | 99.2103 | 106.2564 | 113.3139
MilvertonWind2050RCP6.0 | Milverton | Wind | RCP6.0 | 2050 | 85.4929 | 92.1936 | 99.274 | 106.3259 | 113.3869
MilvertonWind2055RCP6.0 | Milverton | Wind | RCP6.0 | 2055 | 85.5013 | 92.199 | 99.274 | 106.3238 | 113.3779
MilvertonWind2060RCP6.0 | Milverton | Wind | RCP6.0 | 2060 | 85.5098 | 92.2045 | 99.274 | 106.3217 | 113.369
MilvertonWind2065RCP6.0 | Milverton | Wind | RCP6.0 | 2065 | 85.5183 | 92.21 | 99.274 | 106.3197 | 113.36
MilvertonWind2070RCP6.0 | Milverton | Wind | RCP6.0 | 2070 | 85.5267 | 92.2155 | 99.274 | 106.3176 | 113.3511
MilvertonWind2075RCP6.0 | Milverton | Wind | RCP6.0 | 2075 | 85.6685 | 92.4091 | 99.5361 | 106.6374 | 113.731
MilvertonWind2080RCP6.0 | Milverton | Wind | RCP6.0 | 2080 | 85.8102 | 92.6028 | 99.7983 | 106.9572 | 114.1108
MilvertonWind2085RCP6.0 | Milverton | Wind | RCP6.0 | 2085 | 85.9519 | 92.7965 | 100.0605 | 107.277 | 114.4907
MilvertonWind2090RCP6.0 | Milverton | Wind | RCP6.0 | 2090 | 86.4688 | 93.4519 | 100.8877 | 108.2505 | 115.619
MilvertonWind2095RCP6.0 | Milverton | Wind | RCP6.0 | 2095 | 86.844 | 93.9137 | 101.4529 | 108.9041 | 116.3676
MilvertonWind2100RCP6.0 | Milverton | Wind | RCP6.0 | 2100 | 87.2192 | 94.3755 | 102.018 | 109.5577 | 117.1161
MilvertonWind2023RCP8.5 | Milverton | Wind | RCP8.5 | 2023 | 85.2136 | 91.8691 | 98.8918 | 105.8981 | 112.9042
MilvertonWind2025RCP8.5 | Milverton | Wind | RCP8.5 | 2025 | 85.3039 | 91.9754 | 99.0192 | 106.0414 | 113.0681
MilvertonWind2030RCP8.5 | Milverton | Wind | RCP8.5 | 2030 | 85.3942 | 92.0818 | 99.1466 | 106.1847 | 113.2319
MilvertonWind2035RCP8.5 | Milverton | Wind | RCP8.5 | 2035 | 85.4844 | 92.1881 | 99.274 | 106.328 | 113.3958
MilvertonWind2040RCP8.5 | Milverton | Wind | RCP8.5 | 2040 | 85.4985 | 92.1972 | 99.274 | 106.3245 | 113.3809
MilvertonWind2045RCP8.5 | Milverton | Wind | RCP8.5 | 2045 | 85.5126 | 92.2063 | 99.274 | 106.321 | 113.366
MilvertonWind2050RCP8.5 | Milverton | Wind | RCP8.5 | 2050 | 85.7157 | 92.4737 | 99.6235 | 106.744 | 113.8576
MilvertonWind2055RCP8.5 | Milverton | Wind | RCP8.5 | 2055 | 85.9047 | 92.7319 | 99.9731 | 107.1704 | 114.364
MilvertonWind2060RCP8.5 | Milverton | Wind | RCP8.5 | 2060 | 86.4688 | 93.4519 | 100.8877 | 108.2505 | 115.619
MilvertonWind2065RCP8.5 | Milverton | Wind | RCP8.5 | 2065 | 86.844 | 93.9137 | 101.4529 | 108.9041 | 116.3676
MilvertonWind2070RCP8.5 | Milverton | Wind | RCP8.5 | 2070 | 87.4956 | 94.737 | 102.4917 | 110.124 | 117.7789
MilvertonWind2075RCP8.5 | Milverton | Wind | RCP8.5 | 2075 | 87.772 | 95.0985 | 102.9653 | 110.6902 | 118.4418
MilvertonWind2080RCP8.5 | Milverton | Wind | RCP8.5 | 2080 | 88.0484 | 95.46 | 103.439 | 111.2565 | 119.1047
MilvertonWind2085RCP8.5 | Milverton | Wind | RCP8.5 | 2085 | 88.2642 | 95.7471 | 103.8163 | 111.7074 | 119.6298
MilvertonWind2090RCP8.5 | Milverton | Wind | RCP8.5 | 2090 | 88.48 | 96.0342 | 104.1936 | 112.1583 | 120.1549
MilvertonWind2095RCP8.5 | Milverton | Wind | RCP8.5 | 2095 | 88.48 | 96.0342 | 104.1936 | 112.1583 | 120.1549
MilvertonWind2100RCP8.5 | Milverton | Wind | RCP8.5 | 2100 | 88.48 | 96.0342 | 104.1936 | 112.1583 | 120.1549
MindenIce Accretion2023RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2023 | 16.8569 | 20.0652 | 24.125 | 27.233 | 30.366
MindenIce Accretion2025RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2025 | 16.8395 | 20.041 | 24.0917 | 27.1953 | 30.3188
MindenIce Accretion2030RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2030 | 16.8221 | 20.0168 | 24.0583 | 27.1577 | 30.2715
MindenIce Accretion2035RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2035 | 16.8047 | 19.9926 | 24.025 | 27.12 | 30.2242
MindenIce Accretion2040RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2040 | 16.7873 | 19.9684 | 23.9917 | 27.0823 | 30.177
MindenIce Accretion2045RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2045 | 16.7699 | 19.9442 | 23.9583 | 27.0447 | 30.1298
MindenIce Accretion2050RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2050 | 16.749 | 19.9324 | 23.965 | 27.0635 | 30.1581
MindenIce Accretion2055RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2055 | 16.7455 | 19.9449 | 24.005 | 27.12 | 30.2337
MindenIce Accretion2060RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2060 | 16.7421 | 19.9573 | 24.045 | 27.1765 | 30.3093
MindenIce Accretion2065RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2065 | 16.7386 | 19.9698 | 24.085 | 27.233 | 30.3849
MindenIce Accretion2070RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2070 | 16.7351 | 19.9823 | 24.125 | 27.2895 | 30.4605
MindenIce Accretion2075RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2075 | 16.8134 | 20.0929 | 24.2708 | 27.4637 | 30.66
MindenIce Accretion2080RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2080 | 16.8917 | 20.2036 | 24.4167 | 27.6379 | 30.8595
MindenIce Accretion2085RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2085 | 16.9699 | 20.3143 | 24.5625 | 27.8121 | 31.059
MindenIce Accretion2090RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2090 | 17.0482 | 20.4249 | 24.7083 | 27.9863 | 31.2585
MindenIce Accretion2095RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2095 | 17.1265 | 20.5356 | 24.8542 | 28.1605 | 31.458
MindenIce Accretion2100RCP4.5 | Minden | Ice Accretion | RCP4.5 | 2100 | 17.2048 | 20.6462 | 25 | 28.3347 | 31.6575
MindenIce Accretion2023RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2023 | 16.8569 | 20.0652 | 24.125 | 27.233 | 30.366
MindenIce Accretion2025RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2025 | 16.8395 | 20.041 | 24.0917 | 27.1953 | 30.3188
MindenIce Accretion2030RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2030 | 16.8221 | 20.0168 | 24.0583 | 27.1577 | 30.2715
MindenIce Accretion2035RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2035 | 16.8047 | 19.9926 | 24.025 | 27.12 | 30.2242
MindenIce Accretion2040RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2040 | 16.7873 | 19.9684 | 23.9917 | 27.0823 | 30.177
MindenIce Accretion2045RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2045 | 16.7699 | 19.9442 | 23.9583 | 27.0447 | 30.1298
MindenIce Accretion2050RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2050 | 16.749 | 19.9324 | 23.965 | 27.0635 | 30.1581
MindenIce Accretion2055RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2055 | 16.7455 | 19.9449 | 24.005 | 27.12 | 30.2337
MindenIce Accretion2060RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2060 | 16.7421 | 19.9573 | 24.045 | 27.1765 | 30.3093
MindenIce Accretion2065RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2065 | 16.7386 | 19.9698 | 24.085 | 27.233 | 30.3849
MindenIce Accretion2070RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2070 | 16.7351 | 19.9823 | 24.125 | 27.2895 | 30.4605
MindenIce Accretion2075RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2075 | 16.8525 | 20.1483 | 24.3438 | 27.5508 | 30.7597
MindenIce Accretion2080RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2080 | 16.9699 | 20.3143 | 24.5625 | 27.8121 | 31.059
MindenIce Accretion2085RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2085 | 17.0874 | 20.4802 | 24.7812 | 28.0734 | 31.3582
MindenIce Accretion2090RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2090 | 17.3034 | 20.8053 | 25.2417 | 28.6361 | 32.0145
MindenIce Accretion2095RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2095 | 17.402 | 20.9644 | 25.4833 | 28.9374 | 32.3715
MindenIce Accretion2100RCP6.0 | Minden | Ice Accretion | RCP6.0 | 2100 | 17.5005 | 21.1235 | 25.725 | 29.2387 | 32.7285
MindenIce Accretion2023RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2023 | 16.8569 | 20.0652 | 24.125 | 27.233 | 30.366
MindenIce Accretion2025RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2025 | 16.8221 | 20.0168 | 24.0583 | 27.1577 | 30.2715
MindenIce Accretion2030RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2030 | 16.7873 | 19.9684 | 23.9917 | 27.0823 | 30.177
MindenIce Accretion2035RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2035 | 16.7525 | 19.92 | 23.925 | 27.007 | 30.0825
MindenIce Accretion2040RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2040 | 16.7467 | 19.9407 | 23.9917 | 27.1012 | 30.2085
MindenIce Accretion2045RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2045 | 16.7409 | 19.9615 | 24.0583 | 27.1953 | 30.3345
MindenIce Accretion2050RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2050 | 16.8917 | 20.2036 | 24.4167 | 27.6379 | 30.8595
MindenIce Accretion2055RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2055 | 17.0482 | 20.4249 | 24.7083 | 27.9863 | 31.2585
MindenIce Accretion2060RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2060 | 17.3034 | 20.8053 | 25.2417 | 28.6361 | 32.0145
MindenIce Accretion2065RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2065 | 17.402 | 20.9644 | 25.4833 | 28.9374 | 32.3715
MindenIce Accretion2070RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2070 | 17.373 | 20.999 | 25.6 | 29.1163 | 32.613
MindenIce Accretion2075RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2075 | 17.2454 | 20.8745 | 25.475 | 28.9939 | 32.4975
MindenIce Accretion2080RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2080 | 17.1178 | 20.75 | 25.35 | 28.8715 | 32.382
MindenIce Accretion2085RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2085 | 16.6916 | 20.2831 | 24.8375 | 28.3065 | 31.7677
MindenIce Accretion2090RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2090 | 16.2654 | 19.8163 | 24.325 | 27.7415 | 31.1535
MindenIce Accretion2095RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2095 | 16.2654 | 19.8163 | 24.325 | 27.7415 | 31.1535
MindenIce Accretion2100RCP8.5 | Minden | Ice Accretion | RCP8.5 | 2100 | 16.2654 | 19.8163 | 24.325 | 27.7415 | 31.1535
MindenWind2023RCP4.5 | Minden | Wind | RCP4.5 | 2023 | 69.5414 | 74.9134 | 80.576 | 86.2334 | 91.884
MindenWind2025RCP4.5 | Minden | Wind | RCP4.5 | 2025 | 69.6266 | 75.0287 | 80.728 | 86.4161 | 92.0998
MindenWind2030RCP4.5 | Minden | Wind | RCP4.5 | 2030 | 69.7118 | 75.144 | 80.88 | 86.5987 | 92.3157
MindenWind2035RCP4.5 | Minden | Wind | RCP4.5 | 2035 | 69.797 | 75.2593 | 81.032 | 86.7813 | 92.5315
MindenWind2040RCP4.5 | Minden | Wind | RCP4.5 | 2040 | 69.8822 | 75.3746 | 81.184 | 86.9639 | 92.7474
MindenWind2045RCP4.5 | Minden | Wind | RCP4.5 | 2045 | 69.9674 | 75.49 | 81.336 | 87.1465 | 92.9632
MindenWind2050RCP4.5 | Minden | Wind | RCP4.5 | 2050 | 70.0498 | 75.5949 | 81.4672 | 87.3 | 93.1407
MindenWind2055RCP4.5 | Minden | Wind | RCP4.5 | 2055 | 70.0471 | 75.5844 | 81.4464 | 87.2709 | 93.1024
MindenWind2060RCP4.5 | Minden | Wind | RCP4.5 | 2060 | 70.0443 | 75.574 | 81.4256 | 87.2418 | 93.0641
MindenWind2065RCP4.5 | Minden | Wind | RCP4.5 | 2065 | 70.0415 | 75.5636 | 81.4048 | 87.2127 | 93.0258
MindenWind2070RCP4.5 | Minden | Wind | RCP4.5 | 2070 | 70.0388 | 75.5532 | 81.384 | 87.1836 | 92.9875
MindenWind2075RCP4.5 | Minden | Wind | RCP4.5 | 2075 | 69.9996 | 75.5024 | 81.32 | 87.1094 | 92.9009
MindenWind2080RCP4.5 | Minden | Wind | RCP4.5 | 2080 | 69.9605 | 75.4515 | 81.256 | 87.0352 | 92.8142
MindenWind2085RCP4.5 | Minden | Wind | RCP4.5 | 2085 | 69.9214 | 75.4007 | 81.192 | 86.961 | 92.7276
MindenWind2090RCP4.5 | Minden | Wind | RCP4.5 | 2090 | 69.8822 | 75.3498 | 81.128 | 86.8869 | 92.641
MindenWind2095RCP4.5 | Minden | Wind | RCP4.5 | 2095 | 69.8431 | 75.299 | 81.064 | 86.8127 | 92.5543
MindenWind2100RCP4.5 | Minden | Wind | RCP4.5 | 2100 | 69.8039 | 75.2482 | 81 | 86.7385 | 92.4677
MindenWind2023RCP6.0 | Minden | Wind | RCP6.0 | 2023 | 69.5414 | 74.9134 | 80.576 | 86.2334 | 91.884
MindenWind2025RCP6.0 | Minden | Wind | RCP6.0 | 2025 | 69.6266 | 75.0287 | 80.728 | 86.4161 | 92.0998
MindenWind2030RCP6.0 | Minden | Wind | RCP6.0 | 2030 | 69.7118 | 75.144 | 80.88 | 86.5987 | 92.3157
MindenWind2035RCP6.0 | Minden | Wind | RCP6.0 | 2035 | 69.797 | 75.2593 | 81.032 | 86.7813 | 92.5315
MindenWind2040RCP6.0 | Minden | Wind | RCP6.0 | 2040 | 69.8822 | 75.3746 | 81.184 | 86.9639 | 92.7474
MindenWind2045RCP6.0 | Minden | Wind | RCP6.0 | 2045 | 69.9674 | 75.49 | 81.336 | 87.1465 | 92.9632
MindenWind2050RCP6.0 | Minden | Wind | RCP6.0 | 2050 | 70.0498 | 75.5949 | 81.4672 | 87.3 | 93.1407
MindenWind2055RCP6.0 | Minden | Wind | RCP6.0 | 2055 | 70.0471 | 75.5844 | 81.4464 | 87.2709 | 93.1024
MindenWind2060RCP6.0 | Minden | Wind | RCP6.0 | 2060 | 70.0443 | 75.574 | 81.4256 | 87.2418 | 93.0641
MindenWind2065RCP6.0 | Minden | Wind | RCP6.0 | 2065 | 70.0415 | 75.5636 | 81.4048 | 87.2127 | 93.0258
MindenWind2070RCP6.0 | Minden | Wind | RCP6.0 | 2070 | 70.0388 | 75.5532 | 81.384 | 87.1836 | 92.9875
MindenWind2075RCP6.0 | Minden | Wind | RCP6.0 | 2075 | 69.9801 | 75.4769 | 81.288 | 87.0723 | 92.8576
MindenWind2080RCP6.0 | Minden | Wind | RCP6.0 | 2080 | 69.9214 | 75.4007 | 81.192 | 86.961 | 92.7276
MindenWind2085RCP6.0 | Minden | Wind | RCP6.0 | 2085 | 69.8626 | 75.3244 | 81.096 | 86.8498 | 92.5976
MindenWind2090RCP6.0 | Minden | Wind | RCP6.0 | 2090 | 69.7302 | 75.1465 | 80.8613 | 86.5673 | 92.267
MindenWind2095RCP6.0 | Minden | Wind | RCP6.0 | 2095 | 69.6566 | 75.0448 | 80.7227 | 86.3961 | 92.0664
MindenWind2100RCP6.0 | Minden | Wind | RCP6.0 | 2100 | 69.5829 | 74.9431 | 80.584 | 86.2249 | 91.8658
MindenWind2023RCP8.5 | Minden | Wind | RCP8.5 | 2023 | 69.5414 | 74.9134 | 80.576 | 86.2334 | 91.884
MindenWind2025RCP8.5 | Minden | Wind | RCP8.5 | 2025 | 69.7118 | 75.144 | 80.88 | 86.5987 | 92.3157
MindenWind2030RCP8.5 | Minden | Wind | RCP8.5 | 2030 | 69.8822 | 75.3746 | 81.184 | 86.9639 | 92.7474
MindenWind2035RCP8.5 | Minden | Wind | RCP8.5 | 2035 | 70.0526 | 75.6053 | 81.488 | 87.3291 | 93.179
MindenWind2040RCP8.5 | Minden | Wind | RCP8.5 | 2040 | 70.048 | 75.5879 | 81.4533 | 87.2806 | 93.1152
MindenWind2045RCP8.5 | Minden | Wind | RCP8.5 | 2045 | 70.0434 | 75.5706 | 81.4187 | 87.2321 | 93.0514
MindenWind2050RCP8.5 | Minden | Wind | RCP8.5 | 2050 | 69.9605 | 75.4515 | 81.256 | 87.0352 | 92.8142
MindenWind2055RCP8.5 | Minden | Wind | RCP8.5 | 2055 | 69.8822 | 75.3498 | 81.128 | 86.8869 | 92.641
MindenWind2060RCP8.5 | Minden | Wind | RCP8.5 | 2060 | 69.7302 | 75.1465 | 80.8613 | 86.5673 | 92.267
MindenWind2065RCP8.5 | Minden | Wind | RCP8.5 | 2065 | 69.6566 | 75.0448 | 80.7227 | 86.3961 | 92.0664
MindenWind2070RCP8.5 | Minden | Wind | RCP8.5 | 2070 | 69.5944 | 74.9382 | 80.5547 | 86.1764 | 91.7989
MindenWind2075RCP8.5 | Minden | Wind | RCP8.5 | 2075 | 69.6059 | 74.9332 | 80.5253 | 86.1279 | 91.732
MindenWind2080RCP8.5 | Minden | Wind | RCP8.5 | 2080 | 69.6174 | 74.9282 | 80.496 | 86.0794 | 91.6651
MindenWind2085RCP8.5 | Minden | Wind | RCP8.5 | 2085 | 69.8316 | 75.1961 | 80.832 | 86.4731 | 92.1166
MindenWind2090RCP8.5 | Minden | Wind | RCP8.5 | 2090 | 70.0457 | 75.4639 | 81.168 | 86.8669 | 92.568
MindenWind2095RCP8.5 | Minden | Wind | RCP8.5 | 2095 | 70.0457 | 75.4639 | 81.168 | 86.8669 | 92.568
MindenWind2100RCP8.5 | Minden | Wind | RCP8.5 | 2100 | 70.0457 | 75.4639 | 81.168 | 86.8669 | 92.568
MississaugaIce Accretion2023RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
MississaugaIce Accretion2025RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
MississaugaIce Accretion2030RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
MississaugaIce Accretion2035RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
MississaugaIce Accretion2040RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
MississaugaIce Accretion2045RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
MississaugaIce Accretion2050RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
MississaugaIce Accretion2055RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
MississaugaIce Accretion2060RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
MississaugaIce Accretion2065RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
MississaugaIce Accretion2070RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
MississaugaIce Accretion2075RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2075 | 15.5377 | 18.8894 | 23.1125 | 26.329 | 29.5313
MississaugaIce Accretion2080RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2080 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
MississaugaIce Accretion2085RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2085 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
MississaugaIce Accretion2090RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2090 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
MississaugaIce Accretion2095RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2095 | 15.3405 | 18.7511 | 23.0625 | 26.329 | 29.5942
MississaugaIce Accretion2100RCP4.5 | Mississauga | Ice Accretion | RCP4.5 | 2100 | 15.2912 | 18.7165 | 23.05 | 26.329 | 29.61
MississaugaIce Accretion2023RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
MississaugaIce Accretion2025RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
MississaugaIce Accretion2030RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
MississaugaIce Accretion2035RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
MississaugaIce Accretion2040RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
MississaugaIce Accretion2045RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
MississaugaIce Accretion2050RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
MississaugaIce Accretion2055RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
MississaugaIce Accretion2060RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
MississaugaIce Accretion2065RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
MississaugaIce Accretion2070RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
MississaugaIce Accretion2075RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2075 | 15.513 | 18.8721 | 23.1062 | 26.329 | 29.5391
MississaugaIce Accretion2080RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2080 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
MississaugaIce Accretion2085RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2085 | 15.3652 | 18.7684 | 23.0688 | 26.329 | 29.5864
MississaugaIce Accretion2090RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2090 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
MississaugaIce Accretion2095RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2095 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
MississaugaIce Accretion2100RCP6.0 | Mississauga | Ice Accretion | RCP6.0 | 2100 | 14.2127 | 17.596 | 21.825 | 25.0577 | 28.2555
MississaugaIce Accretion2023RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
MississaugaIce Accretion2025RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2025 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
MississaugaIce Accretion2030RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2030 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
MississaugaIce Accretion2035RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2035 | 16.6133 | 20.0652 | 24.425 | 27.7415 | 31.059
MississaugaIce Accretion2040RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2040 | 16.2712 | 19.6848 | 23.9917 | 27.2707 | 30.5445
MississaugaIce Accretion2045RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2045 | 15.9291 | 19.3044 | 23.5583 | 26.7998 | 30.03
MississaugaIce Accretion2050RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2050 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
MississaugaIce Accretion2055RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2055 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
MississaugaIce Accretion2060RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2060 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
MississaugaIce Accretion2065RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2065 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
MississaugaIce Accretion2070RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2070 | 13.8125 | 17.1464 | 21.325 | 24.5022 | 27.657
MississaugaIce Accretion2075RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2075 | 13.4124 | 16.6968 | 20.825 | 23.9466 | 27.0585
MississaugaIce Accretion2080RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2080 | 13.0123 | 16.2473 | 20.325 | 23.391 | 26.46
MississaugaIce Accretion2085RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2085 | 12.1338 | 15.1994 | 19.0625 | 21.9785 | 24.885
MississaugaIce Accretion2090RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2090 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
MississaugaIce Accretion2095RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2095 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
MississaugaIce Accretion2100RCP8.5 | Mississauga | Ice Accretion | RCP8.5 | 2100 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
MississaugaWind2023RCP4.5 | Mississauga | Wind | RCP4.5 | 2023 | 85.0359 | 91.6413 | 98.6076 | 105.5626 | 112.5132
MississaugaWind2025RCP4.5 | Mississauga | Wind | RCP4.5 | 2025 | 85.0669 | 91.6868 | 98.6729 | 105.6447 | 112.6119
MississaugaWind2030RCP4.5 | Mississauga | Wind | RCP4.5 | 2030 | 85.098 | 91.7324 | 98.7383 | 105.7268 | 112.7106
MississaugaWind2035RCP4.5 | Mississauga | Wind | RCP4.5 | 2035 | 85.129 | 91.778 | 98.8036 | 105.809 | 112.8093
MississaugaWind2040RCP4.5 | Mississauga | Wind | RCP4.5 | 2040 | 85.16 | 91.8235 | 98.8689 | 105.8911 | 112.908
MississaugaWind2045RCP4.5 | Mississauga | Wind | RCP4.5 | 2045 | 85.1911 | 91.8691 | 98.9343 | 105.9733 | 113.0066
MississaugaWind2050RCP4.5 | Mississauga | Wind | RCP4.5 | 2050 | 85.2898 | 91.9967 | 99.0996 | 106.1708 | 113.2372
MississaugaWind2055RCP4.5 | Mississauga | Wind | RCP4.5 | 2055 | 85.3575 | 92.0787 | 99.1995 | 106.2861 | 113.369
MississaugaWind2060RCP4.5 | Mississauga | Wind | RCP4.5 | 2060 | 85.4252 | 92.1608 | 99.2995 | 106.4014 | 113.5008
MississaugaWind2065RCP4.5 | Mississauga | Wind | RCP4.5 | 2065 | 85.4929 | 92.2428 | 99.3994 | 106.5168 | 113.6326
MississaugaWind2070RCP4.5 | Mississauga | Wind | RCP4.5 | 2070 | 85.5606 | 92.3248 | 99.4994 | 106.6321 | 113.7645
MississaugaWind2075RCP4.5 | Mississauga | Wind | RCP4.5 | 2075 | 85.6537 | 92.4555 | 99.6774 | 106.8488 | 114.0214
MississaugaWind2080RCP4.5 | Mississauga | Wind | RCP4.5 | 2080 | 85.7467 | 92.5861 | 99.8555 | 107.0656 | 114.2784
MississaugaWind2085RCP4.5 | Mississauga | Wind | RCP4.5 | 2085 | 85.8398 | 92.7167 | 100.0335 | 107.2823 | 114.5353
MississaugaWind2090RCP4.5 | Mississauga | Wind | RCP4.5 | 2090 | 85.9329 | 92.8474 | 100.2115 | 107.499 | 114.7923
MississaugaWind2095RCP4.5 | Mississauga | Wind | RCP4.5 | 2095 | 86.026 | 92.978 | 100.3896 | 107.7157 | 115.0493
MississaugaWind2100RCP4.5 | Mississauga | Wind | RCP4.5 | 2100 | 86.1191 | 93.1086 | 100.5676 | 107.9324 | 115.3062
MississaugaWind2023RCP6.0 | Mississauga | Wind | RCP6.0 | 2023 | 85.0359 | 91.6413 | 98.6076 | 105.5626 | 112.5132
MississaugaWind2025RCP6.0 | Mississauga | Wind | RCP6.0 | 2025 | 85.0669 | 91.6868 | 98.6729 | 105.6447 | 112.6119
MississaugaWind2030RCP6.0 | Mississauga | Wind | RCP6.0 | 2030 | 85.098 | 91.7324 | 98.7383 | 105.7268 | 112.7106
MississaugaWind2035RCP6.0 | Mississauga | Wind | RCP6.0 | 2035 | 85.129 | 91.778 | 98.8036 | 105.809 | 112.8093
MississaugaWind2040RCP6.0 | Mississauga | Wind | RCP6.0 | 2040 | 85.16 | 91.8235 | 98.8689 | 105.8911 | 112.908
MississaugaWind2045RCP6.0 | Mississauga | Wind | RCP6.0 | 2045 | 85.1911 | 91.8691 | 98.9343 | 105.9733 | 113.0066
MississaugaWind2050RCP6.0 | Mississauga | Wind | RCP6.0 | 2050 | 85.2898 | 91.9967 | 99.0996 | 106.1708 | 113.2372
MississaugaWind2055RCP6.0 | Mississauga | Wind | RCP6.0 | 2055 | 85.3575 | 92.0787 | 99.1995 | 106.2861 | 113.369
MississaugaWind2060RCP6.0 | Mississauga | Wind | RCP6.0 | 2060 | 85.4252 | 92.1608 | 99.2995 | 106.4014 | 113.5008
MississaugaWind2065RCP6.0 | Mississauga | Wind | RCP6.0 | 2065 | 85.4929 | 92.2428 | 99.3994 | 106.5168 | 113.6326
MississaugaWind2070RCP6.0 | Mississauga | Wind | RCP6.0 | 2070 | 85.5606 | 92.3248 | 99.4994 | 106.6321 | 113.7645
MississaugaWind2075RCP6.0 | Mississauga | Wind | RCP6.0 | 2075 | 85.7002 | 92.5208 | 99.7665 | 106.9572 | 114.1499
MississaugaWind2080RCP6.0 | Mississauga | Wind | RCP6.0 | 2080 | 85.8398 | 92.7167 | 100.0335 | 107.2823 | 114.5353
MississaugaWind2085RCP6.0 | Mississauga | Wind | RCP6.0 | 2085 | 85.9794 | 92.9127 | 100.3006 | 107.6073 | 114.9208
MississaugaWind2090RCP6.0 | Mississauga | Wind | RCP6.0 | 2090 | 86.4124 | 93.4853 | 101.0478 | 108.5021 | 115.9691
MississaugaWind2095RCP6.0 | Mississauga | Wind | RCP6.0 | 2095 | 86.7058 | 93.862 | 101.528 | 109.0719 | 116.632
MississaugaWind2100RCP6.0 | Mississauga | Wind | RCP6.0 | 2100 | 86.9991 | 94.2388 | 102.0082 | 109.6416 | 117.2948
MississaugaWind2023RCP8.5 | Mississauga | Wind | RCP8.5 | 2023 | 85.0359 | 91.6413 | 98.6076 | 105.5626 | 112.5132
MississaugaWind2025RCP8.5 | Mississauga | Wind | RCP8.5 | 2025 | 85.098 | 91.7324 | 98.7383 | 105.7268 | 112.7106
MississaugaWind2030RCP8.5 | Mississauga | Wind | RCP8.5 | 2030 | 85.16 | 91.8235 | 98.8689 | 105.8911 | 112.908
MississaugaWind2035RCP8.5 | Mississauga | Wind | RCP8.5 | 2035 | 85.2221 | 91.9147 | 98.9996 | 106.0554 | 113.1053
MississaugaWind2040RCP8.5 | Mississauga | Wind | RCP8.5 | 2040 | 85.3349 | 92.0514 | 99.1662 | 106.2476 | 113.325
MississaugaWind2045RCP8.5 | Mississauga | Wind | RCP8.5 | 2045 | 85.4477 | 92.1881 | 99.3328 | 106.4399 | 113.5448
MississaugaWind2050RCP8.5 | Mississauga | Wind | RCP8.5 | 2050 | 85.7467 | 92.5861 | 99.8555 | 107.0656 | 114.2784
MississaugaWind2055RCP8.5 | Mississauga | Wind | RCP8.5 | 2055 | 85.9329 | 92.8474 | 100.2115 | 107.499 | 114.7923
MississaugaWind2060RCP8.5 | Mississauga | Wind | RCP8.5 | 2060 | 86.4124 | 93.4853 | 101.0478 | 108.5021 | 115.9691
MississaugaWind2065RCP8.5 | Mississauga | Wind | RCP8.5 | 2065 | 86.7058 | 93.862 | 101.528 | 109.0719 | 116.632
MississaugaWind2070RCP8.5 | Mississauga | Wind | RCP8.5 | 2070 | 87.1656 | 94.4788 | 102.3414 | 110.0506 | 117.7827
MississaugaWind2075RCP8.5 | Mississauga | Wind | RCP8.5 | 2075 | 87.332 | 94.7188 | 102.6746 | 110.4595 | 118.2705
MississaugaWind2080RCP8.5 | Mississauga | Wind | RCP8.5 | 2080 | 87.4984 | 94.9588 | 103.0078 | 110.8685 | 118.7584
MississaugaWind2085RCP8.5 | Mississauga | Wind | RCP8.5 | 2085 | 87.765 | 95.3051 | 103.4537 | 111.4033 | 119.384
MississaugaWind2090RCP8.5 | Mississauga | Wind | RCP8.5 | 2090 | 88.0315 | 95.6514 | 103.8996 | 111.938 | 120.0096
MississaugaWind2095RCP8.5 | Mississauga | Wind | RCP8.5 | 2095 | 88.0315 | 95.6514 | 103.8996 | 111.938 | 120.0096
MississaugaWind2100RCP8.5 | Mississauga | Wind | RCP8.5 | 2100 | 88.0315 | 95.6514 | 103.8996 | 111.938 | 120.0096
Mississauga Port CreditIce Accretion2023RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2023 | 16.7003 | 20.003 | 24.175 | 27.3742 | 30.555
Mississauga Port CreditIce Accretion2025RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2025 | 16.6191 | 19.9165 | 24.0833 | 27.2801 | 30.4552
Mississauga Port CreditIce Accretion2030RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2030 | 16.5379 | 19.8301 | 23.9917 | 27.1859 | 30.3555
Mississauga Port CreditIce Accretion2035RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2035 | 16.4568 | 19.7436 | 23.9 | 27.0917 | 30.2557
Mississauga Port CreditIce Accretion2040RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2040 | 16.3756 | 19.6572 | 23.8083 | 26.9976 | 30.156
Mississauga Port CreditIce Accretion2045RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2045 | 16.2944 | 19.5707 | 23.7167 | 26.9034 | 30.0562
Mississauga Port CreditIce Accretion2050RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2050 | 15.8896 | 19.1232 | 23.215 | 26.3516 | 29.4588
Mississauga Port CreditIce Accretion2055RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2055 | 15.5661 | 18.7622 | 22.805 | 25.8939 | 28.9611
Mississauga Port CreditIce Accretion2060RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2060 | 15.2425 | 18.4011 | 22.395 | 25.4363 | 28.4634
Mississauga Port CreditIce Accretion2065RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2065 | 14.9189 | 18.0401 | 21.985 | 24.9786 | 27.9657
Mississauga Port CreditIce Accretion2070RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2070 | 14.5954 | 17.679 | 21.575 | 24.521 | 27.468
Mississauga Port CreditIce Accretion2075RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2075 | 14.491 | 17.5752 | 21.4708 | 24.4174 | 27.363
Mississauga Port CreditIce Accretion2080RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2080 | 14.3866 | 17.4715 | 21.3667 | 24.3138 | 27.258
Mississauga Port CreditIce Accretion2085RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2085 | 14.2822 | 17.3678 | 21.2625 | 24.2102 | 27.153
Mississauga Port CreditIce Accretion2090RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2090 | 14.1779 | 17.264 | 21.1583 | 24.1067 | 27.048
Mississauga Port CreditIce Accretion2095RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2095 | 14.0735 | 17.1602 | 21.0542 | 24.0031 | 26.943
Mississauga Port CreditIce Accretion2100RCP4.5 | Mississauga Port Credit | Ice Accretion | RCP4.5 | 2100 | 13.9691 | 17.0565 | 20.95 | 23.8995 | 26.838
Mississauga Port CreditIce Accretion2023RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2023 | 16.7003 | 20.003 | 24.175 | 27.3742 | 30.555
Mississauga Port CreditIce Accretion2025RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2025 | 16.6191 | 19.9165 | 24.0833 | 27.2801 | 30.4552
Mississauga Port CreditIce Accretion2030RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2030 | 16.5379 | 19.8301 | 23.9917 | 27.1859 | 30.3555
Mississauga Port CreditIce Accretion2035RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2035 | 16.4568 | 19.7436 | 23.9 | 27.0917 | 30.2557
Mississauga Port CreditIce Accretion2040RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2040 | 16.3756 | 19.6572 | 23.8083 | 26.9976 | 30.156
Mississauga Port CreditIce Accretion2045RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2045 | 16.2944 | 19.5707 | 23.7167 | 26.9034 | 30.0562
Mississauga Port CreditIce Accretion2050RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2050 | 15.8896 | 19.1232 | 23.215 | 26.3516 | 29.4588
Mississauga Port CreditIce Accretion2055RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2055 | 15.5661 | 18.7622 | 22.805 | 25.8939 | 28.9611
Mississauga Port CreditIce Accretion2060RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2060 | 15.2425 | 18.4011 | 22.395 | 25.4363 | 28.4634
Mississauga Port CreditIce Accretion2065RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2065 | 14.9189 | 18.0401 | 21.985 | 24.9786 | 27.9657
Mississauga Port CreditIce Accretion2070RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2070 | 14.5954 | 17.679 | 21.575 | 24.521 | 27.468
Mississauga Port CreditIce Accretion2075RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2075 | 14.4388 | 17.5234 | 21.4187 | 24.3656 | 27.3105
Mississauga Port CreditIce Accretion2080RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2080 | 14.2822 | 17.3678 | 21.2625 | 24.2102 | 27.153
Mississauga Port CreditIce Accretion2085RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2085 | 14.1257 | 17.2121 | 21.1062 | 24.0549 | 26.9955
Mississauga Port CreditIce Accretion2090RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2090 | 13.4704 | 16.4962 | 20.3 | 23.1838 | 26.0505
Mississauga Port CreditIce Accretion2095RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2095 | 12.9717 | 15.936 | 19.65 | 22.4682 | 25.263
Mississauga Port CreditIce Accretion2100RCP6.0 | Mississauga Port Credit | Ice Accretion | RCP6.0 | 2100 | 12.473 | 15.3758 | 19 | 21.7525 | 24.4755
Mississauga Port CreditIce Accretion2023RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2023 | 16.7003 | 20.003 | 24.175 | 27.3742 | 30.555
Mississauga Port CreditIce Accretion2025RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2025 | 16.5379 | 19.8301 | 23.9917 | 27.1859 | 30.3555
Mississauga Port CreditIce Accretion2030RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2030 | 16.3756 | 19.6572 | 23.8083 | 26.9976 | 30.156
Mississauga Port CreditIce Accretion2035RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2035 | 16.2132 | 19.4843 | 23.625 | 26.8092 | 29.9565
Mississauga Port CreditIce Accretion2040RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2040 | 15.6739 | 18.8825 | 22.9417 | 26.0465 | 29.127
Mississauga Port CreditIce Accretion2045RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2045 | 15.1347 | 18.2808 | 22.2583 | 25.2837 | 28.2975
Mississauga Port CreditIce Accretion2050RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2050 | 14.3866 | 17.4715 | 21.3667 | 24.3138 | 27.258
Mississauga Port CreditIce Accretion2055RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2055 | 14.1779 | 17.264 | 21.1583 | 24.1067 | 27.048
Mississauga Port CreditIce Accretion2060RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2060 | 13.4704 | 16.4962 | 20.3 | 23.1838 | 26.0505
Mississauga Port CreditIce Accretion2065RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2065 | 12.9717 | 15.936 | 19.65 | 22.4682 | 25.263
Mississauga Port CreditIce Accretion2070RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2070 | 12.1831 | 15.0576 | 18.6417 | 21.3664 | 24.0555
Mississauga Port CreditIce Accretion2075RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2075 | 11.8932 | 14.7394 | 18.2833 | 20.9803 | 23.6355
Mississauga Port CreditIce Accretion2080RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2080 | 11.6032 | 14.4213 | 17.925 | 20.5942 | 23.2155
Mississauga Port CreditIce Accretion2085RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2085 | 10.9944 | 13.695 | 17.0625 | 19.6196 | 22.1445
Mississauga Port CreditIce Accretion2090RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2090 | 10.3855 | 12.9688 | 16.2 | 18.645 | 21.0735
Mississauga Port CreditIce Accretion2095RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2095 | 10.3855 | 12.9688 | 16.2 | 18.645 | 21.0735
Mississauga Port CreditIce Accretion2100RCP8.5 | Mississauga Port Credit | Ice Accretion | RCP8.5 | 2100 | 10.3855 | 12.9688 | 16.2 | 18.645 | 21.0735
Mississauga Port CreditWind2023RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2023 | 86.3482 | 93.1564 | 100.3662 | 107.5295 | 114.6996
Mississauga Port CreditWind2025RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2025 | 86.3282 | 93.1349 | 100.3431 | 107.5048 | 114.6733
Mississauga Port CreditWind2030RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2030 | 86.3083 | 93.1135 | 100.32 | 107.4801 | 114.6469
Mississauga Port CreditWind2035RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2035 | 86.2883 | 93.092 | 100.2969 | 107.4554 | 114.6206
Mississauga Port CreditWind2040RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2040 | 86.2684 | 93.0705 | 100.2738 | 107.4307 | 114.5943
Mississauga Port CreditWind2045RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2045 | 86.2484 | 93.049 | 100.2507 | 107.406 | 114.5679
Mississauga Port CreditWind2050RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2050 | 86.3345 | 93.1601 | 100.3939 | 107.5762 | 114.7673
Mississauga Port CreditWind2055RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2055 | 86.4405 | 93.2927 | 100.5602 | 107.7711 | 114.9931
Mississauga Port CreditWind2060RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2060 | 86.5465 | 93.4253 | 100.7266 | 107.966 | 115.2188
Mississauga Port CreditWind2065RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2065 | 86.6525 | 93.5579 | 100.8929 | 108.1609 | 115.4445
Mississauga Port CreditWind2070RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2070 | 86.7585 | 93.6904 | 101.0592 | 108.3558 | 115.6702
Mississauga Port CreditWind2075RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2075 | 86.8112 | 93.7626 | 101.1549 | 108.4741 | 115.8075
Mississauga Port CreditWind2080RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2080 | 86.8639 | 93.8347 | 101.2506 | 108.5924 | 115.9448
Mississauga Port CreditWind2085RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2085 | 86.9166 | 93.9068 | 101.3463 | 108.7107 | 116.0822
Mississauga Port CreditWind2090RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2090 | 86.9693 | 93.9789 | 101.442 | 108.829 | 116.2195
Mississauga Port CreditWind2095RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2095 | 87.0221 | 94.051 | 101.5377 | 108.9472 | 116.3568
Mississauga Port CreditWind2100RCP4.5 | Mississauga Port Credit | Wind | RCP4.5 | 2100 | 87.0748 | 94.1232 | 101.6334 | 109.0655 | 116.4941
Mississauga Port CreditWind2023RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2023 | 86.3482 | 93.1564 | 100.3662 | 107.5295 | 114.6996
Mississauga Port CreditWind2025RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2025 | 86.3282 | 93.1349 | 100.3431 | 107.5048 | 114.6733
Mississauga Port CreditWind2030RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2030 | 86.3083 | 93.1135 | 100.32 | 107.4801 | 114.6469
Mississauga Port CreditWind2035RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2035 | 86.2883 | 93.092 | 100.2969 | 107.4554 | 114.6206
Mississauga Port CreditWind2040RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2040 | 86.2684 | 93.0705 | 100.2738 | 107.4307 | 114.5943
Mississauga Port CreditWind2045RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2045 | 86.2484 | 93.049 | 100.2507 | 107.406 | 114.5679
Mississauga Port CreditWind2050RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2050 | 86.3345 | 93.1601 | 100.3939 | 107.5762 | 114.7673
Mississauga Port CreditWind2055RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2055 | 86.4405 | 93.2927 | 100.5602 | 107.7711 | 114.9931
Mississauga Port CreditWind2060RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2060 | 86.5465 | 93.4253 | 100.7266 | 107.966 | 115.2188
Mississauga Port CreditWind2065RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2065 | 86.6525 | 93.5579 | 100.8929 | 108.1609 | 115.4445
Mississauga Port CreditWind2070RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2070 | 86.7585 | 93.6904 | 101.0592 | 108.3558 | 115.6702
Mississauga Port CreditWind2075RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2075 | 86.8376 | 93.7986 | 101.2027 | 108.5332 | 115.8762
Mississauga Port CreditWind2080RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2080 | 86.9166 | 93.9068 | 101.3463 | 108.7107 | 116.0822
Mississauga Port CreditWind2085RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2085 | 86.9957 | 94.015 | 101.4898 | 108.8881 | 116.2881
Mississauga Port CreditWind2090RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2090 | 87.24 | 94.3411 | 101.9172 | 109.401 | 116.8891
Mississauga Port CreditWind2095RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2095 | 87.4053 | 94.559 | 102.201 | 109.7364 | 117.2841
Mississauga Port CreditWind2100RCP6.0 | Mississauga Port Credit | Wind | RCP6.0 | 2100 | 87.5706 | 94.7769 | 102.4848 | 110.0719 | 117.6791
Mississauga Port CreditWind2023RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2023 | 86.3482 | 93.1564 | 100.3662 | 107.5295 | 114.6996
Mississauga Port CreditWind2025RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2025 | 86.3083 | 93.1135 | 100.32 | 107.4801 | 114.6469
Mississauga Port CreditWind2030RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2030 | 86.2684 | 93.0705 | 100.2738 | 107.4307 | 114.5943
Mississauga Port CreditWind2035RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2035 | 86.2285 | 93.0275 | 100.2276 | 107.3812 | 114.5416
Mississauga Port CreditWind2040RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2040 | 86.4051 | 93.2485 | 100.5048 | 107.7061 | 114.9178
Mississauga Port CreditWind2045RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2045 | 86.5818 | 93.4695 | 100.782 | 108.0309 | 115.294
Mississauga Port CreditWind2050RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2050 | 86.8639 | 93.8347 | 101.2506 | 108.5924 | 115.9448
Mississauga Port CreditWind2055RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2055 | 86.9693 | 93.9789 | 101.442 | 108.829 | 116.2195
Mississauga Port CreditWind2060RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2060 | 87.24 | 94.3411 | 101.9172 | 109.401 | 116.8891
Mississauga Port CreditWind2065RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2065 | 87.4053 | 94.559 | 102.201 | 109.7364 | 117.2841
Mississauga Port CreditWind2070RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2070 | 87.488 | 94.6971 | 102.4122 | 110.0012 | 117.6152
Mississauga Port CreditWind2075RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2075 | 87.4053 | 94.6173 | 102.3396 | 109.9306 | 117.5512
Mississauga Port CreditWind2080RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2080 | 87.3227 | 94.5375 | 102.267 | 109.86 | 117.4873
Mississauga Port CreditWind2085RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2085 | 87.5535 | 94.8827 | 102.757 | 110.4744 | 118.2208
Mississauga Port CreditWind2090RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2090 | 87.7843 | 95.228 | 103.2471 | 111.0888 | 118.9544
Mississauga Port CreditWind2095RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2095 | 87.7843 | 95.228 | 103.2471 | 111.0888 | 118.9544
Mississauga Port CreditWind2100RCP8.5 | Mississauga Port Credit | Wind | RCP8.5 | 2100 | 87.7843 | 95.228 | 103.2471 | 111.0888 | 118.9544
MitchellIce Accretion2023RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2023 | 16.4331 | 19.7009 | 23.808 | 26.9573 | 30.0888
MitchellIce Accretion2025RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2025 | 16.4498 | 19.7341 | 23.868 | 27.0341 | 30.1846
MitchellIce Accretion2030RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2030 | 16.4665 | 19.7673 | 23.928 | 27.111 | 30.2803
MitchellIce Accretion2035RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2035 | 16.4832 | 19.8005 | 23.988 | 27.1878 | 30.3761
MitchellIce Accretion2040RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2040 | 16.4999 | 19.8337 | 24.048 | 27.2646 | 30.4718
MitchellIce Accretion2045RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2045 | 16.5166 | 19.8669 | 24.108 | 27.3415 | 30.5676
MitchellIce Accretion2050RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2050 | 16.4665 | 19.8523 | 24.1392 | 27.402 | 30.6634
MitchellIce Accretion2055RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2055 | 16.3997 | 19.8045 | 24.1104 | 27.3858 | 30.6634
MitchellIce Accretion2060RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2060 | 16.3329 | 19.7567 | 24.0816 | 27.3695 | 30.6634
MitchellIce Accretion2065RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2065 | 16.2661 | 19.7088 | 24.0528 | 27.3532 | 30.6634
MitchellIce Accretion2070RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2070 | 16.1993 | 19.661 | 24.024 | 27.337 | 30.6634
MitchellIce Accretion2075RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2075 | 16.1687 | 19.6478 | 24.036 | 27.3641 | 30.7087
MitchellIce Accretion2080RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2080 | 16.1381 | 19.6345 | 24.048 | 27.3912 | 30.7541
MitchellIce Accretion2085RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2085 | 16.1074 | 19.6212 | 24.06 | 27.4183 | 30.7994
MitchellIce Accretion2090RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2090 | 16.0768 | 19.6079 | 24.072 | 27.4454 | 30.8448
MitchellIce Accretion2095RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2095 | 16.0462 | 19.5946 | 24.084 | 27.4726 | 30.8902
MitchellIce Accretion2100RCP4.5 | Mitchell | Ice Accretion | RCP4.5 | 2100 | 16.0156 | 19.5814 | 24.096 | 27.4997 | 30.9355
MitchellIce Accretion2023RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2023 | 16.4331 | 19.7009 | 23.808 | 26.9573 | 30.0888
MitchellIce Accretion2025RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2025 | 16.4498 | 19.7341 | 23.868 | 27.0341 | 30.1846
MitchellIce Accretion2030RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2030 | 16.4665 | 19.7673 | 23.928 | 27.111 | 30.2803
MitchellIce Accretion2035RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2035 | 16.4832 | 19.8005 | 23.988 | 27.1878 | 30.3761
MitchellIce Accretion2040RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2040 | 16.4999 | 19.8337 | 24.048 | 27.2646 | 30.4718
MitchellIce Accretion2045RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2045 | 16.5166 | 19.8669 | 24.108 | 27.3415 | 30.5676
MitchellIce Accretion2050RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2050 | 16.4665 | 19.8523 | 24.1392 | 27.402 | 30.6634
MitchellIce Accretion2055RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2055 | 16.3997 | 19.8045 | 24.1104 | 27.3858 | 30.6634
MitchellIce Accretion2060RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2060 | 16.3329 | 19.7567 | 24.0816 | 27.3695 | 30.6634
MitchellIce Accretion2065RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2065 | 16.2661 | 19.7088 | 24.0528 | 27.3532 | 30.6634
MitchellIce Accretion2070RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2070 | 16.1993 | 19.661 | 24.024 | 27.337 | 30.6634
MitchellIce Accretion2075RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2075 | 16.1534 | 19.6411 | 24.042 | 27.3776 | 30.7314
MitchellIce Accretion2080RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2080 | 16.1074 | 19.6212 | 24.06 | 27.4183 | 30.7994
MitchellIce Accretion2085RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2085 | 16.0615 | 19.6013 | 24.078 | 27.459 | 30.8675
MitchellIce Accretion2090RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2090 | 15.8152 | 19.3822 | 23.888 | 27.2918 | 30.7138
MitchellIce Accretion2095RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2095 | 15.6148 | 19.183 | 23.68 | 27.0838 | 30.492
MitchellIce Accretion2100RCP6.0 | Mitchell | Ice Accretion | RCP6.0 | 2100 | 15.4144 | 18.9838 | 23.472 | 26.8759 | 30.2702
MitchellIce Accretion2023RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2023 | 16.4331 | 19.7009 | 23.808 | 26.9573 | 30.0888
MitchellIce Accretion2025RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2025 | 16.4665 | 19.7673 | 23.928 | 27.111 | 30.2803
MitchellIce Accretion2030RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2030 | 16.4999 | 19.8337 | 24.048 | 27.2646 | 30.4718
MitchellIce Accretion2035RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2035 | 16.5333 | 19.9001 | 24.168 | 27.4183 | 30.6634
MitchellIce Accretion2040RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2040 | 16.422 | 19.8204 | 24.12 | 27.3912 | 30.6634
MitchellIce Accretion2045RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2045 | 16.3106 | 19.7407 | 24.072 | 27.3641 | 30.6634
MitchellIce Accretion2050RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2050 | 16.1381 | 19.6345 | 24.048 | 27.3912 | 30.7541
MitchellIce Accretion2055RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2055 | 16.0768 | 19.6079 | 24.072 | 27.4454 | 30.8448
MitchellIce Accretion2060RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2060 | 15.8152 | 19.3822 | 23.888 | 27.2918 | 30.7138
MitchellIce Accretion2065RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2065 | 15.6148 | 19.183 | 23.68 | 27.0838 | 30.492
MitchellIce Accretion2070RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2070 | 15.0525 | 18.5787 | 23.016 | 26.3787 | 29.7259
MitchellIce Accretion2075RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2075 | 14.6907 | 18.1737 | 22.56 | 25.8815 | 29.1816
MitchellIce Accretion2080RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2080 | 14.3289 | 17.7686 | 22.104 | 25.3843 | 28.6373
MitchellIce Accretion2085RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2085 | 13.5773 | 16.8822 | 21.048 | 24.2046 | 27.337
MitchellIce Accretion2090RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2090 | 12.8258 | 15.9958 | 19.992 | 23.0249 | 26.0366
MitchellIce Accretion2095RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2095 | 12.8258 | 15.9958 | 19.992 | 23.0249 | 26.0366
MitchellIce Accretion2100RCP8.5 | Mitchell | Ice Accretion | RCP8.5 | 2100 | 12.8258 | 15.9958 | 19.992 | 23.0249 | 26.0366
MitchellWind2023RCP4.5 | Mitchell | Wind | RCP4.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
MitchellWind2025RCP4.5 | Mitchell | Wind | RCP4.5 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
MitchellWind2030RCP4.5 | Mitchell | Wind | RCP4.5 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
MitchellWind2035RCP4.5 | Mitchell | Wind | RCP4.5 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
MitchellWind2040RCP4.5 | Mitchell | Wind | RCP4.5 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
MitchellWind2045RCP4.5 | Mitchell | Wind | RCP4.5 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
MitchellWind2050RCP4.5 | Mitchell | Wind | RCP4.5 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
MitchellWind2055RCP4.5 | Mitchell | Wind | RCP4.5 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
MitchellWind2060RCP4.5 | Mitchell | Wind | RCP4.5 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
MitchellWind2065RCP4.5 | Mitchell | Wind | RCP4.5 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
MitchellWind2070RCP4.5 | Mitchell | Wind | RCP4.5 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
MitchellWind2075RCP4.5 | Mitchell | Wind | RCP4.5 | 2075 | 86.3504 | 93.3577 | 100.8387 | 108.226 | 115.6228
MitchellWind2080RCP4.5 | Mitchell | Wind | RCP4.5 | 2080 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
MitchellWind2085RCP4.5 | Mitchell | Wind | RCP4.5 | 2085 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
MitchellWind2090RCP4.5 | Mitchell | Wind | RCP4.5 | 2090 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
MitchellWind2095RCP4.5 | Mitchell | Wind | RCP4.5 | 2095 | 86.7678 | 93.9167 | 101.5705 | 109.1068 | 116.6655
MitchellWind2100RCP4.5 | Mitchell | Wind | RCP4.5 | 2100 | 86.8722 | 94.0565 | 101.7534 | 109.327 | 116.9262
MitchellWind2023RCP6.0 | Mitchell | Wind | RCP6.0 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
MitchellWind2025RCP6.0 | Mitchell | Wind | RCP6.0 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
MitchellWind2030RCP6.0 | Mitchell | Wind | RCP6.0 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
MitchellWind2035RCP6.0 | Mitchell | Wind | RCP6.0 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
MitchellWind2040RCP6.0 | Mitchell | Wind | RCP6.0 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
MitchellWind2045RCP6.0 | Mitchell | Wind | RCP6.0 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
MitchellWind2050RCP6.0 | Mitchell | Wind | RCP6.0 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
MitchellWind2055RCP6.0 | Mitchell | Wind | RCP6.0 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
MitchellWind2060RCP6.0 | Mitchell | Wind | RCP6.0 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
MitchellWind2065RCP6.0 | Mitchell | Wind | RCP6.0 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
MitchellWind2070RCP6.0 | Mitchell | Wind | RCP6.0 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
MitchellWind2075RCP6.0 | Mitchell | Wind | RCP6.0 | 2075 | 86.4026 | 93.4276 | 100.9302 | 108.3361 | 115.7531
MitchellWind2080RCP6.0 | Mitchell | Wind | RCP6.0 | 2080 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
MitchellWind2085RCP6.0 | Mitchell | Wind | RCP6.0 | 2085 | 86.7157 | 93.8469 | 101.479 | 108.9967 | 116.5351
MitchellWind2090RCP6.0 | Mitchell | Wind | RCP6.0 | 2090 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
MitchellWind2095RCP6.0 | Mitchell | Wind | RCP6.0 | 2095 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
MitchellWind2100RCP6.0 | Mitchell | Wind | RCP6.0 | 2100 | 87.7861 | 95.1502 | 103.0568 | 110.8265 | 118.6131
MitchellWind2023RCP8.5 | Mitchell | Wind | RCP8.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
MitchellWind2025RCP8.5 | Mitchell | Wind | RCP8.5 | 2025 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
MitchellWind2030RCP8.5 | Mitchell | Wind | RCP8.5 | 2030 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
MitchellWind2035RCP8.5 | Mitchell | Wind | RCP8.5 | 2035 | 86.0768 | 93.0084 | 100.3912 | 107.7017 | 115.0269
MitchellWind2040RCP8.5 | Mitchell | Wind | RCP8.5 | 2040 | 86.1332 | 93.0782 | 100.4794 | 107.8031 | 115.1386
MitchellWind2045RCP8.5 | Mitchell | Wind | RCP8.5 | 2045 | 86.1896 | 93.1481 | 100.5676 | 107.9044 | 115.2504
MitchellWind2050RCP8.5 | Mitchell | Wind | RCP8.5 | 2050 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
MitchellWind2055RCP8.5 | Mitchell | Wind | RCP8.5 | 2055 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
MitchellWind2060RCP8.5 | Mitchell | Wind | RCP8.5 | 2060 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
MitchellWind2065RCP8.5 | Mitchell | Wind | RCP8.5 | 2065 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
MitchellWind2070RCP8.5 | Mitchell | Wind | RCP8.5 | 2070 | 88.0541 | 95.5026 | 103.5207 | 111.3788 | 119.2611
MitchellWind2075RCP8.5 | Mitchell | Wind | RCP8.5 | 2075 | 88.322 | 95.855 | 103.9845 | 111.9311 | 119.9091
MitchellWind2080RCP8.5 | Mitchell | Wind | RCP8.5 | 2080 | 88.59 | 96.2074 | 104.4484 | 112.4833 | 120.5571
MitchellWind2085RCP8.5 | Mitchell | Wind | RCP8.5 | 2085 | 88.9454 | 96.6585 | 105.0217 | 113.1649 | 121.3447
MitchellWind2090RCP8.5 | Mitchell | Wind | RCP8.5 | 2090 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
MitchellWind2095RCP8.5 | Mitchell | Wind | RCP8.5 | 2095 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
MitchellWind2100RCP8.5 | Mitchell | Wind | RCP8.5 | 2100 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
MoosoneeIce Accretion2023RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2023 | 10.6256 | 12.6492 | 15.195 | 17.1534 | 19.1079
MoosoneeIce Accretion2025RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2025 | 10.6969 | 12.7363 | 15.305 | 17.2805 | 19.2528
MoosoneeIce Accretion2030RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2030 | 10.7682 | 12.8235 | 15.415 | 17.4076 | 19.3977
MoosoneeIce Accretion2035RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2035 | 10.8395 | 12.9107 | 15.525 | 17.5348 | 19.5426
MoosoneeIce Accretion2040RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2040 | 10.9109 | 12.9978 | 15.635 | 17.6619 | 19.6875
MoosoneeIce Accretion2045RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2045 | 10.9822 | 13.0849 | 15.745 | 17.789 | 19.8324
MoosoneeIce Accretion2050RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2050 | 11.0368 | 13.1646 | 15.858 | 17.9263 | 19.9962
MoosoneeIce Accretion2055RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2055 | 11.0201 | 13.1572 | 15.861 | 17.9365 | 20.0151
MoosoneeIce Accretion2060RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2060 | 11.0034 | 13.1497 | 15.864 | 17.9467 | 20.034
MoosoneeIce Accretion2065RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2065 | 10.9867 | 13.1422 | 15.867 | 17.9568 | 20.0529
MoosoneeIce Accretion2070RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2070 | 10.97 | 13.1347 | 15.87 | 17.967 | 20.0718
MoosoneeIce Accretion2075RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2075 | 10.8865 | 13.0455 | 15.775 | 17.8681 | 19.9647
MoosoneeIce Accretion2080RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2080 | 10.803 | 12.9563 | 15.68 | 17.7692 | 19.8576
MoosoneeIce Accretion2085RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2085 | 10.7195 | 12.8671 | 15.585 | 17.6704 | 19.7505
MoosoneeIce Accretion2090RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2090 | 10.636 | 12.7778 | 15.49 | 17.5715 | 19.6434
MoosoneeIce Accretion2095RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2095 | 10.5525 | 12.6886 | 15.395 | 17.4726 | 19.5363
MoosoneeIce Accretion2100RCP4.5 | Moosonee | Ice Accretion | RCP4.5 | 2100 | 10.469 | 12.5994 | 15.3 | 17.3737 | 19.4292
MoosoneeIce Accretion2023RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2023 | 10.6256 | 12.6492 | 15.195 | 17.1534 | 19.1079
MoosoneeIce Accretion2025RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2025 | 10.6969 | 12.7363 | 15.305 | 17.2805 | 19.2528
MoosoneeIce Accretion2030RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2030 | 10.7682 | 12.8235 | 15.415 | 17.4076 | 19.3977
MoosoneeIce Accretion2035RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2035 | 10.8395 | 12.9107 | 15.525 | 17.5348 | 19.5426
MoosoneeIce Accretion2040RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2040 | 10.9109 | 12.9978 | 15.635 | 17.6619 | 19.6875
MoosoneeIce Accretion2045RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2045 | 10.9822 | 13.0849 | 15.745 | 17.789 | 19.8324
MoosoneeIce Accretion2050RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2050 | 11.0368 | 13.1646 | 15.858 | 17.9263 | 19.9962
MoosoneeIce Accretion2055RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2055 | 11.0201 | 13.1572 | 15.861 | 17.9365 | 20.0151
MoosoneeIce Accretion2060RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2060 | 11.0034 | 13.1497 | 15.864 | 17.9467 | 20.034
MoosoneeIce Accretion2065RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2065 | 10.9867 | 13.1422 | 15.867 | 17.9568 | 20.0529
MoosoneeIce Accretion2070RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2070 | 10.97 | 13.1347 | 15.87 | 17.967 | 20.0718
MoosoneeIce Accretion2075RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2075 | 10.8448 | 13.0009 | 15.7275 | 17.8187 | 19.9111
MoosoneeIce Accretion2080RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2080 | 10.7195 | 12.8671 | 15.585 | 17.6704 | 19.7505
MoosoneeIce Accretion2085RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2085 | 10.5943 | 12.7332 | 15.4425 | 17.5221 | 19.5898
MoosoneeIce Accretion2090RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2090 | 10.1628 | 12.2549 | 14.905 | 16.9387 | 18.9504
MoosoneeIce Accretion2095RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2095 | 9.8567 | 11.9105 | 14.51 | 16.5037 | 18.4716
MoosoneeIce Accretion2100RCP6.0 | Moosonee | Ice Accretion | RCP6.0 | 2100 | 9.5505 | 11.5661 | 14.115 | 16.0686 | 17.9928
MoosoneeIce Accretion2023RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2023 | 10.6256 | 12.6492 | 15.195 | 17.1534 | 19.1079
MoosoneeIce Accretion2025RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2025 | 10.7682 | 12.8235 | 15.415 | 17.4076 | 19.3977
MoosoneeIce Accretion2030RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2030 | 10.9109 | 12.9978 | 15.635 | 17.6619 | 19.6875
MoosoneeIce Accretion2035RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2035 | 11.0535 | 13.1721 | 15.855 | 17.9161 | 19.9773
MoosoneeIce Accretion2040RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2040 | 11.0257 | 13.1596 | 15.86 | 17.9331 | 20.0088
MoosoneeIce Accretion2045RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2045 | 10.9978 | 13.1472 | 15.865 | 17.95 | 20.0403
MoosoneeIce Accretion2050RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2050 | 10.803 | 12.9563 | 15.68 | 17.7692 | 19.8576
MoosoneeIce Accretion2055RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2055 | 10.636 | 12.7778 | 15.49 | 17.5715 | 19.6434
MoosoneeIce Accretion2060RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2060 | 10.1628 | 12.2549 | 14.905 | 16.9387 | 18.9504
MoosoneeIce Accretion2065RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2065 | 9.8567 | 11.9105 | 14.51 | 16.5037 | 18.4716
MoosoneeIce Accretion2070RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2070 | 9.2756 | 11.2631 | 13.775 | 15.6957 | 17.5959
MoosoneeIce Accretion2075RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2075 | 9.0008 | 10.9602 | 13.435 | 15.3228 | 17.199
MoosoneeIce Accretion2080RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2080 | 8.7259 | 10.6572 | 13.095 | 14.9499 | 16.8021
MoosoneeIce Accretion2085RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2085 | 8.2823 | 10.1592 | 12.525 | 14.3312 | 16.1217
MoosoneeIce Accretion2090RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2090 | 7.8387 | 9.6612 | 11.955 | 13.7125 | 15.4413
MoosoneeIce Accretion2095RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2095 | 7.8387 | 9.6612 | 11.955 | 13.7125 | 15.4413
MoosoneeIce Accretion2100RCP8.5 | Moosonee | Ice Accretion | RCP8.5 | 2100 | 7.8387 | 9.6612 | 11.955 | 13.7125 | 15.4413
MoosoneeWind2023RCP4.5 | Moosonee | Wind | RCP4.5 | 2023 | 77.2022 | 83.2886 | 89.7248 | 96.1279 | 102.5371
MoosoneeWind2025RCP4.5 | Moosonee | Wind | RCP4.5 | 2025 | 77.315 | 83.4195 | 89.8803 | 96.3037 | 102.7327
MoosoneeWind2030RCP4.5 | Moosonee | Wind | RCP4.5 | 2030 | 77.4277 | 83.5505 | 90.0357 | 96.4795 | 102.9283
MoosoneeWind2035RCP4.5 | Moosonee | Wind | RCP4.5 | 2035 | 77.5404 | 83.6814 | 90.1912 | 96.6552 | 103.1239
MoosoneeWind2040RCP4.5 | Moosonee | Wind | RCP4.5 | 2040 | 77.6531 | 83.8123 | 90.3467 | 96.831 | 103.3196
MoosoneeWind2045RCP4.5 | Moosonee | Wind | RCP4.5 | 2045 | 77.7658 | 83.9433 | 90.5021 | 97.0068 | 103.5152
MoosoneeWind2050RCP4.5 | Moosonee | Wind | RCP4.5 | 2050 | 77.9287 | 84.1282 | 90.7122 | 97.239 | 103.771
MoosoneeWind2055RCP4.5 | Moosonee | Wind | RCP4.5 | 2055 | 77.9788 | 84.1823 | 90.7667 | 97.2955 | 103.8312
MoosoneeWind2060RCP4.5 | Moosonee | Wind | RCP4.5 | 2060 | 78.029 | 84.2363 | 90.8213 | 97.352 | 103.8914
MoosoneeWind2065RCP4.5 | Moosonee | Wind | RCP4.5 | 2065 | 78.0791 | 84.2903 | 90.8758 | 97.4085 | 103.9516
MoosoneeWind2070RCP4.5 | Moosonee | Wind | RCP4.5 | 2070 | 78.1293 | 84.3443 | 90.9304 | 97.465 | 104.0118
MoosoneeWind2075RCP4.5 | Moosonee | Wind | RCP4.5 | 2075 | 78.1343 | 84.3348 | 90.9025 | 97.4226 | 103.9549
MoosoneeWind2080RCP4.5 | Moosonee | Wind | RCP4.5 | 2080 | 78.1394 | 84.3252 | 90.8747 | 97.3803 | 103.8981
MoosoneeWind2085RCP4.5 | Moosonee | Wind | RCP4.5 | 2085 | 78.1445 | 84.3157 | 90.8468 | 97.3379 | 103.8412
MoosoneeWind2090RCP4.5 | Moosonee | Wind | RCP4.5 | 2090 | 78.1495 | 84.3061 | 90.8189 | 97.2955 | 103.7844
MoosoneeWind2095RCP4.5 | Moosonee | Wind | RCP4.5 | 2095 | 78.1546 | 84.2966 | 90.7911 | 97.2532 | 103.7275
MoosoneeWind2100RCP4.5 | Moosonee | Wind | RCP4.5 | 2100 | 78.1597 | 84.287 | 90.7632 | 97.2108 | 103.6707
MoosoneeWind2023RCP6.0 | Moosonee | Wind | RCP6.0 | 2023 | 77.2022 | 83.2886 | 89.7248 | 96.1279 | 102.5371
MoosoneeWind2025RCP6.0 | Moosonee | Wind | RCP6.0 | 2025 | 77.315 | 83.4195 | 89.8803 | 96.3037 | 102.7327
MoosoneeWind2030RCP6.0 | Moosonee | Wind | RCP6.0 | 2030 | 77.4277 | 83.5505 | 90.0357 | 96.4795 | 102.9283
MoosoneeWind2035RCP6.0 | Moosonee | Wind | RCP6.0 | 2035 | 77.5404 | 83.6814 | 90.1912 | 96.6552 | 103.1239
MoosoneeWind2040RCP6.0 | Moosonee | Wind | RCP6.0 | 2040 | 77.6531 | 83.8123 | 90.3467 | 96.831 | 103.3196
MoosoneeWind2045RCP6.0 | Moosonee | Wind | RCP6.0 | 2045 | 77.7658 | 83.9433 | 90.5021 | 97.0068 | 103.5152
MoosoneeWind2050RCP6.0 | Moosonee | Wind | RCP6.0 | 2050 | 77.9287 | 84.1282 | 90.7122 | 97.239 | 103.771
MoosoneeWind2055RCP6.0 | Moosonee | Wind | RCP6.0 | 2055 | 77.9788 | 84.1823 | 90.7667 | 97.2955 | 103.8312
MoosoneeWind2060RCP6.0 | Moosonee | Wind | RCP6.0 | 2060 | 78.029 | 84.2363 | 90.8213 | 97.352 | 103.8914
MoosoneeWind2065RCP6.0 | Moosonee | Wind | RCP6.0 | 2065 | 78.0791 | 84.2903 | 90.8758 | 97.4085 | 103.9516
MoosoneeWind2070RCP6.0 | Moosonee | Wind | RCP6.0 | 2070 | 78.1293 | 84.3443 | 90.9304 | 97.465 | 104.0118
MoosoneeWind2075RCP6.0 | Moosonee | Wind | RCP6.0 | 2075 | 78.1369 | 84.33 | 90.8886 | 97.4015 | 103.9265
MoosoneeWind2080RCP6.0 | Moosonee | Wind | RCP6.0 | 2080 | 78.1445 | 84.3157 | 90.8468 | 97.3379 | 103.8412
MoosoneeWind2085RCP6.0 | Moosonee | Wind | RCP6.0 | 2085 | 78.1521 | 84.3013 | 90.805 | 97.2743 | 103.756
MoosoneeWind2090RCP6.0 | Moosonee | Wind | RCP6.0 | 2090 | 78.3674 | 84.5134 | 91.0096 | 97.4776 | 103.9549
MoosoneeWind2095RCP6.0 | Moosonee | Wind | RCP6.0 | 2095 | 78.5751 | 84.7399 | 91.256 | 97.7444 | 104.2392
MoosoneeWind2100RCP6.0 | Moosonee | Wind | RCP6.0 | 2100 | 78.7828 | 84.9663 | 91.5024 | 98.0111 | 104.5234
MoosoneeWind2023RCP8.5 | Moosonee | Wind | RCP8.5 | 2023 | 77.2022 | 83.2886 | 89.7248 | 96.1279 | 102.5371
MoosoneeWind2025RCP8.5 | Moosonee | Wind | RCP8.5 | 2025 | 77.4277 | 83.5505 | 90.0357 | 96.4795 | 102.9283
MoosoneeWind2030RCP8.5 | Moosonee | Wind | RCP8.5 | 2030 | 77.6531 | 83.8123 | 90.3467 | 96.831 | 103.3196
MoosoneeWind2035RCP8.5 | Moosonee | Wind | RCP8.5 | 2035 | 77.8785 | 84.0742 | 90.6576 | 97.1825 | 103.7108
MoosoneeWind2040RCP8.5 | Moosonee | Wind | RCP8.5 | 2040 | 77.9621 | 84.1643 | 90.7485 | 97.2767 | 103.8111
MoosoneeWind2045RCP8.5 | Moosonee | Wind | RCP8.5 | 2045 | 78.0457 | 84.2543 | 90.8395 | 97.3709 | 103.9115
MoosoneeWind2050RCP8.5 | Moosonee | Wind | RCP8.5 | 2050 | 78.1394 | 84.3252 | 90.8747 | 97.3803 | 103.8981
MoosoneeWind2055RCP8.5 | Moosonee | Wind | RCP8.5 | 2055 | 78.1495 | 84.3061 | 90.8189 | 97.2955 | 103.7844
MoosoneeWind2060RCP8.5 | Moosonee | Wind | RCP8.5 | 2060 | 78.3674 | 84.5134 | 91.0096 | 97.4776 | 103.9549
MoosoneeWind2065RCP8.5 | Moosonee | Wind | RCP8.5 | 2065 | 78.5751 | 84.7399 | 91.256 | 97.7444 | 104.2392
MoosoneeWind2070RCP8.5 | Moosonee | Wind | RCP8.5 | 2070 | 78.8157 | 84.9772 | 91.4789 | 97.9641 | 104.4498
MoosoneeWind2075RCP8.5 | Moosonee | Wind | RCP8.5 | 2075 | 78.8486 | 84.9881 | 91.4555 | 97.917 | 104.3763
MoosoneeWind2080RCP8.5 | Moosonee | Wind | RCP8.5 | 2080 | 78.8815 | 84.999 | 91.432 | 97.8699 | 104.3027
MoosoneeWind2085RCP8.5 | Moosonee | Wind | RCP8.5 | 2085 | 78.9385 | 85.0481 | 91.4716 | 97.8982 | 104.3228
MoosoneeWind2090RCP8.5 | Moosonee | Wind | RCP8.5 | 2090 | 78.9955 | 85.0972 | 91.5112 | 97.9264 | 104.3428
MoosoneeWind2095RCP8.5 | Moosonee | Wind | RCP8.5 | 2095 | 78.9955 | 85.0972 | 91.5112 | 97.9264 | 104.3428
MoosoneeWind2100RCP8.5 | Moosonee | Wind | RCP8.5 | 2100 | 78.9955 | 85.0972 | 91.5112 | 97.9264 | 104.3428
MorrisburgIce Accretion2023RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2023 | 21.0215 | 25.0743 | 30.21 | 34.1373 | 38.0646
MorrisburgIce Accretion2025RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2025 | 21.0737 | 25.1531 | 30.325 | 34.2842 | 38.2347
MorrisburgIce Accretion2030RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2030 | 21.1259 | 25.232 | 30.44 | 34.4311 | 38.4048
MorrisburgIce Accretion2035RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2035 | 21.1781 | 25.3108 | 30.555 | 34.578 | 38.5749
MorrisburgIce Accretion2040RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2040 | 21.2303 | 25.3897 | 30.67 | 34.7249 | 38.745
MorrisburgIce Accretion2045RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2045 | 21.2825 | 25.4686 | 30.785 | 34.8718 | 38.9151
MorrisburgIce Accretion2050RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2050 | 21.3054 | 25.5325 | 30.9 | 35.0187 | 39.1003
MorrisburgIce Accretion2055RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2055 | 21.2762 | 25.5175 | 30.9 | 35.0187 | 39.1154
MorrisburgIce Accretion2060RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2060 | 21.247 | 25.5026 | 30.9 | 35.0187 | 39.1306
MorrisburgIce Accretion2065RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2065 | 21.2177 | 25.4876 | 30.9 | 35.0187 | 39.1457
MorrisburgIce Accretion2070RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2070 | 21.1885 | 25.4727 | 30.9 | 35.0187 | 39.1608
MorrisburgIce Accretion2075RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2075 | 21.2859 | 25.6138 | 31.1 | 35.2616 | 39.4443
MorrisburgIce Accretion2080RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2080 | 21.3834 | 25.7549 | 31.3 | 35.5046 | 39.7278
MorrisburgIce Accretion2085RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2085 | 21.4808 | 25.896 | 31.5 | 35.7475 | 40.0113
MorrisburgIce Accretion2090RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2090 | 21.5782 | 26.0371 | 31.7 | 35.9905 | 40.2948
MorrisburgIce Accretion2095RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2095 | 21.6756 | 26.1782 | 31.9 | 36.2334 | 40.5783
MorrisburgIce Accretion2100RCP4.5 | Morrisburg | Ice Accretion | RCP4.5 | 2100 | 21.773 | 26.3193 | 32.1 | 36.4764 | 40.8618
MorrisburgIce Accretion2023RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2023 | 21.0215 | 25.0743 | 30.21 | 34.1373 | 38.0646
MorrisburgIce Accretion2025RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2025 | 21.0737 | 25.1531 | 30.325 | 34.2842 | 38.2347
MorrisburgIce Accretion2030RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2030 | 21.1259 | 25.232 | 30.44 | 34.4311 | 38.4048
MorrisburgIce Accretion2035RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2035 | 21.1781 | 25.3108 | 30.555 | 34.578 | 38.5749
MorrisburgIce Accretion2040RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2040 | 21.2303 | 25.3897 | 30.67 | 34.7249 | 38.745
MorrisburgIce Accretion2045RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2045 | 21.2825 | 25.4686 | 30.785 | 34.8718 | 38.9151
MorrisburgIce Accretion2050RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2050 | 21.3054 | 25.5325 | 30.9 | 35.0187 | 39.1003
MorrisburgIce Accretion2055RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2055 | 21.2762 | 25.5175 | 30.9 | 35.0187 | 39.1154
MorrisburgIce Accretion2060RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2060 | 21.247 | 25.5026 | 30.9 | 35.0187 | 39.1306
MorrisburgIce Accretion2065RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2065 | 21.2177 | 25.4876 | 30.9 | 35.0187 | 39.1457
MorrisburgIce Accretion2070RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2070 | 21.1885 | 25.4727 | 30.9 | 35.0187 | 39.1608
MorrisburgIce Accretion2075RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2075 | 21.3346 | 25.6843 | 31.2 | 35.3831 | 39.586
MorrisburgIce Accretion2080RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2080 | 21.4808 | 25.896 | 31.5 | 35.7475 | 40.0113
MorrisburgIce Accretion2085RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2085 | 21.6269 | 26.1076 | 31.8 | 36.112 | 40.4365
MorrisburgIce Accretion2090RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2090 | 21.6269 | 26.1948 | 31.98 | 36.3634 | 40.761
MorrisburgIce Accretion2095RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2095 | 21.4808 | 26.0703 | 31.86 | 36.2504 | 40.6602
MorrisburgIce Accretion2100RCP6.0 | Morrisburg | Ice Accretion | RCP6.0 | 2100 | 21.3346 | 25.9458 | 31.74 | 36.1374 | 40.5594
MorrisburgIce Accretion2023RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2023 | 21.0215 | 25.0743 | 30.21 | 34.1373 | 38.0646
MorrisburgIce Accretion2025RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2025 | 21.1259 | 25.232 | 30.44 | 34.4311 | 38.4048
MorrisburgIce Accretion2030RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2030 | 21.2303 | 25.3897 | 30.67 | 34.7249 | 38.745
MorrisburgIce Accretion2035RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2035 | 21.3346 | 25.5474 | 30.9 | 35.0187 | 39.0852
MorrisburgIce Accretion2040RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2040 | 21.2859 | 25.5225 | 30.9 | 35.0187 | 39.1104
MorrisburgIce Accretion2045RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2045 | 21.2372 | 25.4976 | 30.9 | 35.0187 | 39.1356
MorrisburgIce Accretion2050RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2050 | 21.3834 | 25.7549 | 31.3 | 35.5046 | 39.7278
MorrisburgIce Accretion2055RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2055 | 21.5782 | 26.0371 | 31.7 | 35.9905 | 40.2948
MorrisburgIce Accretion2060RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2060 | 21.6269 | 26.1948 | 31.98 | 36.3634 | 40.761
MorrisburgIce Accretion2065RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2065 | 21.4808 | 26.0703 | 31.86 | 36.2504 | 40.6602
MorrisburgIce Accretion2070RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2070 | 21.0563 | 25.6387 | 31.4 | 35.7758 | 40.1688
MorrisburgIce Accretion2075RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2075 | 20.778 | 25.3316 | 31.06 | 35.4142 | 39.7782
MorrisburgIce Accretion2080RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2080 | 20.4996 | 25.0245 | 30.72 | 35.0526 | 39.3876
MorrisburgIce Accretion2085RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2085 | 19.6333 | 24.0036 | 29.52 | 33.6966 | 37.8756
MorrisburgIce Accretion2090RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2090 | 18.767 | 22.9827 | 28.32 | 32.3406 | 36.3636
MorrisburgIce Accretion2095RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2095 | 18.767 | 22.9827 | 28.32 | 32.3406 | 36.3636
MorrisburgIce Accretion2100RCP8.5 | Morrisburg | Ice Accretion | RCP8.5 | 2100 | 18.767 | 22.9827 | 28.32 | 32.3406 | 36.3636
MorrisburgWind2023RCP4.5 | Morrisburg | Wind | RCP4.5 | 2023 | 80.9302 | 87.2425 | 93.8928 | 100.535 | 107.165
MorrisburgWind2025RCP4.5 | Morrisburg | Wind | RCP4.5 | 2025 | 80.9731 | 87.2828 | 93.9316 | 100.5731 | 107.2021
MorrisburgWind2030RCP4.5 | Morrisburg | Wind | RCP4.5 | 2030 | 81.0159 | 87.3232 | 93.9703 | 100.6112 | 107.2392
MorrisburgWind2035RCP4.5 | Morrisburg | Wind | RCP4.5 | 2035 | 81.0587 | 87.3635 | 94.0091 | 100.6494 | 107.2763
MorrisburgWind2040RCP4.5 | Morrisburg | Wind | RCP4.5 | 2040 | 81.1016 | 87.4039 | 94.0478 | 100.6875 | 107.3134
MorrisburgWind2045RCP4.5 | Morrisburg | Wind | RCP4.5 | 2045 | 81.1444 | 87.4443 | 94.0866 | 100.7257 | 107.3506
MorrisburgWind2050RCP4.5 | Morrisburg | Wind | RCP4.5 | 2050 | 81.1631 | 87.4552 | 94.09 | 100.72 | 107.3389
MorrisburgWind2055RCP4.5 | Morrisburg | Wind | RCP4.5 | 2055 | 81.139 | 87.4258 | 94.0546 | 100.6763 | 107.2901
MorrisburgWind2060RCP4.5 | Morrisburg | Wind | RCP4.5 | 2060 | 81.1149 | 87.3964 | 94.0193 | 100.6325 | 107.2414
MorrisburgWind2065RCP4.5 | Morrisburg | Wind | RCP4.5 | 2065 | 81.0908 | 87.367 | 93.9839 | 100.5887 | 107.1926
MorrisburgWind2070RCP4.5 | Morrisburg | Wind | RCP4.5 | 2070 | 81.0668 | 87.3376 | 93.9486 | 100.5449 | 107.1438
MorrisburgWind2075RCP4.5 | Morrisburg | Wind | RCP4.5 | 2075 | 81.0467 | 87.316 | 93.9253 | 100.5217 | 107.1191
MorrisburgWind2080RCP4.5 | Morrisburg | Wind | RCP4.5 | 2080 | 81.0266 | 87.2944 | 93.9021 | 100.4985 | 107.0943
MorrisburgWind2085RCP4.5 | Morrisburg | Wind | RCP4.5 | 2085 | 81.0065 | 87.2727 | 93.8788 | 100.4752 | 107.0696
MorrisburgWind2090RCP4.5 | Morrisburg | Wind | RCP4.5 | 2090 | 80.9864 | 87.2511 | 93.8556 | 100.452 | 107.0449
MorrisburgWind2095RCP4.5 | Morrisburg | Wind | RCP4.5 | 2095 | 80.9664 | 87.2295 | 93.8323 | 100.4288 | 107.0201
MorrisburgWind2100RCP4.5 | Morrisburg | Wind | RCP4.5 | 2100 | 80.9463 | 87.2079 | 93.8091 | 100.4056 | 106.9954
MorrisburgWind2023RCP6.0 | Morrisburg | Wind | RCP6.0 | 2023 | 80.9302 | 87.2425 | 93.8928 | 100.535 | 107.165
MorrisburgWind2025RCP6.0 | Morrisburg | Wind | RCP6.0 | 2025 | 80.9731 | 87.2828 | 93.9316 | 100.5731 | 107.2021
MorrisburgWind2030RCP6.0 | Morrisburg | Wind | RCP6.0 | 2030 | 81.0159 | 87.3232 | 93.9703 | 100.6112 | 107.2392
MorrisburgWind2035RCP6.0 | Morrisburg | Wind | RCP6.0 | 2035 | 81.0587 | 87.3635 | 94.0091 | 100.6494 | 107.2763
MorrisburgWind2040RCP6.0 | Morrisburg | Wind | RCP6.0 | 2040 | 81.1016 | 87.4039 | 94.0478 | 100.6875 | 107.3134
MorrisburgWind2045RCP6.0 | Morrisburg | Wind | RCP6.0 | 2045 | 81.1444 | 87.4443 | 94.0866 | 100.7257 | 107.3506
MorrisburgWind2050RCP6.0 | Morrisburg | Wind | RCP6.0 | 2050 | 81.1631 | 87.4552 | 94.09 | 100.72 | 107.3389
MorrisburgWind2055RCP6.0 | Morrisburg | Wind | RCP6.0 | 2055 | 81.139 | 87.4258 | 94.0546 | 100.6763 | 107.2901
MorrisburgWind2060RCP6.0 | Morrisburg | Wind | RCP6.0 | 2060 | 81.1149 | 87.3964 | 94.0193 | 100.6325 | 107.2414
MorrisburgWind2065RCP6.0 | Morrisburg | Wind | RCP6.0 | 2065 | 81.0908 | 87.367 | 93.9839 | 100.5887 | 107.1926
MorrisburgWind2070RCP6.0 | Morrisburg | Wind | RCP6.0 | 2070 | 81.0668 | 87.3376 | 93.9486 | 100.5449 | 107.1438
MorrisburgWind2075RCP6.0 | Morrisburg | Wind | RCP6.0 | 2075 | 81.0366 | 87.3052 | 93.9137 | 100.5101 | 107.1067
MorrisburgWind2080RCP6.0 | Morrisburg | Wind | RCP6.0 | 2080 | 81.0065 | 87.2727 | 93.8788 | 100.4752 | 107.0696
MorrisburgWind2085RCP6.0 | Morrisburg | Wind | RCP6.0 | 2085 | 80.9764 | 87.2403 | 93.844 | 100.4404 | 107.0325
MorrisburgWind2090RCP6.0 | Morrisburg | Wind | RCP6.0 | 2090 | 80.8954 | 87.1473 | 93.7347 | 100.3193 | 106.9
MorrisburgWind2095RCP6.0 | Morrisburg | Wind | RCP6.0 | 2095 | 80.8446 | 87.0868 | 93.6603 | 100.2331 | 106.8045
MorrisburgWind2100RCP6.0 | Morrisburg | Wind | RCP6.0 | 2100 | 80.7937 | 87.0262 | 93.5859 | 100.1469 | 106.7091
MorrisburgWind2023RCP8.5 | Morrisburg | Wind | RCP8.5 | 2023 | 80.9302 | 87.2425 | 93.8928 | 100.535 | 107.165
MorrisburgWind2025RCP8.5 | Morrisburg | Wind | RCP8.5 | 2025 | 81.0159 | 87.3232 | 93.9703 | 100.6112 | 107.2392
MorrisburgWind2030RCP8.5 | Morrisburg | Wind | RCP8.5 | 2030 | 81.1016 | 87.4039 | 94.0478 | 100.6875 | 107.3134
MorrisburgWind2035RCP8.5 | Morrisburg | Wind | RCP8.5 | 2035 | 81.1872 | 87.4846 | 94.1253 | 100.7638 | 107.3877
MorrisburgWind2040RCP8.5 | Morrisburg | Wind | RCP8.5 | 2040 | 81.1471 | 87.4356 | 94.0664 | 100.6909 | 107.3064
MorrisburgWind2045RCP8.5 | Morrisburg | Wind | RCP8.5 | 2045 | 81.1069 | 87.3866 | 94.0075 | 100.6179 | 107.2251
MorrisburgWind2050RCP8.5 | Morrisburg | Wind | RCP8.5 | 2050 | 81.0266 | 87.2944 | 93.9021 | 100.4985 | 107.0943
MorrisburgWind2055RCP8.5 | Morrisburg | Wind | RCP8.5 | 2055 | 80.9864 | 87.2511 | 93.8556 | 100.452 | 107.0449
MorrisburgWind2060RCP8.5 | Morrisburg | Wind | RCP8.5 | 2060 | 80.8954 | 87.1473 | 93.7347 | 100.3193 | 106.9
MorrisburgWind2065RCP8.5 | Morrisburg | Wind | RCP8.5 | 2065 | 80.8446 | 87.0868 | 93.6603 | 100.2331 | 106.8045
MorrisburgWind2070RCP8.5 | Morrisburg | Wind | RCP8.5 | 2070 | 80.9517 | 87.2367 | 93.8618 | 100.4786 | 107.0943
MorrisburgWind2075RCP8.5 | Morrisburg | Wind | RCP8.5 | 2075 | 81.1096 | 87.4472 | 94.1377 | 100.8103 | 107.4795
MorrisburgWind2080RCP8.5 | Morrisburg | Wind | RCP8.5 | 2080 | 81.2675 | 87.6576 | 94.4136 | 101.142 | 107.8647
MorrisburgWind2085RCP8.5 | Morrisburg | Wind | RCP8.5 | 2085 | 81.1471 | 87.4803 | 94.1671 | 100.8385 | 107.499
MorrisburgWind2090RCP8.5 | Morrisburg | Wind | RCP8.5 | 2090 | 81.0266 | 87.303 | 93.9207 | 100.535 | 107.1332
MorrisburgWind2095RCP8.5 | Morrisburg | Wind | RCP8.5 | 2095 | 81.0266 | 87.303 | 93.9207 | 100.535 | 107.1332
MorrisburgWind2100RCP8.5 | Morrisburg | Wind | RCP8.5 | 2100 | 81.0266 | 87.303 | 93.9207 | 100.535 | 107.1332
Mount ForestIce Accretion2023RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2023 | 15.2933 | 18.333 | 22.198 | 25.1335 | 28.0804
Mount ForestIce Accretion2025RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2025 | 15.2984 | 18.3543 | 22.231 | 25.179 | 28.1404
Mount ForestIce Accretion2030RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2030 | 15.3035 | 18.3756 | 22.264 | 25.2246 | 28.2005
Mount ForestIce Accretion2035RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2035 | 15.3086 | 18.3969 | 22.297 | 25.2702 | 28.2605
Mount ForestIce Accretion2040RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2040 | 15.3137 | 18.4183 | 22.33 | 25.3158 | 28.3206
Mount ForestIce Accretion2045RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2045 | 15.3188 | 18.4396 | 22.363 | 25.3613 | 28.3807
Mount ForestIce Accretion2050RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2050 | 15.3178 | 18.4718 | 22.4356 | 25.4666 | 28.5183
Mount ForestIce Accretion2055RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2055 | 15.3117 | 18.4828 | 22.4752 | 25.5262 | 28.596
Mount ForestIce Accretion2060RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2060 | 15.3056 | 18.4937 | 22.5148 | 25.5859 | 28.6736
Mount ForestIce Accretion2065RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2065 | 15.2994 | 18.5047 | 22.5544 | 25.6456 | 28.7512
Mount ForestIce Accretion2070RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2070 | 15.2933 | 18.5156 | 22.594 | 25.7052 | 28.8288
Mount ForestIce Accretion2075RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2075 | 15.227 | 18.4609 | 22.5573 | 25.6762 | 28.8103
Mount ForestIce Accretion2080RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2080 | 15.1606 | 18.4061 | 22.5207 | 25.6472 | 28.7918
Mount ForestIce Accretion2085RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2085 | 15.0943 | 18.3513 | 22.484 | 25.6182 | 28.7734
Mount ForestIce Accretion2090RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2090 | 15.028 | 18.2965 | 22.4473 | 25.5892 | 28.7549
Mount ForestIce Accretion2095RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2095 | 14.9616 | 18.2417 | 22.4107 | 25.5602 | 28.7364
Mount ForestIce Accretion2100RCP4.5 | Mount Forest | Ice Accretion | RCP4.5 | 2100 | 14.8953 | 18.187 | 22.374 | 25.5312 | 28.7179
Mount ForestIce Accretion2023RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2023 | 15.2933 | 18.333 | 22.198 | 25.1335 | 28.0804
Mount ForestIce Accretion2025RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2025 | 15.2984 | 18.3543 | 22.231 | 25.179 | 28.1404
Mount ForestIce Accretion2030RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2030 | 15.3035 | 18.3756 | 22.264 | 25.2246 | 28.2005
Mount ForestIce Accretion2035RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2035 | 15.3086 | 18.3969 | 22.297 | 25.2702 | 28.2605
Mount ForestIce Accretion2040RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2040 | 15.3137 | 18.4183 | 22.33 | 25.3158 | 28.3206
Mount ForestIce Accretion2045RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2045 | 15.3188 | 18.4396 | 22.363 | 25.3613 | 28.3807
Mount ForestIce Accretion2050RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2050 | 15.3178 | 18.4718 | 22.4356 | 25.4666 | 28.5183
Mount ForestIce Accretion2055RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2055 | 15.3117 | 18.4828 | 22.4752 | 25.5262 | 28.596
Mount ForestIce Accretion2060RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2060 | 15.3056 | 18.4937 | 22.5148 | 25.5859 | 28.6736
Mount ForestIce Accretion2065RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2065 | 15.2994 | 18.5047 | 22.5544 | 25.6456 | 28.7512
Mount ForestIce Accretion2070RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2070 | 15.2933 | 18.5156 | 22.594 | 25.7052 | 28.8288
Mount ForestIce Accretion2075RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2075 | 15.1938 | 18.4335 | 22.539 | 25.6617 | 28.8011
Mount ForestIce Accretion2080RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2080 | 15.0943 | 18.3513 | 22.484 | 25.6182 | 28.7734
Mount ForestIce Accretion2085RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2085 | 14.9948 | 18.2691 | 22.429 | 25.5747 | 28.7456
Mount ForestIce Accretion2090RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2090 | 14.6401 | 17.9191 | 22.0733 | 25.2163 | 28.376
Mount ForestIce Accretion2095RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2095 | 14.385 | 17.6513 | 21.7727 | 24.9014 | 28.0342
Mount ForestIce Accretion2100RCP6.0 | Mount Forest | Ice Accretion | RCP6.0 | 2100 | 14.1299 | 17.3835 | 21.472 | 24.5865 | 27.6923
Mount ForestIce Accretion2023RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2023 | 15.2933 | 18.333 | 22.198 | 25.1335 | 28.0804
Mount ForestIce Accretion2025RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2025 | 15.3035 | 18.3756 | 22.264 | 25.2246 | 28.2005
Mount ForestIce Accretion2030RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2030 | 15.3137 | 18.4183 | 22.33 | 25.3158 | 28.3206
Mount ForestIce Accretion2035RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2035 | 15.3239 | 18.4609 | 22.396 | 25.4069 | 28.4407
Mount ForestIce Accretion2040RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2040 | 15.3137 | 18.4791 | 22.462 | 25.5064 | 28.5701
Mount ForestIce Accretion2045RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2045 | 15.3035 | 18.4974 | 22.528 | 25.6058 | 28.6994
Mount ForestIce Accretion2050RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2050 | 15.1606 | 18.4061 | 22.5207 | 25.6472 | 28.7918
Mount ForestIce Accretion2055RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2055 | 15.028 | 18.2965 | 22.4473 | 25.5892 | 28.7549
Mount ForestIce Accretion2060RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2060 | 14.6401 | 17.9191 | 22.0733 | 25.2163 | 28.376
Mount ForestIce Accretion2065RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2065 | 14.385 | 17.6513 | 21.7727 | 24.9014 | 28.0342
Mount ForestIce Accretion2070RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2070 | 13.7114 | 16.9088 | 20.9367 | 23.9982 | 27.0547
Mount ForestIce Accretion2075RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2075 | 13.293 | 16.434 | 20.4013 | 23.4098 | 26.4172
Mount ForestIce Accretion2080RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2080 | 12.8745 | 15.9592 | 19.866 | 22.8215 | 25.7796
Mount ForestIce Accretion2085RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2085 | 12.4536 | 15.4936 | 19.338 | 22.2497 | 25.1698
Mount ForestIce Accretion2090RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2090 | 12.0326 | 15.028 | 18.81 | 21.6779 | 24.5599
Mount ForestIce Accretion2095RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2095 | 12.0326 | 15.028 | 18.81 | 21.6779 | 24.5599
Mount ForestIce Accretion2100RCP8.5 | Mount Forest | Ice Accretion | RCP8.5 | 2100 | 12.0326 | 15.028 | 18.81 | 21.6779 | 24.5599
Mount ForestWind2023RCP4.5 | Mount Forest | Wind | RCP4.5 | 2023 | 83.5906 | 90.1639 | 97.1136 | 104.0245 | 110.9393
Mount ForestWind2025RCP4.5 | Mount Forest | Wind | RCP4.5 | 2025 | 83.6708 | 90.2621 | 97.2368 | 104.1684 | 111.1053
Mount ForestWind2030RCP4.5 | Mount Forest | Wind | RCP4.5 | 2030 | 83.7509 | 90.3603 | 97.36 | 104.3122 | 111.2713
Mount ForestWind2035RCP4.5 | Mount Forest | Wind | RCP4.5 | 2035 | 83.831 | 90.4585 | 97.4832 | 104.456 | 111.4373
Mount ForestWind2040RCP4.5 | Mount Forest | Wind | RCP4.5 | 2040 | 83.9111 | 90.5567 | 97.6064 | 104.5998 | 111.6033
Mount ForestWind2045RCP4.5 | Mount Forest | Wind | RCP4.5 | 2045 | 83.9913 | 90.6549 | 97.7296 | 104.7436 | 111.7692
Mount ForestWind2050RCP4.5 | Mount Forest | Wind | RCP4.5 | 2050 | 84.0847 | 90.7656 | 97.8624 | 104.8956 | 111.9418
Mount ForestWind2055RCP4.5 | Mount Forest | Wind | RCP4.5 | 2055 | 84.0979 | 90.7781 | 97.872 | 104.9038 | 111.9484
Mount ForestWind2060RCP4.5 | Mount Forest | Wind | RCP4.5 | 2060 | 84.1112 | 90.7906 | 97.8816 | 104.912 | 111.9549
Mount ForestWind2065RCP4.5 | Mount Forest | Wind | RCP4.5 | 2065 | 84.1245 | 90.8031 | 97.8912 | 104.9203 | 111.9615
Mount ForestWind2070RCP4.5 | Mount Forest | Wind | RCP4.5 | 2070 | 84.1377 | 90.8156 | 97.9008 | 104.9285 | 111.9681
Mount ForestWind2075RCP4.5 | Mount Forest | Wind | RCP4.5 | 2075 | 84.2192 | 90.9213 | 98.0368 | 105.0911 | 112.1559
Mount ForestWind2080RCP4.5 | Mount Forest | Wind | RCP4.5 | 2080 | 84.3008 | 91.0269 | 98.1728 | 105.2538 | 112.3438
Mount ForestWind2085RCP4.5 | Mount Forest | Wind | RCP4.5 | 2085 | 84.3823 | 91.1326 | 98.3088 | 105.4164 | 112.5317
Mount ForestWind2090RCP4.5 | Mount Forest | Wind | RCP4.5 | 2090 | 84.4638 | 91.2382 | 98.4448 | 105.579 | 112.7196
Mount ForestWind2095RCP4.5 | Mount Forest | Wind | RCP4.5 | 2095 | 84.5453 | 91.3439 | 98.5808 | 105.7417 | 112.9074
Mount ForestWind2100RCP4.5 | Mount Forest | Wind | RCP4.5 | 2100 | 84.6268 | 91.4495 | 98.7168 | 105.9043 | 113.0953
Mount ForestWind2023RCP6.0 | Mount Forest | Wind | RCP6.0 | 2023 | 83.5906 | 90.1639 | 97.1136 | 104.0245 | 110.9393
Mount ForestWind2025RCP6.0 | Mount Forest | Wind | RCP6.0 | 2025 | 83.6708 | 90.2621 | 97.2368 | 104.1684 | 111.1053
Mount ForestWind2030RCP6.0 | Mount Forest | Wind | RCP6.0 | 2030 | 83.7509 | 90.3603 | 97.36 | 104.3122 | 111.2713
Mount ForestWind2035RCP6.0 | Mount Forest | Wind | RCP6.0 | 2035 | 83.831 | 90.4585 | 97.4832 | 104.456 | 111.4373
Mount ForestWind2040RCP6.0 | Mount Forest | Wind | RCP6.0 | 2040 | 83.9111 | 90.5567 | 97.6064 | 104.5998 | 111.6033
Mount ForestWind2045RCP6.0 | Mount Forest | Wind | RCP6.0 | 2045 | 83.9913 | 90.6549 | 97.7296 | 104.7436 | 111.7692
Mount ForestWind2050RCP6.0 | Mount Forest | Wind | RCP6.0 | 2050 | 84.0847 | 90.7656 | 97.8624 | 104.8956 | 111.9418
Mount ForestWind2055RCP6.0 | Mount Forest | Wind | RCP6.0 | 2055 | 84.0979 | 90.7781 | 97.872 | 104.9038 | 111.9484
Mount ForestWind2060RCP6.0 | Mount Forest | Wind | RCP6.0 | 2060 | 84.1112 | 90.7906 | 97.8816 | 104.912 | 111.9549
Mount ForestWind2065RCP6.0 | Mount Forest | Wind | RCP6.0 | 2065 | 84.1245 | 90.8031 | 97.8912 | 104.9203 | 111.9615
Mount ForestWind2070RCP6.0 | Mount Forest | Wind | RCP6.0 | 2070 | 84.1377 | 90.8156 | 97.9008 | 104.9285 | 111.9681
Mount ForestWind2075RCP6.0 | Mount Forest | Wind | RCP6.0 | 2075 | 84.26 | 90.9741 | 98.1048 | 105.1724 | 112.2499
Mount ForestWind2080RCP6.0 | Mount Forest | Wind | RCP6.0 | 2080 | 84.3823 | 91.1326 | 98.3088 | 105.4164 | 112.5317
Mount ForestWind2085RCP6.0 | Mount Forest | Wind | RCP6.0 | 2085 | 84.5045 | 91.291 | 98.5128 | 105.6604 | 112.8135
Mount ForestWind2090RCP6.0 | Mount Forest | Wind | RCP6.0 | 2090 | 85.0302 | 91.9554 | 99.3472 | 106.6439 | 113.9489
Mount ForestWind2095RCP6.0 | Mount Forest | Wind | RCP6.0 | 2095 | 85.4336 | 92.4613 | 99.9776 | 107.3835 | 114.8026
Mount ForestWind2100RCP6.0 | Mount Forest | Wind | RCP6.0 | 2100 | 85.8371 | 92.9673 | 100.608 | 108.1231 | 115.6562
Mount ForestWind2023RCP8.5 | Mount Forest | Wind | RCP8.5 | 2023 | 83.5906 | 90.1639 | 97.1136 | 104.0245 | 110.9393
Mount ForestWind2025RCP8.5 | Mount Forest | Wind | RCP8.5 | 2025 | 83.7509 | 90.3603 | 97.36 | 104.3122 | 111.2713
Mount ForestWind2030RCP8.5 | Mount Forest | Wind | RCP8.5 | 2030 | 83.9111 | 90.5567 | 97.6064 | 104.5998 | 111.6033
Mount ForestWind2035RCP8.5 | Mount Forest | Wind | RCP8.5 | 2035 | 84.0714 | 90.7531 | 97.8528 | 104.8874 | 111.9352
Mount ForestWind2040RCP8.5 | Mount Forest | Wind | RCP8.5 | 2040 | 84.0935 | 90.774 | 97.8688 | 104.9011 | 111.9462
Mount ForestWind2045RCP8.5 | Mount Forest | Wind | RCP8.5 | 2045 | 84.1156 | 90.7948 | 97.8848 | 104.9148 | 111.9571
Mount ForestWind2050RCP8.5 | Mount Forest | Wind | RCP8.5 | 2050 | 84.3008 | 91.0269 | 98.1728 | 105.2538 | 112.3438
Mount ForestWind2055RCP8.5 | Mount Forest | Wind | RCP8.5 | 2055 | 84.4638 | 91.2382 | 98.4448 | 105.579 | 112.7196
Mount ForestWind2060RCP8.5 | Mount Forest | Wind | RCP8.5 | 2060 | 85.0302 | 91.9554 | 99.3472 | 106.6439 | 113.9489
Mount ForestWind2065RCP8.5 | Mount Forest | Wind | RCP8.5 | 2065 | 85.4336 | 92.4613 | 99.9776 | 107.3835 | 114.8026
Mount ForestWind2070RCP8.5 | Mount Forest | Wind | RCP8.5 | 2070 | 86.0471 | 93.2232 | 100.9216 | 108.486 | 116.0684
Mount ForestWind2075RCP8.5 | Mount Forest | Wind | RCP8.5 | 2075 | 86.2571 | 93.4791 | 101.2352 | 108.849 | 116.4806
Mount ForestWind2080RCP8.5 | Mount Forest | Wind | RCP8.5 | 2080 | 86.4671 | 93.7351 | 101.5488 | 109.2119 | 116.8929
Mount ForestWind2085RCP8.5 | Mount Forest | Wind | RCP8.5 | 2085 | 86.4878 | 93.744 | 101.5488 | 109.1965 | 116.871
Mount ForestWind2090RCP8.5 | Mount Forest | Wind | RCP8.5 | 2090 | 86.5085 | 93.7529 | 101.5488 | 109.1811 | 116.8491
Mount ForestWind2095RCP8.5 | Mount Forest | Wind | RCP8.5 | 2095 | 86.5085 | 93.7529 | 101.5488 | 109.1811 | 116.8491
Mount ForestWind2100RCP8.5 | Mount Forest | Wind | RCP8.5 | 2100 | 86.5085 | 93.7529 | 101.5488 | 109.1811 | 116.8491
NakinaIce Accretion2023RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2023 | 8.442 | 10.0596 | 12.108 | 13.682 | 15.2561
NakinaIce Accretion2025RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2025 | 8.5213 | 10.1542 | 12.222 | 13.8086 | 15.3972
NakinaIce Accretion2030RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2030 | 8.6007 | 10.2488 | 12.336 | 13.9352 | 15.5383
NakinaIce Accretion2035RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2035 | 8.68 | 10.3435 | 12.45 | 14.0617 | 15.6794
NakinaIce Accretion2040RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2040 | 8.7593 | 10.4381 | 12.564 | 14.1883 | 15.8206
NakinaIce Accretion2045RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2045 | 8.8386 | 10.5327 | 12.678 | 14.3148 | 15.9617
NakinaIce Accretion2050RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2050 | 8.958 | 10.6711 | 12.84 | 14.4956 | 16.1603
NakinaIce Accretion2055RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2055 | 8.9981 | 10.715 | 12.888 | 14.5499 | 16.2177
NakinaIce Accretion2060RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2060 | 9.0382 | 10.7588 | 12.936 | 14.6041 | 16.2752
NakinaIce Accretion2065RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2065 | 9.0783 | 10.8026 | 12.984 | 14.6584 | 16.3326
NakinaIce Accretion2070RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2070 | 9.1184 | 10.8464 | 13.032 | 14.7126 | 16.3901
NakinaIce Accretion2075RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2075 | 9.1198 | 10.8498 | 13.038 | 14.7194 | 16.3976
NakinaIce Accretion2080RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2080 | 9.1212 | 10.8531 | 13.044 | 14.7262 | 16.4052
NakinaIce Accretion2085RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2085 | 9.1225 | 10.8564 | 13.05 | 14.7329 | 16.4128
NakinaIce Accretion2090RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2090 | 9.1239 | 10.8597 | 13.056 | 14.7397 | 16.4203
NakinaIce Accretion2095RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2095 | 9.1253 | 10.863 | 13.062 | 14.7465 | 16.4279
NakinaIce Accretion2100RCP4.5 | Nakina | Ice Accretion | RCP4.5 | 2100 | 9.1267 | 10.8664 | 13.068 | 14.7533 | 16.4354
NakinaIce Accretion2023RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2023 | 8.442 | 10.0596 | 12.108 | 13.682 | 15.2561
NakinaIce Accretion2025RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2025 | 8.5213 | 10.1542 | 12.222 | 13.8086 | 15.3972
NakinaIce Accretion2030RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2030 | 8.6007 | 10.2488 | 12.336 | 13.9352 | 15.5383
NakinaIce Accretion2035RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2035 | 8.68 | 10.3435 | 12.45 | 14.0617 | 15.6794
NakinaIce Accretion2040RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2040 | 8.7593 | 10.4381 | 12.564 | 14.1883 | 15.8206
NakinaIce Accretion2045RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2045 | 8.8386 | 10.5327 | 12.678 | 14.3148 | 15.9617
NakinaIce Accretion2050RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2050 | 8.958 | 10.6711 | 12.84 | 14.4956 | 16.1603
NakinaIce Accretion2055RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2055 | 8.9981 | 10.715 | 12.888 | 14.5499 | 16.2177
NakinaIce Accretion2060RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2060 | 9.0382 | 10.7588 | 12.936 | 14.6041 | 16.2752
NakinaIce Accretion2065RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2065 | 9.0783 | 10.8026 | 12.984 | 14.6584 | 16.3326
NakinaIce Accretion2070RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2070 | 9.1184 | 10.8464 | 13.032 | 14.7126 | 16.3901
NakinaIce Accretion2075RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2075 | 9.1205 | 10.8514 | 13.041 | 14.7228 | 16.4014
NakinaIce Accretion2080RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2080 | 9.1225 | 10.8564 | 13.05 | 14.7329 | 16.4128
NakinaIce Accretion2085RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2085 | 9.1246 | 10.8614 | 13.059 | 14.7431 | 16.4241
NakinaIce Accretion2090RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2090 | 9.0404 | 10.7634 | 12.944 | 14.6132 | 16.2792
NakinaIce Accretion2095RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2095 | 8.9541 | 10.6605 | 12.82 | 14.473 | 16.123
NakinaIce Accretion2100RCP6.0 | Nakina | Ice Accretion | RCP6.0 | 2100 | 8.8679 | 10.5576 | 12.696 | 14.3329 | 15.9667
NakinaIce Accretion2023RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2023 | 8.442 | 10.0596 | 12.108 | 13.682 | 15.2561
NakinaIce Accretion2025RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2025 | 8.6007 | 10.2488 | 12.336 | 13.9352 | 15.5383
NakinaIce Accretion2030RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2030 | 8.7593 | 10.4381 | 12.564 | 14.1883 | 15.8206
NakinaIce Accretion2035RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2035 | 8.918 | 10.6273 | 12.792 | 14.4414 | 16.1028
NakinaIce Accretion2040RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2040 | 8.9848 | 10.7004 | 12.872 | 14.5318 | 16.1986
NakinaIce Accretion2045RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2045 | 9.0516 | 10.7734 | 12.952 | 14.6222 | 16.2943
NakinaIce Accretion2050RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2050 | 9.1212 | 10.8531 | 13.044 | 14.7262 | 16.4052
NakinaIce Accretion2055RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2055 | 9.1239 | 10.8597 | 13.056 | 14.7397 | 16.4203
NakinaIce Accretion2060RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2060 | 9.0404 | 10.7634 | 12.944 | 14.6132 | 16.2792
NakinaIce Accretion2065RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2065 | 8.9541 | 10.6605 | 12.82 | 14.473 | 16.123
NakinaIce Accretion2070RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2070 | 8.8595 | 10.5576 | 12.708 | 14.3555 | 15.997
NakinaIce Accretion2075RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2075 | 8.8512 | 10.5576 | 12.72 | 14.3781 | 16.0272
NakinaIce Accretion2080RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2080 | 8.8428 | 10.5576 | 12.732 | 14.4007 | 16.0574
NakinaIce Accretion2085RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2085 | 8.8595 | 10.5974 | 12.798 | 14.4821 | 16.1633
NakinaIce Accretion2090RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2090 | 8.8762 | 10.6373 | 12.864 | 14.5634 | 16.2691
NakinaIce Accretion2095RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2095 | 8.8762 | 10.6373 | 12.864 | 14.5634 | 16.2691
NakinaIce Accretion2100RCP8.5 | Nakina | Ice Accretion | RCP8.5 | 2100 | 8.8762 | 10.6373 | 12.864 | 14.5634 | 16.2691
NakinaWind2023RCP4.5 | Nakina | Wind | RCP4.5 | 2023 | 69.2858 | 74.5934 | 80.16 | 85.7455 | 91.3186
NakinaWind2025RCP4.5 | Nakina | Wind | RCP4.5 | 2025 | 69.3998 | 74.7323 | 80.332 | 85.9438 | 91.5466
NakinaWind2030RCP4.5 | Nakina | Wind | RCP4.5 | 2030 | 69.5138 | 74.8712 | 80.504 | 86.1421 | 91.7746
NakinaWind2035RCP4.5 | Nakina | Wind | RCP4.5 | 2035 | 69.6278 | 75.0101 | 80.676 | 86.3404 | 92.0026
NakinaWind2040RCP4.5 | Nakina | Wind | RCP4.5 | 2040 | 69.7417 | 75.149 | 80.848 | 86.5387 | 92.2306
NakinaWind2045RCP4.5 | Nakina | Wind | RCP4.5 | 2045 | 69.8557 | 75.2878 | 81.02 | 86.7371 | 92.4586
NakinaWind2050RCP4.5 | Nakina | Wind | RCP4.5 | 2050 | 70.0595 | 75.5339 | 81.3184 | 87.0775 | 92.8452
NakinaWind2055RCP4.5 | Nakina | Wind | RCP4.5 | 2055 | 70.1493 | 75.641 | 81.4448 | 87.2196 | 93.0039
NakinaWind2060RCP4.5 | Nakina | Wind | RCP4.5 | 2060 | 70.2391 | 75.7481 | 81.5712 | 87.3616 | 93.1626
NakinaWind2065RCP4.5 | Nakina | Wind | RCP4.5 | 2065 | 70.3289 | 75.8553 | 81.6976 | 87.5037 | 93.3213
NakinaWind2070RCP4.5 | Nakina | Wind | RCP4.5 | 2070 | 70.4187 | 75.9624 | 81.824 | 87.6458 | 93.48
NakinaWind2075RCP4.5 | Nakina | Wind | RCP4.5 | 2075 | 70.5085 | 76.069 | 81.9507 | 87.7914 | 93.6426
NakinaWind2080RCP4.5 | Nakina | Wind | RCP4.5 | 2080 | 70.5983 | 76.1757 | 82.0773 | 87.9369 | 93.8053
NakinaWind2085RCP4.5 | Nakina | Wind | RCP4.5 | 2085 | 70.6881 | 76.2823 | 82.204 | 88.0824 | 93.9679
NakinaWind2090RCP4.5 | Nakina | Wind | RCP4.5 | 2090 | 70.7779 | 76.389 | 82.3307 | 88.2279 | 94.1306
NakinaWind2095RCP4.5 | Nakina | Wind | RCP4.5 | 2095 | 70.8677 | 76.4956 | 82.4573 | 88.3734 | 94.2932
NakinaWind2100RCP4.5 | Nakina | Wind | RCP4.5 | 2100 | 70.9575 | 76.6022 | 82.584 | 88.519 | 94.4558
NakinaWind2023RCP6.0 | Nakina | Wind | RCP6.0 | 2023 | 69.2858 | 74.5934 | 80.16 | 85.7455 | 91.3186
NakinaWind2025RCP6.0 | Nakina | Wind | RCP6.0 | 2025 | 69.3998 | 74.7323 | 80.332 | 85.9438 | 91.5466
NakinaWind2030RCP6.0 | Nakina | Wind | RCP6.0 | 2030 | 69.5138 | 74.8712 | 80.504 | 86.1421 | 91.7746
NakinaWind2035RCP6.0 | Nakina | Wind | RCP6.0 | 2035 | 69.6278 | 75.0101 | 80.676 | 86.3404 | 92.0026
NakinaWind2040RCP6.0 | Nakina | Wind | RCP6.0 | 2040 | 69.7417 | 75.149 | 80.848 | 86.5387 | 92.2306
NakinaWind2045RCP6.0 | Nakina | Wind | RCP6.0 | 2045 | 69.8557 | 75.2878 | 81.02 | 86.7371 | 92.4586
NakinaWind2050RCP6.0 | Nakina | Wind | RCP6.0 | 2050 | 70.0595 | 75.5339 | 81.3184 | 87.0775 | 92.8452
NakinaWind2055RCP6.0 | Nakina | Wind | RCP6.0 | 2055 | 70.1493 | 75.641 | 81.4448 | 87.2196 | 93.0039
NakinaWind2060RCP6.0 | Nakina | Wind | RCP6.0 | 2060 | 70.2391 | 75.7481 | 81.5712 | 87.3616 | 93.1626
NakinaWind2065RCP6.0 | Nakina | Wind | RCP6.0 | 2065 | 70.3289 | 75.8553 | 81.6976 | 87.5037 | 93.3213
NakinaWind2070RCP6.0 | Nakina | Wind | RCP6.0 | 2070 | 70.4187 | 75.9624 | 81.824 | 87.6458 | 93.48
NakinaWind2075RCP6.0 | Nakina | Wind | RCP6.0 | 2075 | 70.5534 | 76.1224 | 82.014 | 87.8641 | 93.724
NakinaWind2080RCP6.0 | Nakina | Wind | RCP6.0 | 2080 | 70.6881 | 76.2823 | 82.204 | 88.0824 | 93.9679
NakinaWind2085RCP6.0 | Nakina | Wind | RCP6.0 | 2085 | 70.8228 | 76.4423 | 82.394 | 88.3007 | 94.2119
NakinaWind2090RCP6.0 | Nakina | Wind | RCP6.0 | 2090 | 71.0151 | 76.6742 | 82.672 | 88.6217 | 94.5744
NakinaWind2095RCP6.0 | Nakina | Wind | RCP6.0 | 2095 | 71.0727 | 76.7461 | 82.76 | 88.7244 | 94.693
NakinaWind2100RCP6.0 | Nakina | Wind | RCP6.0 | 2100 | 71.1302 | 76.818 | 82.848 | 88.8271 | 94.8115
NakinaWind2023RCP8.5 | Nakina | Wind | RCP8.5 | 2023 | 69.2858 | 74.5934 | 80.16 | 85.7455 | 91.3186
NakinaWind2025RCP8.5 | Nakina | Wind | RCP8.5 | 2025 | 69.5138 | 74.8712 | 80.504 | 86.1421 | 91.7746
NakinaWind2030RCP8.5 | Nakina | Wind | RCP8.5 | 2030 | 69.7417 | 75.149 | 80.848 | 86.5387 | 92.2306
NakinaWind2035RCP8.5 | Nakina | Wind | RCP8.5 | 2035 | 69.9697 | 75.4267 | 81.192 | 86.9354 | 92.6866
NakinaWind2040RCP8.5 | Nakina | Wind | RCP8.5 | 2040 | 70.1194 | 75.6053 | 81.4027 | 87.1722 | 92.951
NakinaWind2045RCP8.5 | Nakina | Wind | RCP8.5 | 2045 | 70.269 | 75.7838 | 81.6133 | 87.409 | 93.2155
NakinaWind2050RCP8.5 | Nakina | Wind | RCP8.5 | 2050 | 70.5983 | 76.1757 | 82.0773 | 87.9369 | 93.8053
NakinaWind2055RCP8.5 | Nakina | Wind | RCP8.5 | 2055 | 70.7779 | 76.389 | 82.3307 | 88.2279 | 94.1306
NakinaWind2060RCP8.5 | Nakina | Wind | RCP8.5 | 2060 | 71.0151 | 76.6742 | 82.672 | 88.6217 | 94.5744
NakinaWind2065RCP8.5 | Nakina | Wind | RCP8.5 | 2065 | 71.0727 | 76.7461 | 82.76 | 88.7244 | 94.693
NakinaWind2070RCP8.5 | Nakina | Wind | RCP8.5 | 2070 | 71.1279 | 76.8056 | 82.824 | 88.7929 | 94.769
NakinaWind2075RCP8.5 | Nakina | Wind | RCP8.5 | 2075 | 71.1256 | 76.7932 | 82.8 | 88.7586 | 94.7264
NakinaWind2080RCP8.5 | Nakina | Wind | RCP8.5 | 2080 | 71.1233 | 76.7808 | 82.776 | 88.7244 | 94.6838
NakinaWind2085RCP8.5 | Nakina | Wind | RCP8.5 | 2085 | 71.1993 | 76.8701 | 82.884 | 88.8485 | 94.8252
NakinaWind2090RCP8.5 | Nakina | Wind | RCP8.5 | 2090 | 71.2753 | 76.9594 | 82.992 | 88.9726 | 94.9666
NakinaWind2095RCP8.5 | Nakina | Wind | RCP8.5 | 2095 | 71.2753 | 76.9594 | 82.992 | 88.9726 | 94.9666
NakinaWind2100RCP8.5 | Nakina | Wind | RCP8.5 | 2100 | 71.2753 | 76.9594 | 82.992 | 88.9726 | 94.9666
Nanticoke (Jarvis)Ice Accretion2023RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2023 | 23.2802 | 27.9096 | 33.796 | 38.2663 | 42.7543
Nanticoke (Jarvis)Ice Accretion2025RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2025 | 23.1619 | 27.7826 | 33.6543 | 38.119 | 42.5972
Nanticoke (Jarvis)Ice Accretion2030RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2030 | 23.0436 | 27.6556 | 33.5127 | 37.9718 | 42.4402
Nanticoke (Jarvis)Ice Accretion2035RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2035 | 22.9253 | 27.5286 | 33.371 | 37.8245 | 42.2831
Nanticoke (Jarvis)Ice Accretion2040RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2040 | 22.8071 | 27.4016 | 33.2293 | 37.6772 | 42.126
Nanticoke (Jarvis)Ice Accretion2045RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2045 | 22.6888 | 27.2746 | 33.0877 | 37.5299 | 41.9689
Nanticoke (Jarvis)Ice Accretion2050RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2050 | 22.2534 | 26.8034 | 32.572 | 36.9754 | 41.3749
Nanticoke (Jarvis)Ice Accretion2055RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2055 | 21.9364 | 26.4591 | 32.198 | 36.5682 | 40.9379
Nanticoke (Jarvis)Ice Accretion2060RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2060 | 21.6194 | 26.1148 | 31.824 | 36.1609 | 40.5009
Nanticoke (Jarvis)Ice Accretion2065RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2065 | 21.3024 | 25.7705 | 31.45 | 35.7537 | 40.064
Nanticoke (Jarvis)Ice Accretion2070RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2070 | 20.9853 | 25.4262 | 31.076 | 35.3464 | 39.627
Nanticoke (Jarvis)Ice Accretion2075RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2075 | 20.8828 | 25.3369 | 30.9967 | 35.276 | 39.5556
Nanticoke (Jarvis)Ice Accretion2080RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2080 | 20.7803 | 25.2475 | 30.9173 | 35.2055 | 39.4842
Nanticoke (Jarvis)Ice Accretion2085RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2085 | 20.6778 | 25.1581 | 30.838 | 35.1351 | 39.4128
Nanticoke (Jarvis)Ice Accretion2090RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2090 | 20.5752 | 25.0688 | 30.7587 | 35.0647 | 39.3414
Nanticoke (Jarvis)Ice Accretion2095RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2095 | 20.4727 | 24.9794 | 30.6793 | 34.9942 | 39.27
Nanticoke (Jarvis)Ice Accretion2100RCP4.5 | Nanticoke (Jarvis) | Ice Accretion | RCP4.5 | 2100 | 20.3702 | 24.89 | 30.6 | 34.9238 | 39.1986
Nanticoke (Jarvis)Ice Accretion2023RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2023 | 23.2802 | 27.9096 | 33.796 | 38.2663 | 42.7543
Nanticoke (Jarvis)Ice Accretion2025RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2025 | 23.1619 | 27.7826 | 33.6543 | 38.119 | 42.5972
Nanticoke (Jarvis)Ice Accretion2030RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2030 | 23.0436 | 27.6556 | 33.5127 | 37.9718 | 42.4402
Nanticoke (Jarvis)Ice Accretion2035RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2035 | 22.9253 | 27.5286 | 33.371 | 37.8245 | 42.2831
Nanticoke (Jarvis)Ice Accretion2040RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2040 | 22.8071 | 27.4016 | 33.2293 | 37.6772 | 42.126
Nanticoke (Jarvis)Ice Accretion2045RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2045 | 22.6888 | 27.2746 | 33.0877 | 37.5299 | 41.9689
Nanticoke (Jarvis)Ice Accretion2050RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2050 | 22.2534 | 26.8034 | 32.572 | 36.9754 | 41.3749
Nanticoke (Jarvis)Ice Accretion2055RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2055 | 21.9364 | 26.4591 | 32.198 | 36.5682 | 40.9379
Nanticoke (Jarvis)Ice Accretion2060RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2060 | 21.6194 | 26.1148 | 31.824 | 36.1609 | 40.5009
Nanticoke (Jarvis)Ice Accretion2065RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2065 | 21.3024 | 25.7705 | 31.45 | 35.7537 | 40.064
Nanticoke (Jarvis)Ice Accretion2070RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2070 | 20.9853 | 25.4262 | 31.076 | 35.3464 | 39.627
Nanticoke (Jarvis)Ice Accretion2075RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2075 | 20.8315 | 25.2922 | 30.957 | 35.2407 | 39.5199
Nanticoke (Jarvis)Ice Accretion2080RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2080 | 20.6778 | 25.1581 | 30.838 | 35.1351 | 39.4128
Nanticoke (Jarvis)Ice Accretion2085RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2085 | 20.524 | 25.0241 | 30.719 | 35.0294 | 39.3057
Nanticoke (Jarvis)Ice Accretion2090RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2090 | 19.6999 | 24.1281 | 29.716 | 33.9505 | 38.1419
Nanticoke (Jarvis)Ice Accretion2095RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2095 | 19.0295 | 23.3662 | 28.832 | 32.9772 | 37.0852
Nanticoke (Jarvis)Ice Accretion2100RCP6.0 | Nanticoke (Jarvis) | Ice Accretion | RCP6.0 | 2100 | 18.3592 | 22.6042 | 27.948 | 32.0039 | 36.0284
Nanticoke (Jarvis)Ice Accretion2023RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2023 | 23.2802 | 27.9096 | 33.796 | 38.2663 | 42.7543
Nanticoke (Jarvis)Ice Accretion2025RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2025 | 23.0436 | 27.6556 | 33.5127 | 37.9718 | 42.4402
Nanticoke (Jarvis)Ice Accretion2030RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2030 | 22.8071 | 27.4016 | 33.2293 | 37.6772 | 42.126
Nanticoke (Jarvis)Ice Accretion2035RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2035 | 22.5705 | 27.1476 | 32.946 | 37.3827 | 41.8118
Nanticoke (Jarvis)Ice Accretion2040RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2040 | 22.0421 | 26.5738 | 32.3227 | 36.7039 | 41.0836
Nanticoke (Jarvis)Ice Accretion2045RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2045 | 21.5137 | 26 | 31.6993 | 36.0252 | 40.3553
Nanticoke (Jarvis)Ice Accretion2050RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2050 | 20.7803 | 25.2475 | 30.9173 | 35.2055 | 39.4842
Nanticoke (Jarvis)Ice Accretion2055RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2055 | 20.5752 | 25.0688 | 30.7587 | 35.0647 | 39.3414
Nanticoke (Jarvis)Ice Accretion2060RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2060 | 19.6999 | 24.1281 | 29.716 | 33.9505 | 38.1419
Nanticoke (Jarvis)Ice Accretion2065RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2065 | 19.0295 | 23.3662 | 28.832 | 32.9772 | 37.0852
Nanticoke (Jarvis)Ice Accretion2070RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2070 | 17.9255 | 22.1245 | 27.4153 | 31.4148 | 35.4001
Nanticoke (Jarvis)Ice Accretion2075RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2075 | 17.4917 | 21.6447 | 26.8827 | 30.8256 | 34.7718
Nanticoke (Jarvis)Ice Accretion2080RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2080 | 17.058 | 21.165 | 26.35 | 30.2365 | 34.1435
Nanticoke (Jarvis)Ice Accretion2085RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2085 | 15.8987 | 19.8104 | 24.701 | 28.3924 | 32.0872
Nanticoke (Jarvis)Ice Accretion2090RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2090 | 14.7394 | 18.4559 | 23.052 | 26.5482 | 30.0308
Nanticoke (Jarvis)Ice Accretion2095RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2095 | 14.7394 | 18.4559 | 23.052 | 26.5482 | 30.0308
Nanticoke (Jarvis)Ice Accretion2100RCP8.5 | Nanticoke (Jarvis) | Ice Accretion | RCP8.5 | 2100 | 14.7394 | 18.4559 | 23.052 | 26.5482 | 30.0308
Nanticoke (Jarvis)Wind2023RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2023 | 87.6216 | 94.4654 | 101.6969 | 108.9021 | 116.1072
Nanticoke (Jarvis)Wind2025RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2025 | 87.6405 | 94.4983 | 101.7474 | 108.967 | 116.1878
Nanticoke (Jarvis)Wind2030RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2030 | 87.6594 | 94.5312 | 101.7979 | 109.0318 | 116.2684
Nanticoke (Jarvis)Wind2035RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2035 | 87.6783 | 94.564 | 101.8484 | 109.0967 | 116.349
Nanticoke (Jarvis)Wind2040RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2040 | 87.6972 | 94.5969 | 101.8989 | 109.1615 | 116.4296
Nanticoke (Jarvis)Wind2045RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2045 | 87.7161 | 94.6298 | 101.9494 | 109.2263 | 116.5102
Nanticoke (Jarvis)Wind2050RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2050 | 87.8083 | 94.7585 | 102.1231 | 109.4403 | 116.7658
Nanticoke (Jarvis)Wind2055RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2055 | 87.8815 | 94.8543 | 102.2463 | 109.5895 | 116.9408
Nanticoke (Jarvis)Wind2060RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2060 | 87.9548 | 94.9501 | 102.3696 | 109.7386 | 117.1158
Nanticoke (Jarvis)Wind2065RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2065 | 88.028 | 95.0459 | 102.4928 | 109.8877 | 117.2908
Nanticoke (Jarvis)Wind2070RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2070 | 88.1013 | 95.1417 | 102.616 | 110.0369 | 117.4658
Nanticoke (Jarvis)Wind2075RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2075 | 88.2103 | 95.2873 | 102.8062 | 110.2638 | 117.7326
Nanticoke (Jarvis)Wind2080RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2080 | 88.3193 | 95.4329 | 102.9964 | 110.4908 | 117.9993
Nanticoke (Jarvis)Wind2085RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2085 | 88.4283 | 95.5785 | 103.1867 | 110.7177 | 118.2661
Nanticoke (Jarvis)Wind2090RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2090 | 88.5373 | 95.7241 | 103.3769 | 110.9447 | 118.5328
Nanticoke (Jarvis)Wind2095RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2095 | 88.6464 | 95.8697 | 103.5671 | 111.1716 | 118.7995
Nanticoke (Jarvis)Wind2100RCP4.5 | Nanticoke (Jarvis) | Wind | RCP4.5 | 2100 | 88.7554 | 96.0152 | 103.7573 | 111.3986 | 119.0663
Nanticoke (Jarvis)Wind2023RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2023 | 87.6216 | 94.4654 | 101.6969 | 108.9021 | 116.1072
Nanticoke (Jarvis)Wind2025RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2025 | 87.6405 | 94.4983 | 101.7474 | 108.967 | 116.1878
Nanticoke (Jarvis)Wind2030RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2030 | 87.6594 | 94.5312 | 101.7979 | 109.0318 | 116.2684
Nanticoke (Jarvis)Wind2035RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2035 | 87.6783 | 94.564 | 101.8484 | 109.0967 | 116.349
Nanticoke (Jarvis)Wind2040RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2040 | 87.6972 | 94.5969 | 101.8989 | 109.1615 | 116.4296
Nanticoke (Jarvis)Wind2045RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2045 | 87.7161 | 94.6298 | 101.9494 | 109.2263 | 116.5102
Nanticoke (Jarvis)Wind2050RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2050 | 87.8083 | 94.7585 | 102.1231 | 109.4403 | 116.7658
Nanticoke (Jarvis)Wind2055RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2055 | 87.8815 | 94.8543 | 102.2463 | 109.5895 | 116.9408
Nanticoke (Jarvis)Wind2060RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2060 | 87.9548 | 94.9501 | 102.3696 | 109.7386 | 117.1158
Nanticoke (Jarvis)Wind2065RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2065 | 88.028 | 95.0459 | 102.4928 | 109.8877 | 117.2908
Nanticoke (Jarvis)Wind2070RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2070 | 88.1013 | 95.1417 | 102.616 | 110.0369 | 117.4658
Nanticoke (Jarvis)Wind2075RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2075 | 88.2648 | 95.3601 | 102.9013 | 110.3773 | 117.8659
Nanticoke (Jarvis)Wind2080RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2080 | 88.4283 | 95.5785 | 103.1867 | 110.7177 | 118.2661
Nanticoke (Jarvis)Wind2085RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2085 | 88.5919 | 95.7969 | 103.472 | 111.0581 | 118.6662
Nanticoke (Jarvis)Wind2090RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2090 | 89.0781 | 96.4254 | 104.2825 | 112.0218 | 119.7878
Nanticoke (Jarvis)Wind2095RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2095 | 89.4007 | 96.8356 | 104.8077 | 112.645 | 120.5094
Nanticoke (Jarvis)Wind2100RCP6.0 | Nanticoke (Jarvis) | Wind | RCP6.0 | 2100 | 89.7234 | 97.2457 | 105.3329 | 113.2682 | 121.2309
Nanticoke (Jarvis)Wind2023RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2023 | 87.6216 | 94.4654 | 101.6969 | 108.9021 | 116.1072
Nanticoke (Jarvis)Wind2025RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2025 | 87.6594 | 94.5312 | 101.7979 | 109.0318 | 116.2684
Nanticoke (Jarvis)Wind2030RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2030 | 87.6972 | 94.5969 | 101.8989 | 109.1615 | 116.4296
Nanticoke (Jarvis)Wind2035RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2035 | 87.735 | 94.6627 | 101.9999 | 109.2912 | 116.5908
Nanticoke (Jarvis)Wind2040RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2040 | 87.8571 | 94.8223 | 102.2053 | 109.5398 | 116.8825
Nanticoke (Jarvis)Wind2045RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2045 | 87.9792 | 94.982 | 102.4106 | 109.7883 | 117.1741
Nanticoke (Jarvis)Wind2050RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2050 | 88.3193 | 95.4329 | 102.9964 | 110.4908 | 117.9993
Nanticoke (Jarvis)Wind2055RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2055 | 88.5373 | 95.7241 | 103.3769 | 110.9447 | 118.5328
Nanticoke (Jarvis)Wind2060RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2060 | 89.0781 | 96.4254 | 104.2825 | 112.0218 | 119.7878
Nanticoke (Jarvis)Wind2065RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2065 | 89.4007 | 96.8356 | 104.8077 | 112.645 | 120.5094
Nanticoke (Jarvis)Wind2070RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2070 | 89.9037 | 97.4962 | 105.6763 | 113.686 | 121.726
Nanticoke (Jarvis)Wind2075RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2075 | 90.0839 | 97.7467 | 106.0197 | 114.1039 | 122.2211
Nanticoke (Jarvis)Wind2080RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2080 | 90.2641 | 97.9972 | 106.3631 | 114.5218 | 122.7162
Nanticoke (Jarvis)Wind2085RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2085 | 90.5389 | 98.3682 | 106.8479 | 115.1108 | 123.4071
Nanticoke (Jarvis)Wind2090RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2090 | 90.8136 | 98.7392 | 107.3327 | 115.6997 | 124.0979
Nanticoke (Jarvis)Wind2095RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2095 | 90.8136 | 98.7392 | 107.3327 | 115.6997 | 124.0979
Nanticoke (Jarvis)Wind2100RCP8.5 | Nanticoke (Jarvis) | Wind | RCP8.5 | 2100 | 90.8136 | 98.7392 | 107.3327 | 115.6997 | 124.0979
Nanticoke (Port Dover)Ice Accretion2023RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
Nanticoke (Port Dover)Ice Accretion2025RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2025 | 22.9175 | 27.5192 | 33.3427 | 37.7989 | 42.2402
Nanticoke (Port Dover)Ice Accretion2030RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2030 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
Nanticoke (Port Dover)Ice Accretion2035RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2035 | 22.6651 | 27.2464 | 33.048 | 37.4787 | 41.8975
Nanticoke (Port Dover)Ice Accretion2040RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2040 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
Nanticoke (Port Dover)Ice Accretion2045RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2045 | 22.4127 | 26.9736 | 32.7533 | 37.1585 | 41.5548
Nanticoke (Port Dover)Ice Accretion2050RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2050 | 21.7945 | 26.2954 | 31.9872 | 36.3223 | 40.6466
Nanticoke (Port Dover)Ice Accretion2055RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2055 | 21.3024 | 25.7536 | 31.3684 | 35.6461 | 39.9097
Nanticoke (Port Dover)Ice Accretion2060RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2060 | 20.8103 | 25.2117 | 30.7496 | 34.9699 | 39.1729
Nanticoke (Port Dover)Ice Accretion2065RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2065 | 20.3181 | 24.6699 | 30.1308 | 34.2937 | 38.436
Nanticoke (Port Dover)Ice Accretion2070RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2070 | 19.826 | 24.1281 | 29.512 | 33.6175 | 37.6992
Nanticoke (Port Dover)Ice Accretion2075RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2075 | 19.5895 | 23.8647 | 29.2117 | 33.2909 | 37.3422
Nanticoke (Port Dover)Ice Accretion2080RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2080 | 19.3529 | 23.6013 | 28.9113 | 32.9644 | 36.9852
Nanticoke (Port Dover)Ice Accretion2085RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2085 | 19.1163 | 23.3379 | 28.611 | 32.6378 | 36.6282
Nanticoke (Port Dover)Ice Accretion2090RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2090 | 18.8797 | 23.0746 | 28.3107 | 32.3112 | 36.2712
Nanticoke (Port Dover)Ice Accretion2095RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2095 | 18.6431 | 22.8112 | 28.0103 | 31.9846 | 35.9142
Nanticoke (Port Dover)Ice Accretion2100RCP4.5 | Nanticoke (Port Dover) | Ice Accretion | RCP4.5 | 2100 | 18.4065 | 22.5478 | 27.71 | 31.6581 | 35.5572
Nanticoke (Port Dover)Ice Accretion2023RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
Nanticoke (Port Dover)Ice Accretion2025RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2025 | 22.9175 | 27.5192 | 33.3427 | 37.7989 | 42.2402
Nanticoke (Port Dover)Ice Accretion2030RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2030 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
Nanticoke (Port Dover)Ice Accretion2035RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2035 | 22.6651 | 27.2464 | 33.048 | 37.4787 | 41.8975
Nanticoke (Port Dover)Ice Accretion2040RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2040 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
Nanticoke (Port Dover)Ice Accretion2045RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2045 | 22.4127 | 26.9736 | 32.7533 | 37.1585 | 41.5548
Nanticoke (Port Dover)Ice Accretion2050RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2050 | 21.7945 | 26.2954 | 31.9872 | 36.3223 | 40.6466
Nanticoke (Port Dover)Ice Accretion2055RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2055 | 21.3024 | 25.7536 | 31.3684 | 35.6461 | 39.9097
Nanticoke (Port Dover)Ice Accretion2060RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2060 | 20.8103 | 25.2117 | 30.7496 | 34.9699 | 39.1729
Nanticoke (Port Dover)Ice Accretion2065RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2065 | 20.3181 | 24.6699 | 30.1308 | 34.2937 | 38.436
Nanticoke (Port Dover)Ice Accretion2070RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2070 | 19.826 | 24.1281 | 29.512 | 33.6175 | 37.6992
Nanticoke (Port Dover)Ice Accretion2075RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2075 | 19.4712 | 23.733 | 29.0615 | 33.1276 | 37.1637
Nanticoke (Port Dover)Ice Accretion2080RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2080 | 19.1163 | 23.3379 | 28.611 | 32.6378 | 36.6282
Nanticoke (Port Dover)Ice Accretion2085RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2085 | 18.7614 | 22.9429 | 28.1605 | 32.1479 | 36.0927
Nanticoke (Port Dover)Ice Accretion2090RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2090 | 17.4365 | 21.4002 | 26.3613 | 30.1341 | 33.8722
Nanticoke (Port Dover)Ice Accretion2095RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2095 | 16.4665 | 20.2526 | 25.0127 | 28.6101 | 32.1871
Nanticoke (Port Dover)Ice Accretion2100RCP6.0 | Nanticoke (Port Dover) | Ice Accretion | RCP6.0 | 2100 | 15.4965 | 19.1049 | 23.664 | 27.0861 | 30.5021
Nanticoke (Port Dover)Ice Accretion2023RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
Nanticoke (Port Dover)Ice Accretion2025RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2025 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
Nanticoke (Port Dover)Ice Accretion2030RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2030 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
Nanticoke (Port Dover)Ice Accretion2035RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2035 | 22.2866 | 26.8372 | 32.606 | 36.9985 | 41.3834
Nanticoke (Port Dover)Ice Accretion2040RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2040 | 21.4664 | 25.9342 | 31.5747 | 35.8715 | 40.1554
Nanticoke (Port Dover)Ice Accretion2045RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2045 | 20.6462 | 25.0311 | 30.5433 | 34.7445 | 38.9273
Nanticoke (Port Dover)Ice Accretion2050RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2050 | 19.3529 | 23.6013 | 28.9113 | 32.9644 | 36.9852
Nanticoke (Port Dover)Ice Accretion2055RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2055 | 18.8797 | 23.0746 | 28.3107 | 32.3112 | 36.2712
Nanticoke (Port Dover)Ice Accretion2060RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2060 | 17.4365 | 21.4002 | 26.3613 | 30.1341 | 33.8722
Nanticoke (Port Dover)Ice Accretion2065RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2065 | 16.4665 | 20.2526 | 25.0127 | 28.6101 | 32.1871
Nanticoke (Port Dover)Ice Accretion2070RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2070 | 15.0312 | 18.5876 | 23.052 | 26.4073 | 29.7595
Nanticoke (Port Dover)Ice Accretion2075RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2075 | 14.5659 | 18.0702 | 22.44 | 25.7286 | 29.017
Nanticoke (Port Dover)Ice Accretion2080RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2080 | 14.1006 | 17.5528 | 21.828 | 25.0498 | 28.2744
Nanticoke (Port Dover)Ice Accretion2085RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2085 | 13.0596 | 16.297 | 20.332 | 23.3594 | 26.3894
Nanticoke (Port Dover)Ice Accretion2090RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2090 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
Nanticoke (Port Dover)Ice Accretion2095RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2095 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
Nanticoke (Port Dover)Ice Accretion2100RCP8.5 | Nanticoke (Port Dover) | Ice Accretion | RCP8.5 | 2100 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
Nanticoke (Port Dover)Wind2023RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2023 | 88.6477 | 95.5809 | 102.8976 | 110.1877 | 117.4893
Nanticoke (Port Dover)Wind2025RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2025 | 88.724 | 95.6821 | 103.0319 | 110.3515 | 117.6792
Nanticoke (Port Dover)Wind2030RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2030 | 88.8004 | 95.7833 | 103.1662 | 110.5152 | 117.8692
Nanticoke (Port Dover)Wind2035RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2035 | 88.8767 | 95.8845 | 103.3005 | 110.6789 | 118.0591
Nanticoke (Port Dover)Wind2040RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2040 | 88.953 | 95.9857 | 103.4348 | 110.8426 | 118.249
Nanticoke (Port Dover)Wind2045RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2045 | 89.0294 | 96.0869 | 103.5691 | 111.0063 | 118.4389
Nanticoke (Port Dover)Wind2050RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2050 | 89.185 | 96.2943 | 103.8442 | 111.3381 | 118.8289
Nanticoke (Port Dover)Wind2055RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2055 | 89.2642 | 96.4005 | 103.9849 | 111.5062 | 119.0289
Nanticoke (Port Dover)Wind2060RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2060 | 89.3435 | 96.5068 | 104.1257 | 111.6742 | 119.2289
Nanticoke (Port Dover)Wind2065RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2065 | 89.4228 | 96.613 | 104.2664 | 111.8423 | 119.4289
Nanticoke (Port Dover)Wind2070RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2070 | 89.502 | 96.7193 | 104.4072 | 112.0104 | 119.6289
Nanticoke (Port Dover)Wind2075RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2075 | 89.6224 | 96.8742 | 104.6061 | 112.2469 | 119.906
Nanticoke (Port Dover)Wind2080RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2080 | 89.7428 | 97.0291 | 104.805 | 112.4833 | 120.1831
Nanticoke (Port Dover)Wind2085RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2085 | 89.8631 | 97.1841 | 105.0039 | 112.7198 | 120.4603
Nanticoke (Port Dover)Wind2090RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2090 | 89.9835 | 97.339 | 105.2028 | 112.9563 | 120.7374
Nanticoke (Port Dover)Wind2095RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2095 | 90.1039 | 97.4939 | 105.4017 | 113.1927 | 121.0145
Nanticoke (Port Dover)Wind2100RCP4.5 | Nanticoke (Port Dover) | Wind | RCP4.5 | 2100 | 90.2242 | 97.6489 | 105.6006 | 113.4292 | 121.2917
Nanticoke (Port Dover)Wind2023RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2023 | 88.6477 | 95.5809 | 102.8976 | 110.1877 | 117.4893
Nanticoke (Port Dover)Wind2025RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2025 | 88.724 | 95.6821 | 103.0319 | 110.3515 | 117.6792
Nanticoke (Port Dover)Wind2030RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2030 | 88.8004 | 95.7833 | 103.1662 | 110.5152 | 117.8692
Nanticoke (Port Dover)Wind2035RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2035 | 88.8767 | 95.8845 | 103.3005 | 110.6789 | 118.0591
Nanticoke (Port Dover)Wind2040RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2040 | 88.953 | 95.9857 | 103.4348 | 110.8426 | 118.249
Nanticoke (Port Dover)Wind2045RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2045 | 89.0294 | 96.0869 | 103.5691 | 111.0063 | 118.4389
Nanticoke (Port Dover)Wind2050RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2050 | 89.185 | 96.2943 | 103.8442 | 111.3381 | 118.8289
Nanticoke (Port Dover)Wind2055RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2055 | 89.2642 | 96.4005 | 103.9849 | 111.5062 | 119.0289
Nanticoke (Port Dover)Wind2060RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2060 | 89.3435 | 96.5068 | 104.1257 | 111.6742 | 119.2289
Nanticoke (Port Dover)Wind2065RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2065 | 89.4228 | 96.613 | 104.2664 | 111.8423 | 119.4289
Nanticoke (Port Dover)Wind2070RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2070 | 89.502 | 96.7193 | 104.4072 | 112.0104 | 119.6289
Nanticoke (Port Dover)Wind2075RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2075 | 89.6826 | 96.9517 | 104.7056 | 112.3651 | 120.0446
Nanticoke (Port Dover)Wind2080RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2080 | 89.8631 | 97.1841 | 105.0039 | 112.7198 | 120.4603
Nanticoke (Port Dover)Wind2085RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2085 | 90.0437 | 97.4165 | 105.3022 | 113.0745 | 120.876
Nanticoke (Port Dover)Wind2090RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2090 | 90.4826 | 97.9841 | 106.0256 | 113.9349 | 121.8731
Nanticoke (Port Dover)Wind2095RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2095 | 90.741 | 98.3192 | 106.4506 | 114.4406 | 122.4545
Nanticoke (Port Dover)Wind2100RCP6.0 | Nanticoke (Port Dover) | Wind | RCP6.0 | 2100 | 90.9993 | 98.6544 | 106.8756 | 114.9462 | 123.0359
Nanticoke (Port Dover)Wind2023RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2023 | 88.6477 | 95.5809 | 102.8976 | 110.1877 | 117.4893
Nanticoke (Port Dover)Wind2025RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2025 | 88.8004 | 95.7833 | 103.1662 | 110.5152 | 117.8692
Nanticoke (Port Dover)Wind2030RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2030 | 88.953 | 95.9857 | 103.4348 | 110.8426 | 118.249
Nanticoke (Port Dover)Wind2035RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2035 | 89.1057 | 96.188 | 103.7034 | 111.17 | 118.6289
Nanticoke (Port Dover)Wind2040RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2040 | 89.2378 | 96.3651 | 103.938 | 111.4501 | 118.9622
Nanticoke (Port Dover)Wind2045RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2045 | 89.3699 | 96.5422 | 104.1726 | 111.7303 | 119.2955
Nanticoke (Port Dover)Wind2050RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2050 | 89.7428 | 97.0291 | 104.805 | 112.4833 | 120.1831
Nanticoke (Port Dover)Wind2055RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2055 | 89.9835 | 97.339 | 105.2028 | 112.9563 | 120.7374
Nanticoke (Port Dover)Wind2060RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2060 | 90.4826 | 97.9841 | 106.0256 | 113.9349 | 121.8731
Nanticoke (Port Dover)Wind2065RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2065 | 90.741 | 98.3192 | 106.4506 | 114.4406 | 122.4545
Nanticoke (Port Dover)Wind2070RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2070 | 91.149 | 98.8663 | 107.168 | 115.3064 | 123.4661
Nanticoke (Port Dover)Wind2075RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2075 | 91.2988 | 99.0781 | 107.4604 | 115.6666 | 123.8963
Nanticoke (Port Dover)Wind2080RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2080 | 91.4485 | 99.29 | 107.7528 | 116.0267 | 124.3266
Nanticoke (Port Dover)Wind2085RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2085 | 91.792 | 99.7405 | 108.3495 | 116.7361 | 125.1638
Nanticoke (Port Dover)Wind2090RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2090 | 92.1355 | 100.1911 | 108.9462 | 117.4456 | 126.001
Nanticoke (Port Dover)Wind2095RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2095 | 92.1355 | 100.1911 | 108.9462 | 117.4456 | 126.001
Nanticoke (Port Dover)Wind2100RCP8.5 | Nanticoke (Port Dover) | Wind | RCP8.5 | 2100 | 92.1355 | 100.1911 | 108.9462 | 117.4456 | 126.001
NapaneeIce Accretion2023RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2023 | 18.1825 | 21.6663 | 26.078 | 29.4681 | 32.8583
NapaneeIce Accretion2025RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2025 | 18.2126 | 21.7095 | 26.1343 | 29.5367 | 32.9347
NapaneeIce Accretion2030RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2030 | 18.2428 | 21.7526 | 26.1907 | 29.6052 | 33.0112
NapaneeIce Accretion2035RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2035 | 18.2729 | 21.7958 | 26.247 | 29.6738 | 33.0876
NapaneeIce Accretion2040RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2040 | 18.3031 | 21.839 | 26.3033 | 29.7424 | 33.164
NapaneeIce Accretion2045RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2045 | 18.3332 | 21.8821 | 26.3597 | 29.8109 | 33.2405
NapaneeIce Accretion2050RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2050 | 18.2874 | 21.8476 | 26.338 | 29.7972 | 33.2317
NapaneeIce Accretion2055RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2055 | 18.2114 | 21.7699 | 26.26 | 29.7149 | 33.1466
NapaneeIce Accretion2060RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2060 | 18.1354 | 21.6922 | 26.182 | 29.6327 | 33.0614
NapaneeIce Accretion2065RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2065 | 18.0594 | 21.6145 | 26.104 | 29.5504 | 32.9762
NapaneeIce Accretion2070RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2070 | 17.9834 | 21.5368 | 26.026 | 29.4681 | 32.891
NapaneeIce Accretion2075RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2075 | 18.0196 | 21.6088 | 26.143 | 29.615 | 33.0712
NapaneeIce Accretion2080RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2080 | 18.0558 | 21.6807 | 26.26 | 29.7619 | 33.2514
NapaneeIce Accretion2085RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2085 | 18.092 | 21.7526 | 26.377 | 29.9088 | 33.4316
NapaneeIce Accretion2090RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2090 | 18.1282 | 21.8246 | 26.494 | 30.0557 | 33.6118
NapaneeIce Accretion2095RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2095 | 18.1644 | 21.8965 | 26.611 | 30.2026 | 33.7919
NapaneeIce Accretion2100RCP4.5 | Napanee | Ice Accretion | RCP4.5 | 2100 | 18.2006 | 21.9684 | 26.728 | 30.3495 | 33.9721
NapaneeIce Accretion2023RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2023 | 18.1825 | 21.6663 | 26.078 | 29.4681 | 32.8583
NapaneeIce Accretion2025RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2025 | 18.2126 | 21.7095 | 26.1343 | 29.5367 | 32.9347
NapaneeIce Accretion2030RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2030 | 18.2428 | 21.7526 | 26.1907 | 29.6052 | 33.0112
NapaneeIce Accretion2035RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2035 | 18.2729 | 21.7958 | 26.247 | 29.6738 | 33.0876
NapaneeIce Accretion2040RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2040 | 18.3031 | 21.839 | 26.3033 | 29.7424 | 33.164
NapaneeIce Accretion2045RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2045 | 18.3332 | 21.8821 | 26.3597 | 29.8109 | 33.2405
NapaneeIce Accretion2050RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2050 | 18.2874 | 21.8476 | 26.338 | 29.7972 | 33.2317
NapaneeIce Accretion2055RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2055 | 18.2114 | 21.7699 | 26.26 | 29.7149 | 33.1466
NapaneeIce Accretion2060RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2060 | 18.1354 | 21.6922 | 26.182 | 29.6327 | 33.0614
NapaneeIce Accretion2065RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2065 | 18.0594 | 21.6145 | 26.104 | 29.5504 | 32.9762
NapaneeIce Accretion2070RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2070 | 17.9834 | 21.5368 | 26.026 | 29.4681 | 32.891
NapaneeIce Accretion2075RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2075 | 18.0377 | 21.6447 | 26.2015 | 29.6885 | 33.1613
NapaneeIce Accretion2080RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2080 | 18.092 | 21.7526 | 26.377 | 29.9088 | 33.4316
NapaneeIce Accretion2085RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2085 | 18.1463 | 21.8605 | 26.5525 | 30.1292 | 33.7018
NapaneeIce Accretion2090RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2090 | 18.0076 | 21.7742 | 26.5287 | 30.1439 | 33.7646
NapaneeIce Accretion2095RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2095 | 17.8146 | 21.58 | 26.3293 | 29.9382 | 33.5572
NapaneeIce Accretion2100RCP6.0 | Napanee | Ice Accretion | RCP6.0 | 2100 | 17.6216 | 21.3858 | 26.13 | 29.7326 | 33.3497
NapaneeIce Accretion2023RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2023 | 18.1825 | 21.6663 | 26.078 | 29.4681 | 32.8583
NapaneeIce Accretion2025RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2025 | 18.2428 | 21.7526 | 26.1907 | 29.6052 | 33.0112
NapaneeIce Accretion2030RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2030 | 18.3031 | 21.839 | 26.3033 | 29.7424 | 33.164
NapaneeIce Accretion2035RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2035 | 18.3634 | 21.9253 | 26.416 | 29.8795 | 33.3169
NapaneeIce Accretion2040RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2040 | 18.2367 | 21.7958 | 26.286 | 29.7424 | 33.175
NapaneeIce Accretion2045RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2045 | 18.1101 | 21.6663 | 26.156 | 29.6052 | 33.033
NapaneeIce Accretion2050RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2050 | 18.0558 | 21.6807 | 26.26 | 29.7619 | 33.2514
NapaneeIce Accretion2055RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2055 | 18.1282 | 21.8246 | 26.494 | 30.0557 | 33.6118
NapaneeIce Accretion2060RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2060 | 18.0076 | 21.7742 | 26.5287 | 30.1439 | 33.7646
NapaneeIce Accretion2065RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2065 | 17.8146 | 21.58 | 26.3293 | 29.9382 | 33.5572
NapaneeIce Accretion2070RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2070 | 17.2779 | 20.9973 | 25.6793 | 29.2429 | 32.8037
NapaneeIce Accretion2075RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2075 | 16.9341 | 20.6089 | 25.2287 | 28.7532 | 32.2577
NapaneeIce Accretion2080RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2080 | 16.5904 | 20.2205 | 24.778 | 28.2636 | 31.7117
NapaneeIce Accretion2085RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2085 | 15.8938 | 19.4004 | 23.803 | 27.1618 | 30.4996
NapaneeIce Accretion2090RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2090 | 15.1973 | 18.5804 | 22.828 | 26.0601 | 29.2874
NapaneeIce Accretion2095RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2095 | 15.1973 | 18.5804 | 22.828 | 26.0601 | 29.2874
NapaneeIce Accretion2100RCP8.5 | Napanee | Ice Accretion | RCP8.5 | 2100 | 15.1973 | 18.5804 | 22.828 | 26.0601 | 29.2874
NapaneeWind2023RCP4.5 | Napanee | Wind | RCP4.5 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.3568
NapaneeWind2025RCP4.5 | Napanee | Wind | RCP4.5 | 2025 | 85.0176 | 91.5972 | 98.5341 | 105.4647 | 112.3885
NapaneeWind2030RCP4.5 | Napanee | Wind | RCP4.5 | 2030 | 85.0331 | 91.617 | 98.5586 | 105.4927 | 112.4201
NapaneeWind2035RCP4.5 | Napanee | Wind | RCP4.5 | 2035 | 85.0486 | 91.6367 | 98.5831 | 105.5206 | 112.4518
NapaneeWind2040RCP4.5 | Napanee | Wind | RCP4.5 | 2040 | 85.0641 | 91.6565 | 98.6076 | 105.5486 | 112.4834
NapaneeWind2045RCP4.5 | Napanee | Wind | RCP4.5 | 2045 | 85.0796 | 91.6762 | 98.6321 | 105.5765 | 112.5151
NapaneeWind2050RCP4.5 | Napanee | Wind | RCP4.5 | 2050 | 85.1747 | 91.7944 | 98.7781 | 105.745 | 112.7076
NapaneeWind2055RCP4.5 | Napanee | Wind | RCP4.5 | 2055 | 85.2542 | 91.8928 | 98.8996 | 105.8855 | 112.8685
NapaneeWind2060RCP4.5 | Napanee | Wind | RCP4.5 | 2060 | 85.3338 | 91.9912 | 99.0212 | 106.026 | 113.0294
NapaneeWind2065RCP4.5 | Napanee | Wind | RCP4.5 | 2065 | 85.4133 | 92.0897 | 99.1427 | 106.1666 | 113.1902
NapaneeWind2070RCP4.5 | Napanee | Wind | RCP4.5 | 2070 | 85.4929 | 92.1881 | 99.2642 | 106.3071 | 113.3511
NapaneeWind2075RCP4.5 | Napanee | Wind | RCP4.5 | 2075 | 85.5549 | 92.2671 | 99.3638 | 106.4259 | 113.4889
NapaneeWind2080RCP4.5 | Napanee | Wind | RCP4.5 | 2080 | 85.617 | 92.3461 | 99.4635 | 106.5448 | 113.6267
NapaneeWind2085RCP4.5 | Napanee | Wind | RCP4.5 | 2085 | 85.679 | 92.4251 | 99.5631 | 106.6636 | 113.7645
NapaneeWind2090RCP4.5 | Napanee | Wind | RCP4.5 | 2090 | 85.7411 | 92.5041 | 99.6627 | 106.7824 | 113.9023
NapaneeWind2095RCP4.5 | Napanee | Wind | RCP4.5 | 2095 | 85.8032 | 92.5831 | 99.7624 | 106.9013 | 114.0401
NapaneeWind2100RCP4.5 | Napanee | Wind | RCP4.5 | 2100 | 85.8652 | 92.662 | 99.862 | 107.0201 | 114.1778
NapaneeWind2023RCP6.0 | Napanee | Wind | RCP6.0 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.3568
NapaneeWind2025RCP6.0 | Napanee | Wind | RCP6.0 | 2025 | 85.0176 | 91.5972 | 98.5341 | 105.4647 | 112.3885
NapaneeWind2030RCP6.0 | Napanee | Wind | RCP6.0 | 2030 | 85.0331 | 91.617 | 98.5586 | 105.4927 | 112.4201
NapaneeWind2035RCP6.0 | Napanee | Wind | RCP6.0 | 2035 | 85.0486 | 91.6367 | 98.5831 | 105.5206 | 112.4518
NapaneeWind2040RCP6.0 | Napanee | Wind | RCP6.0 | 2040 | 85.0641 | 91.6565 | 98.6076 | 105.5486 | 112.4834
NapaneeWind2045RCP6.0 | Napanee | Wind | RCP6.0 | 2045 | 85.0796 | 91.6762 | 98.6321 | 105.5765 | 112.5151
NapaneeWind2050RCP6.0 | Napanee | Wind | RCP6.0 | 2050 | 85.1747 | 91.7944 | 98.7781 | 105.745 | 112.7076
NapaneeWind2055RCP6.0 | Napanee | Wind | RCP6.0 | 2055 | 85.2542 | 91.8928 | 98.8996 | 105.8855 | 112.8685
NapaneeWind2060RCP6.0 | Napanee | Wind | RCP6.0 | 2060 | 85.3338 | 91.9912 | 99.0212 | 106.026 | 113.0294
NapaneeWind2065RCP6.0 | Napanee | Wind | RCP6.0 | 2065 | 85.4133 | 92.0897 | 99.1427 | 106.1666 | 113.1902
NapaneeWind2070RCP6.0 | Napanee | Wind | RCP6.0 | 2070 | 85.4929 | 92.1881 | 99.2642 | 106.3071 | 113.3511
NapaneeWind2075RCP6.0 | Napanee | Wind | RCP6.0 | 2075 | 85.586 | 92.3066 | 99.4136 | 106.4853 | 113.5578
NapaneeWind2080RCP6.0 | Napanee | Wind | RCP6.0 | 2080 | 85.679 | 92.4251 | 99.5631 | 106.6636 | 113.7645
NapaneeWind2085RCP6.0 | Napanee | Wind | RCP6.0 | 2085 | 85.7721 | 92.5436 | 99.7125 | 106.8419 | 113.9712
NapaneeWind2090RCP6.0 | Napanee | Wind | RCP6.0 | 2090 | 86.0091 | 92.817 | 100.0253 | 107.1914 | 114.3603
NapaneeWind2095RCP6.0 | Napanee | Wind | RCP6.0 | 2095 | 86.1529 | 92.9719 | 100.1887 | 107.3627 | 114.5428
NapaneeWind2100RCP6.0 | Napanee | Wind | RCP6.0 | 2100 | 86.2968 | 93.1269 | 100.352 | 107.5339 | 114.7253
NapaneeWind2023RCP8.5 | Napanee | Wind | RCP8.5 | 2023 | 85.0021 | 91.5775 | 98.5096 | 105.4367 | 112.3568
NapaneeWind2025RCP8.5 | Napanee | Wind | RCP8.5 | 2025 | 85.0331 | 91.617 | 98.5586 | 105.4927 | 112.4201
NapaneeWind2030RCP8.5 | Napanee | Wind | RCP8.5 | 2030 | 85.0641 | 91.6565 | 98.6076 | 105.5486 | 112.4834
NapaneeWind2035RCP8.5 | Napanee | Wind | RCP8.5 | 2035 | 85.0952 | 91.696 | 98.6566 | 105.6045 | 112.5467
NapaneeWind2040RCP8.5 | Napanee | Wind | RCP8.5 | 2040 | 85.2277 | 91.86 | 98.8591 | 105.8387 | 112.8149
NapaneeWind2045RCP8.5 | Napanee | Wind | RCP8.5 | 2045 | 85.3603 | 92.0241 | 99.0617 | 106.0729 | 113.083
NapaneeWind2050RCP8.5 | Napanee | Wind | RCP8.5 | 2050 | 85.617 | 92.3461 | 99.4635 | 106.5448 | 113.6267
NapaneeWind2055RCP8.5 | Napanee | Wind | RCP8.5 | 2055 | 85.7411 | 92.5041 | 99.6627 | 106.7824 | 113.9023
NapaneeWind2060RCP8.5 | Napanee | Wind | RCP8.5 | 2060 | 86.0091 | 92.817 | 100.0253 | 107.1914 | 114.3603
NapaneeWind2065RCP8.5 | Napanee | Wind | RCP8.5 | 2065 | 86.1529 | 92.9719 | 100.1887 | 107.3627 | 114.5428
NapaneeWind2070RCP8.5 | Napanee | Wind | RCP8.5 | 2070 | 86.3081 | 93.142 | 100.3749 | 107.5619 | 114.7588
NapaneeWind2075RCP8.5 | Napanee | Wind | RCP8.5 | 2075 | 86.3193 | 93.1572 | 100.3977 | 107.5899 | 114.7923
NapaneeWind2080RCP8.5 | Napanee | Wind | RCP8.5 | 2080 | 86.3306 | 93.1724 | 100.4206 | 107.6178 | 114.8258
NapaneeWind2085RCP8.5 | Napanee | Wind | RCP8.5 | 2085 | 86.4279 | 93.3091 | 100.6117 | 107.8538 | 115.1051
NapaneeWind2090RCP8.5 | Napanee | Wind | RCP8.5 | 2090 | 86.5253 | 93.4458 | 100.8028 | 108.0897 | 115.3844
NapaneeWind2095RCP8.5 | Napanee | Wind | RCP8.5 | 2095 | 86.5253 | 93.4458 | 100.8028 | 108.0897 | 115.3844
NapaneeWind2100RCP8.5 | Napanee | Wind | RCP8.5 | 2100 | 86.5253 | 93.4458 | 100.8028 | 108.0897 | 115.3844
New LiskeardIce Accretion2023RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2023 | 14.7519 | 17.6458 | 21.32 | 24.1142 | 26.9136
New LiskeardIce Accretion2025RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2025 | 14.7311 | 17.6209 | 21.2867 | 24.0765 | 26.8716
New LiskeardIce Accretion2030RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2030 | 14.7102 | 17.596 | 21.2533 | 24.0389 | 26.8296
New LiskeardIce Accretion2035RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2035 | 14.6893 | 17.5711 | 21.22 | 24.0012 | 26.7876
New LiskeardIce Accretion2040RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2040 | 14.6684 | 17.5462 | 21.1867 | 23.9635 | 26.7456
New LiskeardIce Accretion2045RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2045 | 14.6476 | 17.5213 | 21.1533 | 23.9259 | 26.7036
New LiskeardIce Accretion2050RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2050 | 14.635 | 17.5064 | 21.128 | 23.8972 | 26.6717
New LiskeardIce Accretion2055RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2055 | 14.6434 | 17.5163 | 21.136 | 23.9063 | 26.6818
New LiskeardIce Accretion2060RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2060 | 14.6517 | 17.5263 | 21.144 | 23.9153 | 26.6918
New LiskeardIce Accretion2065RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2065 | 14.6601 | 17.5362 | 21.152 | 23.9244 | 26.7019
New LiskeardIce Accretion2070RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2070 | 14.6684 | 17.5462 | 21.16 | 23.9334 | 26.712
New LiskeardIce Accretion2075RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2075 | 14.7055 | 17.5988 | 21.2367 | 24.0276 | 26.8212
New LiskeardIce Accretion2080RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2080 | 14.7427 | 17.6513 | 21.3133 | 24.1217 | 26.9304
New LiskeardIce Accretion2085RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2085 | 14.7798 | 17.7039 | 21.39 | 24.2159 | 27.0396
New LiskeardIce Accretion2090RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2090 | 14.8169 | 17.7565 | 21.4667 | 24.3101 | 27.1488
New LiskeardIce Accretion2095RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2095 | 14.854 | 17.809 | 21.5433 | 24.4042 | 27.258
New LiskeardIce Accretion2100RCP4.5 | New Liskeard | Ice Accretion | RCP4.5 | 2100 | 14.8911 | 17.8616 | 21.62 | 24.4984 | 27.3672
New LiskeardIce Accretion2023RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2023 | 14.7519 | 17.6458 | 21.32 | 24.1142 | 26.9136
New LiskeardIce Accretion2025RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2025 | 14.7311 | 17.6209 | 21.2867 | 24.0765 | 26.8716
New LiskeardIce Accretion2030RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2030 | 14.7102 | 17.596 | 21.2533 | 24.0389 | 26.8296
New LiskeardIce Accretion2035RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2035 | 14.6893 | 17.5711 | 21.22 | 24.0012 | 26.7876
New LiskeardIce Accretion2040RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2040 | 14.6684 | 17.5462 | 21.1867 | 23.9635 | 26.7456
New LiskeardIce Accretion2045RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2045 | 14.6476 | 17.5213 | 21.1533 | 23.9259 | 26.7036
New LiskeardIce Accretion2050RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2050 | 14.635 | 17.5064 | 21.128 | 23.8972 | 26.6717
New LiskeardIce Accretion2055RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2055 | 14.6434 | 17.5163 | 21.136 | 23.9063 | 26.6818
New LiskeardIce Accretion2060RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2060 | 14.6517 | 17.5263 | 21.144 | 23.9153 | 26.6918
New LiskeardIce Accretion2065RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2065 | 14.6601 | 17.5362 | 21.152 | 23.9244 | 26.7019
New LiskeardIce Accretion2070RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2070 | 14.6684 | 17.5462 | 21.16 | 23.9334 | 26.712
New LiskeardIce Accretion2075RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2075 | 14.7241 | 17.625 | 21.275 | 24.0746 | 26.8758
New LiskeardIce Accretion2080RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2080 | 14.7798 | 17.7039 | 21.39 | 24.2159 | 27.0396
New LiskeardIce Accretion2085RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2085 | 14.8354 | 17.7828 | 21.505 | 24.3571 | 27.2034
New LiskeardIce Accretion2090RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2090 | 14.9375 | 17.9225 | 21.7067 | 24.6039 | 27.4848
New LiskeardIce Accretion2095RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2095 | 14.9839 | 17.9833 | 21.7933 | 24.7093 | 27.6024
New LiskeardIce Accretion2100RCP6.0 | New Liskeard | Ice Accretion | RCP6.0 | 2100 | 15.0303 | 18.0442 | 21.88 | 24.8148 | 27.72
New LiskeardIce Accretion2023RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2023 | 14.7519 | 17.6458 | 21.32 | 24.1142 | 26.9136
New LiskeardIce Accretion2025RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2025 | 14.7102 | 17.596 | 21.2533 | 24.0389 | 26.8296
New LiskeardIce Accretion2030RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2030 | 14.6684 | 17.5462 | 21.1867 | 23.9635 | 26.7456
New LiskeardIce Accretion2035RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2035 | 14.6267 | 17.4964 | 21.12 | 23.8882 | 26.6616
New LiskeardIce Accretion2040RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2040 | 14.6406 | 17.513 | 21.1333 | 23.9033 | 26.6784
New LiskeardIce Accretion2045RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2045 | 14.6545 | 17.5296 | 21.1467 | 23.9183 | 26.6952
New LiskeardIce Accretion2050RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2050 | 14.7427 | 17.6513 | 21.3133 | 24.1217 | 26.9304
New LiskeardIce Accretion2055RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2055 | 14.8169 | 17.7565 | 21.4667 | 24.3101 | 27.1488
New LiskeardIce Accretion2060RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2060 | 14.9375 | 17.9225 | 21.7067 | 24.6039 | 27.4848
New LiskeardIce Accretion2065RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2065 | 14.9839 | 17.9833 | 21.7933 | 24.7093 | 27.6024
New LiskeardIce Accretion2070RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2070 | 14.8633 | 17.8616 | 21.6667 | 24.5737 | 27.4596
New LiskeardIce Accretion2075RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2075 | 14.6963 | 17.679 | 21.4533 | 24.3327 | 27.1992
New LiskeardIce Accretion2080RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2080 | 14.5293 | 17.4964 | 21.24 | 24.0916 | 26.9388
New LiskeardIce Accretion2085RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2085 | 14.5641 | 17.5711 | 21.36 | 24.2611 | 27.1404
New LiskeardIce Accretion2090RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2090 | 14.5989 | 17.6458 | 21.48 | 24.4306 | 27.342
New LiskeardIce Accretion2095RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2095 | 14.5989 | 17.6458 | 21.48 | 24.4306 | 27.342
New LiskeardIce Accretion2100RCP8.5 | New Liskeard | Ice Accretion | RCP8.5 | 2100 | 14.5989 | 17.6458 | 21.48 | 24.4306 | 27.342
New LiskeardWind2023RCP4.5 | New Liskeard | Wind | RCP4.5 | 2023 | 76.1156 | 81.9218 | 88.0088 | 94.1129 | 100.2197
New LiskeardWind2025RCP4.5 | New Liskeard | Wind | RCP4.5 | 2025 | 76.122 | 81.9259 | 88.0132 | 94.1176 | 100.223
New LiskeardWind2030RCP4.5 | New Liskeard | Wind | RCP4.5 | 2030 | 76.1283 | 81.93 | 88.0176 | 94.1223 | 100.2264
New LiskeardWind2035RCP4.5 | New Liskeard | Wind | RCP4.5 | 2035 | 76.1346 | 81.9341 | 88.022 | 94.127 | 100.2297
New LiskeardWind2040RCP4.5 | New Liskeard | Wind | RCP4.5 | 2040 | 76.141 | 81.9382 | 88.0264 | 94.1318 | 100.2331
New LiskeardWind2045RCP4.5 | New Liskeard | Wind | RCP4.5 | 2045 | 76.1473 | 81.9423 | 88.0308 | 94.1365 | 100.2364
New LiskeardWind2050RCP4.5 | New Liskeard | Wind | RCP4.5 | 2050 | 76.1551 | 81.9448 | 88.0246 | 94.1261 | 100.2197
New LiskeardWind2055RCP4.5 | New Liskeard | Wind | RCP4.5 | 2055 | 76.1567 | 81.9431 | 88.0141 | 94.111 | 100.1996
New LiskeardWind2060RCP4.5 | New Liskeard | Wind | RCP4.5 | 2060 | 76.1582 | 81.9415 | 88.0035 | 94.096 | 100.1796
New LiskeardWind2065RCP4.5 | New Liskeard | Wind | RCP4.5 | 2065 | 76.1597 | 81.9398 | 87.993 | 94.0809 | 100.1595
New LiskeardWind2070RCP4.5 | New Liskeard | Wind | RCP4.5 | 2070 | 76.1612 | 81.9382 | 87.9824 | 94.0658 | 100.1394
New LiskeardWind2075RCP4.5 | New Liskeard | Wind | RCP4.5 | 2075 | 76.2182 | 82.0078 | 88.0689 | 94.1647 | 100.2514
New LiskeardWind2080RCP4.5 | New Liskeard | Wind | RCP4.5 | 2080 | 76.2752 | 82.0773 | 88.1555 | 94.2636 | 100.3635
New LiskeardWind2085RCP4.5 | New Liskeard | Wind | RCP4.5 | 2085 | 76.3322 | 82.1469 | 88.242 | 94.3624 | 100.4755
New LiskeardWind2090RCP4.5 | New Liskeard | Wind | RCP4.5 | 2090 | 76.3892 | 82.2165 | 88.3285 | 94.4613 | 100.5875
New LiskeardWind2095RCP4.5 | New Liskeard | Wind | RCP4.5 | 2095 | 76.4462 | 82.286 | 88.4151 | 94.5602 | 100.6995
New LiskeardWind2100RCP4.5 | New Liskeard | Wind | RCP4.5 | 2100 | 76.5032 | 82.3556 | 88.5016 | 94.659 | 100.8116
New LiskeardWind2023RCP6.0 | New Liskeard | Wind | RCP6.0 | 2023 | 76.1156 | 81.9218 | 88.0088 | 94.1129 | 100.2197
New LiskeardWind2025RCP6.0 | New Liskeard | Wind | RCP6.0 | 2025 | 76.122 | 81.9259 | 88.0132 | 94.1176 | 100.223
New LiskeardWind2030RCP6.0 | New Liskeard | Wind | RCP6.0 | 2030 | 76.1283 | 81.93 | 88.0176 | 94.1223 | 100.2264
New LiskeardWind2035RCP6.0 | New Liskeard | Wind | RCP6.0 | 2035 | 76.1346 | 81.9341 | 88.022 | 94.127 | 100.2297
New LiskeardWind2040RCP6.0 | New Liskeard | Wind | RCP6.0 | 2040 | 76.141 | 81.9382 | 88.0264 | 94.1318 | 100.2331
New LiskeardWind2045RCP6.0 | New Liskeard | Wind | RCP6.0 | 2045 | 76.1473 | 81.9423 | 88.0308 | 94.1365 | 100.2364
New LiskeardWind2050RCP6.0 | New Liskeard | Wind | RCP6.0 | 2050 | 76.1551 | 81.9448 | 88.0246 | 94.1261 | 100.2197
New LiskeardWind2055RCP6.0 | New Liskeard | Wind | RCP6.0 | 2055 | 76.1567 | 81.9431 | 88.0141 | 94.111 | 100.1996
New LiskeardWind2060RCP6.0 | New Liskeard | Wind | RCP6.0 | 2060 | 76.1582 | 81.9415 | 88.0035 | 94.096 | 100.1796
New LiskeardWind2065RCP6.0 | New Liskeard | Wind | RCP6.0 | 2065 | 76.1597 | 81.9398 | 87.993 | 94.0809 | 100.1595
New LiskeardWind2070RCP6.0 | New Liskeard | Wind | RCP6.0 | 2070 | 76.1612 | 81.9382 | 87.9824 | 94.0658 | 100.1394
New LiskeardWind2075RCP6.0 | New Liskeard | Wind | RCP6.0 | 2075 | 76.2467 | 82.0426 | 88.1122 | 94.2141 | 100.3075
New LiskeardWind2080RCP6.0 | New Liskeard | Wind | RCP6.0 | 2080 | 76.3322 | 82.1469 | 88.242 | 94.3624 | 100.4755
New LiskeardWind2085RCP6.0 | New Liskeard | Wind | RCP6.0 | 2085 | 76.4177 | 82.2512 | 88.3718 | 94.5107 | 100.6435
New LiskeardWind2090RCP6.0 | New Liskeard | Wind | RCP6.0 | 2090 | 76.493 | 82.331 | 88.4576 | 94.6026 | 100.7413
New LiskeardWind2095RCP6.0 | New Liskeard | Wind | RCP6.0 | 2095 | 76.4829 | 82.3065 | 88.4136 | 94.5461 | 100.6711
New LiskeardWind2100RCP6.0 | New Liskeard | Wind | RCP6.0 | 2100 | 76.4728 | 82.2819 | 88.3696 | 94.4896 | 100.6009
New LiskeardWind2023RCP8.5 | New Liskeard | Wind | RCP8.5 | 2023 | 76.1156 | 81.9218 | 88.0088 | 94.1129 | 100.2197
New LiskeardWind2025RCP8.5 | New Liskeard | Wind | RCP8.5 | 2025 | 76.1283 | 81.93 | 88.0176 | 94.1223 | 100.2264
New LiskeardWind2030RCP8.5 | New Liskeard | Wind | RCP8.5 | 2030 | 76.141 | 81.9382 | 88.0264 | 94.1318 | 100.2331
New LiskeardWind2035RCP8.5 | New Liskeard | Wind | RCP8.5 | 2035 | 76.1536 | 81.9464 | 88.0352 | 94.1412 | 100.2397
New LiskeardWind2040RCP8.5 | New Liskeard | Wind | RCP8.5 | 2040 | 76.1562 | 81.9437 | 88.0176 | 94.1161 | 100.2063
New LiskeardWind2045RCP8.5 | New Liskeard | Wind | RCP8.5 | 2045 | 76.1587 | 81.9409 | 88 | 94.0909 | 100.1729
New LiskeardWind2050RCP8.5 | New Liskeard | Wind | RCP8.5 | 2050 | 76.2752 | 82.0773 | 88.1555 | 94.2636 | 100.3635
New LiskeardWind2055RCP8.5 | New Liskeard | Wind | RCP8.5 | 2055 | 76.3892 | 82.2165 | 88.3285 | 94.4613 | 100.5875
New LiskeardWind2060RCP8.5 | New Liskeard | Wind | RCP8.5 | 2060 | 76.493 | 82.331 | 88.4576 | 94.6026 | 100.7413
New LiskeardWind2065RCP8.5 | New Liskeard | Wind | RCP8.5 | 2065 | 76.4829 | 82.3065 | 88.4136 | 94.5461 | 100.6711
New LiskeardWind2070RCP8.5 | New Liskeard | Wind | RCP8.5 | 2070 | 76.5488 | 82.3665 | 88.4635 | 94.59 | 100.7112
New LiskeardWind2075RCP8.5 | New Liskeard | Wind | RCP8.5 | 2075 | 76.6247 | 82.4511 | 88.5573 | 94.6904 | 100.8216
New LiskeardWind2080RCP8.5 | New Liskeard | Wind | RCP8.5 | 2080 | 76.7007 | 82.5356 | 88.6512 | 94.7909 | 100.932
New LiskeardWind2085RCP8.5 | New Liskeard | Wind | RCP8.5 | 2085 | 76.8299 | 82.7075 | 88.8756 | 95.0592 | 101.248
New LiskeardWind2090RCP8.5 | New Liskeard | Wind | RCP8.5 | 2090 | 76.9591 | 82.8794 | 89.1 | 95.3276 | 101.564
New LiskeardWind2095RCP8.5 | New Liskeard | Wind | RCP8.5 | 2095 | 76.9591 | 82.8794 | 89.1 | 95.3276 | 101.564
New LiskeardWind2100RCP8.5 | New Liskeard | Wind | RCP8.5 | 2100 | 76.9591 | 82.8794 | 89.1 | 95.3276 | 101.564
NewcastleIce Accretion2023RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
NewcastleIce Accretion2025RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
NewcastleIce Accretion2030RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
NewcastleIce Accretion2035RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
NewcastleIce Accretion2040RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
NewcastleIce Accretion2045RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
NewcastleIce Accretion2050RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
NewcastleIce Accretion2055RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
NewcastleIce Accretion2060RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
NewcastleIce Accretion2065RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
NewcastleIce Accretion2070RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
NewcastleIce Accretion2075RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
NewcastleIce Accretion2080RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
NewcastleIce Accretion2085RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
NewcastleIce Accretion2090RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
NewcastleIce Accretion2095RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
NewcastleIce Accretion2100RCP4.5 | Newcastle | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
NewcastleIce Accretion2023RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
NewcastleIce Accretion2025RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
NewcastleIce Accretion2030RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
NewcastleIce Accretion2035RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
NewcastleIce Accretion2040RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
NewcastleIce Accretion2045RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
NewcastleIce Accretion2050RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
NewcastleIce Accretion2055RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
NewcastleIce Accretion2060RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
NewcastleIce Accretion2065RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
NewcastleIce Accretion2070RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
NewcastleIce Accretion2075RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
NewcastleIce Accretion2080RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
NewcastleIce Accretion2085RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
NewcastleIce Accretion2090RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
NewcastleIce Accretion2095RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
NewcastleIce Accretion2100RCP6.0 | Newcastle | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
NewcastleIce Accretion2023RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
NewcastleIce Accretion2025RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
NewcastleIce Accretion2030RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
NewcastleIce Accretion2035RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
NewcastleIce Accretion2040RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
NewcastleIce Accretion2045RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
NewcastleIce Accretion2050RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
NewcastleIce Accretion2055RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
NewcastleIce Accretion2060RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
NewcastleIce Accretion2065RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
NewcastleIce Accretion2070RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
NewcastleIce Accretion2075RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
NewcastleIce Accretion2080RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
NewcastleIce Accretion2085RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
NewcastleIce Accretion2090RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
NewcastleIce Accretion2095RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
NewcastleIce Accretion2100RCP8.5 | Newcastle | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
NewcastleWind2023RCP4.5 | Newcastle | Wind | RCP4.5 | 2023 | 85.6899 | 92.2541 | 99.1584 | 106.0677 | 112.9729
NewcastleWind2025RCP4.5 | Newcastle | Wind | RCP4.5 | 2025 | 85.7056 | 92.2879 | 99.2129 | 106.1401 | 113.0631
NewcastleWind2030RCP4.5 | Newcastle | Wind | RCP4.5 | 2030 | 85.7213 | 92.3217 | 99.2673 | 106.2125 | 113.1534
NewcastleWind2035RCP4.5 | Newcastle | Wind | RCP4.5 | 2035 | 85.7369 | 92.3554 | 99.3217 | 106.2849 | 113.2437
NewcastleWind2040RCP4.5 | Newcastle | Wind | RCP4.5 | 2040 | 85.7526 | 92.3892 | 99.3762 | 106.3573 | 113.334
NewcastleWind2045RCP4.5 | Newcastle | Wind | RCP4.5 | 2045 | 85.7683 | 92.4229 | 99.4306 | 106.4296 | 113.4243
NewcastleWind2050RCP4.5 | Newcastle | Wind | RCP4.5 | 2050 | 85.8677 | 92.5617 | 99.6178 | 106.6567 | 113.6952
NewcastleWind2055RCP4.5 | Newcastle | Wind | RCP4.5 | 2055 | 85.9515 | 92.6666 | 99.7504 | 106.8113 | 113.8757
NewcastleWind2060RCP4.5 | Newcastle | Wind | RCP4.5 | 2060 | 86.0353 | 92.7716 | 99.8831 | 106.966 | 114.0563
NewcastleWind2065RCP4.5 | Newcastle | Wind | RCP4.5 | 2065 | 86.1191 | 92.8765 | 100.0157 | 107.1207 | 114.2369
NewcastleWind2070RCP4.5 | Newcastle | Wind | RCP4.5 | 2070 | 86.2028 | 92.9815 | 100.1484 | 107.2753 | 114.4175
NewcastleWind2075RCP4.5 | Newcastle | Wind | RCP4.5 | 2075 | 86.3482 | 93.1687 | 100.3877 | 107.5596 | 114.7466
NewcastleWind2080RCP4.5 | Newcastle | Wind | RCP4.5 | 2080 | 86.4935 | 93.3559 | 100.6269 | 107.8438 | 115.0758
NewcastleWind2085RCP4.5 | Newcastle | Wind | RCP4.5 | 2085 | 86.6388 | 93.5431 | 100.8662 | 108.128 | 115.405
NewcastleWind2090RCP4.5 | Newcastle | Wind | RCP4.5 | 2090 | 86.7841 | 93.7303 | 101.1054 | 108.4123 | 115.7342
NewcastleWind2095RCP4.5 | Newcastle | Wind | RCP4.5 | 2095 | 86.9295 | 93.9175 | 101.3447 | 108.6965 | 116.0633
NewcastleWind2100RCP4.5 | Newcastle | Wind | RCP4.5 | 2100 | 87.0748 | 94.1047 | 101.5839 | 108.9808 | 116.3925
NewcastleWind2023RCP6.0 | Newcastle | Wind | RCP6.0 | 2023 | 85.6899 | 92.2541 | 99.1584 | 106.0677 | 112.9729
NewcastleWind2025RCP6.0 | Newcastle | Wind | RCP6.0 | 2025 | 85.7056 | 92.2879 | 99.2129 | 106.1401 | 113.0631
NewcastleWind2030RCP6.0 | Newcastle | Wind | RCP6.0 | 2030 | 85.7213 | 92.3217 | 99.2673 | 106.2125 | 113.1534
NewcastleWind2035RCP6.0 | Newcastle | Wind | RCP6.0 | 2035 | 85.7369 | 92.3554 | 99.3217 | 106.2849 | 113.2437
NewcastleWind2040RCP6.0 | Newcastle | Wind | RCP6.0 | 2040 | 85.7526 | 92.3892 | 99.3762 | 106.3573 | 113.334
NewcastleWind2045RCP6.0 | Newcastle | Wind | RCP6.0 | 2045 | 85.7683 | 92.4229 | 99.4306 | 106.4296 | 113.4243
NewcastleWind2050RCP6.0 | Newcastle | Wind | RCP6.0 | 2050 | 85.8677 | 92.5617 | 99.6178 | 106.6567 | 113.6952
NewcastleWind2055RCP6.0 | Newcastle | Wind | RCP6.0 | 2055 | 85.9515 | 92.6666 | 99.7504 | 106.8113 | 113.8757
NewcastleWind2060RCP6.0 | Newcastle | Wind | RCP6.0 | 2060 | 86.0353 | 92.7716 | 99.8831 | 106.966 | 114.0563
NewcastleWind2065RCP6.0 | Newcastle | Wind | RCP6.0 | 2065 | 86.1191 | 92.8765 | 100.0157 | 107.1207 | 114.2369
NewcastleWind2070RCP6.0 | Newcastle | Wind | RCP6.0 | 2070 | 86.2028 | 92.9815 | 100.1484 | 107.2753 | 114.4175
NewcastleWind2075RCP6.0 | Newcastle | Wind | RCP6.0 | 2075 | 86.4208 | 93.2623 | 100.5073 | 107.7017 | 114.9112
NewcastleWind2080RCP6.0 | Newcastle | Wind | RCP6.0 | 2080 | 86.6388 | 93.5431 | 100.8662 | 108.128 | 115.405
NewcastleWind2085RCP6.0 | Newcastle | Wind | RCP6.0 | 2085 | 86.8568 | 93.8239 | 101.225 | 108.5544 | 115.8988
NewcastleWind2090RCP6.0 | Newcastle | Wind | RCP6.0 | 2090 | 87.525 | 94.6572 | 102.267 | 109.7753 | 117.3029
NewcastleWind2095RCP6.0 | Newcastle | Wind | RCP6.0 | 2095 | 87.9752 | 95.2096 | 102.9501 | 110.5697 | 118.2133
NewcastleWind2100RCP6.0 | Newcastle | Wind | RCP6.0 | 2100 | 88.4254 | 95.762 | 103.6332 | 111.3642 | 119.1237
NewcastleWind2023RCP8.5 | Newcastle | Wind | RCP8.5 | 2023 | 85.6899 | 92.2541 | 99.1584 | 106.0677 | 112.9729
NewcastleWind2025RCP8.5 | Newcastle | Wind | RCP8.5 | 2025 | 85.7213 | 92.3217 | 99.2673 | 106.2125 | 113.1534
NewcastleWind2030RCP8.5 | Newcastle | Wind | RCP8.5 | 2030 | 85.7526 | 92.3892 | 99.3762 | 106.3573 | 113.334
NewcastleWind2035RCP8.5 | Newcastle | Wind | RCP8.5 | 2035 | 85.784 | 92.4567 | 99.4851 | 106.502 | 113.5146
NewcastleWind2040RCP8.5 | Newcastle | Wind | RCP8.5 | 2040 | 85.9236 | 92.6316 | 99.7062 | 106.7598 | 113.8155
NewcastleWind2045RCP8.5 | Newcastle | Wind | RCP8.5 | 2045 | 86.0632 | 92.8066 | 99.9273 | 107.0175 | 114.1165
NewcastleWind2050RCP8.5 | Newcastle | Wind | RCP8.5 | 2050 | 86.4935 | 93.3559 | 100.6269 | 107.8438 | 115.0758
NewcastleWind2055RCP8.5 | Newcastle | Wind | RCP8.5 | 2055 | 86.7841 | 93.7303 | 101.1054 | 108.4123 | 115.7342
NewcastleWind2060RCP8.5 | Newcastle | Wind | RCP8.5 | 2060 | 87.525 | 94.6572 | 102.267 | 109.7753 | 117.3029
NewcastleWind2065RCP8.5 | Newcastle | Wind | RCP8.5 | 2065 | 87.9752 | 95.2096 | 102.9501 | 110.5697 | 118.2133
NewcastleWind2070RCP8.5 | Newcastle | Wind | RCP8.5 | 2070 | 88.5594 | 95.9431 | 103.8741 | 111.6608 | 119.4698
NewcastleWind2075RCP8.5 | Newcastle | Wind | RCP8.5 | 2075 | 88.6933 | 96.1241 | 104.115 | 111.9574 | 119.8159
NewcastleWind2080RCP8.5 | Newcastle | Wind | RCP8.5 | 2080 | 88.8272 | 96.3052 | 104.3559 | 112.254 | 120.162
NewcastleWind2085RCP8.5 | Newcastle | Wind | RCP8.5 | 2085 | 89.1136 | 96.7103 | 104.9103 | 112.932 | 120.969
NewcastleWind2090RCP8.5 | Newcastle | Wind | RCP8.5 | 2090 | 89.4 | 97.1154 | 105.4647 | 113.6099 | 121.7759
NewcastleWind2095RCP8.5 | Newcastle | Wind | RCP8.5 | 2095 | 89.4 | 97.1154 | 105.4647 | 113.6099 | 121.7759
NewcastleWind2100RCP8.5 | Newcastle | Wind | RCP8.5 | 2100 | 89.4 | 97.1154 | 105.4647 | 113.6099 | 121.7759
NewmarketIce Accretion2023RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
NewmarketIce Accretion2025RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2025 | 17.4222 | 20.9229 | 25.3542 | 28.7444 | 32.1247
NewmarketIce Accretion2030RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2030 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
NewmarketIce Accretion2035RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2035 | 17.5092 | 21.0612 | 25.5625 | 28.9986 | 32.4292
NewmarketIce Accretion2040RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2040 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
NewmarketIce Accretion2045RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2045 | 17.5962 | 21.1996 | 25.7708 | 29.2529 | 32.7338
NewmarketIce Accretion2050RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2050 | 17.5214 | 21.1484 | 25.745 | 29.2444 | 32.7411
NewmarketIce Accretion2055RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2055 | 17.4031 | 21.0281 | 25.615 | 29.1088 | 32.5962
NewmarketIce Accretion2060RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2060 | 17.2848 | 20.9077 | 25.485 | 28.9732 | 32.4513
NewmarketIce Accretion2065RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2065 | 17.1665 | 20.7873 | 25.355 | 28.8376 | 32.3064
NewmarketIce Accretion2070RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2070 | 17.0482 | 20.667 | 25.225 | 28.702 | 32.1615
NewmarketIce Accretion2075RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2075 | 17.0105 | 20.6497 | 25.2333 | 28.7255 | 32.2035
NewmarketIce Accretion2080RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2080 | 16.9728 | 20.6324 | 25.2417 | 28.7491 | 32.2455
NewmarketIce Accretion2085RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2085 | 16.9352 | 20.6151 | 25.25 | 28.7726 | 32.2875
NewmarketIce Accretion2090RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2090 | 16.8975 | 20.5978 | 25.2583 | 28.7962 | 32.3295
NewmarketIce Accretion2095RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2095 | 16.8598 | 20.5805 | 25.2667 | 28.8197 | 32.3715
NewmarketIce Accretion2100RCP4.5 | Newmarket | Ice Accretion | RCP4.5 | 2100 | 16.8221 | 20.5633 | 25.275 | 28.8432 | 32.4135
NewmarketIce Accretion2023RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
NewmarketIce Accretion2025RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2025 | 17.4222 | 20.9229 | 25.3542 | 28.7444 | 32.1247
NewmarketIce Accretion2030RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2030 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
NewmarketIce Accretion2035RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2035 | 17.5092 | 21.0612 | 25.5625 | 28.9986 | 32.4292
NewmarketIce Accretion2040RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2040 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
NewmarketIce Accretion2045RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2045 | 17.5962 | 21.1996 | 25.7708 | 29.2529 | 32.7338
NewmarketIce Accretion2050RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2050 | 17.5214 | 21.1484 | 25.745 | 29.2444 | 32.7411
NewmarketIce Accretion2055RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2055 | 17.4031 | 21.0281 | 25.615 | 29.1088 | 32.5962
NewmarketIce Accretion2060RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2060 | 17.2848 | 20.9077 | 25.485 | 28.9732 | 32.4513
NewmarketIce Accretion2065RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2065 | 17.1665 | 20.7873 | 25.355 | 28.8376 | 32.3064
NewmarketIce Accretion2070RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2070 | 17.0482 | 20.667 | 25.225 | 28.702 | 32.1615
NewmarketIce Accretion2075RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2075 | 16.9917 | 20.6411 | 25.2375 | 28.7373 | 32.2245
NewmarketIce Accretion2080RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2080 | 16.9352 | 20.6151 | 25.25 | 28.7726 | 32.2875
NewmarketIce Accretion2085RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2085 | 16.8786 | 20.5892 | 25.2625 | 28.8079 | 32.3505
NewmarketIce Accretion2090RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2090 | 16.5147 | 20.2382 | 24.925 | 28.4854 | 32.0355
NewmarketIce Accretion2095RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2095 | 16.2074 | 19.9131 | 24.575 | 28.1276 | 31.6575
NewmarketIce Accretion2100RCP6.0 | Newmarket | Ice Accretion | RCP6.0 | 2100 | 15.9001 | 19.588 | 24.225 | 27.7697 | 31.2795
NewmarketIce Accretion2023RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
NewmarketIce Accretion2025RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2025 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
NewmarketIce Accretion2030RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2030 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
NewmarketIce Accretion2035RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2035 | 17.6397 | 21.2687 | 25.875 | 29.38 | 32.886
NewmarketIce Accretion2040RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2040 | 17.4425 | 21.0682 | 25.6583 | 29.154 | 32.6445
NewmarketIce Accretion2045RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2045 | 17.2454 | 20.8676 | 25.4417 | 28.928 | 32.403
NewmarketIce Accretion2050RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2050 | 16.9728 | 20.6324 | 25.2417 | 28.7491 | 32.2455
NewmarketIce Accretion2055RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2055 | 16.8975 | 20.5978 | 25.2583 | 28.7962 | 32.3295
NewmarketIce Accretion2060RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2060 | 16.5147 | 20.2382 | 24.925 | 28.4854 | 32.0355
NewmarketIce Accretion2065RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2065 | 16.2074 | 19.9131 | 24.575 | 28.1276 | 31.6575
NewmarketIce Accretion2070RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2070 | 15.5116 | 19.173 | 23.775 | 27.2801 | 30.765
NewmarketIce Accretion2075RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2075 | 15.1231 | 18.758 | 23.325 | 26.7904 | 30.2505
NewmarketIce Accretion2080RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2080 | 14.7345 | 18.343 | 22.875 | 26.3007 | 29.736
NewmarketIce Accretion2085RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2085 | 13.9691 | 17.4404 | 21.8 | 25.1001 | 28.3972
NewmarketIce Accretion2090RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2090 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
NewmarketIce Accretion2095RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2095 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
NewmarketIce Accretion2100RCP8.5 | Newmarket | Ice Accretion | RCP8.5 | 2100 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
NewmarketWind2023RCP4.5 | Newmarket | Wind | RCP4.5 | 2023 | 76.2676 | 82.1428 | 88.3256 | 94.5084 | 100.6912
NewmarketWind2025RCP4.5 | Newmarket | Wind | RCP4.5 | 2025 | 76.2917 | 82.1769 | 88.3725 | 94.5665 | 100.7614
NewmarketWind2030RCP4.5 | Newmarket | Wind | RCP4.5 | 2030 | 76.3157 | 82.211 | 88.4195 | 94.6245 | 100.8316
NewmarketWind2035RCP4.5 | Newmarket | Wind | RCP4.5 | 2035 | 76.3398 | 82.2451 | 88.4664 | 94.6826 | 100.9019
NewmarketWind2040RCP4.5 | Newmarket | Wind | RCP4.5 | 2040 | 76.3639 | 82.2792 | 88.5133 | 94.7407 | 100.9721
NewmarketWind2045RCP4.5 | Newmarket | Wind | RCP4.5 | 2045 | 76.3879 | 82.3133 | 88.5603 | 94.7987 | 101.0423
NewmarketWind2050RCP4.5 | Newmarket | Wind | RCP4.5 | 2050 | 76.4621 | 82.3949 | 88.6512 | 94.8982 | 101.1506
NewmarketWind2055RCP4.5 | Newmarket | Wind | RCP4.5 | 2055 | 76.5123 | 82.4423 | 88.6952 | 94.9396 | 101.1888
NewmarketWind2060RCP4.5 | Newmarket | Wind | RCP4.5 | 2060 | 76.5624 | 82.4898 | 88.7392 | 94.9811 | 101.2269
NewmarketWind2065RCP4.5 | Newmarket | Wind | RCP4.5 | 2065 | 76.6126 | 82.5373 | 88.7832 | 95.0225 | 101.265
NewmarketWind2070RCP4.5 | Newmarket | Wind | RCP4.5 | 2070 | 76.6627 | 82.5847 | 88.8272 | 95.0639 | 101.3031
NewmarketWind2075RCP4.5 | Newmarket | Wind | RCP4.5 | 2075 | 76.7362 | 82.6857 | 88.9621 | 95.2271 | 101.4954
NewmarketWind2080RCP4.5 | Newmarket | Wind | RCP4.5 | 2080 | 76.8096 | 82.7866 | 89.0971 | 95.3904 | 101.6877
NewmarketWind2085RCP4.5 | Newmarket | Wind | RCP4.5 | 2085 | 76.8831 | 82.8876 | 89.232 | 95.5536 | 101.88
NewmarketWind2090RCP4.5 | Newmarket | Wind | RCP4.5 | 2090 | 76.9565 | 82.9885 | 89.3669 | 95.7168 | 102.0723
NewmarketWind2095RCP4.5 | Newmarket | Wind | RCP4.5 | 2095 | 77.03 | 83.0894 | 89.5019 | 95.88 | 102.2645
NewmarketWind2100RCP4.5 | Newmarket | Wind | RCP4.5 | 2100 | 77.1035 | 83.1904 | 89.6368 | 96.0432 | 102.4568
NewmarketWind2023RCP6.0 | Newmarket | Wind | RCP6.0 | 2023 | 76.2676 | 82.1428 | 88.3256 | 94.5084 | 100.6912
NewmarketWind2025RCP6.0 | Newmarket | Wind | RCP6.0 | 2025 | 76.2917 | 82.1769 | 88.3725 | 94.5665 | 100.7614
NewmarketWind2030RCP6.0 | Newmarket | Wind | RCP6.0 | 2030 | 76.3157 | 82.211 | 88.4195 | 94.6245 | 100.8316
NewmarketWind2035RCP6.0 | Newmarket | Wind | RCP6.0 | 2035 | 76.3398 | 82.2451 | 88.4664 | 94.6826 | 100.9019
NewmarketWind2040RCP6.0 | Newmarket | Wind | RCP6.0 | 2040 | 76.3639 | 82.2792 | 88.5133 | 94.7407 | 100.9721
NewmarketWind2045RCP6.0 | Newmarket | Wind | RCP6.0 | 2045 | 76.3879 | 82.3133 | 88.5603 | 94.7987 | 101.0423
NewmarketWind2050RCP6.0 | Newmarket | Wind | RCP6.0 | 2050 | 76.4621 | 82.3949 | 88.6512 | 94.8982 | 101.1506
NewmarketWind2055RCP6.0 | Newmarket | Wind | RCP6.0 | 2055 | 76.5123 | 82.4423 | 88.6952 | 94.9396 | 101.1888
NewmarketWind2060RCP6.0 | Newmarket | Wind | RCP6.0 | 2060 | 76.5624 | 82.4898 | 88.7392 | 94.9811 | 101.2269
NewmarketWind2065RCP6.0 | Newmarket | Wind | RCP6.0 | 2065 | 76.6126 | 82.5373 | 88.7832 | 95.0225 | 101.265
NewmarketWind2070RCP6.0 | Newmarket | Wind | RCP6.0 | 2070 | 76.6627 | 82.5847 | 88.8272 | 95.0639 | 101.3031
NewmarketWind2075RCP6.0 | Newmarket | Wind | RCP6.0 | 2075 | 76.7729 | 82.7361 | 89.0296 | 95.3088 | 101.5916
NewmarketWind2080RCP6.0 | Newmarket | Wind | RCP6.0 | 2080 | 76.8831 | 82.8876 | 89.232 | 95.5536 | 101.88
NewmarketWind2085RCP6.0 | Newmarket | Wind | RCP6.0 | 2085 | 76.9933 | 83.039 | 89.4344 | 95.7984 | 102.1684
NewmarketWind2090RCP6.0 | Newmarket | Wind | RCP6.0 | 2090 | 77.3593 | 83.5068 | 90.0269 | 96.4983 | 102.9785
NewmarketWind2095RCP6.0 | Newmarket | Wind | RCP6.0 | 2095 | 77.6151 | 83.8233 | 90.4171 | 96.9534 | 103.5001
NewmarketWind2100RCP6.0 | Newmarket | Wind | RCP6.0 | 2100 | 77.8709 | 84.1397 | 90.8072 | 97.4085 | 104.0218
NewmarketWind2023RCP8.5 | Newmarket | Wind | RCP8.5 | 2023 | 76.2676 | 82.1428 | 88.3256 | 94.5084 | 100.6912
NewmarketWind2025RCP8.5 | Newmarket | Wind | RCP8.5 | 2025 | 76.3157 | 82.211 | 88.4195 | 94.6245 | 100.8316
NewmarketWind2030RCP8.5 | Newmarket | Wind | RCP8.5 | 2030 | 76.3639 | 82.2792 | 88.5133 | 94.7407 | 100.9721
NewmarketWind2035RCP8.5 | Newmarket | Wind | RCP8.5 | 2035 | 76.412 | 82.3474 | 88.6072 | 94.8568 | 101.1125
NewmarketWind2040RCP8.5 | Newmarket | Wind | RCP8.5 | 2040 | 76.4956 | 82.4265 | 88.6805 | 94.9258 | 101.1761
NewmarketWind2045RCP8.5 | Newmarket | Wind | RCP8.5 | 2045 | 76.5791 | 82.5056 | 88.7539 | 94.9949 | 101.2396
NewmarketWind2050RCP8.5 | Newmarket | Wind | RCP8.5 | 2050 | 76.8096 | 82.7866 | 89.0971 | 95.3904 | 101.6877
NewmarketWind2055RCP8.5 | Newmarket | Wind | RCP8.5 | 2055 | 76.9565 | 82.9885 | 89.3669 | 95.7168 | 102.0723
NewmarketWind2060RCP8.5 | Newmarket | Wind | RCP8.5 | 2060 | 77.3593 | 83.5068 | 90.0269 | 96.4983 | 102.9785
NewmarketWind2065RCP8.5 | Newmarket | Wind | RCP8.5 | 2065 | 77.6151 | 83.8233 | 90.4171 | 96.9534 | 103.5001
NewmarketWind2070RCP8.5 | Newmarket | Wind | RCP8.5 | 2070 | 78.0659 | 84.4016 | 91.1533 | 97.826 | 104.51
NewmarketWind2075RCP8.5 | Newmarket | Wind | RCP8.5 | 2075 | 78.261 | 84.6635 | 91.4995 | 98.2434 | 104.9983
NewmarketWind2080RCP8.5 | Newmarket | Wind | RCP8.5 | 2080 | 78.456 | 84.9254 | 91.8456 | 98.6608 | 105.4865
NewmarketWind2085RCP8.5 | Newmarket | Wind | RCP8.5 | 2085 | 78.5548 | 85.0563 | 92.0216 | 98.868 | 105.7323
NewmarketWind2090RCP8.5 | Newmarket | Wind | RCP8.5 | 2090 | 78.6536 | 85.1873 | 92.1976 | 99.0752 | 105.978
NewmarketWind2095RCP8.5 | Newmarket | Wind | RCP8.5 | 2095 | 78.6536 | 85.1873 | 92.1976 | 99.0752 | 105.978
NewmarketWind2100RCP8.5 | Newmarket | Wind | RCP8.5 | 2100 | 78.6536 | 85.1873 | 92.1976 | 99.0752 | 105.978
Niagara FallsIce Accretion2023RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2023 | 20.7501 | 24.8253 | 29.97 | 33.9339 | 37.8378
Niagara FallsIce Accretion2025RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2025 | 20.7084 | 24.7838 | 29.935 | 33.8943 | 37.8
Niagara FallsIce Accretion2030RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2030 | 20.6666 | 24.7423 | 29.9 | 33.8548 | 37.7622
Niagara FallsIce Accretion2035RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2035 | 20.6249 | 24.7008 | 29.865 | 33.8152 | 37.7244
Niagara FallsIce Accretion2040RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2040 | 20.5831 | 24.6593 | 29.83 | 33.7757 | 37.6866
Niagara FallsIce Accretion2045RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2045 | 20.5414 | 24.6178 | 29.795 | 33.7361 | 37.6488
Niagara FallsIce Accretion2050RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2050 | 20.1531 | 24.1879 | 29.31 | 33.2017 | 37.0742
Niagara FallsIce Accretion2055RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2055 | 19.8066 | 23.7994 | 28.86 | 32.7067 | 36.5375
Niagara FallsIce Accretion2060RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2060 | 19.46 | 23.411 | 28.41 | 32.2118 | 36.0007
Niagara FallsIce Accretion2065RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2065 | 19.1135 | 23.0225 | 27.96 | 31.7168 | 35.464
Niagara FallsIce Accretion2070RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2070 | 18.767 | 22.6341 | 27.51 | 31.2219 | 34.9272
Niagara FallsIce Accretion2075RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2075 | 18.6139 | 22.4806 | 27.355 | 31.0637 | 34.7634
Niagara FallsIce Accretion2080RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2080 | 18.4608 | 22.327 | 27.2 | 30.9055 | 34.5996
Niagara FallsIce Accretion2085RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2085 | 18.3077 | 22.1734 | 27.045 | 30.7473 | 34.4358
Niagara FallsIce Accretion2090RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2090 | 18.1546 | 22.0199 | 26.89 | 30.5891 | 34.272
Niagara FallsIce Accretion2095RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2095 | 18.0015 | 21.8663 | 26.735 | 30.4309 | 34.1082
Niagara FallsIce Accretion2100RCP4.5 | Niagara Falls | Ice Accretion | RCP4.5 | 2100 | 17.8485 | 21.7128 | 26.58 | 30.2727 | 33.9444
Niagara FallsIce Accretion2023RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2023 | 20.7501 | 24.8253 | 29.97 | 33.9339 | 37.8378
Niagara FallsIce Accretion2025RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2025 | 20.7084 | 24.7838 | 29.935 | 33.8943 | 37.8
Niagara FallsIce Accretion2030RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2030 | 20.6666 | 24.7423 | 29.9 | 33.8548 | 37.7622
Niagara FallsIce Accretion2035RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2035 | 20.6249 | 24.7008 | 29.865 | 33.8152 | 37.7244
Niagara FallsIce Accretion2040RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2040 | 20.5831 | 24.6593 | 29.83 | 33.7757 | 37.6866
Niagara FallsIce Accretion2045RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2045 | 20.5414 | 24.6178 | 29.795 | 33.7361 | 37.6488
Niagara FallsIce Accretion2050RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2050 | 20.1531 | 24.1879 | 29.31 | 33.2017 | 37.0742
Niagara FallsIce Accretion2055RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2055 | 19.8066 | 23.7994 | 28.86 | 32.7067 | 36.5375
Niagara FallsIce Accretion2060RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2060 | 19.46 | 23.411 | 28.41 | 32.2118 | 36.0007
Niagara FallsIce Accretion2065RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2065 | 19.1135 | 23.0225 | 27.96 | 31.7168 | 35.464
Niagara FallsIce Accretion2070RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2070 | 18.767 | 22.6341 | 27.51 | 31.2219 | 34.9272
Niagara FallsIce Accretion2075RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2075 | 18.5373 | 22.4038 | 27.2775 | 30.9846 | 34.6815
Niagara FallsIce Accretion2080RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2080 | 18.3077 | 22.1734 | 27.045 | 30.7473 | 34.4358
Niagara FallsIce Accretion2085RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2085 | 18.0781 | 21.9431 | 26.8125 | 30.51 | 34.1901
Niagara FallsIce Accretion2090RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2090 | 17.2848 | 21.082 | 25.85 | 29.4704 | 33.075
Niagara FallsIce Accretion2095RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2095 | 16.7212 | 20.4512 | 25.12 | 28.6681 | 32.2056
Niagara FallsIce Accretion2100RCP6.0 | Niagara Falls | Ice Accretion | RCP6.0 | 2100 | 16.1575 | 19.8204 | 24.39 | 27.8658 | 31.3362
Niagara FallsIce Accretion2023RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2023 | 20.7501 | 24.8253 | 29.97 | 33.9339 | 37.8378
Niagara FallsIce Accretion2025RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2025 | 20.6666 | 24.7423 | 29.9 | 33.8548 | 37.7622
Niagara FallsIce Accretion2030RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2030 | 20.5831 | 24.6593 | 29.83 | 33.7757 | 37.6866
Niagara FallsIce Accretion2035RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2035 | 20.4996 | 24.5763 | 29.76 | 33.6966 | 37.611
Niagara FallsIce Accretion2040RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2040 | 19.9221 | 23.9289 | 29.01 | 32.8717 | 36.7164
Niagara FallsIce Accretion2045RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2045 | 19.3445 | 23.2815 | 28.26 | 32.0468 | 35.8218
Niagara FallsIce Accretion2050RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2050 | 18.4608 | 22.327 | 27.2 | 30.9055 | 34.5996
Niagara FallsIce Accretion2055RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2055 | 18.1546 | 22.0199 | 26.89 | 30.5891 | 34.272
Niagara FallsIce Accretion2060RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2060 | 17.2848 | 21.082 | 25.85 | 29.4704 | 33.075
Niagara FallsIce Accretion2065RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2065 | 16.7212 | 20.4512 | 25.12 | 28.6681 | 32.2056
Niagara FallsIce Accretion2070RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2070 | 15.9418 | 19.588 | 24.14 | 27.6059 | 31.0464
Niagara FallsIce Accretion2075RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2075 | 15.7261 | 19.3556 | 23.89 | 27.346 | 30.7566
Niagara FallsIce Accretion2080RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2080 | 15.5104 | 19.1232 | 23.64 | 27.0861 | 30.4668
Niagara FallsIce Accretion2085RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2085 | 14.8946 | 18.426 | 22.83 | 26.1878 | 29.484
Niagara FallsIce Accretion2090RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2090 | 14.2788 | 17.7288 | 22.02 | 25.2894 | 28.5012
Niagara FallsIce Accretion2095RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2095 | 14.2788 | 17.7288 | 22.02 | 25.2894 | 28.5012
Niagara FallsIce Accretion2100RCP8.5 | Niagara Falls | Ice Accretion | RCP8.5 | 2100 | 14.2788 | 17.7288 | 22.02 | 25.2894 | 28.5012
Niagara FallsWind2023RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2023 | 87.3758 | 94.2648 | 101.55 | 108.7976 | 116.052
Niagara FallsWind2025RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2025 | 87.3729 | 94.2679 | 101.5617 | 108.8154 | 116.0767
Niagara FallsWind2030RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2030 | 87.37 | 94.271 | 101.5733 | 108.8333 | 116.1014
Niagara FallsWind2035RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2035 | 87.3672 | 94.2741 | 101.585 | 108.8511 | 116.1261
Niagara FallsWind2040RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2040 | 87.3643 | 94.2772 | 101.5967 | 108.8689 | 116.1508
Niagara FallsWind2045RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2045 | 87.3614 | 94.2803 | 101.6083 | 108.8868 | 116.1755
Niagara FallsWind2050RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2050 | 87.3602 | 94.2964 | 101.65 | 108.9474 | 116.2549
Niagara FallsWind2055RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2055 | 87.362 | 94.3094 | 101.68 | 108.9902 | 116.3096
Niagara FallsWind2060RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2060 | 87.3637 | 94.3225 | 101.71 | 109.033 | 116.3644
Niagara FallsWind2065RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2065 | 87.3654 | 94.3355 | 101.74 | 109.0758 | 116.4191
Niagara FallsWind2070RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2070 | 87.3672 | 94.3485 | 101.77 | 109.1186 | 116.4738
Niagara FallsWind2075RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2075 | 87.3873 | 94.3795 | 101.815 | 109.1757 | 116.5422
Niagara FallsWind2080RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2080 | 87.4074 | 94.4105 | 101.86 | 109.2327 | 116.6106
Niagara FallsWind2085RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2085 | 87.4276 | 94.4415 | 101.905 | 109.2898 | 116.679
Niagara FallsWind2090RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2090 | 87.4477 | 94.4725 | 101.95 | 109.3469 | 116.7474
Niagara FallsWind2095RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2095 | 87.4679 | 94.5035 | 101.995 | 109.4039 | 116.8158
Niagara FallsWind2100RCP4.5 | Niagara Falls | Wind | RCP4.5 | 2100 | 87.488 | 94.5345 | 102.04 | 109.461 | 116.8842
Niagara FallsWind2023RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2023 | 87.3758 | 94.2648 | 101.55 | 108.7976 | 116.052
Niagara FallsWind2025RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2025 | 87.3729 | 94.2679 | 101.5617 | 108.8154 | 116.0767
Niagara FallsWind2030RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2030 | 87.37 | 94.271 | 101.5733 | 108.8333 | 116.1014
Niagara FallsWind2035RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2035 | 87.3672 | 94.2741 | 101.585 | 108.8511 | 116.1261
Niagara FallsWind2040RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2040 | 87.3643 | 94.2772 | 101.5967 | 108.8689 | 116.1508
Niagara FallsWind2045RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2045 | 87.3614 | 94.2803 | 101.6083 | 108.8868 | 116.1755
Niagara FallsWind2050RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2050 | 87.3602 | 94.2964 | 101.65 | 108.9474 | 116.2549
Niagara FallsWind2055RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2055 | 87.362 | 94.3094 | 101.68 | 108.9902 | 116.3096
Niagara FallsWind2060RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2060 | 87.3637 | 94.3225 | 101.71 | 109.033 | 116.3644
Niagara FallsWind2065RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2065 | 87.3654 | 94.3355 | 101.74 | 109.0758 | 116.4191
Niagara FallsWind2070RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2070 | 87.3672 | 94.3485 | 101.77 | 109.1186 | 116.4738
Niagara FallsWind2075RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2075 | 87.3974 | 94.395 | 101.8375 | 109.2042 | 116.5764
Niagara FallsWind2080RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2080 | 87.4276 | 94.4415 | 101.905 | 109.2898 | 116.679
Niagara FallsWind2085RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2085 | 87.4578 | 94.488 | 101.9725 | 109.3754 | 116.7816
Niagara FallsWind2090RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2090 | 87.5888 | 94.6771 | 102.23 | 109.6928 | 117.1654
Niagara FallsWind2095RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2095 | 87.6895 | 94.8197 | 102.42 | 109.9247 | 117.4466
Niagara FallsWind2100RCP6.0 | Niagara Falls | Wind | RCP6.0 | 2100 | 87.7903 | 94.9623 | 102.61 | 110.1565 | 117.7278
Niagara FallsWind2023RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2023 | 87.3758 | 94.2648 | 101.55 | 108.7976 | 116.052
Niagara FallsWind2025RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2025 | 87.37 | 94.271 | 101.5733 | 108.8333 | 116.1014
Niagara FallsWind2030RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2030 | 87.3643 | 94.2772 | 101.5967 | 108.8689 | 116.1508
Niagara FallsWind2035RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2035 | 87.3585 | 94.2834 | 101.62 | 108.9046 | 116.2002
Niagara FallsWind2040RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2040 | 87.3614 | 94.3051 | 101.67 | 108.9759 | 116.2914
Niagara FallsWind2045RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2045 | 87.3643 | 94.3268 | 101.72 | 109.0473 | 116.3826
Niagara FallsWind2050RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2050 | 87.4074 | 94.4105 | 101.86 | 109.2327 | 116.6106
Niagara FallsWind2055RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2055 | 87.4477 | 94.4725 | 101.95 | 109.3469 | 116.7474
Niagara FallsWind2060RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2060 | 87.5888 | 94.6771 | 102.23 | 109.6928 | 117.1654
Niagara FallsWind2065RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2065 | 87.6895 | 94.8197 | 102.42 | 109.9247 | 117.4466
Niagara FallsWind2070RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2070 | 87.7931 | 94.9871 | 102.6667 | 110.2385 | 117.8304
Niagara FallsWind2075RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2075 | 87.796 | 95.0119 | 102.7233 | 110.3206 | 117.933
Niagara FallsWind2080RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2080 | 87.7989 | 95.0367 | 102.78 | 110.4026 | 118.0356
Niagara FallsWind2085RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2085 | 87.8334 | 95.1437 | 102.975 | 110.6701 | 118.3776
Niagara FallsWind2090RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2090 | 87.868 | 95.2506 | 103.17 | 110.9376 | 118.7196
Niagara FallsWind2095RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2095 | 87.868 | 95.2506 | 103.17 | 110.9376 | 118.7196
Niagara FallsWind2100RCP8.5 | Niagara Falls | Wind | RCP8.5 | 2100 | 87.868 | 95.2506 | 103.17 | 110.9376 | 118.7196
North BayIce Accretion2023RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2023 | 15.6913 | 18.753 | 22.638 | 25.5809 | 28.5516
North BayIce Accretion2025RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2025 | 15.7908 | 18.8778 | 22.7993 | 25.7715 | 28.7641
North BayIce Accretion2030RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2030 | 15.8903 | 19.0026 | 22.9607 | 25.9621 | 28.9766
North BayIce Accretion2035RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2035 | 15.9898 | 19.1273 | 23.122 | 26.1527 | 29.1892
North BayIce Accretion2040RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2040 | 16.0894 | 19.2521 | 23.2833 | 26.3433 | 29.4017
North BayIce Accretion2045RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2045 | 16.1889 | 19.3769 | 23.4447 | 26.5339 | 29.6142
North BayIce Accretion2050RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2050 | 16.4139 | 19.6806 | 23.848 | 27.0129 | 30.1704
North BayIce Accretion2055RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2055 | 16.5394 | 19.8596 | 24.09 | 27.3013 | 30.5142
North BayIce Accretion2060RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2060 | 16.665 | 20.0385 | 24.332 | 27.5896 | 30.8579
North BayIce Accretion2065RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2065 | 16.7905 | 20.2175 | 24.574 | 27.878 | 31.2016
North BayIce Accretion2070RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2070 | 16.916 | 20.3964 | 24.816 | 28.1664 | 31.5454
North BayIce Accretion2075RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2075 | 16.8548 | 20.3356 | 24.7573 | 28.1084 | 31.4853
North BayIce Accretion2080RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2080 | 16.7936 | 20.2747 | 24.6987 | 28.0504 | 31.4252
North BayIce Accretion2085RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2085 | 16.7323 | 20.2138 | 24.64 | 27.9924 | 31.3652
North BayIce Accretion2090RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2090 | 16.6711 | 20.153 | 24.5813 | 27.9344 | 31.3051
North BayIce Accretion2095RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2095 | 16.6098 | 20.0921 | 24.5227 | 27.8763 | 31.2451
North BayIce Accretion2100RCP4.5 | North Bay | Ice Accretion | RCP4.5 | 2100 | 16.5486 | 20.0312 | 24.464 | 27.8183 | 31.185
North BayIce Accretion2023RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2023 | 15.6913 | 18.753 | 22.638 | 25.5809 | 28.5516
North BayIce Accretion2025RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2025 | 15.7908 | 18.8778 | 22.7993 | 25.7715 | 28.7641
North BayIce Accretion2030RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2030 | 15.8903 | 19.0026 | 22.9607 | 25.9621 | 28.9766
North BayIce Accretion2035RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2035 | 15.9898 | 19.1273 | 23.122 | 26.1527 | 29.1892
North BayIce Accretion2040RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2040 | 16.0894 | 19.2521 | 23.2833 | 26.3433 | 29.4017
North BayIce Accretion2045RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2045 | 16.1889 | 19.3769 | 23.4447 | 26.5339 | 29.6142
North BayIce Accretion2050RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2050 | 16.4139 | 19.6806 | 23.848 | 27.0129 | 30.1704
North BayIce Accretion2055RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2055 | 16.5394 | 19.8596 | 24.09 | 27.3013 | 30.5142
North BayIce Accretion2060RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2060 | 16.665 | 20.0385 | 24.332 | 27.5896 | 30.8579
North BayIce Accretion2065RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2065 | 16.7905 | 20.2175 | 24.574 | 27.878 | 31.2016
North BayIce Accretion2070RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2070 | 16.916 | 20.3964 | 24.816 | 28.1664 | 31.5454
North BayIce Accretion2075RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2075 | 16.8242 | 20.3051 | 24.728 | 28.0794 | 31.4553
North BayIce Accretion2080RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2080 | 16.7323 | 20.2138 | 24.64 | 27.9924 | 31.3652
North BayIce Accretion2085RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2085 | 16.6405 | 20.1225 | 24.552 | 27.9053 | 31.2751
North BayIce Accretion2090RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2090 | 16.5282 | 20.0251 | 24.4713 | 27.8432 | 31.222
North BayIce Accretion2095RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2095 | 16.5078 | 20.019 | 24.4787 | 27.8681 | 31.2589
North BayIce Accretion2100RCP6.0 | North Bay | Ice Accretion | RCP6.0 | 2100 | 16.4874 | 20.013 | 24.486 | 27.8929 | 31.2959
North BayIce Accretion2023RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2023 | 15.6913 | 18.753 | 22.638 | 25.5809 | 28.5516
North BayIce Accretion2025RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2025 | 15.8903 | 19.0026 | 22.9607 | 25.9621 | 28.9766
North BayIce Accretion2030RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2030 | 16.0894 | 19.2521 | 23.2833 | 26.3433 | 29.4017
North BayIce Accretion2035RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2035 | 16.2884 | 19.5017 | 23.606 | 26.7245 | 29.8267
North BayIce Accretion2040RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2040 | 16.4976 | 19.7999 | 24.0093 | 27.2051 | 30.3996
North BayIce Accretion2045RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2045 | 16.7068 | 20.0982 | 24.4127 | 27.6858 | 30.9725
North BayIce Accretion2050RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2050 | 16.7936 | 20.2747 | 24.6987 | 28.0504 | 31.4252
North BayIce Accretion2055RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2055 | 16.6711 | 20.153 | 24.5813 | 27.9344 | 31.3051
North BayIce Accretion2060RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2060 | 16.5282 | 20.0251 | 24.4713 | 27.8432 | 31.222
North BayIce Accretion2065RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2065 | 16.5078 | 20.019 | 24.4787 | 27.8681 | 31.2589
North BayIce Accretion2070RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2070 | 16.0689 | 19.5199 | 23.8847 | 27.2134 | 30.5382
North BayIce Accretion2075RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2075 | 15.6505 | 19.0269 | 23.2833 | 26.5339 | 29.7805
North BayIce Accretion2080RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2080 | 15.2321 | 18.5339 | 22.682 | 25.8544 | 29.0228
North BayIce Accretion2085RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2085 | 14.9948 | 18.2874 | 22.44 | 25.5934 | 28.7595
North BayIce Accretion2090RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2090 | 14.7575 | 18.0409 | 22.198 | 25.3323 | 28.4962
North BayIce Accretion2095RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2095 | 14.7575 | 18.0409 | 22.198 | 25.3323 | 28.4962
North BayIce Accretion2100RCP8.5 | North Bay | Ice Accretion | RCP8.5 | 2100 | 14.7575 | 18.0409 | 22.198 | 25.3323 | 28.4962
North BayWind2023RCP4.5 | North Bay | Wind | RCP4.5 | 2023 | 73.1273 | 78.745 | 84.6552 | 90.5721 | 96.4878
North BayWind2025RCP4.5 | North Bay | Wind | RCP4.5 | 2025 | 73.1515 | 78.771 | 84.6818 | 90.6005 | 96.5165
North BayWind2030RCP4.5 | North Bay | Wind | RCP4.5 | 2030 | 73.1756 | 78.797 | 84.7084 | 90.629 | 96.5452
North BayWind2035RCP4.5 | North Bay | Wind | RCP4.5 | 2035 | 73.1998 | 78.8231 | 84.735 | 90.6575 | 96.574
North BayWind2040RCP4.5 | North Bay | Wind | RCP4.5 | 2040 | 73.224 | 78.8491 | 84.7616 | 90.6859 | 96.6027
North BayWind2045RCP4.5 | North Bay | Wind | RCP4.5 | 2045 | 73.2482 | 78.8752 | 84.7882 | 90.7144 | 96.6314
North BayWind2050RCP4.5 | North Bay | Wind | RCP4.5 | 2050 | 73.2143 | 78.8215 | 84.709 | 90.6152 | 96.5108
North BayWind2055RCP4.5 | North Bay | Wind | RCP4.5 | 2055 | 73.1563 | 78.7418 | 84.6031 | 90.4876 | 96.3614
North BayWind2060RCP4.5 | North Bay | Wind | RCP4.5 | 2060 | 73.0983 | 78.6622 | 84.4973 | 90.36 | 96.212
North BayWind2065RCP4.5 | North Bay | Wind | RCP4.5 | 2065 | 73.0403 | 78.5825 | 84.3914 | 90.2323 | 96.0626
North BayWind2070RCP4.5 | North Bay | Wind | RCP4.5 | 2070 | 72.9822 | 78.5028 | 84.2856 | 90.1047 | 95.9132
North BayWind2075RCP4.5 | North Bay | Wind | RCP4.5 | 2075 | 73.0439 | 78.5822 | 84.3864 | 90.223 | 96.0505
North BayWind2080RCP4.5 | North Bay | Wind | RCP4.5 | 2080 | 73.1055 | 78.6616 | 84.4872 | 90.3414 | 96.1877
North BayWind2085RCP4.5 | North Bay | Wind | RCP4.5 | 2085 | 73.1672 | 78.7411 | 84.588 | 90.4597 | 96.325
North BayWind2090RCP4.5 | North Bay | Wind | RCP4.5 | 2090 | 73.2288 | 78.8205 | 84.6888 | 90.5781 | 96.4622
North BayWind2095RCP4.5 | North Bay | Wind | RCP4.5 | 2095 | 73.2905 | 78.8999 | 84.7896 | 90.6964 | 96.5995
North BayWind2100RCP4.5 | North Bay | Wind | RCP4.5 | 2100 | 73.3521 | 78.9793 | 84.8904 | 90.8148 | 96.7368
North BayWind2023RCP6.0 | North Bay | Wind | RCP6.0 | 2023 | 73.1273 | 78.745 | 84.6552 | 90.5721 | 96.4878
North BayWind2025RCP6.0 | North Bay | Wind | RCP6.0 | 2025 | 73.1515 | 78.771 | 84.6818 | 90.6005 | 96.5165
North BayWind2030RCP6.0 | North Bay | Wind | RCP6.0 | 2030 | 73.1756 | 78.797 | 84.7084 | 90.629 | 96.5452
North BayWind2035RCP6.0 | North Bay | Wind | RCP6.0 | 2035 | 73.1998 | 78.8231 | 84.735 | 90.6575 | 96.574
North BayWind2040RCP6.0 | North Bay | Wind | RCP6.0 | 2040 | 73.224 | 78.8491 | 84.7616 | 90.6859 | 96.6027
North BayWind2045RCP6.0 | North Bay | Wind | RCP6.0 | 2045 | 73.2482 | 78.8752 | 84.7882 | 90.7144 | 96.6314
North BayWind2050RCP6.0 | North Bay | Wind | RCP6.0 | 2050 | 73.2143 | 78.8215 | 84.709 | 90.6152 | 96.5108
North BayWind2055RCP6.0 | North Bay | Wind | RCP6.0 | 2055 | 73.1563 | 78.7418 | 84.6031 | 90.4876 | 96.3614
North BayWind2060RCP6.0 | North Bay | Wind | RCP6.0 | 2060 | 73.0983 | 78.6622 | 84.4973 | 90.36 | 96.212
North BayWind2065RCP6.0 | North Bay | Wind | RCP6.0 | 2065 | 73.0403 | 78.5825 | 84.3914 | 90.2323 | 96.0626
North BayWind2070RCP6.0 | North Bay | Wind | RCP6.0 | 2070 | 72.9822 | 78.5028 | 84.2856 | 90.1047 | 95.9132
North BayWind2075RCP6.0 | North Bay | Wind | RCP6.0 | 2075 | 73.0747 | 78.6219 | 84.4368 | 90.2822 | 96.1191
North BayWind2080RCP6.0 | North Bay | Wind | RCP6.0 | 2080 | 73.1672 | 78.7411 | 84.588 | 90.4597 | 96.325
North BayWind2085RCP6.0 | North Bay | Wind | RCP6.0 | 2085 | 73.2597 | 78.8602 | 84.7392 | 90.6372 | 96.5309
North BayWind2090RCP6.0 | North Bay | Wind | RCP6.0 | 2090 | 73.3497 | 78.9741 | 84.882 | 90.8028 | 96.7208
North BayWind2095RCP6.0 | North Bay | Wind | RCP6.0 | 2095 | 73.3473 | 78.9689 | 84.8736 | 90.7908 | 96.7048
North BayWind2100RCP6.0 | North Bay | Wind | RCP6.0 | 2100 | 73.3449 | 78.9637 | 84.8652 | 90.7788 | 96.6889
North BayWind2023RCP8.5 | North Bay | Wind | RCP8.5 | 2023 | 73.1273 | 78.745 | 84.6552 | 90.5721 | 96.4878
North BayWind2025RCP8.5 | North Bay | Wind | RCP8.5 | 2025 | 73.1756 | 78.797 | 84.7084 | 90.629 | 96.5452
North BayWind2030RCP8.5 | North Bay | Wind | RCP8.5 | 2030 | 73.224 | 78.8491 | 84.7616 | 90.6859 | 96.6027
North BayWind2035RCP8.5 | North Bay | Wind | RCP8.5 | 2035 | 73.2724 | 78.9012 | 84.8148 | 90.7428 | 96.6601
North BayWind2040RCP8.5 | North Bay | Wind | RCP8.5 | 2040 | 73.1756 | 78.7684 | 84.6384 | 90.5301 | 96.4112
North BayWind2045RCP8.5 | North Bay | Wind | RCP8.5 | 2045 | 73.0789 | 78.6356 | 84.462 | 90.3174 | 96.1622
North BayWind2050RCP8.5 | North Bay | Wind | RCP8.5 | 2050 | 73.1055 | 78.6616 | 84.4872 | 90.3414 | 96.1877
North BayWind2055RCP8.5 | North Bay | Wind | RCP8.5 | 2055 | 73.2288 | 78.8205 | 84.6888 | 90.5781 | 96.4622
North BayWind2060RCP8.5 | North Bay | Wind | RCP8.5 | 2060 | 73.3497 | 78.9741 | 84.882 | 90.8028 | 96.7208
North BayWind2065RCP8.5 | North Bay | Wind | RCP8.5 | 2065 | 73.3473 | 78.9689 | 84.8736 | 90.7908 | 96.7048
North BayWind2070RCP8.5 | North Bay | Wind | RCP8.5 | 2070 | 73.6229 | 79.3178 | 85.316 | 91.3061 | 97.2985
North BayWind2075RCP8.5 | North Bay | Wind | RCP8.5 | 2075 | 73.901 | 79.672 | 85.7668 | 91.8334 | 97.9082
North BayWind2080RCP8.5 | North Bay | Wind | RCP8.5 | 2080 | 74.179 | 80.0261 | 86.2176 | 92.3607 | 98.5179
North BayWind2085RCP8.5 | North Bay | Wind | RCP8.5 | 2085 | 74.4365 | 80.3035 | 86.5116 | 92.6798 | 98.853
North BayWind2090RCP8.5 | North Bay | Wind | RCP8.5 | 2090 | 74.694 | 80.5808 | 86.8056 | 92.9988 | 99.1882
North BayWind2095RCP8.5 | North Bay | Wind | RCP8.5 | 2095 | 74.694 | 80.5808 | 86.8056 | 92.9988 | 99.1882
North BayWind2100RCP8.5 | North Bay | Wind | RCP8.5 | 2100 | 74.694 | 80.5808 | 86.8056 | 92.9988 | 99.1882
North YorkIce Accretion2023RCP4.5 | North York | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
North YorkIce Accretion2025RCP4.5 | North York | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
North YorkIce Accretion2030RCP4.5 | North York | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
North YorkIce Accretion2035RCP4.5 | North York | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
North YorkIce Accretion2040RCP4.5 | North York | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
North YorkIce Accretion2045RCP4.5 | North York | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
North YorkIce Accretion2050RCP4.5 | North York | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
North YorkIce Accretion2055RCP4.5 | North York | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
North YorkIce Accretion2060RCP4.5 | North York | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
North YorkIce Accretion2065RCP4.5 | North York | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
North YorkIce Accretion2070RCP4.5 | North York | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
North YorkIce Accretion2075RCP4.5 | North York | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
North YorkIce Accretion2080RCP4.5 | North York | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
North YorkIce Accretion2085RCP4.5 | North York | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
North YorkIce Accretion2090RCP4.5 | North York | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
North YorkIce Accretion2095RCP4.5 | North York | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
North YorkIce Accretion2100RCP4.5 | North York | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
North YorkIce Accretion2023RCP6.0 | North York | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
North YorkIce Accretion2025RCP6.0 | North York | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
North YorkIce Accretion2030RCP6.0 | North York | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
North YorkIce Accretion2035RCP6.0 | North York | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
North YorkIce Accretion2040RCP6.0 | North York | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
North YorkIce Accretion2045RCP6.0 | North York | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
North YorkIce Accretion2050RCP6.0 | North York | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
North YorkIce Accretion2055RCP6.0 | North York | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
North YorkIce Accretion2060RCP6.0 | North York | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
North YorkIce Accretion2065RCP6.0 | North York | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
North YorkIce Accretion2070RCP6.0 | North York | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
North YorkIce Accretion2075RCP6.0 | North York | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
North YorkIce Accretion2080RCP6.0 | North York | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
North YorkIce Accretion2085RCP6.0 | North York | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
North YorkIce Accretion2090RCP6.0 | North York | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
North YorkIce Accretion2095RCP6.0 | North York | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
North YorkIce Accretion2100RCP6.0 | North York | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
North YorkIce Accretion2023RCP8.5 | North York | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
North YorkIce Accretion2025RCP8.5 | North York | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
North YorkIce Accretion2030RCP8.5 | North York | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
North YorkIce Accretion2035RCP8.5 | North York | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
North YorkIce Accretion2040RCP8.5 | North York | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
North YorkIce Accretion2045RCP8.5 | North York | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
North YorkIce Accretion2050RCP8.5 | North York | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
North YorkIce Accretion2055RCP8.5 | North York | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
North YorkIce Accretion2060RCP8.5 | North York | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
North YorkIce Accretion2065RCP8.5 | North York | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
North YorkIce Accretion2070RCP8.5 | North York | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
North YorkIce Accretion2075RCP8.5 | North York | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
North YorkIce Accretion2080RCP8.5 | North York | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
North YorkIce Accretion2085RCP8.5 | North York | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
North YorkIce Accretion2090RCP8.5 | North York | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
North YorkIce Accretion2095RCP8.5 | North York | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
North YorkIce Accretion2100RCP8.5 | North York | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
North YorkWind2023RCP4.5 | North York | Wind | RCP4.5 | 2023 | 83.9588 | 90.3904 | 97.1552 | 103.9249 | 110.6906
North YorkWind2025RCP4.5 | North York | Wind | RCP4.5 | 2025 | 83.9742 | 90.4235 | 97.2086 | 103.9959 | 110.779
North YorkWind2030RCP4.5 | North York | Wind | RCP4.5 | 2030 | 83.9895 | 90.4566 | 97.2619 | 104.0668 | 110.8675
North YorkWind2035RCP4.5 | North York | Wind | RCP4.5 | 2035 | 84.0049 | 90.4897 | 97.3152 | 104.1377 | 110.956
North YorkWind2040RCP4.5 | North York | Wind | RCP4.5 | 2040 | 84.0202 | 90.5227 | 97.3686 | 104.2086 | 111.0444
North YorkWind2045RCP4.5 | North York | Wind | RCP4.5 | 2045 | 84.0356 | 90.5558 | 97.4219 | 104.2795 | 111.1329
North YorkWind2050RCP4.5 | North York | Wind | RCP4.5 | 2050 | 84.133 | 90.6917 | 97.6053 | 104.502 | 111.3983
North YorkWind2055RCP4.5 | North York | Wind | RCP4.5 | 2055 | 84.2151 | 90.7946 | 97.7353 | 104.6535 | 111.5752
North YorkWind2060RCP4.5 | North York | Wind | RCP4.5 | 2060 | 84.2972 | 90.8974 | 97.8652 | 104.8051 | 111.7521
North YorkWind2065RCP4.5 | North York | Wind | RCP4.5 | 2065 | 84.3793 | 91.0002 | 97.9952 | 104.9566 | 111.9291
North YorkWind2070RCP4.5 | North York | Wind | RCP4.5 | 2070 | 84.4614 | 91.1031 | 98.1252 | 105.1081 | 112.106
North YorkWind2075RCP4.5 | North York | Wind | RCP4.5 | 2075 | 84.6037 | 91.2865 | 98.3596 | 105.3866 | 112.4285
North YorkWind2080RCP4.5 | North York | Wind | RCP4.5 | 2080 | 84.7461 | 91.4699 | 98.594 | 105.6651 | 112.7511
North YorkWind2085RCP4.5 | North York | Wind | RCP4.5 | 2085 | 84.8885 | 91.6534 | 98.8285 | 105.9436 | 113.0736
North YorkWind2090RCP4.5 | North York | Wind | RCP4.5 | 2090 | 85.0309 | 91.8368 | 99.0629 | 106.2221 | 113.3961
North YorkWind2095RCP4.5 | North York | Wind | RCP4.5 | 2095 | 85.1733 | 92.0202 | 99.2973 | 106.5006 | 113.7186
North YorkWind2100RCP4.5 | North York | Wind | RCP4.5 | 2100 | 85.3157 | 92.2036 | 99.5317 | 106.7792 | 114.0412
North YorkWind2023RCP6.0 | North York | Wind | RCP6.0 | 2023 | 83.9588 | 90.3904 | 97.1552 | 103.9249 | 110.6906
North YorkWind2025RCP6.0 | North York | Wind | RCP6.0 | 2025 | 83.9742 | 90.4235 | 97.2086 | 103.9959 | 110.779
North YorkWind2030RCP6.0 | North York | Wind | RCP6.0 | 2030 | 83.9895 | 90.4566 | 97.2619 | 104.0668 | 110.8675
North YorkWind2035RCP6.0 | North York | Wind | RCP6.0 | 2035 | 84.0049 | 90.4897 | 97.3152 | 104.1377 | 110.956
North YorkWind2040RCP6.0 | North York | Wind | RCP6.0 | 2040 | 84.0202 | 90.5227 | 97.3686 | 104.2086 | 111.0444
North YorkWind2045RCP6.0 | North York | Wind | RCP6.0 | 2045 | 84.0356 | 90.5558 | 97.4219 | 104.2795 | 111.1329
North YorkWind2050RCP6.0 | North York | Wind | RCP6.0 | 2050 | 84.133 | 90.6917 | 97.6053 | 104.502 | 111.3983
North YorkWind2055RCP6.0 | North York | Wind | RCP6.0 | 2055 | 84.2151 | 90.7946 | 97.7353 | 104.6535 | 111.5752
North YorkWind2060RCP6.0 | North York | Wind | RCP6.0 | 2060 | 84.2972 | 90.8974 | 97.8652 | 104.8051 | 111.7521
North YorkWind2065RCP6.0 | North York | Wind | RCP6.0 | 2065 | 84.3793 | 91.0002 | 97.9952 | 104.9566 | 111.9291
North YorkWind2070RCP6.0 | North York | Wind | RCP6.0 | 2070 | 84.4614 | 91.1031 | 98.1252 | 105.1081 | 112.106
North YorkWind2075RCP6.0 | North York | Wind | RCP6.0 | 2075 | 84.6749 | 91.3782 | 98.4768 | 105.5259 | 112.5898
North YorkWind2080RCP6.0 | North York | Wind | RCP6.0 | 2080 | 84.8885 | 91.6534 | 98.8285 | 105.9436 | 113.0736
North YorkWind2085RCP6.0 | North York | Wind | RCP6.0 | 2085 | 85.1021 | 91.9285 | 99.1801 | 106.3614 | 113.5574
North YorkWind2090RCP6.0 | North York | Wind | RCP6.0 | 2090 | 85.7568 | 92.7449 | 100.201 | 107.5576 | 114.9332
North YorkWind2095RCP6.0 | North York | Wind | RCP6.0 | 2095 | 86.1979 | 93.2862 | 100.8703 | 108.336 | 115.8252
North YorkWind2100RCP6.0 | North York | Wind | RCP6.0 | 2100 | 86.6391 | 93.8274 | 101.5396 | 109.1144 | 116.7172
North YorkWind2023RCP8.5 | North York | Wind | RCP8.5 | 2023 | 83.9588 | 90.3904 | 97.1552 | 103.9249 | 110.6906
North YorkWind2025RCP8.5 | North York | Wind | RCP8.5 | 2025 | 83.9895 | 90.4566 | 97.2619 | 104.0668 | 110.8675
North YorkWind2030RCP8.5 | North York | Wind | RCP8.5 | 2030 | 84.0202 | 90.5227 | 97.3686 | 104.2086 | 111.0444
North YorkWind2035RCP8.5 | North York | Wind | RCP8.5 | 2035 | 84.0509 | 90.5889 | 97.4753 | 104.3505 | 111.2214
North YorkWind2040RCP8.5 | North York | Wind | RCP8.5 | 2040 | 84.1878 | 90.7603 | 97.6919 | 104.603 | 111.5162
North YorkWind2045RCP8.5 | North York | Wind | RCP8.5 | 2045 | 84.3246 | 90.9317 | 97.9086 | 104.8556 | 111.8111
North YorkWind2050RCP8.5 | North York | Wind | RCP8.5 | 2050 | 84.7461 | 91.4699 | 98.594 | 105.6651 | 112.7511
North YorkWind2055RCP8.5 | North York | Wind | RCP8.5 | 2055 | 85.0309 | 91.8368 | 99.0629 | 106.2221 | 113.3961
North YorkWind2060RCP8.5 | North York | Wind | RCP8.5 | 2060 | 85.7568 | 92.7449 | 100.201 | 107.5576 | 114.9332
North YorkWind2065RCP8.5 | North York | Wind | RCP8.5 | 2065 | 86.1979 | 93.2862 | 100.8703 | 108.336 | 115.8252
North YorkWind2070RCP8.5 | North York | Wind | RCP8.5 | 2070 | 86.7703 | 94.0048 | 101.7756 | 109.405 | 117.0563
North YorkWind2075RCP8.5 | North York | Wind | RCP8.5 | 2075 | 86.9015 | 94.1822 | 102.0117 | 109.6957 | 117.3954
North YorkWind2080RCP8.5 | North York | Wind | RCP8.5 | 2080 | 87.0327 | 94.3597 | 102.2477 | 109.9863 | 117.7345
North YorkWind2085RCP8.5 | North York | Wind | RCP8.5 | 2085 | 87.3133 | 94.7566 | 102.7909 | 110.6505 | 118.5252
North YorkWind2090RCP8.5 | North York | Wind | RCP8.5 | 2090 | 87.5939 | 95.1535 | 103.3341 | 111.3148 | 119.3158
North YorkWind2095RCP8.5 | North York | Wind | RCP8.5 | 2095 | 87.5939 | 95.1535 | 103.3341 | 111.3148 | 119.3158
North YorkWind2100RCP8.5 | North York | Wind | RCP8.5 | 2100 | 87.5939 | 95.1535 | 103.3341 | 111.3148 | 119.3158
NorwoodIce Accretion2023RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3065 | 31.563
NorwoodIce Accretion2025RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2025 | 17.544 | 20.9091 | 25.1667 | 28.4148 | 31.6837
NorwoodIce Accretion2030RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2030 | 17.6049 | 20.9852 | 25.2583 | 28.5231 | 31.8045
NorwoodIce Accretion2035RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2035 | 17.6658 | 21.0613 | 25.35 | 28.6314 | 31.9252
NorwoodIce Accretion2040RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2040 | 17.7267 | 21.1373 | 25.4417 | 28.7397 | 32.046
NorwoodIce Accretion2045RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2045 | 17.7876 | 21.2134 | 25.5333 | 28.848 | 32.1667
NorwoodIce Accretion2050RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2050 | 17.8032 | 21.248 | 25.595 | 28.928 | 32.2623
NorwoodIce Accretion2055RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2055 | 17.758 | 21.2065 | 25.565 | 28.8997 | 32.2371
NorwoodIce Accretion2060RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2060 | 17.7128 | 21.165 | 25.535 | 28.8715 | 32.2119
NorwoodIce Accretion2065RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2065 | 17.6675 | 21.1235 | 25.505 | 28.8432 | 32.1867
NorwoodIce Accretion2070RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2070 | 17.6223 | 21.082 | 25.475 | 28.815 | 32.1615
NorwoodIce Accretion2075RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2075 | 17.6919 | 21.1927 | 25.6375 | 29.0175 | 32.403
NorwoodIce Accretion2080RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2080 | 17.7615 | 21.3033 | 25.8 | 29.2199 | 32.6445
NorwoodIce Accretion2085RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2085 | 17.8311 | 21.414 | 25.9625 | 29.4224 | 32.886
NorwoodIce Accretion2090RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2090 | 17.9006 | 21.5247 | 26.125 | 29.6248 | 33.1275
NorwoodIce Accretion2095RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2095 | 17.9702 | 21.6353 | 26.2875 | 29.8273 | 33.369
NorwoodIce Accretion2100RCP4.5 | Norwood | Ice Accretion | RCP4.5 | 2100 | 18.0398 | 21.746 | 26.45 | 30.0297 | 33.6105
NorwoodIce Accretion2023RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3065 | 31.563
NorwoodIce Accretion2025RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2025 | 17.544 | 20.9091 | 25.1667 | 28.4148 | 31.6837
NorwoodIce Accretion2030RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2030 | 17.6049 | 20.9852 | 25.2583 | 28.5231 | 31.8045
NorwoodIce Accretion2035RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2035 | 17.6658 | 21.0613 | 25.35 | 28.6314 | 31.9252
NorwoodIce Accretion2040RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2040 | 17.7267 | 21.1373 | 25.4417 | 28.7397 | 32.046
NorwoodIce Accretion2045RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2045 | 17.7876 | 21.2134 | 25.5333 | 28.848 | 32.1667
NorwoodIce Accretion2050RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2050 | 17.8032 | 21.248 | 25.595 | 28.928 | 32.2623
NorwoodIce Accretion2055RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2055 | 17.758 | 21.2065 | 25.565 | 28.8997 | 32.2371
NorwoodIce Accretion2060RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2060 | 17.7128 | 21.165 | 25.535 | 28.8715 | 32.2119
NorwoodIce Accretion2065RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2065 | 17.6675 | 21.1235 | 25.505 | 28.8432 | 32.1867
NorwoodIce Accretion2070RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2070 | 17.6223 | 21.082 | 25.475 | 28.815 | 32.1615
NorwoodIce Accretion2075RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2075 | 17.7267 | 21.248 | 25.7188 | 29.1187 | 32.5237
NorwoodIce Accretion2080RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2080 | 17.8311 | 21.414 | 25.9625 | 29.4224 | 32.886
NorwoodIce Accretion2085RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2085 | 17.9354 | 21.58 | 26.2063 | 29.7261 | 33.2482
NorwoodIce Accretion2090RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2090 | 17.7499 | 21.4486 | 26.1333 | 29.7002 | 33.264
NorwoodIce Accretion2095RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2095 | 17.4599 | 21.1512 | 25.8167 | 29.3706 | 32.9175
NorwoodIce Accretion2100RCP6.0 | Norwood | Ice Accretion | RCP6.0 | 2100 | 17.17 | 20.8537 | 25.5 | 29.041 | 32.571
NorwoodIce Accretion2023RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3065 | 31.563
NorwoodIce Accretion2025RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2025 | 17.6049 | 20.9852 | 25.2583 | 28.5231 | 31.8045
NorwoodIce Accretion2030RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2030 | 17.7267 | 21.1373 | 25.4417 | 28.7397 | 32.046
NorwoodIce Accretion2035RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2035 | 17.8485 | 21.2895 | 25.625 | 28.9562 | 32.2875
NorwoodIce Accretion2040RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2040 | 17.7731 | 21.2203 | 25.575 | 28.9092 | 32.2455
NorwoodIce Accretion2045RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2045 | 17.6977 | 21.1512 | 25.525 | 28.8621 | 32.2035
NorwoodIce Accretion2050RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2050 | 17.7615 | 21.3033 | 25.8 | 29.2199 | 32.6445
NorwoodIce Accretion2055RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2055 | 17.9006 | 21.5247 | 26.125 | 29.6248 | 33.1275
NorwoodIce Accretion2060RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2060 | 17.7499 | 21.4486 | 26.1333 | 29.7002 | 33.264
NorwoodIce Accretion2065RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2065 | 17.4599 | 21.1512 | 25.8167 | 29.3706 | 32.9175
NorwoodIce Accretion2070RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2070 | 16.8801 | 20.5287 | 25.1417 | 28.6455 | 32.151
NorwoodIce Accretion2075RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2075 | 16.5901 | 20.2036 | 24.7833 | 28.25 | 31.731
NorwoodIce Accretion2080RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2080 | 16.3002 | 19.8785 | 24.425 | 27.8545 | 31.311
NorwoodIce Accretion2085RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2085 | 15.6826 | 19.1626 | 23.5875 | 26.9222 | 30.2715
NorwoodIce Accretion2090RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2090 | 15.0651 | 18.4468 | 22.75 | 25.99 | 29.232
NorwoodIce Accretion2095RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2095 | 15.0651 | 18.4468 | 22.75 | 25.99 | 29.232
NorwoodIce Accretion2100RCP8.5 | Norwood | Ice Accretion | RCP8.5 | 2100 | 15.0651 | 18.4468 | 22.75 | 25.99 | 29.232
NorwoodWind2023RCP4.5 | Norwood | Wind | RCP4.5 | 2023 | 74.4377 | 80.2119 | 86.301 | 92.3697 | 98.4518
NorwoodWind2025RCP4.5 | Norwood | Wind | RCP4.5 | 2025 | 74.4674 | 80.2559 | 86.3612 | 92.4464 | 98.5433
NorwoodWind2030RCP4.5 | Norwood | Wind | RCP4.5 | 2030 | 74.4971 | 80.2999 | 86.4214 | 92.523 | 98.6348
NorwoodWind2035RCP4.5 | Norwood | Wind | RCP4.5 | 2035 | 74.5268 | 80.3439 | 86.4816 | 92.5997 | 98.7263
NorwoodWind2040RCP4.5 | Norwood | Wind | RCP4.5 | 2040 | 74.5565 | 80.3879 | 86.5418 | 92.6764 | 98.8178
NorwoodWind2045RCP4.5 | Norwood | Wind | RCP4.5 | 2045 | 74.5862 | 80.4319 | 86.602 | 92.7531 | 98.9093
NorwoodWind2050RCP4.5 | Norwood | Wind | RCP4.5 | 2050 | 74.5922 | 80.4311 | 86.5951 | 92.7414 | 98.891
NorwoodWind2055RCP4.5 | Norwood | Wind | RCP4.5 | 2055 | 74.5684 | 80.3863 | 86.528 | 92.6531 | 98.7812
NorwoodWind2060RCP4.5 | Norwood | Wind | RCP4.5 | 2060 | 74.5446 | 80.3415 | 86.461 | 92.5648 | 98.6714
NorwoodWind2065RCP4.5 | Norwood | Wind | RCP4.5 | 2065 | 74.5209 | 80.2967 | 86.3939 | 92.4764 | 98.5616
NorwoodWind2070RCP4.5 | Norwood | Wind | RCP4.5 | 2070 | 74.4971 | 80.2519 | 86.3268 | 92.3881 | 98.4518
NorwoodWind2075RCP4.5 | Norwood | Wind | RCP4.5 | 2075 | 74.4748 | 80.2266 | 86.2967 | 92.3543 | 98.4158
NorwoodWind2080RCP4.5 | Norwood | Wind | RCP4.5 | 2080 | 74.4526 | 80.2013 | 86.2666 | 92.3206 | 98.3799
NorwoodWind2085RCP4.5 | Norwood | Wind | RCP4.5 | 2085 | 74.4303 | 80.176 | 86.2365 | 92.2869 | 98.3439
NorwoodWind2090RCP4.5 | Norwood | Wind | RCP4.5 | 2090 | 74.408 | 80.1506 | 86.2064 | 92.2531 | 98.308
NorwoodWind2095RCP4.5 | Norwood | Wind | RCP4.5 | 2095 | 74.3857 | 80.1253 | 86.1763 | 92.2194 | 98.272
NorwoodWind2100RCP4.5 | Norwood | Wind | RCP4.5 | 2100 | 74.3635 | 80.1 | 86.1462 | 92.1856 | 98.2361
NorwoodWind2023RCP6.0 | Norwood | Wind | RCP6.0 | 2023 | 74.4377 | 80.2119 | 86.301 | 92.3697 | 98.4518
NorwoodWind2025RCP6.0 | Norwood | Wind | RCP6.0 | 2025 | 74.4674 | 80.2559 | 86.3612 | 92.4464 | 98.5433
NorwoodWind2030RCP6.0 | Norwood | Wind | RCP6.0 | 2030 | 74.4971 | 80.2999 | 86.4214 | 92.523 | 98.6348
NorwoodWind2035RCP6.0 | Norwood | Wind | RCP6.0 | 2035 | 74.5268 | 80.3439 | 86.4816 | 92.5997 | 98.7263
NorwoodWind2040RCP6.0 | Norwood | Wind | RCP6.0 | 2040 | 74.5565 | 80.3879 | 86.5418 | 92.6764 | 98.8178
NorwoodWind2045RCP6.0 | Norwood | Wind | RCP6.0 | 2045 | 74.5862 | 80.4319 | 86.602 | 92.7531 | 98.9093
NorwoodWind2050RCP6.0 | Norwood | Wind | RCP6.0 | 2050 | 74.5922 | 80.4311 | 86.5951 | 92.7414 | 98.891
NorwoodWind2055RCP6.0 | Norwood | Wind | RCP6.0 | 2055 | 74.5684 | 80.3863 | 86.528 | 92.6531 | 98.7812
NorwoodWind2060RCP6.0 | Norwood | Wind | RCP6.0 | 2060 | 74.5446 | 80.3415 | 86.461 | 92.5648 | 98.6714
NorwoodWind2065RCP6.0 | Norwood | Wind | RCP6.0 | 2065 | 74.5209 | 80.2967 | 86.3939 | 92.4764 | 98.5616
NorwoodWind2070RCP6.0 | Norwood | Wind | RCP6.0 | 2070 | 74.4971 | 80.2519 | 86.3268 | 92.3881 | 98.4518
NorwoodWind2075RCP6.0 | Norwood | Wind | RCP6.0 | 2075 | 74.4637 | 80.2139 | 86.2817 | 92.3375 | 98.3978
NorwoodWind2080RCP6.0 | Norwood | Wind | RCP6.0 | 2080 | 74.4303 | 80.176 | 86.2365 | 92.2869 | 98.3439
NorwoodWind2085RCP6.0 | Norwood | Wind | RCP6.0 | 2085 | 74.3969 | 80.138 | 86.1913 | 92.2362 | 98.29
NorwoodWind2090RCP6.0 | Norwood | Wind | RCP6.0 | 2090 | 74.3511 | 80.076 | 86.1061 | 92.1304 | 98.1642
NorwoodWind2095RCP6.0 | Norwood | Wind | RCP6.0 | 2095 | 74.3387 | 80.052 | 86.0659 | 92.0752 | 98.0923
NorwoodWind2100RCP6.0 | Norwood | Wind | RCP6.0 | 2100 | 74.3263 | 80.028 | 86.0258 | 92.02 | 98.0204
NorwoodWind2023RCP8.5 | Norwood | Wind | RCP8.5 | 2023 | 74.4377 | 80.2119 | 86.301 | 92.3697 | 98.4518
NorwoodWind2025RCP8.5 | Norwood | Wind | RCP8.5 | 2025 | 74.4971 | 80.2999 | 86.4214 | 92.523 | 98.6348
NorwoodWind2030RCP8.5 | Norwood | Wind | RCP8.5 | 2030 | 74.5565 | 80.3879 | 86.5418 | 92.6764 | 98.8178
NorwoodWind2035RCP8.5 | Norwood | Wind | RCP8.5 | 2035 | 74.6159 | 80.4759 | 86.6622 | 92.8298 | 99.0008
NorwoodWind2040RCP8.5 | Norwood | Wind | RCP8.5 | 2040 | 74.5763 | 80.4012 | 86.5504 | 92.6825 | 98.8178
NorwoodWind2045RCP8.5 | Norwood | Wind | RCP8.5 | 2045 | 74.5367 | 80.3266 | 86.4386 | 92.5353 | 98.6348
NorwoodWind2050RCP8.5 | Norwood | Wind | RCP8.5 | 2050 | 74.4526 | 80.2013 | 86.2666 | 92.3206 | 98.3799
NorwoodWind2055RCP8.5 | Norwood | Wind | RCP8.5 | 2055 | 74.408 | 80.1506 | 86.2064 | 92.2531 | 98.308
NorwoodWind2060RCP8.5 | Norwood | Wind | RCP8.5 | 2060 | 74.3511 | 80.076 | 86.1061 | 92.1304 | 98.1642
NorwoodWind2065RCP8.5 | Norwood | Wind | RCP8.5 | 2065 | 74.3387 | 80.052 | 86.0659 | 92.0752 | 98.0923
NorwoodWind2070RCP8.5 | Norwood | Wind | RCP8.5 | 2070 | 74.2941 | 79.9853 | 85.9713 | 91.9556 | 97.9452
NorwoodWind2075RCP8.5 | Norwood | Wind | RCP8.5 | 2075 | 74.262 | 79.9427 | 85.9169 | 91.8912 | 97.8701
NorwoodWind2080RCP8.5 | Norwood | Wind | RCP8.5 | 2080 | 74.2298 | 79.9 | 85.8624 | 91.8268 | 97.7949
NorwoodWind2085RCP8.5 | Norwood | Wind | RCP8.5 | 2085 | 74.1889 | 79.872 | 85.8495 | 91.8314 | 97.8096
NorwoodWind2090RCP8.5 | Norwood | Wind | RCP8.5 | 2090 | 74.1481 | 79.844 | 85.8366 | 91.836 | 97.8243
NorwoodWind2095RCP8.5 | Norwood | Wind | RCP8.5 | 2095 | 74.1481 | 79.844 | 85.8366 | 91.836 | 97.8243
NorwoodWind2100RCP8.5 | Norwood | Wind | RCP8.5 | 2100 | 74.1481 | 79.844 | 85.8366 | 91.836 | 97.8243
OakvilleIce Accretion2023RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
OakvilleIce Accretion2025RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
OakvilleIce Accretion2030RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
OakvilleIce Accretion2035RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
OakvilleIce Accretion2040RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
OakvilleIce Accretion2045RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
OakvilleIce Accretion2050RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
OakvilleIce Accretion2055RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
OakvilleIce Accretion2060RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
OakvilleIce Accretion2065RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
OakvilleIce Accretion2070RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
OakvilleIce Accretion2075RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2075 | 15.5377 | 18.8894 | 23.1125 | 26.329 | 29.5313
OakvilleIce Accretion2080RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2080 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
OakvilleIce Accretion2085RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2085 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
OakvilleIce Accretion2090RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2090 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
OakvilleIce Accretion2095RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2095 | 15.3405 | 18.7511 | 23.0625 | 26.329 | 29.5942
OakvilleIce Accretion2100RCP4.5 | Oakville | Ice Accretion | RCP4.5 | 2100 | 15.2912 | 18.7165 | 23.05 | 26.329 | 29.61
OakvilleIce Accretion2023RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
OakvilleIce Accretion2025RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
OakvilleIce Accretion2030RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
OakvilleIce Accretion2035RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
OakvilleIce Accretion2040RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
OakvilleIce Accretion2045RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
OakvilleIce Accretion2050RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
OakvilleIce Accretion2055RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
OakvilleIce Accretion2060RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
OakvilleIce Accretion2065RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
OakvilleIce Accretion2070RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
OakvilleIce Accretion2075RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2075 | 15.513 | 18.8721 | 23.1062 | 26.329 | 29.5391
OakvilleIce Accretion2080RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2080 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
OakvilleIce Accretion2085RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2085 | 15.3652 | 18.7684 | 23.0688 | 26.329 | 29.5864
OakvilleIce Accretion2090RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2090 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
OakvilleIce Accretion2095RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2095 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
OakvilleIce Accretion2100RCP6.0 | Oakville | Ice Accretion | RCP6.0 | 2100 | 14.2127 | 17.596 | 21.825 | 25.0577 | 28.2555
OakvilleIce Accretion2023RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
OakvilleIce Accretion2025RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2025 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
OakvilleIce Accretion2030RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2030 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
OakvilleIce Accretion2035RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2035 | 16.6133 | 20.0652 | 24.425 | 27.7415 | 31.059
OakvilleIce Accretion2040RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2040 | 16.2712 | 19.6848 | 23.9917 | 27.2707 | 30.5445
OakvilleIce Accretion2045RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2045 | 15.9291 | 19.3044 | 23.5583 | 26.7998 | 30.03
OakvilleIce Accretion2050RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2050 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
OakvilleIce Accretion2055RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2055 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
OakvilleIce Accretion2060RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2060 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
OakvilleIce Accretion2065RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2065 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
OakvilleIce Accretion2070RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2070 | 13.8125 | 17.1464 | 21.325 | 24.5022 | 27.657
OakvilleIce Accretion2075RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2075 | 13.4124 | 16.6968 | 20.825 | 23.9466 | 27.0585
OakvilleIce Accretion2080RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2080 | 13.0123 | 16.2473 | 20.325 | 23.391 | 26.46
OakvilleIce Accretion2085RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2085 | 12.1338 | 15.1994 | 19.0625 | 21.9785 | 24.885
OakvilleIce Accretion2090RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2090 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
OakvilleIce Accretion2095RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2095 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
OakvilleIce Accretion2100RCP8.5 | Oakville | Ice Accretion | RCP8.5 | 2100 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
OakvilleWind2023RCP4.5 | Oakville | Wind | RCP4.5 | 2023 | 85.9036 | 92.5764 | 99.6138 | 106.6397 | 113.6613
OakvilleWind2025RCP4.5 | Oakville | Wind | RCP4.5 | 2025 | 85.935 | 92.6224 | 99.6798 | 106.7227 | 113.761
OakvilleWind2030RCP4.5 | Oakville | Wind | RCP4.5 | 2030 | 85.9663 | 92.6685 | 99.7458 | 106.8057 | 113.8607
OakvilleWind2035RCP4.5 | Oakville | Wind | RCP4.5 | 2035 | 85.9977 | 92.7145 | 99.8118 | 106.8887 | 113.9604
OakvilleWind2040RCP4.5 | Oakville | Wind | RCP4.5 | 2040 | 86.029 | 92.7605 | 99.8778 | 106.9716 | 114.0601
OakvilleWind2045RCP4.5 | Oakville | Wind | RCP4.5 | 2045 | 86.0604 | 92.8066 | 99.9438 | 107.0546 | 114.1598
OakvilleWind2050RCP4.5 | Oakville | Wind | RCP4.5 | 2050 | 86.1601 | 92.9355 | 100.1108 | 107.2541 | 114.3926
OakvilleWind2055RCP4.5 | Oakville | Wind | RCP4.5 | 2055 | 86.2285 | 93.0183 | 100.2118 | 107.3706 | 114.5258
OakvilleWind2060RCP4.5 | Oakville | Wind | RCP4.5 | 2060 | 86.2969 | 93.1012 | 100.3127 | 107.4872 | 114.659
OakvilleWind2065RCP4.5 | Oakville | Wind | RCP4.5 | 2065 | 86.3653 | 93.184 | 100.4137 | 107.6037 | 114.7922
OakvilleWind2070RCP4.5 | Oakville | Wind | RCP4.5 | 2070 | 86.4336 | 93.2669 | 100.5147 | 107.7202 | 114.9253
OakvilleWind2075RCP4.5 | Oakville | Wind | RCP4.5 | 2075 | 86.5277 | 93.3989 | 100.6946 | 107.9391 | 115.1849
OakvilleWind2080RCP4.5 | Oakville | Wind | RCP4.5 | 2080 | 86.6217 | 93.5308 | 100.8744 | 108.1581 | 115.4445
OakvilleWind2085RCP4.5 | Oakville | Wind | RCP4.5 | 2085 | 86.7157 | 93.6628 | 101.0542 | 108.377 | 115.7041
OakvilleWind2090RCP4.5 | Oakville | Wind | RCP4.5 | 2090 | 86.8098 | 93.7948 | 101.2341 | 108.5959 | 115.9636
OakvilleWind2095RCP4.5 | Oakville | Wind | RCP4.5 | 2095 | 86.9038 | 93.9267 | 101.4139 | 108.8148 | 116.2232
OakvilleWind2100RCP4.5 | Oakville | Wind | RCP4.5 | 2100 | 86.9978 | 94.0587 | 101.5938 | 109.0337 | 116.4828
OakvilleWind2023RCP6.0 | Oakville | Wind | RCP6.0 | 2023 | 85.9036 | 92.5764 | 99.6138 | 106.6397 | 113.6613
OakvilleWind2025RCP6.0 | Oakville | Wind | RCP6.0 | 2025 | 85.935 | 92.6224 | 99.6798 | 106.7227 | 113.761
OakvilleWind2030RCP6.0 | Oakville | Wind | RCP6.0 | 2030 | 85.9663 | 92.6685 | 99.7458 | 106.8057 | 113.8607
OakvilleWind2035RCP6.0 | Oakville | Wind | RCP6.0 | 2035 | 85.9977 | 92.7145 | 99.8118 | 106.8887 | 113.9604
OakvilleWind2040RCP6.0 | Oakville | Wind | RCP6.0 | 2040 | 86.029 | 92.7605 | 99.8778 | 106.9716 | 114.0601
OakvilleWind2045RCP6.0 | Oakville | Wind | RCP6.0 | 2045 | 86.0604 | 92.8066 | 99.9438 | 107.0546 | 114.1598
OakvilleWind2050RCP6.0 | Oakville | Wind | RCP6.0 | 2050 | 86.1601 | 92.9355 | 100.1108 | 107.2541 | 114.3926
OakvilleWind2055RCP6.0 | Oakville | Wind | RCP6.0 | 2055 | 86.2285 | 93.0183 | 100.2118 | 107.3706 | 114.5258
OakvilleWind2060RCP6.0 | Oakville | Wind | RCP6.0 | 2060 | 86.2969 | 93.1012 | 100.3127 | 107.4872 | 114.659
OakvilleWind2065RCP6.0 | Oakville | Wind | RCP6.0 | 2065 | 86.3653 | 93.184 | 100.4137 | 107.6037 | 114.7922
OakvilleWind2070RCP6.0 | Oakville | Wind | RCP6.0 | 2070 | 86.4336 | 93.2669 | 100.5147 | 107.7202 | 114.9253
OakvilleWind2075RCP6.0 | Oakville | Wind | RCP6.0 | 2075 | 86.5747 | 93.4649 | 100.7845 | 108.0486 | 115.3147
OakvilleWind2080RCP6.0 | Oakville | Wind | RCP6.0 | 2080 | 86.7157 | 93.6628 | 101.0542 | 108.377 | 115.7041
OakvilleWind2085RCP6.0 | Oakville | Wind | RCP6.0 | 2085 | 86.8568 | 93.8608 | 101.324 | 108.7054 | 116.0934
OakvilleWind2090RCP6.0 | Oakville | Wind | RCP6.0 | 2090 | 87.2942 | 94.4393 | 102.0789 | 109.6093 | 117.1524
OakvilleWind2095RCP6.0 | Oakville | Wind | RCP6.0 | 2095 | 87.5905 | 94.8198 | 102.564 | 110.1849 | 117.8221
OakvilleWind2100RCP6.0 | Oakville | Wind | RCP6.0 | 2100 | 87.8869 | 95.2004 | 103.0491 | 110.7604 | 118.4917
OakvilleWind2023RCP8.5 | Oakville | Wind | RCP8.5 | 2023 | 85.9036 | 92.5764 | 99.6138 | 106.6397 | 113.6613
OakvilleWind2025RCP8.5 | Oakville | Wind | RCP8.5 | 2025 | 85.9663 | 92.6685 | 99.7458 | 106.8057 | 113.8607
OakvilleWind2030RCP8.5 | Oakville | Wind | RCP8.5 | 2030 | 86.029 | 92.7605 | 99.8778 | 106.9716 | 114.0601
OakvilleWind2035RCP8.5 | Oakville | Wind | RCP8.5 | 2035 | 86.0917 | 92.8526 | 100.0098 | 107.1376 | 114.2595
OakvilleWind2040RCP8.5 | Oakville | Wind | RCP8.5 | 2040 | 86.2057 | 92.9907 | 100.1781 | 107.3318 | 114.4814
OakvilleWind2045RCP8.5 | Oakville | Wind | RCP8.5 | 2045 | 86.3197 | 93.1288 | 100.3464 | 107.526 | 114.7034
OakvilleWind2050RCP8.5 | Oakville | Wind | RCP8.5 | 2050 | 86.6217 | 93.5308 | 100.8744 | 108.1581 | 115.4445
OakvilleWind2055RCP8.5 | Oakville | Wind | RCP8.5 | 2055 | 86.8098 | 93.7948 | 101.2341 | 108.5959 | 115.9636
OakvilleWind2060RCP8.5 | Oakville | Wind | RCP8.5 | 2060 | 87.2942 | 94.4393 | 102.0789 | 109.6093 | 117.1524
OakvilleWind2065RCP8.5 | Oakville | Wind | RCP8.5 | 2065 | 87.5905 | 94.8198 | 102.564 | 110.1849 | 117.8221
OakvilleWind2070RCP8.5 | Oakville | Wind | RCP8.5 | 2070 | 88.055 | 95.4428 | 103.3857 | 111.1735 | 118.9845
OakvilleWind2075RCP8.5 | Oakville | Wind | RCP8.5 | 2075 | 88.2231 | 95.6853 | 103.7223 | 111.5867 | 119.4774
OakvilleWind2080RCP8.5 | Oakville | Wind | RCP8.5 | 2080 | 88.3912 | 95.9277 | 104.0589 | 111.9998 | 119.9702
OakvilleWind2085RCP8.5 | Oakville | Wind | RCP8.5 | 2085 | 88.6605 | 96.2776 | 104.5093 | 112.54 | 120.6022
OakvilleWind2090RCP8.5 | Oakville | Wind | RCP8.5 | 2090 | 88.9298 | 96.6275 | 104.9598 | 113.0803 | 121.2342
OakvilleWind2095RCP8.5 | Oakville | Wind | RCP8.5 | 2095 | 88.9298 | 96.6275 | 104.9598 | 113.0803 | 121.2342
OakvilleWind2100RCP8.5 | Oakville | Wind | RCP8.5 | 2100 | 88.9298 | 96.6275 | 104.9598 | 113.0803 | 121.2342
OrangevilleIce Accretion2023RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2023 | 16.8005 | 20.159 | 24.432 | 27.6895 | 30.9355
OrangevilleIce Accretion2025RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2025 | 16.8228 | 20.1989 | 24.492 | 27.7664 | 31.0262
OrangevilleIce Accretion2030RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2030 | 16.845 | 20.2387 | 24.552 | 27.8432 | 31.117
OrangevilleIce Accretion2035RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2035 | 16.8673 | 20.2786 | 24.612 | 27.92 | 31.2077
OrangevilleIce Accretion2040RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2040 | 16.8896 | 20.3184 | 24.672 | 27.9969 | 31.2984
OrangevilleIce Accretion2045RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2045 | 16.9118 | 20.3582 | 24.732 | 28.0737 | 31.3891
OrangevilleIce Accretion2050RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2050 | 16.8974 | 20.3702 | 24.7776 | 28.1451 | 31.4919
OrangevilleIce Accretion2055RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2055 | 16.8606 | 20.3423 | 24.7632 | 28.1397 | 31.504
OrangevilleIce Accretion2060RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2060 | 16.8239 | 20.3144 | 24.7488 | 28.1343 | 31.5161
OrangevilleIce Accretion2065RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2065 | 16.7871 | 20.2865 | 24.7344 | 28.1289 | 31.5282
OrangevilleIce Accretion2070RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2070 | 16.7504 | 20.2586 | 24.72 | 28.1234 | 31.5403
OrangevilleIce Accretion2075RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2075 | 16.7281 | 20.262 | 24.752 | 28.1777 | 31.6159
OrangevilleIce Accretion2080RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2080 | 16.7059 | 20.2653 | 24.784 | 28.2319 | 31.6915
OrangevilleIce Accretion2085RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2085 | 16.6836 | 20.2686 | 24.816 | 28.2862 | 31.7671
OrangevilleIce Accretion2090RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2090 | 16.6613 | 20.2719 | 24.848 | 28.3404 | 31.8427
OrangevilleIce Accretion2095RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2095 | 16.6391 | 20.2752 | 24.88 | 28.3946 | 31.9183
OrangevilleIce Accretion2100RCP4.5 | Orangeville | Ice Accretion | RCP4.5 | 2100 | 16.6168 | 20.2786 | 24.912 | 28.4489 | 31.9939
OrangevilleIce Accretion2023RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2023 | 16.8005 | 20.159 | 24.432 | 27.6895 | 30.9355
OrangevilleIce Accretion2025RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2025 | 16.8228 | 20.1989 | 24.492 | 27.7664 | 31.0262
OrangevilleIce Accretion2030RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2030 | 16.845 | 20.2387 | 24.552 | 27.8432 | 31.117
OrangevilleIce Accretion2035RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2035 | 16.8673 | 20.2786 | 24.612 | 27.92 | 31.2077
OrangevilleIce Accretion2040RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2040 | 16.8896 | 20.3184 | 24.672 | 27.9969 | 31.2984
OrangevilleIce Accretion2045RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2045 | 16.9118 | 20.3582 | 24.732 | 28.0737 | 31.3891
OrangevilleIce Accretion2050RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2050 | 16.8974 | 20.3702 | 24.7776 | 28.1451 | 31.4919
OrangevilleIce Accretion2055RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2055 | 16.8606 | 20.3423 | 24.7632 | 28.1397 | 31.504
OrangevilleIce Accretion2060RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2060 | 16.8239 | 20.3144 | 24.7488 | 28.1343 | 31.5161
OrangevilleIce Accretion2065RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2065 | 16.7871 | 20.2865 | 24.7344 | 28.1289 | 31.5282
OrangevilleIce Accretion2070RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2070 | 16.7504 | 20.2586 | 24.72 | 28.1234 | 31.5403
OrangevilleIce Accretion2075RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2075 | 16.717 | 20.2636 | 24.768 | 28.2048 | 31.6537
OrangevilleIce Accretion2080RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2080 | 16.6836 | 20.2686 | 24.816 | 28.2862 | 31.7671
OrangevilleIce Accretion2085RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2085 | 16.6502 | 20.2736 | 24.864 | 28.3675 | 31.8805
OrangevilleIce Accretion2090RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2090 | 16.3997 | 20.0661 | 24.704 | 28.241 | 31.7722
OrangevilleIce Accretion2095RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2095 | 16.1826 | 19.8536 | 24.496 | 28.033 | 31.5504
OrangevilleIce Accretion2100RCP6.0 | Orangeville | Ice Accretion | RCP6.0 | 2100 | 15.9655 | 19.6411 | 24.288 | 27.8251 | 31.3286
OrangevilleIce Accretion2023RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2023 | 16.8005 | 20.159 | 24.432 | 27.6895 | 30.9355
OrangevilleIce Accretion2025RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2025 | 16.845 | 20.2387 | 24.552 | 27.8432 | 31.117
OrangevilleIce Accretion2030RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2030 | 16.8896 | 20.3184 | 24.672 | 27.9969 | 31.2984
OrangevilleIce Accretion2035RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2035 | 16.9341 | 20.3981 | 24.792 | 28.1506 | 31.4798
OrangevilleIce Accretion2040RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2040 | 16.8729 | 20.3516 | 24.768 | 28.1415 | 31.5
OrangevilleIce Accretion2045RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2045 | 16.8116 | 20.3051 | 24.744 | 28.1325 | 31.5202
OrangevilleIce Accretion2050RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2050 | 16.7059 | 20.2653 | 24.784 | 28.2319 | 31.6915
OrangevilleIce Accretion2055RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2055 | 16.6613 | 20.2719 | 24.848 | 28.3404 | 31.8427
OrangevilleIce Accretion2060RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2060 | 16.3997 | 20.0661 | 24.704 | 28.241 | 31.7722
OrangevilleIce Accretion2065RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2065 | 16.1826 | 19.8536 | 24.496 | 28.033 | 31.5504
OrangevilleIce Accretion2070RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2070 | 15.5758 | 19.2095 | 23.8 | 27.2918 | 30.7642
OrangevilleIce Accretion2075RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2075 | 15.1861 | 18.7779 | 23.312 | 26.7584 | 30.1997
OrangevilleIce Accretion2080RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2080 | 14.7965 | 18.3463 | 22.824 | 26.225 | 29.6352
OrangevilleIce Accretion2085RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2085 | 14.1619 | 17.6292 | 22.008 | 25.3301 | 28.6524
OrangevilleIce Accretion2090RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2090 | 13.5272 | 16.9121 | 21.192 | 24.4351 | 27.6696
OrangevilleIce Accretion2095RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2095 | 13.5272 | 16.9121 | 21.192 | 24.4351 | 27.6696
OrangevilleIce Accretion2100RCP8.5 | Orangeville | Ice Accretion | RCP8.5 | 2100 | 13.5272 | 16.9121 | 21.192 | 24.4351 | 27.6696
OrangevilleWind2023RCP4.5 | Orangeville | Wind | RCP4.5 | 2023 | 79.6946 | 85.8509 | 92.3312 | 98.8042 | 105.2785
OrangevilleWind2025RCP4.5 | Orangeville | Wind | RCP4.5 | 2025 | 79.7025 | 85.8652 | 92.3542 | 98.8338 | 105.317
OrangevilleWind2030RCP4.5 | Orangeville | Wind | RCP4.5 | 2030 | 79.7105 | 85.8794 | 92.3772 | 98.8633 | 105.3555
OrangevilleWind2035RCP4.5 | Orangeville | Wind | RCP4.5 | 2035 | 79.7184 | 85.8937 | 92.4002 | 98.8928 | 105.3939
OrangevilleWind2040RCP4.5 | Orangeville | Wind | RCP4.5 | 2040 | 79.7264 | 85.9079 | 92.4232 | 98.9224 | 105.4324
OrangevilleWind2045RCP4.5 | Orangeville | Wind | RCP4.5 | 2045 | 79.7343 | 85.9222 | 92.4462 | 98.9519 | 105.4708
OrangevilleWind2050RCP4.5 | Orangeville | Wind | RCP4.5 | 2050 | 79.7963 | 85.9946 | 92.5318 | 99.0484 | 105.5806
OrangevilleWind2055RCP4.5 | Orangeville | Wind | RCP4.5 | 2055 | 79.8503 | 86.0528 | 92.5943 | 99.1153 | 105.6519
OrangevilleWind2060RCP4.5 | Orangeville | Wind | RCP4.5 | 2060 | 79.9043 | 86.111 | 92.6569 | 99.1822 | 105.7232
OrangevilleWind2065RCP4.5 | Orangeville | Wind | RCP4.5 | 2065 | 79.9583 | 86.1692 | 92.7194 | 99.2492 | 105.7946
OrangevilleWind2070RCP4.5 | Orangeville | Wind | RCP4.5 | 2070 | 80.0124 | 86.2274 | 92.782 | 99.3161 | 105.8659
OrangevilleWind2075RCP4.5 | Orangeville | Wind | RCP4.5 | 2075 | 80.0799 | 86.3186 | 92.9047 | 99.4671 | 106.0424
OrangevilleWind2080RCP4.5 | Orangeville | Wind | RCP4.5 | 2080 | 80.1474 | 86.4099 | 93.0273 | 99.618 | 106.219
OrangevilleWind2085RCP4.5 | Orangeville | Wind | RCP4.5 | 2085 | 80.2149 | 86.5012 | 93.15 | 99.7689 | 106.3955
OrangevilleWind2090RCP4.5 | Orangeville | Wind | RCP4.5 | 2090 | 80.2825 | 86.5924 | 93.2727 | 99.9199 | 106.5721
OrangevilleWind2095RCP4.5 | Orangeville | Wind | RCP4.5 | 2095 | 80.35 | 86.6837 | 93.3953 | 100.0708 | 106.7486
OrangevilleWind2100RCP4.5 | Orangeville | Wind | RCP4.5 | 2100 | 80.4175 | 86.775 | 93.518 | 100.2218 | 106.9252
OrangevilleWind2023RCP6.0 | Orangeville | Wind | RCP6.0 | 2023 | 79.6946 | 85.8509 | 92.3312 | 98.8042 | 105.2785
OrangevilleWind2025RCP6.0 | Orangeville | Wind | RCP6.0 | 2025 | 79.7025 | 85.8652 | 92.3542 | 98.8338 | 105.317
OrangevilleWind2030RCP6.0 | Orangeville | Wind | RCP6.0 | 2030 | 79.7105 | 85.8794 | 92.3772 | 98.8633 | 105.3555
OrangevilleWind2035RCP6.0 | Orangeville | Wind | RCP6.0 | 2035 | 79.7184 | 85.8937 | 92.4002 | 98.8928 | 105.3939
OrangevilleWind2040RCP6.0 | Orangeville | Wind | RCP6.0 | 2040 | 79.7264 | 85.9079 | 92.4232 | 98.9224 | 105.4324
OrangevilleWind2045RCP6.0 | Orangeville | Wind | RCP6.0 | 2045 | 79.7343 | 85.9222 | 92.4462 | 98.9519 | 105.4708
OrangevilleWind2050RCP6.0 | Orangeville | Wind | RCP6.0 | 2050 | 79.7963 | 85.9946 | 92.5318 | 99.0484 | 105.5806
OrangevilleWind2055RCP6.0 | Orangeville | Wind | RCP6.0 | 2055 | 79.8503 | 86.0528 | 92.5943 | 99.1153 | 105.6519
OrangevilleWind2060RCP6.0 | Orangeville | Wind | RCP6.0 | 2060 | 79.9043 | 86.111 | 92.6569 | 99.1822 | 105.7232
OrangevilleWind2065RCP6.0 | Orangeville | Wind | RCP6.0 | 2065 | 79.9583 | 86.1692 | 92.7194 | 99.2492 | 105.7946
OrangevilleWind2070RCP6.0 | Orangeville | Wind | RCP6.0 | 2070 | 80.0124 | 86.2274 | 92.782 | 99.3161 | 105.8659
OrangevilleWind2075RCP6.0 | Orangeville | Wind | RCP6.0 | 2075 | 80.1136 | 86.3643 | 92.966 | 99.5425 | 106.1307
OrangevilleWind2080RCP6.0 | Orangeville | Wind | RCP6.0 | 2080 | 80.2149 | 86.5012 | 93.15 | 99.7689 | 106.3955
OrangevilleWind2085RCP6.0 | Orangeville | Wind | RCP6.0 | 2085 | 80.3162 | 86.6381 | 93.334 | 99.9954 | 106.6603
OrangevilleWind2090RCP6.0 | Orangeville | Wind | RCP6.0 | 2090 | 80.7962 | 87.2427 | 94.0915 | 100.8879 | 107.6838
OrangevilleWind2095RCP6.0 | Orangeville | Wind | RCP6.0 | 2095 | 81.1748 | 87.7104 | 94.6649 | 101.554 | 108.4424
OrangevilleWind2100RCP6.0 | Orangeville | Wind | RCP6.0 | 2100 | 81.5535 | 88.1781 | 95.2384 | 102.2201 | 109.2011
OrangevilleWind2023RCP8.5 | Orangeville | Wind | RCP8.5 | 2023 | 79.6946 | 85.8509 | 92.3312 | 98.8042 | 105.2785
OrangevilleWind2025RCP8.5 | Orangeville | Wind | RCP8.5 | 2025 | 79.7105 | 85.8794 | 92.3772 | 98.8633 | 105.3555
OrangevilleWind2030RCP8.5 | Orangeville | Wind | RCP8.5 | 2030 | 79.7264 | 85.9079 | 92.4232 | 98.9224 | 105.4324
OrangevilleWind2035RCP8.5 | Orangeville | Wind | RCP8.5 | 2035 | 79.7423 | 85.9365 | 92.4692 | 98.9814 | 105.5093
OrangevilleWind2040RCP8.5 | Orangeville | Wind | RCP8.5 | 2040 | 79.8323 | 86.0334 | 92.5735 | 99.093 | 105.6281
OrangevilleWind2045RCP8.5 | Orangeville | Wind | RCP8.5 | 2045 | 79.9223 | 86.1304 | 92.6777 | 99.2046 | 105.747
OrangevilleWind2050RCP8.5 | Orangeville | Wind | RCP8.5 | 2050 | 80.1474 | 86.4099 | 93.0273 | 99.618 | 106.219
OrangevilleWind2055RCP8.5 | Orangeville | Wind | RCP8.5 | 2055 | 80.2825 | 86.5924 | 93.2727 | 99.9199 | 106.5721
OrangevilleWind2060RCP8.5 | Orangeville | Wind | RCP8.5 | 2060 | 80.7962 | 87.2427 | 94.0915 | 100.8879 | 107.6838
OrangevilleWind2065RCP8.5 | Orangeville | Wind | RCP8.5 | 2065 | 81.1748 | 87.7104 | 94.6649 | 101.554 | 108.4424
OrangevilleWind2070RCP8.5 | Orangeville | Wind | RCP8.5 | 2070 | 81.7627 | 88.4462 | 95.5819 | 102.6204 | 109.666
OrangevilleWind2075RCP8.5 | Orangeville | Wind | RCP8.5 | 2075 | 81.9719 | 88.7143 | 95.9253 | 103.0207 | 110.131
OrangevilleWind2080RCP8.5 | Orangeville | Wind | RCP8.5 | 2080 | 82.1811 | 88.9824 | 96.2688 | 103.4211 | 110.596
OrangevilleWind2085RCP8.5 | Orangeville | Wind | RCP8.5 | 2085 | 82.3558 | 89.1963 | 96.531 | 103.7262 | 110.9473
OrangevilleWind2090RCP8.5 | Orangeville | Wind | RCP8.5 | 2090 | 82.5306 | 89.4102 | 96.7932 | 104.0314 | 111.2987
OrangevilleWind2095RCP8.5 | Orangeville | Wind | RCP8.5 | 2095 | 82.5306 | 89.4102 | 96.7932 | 104.0314 | 111.2987
OrangevilleWind2100RCP8.5 | Orangeville | Wind | RCP8.5 | 2100 | 82.5306 | 89.4102 | 96.7932 | 104.0314 | 111.2987
OrilliaIce Accretion2023RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2023 | 15.0178 | 17.9131 | 21.582 | 24.3877 | 27.221
OrilliaIce Accretion2025RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2025 | 14.9999 | 17.9009 | 21.5747 | 24.3877 | 27.221
OrilliaIce Accretion2030RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2030 | 14.982 | 17.8887 | 21.5673 | 24.3877 | 27.221
OrilliaIce Accretion2035RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2035 | 14.9642 | 17.8765 | 21.56 | 24.3877 | 27.221
OrilliaIce Accretion2040RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2040 | 14.9463 | 17.8644 | 21.5527 | 24.3877 | 27.221
OrilliaIce Accretion2045RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2045 | 14.9285 | 17.8522 | 21.5453 | 24.3877 | 27.221
OrilliaIce Accretion2050RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2050 | 14.9075 | 17.851 | 21.5732 | 24.4324 | 27.282
OrilliaIce Accretion2055RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2055 | 14.9045 | 17.8619 | 21.6084 | 24.4772 | 27.343
OrilliaIce Accretion2060RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2060 | 14.9014 | 17.8729 | 21.6436 | 24.5219 | 27.404
OrilliaIce Accretion2065RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2065 | 14.8983 | 17.8838 | 21.6788 | 24.5667 | 27.465
OrilliaIce Accretion2070RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2070 | 14.8953 | 17.8948 | 21.714 | 24.6114 | 27.526
OrilliaIce Accretion2075RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2075 | 14.9387 | 17.9648 | 21.813 | 24.7316 | 27.6692
OrilliaIce Accretion2080RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2080 | 14.982 | 18.0348 | 21.912 | 24.8517 | 27.8124
OrilliaIce Accretion2085RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2085 | 15.0254 | 18.1048 | 22.011 | 24.9719 | 27.9556
OrilliaIce Accretion2090RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2090 | 15.0688 | 18.1748 | 22.11 | 25.092 | 28.0988
OrilliaIce Accretion2095RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2095 | 15.1122 | 18.2448 | 22.209 | 25.2122 | 28.2421
OrilliaIce Accretion2100RCP4.5 | Orillia | Ice Accretion | RCP4.5 | 2100 | 15.1555 | 18.3148 | 22.308 | 25.3323 | 28.3853
OrilliaIce Accretion2023RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2023 | 15.0178 | 17.9131 | 21.582 | 24.3877 | 27.221
OrilliaIce Accretion2025RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2025 | 14.9999 | 17.9009 | 21.5747 | 24.3877 | 27.221
OrilliaIce Accretion2030RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2030 | 14.982 | 17.8887 | 21.5673 | 24.3877 | 27.221
OrilliaIce Accretion2035RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2035 | 14.9642 | 17.8765 | 21.56 | 24.3877 | 27.221
OrilliaIce Accretion2040RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2040 | 14.9463 | 17.8644 | 21.5527 | 24.3877 | 27.221
OrilliaIce Accretion2045RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2045 | 14.9285 | 17.8522 | 21.5453 | 24.3877 | 27.221
OrilliaIce Accretion2050RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2050 | 14.9075 | 17.851 | 21.5732 | 24.4324 | 27.282
OrilliaIce Accretion2055RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2055 | 14.9045 | 17.8619 | 21.6084 | 24.4772 | 27.343
OrilliaIce Accretion2060RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2060 | 14.9014 | 17.8729 | 21.6436 | 24.5219 | 27.404
OrilliaIce Accretion2065RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2065 | 14.8983 | 17.8838 | 21.6788 | 24.5667 | 27.465
OrilliaIce Accretion2070RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2070 | 14.8953 | 17.8948 | 21.714 | 24.6114 | 27.526
OrilliaIce Accretion2075RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2075 | 14.9603 | 17.9998 | 21.8625 | 24.7916 | 27.7408
OrilliaIce Accretion2080RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2080 | 15.0254 | 18.1048 | 22.011 | 24.9719 | 27.9556
OrilliaIce Accretion2085RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2085 | 15.0905 | 18.2098 | 22.1595 | 25.1521 | 28.1704
OrilliaIce Accretion2090RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2090 | 15.13 | 18.327 | 22.3667 | 25.4318 | 28.5146
OrilliaIce Accretion2095RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2095 | 15.1045 | 18.3391 | 22.4253 | 25.5312 | 28.644
OrilliaIce Accretion2100RCP6.0 | Orillia | Ice Accretion | RCP6.0 | 2100 | 15.079 | 18.3513 | 22.484 | 25.6307 | 28.7734
OrilliaIce Accretion2023RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2023 | 15.0178 | 17.9131 | 21.582 | 24.3877 | 27.221
OrilliaIce Accretion2025RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2025 | 14.982 | 17.8887 | 21.5673 | 24.3877 | 27.221
OrilliaIce Accretion2030RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2030 | 14.9463 | 17.8644 | 21.5527 | 24.3877 | 27.221
OrilliaIce Accretion2035RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2035 | 14.9106 | 17.84 | 21.538 | 24.3877 | 27.221
OrilliaIce Accretion2040RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2040 | 14.9055 | 17.8583 | 21.5967 | 24.4622 | 27.3227
OrilliaIce Accretion2045RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2045 | 14.9004 | 17.8765 | 21.6553 | 24.5368 | 27.4243
OrilliaIce Accretion2050RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2050 | 14.982 | 18.0348 | 21.912 | 24.8517 | 27.8124
OrilliaIce Accretion2055RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2055 | 15.0688 | 18.1748 | 22.11 | 25.092 | 28.0988
OrilliaIce Accretion2060RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2060 | 15.13 | 18.327 | 22.3667 | 25.4318 | 28.5146
OrilliaIce Accretion2065RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2065 | 15.1045 | 18.3391 | 22.4253 | 25.5312 | 28.644
OrilliaIce Accretion2070RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2070 | 14.8034 | 18.0591 | 22.1687 | 25.2909 | 28.413
OrilliaIce Accretion2075RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2075 | 14.5279 | 17.767 | 21.8533 | 24.9512 | 28.0526
OrilliaIce Accretion2080RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2080 | 14.2523 | 17.4748 | 21.538 | 24.6114 | 27.6923
OrilliaIce Accretion2085RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2085 | 13.6782 | 16.8266 | 20.79 | 23.791 | 26.7914
OrilliaIce Accretion2090RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2090 | 13.1042 | 16.1784 | 20.042 | 22.9706 | 25.8905
OrilliaIce Accretion2095RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2095 | 13.1042 | 16.1784 | 20.042 | 22.9706 | 25.8905
OrilliaIce Accretion2100RCP8.5 | Orillia | Ice Accretion | RCP8.5 | 2100 | 13.1042 | 16.1784 | 20.042 | 22.9706 | 25.8905
OrilliaWind2023RCP4.5 | Orillia | Wind | RCP4.5 | 2023 | 76.4728 | 82.3965 | 88.6424 | 94.8756 | 101.1125
OrilliaWind2025RCP4.5 | Orillia | Wind | RCP4.5 | 2025 | 76.5513 | 82.4906 | 88.7539 | 95.0027 | 101.2546
OrilliaWind2030RCP4.5 | Orillia | Wind | RCP4.5 | 2030 | 76.6298 | 82.5847 | 88.8653 | 95.1298 | 101.3968
OrilliaWind2035RCP4.5 | Orillia | Wind | RCP4.5 | 2035 | 76.7083 | 82.6789 | 88.9768 | 95.257 | 101.5389
OrilliaWind2040RCP4.5 | Orillia | Wind | RCP4.5 | 2040 | 76.7868 | 82.773 | 89.0883 | 95.3841 | 101.681
OrilliaWind2045RCP4.5 | Orillia | Wind | RCP4.5 | 2045 | 76.8654 | 82.8671 | 89.1997 | 95.5112 | 101.8231
OrilliaWind2050RCP4.5 | Orillia | Wind | RCP4.5 | 2050 | 77.0533 | 83.0922 | 89.4696 | 95.821 | 102.1739
OrilliaWind2055RCP4.5 | Orillia | Wind | RCP4.5 | 2055 | 77.1627 | 83.2231 | 89.628 | 96.0037 | 102.3826
OrilliaWind2060RCP4.5 | Orillia | Wind | RCP4.5 | 2060 | 77.2721 | 83.354 | 89.7864 | 96.1863 | 102.5912
OrilliaWind2065RCP4.5 | Orillia | Wind | RCP4.5 | 2065 | 77.3816 | 83.485 | 89.9448 | 96.369 | 102.7999
OrilliaWind2070RCP4.5 | Orillia | Wind | RCP4.5 | 2070 | 77.491 | 83.6159 | 90.1032 | 96.5517 | 103.0086
OrilliaWind2075RCP4.5 | Orillia | Wind | RCP4.5 | 2075 | 77.5252 | 83.665 | 90.1721 | 96.6364 | 103.1089
OrilliaWind2080RCP4.5 | Orillia | Wind | RCP4.5 | 2080 | 77.5594 | 83.7141 | 90.2411 | 96.7212 | 103.2092
OrilliaWind2085RCP4.5 | Orillia | Wind | RCP4.5 | 2085 | 77.5936 | 83.7632 | 90.31 | 96.8059 | 103.3095
OrilliaWind2090RCP4.5 | Orillia | Wind | RCP4.5 | 2090 | 77.6278 | 83.8123 | 90.3789 | 96.8906 | 103.4099
OrilliaWind2095RCP4.5 | Orillia | Wind | RCP4.5 | 2095 | 77.662 | 83.8614 | 90.4479 | 96.9754 | 103.5102
OrilliaWind2100RCP4.5 | Orillia | Wind | RCP4.5 | 2100 | 77.6961 | 83.9106 | 90.5168 | 97.0601 | 103.6105
OrilliaWind2023RCP6.0 | Orillia | Wind | RCP6.0 | 2023 | 76.4728 | 82.3965 | 88.6424 | 94.8756 | 101.1125
OrilliaWind2025RCP6.0 | Orillia | Wind | RCP6.0 | 2025 | 76.5513 | 82.4906 | 88.7539 | 95.0027 | 101.2546
OrilliaWind2030RCP6.0 | Orillia | Wind | RCP6.0 | 2030 | 76.6298 | 82.5847 | 88.8653 | 95.1298 | 101.3968
OrilliaWind2035RCP6.0 | Orillia | Wind | RCP6.0 | 2035 | 76.7083 | 82.6789 | 88.9768 | 95.257 | 101.5389
OrilliaWind2040RCP6.0 | Orillia | Wind | RCP6.0 | 2040 | 76.7868 | 82.773 | 89.0883 | 95.3841 | 101.681
OrilliaWind2045RCP6.0 | Orillia | Wind | RCP6.0 | 2045 | 76.8654 | 82.8671 | 89.1997 | 95.5112 | 101.8231
OrilliaWind2050RCP6.0 | Orillia | Wind | RCP6.0 | 2050 | 77.0533 | 83.0922 | 89.4696 | 95.821 | 102.1739
OrilliaWind2055RCP6.0 | Orillia | Wind | RCP6.0 | 2055 | 77.1627 | 83.2231 | 89.628 | 96.0037 | 102.3826
OrilliaWind2060RCP6.0 | Orillia | Wind | RCP6.0 | 2060 | 77.2721 | 83.354 | 89.7864 | 96.1863 | 102.5912
OrilliaWind2065RCP6.0 | Orillia | Wind | RCP6.0 | 2065 | 77.3816 | 83.485 | 89.9448 | 96.369 | 102.7999
OrilliaWind2070RCP6.0 | Orillia | Wind | RCP6.0 | 2070 | 77.491 | 83.6159 | 90.1032 | 96.5517 | 103.0086
OrilliaWind2075RCP6.0 | Orillia | Wind | RCP6.0 | 2075 | 77.5423 | 83.6896 | 90.2066 | 96.6788 | 103.1591
OrilliaWind2080RCP6.0 | Orillia | Wind | RCP6.0 | 2080 | 77.5936 | 83.7632 | 90.31 | 96.8059 | 103.3095
OrilliaWind2085RCP6.0 | Orillia | Wind | RCP6.0 | 2085 | 77.6449 | 83.8369 | 90.4134 | 96.933 | 103.46
OrilliaWind2090RCP6.0 | Orillia | Wind | RCP6.0 | 2090 | 77.8101 | 84.0633 | 90.7133 | 97.2955 | 103.8847
OrilliaWind2095RCP6.0 | Orillia | Wind | RCP6.0 | 2095 | 77.9241 | 84.2161 | 90.9099 | 97.5309 | 104.1589
OrilliaWind2100RCP6.0 | Orillia | Wind | RCP6.0 | 2100 | 78.0381 | 84.3689 | 91.1064 | 97.7663 | 104.4331
OrilliaWind2023RCP8.5 | Orillia | Wind | RCP8.5 | 2023 | 76.4728 | 82.3965 | 88.6424 | 94.8756 | 101.1125
OrilliaWind2025RCP8.5 | Orillia | Wind | RCP8.5 | 2025 | 76.6298 | 82.5847 | 88.8653 | 95.1298 | 101.3968
OrilliaWind2030RCP8.5 | Orillia | Wind | RCP8.5 | 2030 | 76.7868 | 82.773 | 89.0883 | 95.3841 | 101.681
OrilliaWind2035RCP8.5 | Orillia | Wind | RCP8.5 | 2035 | 76.9439 | 82.9612 | 89.3112 | 95.6383 | 101.9652
OrilliaWind2040RCP8.5 | Orillia | Wind | RCP8.5 | 2040 | 77.1263 | 83.1794 | 89.5752 | 95.9428 | 102.313
OrilliaWind2045RCP8.5 | Orillia | Wind | RCP8.5 | 2045 | 77.3086 | 83.3977 | 89.8392 | 96.2472 | 102.6608
OrilliaWind2050RCP8.5 | Orillia | Wind | RCP8.5 | 2050 | 77.5594 | 83.7141 | 90.2411 | 96.7212 | 103.2092
OrilliaWind2055RCP8.5 | Orillia | Wind | RCP8.5 | 2055 | 77.6278 | 83.8123 | 90.3789 | 96.8906 | 103.4099
OrilliaWind2060RCP8.5 | Orillia | Wind | RCP8.5 | 2060 | 77.8101 | 84.0633 | 90.7133 | 97.2955 | 103.8847
OrilliaWind2065RCP8.5 | Orillia | Wind | RCP8.5 | 2065 | 77.9241 | 84.2161 | 90.9099 | 97.5309 | 104.1589
OrilliaWind2070RCP8.5 | Orillia | Wind | RCP8.5 | 2070 | 78.0254 | 84.3634 | 91.1123 | 97.7789 | 104.4565
OrilliaWind2075RCP8.5 | Orillia | Wind | RCP8.5 | 2075 | 78.0128 | 84.3579 | 91.1181 | 97.7914 | 104.4799
OrilliaWind2080RCP8.5 | Orillia | Wind | RCP8.5 | 2080 | 78.0001 | 84.3525 | 91.124 | 97.804 | 104.5033
OrilliaWind2085RCP8.5 | Orillia | Wind | RCP8.5 | 2085 | 78.0989 | 84.4793 | 91.2912 | 98.0017 | 104.7341
OrilliaWind2090RCP8.5 | Orillia | Wind | RCP8.5 | 2090 | 78.1977 | 84.6062 | 91.4584 | 98.1995 | 104.9648
OrilliaWind2095RCP8.5 | Orillia | Wind | RCP8.5 | 2095 | 78.1977 | 84.6062 | 91.4584 | 98.1995 | 104.9648
OrilliaWind2100RCP8.5 | Orillia | Wind | RCP8.5 | 2100 | 78.1977 | 84.6062 | 91.4584 | 98.1995 | 104.9648
OshawaIce Accretion2023RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
OshawaIce Accretion2025RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
OshawaIce Accretion2030RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
OshawaIce Accretion2035RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
OshawaIce Accretion2040RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
OshawaIce Accretion2045RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
OshawaIce Accretion2050RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
OshawaIce Accretion2055RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
OshawaIce Accretion2060RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
OshawaIce Accretion2065RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
OshawaIce Accretion2070RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
OshawaIce Accretion2075RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
OshawaIce Accretion2080RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
OshawaIce Accretion2085RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
OshawaIce Accretion2090RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
OshawaIce Accretion2095RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
OshawaIce Accretion2100RCP4.5 | Oshawa | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
OshawaIce Accretion2023RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
OshawaIce Accretion2025RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
OshawaIce Accretion2030RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
OshawaIce Accretion2035RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
OshawaIce Accretion2040RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
OshawaIce Accretion2045RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
OshawaIce Accretion2050RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
OshawaIce Accretion2055RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
OshawaIce Accretion2060RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
OshawaIce Accretion2065RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
OshawaIce Accretion2070RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
OshawaIce Accretion2075RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
OshawaIce Accretion2080RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
OshawaIce Accretion2085RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
OshawaIce Accretion2090RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
OshawaIce Accretion2095RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
OshawaIce Accretion2100RCP6.0 | Oshawa | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
OshawaIce Accretion2023RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
OshawaIce Accretion2025RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
OshawaIce Accretion2030RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
OshawaIce Accretion2035RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
OshawaIce Accretion2040RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
OshawaIce Accretion2045RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
OshawaIce Accretion2050RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
OshawaIce Accretion2055RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
OshawaIce Accretion2060RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
OshawaIce Accretion2065RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
OshawaIce Accretion2070RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
OshawaIce Accretion2075RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
OshawaIce Accretion2080RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
OshawaIce Accretion2085RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
OshawaIce Accretion2090RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
OshawaIce Accretion2095RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
OshawaIce Accretion2100RCP8.5 | Oshawa | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
OshawaWind2023RCP4.5 | Oshawa | Wind | RCP4.5 | 2023 | 84.8244 | 91.3223 | 98.1568 | 104.9963 | 111.8317
OshawaWind2025RCP4.5 | Oshawa | Wind | RCP4.5 | 2025 | 84.8399 | 91.3557 | 98.2107 | 105.068 | 111.9211
OshawaWind2030RCP4.5 | Oshawa | Wind | RCP4.5 | 2030 | 84.8554 | 91.3891 | 98.2646 | 105.1396 | 112.0105
OshawaWind2035RCP4.5 | Oshawa | Wind | RCP4.5 | 2035 | 84.8709 | 91.4225 | 98.3185 | 105.2113 | 112.0998
OshawaWind2040RCP4.5 | Oshawa | Wind | RCP4.5 | 2040 | 84.8864 | 91.456 | 98.3724 | 105.2829 | 112.1892
OshawaWind2045RCP4.5 | Oshawa | Wind | RCP4.5 | 2045 | 84.9019 | 91.4894 | 98.4263 | 105.3546 | 112.2786
OshawaWind2050RCP4.5 | Oshawa | Wind | RCP4.5 | 2050 | 85.0004 | 91.6267 | 98.6115 | 105.5793 | 112.5467
OshawaWind2055RCP4.5 | Oshawa | Wind | RCP4.5 | 2055 | 85.0833 | 91.7306 | 98.7428 | 105.7324 | 112.7255
OshawaWind2060RCP4.5 | Oshawa | Wind | RCP4.5 | 2060 | 85.1662 | 91.8345 | 98.8742 | 105.8855 | 112.9042
OshawaWind2065RCP4.5 | Oshawa | Wind | RCP4.5 | 2065 | 85.2492 | 91.9384 | 99.0055 | 106.0386 | 113.083
OshawaWind2070RCP4.5 | Oshawa | Wind | RCP4.5 | 2070 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2617
OshawaWind2075RCP4.5 | Oshawa | Wind | RCP4.5 | 2075 | 85.476 | 92.2276 | 99.3736 | 106.4731 | 113.5876
OshawaWind2080RCP4.5 | Oshawa | Wind | RCP4.5 | 2080 | 85.6198 | 92.4129 | 99.6105 | 106.7545 | 113.9134
OshawaWind2085RCP4.5 | Oshawa | Wind | RCP4.5 | 2085 | 85.7637 | 92.5982 | 99.8473 | 107.0358 | 114.2393
OshawaWind2090RCP4.5 | Oshawa | Wind | RCP4.5 | 2090 | 85.9075 | 92.7836 | 100.0841 | 107.3172 | 114.5651
OshawaWind2095RCP4.5 | Oshawa | Wind | RCP4.5 | 2095 | 86.0514 | 92.9689 | 100.321 | 107.5986 | 114.891
OshawaWind2100RCP4.5 | Oshawa | Wind | RCP4.5 | 2100 | 86.1952 | 93.1542 | 100.5578 | 107.88 | 115.2168
OshawaWind2023RCP6.0 | Oshawa | Wind | RCP6.0 | 2023 | 84.8244 | 91.3223 | 98.1568 | 104.9963 | 111.8317
OshawaWind2025RCP6.0 | Oshawa | Wind | RCP6.0 | 2025 | 84.8399 | 91.3557 | 98.2107 | 105.068 | 111.9211
OshawaWind2030RCP6.0 | Oshawa | Wind | RCP6.0 | 2030 | 84.8554 | 91.3891 | 98.2646 | 105.1396 | 112.0105
OshawaWind2035RCP6.0 | Oshawa | Wind | RCP6.0 | 2035 | 84.8709 | 91.4225 | 98.3185 | 105.2113 | 112.0998
OshawaWind2040RCP6.0 | Oshawa | Wind | RCP6.0 | 2040 | 84.8864 | 91.456 | 98.3724 | 105.2829 | 112.1892
OshawaWind2045RCP6.0 | Oshawa | Wind | RCP6.0 | 2045 | 84.9019 | 91.4894 | 98.4263 | 105.3546 | 112.2786
OshawaWind2050RCP6.0 | Oshawa | Wind | RCP6.0 | 2050 | 85.0004 | 91.6267 | 98.6115 | 105.5793 | 112.5467
OshawaWind2055RCP6.0 | Oshawa | Wind | RCP6.0 | 2055 | 85.0833 | 91.7306 | 98.7428 | 105.7324 | 112.7255
OshawaWind2060RCP6.0 | Oshawa | Wind | RCP6.0 | 2060 | 85.1662 | 91.8345 | 98.8742 | 105.8855 | 112.9042
OshawaWind2065RCP6.0 | Oshawa | Wind | RCP6.0 | 2065 | 85.2492 | 91.9384 | 99.0055 | 106.0386 | 113.083
OshawaWind2070RCP6.0 | Oshawa | Wind | RCP6.0 | 2070 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2617
OshawaWind2075RCP6.0 | Oshawa | Wind | RCP6.0 | 2075 | 85.5479 | 92.3203 | 99.4921 | 106.6138 | 113.7505
OshawaWind2080RCP6.0 | Oshawa | Wind | RCP6.0 | 2080 | 85.7637 | 92.5982 | 99.8473 | 107.0358 | 114.2393
OshawaWind2085RCP6.0 | Oshawa | Wind | RCP6.0 | 2085 | 85.9794 | 92.8762 | 100.2026 | 107.4579 | 114.7281
OshawaWind2090RCP6.0 | Oshawa | Wind | RCP6.0 | 2090 | 86.6409 | 93.701 | 101.234 | 108.6664 | 116.118
OshawaWind2095RCP6.0 | Oshawa | Wind | RCP6.0 | 2095 | 87.0866 | 94.2479 | 101.9102 | 109.4529 | 117.0193
OshawaWind2100RCP6.0 | Oshawa | Wind | RCP6.0 | 2100 | 87.5322 | 94.7947 | 102.5864 | 110.2393 | 117.9205
OshawaWind2023RCP8.5 | Oshawa | Wind | RCP8.5 | 2023 | 84.8244 | 91.3223 | 98.1568 | 104.9963 | 111.8317
OshawaWind2025RCP8.5 | Oshawa | Wind | RCP8.5 | 2025 | 84.8554 | 91.3891 | 98.2646 | 105.1396 | 112.0105
OshawaWind2030RCP8.5 | Oshawa | Wind | RCP8.5 | 2030 | 84.8864 | 91.456 | 98.3724 | 105.2829 | 112.1892
OshawaWind2035RCP8.5 | Oshawa | Wind | RCP8.5 | 2035 | 84.9175 | 91.5228 | 98.4802 | 105.4262 | 112.368
OshawaWind2040RCP8.5 | Oshawa | Wind | RCP8.5 | 2040 | 85.0557 | 91.696 | 98.6991 | 105.6814 | 112.6659
OshawaWind2045RCP8.5 | Oshawa | Wind | RCP8.5 | 2045 | 85.1939 | 91.8691 | 98.9179 | 105.9366 | 112.9638
OshawaWind2050RCP8.5 | Oshawa | Wind | RCP8.5 | 2050 | 85.6198 | 92.4129 | 99.6105 | 106.7545 | 113.9134
OshawaWind2055RCP8.5 | Oshawa | Wind | RCP8.5 | 2055 | 85.9075 | 92.7836 | 100.0841 | 107.3172 | 114.5651
OshawaWind2060RCP8.5 | Oshawa | Wind | RCP8.5 | 2060 | 86.6409 | 93.701 | 101.234 | 108.6664 | 116.118
OshawaWind2065RCP8.5 | Oshawa | Wind | RCP8.5 | 2065 | 87.0866 | 94.2479 | 101.9102 | 109.4529 | 117.0193
OshawaWind2070RCP8.5 | Oshawa | Wind | RCP8.5 | 2070 | 87.6648 | 94.974 | 102.8249 | 110.5329 | 118.2631
OshawaWind2075RCP8.5 | Oshawa | Wind | RCP8.5 | 2075 | 87.7974 | 95.1532 | 103.0633 | 110.8265 | 118.6057
OshawaWind2080RCP8.5 | Oshawa | Wind | RCP8.5 | 2080 | 87.93 | 95.3324 | 103.3018 | 111.1201 | 118.9483
OshawaWind2085RCP8.5 | Oshawa | Wind | RCP8.5 | 2085 | 88.2135 | 95.7335 | 103.8506 | 111.7912 | 119.7471
OshawaWind2090RCP8.5 | Oshawa | Wind | RCP8.5 | 2090 | 88.4969 | 96.1345 | 104.3994 | 112.4624 | 120.5459
OshawaWind2095RCP8.5 | Oshawa | Wind | RCP8.5 | 2095 | 88.4969 | 96.1345 | 104.3994 | 112.4624 | 120.5459
OshawaWind2100RCP8.5 | Oshawa | Wind | RCP8.5 | 2100 | 88.4969 | 96.1345 | 104.3994 | 112.4624 | 120.5459
Ottawa (Barrhaven)Ice Accretion2023RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
Ottawa (Barrhaven)Ice Accretion2025RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
Ottawa (Barrhaven)Ice Accretion2030RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
Ottawa (Barrhaven)Ice Accretion2035RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
Ottawa (Barrhaven)Ice Accretion2040RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
Ottawa (Barrhaven)Ice Accretion2045RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
Ottawa (Barrhaven)Ice Accretion2050RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
Ottawa (Barrhaven)Ice Accretion2055RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
Ottawa (Barrhaven)Ice Accretion2060RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
Ottawa (Barrhaven)Ice Accretion2065RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
Ottawa (Barrhaven)Ice Accretion2070RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
Ottawa (Barrhaven)Ice Accretion2075RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2075 | 20.6423 | 24.7215 | 29.87 | 33.8039 | 37.7496
Ottawa (Barrhaven)Ice Accretion2080RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2080 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
Ottawa (Barrhaven)Ice Accretion2085RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2085 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
Ottawa (Barrhaven)Ice Accretion2090RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2090 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
Ottawa (Barrhaven)Ice Accretion2095RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2095 | 20.9624 | 25.2029 | 30.55 | 34.6401 | 38.7576
Ottawa (Barrhaven)Ice Accretion2100RCP4.5 | Ottawa (Barrhaven) | Ice Accretion | RCP4.5 | 2100 | 21.0424 | 25.3233 | 30.72 | 34.8492 | 39.0096
Ottawa (Barrhaven)Ice Accretion2023RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
Ottawa (Barrhaven)Ice Accretion2025RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
Ottawa (Barrhaven)Ice Accretion2030RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
Ottawa (Barrhaven)Ice Accretion2035RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
Ottawa (Barrhaven)Ice Accretion2040RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
Ottawa (Barrhaven)Ice Accretion2045RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
Ottawa (Barrhaven)Ice Accretion2050RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
Ottawa (Barrhaven)Ice Accretion2055RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
Ottawa (Barrhaven)Ice Accretion2060RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
Ottawa (Barrhaven)Ice Accretion2065RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
Ottawa (Barrhaven)Ice Accretion2070RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
Ottawa (Barrhaven)Ice Accretion2075RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2075 | 20.6823 | 24.7817 | 29.955 | 33.9085 | 37.8756
Ottawa (Barrhaven)Ice Accretion2080RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2080 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
Ottawa (Barrhaven)Ice Accretion2085RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2085 | 20.9224 | 25.1428 | 30.465 | 34.5356 | 38.6316
Ottawa (Barrhaven)Ice Accretion2090RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2090 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
Ottawa (Barrhaven)Ice Accretion2095RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2095 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
Ottawa (Barrhaven)Ice Accretion2100RCP6.0 | Ottawa (Barrhaven) | Ice Accretion | RCP6.0 | 2100 | 21.439 | 25.9458 | 31.65 | 36.0018 | 40.3326
Ottawa (Barrhaven)Ice Accretion2023RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
Ottawa (Barrhaven)Ice Accretion2025RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2025 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
Ottawa (Barrhaven)Ice Accretion2030RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2030 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
Ottawa (Barrhaven)Ice Accretion2035RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2035 | 20.2074 | 24.0285 | 28.86 | 32.5779 | 36.288
Ottawa (Barrhaven)Ice Accretion2040RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2040 | 20.3257 | 24.2194 | 29.14 | 32.9169 | 36.6912
Ottawa (Barrhaven)Ice Accretion2045RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2045 | 20.444 | 24.4103 | 29.42 | 33.2559 | 37.0944
Ottawa (Barrhaven)Ice Accretion2050RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2050 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
Ottawa (Barrhaven)Ice Accretion2055RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2055 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
Ottawa (Barrhaven)Ice Accretion2060RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2060 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
Ottawa (Barrhaven)Ice Accretion2065RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2065 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
Ottawa (Barrhaven)Ice Accretion2070RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2070 | 21.2372 | 25.7383 | 31.44 | 35.7871 | 40.1184
Ottawa (Barrhaven)Ice Accretion2075RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2075 | 21.0354 | 25.5308 | 31.23 | 35.5724 | 39.9042
Ottawa (Barrhaven)Ice Accretion2080RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2080 | 20.8336 | 25.3233 | 31.02 | 35.3577 | 39.69
Ottawa (Barrhaven)Ice Accretion2085RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2085 | 20.0926 | 24.5016 | 30.09 | 34.3237 | 38.5749
Ottawa (Barrhaven)Ice Accretion2090RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2090 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
Ottawa (Barrhaven)Ice Accretion2095RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2095 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
Ottawa (Barrhaven)Ice Accretion2100RCP8.5 | Ottawa (Barrhaven) | Ice Accretion | RCP8.5 | 2100 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
Ottawa (Barrhaven)Wind2023RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2023 | 77.8688 | 83.9427 | 90.351 | 96.743 | 103.1335
Ottawa (Barrhaven)Wind2025RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2025 | 77.8986 | 83.9776 | 90.3915 | 96.7895 | 103.1848
Ottawa (Barrhaven)Wind2030RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2030 | 77.9284 | 84.0125 | 90.432 | 96.8361 | 103.2361
Ottawa (Barrhaven)Wind2035RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2035 | 77.9582 | 84.0474 | 90.4725 | 96.8826 | 103.2874
Ottawa (Barrhaven)Wind2040RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2040 | 77.988 | 84.0822 | 90.513 | 96.9292 | 103.3387
Ottawa (Barrhaven)Wind2045RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2045 | 78.0178 | 84.1171 | 90.5535 | 96.9757 | 103.39
Ottawa (Barrhaven)Wind2050RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2050 | 77.9745 | 84.0515 | 90.4626 | 96.8624 | 103.2546
Ottawa (Barrhaven)Wind2055RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2055 | 77.9015 | 83.9511 | 90.3312 | 96.7025 | 103.0679
Ottawa (Barrhaven)Wind2060RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2060 | 77.8284 | 83.8507 | 90.1998 | 96.5427 | 102.8811
Ottawa (Barrhaven)Wind2065RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2065 | 77.7554 | 83.7502 | 90.0684 | 96.3828 | 102.6944
Ottawa (Barrhaven)Wind2070RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2070 | 77.6823 | 83.6498 | 89.937 | 96.223 | 102.5077
Ottawa (Barrhaven)Wind2075RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2075 | 77.7018 | 83.6819 | 89.9835 | 96.2823 | 102.5812
Ottawa (Barrhaven)Wind2080RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2080 | 77.7212 | 83.7139 | 90.03 | 96.3417 | 102.6547
Ottawa (Barrhaven)Wind2085RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2085 | 77.7406 | 83.746 | 90.0765 | 96.4011 | 102.7283
Ottawa (Barrhaven)Wind2090RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2090 | 77.76 | 83.7781 | 90.123 | 96.4605 | 102.8018
Ottawa (Barrhaven)Wind2095RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2095 | 77.7795 | 83.8102 | 90.1695 | 96.5199 | 102.8753
Ottawa (Barrhaven)Wind2100RCP4.5 | Ottawa (Barrhaven) | Wind | RCP4.5 | 2100 | 77.7989 | 83.8423 | 90.216 | 96.5793 | 102.9488
Ottawa (Barrhaven)Wind2023RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2023 | 77.8688 | 83.9427 | 90.351 | 96.743 | 103.1335
Ottawa (Barrhaven)Wind2025RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2025 | 77.8986 | 83.9776 | 90.3915 | 96.7895 | 103.1848
Ottawa (Barrhaven)Wind2030RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2030 | 77.9284 | 84.0125 | 90.432 | 96.8361 | 103.2361
Ottawa (Barrhaven)Wind2035RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2035 | 77.9582 | 84.0474 | 90.4725 | 96.8826 | 103.2874
Ottawa (Barrhaven)Wind2040RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2040 | 77.988 | 84.0822 | 90.513 | 96.9292 | 103.3387
Ottawa (Barrhaven)Wind2045RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2045 | 78.0178 | 84.1171 | 90.5535 | 96.9757 | 103.39
Ottawa (Barrhaven)Wind2050RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2050 | 77.9745 | 84.0515 | 90.4626 | 96.8624 | 103.2546
Ottawa (Barrhaven)Wind2055RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2055 | 77.9015 | 83.9511 | 90.3312 | 96.7025 | 103.0679
Ottawa (Barrhaven)Wind2060RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2060 | 77.8284 | 83.8507 | 90.1998 | 96.5427 | 102.8811
Ottawa (Barrhaven)Wind2065RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2065 | 77.7554 | 83.7502 | 90.0684 | 96.3828 | 102.6944
Ottawa (Barrhaven)Wind2070RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2070 | 77.6823 | 83.6498 | 89.937 | 96.223 | 102.5077
Ottawa (Barrhaven)Wind2075RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2075 | 77.7115 | 83.6979 | 90.0067 | 96.312 | 102.618
Ottawa (Barrhaven)Wind2080RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2080 | 77.7406 | 83.746 | 90.0765 | 96.4011 | 102.7283
Ottawa (Barrhaven)Wind2085RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2085 | 77.7698 | 83.7942 | 90.1462 | 96.4902 | 102.8385
Ottawa (Barrhaven)Wind2090RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2090 | 77.6797 | 83.6916 | 90.03 | 96.361 | 102.6958
Ottawa (Barrhaven)Wind2095RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2095 | 77.5606 | 83.541 | 89.844 | 96.1427 | 102.4427
Ottawa (Barrhaven)Wind2100RCP6.0 | Ottawa (Barrhaven) | Wind | RCP6.0 | 2100 | 77.4414 | 83.3903 | 89.658 | 95.9244 | 102.1896
Ottawa (Barrhaven)Wind2023RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2023 | 77.8688 | 83.9427 | 90.351 | 96.743 | 103.1335
Ottawa (Barrhaven)Wind2025RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2025 | 77.9284 | 84.0125 | 90.432 | 96.8361 | 103.2361
Ottawa (Barrhaven)Wind2030RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2030 | 77.988 | 84.0822 | 90.513 | 96.9292 | 103.3387
Ottawa (Barrhaven)Wind2035RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2035 | 78.0476 | 84.152 | 90.594 | 97.0223 | 103.4413
Ottawa (Barrhaven)Wind2040RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2040 | 77.9258 | 83.9846 | 90.375 | 96.7558 | 103.1301
Ottawa (Barrhaven)Wind2045RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2045 | 77.8041 | 83.8172 | 90.156 | 96.4894 | 102.8189
Ottawa (Barrhaven)Wind2050RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2050 | 77.7212 | 83.7139 | 90.03 | 96.3417 | 102.6547
Ottawa (Barrhaven)Wind2055RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2055 | 77.76 | 83.7781 | 90.123 | 96.4605 | 102.8018
Ottawa (Barrhaven)Wind2060RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2060 | 77.6797 | 83.6916 | 90.03 | 96.361 | 102.6958
Ottawa (Barrhaven)Wind2065RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2065 | 77.5606 | 83.541 | 89.844 | 96.1427 | 102.4427
Ottawa (Barrhaven)Wind2070RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2070 | 77.5165 | 83.4908 | 89.784 | 96.0721 | 102.364
Ottawa (Barrhaven)Wind2075RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2075 | 77.5917 | 83.5912 | 89.91 | 96.2198 | 102.5384
Ottawa (Barrhaven)Wind2080RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2080 | 77.6668 | 83.6916 | 90.036 | 96.3674 | 102.7129
Ottawa (Barrhaven)Wind2085RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2085 | 77.6435 | 83.6498 | 89.9775 | 96.2952 | 102.6205
Ottawa (Barrhaven)Wind2090RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2090 | 77.6202 | 83.6079 | 89.919 | 96.223 | 102.5282
Ottawa (Barrhaven)Wind2095RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2095 | 77.6202 | 83.6079 | 89.919 | 96.223 | 102.5282
Ottawa (Barrhaven)Wind2100RCP8.5 | Ottawa (Barrhaven) | Wind | RCP8.5 | 2100 | 77.6202 | 83.6079 | 89.919 | 96.223 | 102.5282
Ottawa (Kanata)Ice Accretion2023RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2023 | 19.2694 | 22.8914 | 27.496 | 31.0072 | 34.5391
Ottawa (Kanata)Ice Accretion2025RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2025 | 19.2661 | 22.8837 | 27.482 | 30.9914 | 34.5156
Ottawa (Kanata)Ice Accretion2030RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2030 | 19.2629 | 22.8759 | 27.468 | 30.9756 | 34.4921
Ottawa (Kanata)Ice Accretion2035RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2035 | 19.2596 | 22.8682 | 27.454 | 30.9597 | 34.4686
Ottawa (Kanata)Ice Accretion2040RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2040 | 19.2564 | 22.8604 | 27.44 | 30.9439 | 34.445
Ottawa (Kanata)Ice Accretion2045RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2045 | 19.2531 | 22.8527 | 27.426 | 30.9281 | 34.4215
Ottawa (Kanata)Ice Accretion2050RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2050 | 19.2616 | 22.8775 | 27.4736 | 30.9945 | 34.4968
Ottawa (Kanata)Ice Accretion2055RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2055 | 19.2733 | 22.91 | 27.5352 | 31.0768 | 34.5956
Ottawa (Kanata)Ice Accretion2060RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2060 | 19.285 | 22.9425 | 27.5968 | 31.1591 | 34.6944
Ottawa (Kanata)Ice Accretion2065RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2065 | 19.2966 | 22.9751 | 27.6584 | 31.2413 | 34.7931
Ottawa (Kanata)Ice Accretion2070RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2070 | 19.3083 | 23.0076 | 27.72 | 31.3236 | 34.8919
Ottawa (Kanata)Ice Accretion2075RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2075 | 19.3798 | 23.1199 | 27.8787 | 31.5187 | 35.1271
Ottawa (Kanata)Ice Accretion2080RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2080 | 19.4512 | 23.2323 | 28.0373 | 31.7138 | 35.3623
Ottawa (Kanata)Ice Accretion2085RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2085 | 19.5227 | 23.3446 | 28.196 | 31.9089 | 35.5975
Ottawa (Kanata)Ice Accretion2090RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2090 | 19.5941 | 23.4569 | 28.3547 | 32.1041 | 35.8327
Ottawa (Kanata)Ice Accretion2095RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2095 | 19.6655 | 23.5692 | 28.5133 | 32.2992 | 36.0679
Ottawa (Kanata)Ice Accretion2100RCP4.5 | Ottawa (Kanata) | Ice Accretion | RCP4.5 | 2100 | 19.737 | 23.6816 | 28.672 | 32.4943 | 36.3031
Ottawa (Kanata)Ice Accretion2023RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2023 | 19.2694 | 22.8914 | 27.496 | 31.0072 | 34.5391
Ottawa (Kanata)Ice Accretion2025RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2025 | 19.2661 | 22.8837 | 27.482 | 30.9914 | 34.5156
Ottawa (Kanata)Ice Accretion2030RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2030 | 19.2629 | 22.8759 | 27.468 | 30.9756 | 34.4921
Ottawa (Kanata)Ice Accretion2035RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2035 | 19.2596 | 22.8682 | 27.454 | 30.9597 | 34.4686
Ottawa (Kanata)Ice Accretion2040RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2040 | 19.2564 | 22.8604 | 27.44 | 30.9439 | 34.445
Ottawa (Kanata)Ice Accretion2045RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2045 | 19.2531 | 22.8527 | 27.426 | 30.9281 | 34.4215
Ottawa (Kanata)Ice Accretion2050RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2050 | 19.2616 | 22.8775 | 27.4736 | 30.9945 | 34.4968
Ottawa (Kanata)Ice Accretion2055RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2055 | 19.2733 | 22.91 | 27.5352 | 31.0768 | 34.5956
Ottawa (Kanata)Ice Accretion2060RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2060 | 19.285 | 22.9425 | 27.5968 | 31.1591 | 34.6944
Ottawa (Kanata)Ice Accretion2065RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2065 | 19.2966 | 22.9751 | 27.6584 | 31.2413 | 34.7931
Ottawa (Kanata)Ice Accretion2070RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2070 | 19.3083 | 23.0076 | 27.72 | 31.3236 | 34.8919
Ottawa (Kanata)Ice Accretion2075RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2075 | 19.4155 | 23.1761 | 27.958 | 31.6163 | 35.2447
Ottawa (Kanata)Ice Accretion2080RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2080 | 19.5227 | 23.3446 | 28.196 | 31.9089 | 35.5975
Ottawa (Kanata)Ice Accretion2085RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2085 | 19.6298 | 23.5131 | 28.434 | 32.2016 | 35.9503
Ottawa (Kanata)Ice Accretion2090RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2090 | 19.7435 | 23.7358 | 28.7933 | 32.6525 | 36.503
Ottawa (Kanata)Ice Accretion2095RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2095 | 19.75 | 23.79 | 28.9147 | 32.8107 | 36.703
Ottawa (Kanata)Ice Accretion2100RCP6.0 | Ottawa (Kanata) | Ice Accretion | RCP6.0 | 2100 | 19.7565 | 23.8442 | 29.036 | 32.9689 | 36.9029
Ottawa (Kanata)Ice Accretion2023RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2023 | 19.2694 | 22.8914 | 27.496 | 31.0072 | 34.5391
Ottawa (Kanata)Ice Accretion2025RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2025 | 19.2629 | 22.8759 | 27.468 | 30.9756 | 34.4921
Ottawa (Kanata)Ice Accretion2030RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2030 | 19.2564 | 22.8604 | 27.44 | 30.9439 | 34.445
Ottawa (Kanata)Ice Accretion2035RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2035 | 19.2499 | 22.8449 | 27.412 | 30.9123 | 34.398
Ottawa (Kanata)Ice Accretion2040RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2040 | 19.2694 | 22.8991 | 27.5147 | 31.0494 | 34.5626
Ottawa (Kanata)Ice Accretion2045RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2045 | 19.2889 | 22.9534 | 27.6173 | 31.1865 | 34.7273
Ottawa (Kanata)Ice Accretion2050RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2050 | 19.4512 | 23.2323 | 28.0373 | 31.7138 | 35.3623
Ottawa (Kanata)Ice Accretion2055RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2055 | 19.5941 | 23.4569 | 28.3547 | 32.1041 | 35.8327
Ottawa (Kanata)Ice Accretion2060RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2060 | 19.7435 | 23.7358 | 28.7933 | 32.6525 | 36.503
Ottawa (Kanata)Ice Accretion2065RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2065 | 19.75 | 23.79 | 28.9147 | 32.8107 | 36.703
Ottawa (Kanata)Ice Accretion2070RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2070 | 19.6525 | 23.759 | 28.9707 | 32.9267 | 36.8794
Ottawa (Kanata)Ice Accretion2075RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2075 | 19.5486 | 23.6738 | 28.9053 | 32.8845 | 36.8558
Ottawa (Kanata)Ice Accretion2080RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2080 | 19.4447 | 23.5886 | 28.84 | 32.8423 | 36.8323
Ottawa (Kanata)Ice Accretion2085RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2085 | 18.831 | 22.8914 | 28.028 | 31.9406 | 35.8445
Ottawa (Kanata)Ice Accretion2090RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2090 | 18.2173 | 22.1942 | 27.216 | 31.0388 | 34.8566
Ottawa (Kanata)Ice Accretion2095RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2095 | 18.2173 | 22.1942 | 27.216 | 31.0388 | 34.8566
Ottawa (Kanata)Ice Accretion2100RCP8.5 | Ottawa (Kanata) | Ice Accretion | RCP8.5 | 2100 | 18.2173 | 22.1942 | 27.216 | 31.0388 | 34.8566
Ottawa (Kanata)Wind2023RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2023 | 78.0554 | 84.1771 | 90.639 | 97.08 | 103.5234
Ottawa (Kanata)Wind2025RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2025 | 78.146 | 84.2929 | 90.7875 | 97.255 | 103.7269
Ottawa (Kanata)Wind2030RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2030 | 78.2367 | 84.4087 | 90.936 | 97.4299 | 103.9304
Ottawa (Kanata)Wind2035RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2035 | 78.3274 | 84.5244 | 91.0845 | 97.6049 | 104.1339
Ottawa (Kanata)Wind2040RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2040 | 78.418 | 84.6402 | 91.233 | 97.7798 | 104.3374
Ottawa (Kanata)Wind2045RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2045 | 78.5087 | 84.756 | 91.3815 | 97.9548 | 104.5408
Ottawa (Kanata)Wind2050RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2050 | 78.5108 | 84.7513 | 91.3698 | 97.9352 | 104.5145
Ottawa (Kanata)Wind2055RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2055 | 78.4222 | 84.6307 | 91.2096 | 97.7406 | 104.2847
Ottawa (Kanata)Wind2060RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2060 | 78.3336 | 84.5102 | 91.0494 | 97.5461 | 104.0549
Ottawa (Kanata)Wind2065RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2065 | 78.245 | 84.3897 | 90.8892 | 97.3516 | 103.825
Ottawa (Kanata)Wind2070RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2070 | 78.1564 | 84.2692 | 90.729 | 97.1571 | 103.5952
Ottawa (Kanata)Wind2075RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2075 | 78.1991 | 84.325 | 90.7995 | 97.2405 | 103.6927
Ottawa (Kanata)Wind2080RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2080 | 78.2419 | 84.3808 | 90.87 | 97.324 | 103.7902
Ottawa (Kanata)Wind2085RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2085 | 78.2846 | 84.4366 | 90.9405 | 97.4075 | 103.8876
Ottawa (Kanata)Wind2090RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2090 | 78.3274 | 84.4924 | 91.011 | 97.4909 | 103.9851
Ottawa (Kanata)Wind2095RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2095 | 78.3701 | 84.5482 | 91.0815 | 97.5744 | 104.0826
Ottawa (Kanata)Wind2100RCP4.5 | Ottawa (Kanata) | Wind | RCP4.5 | 2100 | 78.4128 | 84.604 | 91.152 | 97.6578 | 104.18
Ottawa (Kanata)Wind2023RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2023 | 78.0554 | 84.1771 | 90.639 | 97.08 | 103.5234
Ottawa (Kanata)Wind2025RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2025 | 78.146 | 84.2929 | 90.7875 | 97.255 | 103.7269
Ottawa (Kanata)Wind2030RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2030 | 78.2367 | 84.4087 | 90.936 | 97.4299 | 103.9304
Ottawa (Kanata)Wind2035RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2035 | 78.3274 | 84.5244 | 91.0845 | 97.6049 | 104.1339
Ottawa (Kanata)Wind2040RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2040 | 78.418 | 84.6402 | 91.233 | 97.7798 | 104.3374
Ottawa (Kanata)Wind2045RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2045 | 78.5087 | 84.756 | 91.3815 | 97.9548 | 104.5408
Ottawa (Kanata)Wind2050RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2050 | 78.5108 | 84.7513 | 91.3698 | 97.9352 | 104.5145
Ottawa (Kanata)Wind2055RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2055 | 78.4222 | 84.6307 | 91.2096 | 97.7406 | 104.2847
Ottawa (Kanata)Wind2060RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2060 | 78.3336 | 84.5102 | 91.0494 | 97.5461 | 104.0549
Ottawa (Kanata)Wind2065RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2065 | 78.245 | 84.3897 | 90.8892 | 97.3516 | 103.825
Ottawa (Kanata)Wind2070RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2070 | 78.1564 | 84.2692 | 90.729 | 97.1571 | 103.5952
Ottawa (Kanata)Wind2075RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2075 | 78.2205 | 84.3529 | 90.8347 | 97.2823 | 103.7414
Ottawa (Kanata)Wind2080RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2080 | 78.2846 | 84.4366 | 90.9405 | 97.4075 | 103.8876
Ottawa (Kanata)Wind2085RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2085 | 78.3487 | 84.5203 | 91.0462 | 97.5326 | 104.0338
Ottawa (Kanata)Wind2090RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2090 | 78.2263 | 84.3612 | 90.84 | 97.2919 | 103.7525
Ottawa (Kanata)Wind2095RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2095 | 78.0398 | 84.1185 | 90.528 | 96.926 | 103.325
Ottawa (Kanata)Wind2100RCP6.0 | Ottawa (Kanata) | Wind | RCP6.0 | 2100 | 77.8533 | 83.8758 | 90.216 | 96.56 | 102.8975
Ottawa (Kanata)Wind2023RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2023 | 78.0554 | 84.1771 | 90.639 | 97.08 | 103.5234
Ottawa (Kanata)Wind2025RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2025 | 78.2367 | 84.4087 | 90.936 | 97.4299 | 103.9304
Ottawa (Kanata)Wind2030RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2030 | 78.418 | 84.6402 | 91.233 | 97.7798 | 104.3374
Ottawa (Kanata)Wind2035RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2035 | 78.5994 | 84.8718 | 91.53 | 98.1297 | 104.7443
Ottawa (Kanata)Wind2040RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2040 | 78.4517 | 84.6709 | 91.263 | 97.8055 | 104.3613
Ottawa (Kanata)Wind2045RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2045 | 78.304 | 84.47 | 90.996 | 97.4813 | 103.9783
Ottawa (Kanata)Wind2050RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2050 | 78.2419 | 84.3808 | 90.87 | 97.324 | 103.7902
Ottawa (Kanata)Wind2055RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2055 | 78.3274 | 84.4924 | 91.011 | 97.4909 | 103.9851
Ottawa (Kanata)Wind2060RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2060 | 78.2263 | 84.3612 | 90.84 | 97.2919 | 103.7525
Ottawa (Kanata)Wind2065RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2065 | 78.0398 | 84.1185 | 90.528 | 96.926 | 103.325
Ottawa (Kanata)Wind2070RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2070 | 77.8222 | 83.82 | 90.129 | 96.4445 | 102.7539
Ottawa (Kanata)Wind2075RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2075 | 77.7911 | 83.7642 | 90.042 | 96.3289 | 102.6103
Ottawa (Kanata)Wind2080RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2080 | 77.76 | 83.7084 | 89.955 | 96.2133 | 102.4666
Ottawa (Kanata)Wind2085RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2085 | 77.5463 | 83.4489 | 89.64 | 95.8522 | 102.0562
Ottawa (Kanata)Wind2090RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2090 | 77.3326 | 83.1894 | 89.325 | 95.4911 | 101.6458
Ottawa (Kanata)Wind2095RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2095 | 77.3326 | 83.1894 | 89.325 | 95.4911 | 101.6458
Ottawa (Kanata)Wind2100RCP8.5 | Ottawa (Kanata) | Wind | RCP8.5 | 2100 | 77.3326 | 83.1894 | 89.325 | 95.4911 | 101.6458
Ottawa (M-C Int'l Airport)Ice Accretion2023RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
Ottawa (M-C Int'l Airport)Ice Accretion2025RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
Ottawa (M-C Int'l Airport)Ice Accretion2030RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
Ottawa (M-C Int'l Airport)Ice Accretion2035RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
Ottawa (M-C Int'l Airport)Ice Accretion2040RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
Ottawa (M-C Int'l Airport)Ice Accretion2045RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
Ottawa (M-C Int'l Airport)Ice Accretion2050RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
Ottawa (M-C Int'l Airport)Ice Accretion2055RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
Ottawa (M-C Int'l Airport)Ice Accretion2060RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
Ottawa (M-C Int'l Airport)Ice Accretion2065RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
Ottawa (M-C Int'l Airport)Ice Accretion2070RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
Ottawa (M-C Int'l Airport)Ice Accretion2075RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2075 | 20.6423 | 24.7215 | 29.87 | 33.8039 | 37.7496
Ottawa (M-C Int'l Airport)Ice Accretion2080RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2080 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
Ottawa (M-C Int'l Airport)Ice Accretion2085RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2085 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
Ottawa (M-C Int'l Airport)Ice Accretion2090RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2090 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
Ottawa (M-C Int'l Airport)Ice Accretion2095RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2095 | 20.9624 | 25.2029 | 30.55 | 34.6401 | 38.7576
Ottawa (M-C Int'l Airport)Ice Accretion2100RCP4.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP4.5 | 2100 | 21.0424 | 25.3233 | 30.72 | 34.8492 | 39.0096
Ottawa (M-C Int'l Airport)Ice Accretion2023RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
Ottawa (M-C Int'l Airport)Ice Accretion2025RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
Ottawa (M-C Int'l Airport)Ice Accretion2030RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
Ottawa (M-C Int'l Airport)Ice Accretion2035RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
Ottawa (M-C Int'l Airport)Ice Accretion2040RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
Ottawa (M-C Int'l Airport)Ice Accretion2045RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
Ottawa (M-C Int'l Airport)Ice Accretion2050RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
Ottawa (M-C Int'l Airport)Ice Accretion2055RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
Ottawa (M-C Int'l Airport)Ice Accretion2060RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
Ottawa (M-C Int'l Airport)Ice Accretion2065RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
Ottawa (M-C Int'l Airport)Ice Accretion2070RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
Ottawa (M-C Int'l Airport)Ice Accretion2075RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2075 | 20.6823 | 24.7817 | 29.955 | 33.9085 | 37.8756
Ottawa (M-C Int'l Airport)Ice Accretion2080RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2080 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
Ottawa (M-C Int'l Airport)Ice Accretion2085RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2085 | 20.9224 | 25.1428 | 30.465 | 34.5356 | 38.6316
Ottawa (M-C Int'l Airport)Ice Accretion2090RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2090 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
Ottawa (M-C Int'l Airport)Ice Accretion2095RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2095 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
Ottawa (M-C Int'l Airport)Ice Accretion2100RCP6.0 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP6.0 | 2100 | 21.439 | 25.9458 | 31.65 | 36.0018 | 40.3326
Ottawa (M-C Int'l Airport)Ice Accretion2023RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
Ottawa (M-C Int'l Airport)Ice Accretion2025RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2025 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
Ottawa (M-C Int'l Airport)Ice Accretion2030RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2030 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
Ottawa (M-C Int'l Airport)Ice Accretion2035RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2035 | 20.2074 | 24.0285 | 28.86 | 32.5779 | 36.288
Ottawa (M-C Int'l Airport)Ice Accretion2040RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2040 | 20.3257 | 24.2194 | 29.14 | 32.9169 | 36.6912
Ottawa (M-C Int'l Airport)Ice Accretion2045RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2045 | 20.444 | 24.4103 | 29.42 | 33.2559 | 37.0944
Ottawa (M-C Int'l Airport)Ice Accretion2050RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2050 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
Ottawa (M-C Int'l Airport)Ice Accretion2055RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2055 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
Ottawa (M-C Int'l Airport)Ice Accretion2060RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2060 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
Ottawa (M-C Int'l Airport)Ice Accretion2065RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2065 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
Ottawa (M-C Int'l Airport)Ice Accretion2070RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2070 | 21.2372 | 25.7383 | 31.44 | 35.7871 | 40.1184
Ottawa (M-C Int'l Airport)Ice Accretion2075RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2075 | 21.0354 | 25.5308 | 31.23 | 35.5724 | 39.9042
Ottawa (M-C Int'l Airport)Ice Accretion2080RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2080 | 20.8336 | 25.3233 | 31.02 | 35.3577 | 39.69
Ottawa (M-C Int'l Airport)Ice Accretion2085RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2085 | 20.0926 | 24.5016 | 30.09 | 34.3237 | 38.5749
Ottawa (M-C Int'l Airport)Ice Accretion2090RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2090 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
Ottawa (M-C Int'l Airport)Ice Accretion2095RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2095 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
Ottawa (M-C Int'l Airport)Ice Accretion2100RCP8.5 | Ottawa (M-C Int'l Airport) | Ice Accretion | RCP8.5 | 2100 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
Ottawa (M-C Int'l Airport)Wind2023RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2023 | 77.8688 | 83.9427 | 90.351 | 96.743 | 103.1335
Ottawa (M-C Int'l Airport)Wind2025RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2025 | 77.8986 | 83.9776 | 90.3915 | 96.7895 | 103.1848
Ottawa (M-C Int'l Airport)Wind2030RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2030 | 77.9284 | 84.0125 | 90.432 | 96.8361 | 103.2361
Ottawa (M-C Int'l Airport)Wind2035RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2035 | 77.9582 | 84.0474 | 90.4725 | 96.8826 | 103.2874
Ottawa (M-C Int'l Airport)Wind2040RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2040 | 77.988 | 84.0822 | 90.513 | 96.9292 | 103.3387
Ottawa (M-C Int'l Airport)Wind2045RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2045 | 78.0178 | 84.1171 | 90.5535 | 96.9757 | 103.39
Ottawa (M-C Int'l Airport)Wind2050RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2050 | 77.9745 | 84.0515 | 90.4626 | 96.8624 | 103.2546
Ottawa (M-C Int'l Airport)Wind2055RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2055 | 77.9015 | 83.9511 | 90.3312 | 96.7025 | 103.0679
Ottawa (M-C Int'l Airport)Wind2060RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2060 | 77.8284 | 83.8507 | 90.1998 | 96.5427 | 102.8811
Ottawa (M-C Int'l Airport)Wind2065RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2065 | 77.7554 | 83.7502 | 90.0684 | 96.3828 | 102.6944
Ottawa (M-C Int'l Airport)Wind2070RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2070 | 77.6823 | 83.6498 | 89.937 | 96.223 | 102.5077
Ottawa (M-C Int'l Airport)Wind2075RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2075 | 77.7018 | 83.6819 | 89.9835 | 96.2823 | 102.5812
Ottawa (M-C Int'l Airport)Wind2080RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2080 | 77.7212 | 83.7139 | 90.03 | 96.3417 | 102.6547
Ottawa (M-C Int'l Airport)Wind2085RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2085 | 77.7406 | 83.746 | 90.0765 | 96.4011 | 102.7283
Ottawa (M-C Int'l Airport)Wind2090RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2090 | 77.76 | 83.7781 | 90.123 | 96.4605 | 102.8018
Ottawa (M-C Int'l Airport)Wind2095RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2095 | 77.7795 | 83.8102 | 90.1695 | 96.5199 | 102.8753
Ottawa (M-C Int'l Airport)Wind2100RCP4.5 | Ottawa (M-C Int'l Airport) | Wind | RCP4.5 | 2100 | 77.7989 | 83.8423 | 90.216 | 96.5793 | 102.9488
Ottawa (M-C Int'l Airport)Wind2023RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2023 | 77.8688 | 83.9427 | 90.351 | 96.743 | 103.1335
Ottawa (M-C Int'l Airport)Wind2025RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2025 | 77.8986 | 83.9776 | 90.3915 | 96.7895 | 103.1848
Ottawa (M-C Int'l Airport)Wind2030RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2030 | 77.9284 | 84.0125 | 90.432 | 96.8361 | 103.2361
Ottawa (M-C Int'l Airport)Wind2035RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2035 | 77.9582 | 84.0474 | 90.4725 | 96.8826 | 103.2874
Ottawa (M-C Int'l Airport)Wind2040RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2040 | 77.988 | 84.0822 | 90.513 | 96.9292 | 103.3387
Ottawa (M-C Int'l Airport)Wind2045RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2045 | 78.0178 | 84.1171 | 90.5535 | 96.9757 | 103.39
Ottawa (M-C Int'l Airport)Wind2050RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2050 | 77.9745 | 84.0515 | 90.4626 | 96.8624 | 103.2546
Ottawa (M-C Int'l Airport)Wind2055RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2055 | 77.9015 | 83.9511 | 90.3312 | 96.7025 | 103.0679
Ottawa (M-C Int'l Airport)Wind2060RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2060 | 77.8284 | 83.8507 | 90.1998 | 96.5427 | 102.8811
Ottawa (M-C Int'l Airport)Wind2065RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2065 | 77.7554 | 83.7502 | 90.0684 | 96.3828 | 102.6944
Ottawa (M-C Int'l Airport)Wind2070RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2070 | 77.6823 | 83.6498 | 89.937 | 96.223 | 102.5077
Ottawa (M-C Int'l Airport)Wind2075RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2075 | 77.7115 | 83.6979 | 90.0067 | 96.312 | 102.618
Ottawa (M-C Int'l Airport)Wind2080RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2080 | 77.7406 | 83.746 | 90.0765 | 96.4011 | 102.7283
Ottawa (M-C Int'l Airport)Wind2085RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2085 | 77.7698 | 83.7942 | 90.1462 | 96.4902 | 102.8385
Ottawa (M-C Int'l Airport)Wind2090RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2090 | 77.6797 | 83.6916 | 90.03 | 96.361 | 102.6958
Ottawa (M-C Int'l Airport)Wind2095RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2095 | 77.5606 | 83.541 | 89.844 | 96.1427 | 102.4427
Ottawa (M-C Int'l Airport)Wind2100RCP6.0 | Ottawa (M-C Int'l Airport) | Wind | RCP6.0 | 2100 | 77.4414 | 83.3903 | 89.658 | 95.9244 | 102.1896
Ottawa (M-C Int'l Airport)Wind2023RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2023 | 77.8688 | 83.9427 | 90.351 | 96.743 | 103.1335
Ottawa (M-C Int'l Airport)Wind2025RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2025 | 77.9284 | 84.0125 | 90.432 | 96.8361 | 103.2361
Ottawa (M-C Int'l Airport)Wind2030RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2030 | 77.988 | 84.0822 | 90.513 | 96.9292 | 103.3387
Ottawa (M-C Int'l Airport)Wind2035RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2035 | 78.0476 | 84.152 | 90.594 | 97.0223 | 103.4413
Ottawa (M-C Int'l Airport)Wind2040RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2040 | 77.9258 | 83.9846 | 90.375 | 96.7558 | 103.1301
Ottawa (M-C Int'l Airport)Wind2045RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2045 | 77.8041 | 83.8172 | 90.156 | 96.4894 | 102.8189
Ottawa (M-C Int'l Airport)Wind2050RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2050 | 77.7212 | 83.7139 | 90.03 | 96.3417 | 102.6547
Ottawa (M-C Int'l Airport)Wind2055RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2055 | 77.76 | 83.7781 | 90.123 | 96.4605 | 102.8018
Ottawa (M-C Int'l Airport)Wind2060RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2060 | 77.6797 | 83.6916 | 90.03 | 96.361 | 102.6958
Ottawa (M-C Int'l Airport)Wind2065RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2065 | 77.5606 | 83.541 | 89.844 | 96.1427 | 102.4427
Ottawa (M-C Int'l Airport)Wind2070RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2070 | 77.5165 | 83.4908 | 89.784 | 96.0721 | 102.364
Ottawa (M-C Int'l Airport)Wind2075RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2075 | 77.5917 | 83.5912 | 89.91 | 96.2198 | 102.5384
Ottawa (M-C Int'l Airport)Wind2080RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2080 | 77.6668 | 83.6916 | 90.036 | 96.3674 | 102.7129
Ottawa (M-C Int'l Airport)Wind2085RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2085 | 77.6435 | 83.6498 | 89.9775 | 96.2952 | 102.6205
Ottawa (M-C Int'l Airport)Wind2090RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2090 | 77.6202 | 83.6079 | 89.919 | 96.223 | 102.5282
Ottawa (M-C Int'l Airport)Wind2095RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2095 | 77.6202 | 83.6079 | 89.919 | 96.223 | 102.5282
Ottawa (M-C Int'l Airport)Wind2100RCP8.5 | Ottawa (M-C Int'l Airport) | Wind | RCP8.5 | 2100 | 77.6202 | 83.6079 | 89.919 | 96.223 | 102.5282
Ottawa (Orleans)Ice Accretion2023RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
Ottawa (Orleans)Ice Accretion2025RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
Ottawa (Orleans)Ice Accretion2030RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
Ottawa (Orleans)Ice Accretion2035RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
Ottawa (Orleans)Ice Accretion2040RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
Ottawa (Orleans)Ice Accretion2045RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
Ottawa (Orleans)Ice Accretion2050RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
Ottawa (Orleans)Ice Accretion2055RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
Ottawa (Orleans)Ice Accretion2060RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
Ottawa (Orleans)Ice Accretion2065RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
Ottawa (Orleans)Ice Accretion2070RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
Ottawa (Orleans)Ice Accretion2075RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2075 | 20.6423 | 24.7215 | 29.87 | 33.8039 | 37.7496
Ottawa (Orleans)Ice Accretion2080RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2080 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
Ottawa (Orleans)Ice Accretion2085RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2085 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
Ottawa (Orleans)Ice Accretion2090RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2090 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
Ottawa (Orleans)Ice Accretion2095RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2095 | 20.9624 | 25.2029 | 30.55 | 34.6401 | 38.7576
Ottawa (Orleans)Ice Accretion2100RCP4.5 | Ottawa (Orleans) | Ice Accretion | RCP4.5 | 2100 | 21.0424 | 25.3233 | 30.72 | 34.8492 | 39.0096
Ottawa (Orleans)Ice Accretion2023RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
Ottawa (Orleans)Ice Accretion2025RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
Ottawa (Orleans)Ice Accretion2030RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
Ottawa (Orleans)Ice Accretion2035RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
Ottawa (Orleans)Ice Accretion2040RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
Ottawa (Orleans)Ice Accretion2045RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
Ottawa (Orleans)Ice Accretion2050RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
Ottawa (Orleans)Ice Accretion2055RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
Ottawa (Orleans)Ice Accretion2060RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
Ottawa (Orleans)Ice Accretion2065RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
Ottawa (Orleans)Ice Accretion2070RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
Ottawa (Orleans)Ice Accretion2075RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2075 | 20.6823 | 24.7817 | 29.955 | 33.9085 | 37.8756
Ottawa (Orleans)Ice Accretion2080RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2080 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
Ottawa (Orleans)Ice Accretion2085RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2085 | 20.9224 | 25.1428 | 30.465 | 34.5356 | 38.6316
Ottawa (Orleans)Ice Accretion2090RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2090 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
Ottawa (Orleans)Ice Accretion2095RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2095 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
Ottawa (Orleans)Ice Accretion2100RCP6.0 | Ottawa (Orleans) | Ice Accretion | RCP6.0 | 2100 | 21.439 | 25.9458 | 31.65 | 36.0018 | 40.3326
Ottawa (Orleans)Ice Accretion2023RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
Ottawa (Orleans)Ice Accretion2025RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2025 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
Ottawa (Orleans)Ice Accretion2030RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2030 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
Ottawa (Orleans)Ice Accretion2035RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2035 | 20.2074 | 24.0285 | 28.86 | 32.5779 | 36.288
Ottawa (Orleans)Ice Accretion2040RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2040 | 20.3257 | 24.2194 | 29.14 | 32.9169 | 36.6912
Ottawa (Orleans)Ice Accretion2045RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2045 | 20.444 | 24.4103 | 29.42 | 33.2559 | 37.0944
Ottawa (Orleans)Ice Accretion2050RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2050 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
Ottawa (Orleans)Ice Accretion2055RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2055 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
Ottawa (Orleans)Ice Accretion2060RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2060 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
Ottawa (Orleans)Ice Accretion2065RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2065 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
Ottawa (Orleans)Ice Accretion2070RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2070 | 21.2372 | 25.7383 | 31.44 | 35.7871 | 40.1184
Ottawa (Orleans)Ice Accretion2075RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2075 | 21.0354 | 25.5308 | 31.23 | 35.5724 | 39.9042
Ottawa (Orleans)Ice Accretion2080RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2080 | 20.8336 | 25.3233 | 31.02 | 35.3577 | 39.69
Ottawa (Orleans)Ice Accretion2085RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2085 | 20.0926 | 24.5016 | 30.09 | 34.3237 | 38.5749
Ottawa (Orleans)Ice Accretion2090RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2090 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
Ottawa (Orleans)Ice Accretion2095RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2095 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
Ottawa (Orleans)Ice Accretion2100RCP8.5 | Ottawa (Orleans) | Ice Accretion | RCP8.5 | 2100 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
Ottawa (Orleans)Wind2023RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2023 | 79.5993 | 85.8081 | 92.3588 | 98.8928 | 105.4254
Ottawa (Orleans)Wind2025RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2025 | 79.6297 | 85.8438 | 92.4002 | 98.9404 | 105.4778
Ottawa (Orleans)Wind2030RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2030 | 79.6602 | 85.8794 | 92.4416 | 98.988 | 105.5303
Ottawa (Orleans)Wind2035RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2035 | 79.6906 | 85.9151 | 92.483 | 99.0356 | 105.5827
Ottawa (Orleans)Wind2040RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2040 | 79.7211 | 85.9507 | 92.5244 | 99.0831 | 105.6351
Ottawa (Orleans)Wind2045RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2045 | 79.7515 | 85.9864 | 92.5658 | 99.1307 | 105.6876
Ottawa (Orleans)Wind2050RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2050 | 79.7073 | 85.9194 | 92.4729 | 99.0149 | 105.5491
Ottawa (Orleans)Wind2055RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2055 | 79.6326 | 85.8167 | 92.3386 | 98.8515 | 105.3583
Ottawa (Orleans)Wind2060RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2060 | 79.558 | 85.714 | 92.2042 | 98.6881 | 105.1674
Ottawa (Orleans)Wind2065RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2065 | 79.4833 | 85.6113 | 92.0699 | 98.5247 | 104.9765
Ottawa (Orleans)Wind2070RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2070 | 79.4086 | 85.5087 | 91.9356 | 98.3612 | 104.7856
Ottawa (Orleans)Wind2075RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2075 | 79.4285 | 85.5415 | 91.9831 | 98.422 | 104.8608
Ottawa (Orleans)Wind2080RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2080 | 79.4483 | 85.5743 | 92.0307 | 98.4827 | 104.9359
Ottawa (Orleans)Wind2085RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2085 | 79.4682 | 85.6071 | 92.0782 | 98.5434 | 105.0111
Ottawa (Orleans)Wind2090RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2090 | 79.488 | 85.6399 | 92.1257 | 98.6041 | 105.0863
Ottawa (Orleans)Wind2095RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2095 | 79.5079 | 85.6727 | 92.1733 | 98.6648 | 105.1614
Ottawa (Orleans)Wind2100RCP4.5 | Ottawa (Orleans) | Wind | RCP4.5 | 2100 | 79.5278 | 85.7055 | 92.2208 | 98.7255 | 105.2366
Ottawa (Orleans)Wind2023RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2023 | 79.5993 | 85.8081 | 92.3588 | 98.8928 | 105.4254
Ottawa (Orleans)Wind2025RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2025 | 79.6297 | 85.8438 | 92.4002 | 98.9404 | 105.4778
Ottawa (Orleans)Wind2030RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2030 | 79.6602 | 85.8794 | 92.4416 | 98.988 | 105.5303
Ottawa (Orleans)Wind2035RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2035 | 79.6906 | 85.9151 | 92.483 | 99.0356 | 105.5827
Ottawa (Orleans)Wind2040RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2040 | 79.7211 | 85.9507 | 92.5244 | 99.0831 | 105.6351
Ottawa (Orleans)Wind2045RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2045 | 79.7515 | 85.9864 | 92.5658 | 99.1307 | 105.6876
Ottawa (Orleans)Wind2050RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2050 | 79.7073 | 85.9194 | 92.4729 | 99.0149 | 105.5491
Ottawa (Orleans)Wind2055RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2055 | 79.6326 | 85.8167 | 92.3386 | 98.8515 | 105.3583
Ottawa (Orleans)Wind2060RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2060 | 79.558 | 85.714 | 92.2042 | 98.6881 | 105.1674
Ottawa (Orleans)Wind2065RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2065 | 79.4833 | 85.6113 | 92.0699 | 98.5247 | 104.9765
Ottawa (Orleans)Wind2070RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2070 | 79.4086 | 85.5087 | 91.9356 | 98.3612 | 104.7856
Ottawa (Orleans)Wind2075RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2075 | 79.4384 | 85.5579 | 92.0069 | 98.4523 | 104.8984
Ottawa (Orleans)Wind2080RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2080 | 79.4682 | 85.6071 | 92.0782 | 98.5434 | 105.0111
Ottawa (Orleans)Wind2085RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2085 | 79.498 | 85.6563 | 92.1495 | 98.6344 | 105.1238
Ottawa (Orleans)Wind2090RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2090 | 79.406 | 85.5514 | 92.0307 | 98.5023 | 104.9779
Ottawa (Orleans)Wind2095RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2095 | 79.2842 | 85.3974 | 91.8405 | 98.2792 | 104.7192
Ottawa (Orleans)Wind2100RCP6.0 | Ottawa (Orleans) | Wind | RCP6.0 | 2100 | 79.1623 | 85.2434 | 91.6504 | 98.0561 | 104.4605
Ottawa (Orleans)Wind2023RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2023 | 79.5993 | 85.8081 | 92.3588 | 98.8928 | 105.4254
Ottawa (Orleans)Wind2025RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2025 | 79.6602 | 85.8794 | 92.4416 | 98.988 | 105.5303
Ottawa (Orleans)Wind2030RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2030 | 79.7211 | 85.9507 | 92.5244 | 99.0831 | 105.6351
Ottawa (Orleans)Wind2035RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2035 | 79.782 | 86.022 | 92.6072 | 99.1783 | 105.74
Ottawa (Orleans)Wind2040RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2040 | 79.6575 | 85.8509 | 92.3833 | 98.9059 | 105.4219
Ottawa (Orleans)Wind2045RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2045 | 79.5331 | 85.6798 | 92.1595 | 98.6336 | 105.1037
Ottawa (Orleans)Wind2050RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2050 | 79.4483 | 85.5743 | 92.0307 | 98.4827 | 104.9359
Ottawa (Orleans)Wind2055RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2055 | 79.488 | 85.6399 | 92.1257 | 98.6041 | 105.0863
Ottawa (Orleans)Wind2060RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2060 | 79.406 | 85.5514 | 92.0307 | 98.5023 | 104.9779
Ottawa (Orleans)Wind2065RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2065 | 79.2842 | 85.3974 | 91.8405 | 98.2792 | 104.7192
Ottawa (Orleans)Wind2070RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2070 | 79.2391 | 85.3461 | 91.7792 | 98.207 | 104.6388
Ottawa (Orleans)Wind2075RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2075 | 79.3159 | 85.4488 | 91.908 | 98.358 | 104.8171
Ottawa (Orleans)Wind2080RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2080 | 79.3927 | 85.5514 | 92.0368 | 98.5089 | 104.9954
Ottawa (Orleans)Wind2085RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2085 | 79.3689 | 85.5087 | 91.977 | 98.4351 | 104.901
Ottawa (Orleans)Wind2090RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2090 | 79.3451 | 85.4659 | 91.9172 | 98.3612 | 104.8066
Ottawa (Orleans)Wind2095RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2095 | 79.3451 | 85.4659 | 91.9172 | 98.3612 | 104.8066
Ottawa (Orleans)Wind2100RCP8.5 | Ottawa (Orleans) | Wind | RCP8.5 | 2100 | 79.3451 | 85.4659 | 91.9172 | 98.3612 | 104.8066
Ottawa (city hall)Ice Accretion2023RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
Ottawa (city hall)Ice Accretion2025RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
Ottawa (city hall)Ice Accretion2030RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
Ottawa (city hall)Ice Accretion2035RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
Ottawa (city hall)Ice Accretion2040RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
Ottawa (city hall)Ice Accretion2045RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
Ottawa (city hall)Ice Accretion2050RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
Ottawa (city hall)Ice Accretion2055RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
Ottawa (city hall)Ice Accretion2060RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
Ottawa (city hall)Ice Accretion2065RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
Ottawa (city hall)Ice Accretion2070RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
Ottawa (city hall)Ice Accretion2075RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2075 | 20.6423 | 24.7215 | 29.87 | 33.8039 | 37.7496
Ottawa (city hall)Ice Accretion2080RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2080 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
Ottawa (city hall)Ice Accretion2085RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2085 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
Ottawa (city hall)Ice Accretion2090RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2090 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
Ottawa (city hall)Ice Accretion2095RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2095 | 20.9624 | 25.2029 | 30.55 | 34.6401 | 38.7576
Ottawa (city hall)Ice Accretion2100RCP4.5 | Ottawa (city hall) | Ice Accretion | RCP4.5 | 2100 | 21.0424 | 25.3233 | 30.72 | 34.8492 | 39.0096
Ottawa (city hall)Ice Accretion2023RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
Ottawa (city hall)Ice Accretion2025RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
Ottawa (city hall)Ice Accretion2030RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
Ottawa (city hall)Ice Accretion2035RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
Ottawa (city hall)Ice Accretion2040RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
Ottawa (city hall)Ice Accretion2045RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
Ottawa (city hall)Ice Accretion2050RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
Ottawa (city hall)Ice Accretion2055RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
Ottawa (city hall)Ice Accretion2060RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
Ottawa (city hall)Ice Accretion2065RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
Ottawa (city hall)Ice Accretion2070RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
Ottawa (city hall)Ice Accretion2075RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2075 | 20.6823 | 24.7817 | 29.955 | 33.9085 | 37.8756
Ottawa (city hall)Ice Accretion2080RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2080 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
Ottawa (city hall)Ice Accretion2085RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2085 | 20.9224 | 25.1428 | 30.465 | 34.5356 | 38.6316
Ottawa (city hall)Ice Accretion2090RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2090 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
Ottawa (city hall)Ice Accretion2095RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2095 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
Ottawa (city hall)Ice Accretion2100RCP6.0 | Ottawa (city hall) | Ice Accretion | RCP6.0 | 2100 | 21.439 | 25.9458 | 31.65 | 36.0018 | 40.3326
Ottawa (city hall)Ice Accretion2023RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
Ottawa (city hall)Ice Accretion2025RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2025 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
Ottawa (city hall)Ice Accretion2030RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2030 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
Ottawa (city hall)Ice Accretion2035RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2035 | 20.2074 | 24.0285 | 28.86 | 32.5779 | 36.288
Ottawa (city hall)Ice Accretion2040RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2040 | 20.3257 | 24.2194 | 29.14 | 32.9169 | 36.6912
Ottawa (city hall)Ice Accretion2045RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2045 | 20.444 | 24.4103 | 29.42 | 33.2559 | 37.0944
Ottawa (city hall)Ice Accretion2050RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2050 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
Ottawa (city hall)Ice Accretion2055RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2055 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
Ottawa (city hall)Ice Accretion2060RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2060 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
Ottawa (city hall)Ice Accretion2065RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2065 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
Ottawa (city hall)Ice Accretion2070RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2070 | 21.2372 | 25.7383 | 31.44 | 35.7871 | 40.1184
Ottawa (city hall)Ice Accretion2075RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2075 | 21.0354 | 25.5308 | 31.23 | 35.5724 | 39.9042
Ottawa (city hall)Ice Accretion2080RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2080 | 20.8336 | 25.3233 | 31.02 | 35.3577 | 39.69
Ottawa (city hall)Ice Accretion2085RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2085 | 20.0926 | 24.5016 | 30.09 | 34.3237 | 38.5749
Ottawa (city hall)Ice Accretion2090RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2090 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
Ottawa (city hall)Ice Accretion2095RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2095 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
Ottawa (city hall)Ice Accretion2100RCP8.5 | Ottawa (city hall) | Ice Accretion | RCP8.5 | 2100 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
Ottawa (city hall)Wind2023RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2023 | 77.8688 | 83.9427 | 90.351 | 96.743 | 103.1335
Ottawa (city hall)Wind2025RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2025 | 77.8986 | 83.9776 | 90.3915 | 96.7895 | 103.1848
Ottawa (city hall)Wind2030RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2030 | 77.9284 | 84.0125 | 90.432 | 96.8361 | 103.2361
Ottawa (city hall)Wind2035RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2035 | 77.9582 | 84.0474 | 90.4725 | 96.8826 | 103.2874
Ottawa (city hall)Wind2040RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2040 | 77.988 | 84.0822 | 90.513 | 96.9292 | 103.3387
Ottawa (city hall)Wind2045RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2045 | 78.0178 | 84.1171 | 90.5535 | 96.9757 | 103.39
Ottawa (city hall)Wind2050RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2050 | 77.9745 | 84.0515 | 90.4626 | 96.8624 | 103.2546
Ottawa (city hall)Wind2055RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2055 | 77.9015 | 83.9511 | 90.3312 | 96.7025 | 103.0679
Ottawa (city hall)Wind2060RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2060 | 77.8284 | 83.8507 | 90.1998 | 96.5427 | 102.8811
Ottawa (city hall)Wind2065RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2065 | 77.7554 | 83.7502 | 90.0684 | 96.3828 | 102.6944
Ottawa (city hall)Wind2070RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2070 | 77.6823 | 83.6498 | 89.937 | 96.223 | 102.5077
Ottawa (city hall)Wind2075RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2075 | 77.7018 | 83.6819 | 89.9835 | 96.2823 | 102.5812
Ottawa (city hall)Wind2080RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2080 | 77.7212 | 83.7139 | 90.03 | 96.3417 | 102.6547
Ottawa (city hall)Wind2085RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2085 | 77.7406 | 83.746 | 90.0765 | 96.4011 | 102.7283
Ottawa (city hall)Wind2090RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2090 | 77.76 | 83.7781 | 90.123 | 96.4605 | 102.8018
Ottawa (city hall)Wind2095RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2095 | 77.7795 | 83.8102 | 90.1695 | 96.5199 | 102.8753
Ottawa (city hall)Wind2100RCP4.5 | Ottawa (city hall) | Wind | RCP4.5 | 2100 | 77.7989 | 83.8423 | 90.216 | 96.5793 | 102.9488
Ottawa (city hall)Wind2023RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2023 | 77.8688 | 83.9427 | 90.351 | 96.743 | 103.1335
Ottawa (city hall)Wind2025RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2025 | 77.8986 | 83.9776 | 90.3915 | 96.7895 | 103.1848
Ottawa (city hall)Wind2030RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2030 | 77.9284 | 84.0125 | 90.432 | 96.8361 | 103.2361
Ottawa (city hall)Wind2035RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2035 | 77.9582 | 84.0474 | 90.4725 | 96.8826 | 103.2874
Ottawa (city hall)Wind2040RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2040 | 77.988 | 84.0822 | 90.513 | 96.9292 | 103.3387
Ottawa (city hall)Wind2045RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2045 | 78.0178 | 84.1171 | 90.5535 | 96.9757 | 103.39
Ottawa (city hall)Wind2050RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2050 | 77.9745 | 84.0515 | 90.4626 | 96.8624 | 103.2546
Ottawa (city hall)Wind2055RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2055 | 77.9015 | 83.9511 | 90.3312 | 96.7025 | 103.0679
Ottawa (city hall)Wind2060RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2060 | 77.8284 | 83.8507 | 90.1998 | 96.5427 | 102.8811
Ottawa (city hall)Wind2065RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2065 | 77.7554 | 83.7502 | 90.0684 | 96.3828 | 102.6944
Ottawa (city hall)Wind2070RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2070 | 77.6823 | 83.6498 | 89.937 | 96.223 | 102.5077
Ottawa (city hall)Wind2075RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2075 | 77.7115 | 83.6979 | 90.0067 | 96.312 | 102.618
Ottawa (city hall)Wind2080RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2080 | 77.7406 | 83.746 | 90.0765 | 96.4011 | 102.7283
Ottawa (city hall)Wind2085RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2085 | 77.7698 | 83.7942 | 90.1462 | 96.4902 | 102.8385
Ottawa (city hall)Wind2090RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2090 | 77.6797 | 83.6916 | 90.03 | 96.361 | 102.6958
Ottawa (city hall)Wind2095RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2095 | 77.5606 | 83.541 | 89.844 | 96.1427 | 102.4427
Ottawa (city hall)Wind2100RCP6.0 | Ottawa (city hall) | Wind | RCP6.0 | 2100 | 77.4414 | 83.3903 | 89.658 | 95.9244 | 102.1896
Ottawa (city hall)Wind2023RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2023 | 77.8688 | 83.9427 | 90.351 | 96.743 | 103.1335
Ottawa (city hall)Wind2025RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2025 | 77.9284 | 84.0125 | 90.432 | 96.8361 | 103.2361
Ottawa (city hall)Wind2030RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2030 | 77.988 | 84.0822 | 90.513 | 96.9292 | 103.3387
Ottawa (city hall)Wind2035RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2035 | 78.0476 | 84.152 | 90.594 | 97.0223 | 103.4413
Ottawa (city hall)Wind2040RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2040 | 77.9258 | 83.9846 | 90.375 | 96.7558 | 103.1301
Ottawa (city hall)Wind2045RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2045 | 77.8041 | 83.8172 | 90.156 | 96.4894 | 102.8189
Ottawa (city hall)Wind2050RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2050 | 77.7212 | 83.7139 | 90.03 | 96.3417 | 102.6547
Ottawa (city hall)Wind2055RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2055 | 77.76 | 83.7781 | 90.123 | 96.4605 | 102.8018
Ottawa (city hall)Wind2060RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2060 | 77.6797 | 83.6916 | 90.03 | 96.361 | 102.6958
Ottawa (city hall)Wind2065RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2065 | 77.5606 | 83.541 | 89.844 | 96.1427 | 102.4427
Ottawa (city hall)Wind2070RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2070 | 77.5165 | 83.4908 | 89.784 | 96.0721 | 102.364
Ottawa (city hall)Wind2075RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2075 | 77.5917 | 83.5912 | 89.91 | 96.2198 | 102.5384
Ottawa (city hall)Wind2080RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2080 | 77.6668 | 83.6916 | 90.036 | 96.3674 | 102.7129
Ottawa (city hall)Wind2085RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2085 | 77.6435 | 83.6498 | 89.9775 | 96.2952 | 102.6205
Ottawa (city hall)Wind2090RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2090 | 77.6202 | 83.6079 | 89.919 | 96.223 | 102.5282
Ottawa (city hall)Wind2095RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2095 | 77.6202 | 83.6079 | 89.919 | 96.223 | 102.5282
Ottawa (city hall)Wind2100RCP8.5 | Ottawa (city hall) | Wind | RCP8.5 | 2100 | 77.6202 | 83.6079 | 89.919 | 96.223 | 102.5282
Owen SoundIce Accretion2023RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2023 | 14.6858 | 17.552 | 21.189 | 23.991 | 26.7511
Owen SoundIce Accretion2025RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2025 | 14.6956 | 17.5753 | 21.2275 | 24.0385 | 26.8128
Owen SoundIce Accretion2030RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2030 | 14.7053 | 17.5985 | 21.266 | 24.0859 | 26.8745
Owen SoundIce Accretion2035RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2035 | 14.7151 | 17.6217 | 21.3045 | 24.1334 | 26.9363
Owen SoundIce Accretion2040RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2040 | 14.7248 | 17.645 | 21.343 | 24.1809 | 26.998
Owen SoundIce Accretion2045RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2045 | 14.7345 | 17.6682 | 21.3815 | 24.2283 | 27.0598
Owen SoundIce Accretion2050RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2050 | 14.6917 | 17.6426 | 21.378 | 24.2378 | 27.0845
Owen SoundIce Accretion2055RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2055 | 14.6391 | 17.5938 | 21.336 | 24.1999 | 27.0474
Owen SoundIce Accretion2060RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2060 | 14.5865 | 17.545 | 21.294 | 24.1619 | 27.0104
Owen SoundIce Accretion2065RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2065 | 14.5339 | 17.4962 | 21.252 | 24.1239 | 26.9733
Owen SoundIce Accretion2070RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2070 | 14.4813 | 17.4474 | 21.21 | 24.0859 | 26.9363
Owen SoundIce Accretion2075RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2075 | 14.4277 | 17.4097 | 21.189 | 24.0741 | 26.9363
Owen SoundIce Accretion2080RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2080 | 14.3741 | 17.3719 | 21.168 | 24.0622 | 26.9363
Owen SoundIce Accretion2085RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2085 | 14.3205 | 17.3341 | 21.147 | 24.0504 | 26.9363
Owen SoundIce Accretion2090RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2090 | 14.2669 | 17.2964 | 21.126 | 24.0385 | 26.9363
Owen SoundIce Accretion2095RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2095 | 14.2134 | 17.2586 | 21.105 | 24.0266 | 26.9363
Owen SoundIce Accretion2100RCP4.5 | Owen Sound | Ice Accretion | RCP4.5 | 2100 | 14.1598 | 17.2208 | 21.084 | 24.0148 | 26.9363
Owen SoundIce Accretion2023RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2023 | 14.6858 | 17.552 | 21.189 | 23.991 | 26.7511
Owen SoundIce Accretion2025RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2025 | 14.6956 | 17.5753 | 21.2275 | 24.0385 | 26.8128
Owen SoundIce Accretion2030RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2030 | 14.7053 | 17.5985 | 21.266 | 24.0859 | 26.8745
Owen SoundIce Accretion2035RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2035 | 14.7151 | 17.6217 | 21.3045 | 24.1334 | 26.9363
Owen SoundIce Accretion2040RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2040 | 14.7248 | 17.645 | 21.343 | 24.1809 | 26.998
Owen SoundIce Accretion2045RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2045 | 14.7345 | 17.6682 | 21.3815 | 24.2283 | 27.0598
Owen SoundIce Accretion2050RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2050 | 14.6917 | 17.6426 | 21.378 | 24.2378 | 27.0845
Owen SoundIce Accretion2055RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2055 | 14.6391 | 17.5938 | 21.336 | 24.1999 | 27.0474
Owen SoundIce Accretion2060RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2060 | 14.5865 | 17.545 | 21.294 | 24.1619 | 27.0104
Owen SoundIce Accretion2065RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2065 | 14.5339 | 17.4962 | 21.252 | 24.1239 | 26.9733
Owen SoundIce Accretion2070RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2070 | 14.4813 | 17.4474 | 21.21 | 24.0859 | 26.9363
Owen SoundIce Accretion2075RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2075 | 14.4009 | 17.3908 | 21.1785 | 24.0682 | 26.9363
Owen SoundIce Accretion2080RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2080 | 14.3205 | 17.3341 | 21.147 | 24.0504 | 26.9363
Owen SoundIce Accretion2085RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2085 | 14.2401 | 17.2775 | 21.1155 | 24.0326 | 26.9363
Owen SoundIce Accretion2090RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2090 | 13.9114 | 16.9594 | 20.797 | 23.7142 | 26.6188
Owen SoundIce Accretion2095RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2095 | 13.6629 | 16.6979 | 20.51 | 23.4136 | 26.3012
Owen SoundIce Accretion2100RCP6.0 | Owen Sound | Ice Accretion | RCP6.0 | 2100 | 13.4145 | 16.4365 | 20.223 | 23.113 | 25.9837
Owen SoundIce Accretion2023RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2023 | 14.6858 | 17.552 | 21.189 | 23.991 | 26.7511
Owen SoundIce Accretion2025RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2025 | 14.7053 | 17.5985 | 21.266 | 24.0859 | 26.8745
Owen SoundIce Accretion2030RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2030 | 14.7248 | 17.645 | 21.343 | 24.1809 | 26.998
Owen SoundIce Accretion2035RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2035 | 14.7443 | 17.6914 | 21.42 | 24.2758 | 27.1215
Owen SoundIce Accretion2040RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2040 | 14.6566 | 17.6101 | 21.35 | 24.2125 | 27.0598
Owen SoundIce Accretion2045RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2045 | 14.5689 | 17.5288 | 21.28 | 24.1492 | 26.998
Owen SoundIce Accretion2050RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2050 | 14.3741 | 17.3719 | 21.168 | 24.0622 | 26.9363
Owen SoundIce Accretion2055RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2055 | 14.2669 | 17.2964 | 21.126 | 24.0385 | 26.9363
Owen SoundIce Accretion2060RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2060 | 13.9114 | 16.9594 | 20.797 | 23.7142 | 26.6188
Owen SoundIce Accretion2065RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2065 | 13.6629 | 16.6979 | 20.51 | 23.4136 | 26.3012
Owen SoundIce Accretion2070RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2070 | 13.0443 | 16.024 | 19.761 | 22.6147 | 25.4457
Owen SoundIce Accretion2075RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2075 | 12.6741 | 15.6115 | 19.299 | 22.1164 | 24.9077
Owen SoundIce Accretion2080RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2080 | 12.304 | 15.199 | 18.837 | 21.618 | 24.3697
Owen SoundIce Accretion2085RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2085 | 11.6756 | 14.4756 | 17.9865 | 20.657 | 23.3113
Owen SoundIce Accretion2090RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2090 | 11.0473 | 13.7523 | 17.136 | 19.6959 | 22.2529
Owen SoundIce Accretion2095RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2095 | 11.0473 | 13.7523 | 17.136 | 19.6959 | 22.2529
Owen SoundIce Accretion2100RCP8.5 | Owen Sound | Ice Accretion | RCP8.5 | 2100 | 11.0473 | 13.7523 | 17.136 | 19.6959 | 22.2529
Owen SoundWind2023RCP4.5 | Owen Sound | Wind | RCP4.5 | 2023 | 82.0308 | 88.2528 | 94.772 | 101.3247 | 107.8668
Owen SoundWind2025RCP4.5 | Owen Sound | Wind | RCP4.5 | 2025 | 82.106 | 88.3456 | 94.8892 | 101.4603 | 108.0238
Owen SoundWind2030RCP4.5 | Owen Sound | Wind | RCP4.5 | 2030 | 82.1812 | 88.4384 | 95.0063 | 101.5958 | 108.1809
Owen SoundWind2035RCP4.5 | Owen Sound | Wind | RCP4.5 | 2035 | 82.2564 | 88.5311 | 95.1235 | 101.7313 | 108.3379
Owen SoundWind2040RCP4.5 | Owen Sound | Wind | RCP4.5 | 2040 | 82.3316 | 88.6239 | 95.2407 | 101.8669 | 108.4949
Owen SoundWind2045RCP4.5 | Owen Sound | Wind | RCP4.5 | 2045 | 82.4068 | 88.7167 | 95.3578 | 102.0024 | 108.652
Owen SoundWind2050RCP4.5 | Owen Sound | Wind | RCP4.5 | 2050 | 82.4787 | 88.8006 | 95.456 | 102.1135 | 108.7765
Owen SoundWind2055RCP4.5 | Owen Sound | Wind | RCP4.5 | 2055 | 82.4754 | 88.7918 | 95.437 | 102.0891 | 108.744
Owen SoundWind2060RCP4.5 | Owen Sound | Wind | RCP4.5 | 2060 | 82.4722 | 88.7829 | 95.418 | 102.0647 | 108.7115
Owen SoundWind2065RCP4.5 | Owen Sound | Wind | RCP4.5 | 2065 | 82.4689 | 88.7741 | 95.399 | 102.0403 | 108.6791
Owen SoundWind2070RCP4.5 | Owen Sound | Wind | RCP4.5 | 2070 | 82.4656 | 88.7652 | 95.38 | 102.0159 | 108.6466
Owen SoundWind2075RCP4.5 | Owen Sound | Wind | RCP4.5 | 2075 | 82.4834 | 88.7844 | 95.4006 | 102.038 | 108.67
Owen SoundWind2080RCP4.5 | Owen Sound | Wind | RCP4.5 | 2080 | 82.5011 | 88.8035 | 95.4212 | 102.06 | 108.6935
Owen SoundWind2085RCP4.5 | Owen Sound | Wind | RCP4.5 | 2085 | 82.5189 | 88.8227 | 95.4417 | 102.082 | 108.717
Owen SoundWind2090RCP4.5 | Owen Sound | Wind | RCP4.5 | 2090 | 82.5367 | 88.8418 | 95.4623 | 102.104 | 108.7404
Owen SoundWind2095RCP4.5 | Owen Sound | Wind | RCP4.5 | 2095 | 82.5545 | 88.861 | 95.4829 | 102.1261 | 108.7639
Owen SoundWind2100RCP4.5 | Owen Sound | Wind | RCP4.5 | 2100 | 82.5722 | 88.8801 | 95.5035 | 102.1481 | 108.7873
Owen SoundWind2023RCP6.0 | Owen Sound | Wind | RCP6.0 | 2023 | 82.0308 | 88.2528 | 94.772 | 101.3247 | 107.8668
Owen SoundWind2025RCP6.0 | Owen Sound | Wind | RCP6.0 | 2025 | 82.106 | 88.3456 | 94.8892 | 101.4603 | 108.0238
Owen SoundWind2030RCP6.0 | Owen Sound | Wind | RCP6.0 | 2030 | 82.1812 | 88.4384 | 95.0063 | 101.5958 | 108.1809
Owen SoundWind2035RCP6.0 | Owen Sound | Wind | RCP6.0 | 2035 | 82.2564 | 88.5311 | 95.1235 | 101.7313 | 108.3379
Owen SoundWind2040RCP6.0 | Owen Sound | Wind | RCP6.0 | 2040 | 82.3316 | 88.6239 | 95.2407 | 101.8669 | 108.4949
Owen SoundWind2045RCP6.0 | Owen Sound | Wind | RCP6.0 | 2045 | 82.4068 | 88.7167 | 95.3578 | 102.0024 | 108.652
Owen SoundWind2050RCP6.0 | Owen Sound | Wind | RCP6.0 | 2050 | 82.4787 | 88.8006 | 95.456 | 102.1135 | 108.7765
Owen SoundWind2055RCP6.0 | Owen Sound | Wind | RCP6.0 | 2055 | 82.4754 | 88.7918 | 95.437 | 102.0891 | 108.744
Owen SoundWind2060RCP6.0 | Owen Sound | Wind | RCP6.0 | 2060 | 82.4722 | 88.7829 | 95.418 | 102.0647 | 108.7115
Owen SoundWind2065RCP6.0 | Owen Sound | Wind | RCP6.0 | 2065 | 82.4689 | 88.7741 | 95.399 | 102.0403 | 108.6791
Owen SoundWind2070RCP6.0 | Owen Sound | Wind | RCP6.0 | 2070 | 82.4656 | 88.7652 | 95.38 | 102.0159 | 108.6466
Owen SoundWind2075RCP6.0 | Owen Sound | Wind | RCP6.0 | 2075 | 82.4923 | 88.794 | 95.4109 | 102.049 | 108.6818
Owen SoundWind2080RCP6.0 | Owen Sound | Wind | RCP6.0 | 2080 | 82.5189 | 88.8227 | 95.4417 | 102.082 | 108.717
Owen SoundWind2085RCP6.0 | Owen Sound | Wind | RCP6.0 | 2085 | 82.5456 | 88.8514 | 95.4726 | 102.115 | 108.7522
Owen SoundWind2090RCP6.0 | Owen Sound | Wind | RCP6.0 | 2090 | 82.7035 | 89.0391 | 95.6967 | 102.3683 | 109.0328
Owen SoundWind2095RCP6.0 | Owen Sound | Wind | RCP6.0 | 2095 | 82.8347 | 89.1982 | 95.8898 | 102.5886 | 109.2783
Owen SoundWind2100RCP6.0 | Owen Sound | Wind | RCP6.0 | 2100 | 82.966 | 89.3572 | 96.083 | 102.8088 | 109.5238
Owen SoundWind2023RCP8.5 | Owen Sound | Wind | RCP8.5 | 2023 | 82.0308 | 88.2528 | 94.772 | 101.3247 | 107.8668
Owen SoundWind2025RCP8.5 | Owen Sound | Wind | RCP8.5 | 2025 | 82.1812 | 88.4384 | 95.0063 | 101.5958 | 108.1809
Owen SoundWind2030RCP8.5 | Owen Sound | Wind | RCP8.5 | 2030 | 82.3316 | 88.6239 | 95.2407 | 101.8669 | 108.4949
Owen SoundWind2035RCP8.5 | Owen Sound | Wind | RCP8.5 | 2035 | 82.482 | 88.8094 | 95.475 | 102.1379 | 108.809
Owen SoundWind2040RCP8.5 | Owen Sound | Wind | RCP8.5 | 2040 | 82.4765 | 88.7947 | 95.4433 | 102.0973 | 108.7549
Owen SoundWind2045RCP8.5 | Owen Sound | Wind | RCP8.5 | 2045 | 82.4711 | 88.78 | 95.4117 | 102.0566 | 108.7007
Owen SoundWind2050RCP8.5 | Owen Sound | Wind | RCP8.5 | 2050 | 82.5011 | 88.8035 | 95.4212 | 102.06 | 108.6935
Owen SoundWind2055RCP8.5 | Owen Sound | Wind | RCP8.5 | 2055 | 82.5367 | 88.8418 | 95.4623 | 102.104 | 108.7404
Owen SoundWind2060RCP8.5 | Owen Sound | Wind | RCP8.5 | 2060 | 82.7035 | 89.0391 | 95.6967 | 102.3683 | 109.0328
Owen SoundWind2065RCP8.5 | Owen Sound | Wind | RCP8.5 | 2065 | 82.8347 | 89.1982 | 95.8898 | 102.5886 | 109.2783
Owen SoundWind2070RCP8.5 | Owen Sound | Wind | RCP8.5 | 2070 | 83.0343 | 89.4397 | 96.178 | 102.9172 | 109.6501
Owen SoundWind2075RCP8.5 | Owen Sound | Wind | RCP8.5 | 2075 | 83.1027 | 89.5221 | 96.273 | 103.0257 | 109.7765
Owen SoundWind2080RCP8.5 | Owen Sound | Wind | RCP8.5 | 2080 | 83.1711 | 89.6046 | 96.368 | 103.1341 | 109.9028
Owen SoundWind2085RCP8.5 | Owen Sound | Wind | RCP8.5 | 2085 | 83.4869 | 90.0287 | 96.9332 | 103.8151 | 110.6988
Owen SoundWind2090RCP8.5 | Owen Sound | Wind | RCP8.5 | 2090 | 83.8027 | 90.4527 | 97.4985 | 104.4962 | 111.4948
Owen SoundWind2095RCP8.5 | Owen Sound | Wind | RCP8.5 | 2095 | 83.8027 | 90.4527 | 97.4985 | 104.4962 | 111.4948
Owen SoundWind2100RCP8.5 | Owen Sound | Wind | RCP8.5 | 2100 | 83.8027 | 90.4527 | 97.4985 | 104.4962 | 111.4948
Pagwa RiverIce Accretion2023RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2023 | 9.3626 | 11.1676 | 13.468 | 15.2188 | 16.9697
Pagwa RiverIce Accretion2025RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2025 | 9.4259 | 11.245 | 13.5612 | 15.3241 | 17.0898
Pagwa RiverIce Accretion2030RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2030 | 9.4893 | 11.3223 | 13.6543 | 15.4294 | 17.2099
Pagwa RiverIce Accretion2035RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2035 | 9.5526 | 11.3996 | 13.7475 | 15.5347 | 17.33
Pagwa RiverIce Accretion2040RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2040 | 9.6159 | 11.477 | 13.8407 | 15.64 | 17.4502
Pagwa RiverIce Accretion2045RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2045 | 9.6792 | 11.5543 | 13.9338 | 15.7452 | 17.5703
Pagwa RiverIce Accretion2050RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2050 | 9.7624 | 11.6532 | 14.0504 | 15.877 | 17.7166
Pagwa RiverIce Accretion2055RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2055 | 9.7823 | 11.6748 | 14.0738 | 15.9034 | 17.7428
Pagwa RiverIce Accretion2060RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2060 | 9.8022 | 11.6964 | 14.0972 | 15.9298 | 17.769
Pagwa RiverIce Accretion2065RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2065 | 9.8221 | 11.7179 | 14.1206 | 15.9563 | 17.7952
Pagwa RiverIce Accretion2070RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2070 | 9.842 | 11.7395 | 14.144 | 15.9827 | 17.8214
Pagwa RiverIce Accretion2075RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2075 | 9.8405 | 11.7413 | 14.1483 | 15.9901 | 17.8296
Pagwa RiverIce Accretion2080RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2080 | 9.839 | 11.7431 | 14.1527 | 15.9974 | 17.8378
Pagwa RiverIce Accretion2085RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2085 | 9.8375 | 11.7449 | 14.157 | 16.0048 | 17.846
Pagwa RiverIce Accretion2090RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2090 | 9.836 | 11.7467 | 14.1613 | 16.0121 | 17.8542
Pagwa RiverIce Accretion2095RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2095 | 9.8345 | 11.7485 | 14.1657 | 16.0194 | 17.8624
Pagwa RiverIce Accretion2100RCP4.5 | Pagwa River | Ice Accretion | RCP4.5 | 2100 | 9.833 | 11.7503 | 14.17 | 16.0268 | 17.8706
Pagwa RiverIce Accretion2023RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2023 | 9.3626 | 11.1676 | 13.468 | 15.2188 | 16.9697
Pagwa RiverIce Accretion2025RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2025 | 9.4259 | 11.245 | 13.5612 | 15.3241 | 17.0898
Pagwa RiverIce Accretion2030RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2030 | 9.4893 | 11.3223 | 13.6543 | 15.4294 | 17.2099
Pagwa RiverIce Accretion2035RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2035 | 9.5526 | 11.3996 | 13.7475 | 15.5347 | 17.33
Pagwa RiverIce Accretion2040RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2040 | 9.6159 | 11.477 | 13.8407 | 15.64 | 17.4502
Pagwa RiverIce Accretion2045RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2045 | 9.6792 | 11.5543 | 13.9338 | 15.7452 | 17.5703
Pagwa RiverIce Accretion2050RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2050 | 9.7624 | 11.6532 | 14.0504 | 15.877 | 17.7166
Pagwa RiverIce Accretion2055RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2055 | 9.7823 | 11.6748 | 14.0738 | 15.9034 | 17.7428
Pagwa RiverIce Accretion2060RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2060 | 9.8022 | 11.6964 | 14.0972 | 15.9298 | 17.769
Pagwa RiverIce Accretion2065RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2065 | 9.8221 | 11.7179 | 14.1206 | 15.9563 | 17.7952
Pagwa RiverIce Accretion2070RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2070 | 9.842 | 11.7395 | 14.144 | 15.9827 | 17.8214
Pagwa RiverIce Accretion2075RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2075 | 9.8398 | 11.7422 | 14.1505 | 15.9937 | 17.8337
Pagwa RiverIce Accretion2080RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2080 | 9.8375 | 11.7449 | 14.157 | 16.0048 | 17.846
Pagwa RiverIce Accretion2085RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2085 | 9.8353 | 11.7476 | 14.1635 | 16.0158 | 17.8583
Pagwa RiverIce Accretion2090RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2090 | 9.7395 | 11.6388 | 14.0357 | 15.875 | 17.7068
Pagwa RiverIce Accretion2095RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2095 | 9.6461 | 11.5273 | 13.9013 | 15.7232 | 17.543
Pagwa RiverIce Accretion2100RCP6.0 | Pagwa River | Ice Accretion | RCP6.0 | 2100 | 9.5526 | 11.4158 | 13.767 | 15.5714 | 17.3792
Pagwa RiverIce Accretion2023RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2023 | 9.3626 | 11.1676 | 13.468 | 15.2188 | 16.9697
Pagwa RiverIce Accretion2025RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2025 | 9.4893 | 11.3223 | 13.6543 | 15.4294 | 17.2099
Pagwa RiverIce Accretion2030RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2030 | 9.6159 | 11.477 | 13.8407 | 15.64 | 17.4502
Pagwa RiverIce Accretion2035RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2035 | 9.7425 | 11.6316 | 14.027 | 15.8505 | 17.6904
Pagwa RiverIce Accretion2040RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2040 | 9.7757 | 11.6676 | 14.066 | 15.8946 | 17.7341
Pagwa RiverIce Accretion2045RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2045 | 9.8089 | 11.7036 | 14.105 | 15.9386 | 17.7778
Pagwa RiverIce Accretion2050RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2050 | 9.839 | 11.7431 | 14.1527 | 15.9974 | 17.8378
Pagwa RiverIce Accretion2055RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2055 | 9.836 | 11.7467 | 14.1613 | 16.0121 | 17.8542
Pagwa RiverIce Accretion2060RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2060 | 9.7395 | 11.6388 | 14.0357 | 15.875 | 17.7068
Pagwa RiverIce Accretion2065RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2065 | 9.6461 | 11.5273 | 13.9013 | 15.7232 | 17.543
Pagwa RiverIce Accretion2070RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2070 | 9.5254 | 11.3942 | 13.7497 | 15.5567 | 17.3628
Pagwa RiverIce Accretion2075RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2075 | 9.4983 | 11.3727 | 13.7323 | 15.542 | 17.3464
Pagwa RiverIce Accretion2080RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2080 | 9.4712 | 11.3511 | 13.715 | 15.5273 | 17.33
Pagwa RiverIce Accretion2085RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2085 | 9.2812 | 11.1353 | 13.468 | 15.2556 | 17.0352
Pagwa RiverIce Accretion2090RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2090 | 9.0912 | 10.9195 | 13.221 | 14.9838 | 16.7404
Pagwa RiverIce Accretion2095RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2095 | 9.0912 | 10.9195 | 13.221 | 14.9838 | 16.7404
Pagwa RiverIce Accretion2100RCP8.5 | Pagwa River | Ice Accretion | RCP8.5 | 2100 | 9.0912 | 10.9195 | 13.221 | 14.9838 | 16.7404
Pagwa RiverWind2023RCP4.5 | Pagwa River | Wind | RCP4.5 | 2023 | 69.3549 | 74.6381 | 80.184 | 85.7455 | 91.3003
Pagwa RiverWind2025RCP4.5 | Pagwa River | Wind | RCP4.5 | 2025 | 69.4712 | 74.7819 | 80.3627 | 85.9524 | 91.5374
Pagwa RiverWind2030RCP4.5 | Pagwa River | Wind | RCP4.5 | 2030 | 69.5875 | 74.9258 | 80.5413 | 86.1593 | 91.7746
Pagwa RiverWind2035RCP4.5 | Pagwa River | Wind | RCP4.5 | 2035 | 69.7038 | 75.0696 | 80.72 | 86.3661 | 92.0117
Pagwa RiverWind2040RCP4.5 | Pagwa River | Wind | RCP4.5 | 2040 | 69.82 | 75.2134 | 80.8987 | 86.573 | 92.2488
Pagwa RiverWind2045RCP4.5 | Pagwa River | Wind | RCP4.5 | 2045 | 69.9363 | 75.3573 | 81.0773 | 86.7799 | 92.4859
Pagwa RiverWind2050RCP4.5 | Pagwa River | Wind | RCP4.5 | 2050 | 70.1852 | 75.6574 | 81.44 | 87.1973 | 92.9583
Pagwa RiverWind2055RCP4.5 | Pagwa River | Wind | RCP4.5 | 2055 | 70.3179 | 75.8136 | 81.624 | 87.4079 | 93.1936
Pagwa RiverWind2060RCP4.5 | Pagwa River | Wind | RCP4.5 | 2060 | 70.4505 | 75.9698 | 81.808 | 87.6184 | 93.4289
Pagwa RiverWind2065RCP4.5 | Pagwa River | Wind | RCP4.5 | 2065 | 70.5831 | 76.1261 | 81.992 | 87.829 | 93.6642
Pagwa RiverWind2070RCP4.5 | Pagwa River | Wind | RCP4.5 | 2070 | 70.7158 | 76.2823 | 82.176 | 88.0396 | 93.8995
Pagwa RiverWind2075RCP4.5 | Pagwa River | Wind | RCP4.5 | 2075 | 70.7641 | 76.3381 | 82.24 | 88.1109 | 93.9786
Pagwa RiverWind2080RCP4.5 | Pagwa River | Wind | RCP4.5 | 2080 | 70.8125 | 76.3939 | 82.304 | 88.1823 | 94.0576
Pagwa RiverWind2085RCP4.5 | Pagwa River | Wind | RCP4.5 | 2085 | 70.8608 | 76.4497 | 82.368 | 88.2536 | 94.1366
Pagwa RiverWind2090RCP4.5 | Pagwa River | Wind | RCP4.5 | 2090 | 70.9092 | 76.5055 | 82.432 | 88.3249 | 94.2157
Pagwa RiverWind2095RCP4.5 | Pagwa River | Wind | RCP4.5 | 2095 | 70.9575 | 76.5613 | 82.496 | 88.3963 | 94.2947
Pagwa RiverWind2100RCP4.5 | Pagwa River | Wind | RCP4.5 | 2100 | 71.0059 | 76.6171 | 82.56 | 88.4676 | 94.3738
Pagwa RiverWind2023RCP6.0 | Pagwa River | Wind | RCP6.0 | 2023 | 69.3549 | 74.6381 | 80.184 | 85.7455 | 91.3003
Pagwa RiverWind2025RCP6.0 | Pagwa River | Wind | RCP6.0 | 2025 | 69.4712 | 74.7819 | 80.3627 | 85.9524 | 91.5374
Pagwa RiverWind2030RCP6.0 | Pagwa River | Wind | RCP6.0 | 2030 | 69.5875 | 74.9258 | 80.5413 | 86.1593 | 91.7746
Pagwa RiverWind2035RCP6.0 | Pagwa River | Wind | RCP6.0 | 2035 | 69.7038 | 75.0696 | 80.72 | 86.3661 | 92.0117
Pagwa RiverWind2040RCP6.0 | Pagwa River | Wind | RCP6.0 | 2040 | 69.82 | 75.2134 | 80.8987 | 86.573 | 92.2488
Pagwa RiverWind2045RCP6.0 | Pagwa River | Wind | RCP6.0 | 2045 | 69.9363 | 75.3573 | 81.0773 | 86.7799 | 92.4859
Pagwa RiverWind2050RCP6.0 | Pagwa River | Wind | RCP6.0 | 2050 | 70.1852 | 75.6574 | 81.44 | 87.1973 | 92.9583
Pagwa RiverWind2055RCP6.0 | Pagwa River | Wind | RCP6.0 | 2055 | 70.3179 | 75.8136 | 81.624 | 87.4079 | 93.1936
Pagwa RiverWind2060RCP6.0 | Pagwa River | Wind | RCP6.0 | 2060 | 70.4505 | 75.9698 | 81.808 | 87.6184 | 93.4289
Pagwa RiverWind2065RCP6.0 | Pagwa River | Wind | RCP6.0 | 2065 | 70.5831 | 76.1261 | 81.992 | 87.829 | 93.6642
Pagwa RiverWind2070RCP6.0 | Pagwa River | Wind | RCP6.0 | 2070 | 70.7158 | 76.2823 | 82.176 | 88.0396 | 93.8995
Pagwa RiverWind2075RCP6.0 | Pagwa River | Wind | RCP6.0 | 2075 | 70.7883 | 76.366 | 82.272 | 88.1466 | 94.0181
Pagwa RiverWind2080RCP6.0 | Pagwa River | Wind | RCP6.0 | 2080 | 70.8608 | 76.4497 | 82.368 | 88.2536 | 94.1366
Pagwa RiverWind2085RCP6.0 | Pagwa River | Wind | RCP6.0 | 2085 | 70.9334 | 76.5334 | 82.464 | 88.3606 | 94.2552
Pagwa RiverWind2090RCP6.0 | Pagwa River | Wind | RCP6.0 | 2090 | 71.0427 | 76.6494 | 82.584 | 88.4847 | 94.3859
Pagwa RiverWind2095RCP6.0 | Pagwa River | Wind | RCP6.0 | 2095 | 71.0796 | 76.6816 | 82.608 | 88.5018 | 94.3981
Pagwa RiverWind2100RCP6.0 | Pagwa River | Wind | RCP6.0 | 2100 | 71.1164 | 76.7138 | 82.632 | 88.519 | 94.4102
Pagwa RiverWind2023RCP8.5 | Pagwa River | Wind | RCP8.5 | 2023 | 69.3549 | 74.6381 | 80.184 | 85.7455 | 91.3003
Pagwa RiverWind2025RCP8.5 | Pagwa River | Wind | RCP8.5 | 2025 | 69.5875 | 74.9258 | 80.5413 | 86.1593 | 91.7746
Pagwa RiverWind2030RCP8.5 | Pagwa River | Wind | RCP8.5 | 2030 | 69.82 | 75.2134 | 80.8987 | 86.573 | 92.2488
Pagwa RiverWind2035RCP8.5 | Pagwa River | Wind | RCP8.5 | 2035 | 70.0526 | 75.5011 | 81.256 | 86.9867 | 92.723
Pagwa RiverWind2040RCP8.5 | Pagwa River | Wind | RCP8.5 | 2040 | 70.2737 | 75.7615 | 81.5627 | 87.3377 | 93.1152
Pagwa RiverWind2045RCP8.5 | Pagwa River | Wind | RCP8.5 | 2045 | 70.4947 | 76.0219 | 81.8693 | 87.6886 | 93.5074
Pagwa RiverWind2050RCP8.5 | Pagwa River | Wind | RCP8.5 | 2050 | 70.8125 | 76.3939 | 82.304 | 88.1823 | 94.0576
Pagwa RiverWind2055RCP8.5 | Pagwa River | Wind | RCP8.5 | 2055 | 70.9092 | 76.5055 | 82.432 | 88.3249 | 94.2157
Pagwa RiverWind2060RCP8.5 | Pagwa River | Wind | RCP8.5 | 2060 | 71.0427 | 76.6494 | 82.584 | 88.4847 | 94.3859
Pagwa RiverWind2065RCP8.5 | Pagwa River | Wind | RCP8.5 | 2065 | 71.0796 | 76.6816 | 82.608 | 88.5018 | 94.3981
Pagwa RiverWind2070RCP8.5 | Pagwa River | Wind | RCP8.5 | 2070 | 71.1371 | 76.7386 | 82.6613 | 88.5503 | 94.4467
Pagwa RiverWind2075RCP8.5 | Pagwa River | Wind | RCP8.5 | 2075 | 71.1579 | 76.7634 | 82.6907 | 88.5817 | 94.4832
Pagwa RiverWind2080RCP8.5 | Pagwa River | Wind | RCP8.5 | 2080 | 71.1786 | 76.7882 | 82.72 | 88.6131 | 94.5197
Pagwa RiverWind2085RCP8.5 | Pagwa River | Wind | RCP8.5 | 2085 | 71.3271 | 76.9631 | 82.928 | 88.8528 | 94.7842
Pagwa RiverWind2090RCP8.5 | Pagwa River | Wind | RCP8.5 | 2090 | 71.4756 | 77.1379 | 83.136 | 89.0925 | 95.0486
Pagwa RiverWind2095RCP8.5 | Pagwa River | Wind | RCP8.5 | 2095 | 71.4756 | 77.1379 | 83.136 | 89.0925 | 95.0486
Pagwa RiverWind2100RCP8.5 | Pagwa River | Wind | RCP8.5 | 2100 | 71.4756 | 77.1379 | 83.136 | 89.0925 | 95.0486
ParisIce Accretion2023RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
ParisIce Accretion2025RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2025 | 20.3952 | 24.4642 | 29.605 | 33.5328 | 37.4661
ParisIce Accretion2030RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2030 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
ParisIce Accretion2035RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2035 | 20.3117 | 24.3895 | 29.535 | 33.4763 | 37.4031
ParisIce Accretion2040RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2040 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
ParisIce Accretion2045RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2045 | 20.2282 | 24.3148 | 29.465 | 33.4198 | 37.3401
ParisIce Accretion2050RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2050 | 20.0571 | 24.153 | 29.316 | 33.2762 | 37.2028
ParisIce Accretion2055RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2055 | 19.9276 | 24.0285 | 29.202 | 33.161 | 37.0969
ParisIce Accretion2060RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2060 | 19.7982 | 23.904 | 29.088 | 33.0457 | 36.9911
ParisIce Accretion2065RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2065 | 19.6688 | 23.7795 | 28.974 | 32.9305 | 36.8852
ParisIce Accretion2070RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2070 | 19.5394 | 23.655 | 28.86 | 32.8152 | 36.7794
ParisIce Accretion2075RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2075 | 19.4837 | 23.6135 | 28.84 | 32.8095 | 36.7857
ParisIce Accretion2080RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2080 | 19.428 | 23.572 | 28.82 | 32.8039 | 36.792
ParisIce Accretion2085RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2085 | 19.3724 | 23.5305 | 28.8 | 32.7982 | 36.7983
ParisIce Accretion2090RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2090 | 19.3167 | 23.489 | 28.78 | 32.7926 | 36.8046
ParisIce Accretion2095RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2095 | 19.261 | 23.4475 | 28.76 | 32.7869 | 36.8109
ParisIce Accretion2100RCP4.5 | Paris | Ice Accretion | RCP4.5 | 2100 | 19.2054 | 23.406 | 28.74 | 32.7813 | 36.8172
ParisIce Accretion2023RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
ParisIce Accretion2025RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2025 | 20.3952 | 24.4642 | 29.605 | 33.5328 | 37.4661
ParisIce Accretion2030RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2030 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
ParisIce Accretion2035RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2035 | 20.3117 | 24.3895 | 29.535 | 33.4763 | 37.4031
ParisIce Accretion2040RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2040 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
ParisIce Accretion2045RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2045 | 20.2282 | 24.3148 | 29.465 | 33.4198 | 37.3401
ParisIce Accretion2050RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2050 | 20.0571 | 24.153 | 29.316 | 33.2762 | 37.2028
ParisIce Accretion2055RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2055 | 19.9276 | 24.0285 | 29.202 | 33.161 | 37.0969
ParisIce Accretion2060RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2060 | 19.7982 | 23.904 | 29.088 | 33.0457 | 36.9911
ParisIce Accretion2065RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2065 | 19.6688 | 23.7795 | 28.974 | 32.9305 | 36.8852
ParisIce Accretion2070RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2070 | 19.5394 | 23.655 | 28.86 | 32.8152 | 36.7794
ParisIce Accretion2075RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2075 | 19.4559 | 23.5927 | 28.83 | 32.8067 | 36.7888
ParisIce Accretion2080RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2080 | 19.3724 | 23.5305 | 28.8 | 32.7982 | 36.7983
ParisIce Accretion2085RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2085 | 19.2889 | 23.4682 | 28.77 | 32.7898 | 36.8077
ParisIce Accretion2090RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2090 | 18.7739 | 22.9412 | 28.21 | 32.2163 | 36.1998
ParisIce Accretion2095RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2095 | 18.3425 | 22.4764 | 27.68 | 31.6513 | 35.5824
ParisIce Accretion2100RCP6.0 | Paris | Ice Accretion | RCP6.0 | 2100 | 17.9111 | 22.0116 | 27.15 | 31.0863 | 34.965
ParisIce Accretion2023RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
ParisIce Accretion2025RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2025 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
ParisIce Accretion2030RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2030 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
ParisIce Accretion2035RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2035 | 20.1865 | 24.2775 | 29.43 | 33.3915 | 37.3086
ParisIce Accretion2040RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2040 | 19.9708 | 24.07 | 29.24 | 33.1994 | 37.1322
ParisIce Accretion2045RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2045 | 19.7551 | 23.8625 | 29.05 | 33.0073 | 36.9558
ParisIce Accretion2050RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2050 | 19.428 | 23.572 | 28.82 | 32.8039 | 36.792
ParisIce Accretion2055RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2055 | 19.3167 | 23.489 | 28.78 | 32.7926 | 36.8046
ParisIce Accretion2060RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2060 | 18.7739 | 22.9412 | 28.21 | 32.2163 | 36.1998
ParisIce Accretion2065RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2065 | 18.3425 | 22.4764 | 27.68 | 31.6513 | 35.5824
ParisIce Accretion2070RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2070 | 17.5353 | 21.6049 | 26.71 | 30.6117 | 34.461
ParisIce Accretion2075RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2075 | 17.1596 | 21.1982 | 26.27 | 30.1371 | 33.957
ParisIce Accretion2080RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2080 | 16.7838 | 20.7915 | 25.83 | 29.6625 | 33.453
ParisIce Accretion2085RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2085 | 15.8549 | 19.7208 | 24.57 | 28.2387 | 31.9032
ParisIce Accretion2090RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2090 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
ParisIce Accretion2095RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2095 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
ParisIce Accretion2100RCP8.5 | Paris | Ice Accretion | RCP8.5 | 2100 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
ParisWind2023RCP4.5 | Paris | Wind | RCP4.5 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
ParisWind2025RCP4.5 | Paris | Wind | RCP4.5 | 2025 | 87.206 | 94.102 | 101.4083 | 108.6746 | 115.9494
ParisWind2030RCP4.5 | Paris | Wind | RCP4.5 | 2030 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
ParisWind2035RCP4.5 | Paris | Wind | RCP4.5 | 2035 | 87.3672 | 94.316 | 101.685 | 109.0063 | 116.337
ParisWind2040RCP4.5 | Paris | Wind | RCP4.5 | 2040 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
ParisWind2045RCP4.5 | Paris | Wind | RCP4.5 | 2045 | 87.5283 | 94.5299 | 101.9617 | 109.338 | 116.7246
ParisWind2050RCP4.5 | Paris | Wind | RCP4.5 | 2050 | 87.678 | 94.7205 | 102.206 | 109.6258 | 117.0575
ParisWind2055RCP4.5 | Paris | Wind | RCP4.5 | 2055 | 87.7471 | 94.8042 | 102.312 | 109.7478 | 117.1966
ParisWind2060RCP4.5 | Paris | Wind | RCP4.5 | 2060 | 87.8162 | 94.8879 | 102.418 | 109.8697 | 117.3356
ParisWind2065RCP4.5 | Paris | Wind | RCP4.5 | 2065 | 87.8852 | 94.9716 | 102.524 | 109.9917 | 117.4747
ParisWind2070RCP4.5 | Paris | Wind | RCP4.5 | 2070 | 87.9543 | 95.0553 | 102.63 | 110.1137 | 117.6138
ParisWind2075RCP4.5 | Paris | Wind | RCP4.5 | 2075 | 88.0407 | 95.1746 | 102.7917 | 110.3117 | 117.8494
ParisWind2080RCP4.5 | Paris | Wind | RCP4.5 | 2080 | 88.127 | 95.294 | 102.9533 | 110.5096 | 118.085
ParisWind2085RCP4.5 | Paris | Wind | RCP4.5 | 2085 | 88.2134 | 95.4134 | 103.115 | 110.7075 | 118.3206
ParisWind2090RCP4.5 | Paris | Wind | RCP4.5 | 2090 | 88.2997 | 95.5327 | 103.2767 | 110.9055 | 118.5562
ParisWind2095RCP4.5 | Paris | Wind | RCP4.5 | 2095 | 88.3861 | 95.6521 | 103.4383 | 111.1034 | 118.7918
ParisWind2100RCP4.5 | Paris | Wind | RCP4.5 | 2100 | 88.4724 | 95.7714 | 103.6 | 111.3014 | 119.0274
ParisWind2023RCP6.0 | Paris | Wind | RCP6.0 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
ParisWind2025RCP6.0 | Paris | Wind | RCP6.0 | 2025 | 87.206 | 94.102 | 101.4083 | 108.6746 | 115.9494
ParisWind2030RCP6.0 | Paris | Wind | RCP6.0 | 2030 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
ParisWind2035RCP6.0 | Paris | Wind | RCP6.0 | 2035 | 87.3672 | 94.316 | 101.685 | 109.0063 | 116.337
ParisWind2040RCP6.0 | Paris | Wind | RCP6.0 | 2040 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
ParisWind2045RCP6.0 | Paris | Wind | RCP6.0 | 2045 | 87.5283 | 94.5299 | 101.9617 | 109.338 | 116.7246
ParisWind2050RCP6.0 | Paris | Wind | RCP6.0 | 2050 | 87.678 | 94.7205 | 102.206 | 109.6258 | 117.0575
ParisWind2055RCP6.0 | Paris | Wind | RCP6.0 | 2055 | 87.7471 | 94.8042 | 102.312 | 109.7478 | 117.1966
ParisWind2060RCP6.0 | Paris | Wind | RCP6.0 | 2060 | 87.8162 | 94.8879 | 102.418 | 109.8697 | 117.3356
ParisWind2065RCP6.0 | Paris | Wind | RCP6.0 | 2065 | 87.8852 | 94.9716 | 102.524 | 109.9917 | 117.4747
ParisWind2070RCP6.0 | Paris | Wind | RCP6.0 | 2070 | 87.9543 | 95.0553 | 102.63 | 110.1137 | 117.6138
ParisWind2075RCP6.0 | Paris | Wind | RCP6.0 | 2075 | 88.0838 | 95.2343 | 102.8725 | 110.4106 | 117.9672
ParisWind2080RCP6.0 | Paris | Wind | RCP6.0 | 2080 | 88.2134 | 95.4134 | 103.115 | 110.7075 | 118.3206
ParisWind2085RCP6.0 | Paris | Wind | RCP6.0 | 2085 | 88.3429 | 95.5924 | 103.3575 | 111.0045 | 118.674
ParisWind2090RCP6.0 | Paris | Wind | RCP6.0 | 2090 | 88.8264 | 96.2271 | 104.18 | 111.9862 | 119.8216
ParisWind2095RCP6.0 | Paris | Wind | RCP6.0 | 2095 | 89.1805 | 96.6828 | 104.76 | 112.671 | 120.6158
ParisWind2100RCP6.0 | Paris | Wind | RCP6.0 | 2100 | 89.5345 | 97.1385 | 105.34 | 113.3558 | 121.41
ParisWind2023RCP8.5 | Paris | Wind | RCP8.5 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
ParisWind2025RCP8.5 | Paris | Wind | RCP8.5 | 2025 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
ParisWind2030RCP8.5 | Paris | Wind | RCP8.5 | 2030 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
ParisWind2035RCP8.5 | Paris | Wind | RCP8.5 | 2035 | 87.6089 | 94.6368 | 102.1 | 109.5038 | 116.9184
ParisWind2040RCP8.5 | Paris | Wind | RCP8.5 | 2040 | 87.7241 | 94.7763 | 102.2767 | 109.7071 | 117.1502
ParisWind2045RCP8.5 | Paris | Wind | RCP8.5 | 2045 | 87.8392 | 94.9158 | 102.4533 | 109.9104 | 117.382
ParisWind2050RCP8.5 | Paris | Wind | RCP8.5 | 2050 | 88.127 | 95.294 | 102.9533 | 110.5096 | 118.085
ParisWind2055RCP8.5 | Paris | Wind | RCP8.5 | 2055 | 88.2997 | 95.5327 | 103.2767 | 110.9055 | 118.5562
ParisWind2060RCP8.5 | Paris | Wind | RCP8.5 | 2060 | 88.8264 | 96.2271 | 104.18 | 111.9862 | 119.8216
ParisWind2065RCP8.5 | Paris | Wind | RCP8.5 | 2065 | 89.1805 | 96.6828 | 104.76 | 112.671 | 120.6158
ParisWind2070RCP8.5 | Paris | Wind | RCP8.5 | 2070 | 89.759 | 97.4392 | 105.7367 | 113.8337 | 121.9724
ParisWind2075RCP8.5 | Paris | Wind | RCP8.5 | 2075 | 89.9835 | 97.7399 | 106.1333 | 114.3117 | 122.5348
ParisWind2080RCP8.5 | Paris | Wind | RCP8.5 | 2080 | 90.208 | 98.0406 | 106.53 | 114.7896 | 123.0972
ParisWind2085RCP8.5 | Paris | Wind | RCP8.5 | 2085 | 90.6484 | 98.6172 | 107.285 | 115.6937 | 124.1517
ParisWind2090RCP8.5 | Paris | Wind | RCP8.5 | 2090 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
ParisWind2095RCP8.5 | Paris | Wind | RCP8.5 | 2095 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
ParisWind2100RCP8.5 | Paris | Wind | RCP8.5 | 2100 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
ParkhillIce Accretion2023RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2023 | 16.4331 | 19.7009 | 23.808 | 26.9573 | 30.0888
ParkhillIce Accretion2025RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2025 | 16.4498 | 19.7341 | 23.868 | 27.0341 | 30.1846
ParkhillIce Accretion2030RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2030 | 16.4665 | 19.7673 | 23.928 | 27.111 | 30.2803
ParkhillIce Accretion2035RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2035 | 16.4832 | 19.8005 | 23.988 | 27.1878 | 30.3761
ParkhillIce Accretion2040RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2040 | 16.4999 | 19.8337 | 24.048 | 27.2646 | 30.4718
ParkhillIce Accretion2045RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2045 | 16.5166 | 19.8669 | 24.108 | 27.3415 | 30.5676
ParkhillIce Accretion2050RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2050 | 16.4665 | 19.8523 | 24.1392 | 27.402 | 30.6634
ParkhillIce Accretion2055RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2055 | 16.3997 | 19.8045 | 24.1104 | 27.3858 | 30.6634
ParkhillIce Accretion2060RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2060 | 16.3329 | 19.7567 | 24.0816 | 27.3695 | 30.6634
ParkhillIce Accretion2065RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2065 | 16.2661 | 19.7088 | 24.0528 | 27.3532 | 30.6634
ParkhillIce Accretion2070RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2070 | 16.1993 | 19.661 | 24.024 | 27.337 | 30.6634
ParkhillIce Accretion2075RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2075 | 16.1687 | 19.6478 | 24.036 | 27.3641 | 30.7087
ParkhillIce Accretion2080RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2080 | 16.1381 | 19.6345 | 24.048 | 27.3912 | 30.7541
ParkhillIce Accretion2085RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2085 | 16.1074 | 19.6212 | 24.06 | 27.4183 | 30.7994
ParkhillIce Accretion2090RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2090 | 16.0768 | 19.6079 | 24.072 | 27.4454 | 30.8448
ParkhillIce Accretion2095RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2095 | 16.0462 | 19.5946 | 24.084 | 27.4726 | 30.8902
ParkhillIce Accretion2100RCP4.5 | Parkhill | Ice Accretion | RCP4.5 | 2100 | 16.0156 | 19.5814 | 24.096 | 27.4997 | 30.9355
ParkhillIce Accretion2023RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2023 | 16.4331 | 19.7009 | 23.808 | 26.9573 | 30.0888
ParkhillIce Accretion2025RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2025 | 16.4498 | 19.7341 | 23.868 | 27.0341 | 30.1846
ParkhillIce Accretion2030RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2030 | 16.4665 | 19.7673 | 23.928 | 27.111 | 30.2803
ParkhillIce Accretion2035RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2035 | 16.4832 | 19.8005 | 23.988 | 27.1878 | 30.3761
ParkhillIce Accretion2040RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2040 | 16.4999 | 19.8337 | 24.048 | 27.2646 | 30.4718
ParkhillIce Accretion2045RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2045 | 16.5166 | 19.8669 | 24.108 | 27.3415 | 30.5676
ParkhillIce Accretion2050RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2050 | 16.4665 | 19.8523 | 24.1392 | 27.402 | 30.6634
ParkhillIce Accretion2055RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2055 | 16.3997 | 19.8045 | 24.1104 | 27.3858 | 30.6634
ParkhillIce Accretion2060RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2060 | 16.3329 | 19.7567 | 24.0816 | 27.3695 | 30.6634
ParkhillIce Accretion2065RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2065 | 16.2661 | 19.7088 | 24.0528 | 27.3532 | 30.6634
ParkhillIce Accretion2070RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2070 | 16.1993 | 19.661 | 24.024 | 27.337 | 30.6634
ParkhillIce Accretion2075RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2075 | 16.1534 | 19.6411 | 24.042 | 27.3776 | 30.7314
ParkhillIce Accretion2080RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2080 | 16.1074 | 19.6212 | 24.06 | 27.4183 | 30.7994
ParkhillIce Accretion2085RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2085 | 16.0615 | 19.6013 | 24.078 | 27.459 | 30.8675
ParkhillIce Accretion2090RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2090 | 15.8152 | 19.3822 | 23.888 | 27.2918 | 30.7138
ParkhillIce Accretion2095RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2095 | 15.6148 | 19.183 | 23.68 | 27.0838 | 30.492
ParkhillIce Accretion2100RCP6.0 | Parkhill | Ice Accretion | RCP6.0 | 2100 | 15.4144 | 18.9838 | 23.472 | 26.8759 | 30.2702
ParkhillIce Accretion2023RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2023 | 16.4331 | 19.7009 | 23.808 | 26.9573 | 30.0888
ParkhillIce Accretion2025RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2025 | 16.4665 | 19.7673 | 23.928 | 27.111 | 30.2803
ParkhillIce Accretion2030RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2030 | 16.4999 | 19.8337 | 24.048 | 27.2646 | 30.4718
ParkhillIce Accretion2035RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2035 | 16.5333 | 19.9001 | 24.168 | 27.4183 | 30.6634
ParkhillIce Accretion2040RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2040 | 16.422 | 19.8204 | 24.12 | 27.3912 | 30.6634
ParkhillIce Accretion2045RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2045 | 16.3106 | 19.7407 | 24.072 | 27.3641 | 30.6634
ParkhillIce Accretion2050RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2050 | 16.1381 | 19.6345 | 24.048 | 27.3912 | 30.7541
ParkhillIce Accretion2055RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2055 | 16.0768 | 19.6079 | 24.072 | 27.4454 | 30.8448
ParkhillIce Accretion2060RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2060 | 15.8152 | 19.3822 | 23.888 | 27.2918 | 30.7138
ParkhillIce Accretion2065RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2065 | 15.6148 | 19.183 | 23.68 | 27.0838 | 30.492
ParkhillIce Accretion2070RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2070 | 15.0525 | 18.5787 | 23.016 | 26.3787 | 29.7259
ParkhillIce Accretion2075RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2075 | 14.6907 | 18.1737 | 22.56 | 25.8815 | 29.1816
ParkhillIce Accretion2080RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2080 | 14.3289 | 17.7686 | 22.104 | 25.3843 | 28.6373
ParkhillIce Accretion2085RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2085 | 13.5773 | 16.8822 | 21.048 | 24.2046 | 27.337
ParkhillIce Accretion2090RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2090 | 12.8258 | 15.9958 | 19.992 | 23.0249 | 26.0366
ParkhillIce Accretion2095RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2095 | 12.8258 | 15.9958 | 19.992 | 23.0249 | 26.0366
ParkhillIce Accretion2100RCP8.5 | Parkhill | Ice Accretion | RCP8.5 | 2100 | 12.8258 | 15.9958 | 19.992 | 23.0249 | 26.0366
ParkhillWind2023RCP4.5 | Parkhill | Wind | RCP4.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
ParkhillWind2025RCP4.5 | Parkhill | Wind | RCP4.5 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
ParkhillWind2030RCP4.5 | Parkhill | Wind | RCP4.5 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
ParkhillWind2035RCP4.5 | Parkhill | Wind | RCP4.5 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
ParkhillWind2040RCP4.5 | Parkhill | Wind | RCP4.5 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
ParkhillWind2045RCP4.5 | Parkhill | Wind | RCP4.5 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
ParkhillWind2050RCP4.5 | Parkhill | Wind | RCP4.5 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
ParkhillWind2055RCP4.5 | Parkhill | Wind | RCP4.5 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
ParkhillWind2060RCP4.5 | Parkhill | Wind | RCP4.5 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
ParkhillWind2065RCP4.5 | Parkhill | Wind | RCP4.5 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
ParkhillWind2070RCP4.5 | Parkhill | Wind | RCP4.5 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
ParkhillWind2075RCP4.5 | Parkhill | Wind | RCP4.5 | 2075 | 86.3504 | 93.3577 | 100.8387 | 108.226 | 115.6228
ParkhillWind2080RCP4.5 | Parkhill | Wind | RCP4.5 | 2080 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
ParkhillWind2085RCP4.5 | Parkhill | Wind | RCP4.5 | 2085 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
ParkhillWind2090RCP4.5 | Parkhill | Wind | RCP4.5 | 2090 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
ParkhillWind2095RCP4.5 | Parkhill | Wind | RCP4.5 | 2095 | 86.7678 | 93.9167 | 101.5705 | 109.1068 | 116.6655
ParkhillWind2100RCP4.5 | Parkhill | Wind | RCP4.5 | 2100 | 86.8722 | 94.0565 | 101.7534 | 109.327 | 116.9262
ParkhillWind2023RCP6.0 | Parkhill | Wind | RCP6.0 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
ParkhillWind2025RCP6.0 | Parkhill | Wind | RCP6.0 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
ParkhillWind2030RCP6.0 | Parkhill | Wind | RCP6.0 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
ParkhillWind2035RCP6.0 | Parkhill | Wind | RCP6.0 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
ParkhillWind2040RCP6.0 | Parkhill | Wind | RCP6.0 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
ParkhillWind2045RCP6.0 | Parkhill | Wind | RCP6.0 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
ParkhillWind2050RCP6.0 | Parkhill | Wind | RCP6.0 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
ParkhillWind2055RCP6.0 | Parkhill | Wind | RCP6.0 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
ParkhillWind2060RCP6.0 | Parkhill | Wind | RCP6.0 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
ParkhillWind2065RCP6.0 | Parkhill | Wind | RCP6.0 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
ParkhillWind2070RCP6.0 | Parkhill | Wind | RCP6.0 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
ParkhillWind2075RCP6.0 | Parkhill | Wind | RCP6.0 | 2075 | 86.4026 | 93.4276 | 100.9302 | 108.3361 | 115.7531
ParkhillWind2080RCP6.0 | Parkhill | Wind | RCP6.0 | 2080 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
ParkhillWind2085RCP6.0 | Parkhill | Wind | RCP6.0 | 2085 | 86.7157 | 93.8469 | 101.479 | 108.9967 | 116.5351
ParkhillWind2090RCP6.0 | Parkhill | Wind | RCP6.0 | 2090 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
ParkhillWind2095RCP6.0 | Parkhill | Wind | RCP6.0 | 2095 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
ParkhillWind2100RCP6.0 | Parkhill | Wind | RCP6.0 | 2100 | 87.7861 | 95.1502 | 103.0568 | 110.8265 | 118.6131
ParkhillWind2023RCP8.5 | Parkhill | Wind | RCP8.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
ParkhillWind2025RCP8.5 | Parkhill | Wind | RCP8.5 | 2025 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
ParkhillWind2030RCP8.5 | Parkhill | Wind | RCP8.5 | 2030 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
ParkhillWind2035RCP8.5 | Parkhill | Wind | RCP8.5 | 2035 | 86.0768 | 93.0084 | 100.3912 | 107.7017 | 115.0269
ParkhillWind2040RCP8.5 | Parkhill | Wind | RCP8.5 | 2040 | 86.1332 | 93.0782 | 100.4794 | 107.8031 | 115.1386
ParkhillWind2045RCP8.5 | Parkhill | Wind | RCP8.5 | 2045 | 86.1896 | 93.1481 | 100.5676 | 107.9044 | 115.2504
ParkhillWind2050RCP8.5 | Parkhill | Wind | RCP8.5 | 2050 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
ParkhillWind2055RCP8.5 | Parkhill | Wind | RCP8.5 | 2055 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
ParkhillWind2060RCP8.5 | Parkhill | Wind | RCP8.5 | 2060 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
ParkhillWind2065RCP8.5 | Parkhill | Wind | RCP8.5 | 2065 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
ParkhillWind2070RCP8.5 | Parkhill | Wind | RCP8.5 | 2070 | 88.0541 | 95.5026 | 103.5207 | 111.3788 | 119.2611
ParkhillWind2075RCP8.5 | Parkhill | Wind | RCP8.5 | 2075 | 88.322 | 95.855 | 103.9845 | 111.9311 | 119.9091
ParkhillWind2080RCP8.5 | Parkhill | Wind | RCP8.5 | 2080 | 88.59 | 96.2074 | 104.4484 | 112.4833 | 120.5571
ParkhillWind2085RCP8.5 | Parkhill | Wind | RCP8.5 | 2085 | 88.9454 | 96.6585 | 105.0217 | 113.1649 | 121.3447
ParkhillWind2090RCP8.5 | Parkhill | Wind | RCP8.5 | 2090 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
ParkhillWind2095RCP8.5 | Parkhill | Wind | RCP8.5 | 2095 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
ParkhillWind2100RCP8.5 | Parkhill | Wind | RCP8.5 | 2100 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
Parry SoundIce Accretion2023RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2023 | 14.0839 | 16.8324 | 20.32 | 22.9842 | 25.6536
Parry SoundIce Accretion2025RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2025 | 14.1396 | 16.9126 | 20.4333 | 23.1198 | 25.8132
Parry SoundIce Accretion2030RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2030 | 14.1953 | 16.9929 | 20.5467 | 23.2554 | 25.9728
Parry SoundIce Accretion2035RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2035 | 14.2509 | 17.0731 | 20.66 | 23.391 | 26.1324
Parry SoundIce Accretion2040RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2040 | 14.3066 | 17.1533 | 20.7733 | 23.5266 | 26.292
Parry SoundIce Accretion2045RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2045 | 14.3623 | 17.2336 | 20.8867 | 23.6622 | 26.4516
Parry SoundIce Accretion2050RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2050 | 14.4179 | 17.3304 | 21.032 | 23.843 | 26.6717
Parry SoundIce Accretion2055RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2055 | 14.4179 | 17.347 | 21.064 | 23.8882 | 26.7322
Parry SoundIce Accretion2060RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2060 | 14.4179 | 17.3636 | 21.096 | 23.9334 | 26.7926
Parry SoundIce Accretion2065RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2065 | 14.4179 | 17.3802 | 21.128 | 23.9786 | 26.8531
Parry SoundIce Accretion2070RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2070 | 14.4179 | 17.3968 | 21.16 | 24.0238 | 26.9136
Parry SoundIce Accretion2075RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2075 | 14.4643 | 17.466 | 21.26 | 24.1443 | 27.0522
Parry SoundIce Accretion2080RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2080 | 14.5107 | 17.5351 | 21.36 | 24.2649 | 27.1908
Parry SoundIce Accretion2085RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2085 | 14.5571 | 17.6043 | 21.46 | 24.3854 | 27.3294
Parry SoundIce Accretion2090RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2090 | 14.6035 | 17.6735 | 21.56 | 24.5059 | 27.468
Parry SoundIce Accretion2095RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2095 | 14.6499 | 17.7426 | 21.66 | 24.6265 | 27.6066
Parry SoundIce Accretion2100RCP4.5 | Parry Sound | Ice Accretion | RCP4.5 | 2100 | 14.6963 | 17.8118 | 21.76 | 24.747 | 27.7452
Parry SoundIce Accretion2023RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2023 | 14.0839 | 16.8324 | 20.32 | 22.9842 | 25.6536
Parry SoundIce Accretion2025RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2025 | 14.1396 | 16.9126 | 20.4333 | 23.1198 | 25.8132
Parry SoundIce Accretion2030RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2030 | 14.1953 | 16.9929 | 20.5467 | 23.2554 | 25.9728
Parry SoundIce Accretion2035RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2035 | 14.2509 | 17.0731 | 20.66 | 23.391 | 26.1324
Parry SoundIce Accretion2040RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2040 | 14.3066 | 17.1533 | 20.7733 | 23.5266 | 26.292
Parry SoundIce Accretion2045RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2045 | 14.3623 | 17.2336 | 20.8867 | 23.6622 | 26.4516
Parry SoundIce Accretion2050RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2050 | 14.4179 | 17.3304 | 21.032 | 23.843 | 26.6717
Parry SoundIce Accretion2055RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2055 | 14.4179 | 17.347 | 21.064 | 23.8882 | 26.7322
Parry SoundIce Accretion2060RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2060 | 14.4179 | 17.3636 | 21.096 | 23.9334 | 26.7926
Parry SoundIce Accretion2065RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2065 | 14.4179 | 17.3802 | 21.128 | 23.9786 | 26.8531
Parry SoundIce Accretion2070RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2070 | 14.4179 | 17.3968 | 21.16 | 24.0238 | 26.9136
Parry SoundIce Accretion2075RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2075 | 14.4875 | 17.5005 | 21.31 | 24.2046 | 27.1215
Parry SoundIce Accretion2080RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2080 | 14.5571 | 17.6043 | 21.46 | 24.3854 | 27.3294
Parry SoundIce Accretion2085RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2085 | 14.6267 | 17.7081 | 21.61 | 24.5662 | 27.5373
Parry SoundIce Accretion2090RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2090 | 14.6592 | 17.8063 | 21.78 | 24.7997 | 27.8208
Parry SoundIce Accretion2095RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2095 | 14.622 | 17.8007 | 21.8 | 24.8525 | 27.8964
Parry SoundIce Accretion2100RCP6.0 | Parry Sound | Ice Accretion | RCP6.0 | 2100 | 14.5849 | 17.7952 | 21.82 | 24.9052 | 27.972
Parry SoundIce Accretion2023RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2023 | 14.0839 | 16.8324 | 20.32 | 22.9842 | 25.6536
Parry SoundIce Accretion2025RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2025 | 14.1953 | 16.9929 | 20.5467 | 23.2554 | 25.9728
Parry SoundIce Accretion2030RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2030 | 14.3066 | 17.1533 | 20.7733 | 23.5266 | 26.292
Parry SoundIce Accretion2035RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2035 | 14.4179 | 17.3138 | 21 | 23.7978 | 26.6112
Parry SoundIce Accretion2040RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2040 | 14.4179 | 17.3415 | 21.0533 | 23.8731 | 26.712
Parry SoundIce Accretion2045RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2045 | 14.4179 | 17.3691 | 21.1067 | 23.9485 | 26.8128
Parry SoundIce Accretion2050RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2050 | 14.5107 | 17.5351 | 21.36 | 24.2649 | 27.1908
Parry SoundIce Accretion2055RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2055 | 14.6035 | 17.6735 | 21.56 | 24.5059 | 27.468
Parry SoundIce Accretion2060RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2060 | 14.6592 | 17.8063 | 21.78 | 24.7997 | 27.8208
Parry SoundIce Accretion2065RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2065 | 14.622 | 17.8007 | 21.8 | 24.8525 | 27.8964
Parry SoundIce Accretion2070RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2070 | 14.3205 | 17.4964 | 21.4867 | 24.5361 | 27.5688
Parry SoundIce Accretion2075RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2075 | 14.0561 | 17.1976 | 21.1533 | 24.1669 | 27.1656
Parry SoundIce Accretion2080RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2080 | 13.7917 | 16.8988 | 20.82 | 23.7978 | 26.7624
Parry SoundIce Accretion2085RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2085 | 13.235 | 16.2514 | 20.06 | 22.9616 | 25.8426
Parry SoundIce Accretion2090RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2090 | 12.6783 | 15.604 | 19.3 | 22.1254 | 24.9228
Parry SoundIce Accretion2095RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2095 | 12.6783 | 15.604 | 19.3 | 22.1254 | 24.9228
Parry SoundIce Accretion2100RCP8.5 | Parry Sound | Ice Accretion | RCP8.5 | 2100 | 12.6783 | 15.604 | 19.3 | 22.1254 | 24.9228
Parry SoundWind2023RCP4.5 | Parry Sound | Wind | RCP4.5 | 2023 | 78.1875 | 84.2524 | 90.648 | 97.0319 | 103.4105
Parry SoundWind2025RCP4.5 | Parry Sound | Wind | RCP4.5 | 2025 | 78.26 | 84.3417 | 90.7575 | 97.1587 | 103.5559
Parry SoundWind2030RCP4.5 | Parry Sound | Wind | RCP4.5 | 2030 | 78.3325 | 84.431 | 90.867 | 97.2855 | 103.7012
Parry SoundWind2035RCP4.5 | Parry Sound | Wind | RCP4.5 | 2035 | 78.4051 | 84.5203 | 90.9765 | 97.4123 | 103.8466
Parry SoundWind2040RCP4.5 | Parry Sound | Wind | RCP4.5 | 2040 | 78.4776 | 84.6095 | 91.086 | 97.5391 | 103.9919
Parry SoundWind2045RCP4.5 | Parry Sound | Wind | RCP4.5 | 2045 | 78.5501 | 84.6988 | 91.1955 | 97.6659 | 104.1373
Parry SoundWind2050RCP4.5 | Parry Sound | Wind | RCP4.5 | 2050 | 78.6942 | 84.8818 | 91.4256 | 97.9352 | 104.4489
Parry SoundWind2055RCP4.5 | Parry Sound | Wind | RCP4.5 | 2055 | 78.7657 | 84.9756 | 91.5462 | 98.0777 | 104.6151
Parry SoundWind2060RCP4.5 | Parry Sound | Wind | RCP4.5 | 2060 | 78.8372 | 85.0693 | 91.6668 | 98.2202 | 104.7813
Parry SoundWind2065RCP4.5 | Parry Sound | Wind | RCP4.5 | 2065 | 78.9087 | 85.1631 | 91.7874 | 98.3627 | 104.9475
Parry SoundWind2070RCP4.5 | Parry Sound | Wind | RCP4.5 | 2070 | 78.9801 | 85.2568 | 91.908 | 98.5053 | 105.1137
Parry SoundWind2075RCP4.5 | Parry Sound | Wind | RCP4.5 | 2075 | 78.9685 | 85.2471 | 91.902 | 98.5037 | 105.1154
Parry SoundWind2080RCP4.5 | Parry Sound | Wind | RCP4.5 | 2080 | 78.9568 | 85.2373 | 91.896 | 98.5021 | 105.1171
Parry SoundWind2085RCP4.5 | Parry Sound | Wind | RCP4.5 | 2085 | 78.9452 | 85.2275 | 91.89 | 98.5005 | 105.1188
Parry SoundWind2090RCP4.5 | Parry Sound | Wind | RCP4.5 | 2090 | 78.9335 | 85.2178 | 91.884 | 98.4989 | 105.1205
Parry SoundWind2095RCP4.5 | Parry Sound | Wind | RCP4.5 | 2095 | 78.9219 | 85.208 | 91.878 | 98.4972 | 105.1222
Parry SoundWind2100RCP4.5 | Parry Sound | Wind | RCP4.5 | 2100 | 78.9102 | 85.1982 | 91.872 | 98.4956 | 105.124
Parry SoundWind2023RCP6.0 | Parry Sound | Wind | RCP6.0 | 2023 | 78.1875 | 84.2524 | 90.648 | 97.0319 | 103.4105
Parry SoundWind2025RCP6.0 | Parry Sound | Wind | RCP6.0 | 2025 | 78.26 | 84.3417 | 90.7575 | 97.1587 | 103.5559
Parry SoundWind2030RCP6.0 | Parry Sound | Wind | RCP6.0 | 2030 | 78.3325 | 84.431 | 90.867 | 97.2855 | 103.7012
Parry SoundWind2035RCP6.0 | Parry Sound | Wind | RCP6.0 | 2035 | 78.4051 | 84.5203 | 90.9765 | 97.4123 | 103.8466
Parry SoundWind2040RCP6.0 | Parry Sound | Wind | RCP6.0 | 2040 | 78.4776 | 84.6095 | 91.086 | 97.5391 | 103.9919
Parry SoundWind2045RCP6.0 | Parry Sound | Wind | RCP6.0 | 2045 | 78.5501 | 84.6988 | 91.1955 | 97.6659 | 104.1373
Parry SoundWind2050RCP6.0 | Parry Sound | Wind | RCP6.0 | 2050 | 78.6942 | 84.8818 | 91.4256 | 97.9352 | 104.4489
Parry SoundWind2055RCP6.0 | Parry Sound | Wind | RCP6.0 | 2055 | 78.7657 | 84.9756 | 91.5462 | 98.0777 | 104.6151
Parry SoundWind2060RCP6.0 | Parry Sound | Wind | RCP6.0 | 2060 | 78.8372 | 85.0693 | 91.6668 | 98.2202 | 104.7813
Parry SoundWind2065RCP6.0 | Parry Sound | Wind | RCP6.0 | 2065 | 78.9087 | 85.1631 | 91.7874 | 98.3627 | 104.9475
Parry SoundWind2070RCP6.0 | Parry Sound | Wind | RCP6.0 | 2070 | 78.9801 | 85.2568 | 91.908 | 98.5053 | 105.1137
Parry SoundWind2075RCP6.0 | Parry Sound | Wind | RCP6.0 | 2075 | 78.9627 | 85.2422 | 91.899 | 98.5029 | 105.1163
Parry SoundWind2080RCP6.0 | Parry Sound | Wind | RCP6.0 | 2080 | 78.9452 | 85.2275 | 91.89 | 98.5005 | 105.1188
Parry SoundWind2085RCP6.0 | Parry Sound | Wind | RCP6.0 | 2085 | 78.9277 | 85.2129 | 91.881 | 98.498 | 105.1214
Parry SoundWind2090RCP6.0 | Parry Sound | Wind | RCP6.0 | 2090 | 78.9957 | 85.3126 | 92.022 | 98.6722 | 105.3292
Parry SoundWind2095RCP6.0 | Parry Sound | Wind | RCP6.0 | 2095 | 79.0812 | 85.427 | 92.172 | 98.8487 | 105.5344
Parry SoundWind2100RCP6.0 | Parry Sound | Wind | RCP6.0 | 2100 | 79.1667 | 85.5414 | 92.322 | 99.0253 | 105.7396
Parry SoundWind2023RCP8.5 | Parry Sound | Wind | RCP8.5 | 2023 | 78.1875 | 84.2524 | 90.648 | 97.0319 | 103.4105
Parry SoundWind2025RCP8.5 | Parry Sound | Wind | RCP8.5 | 2025 | 78.3325 | 84.431 | 90.867 | 97.2855 | 103.7012
Parry SoundWind2030RCP8.5 | Parry Sound | Wind | RCP8.5 | 2030 | 78.4776 | 84.6095 | 91.086 | 97.5391 | 103.9919
Parry SoundWind2035RCP8.5 | Parry Sound | Wind | RCP8.5 | 2035 | 78.6227 | 84.7881 | 91.305 | 97.7927 | 104.2826
Parry SoundWind2040RCP8.5 | Parry Sound | Wind | RCP8.5 | 2040 | 78.7418 | 84.9443 | 91.506 | 98.0302 | 104.5597
Parry SoundWind2045RCP8.5 | Parry Sound | Wind | RCP8.5 | 2045 | 78.861 | 85.1006 | 91.707 | 98.2677 | 104.8367
Parry SoundWind2050RCP8.5 | Parry Sound | Wind | RCP8.5 | 2050 | 78.9568 | 85.2373 | 91.896 | 98.5021 | 105.1171
Parry SoundWind2055RCP8.5 | Parry Sound | Wind | RCP8.5 | 2055 | 78.9335 | 85.2178 | 91.884 | 98.4989 | 105.1205
Parry SoundWind2060RCP8.5 | Parry Sound | Wind | RCP8.5 | 2060 | 78.9957 | 85.3126 | 92.022 | 98.6722 | 105.3292
Parry SoundWind2065RCP8.5 | Parry Sound | Wind | RCP8.5 | 2065 | 79.0812 | 85.427 | 92.172 | 98.8487 | 105.5344
Parry SoundWind2070RCP8.5 | Parry Sound | Wind | RCP8.5 | 2070 | 79.1485 | 85.5581 | 92.388 | 99.1312 | 105.8866
Parry SoundWind2075RCP8.5 | Parry Sound | Wind | RCP8.5 | 2075 | 79.1304 | 85.5749 | 92.454 | 99.2372 | 106.0337
Parry SoundWind2080RCP8.5 | Parry Sound | Wind | RCP8.5 | 2080 | 79.1123 | 85.5916 | 92.52 | 99.3431 | 106.1807
Parry SoundWind2085RCP8.5 | Parry Sound | Wind | RCP8.5 | 2085 | 79.3454 | 85.9013 | 92.916 | 99.815 | 106.7296
Parry SoundWind2090RCP8.5 | Parry Sound | Wind | RCP8.5 | 2090 | 79.5785 | 86.211 | 93.312 | 100.2868 | 107.2786
Parry SoundWind2095RCP8.5 | Parry Sound | Wind | RCP8.5 | 2095 | 79.5785 | 86.211 | 93.312 | 100.2868 | 107.2786
Parry SoundWind2100RCP8.5 | Parry Sound | Wind | RCP8.5 | 2100 | 79.5785 | 86.211 | 93.312 | 100.2868 | 107.2786
Pelham (Fonthill)Ice Accretion2023RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
Pelham (Fonthill)Ice Accretion2025RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2025 | 21.9182 | 26.3121 | 31.8773 | 36.1299 | 40.3738
Pelham (Fonthill)Ice Accretion2030RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2030 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
Pelham (Fonthill)Ice Accretion2035RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2035 | 21.7104 | 26.0819 | 31.632 | 35.8526 | 40.0781
Pelham (Fonthill)Ice Accretion2040RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2040 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
Pelham (Fonthill)Ice Accretion2045RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2045 | 21.5026 | 25.8517 | 31.3867 | 35.5754 | 39.7824
Pelham (Fonthill)Ice Accretion2050RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2050 | 20.9221 | 25.2001 | 30.6368 | 34.7425 | 38.8765
Pelham (Fonthill)Ice Accretion2055RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2055 | 20.4456 | 24.6636 | 30.0096 | 34.0483 | 38.1185
Pelham (Fonthill)Ice Accretion2060RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2060 | 19.9691 | 24.1271 | 29.3824 | 33.354 | 37.3605
Pelham (Fonthill)Ice Accretion2065RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2065 | 19.4926 | 23.5906 | 28.7552 | 32.6597 | 36.6025
Pelham (Fonthill)Ice Accretion2070RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2070 | 19.0161 | 23.0541 | 28.128 | 31.9654 | 35.8445
Pelham (Fonthill)Ice Accretion2075RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2075 | 18.8379 | 22.8682 | 27.9307 | 31.7605 | 35.6294
Pelham (Fonthill)Ice Accretion2080RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2080 | 18.6598 | 22.6822 | 27.7333 | 31.5556 | 35.4144
Pelham (Fonthill)Ice Accretion2085RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2085 | 18.4817 | 22.4963 | 27.536 | 31.3507 | 35.1994
Pelham (Fonthill)Ice Accretion2090RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2090 | 18.3035 | 22.3104 | 27.3387 | 31.1458 | 34.9843
Pelham (Fonthill)Ice Accretion2095RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2095 | 18.1254 | 22.1245 | 27.1413 | 30.9409 | 34.7693
Pelham (Fonthill)Ice Accretion2100RCP4.5 | Pelham (Fonthill) | Ice Accretion | RCP4.5 | 2100 | 17.9473 | 21.9386 | 26.944 | 30.736 | 34.5542
Pelham (Fonthill)Ice Accretion2023RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
Pelham (Fonthill)Ice Accretion2025RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2025 | 21.9182 | 26.3121 | 31.8773 | 36.1299 | 40.3738
Pelham (Fonthill)Ice Accretion2030RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2030 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
Pelham (Fonthill)Ice Accretion2035RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2035 | 21.7104 | 26.0819 | 31.632 | 35.8526 | 40.0781
Pelham (Fonthill)Ice Accretion2040RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2040 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
Pelham (Fonthill)Ice Accretion2045RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2045 | 21.5026 | 25.8517 | 31.3867 | 35.5754 | 39.7824
Pelham (Fonthill)Ice Accretion2050RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2050 | 20.9221 | 25.2001 | 30.6368 | 34.7425 | 38.8765
Pelham (Fonthill)Ice Accretion2055RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2055 | 20.4456 | 24.6636 | 30.0096 | 34.0483 | 38.1185
Pelham (Fonthill)Ice Accretion2060RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2060 | 19.9691 | 24.1271 | 29.3824 | 33.354 | 37.3605
Pelham (Fonthill)Ice Accretion2065RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2065 | 19.4926 | 23.5906 | 28.7552 | 32.6597 | 36.6025
Pelham (Fonthill)Ice Accretion2070RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2070 | 19.0161 | 23.0541 | 28.128 | 31.9654 | 35.8445
Pelham (Fonthill)Ice Accretion2075RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2075 | 18.7489 | 22.7752 | 27.832 | 31.6581 | 35.5219
Pelham (Fonthill)Ice Accretion2080RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2080 | 18.4817 | 22.4963 | 27.536 | 31.3507 | 35.1994
Pelham (Fonthill)Ice Accretion2085RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2085 | 18.2145 | 22.2174 | 27.24 | 31.0434 | 34.8768
Pelham (Fonthill)Ice Accretion2090RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2090 | 17.2199 | 21.1063 | 25.9733 | 29.6633 | 33.3581
Pelham (Fonthill)Ice Accretion2095RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2095 | 16.4925 | 20.2741 | 25.0027 | 28.5905 | 32.1619
Pelham (Fonthill)Ice Accretion2100RCP6.0 | Pelham (Fonthill) | Ice Accretion | RCP6.0 | 2100 | 15.7651 | 19.4419 | 24.032 | 27.5178 | 30.9658
Pelham (Fonthill)Ice Accretion2023RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
Pelham (Fonthill)Ice Accretion2025RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2025 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
Pelham (Fonthill)Ice Accretion2030RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2030 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
Pelham (Fonthill)Ice Accretion2035RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2035 | 21.3987 | 25.7366 | 31.264 | 35.4368 | 39.6346
Pelham (Fonthill)Ice Accretion2040RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2040 | 20.6045 | 24.8425 | 30.2187 | 34.2797 | 38.3712
Pelham (Fonthill)Ice Accretion2045RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2045 | 19.8103 | 23.9483 | 29.1733 | 33.1226 | 37.1078
Pelham (Fonthill)Ice Accretion2050RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2050 | 18.6598 | 22.6822 | 27.7333 | 31.5556 | 35.4144
Pelham (Fonthill)Ice Accretion2055RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2055 | 18.3035 | 22.3104 | 27.3387 | 31.1458 | 34.9843
Pelham (Fonthill)Ice Accretion2060RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2060 | 17.2199 | 21.1063 | 25.9733 | 29.6633 | 33.3581
Pelham (Fonthill)Ice Accretion2065RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2065 | 16.4925 | 20.2741 | 25.0027 | 28.5905 | 32.1619
Pelham (Fonthill)Ice Accretion2070RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2070 | 15.4014 | 19.0258 | 23.5627 | 26.9995 | 30.4013
Pelham (Fonthill)Ice Accretion2075RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2075 | 15.0377 | 18.6097 | 23.0933 | 26.4812 | 29.8368
Pelham (Fonthill)Ice Accretion2080RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2080 | 14.674 | 18.1936 | 22.624 | 25.9629 | 29.2723
Pelham (Fonthill)Ice Accretion2085RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2085 | 13.8501 | 17.2242 | 21.456 | 24.643 | 27.8006
Pelham (Fonthill)Ice Accretion2090RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2090 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
Pelham (Fonthill)Ice Accretion2095RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2095 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
Pelham (Fonthill)Ice Accretion2100RCP8.5 | Pelham (Fonthill) | Ice Accretion | RCP8.5 | 2100 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
Pelham (Fonthill)Wind2023RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2023 | 88.11 | 95.1229 | 102.5655 | 109.9612 | 117.3507
Pelham (Fonthill)Wind2025RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2025 | 88.0809 | 95.0932 | 102.5335 | 109.927 | 117.3142
Pelham (Fonthill)Wind2030RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2030 | 88.0519 | 95.0634 | 102.5015 | 109.8928 | 117.2778
Pelham (Fonthill)Wind2035RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2035 | 88.0228 | 95.0337 | 102.4695 | 109.8586 | 117.2413
Pelham (Fonthill)Wind2040RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2040 | 87.9937 | 95.0039 | 102.4376 | 109.8243 | 117.2048
Pelham (Fonthill)Wind2045RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2045 | 87.9647 | 94.9742 | 102.4056 | 109.7901 | 117.1684
Pelham (Fonthill)Wind2050RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2050 | 87.9931 | 95.0177 | 102.4685 | 109.8661 | 117.2609
Pelham (Fonthill)Wind2055RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2055 | 88.0507 | 95.091 | 102.5635 | 109.9764 | 117.3898
Pelham (Fonthill)Wind2060RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2060 | 88.1083 | 95.1642 | 102.6584 | 110.0866 | 117.5188
Pelham (Fonthill)Wind2065RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2065 | 88.1658 | 95.2375 | 102.7534 | 110.1968 | 117.6477
Pelham (Fonthill)Wind2070RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2070 | 88.2234 | 95.3108 | 102.8483 | 110.307 | 117.7767
Pelham (Fonthill)Wind2075RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2075 | 88.3048 | 95.4251 | 103.0049 | 110.498 | 118.0051
Pelham (Fonthill)Wind2080RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2080 | 88.3862 | 95.5393 | 103.1614 | 110.6889 | 118.2334
Pelham (Fonthill)Wind2085RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2085 | 88.4676 | 95.6536 | 103.3179 | 110.8798 | 118.4618
Pelham (Fonthill)Wind2090RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2090 | 88.549 | 95.7679 | 103.4745 | 111.0707 | 118.6901
Pelham (Fonthill)Wind2095RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2095 | 88.6304 | 95.8822 | 103.6311 | 111.2617 | 118.9185
Pelham (Fonthill)Wind2100RCP4.5 | Pelham (Fonthill) | Wind | RCP4.5 | 2100 | 88.7118 | 95.9965 | 103.7876 | 111.4526 | 119.1469
Pelham (Fonthill)Wind2023RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2023 | 88.11 | 95.1229 | 102.5655 | 109.9612 | 117.3507
Pelham (Fonthill)Wind2025RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2025 | 88.0809 | 95.0932 | 102.5335 | 109.927 | 117.3142
Pelham (Fonthill)Wind2030RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2030 | 88.0519 | 95.0634 | 102.5015 | 109.8928 | 117.2778
Pelham (Fonthill)Wind2035RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2035 | 88.0228 | 95.0337 | 102.4695 | 109.8586 | 117.2413
Pelham (Fonthill)Wind2040RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2040 | 87.9937 | 95.0039 | 102.4376 | 109.8243 | 117.2048
Pelham (Fonthill)Wind2045RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2045 | 87.9647 | 94.9742 | 102.4056 | 109.7901 | 117.1684
Pelham (Fonthill)Wind2050RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2050 | 87.9931 | 95.0177 | 102.4685 | 109.8661 | 117.2609
Pelham (Fonthill)Wind2055RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2055 | 88.0507 | 95.091 | 102.5635 | 109.9764 | 117.3898
Pelham (Fonthill)Wind2060RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2060 | 88.1083 | 95.1642 | 102.6584 | 110.0866 | 117.5188
Pelham (Fonthill)Wind2065RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2065 | 88.1658 | 95.2375 | 102.7534 | 110.1968 | 117.6477
Pelham (Fonthill)Wind2070RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2070 | 88.2234 | 95.3108 | 102.8483 | 110.307 | 117.7767
Pelham (Fonthill)Wind2075RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2075 | 88.3455 | 95.4822 | 103.0831 | 110.5934 | 118.1192
Pelham (Fonthill)Wind2080RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2080 | 88.4676 | 95.6536 | 103.3179 | 110.8798 | 118.4618
Pelham (Fonthill)Wind2085RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2085 | 88.5897 | 95.825 | 103.5528 | 111.1662 | 118.8043
Pelham (Fonthill)Wind2090RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2090 | 88.8978 | 96.2344 | 104.0872 | 111.8092 | 119.5614
Pelham (Fonthill)Wind2095RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2095 | 89.0839 | 96.4724 | 104.3869 | 112.1659 | 119.9759
Pelham (Fonthill)Wind2100RCP6.0 | Pelham (Fonthill) | Wind | RCP6.0 | 2100 | 89.2699 | 96.7103 | 104.6865 | 112.5225 | 120.3904
Pelham (Fonthill)Wind2023RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2023 | 88.11 | 95.1229 | 102.5655 | 109.9612 | 117.3507
Pelham (Fonthill)Wind2025RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2025 | 88.0519 | 95.0634 | 102.5015 | 109.8928 | 117.2778
Pelham (Fonthill)Wind2030RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2030 | 87.9937 | 95.0039 | 102.4376 | 109.8243 | 117.2048
Pelham (Fonthill)Wind2035RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2035 | 87.9356 | 94.9444 | 102.3736 | 109.7559 | 117.1319
Pelham (Fonthill)Wind2040RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2040 | 88.0315 | 95.0666 | 102.5318 | 109.9396 | 117.3468
Pelham (Fonthill)Wind2045RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2045 | 88.1274 | 95.1887 | 102.6901 | 110.1233 | 117.5618
Pelham (Fonthill)Wind2050RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2050 | 88.3862 | 95.5393 | 103.1614 | 110.6889 | 118.2334
Pelham (Fonthill)Wind2055RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2055 | 88.549 | 95.7679 | 103.4745 | 111.0707 | 118.6901
Pelham (Fonthill)Wind2060RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2060 | 88.8978 | 96.2344 | 104.0872 | 111.8092 | 119.5614
Pelham (Fonthill)Wind2065RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2065 | 89.0839 | 96.4724 | 104.3869 | 112.1659 | 119.9759
Pelham (Fonthill)Wind2070RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2070 | 89.331 | 96.8137 | 104.8515 | 112.7386 | 120.6514
Pelham (Fonthill)Wind2075RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2075 | 89.392 | 96.917 | 105.0164 | 112.9548 | 120.9124
Pelham (Fonthill)Wind2080RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2080 | 89.4531 | 97.0203 | 105.1814 | 113.1709 | 121.1733
Pelham (Fonthill)Wind2085RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2085 | 89.5185 | 97.1283 | 105.338 | 113.3654 | 121.4151
Pelham (Fonthill)Wind2090RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2090 | 89.5839 | 97.2363 | 105.4945 | 113.56 | 121.6569
Pelham (Fonthill)Wind2095RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2095 | 89.5839 | 97.2363 | 105.4945 | 113.56 | 121.6569
Pelham (Fonthill)Wind2100RCP8.5 | Pelham (Fonthill) | Wind | RCP8.5 | 2100 | 89.5839 | 97.2363 | 105.4945 | 113.56 | 121.6569
PembrokeIce Accretion2023RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2023 | 14.0283 | 16.7162 | 20.12 | 22.713 | 25.326
PembrokeIce Accretion2025RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2025 | 14.1628 | 16.885 | 20.33 | 22.9578 | 25.599
PembrokeIce Accretion2030RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2030 | 14.2973 | 17.0537 | 20.54 | 23.2027 | 25.872
PembrokeIce Accretion2035RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2035 | 14.4318 | 17.2225 | 20.75 | 23.4475 | 26.145
PembrokeIce Accretion2040RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2040 | 14.5664 | 17.3913 | 20.96 | 23.6923 | 26.418
PembrokeIce Accretion2045RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2045 | 14.7009 | 17.56 | 21.17 | 23.9372 | 26.691
PembrokeIce Accretion2050RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2050 | 14.8327 | 17.7388 | 21.412 | 24.2227 | 27.0245
PembrokeIce Accretion2055RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2055 | 14.8299 | 17.7487 | 21.444 | 24.2634 | 27.085
PembrokeIce Accretion2060RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2060 | 14.8271 | 17.7587 | 21.476 | 24.304 | 27.1454
PembrokeIce Accretion2065RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2065 | 14.8243 | 17.7686 | 21.508 | 24.3447 | 27.2059
PembrokeIce Accretion2070RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2070 | 14.8215 | 17.7786 | 21.54 | 24.3854 | 27.2664
PembrokeIce Accretion2075RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2075 | 14.8285 | 17.8007 | 21.5767 | 24.4381 | 27.3294
PembrokeIce Accretion2080RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2080 | 14.8354 | 17.8229 | 21.6133 | 24.4909 | 27.3924
PembrokeIce Accretion2085RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2085 | 14.8424 | 17.845 | 21.65 | 24.5436 | 27.4554
PembrokeIce Accretion2090RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2090 | 14.8494 | 17.8671 | 21.6867 | 24.5963 | 27.5184
PembrokeIce Accretion2095RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2095 | 14.8563 | 17.8893 | 21.7233 | 24.6491 | 27.5814
PembrokeIce Accretion2100RCP4.5 | Pembroke | Ice Accretion | RCP4.5 | 2100 | 14.8633 | 17.9114 | 21.76 | 24.7018 | 27.6444
PembrokeIce Accretion2023RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2023 | 14.0283 | 16.7162 | 20.12 | 22.713 | 25.326
PembrokeIce Accretion2025RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2025 | 14.1628 | 16.885 | 20.33 | 22.9578 | 25.599
PembrokeIce Accretion2030RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2030 | 14.2973 | 17.0537 | 20.54 | 23.2027 | 25.872
PembrokeIce Accretion2035RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2035 | 14.4318 | 17.2225 | 20.75 | 23.4475 | 26.145
PembrokeIce Accretion2040RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2040 | 14.5664 | 17.3913 | 20.96 | 23.6923 | 26.418
PembrokeIce Accretion2045RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2045 | 14.7009 | 17.56 | 21.17 | 23.9372 | 26.691
PembrokeIce Accretion2050RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2050 | 14.8327 | 17.7388 | 21.412 | 24.2227 | 27.0245
PembrokeIce Accretion2055RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2055 | 14.8299 | 17.7487 | 21.444 | 24.2634 | 27.085
PembrokeIce Accretion2060RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2060 | 14.8271 | 17.7587 | 21.476 | 24.304 | 27.1454
PembrokeIce Accretion2065RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2065 | 14.8243 | 17.7686 | 21.508 | 24.3447 | 27.2059
PembrokeIce Accretion2070RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2070 | 14.8215 | 17.7786 | 21.54 | 24.3854 | 27.2664
PembrokeIce Accretion2075RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2075 | 14.832 | 17.8118 | 21.595 | 24.4645 | 27.3609
PembrokeIce Accretion2080RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2080 | 14.8424 | 17.845 | 21.65 | 24.5436 | 27.4554
PembrokeIce Accretion2085RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2085 | 14.8528 | 17.8782 | 21.705 | 24.6227 | 27.5499
PembrokeIce Accretion2090RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2090 | 14.6592 | 17.6569 | 21.4467 | 24.3477 | 27.2412
PembrokeIce Accretion2095RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2095 | 14.455 | 17.4023 | 21.1333 | 23.9937 | 26.838
PembrokeIce Accretion2100RCP6.0 | Pembroke | Ice Accretion | RCP6.0 | 2100 | 14.2509 | 17.1478 | 20.82 | 23.6396 | 26.4348
PembrokeIce Accretion2023RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2023 | 14.0283 | 16.7162 | 20.12 | 22.713 | 25.326
PembrokeIce Accretion2025RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2025 | 14.2973 | 17.0537 | 20.54 | 23.2027 | 25.872
PembrokeIce Accretion2030RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2030 | 14.5664 | 17.3913 | 20.96 | 23.6923 | 26.418
PembrokeIce Accretion2035RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2035 | 14.8354 | 17.7288 | 21.38 | 24.182 | 26.964
PembrokeIce Accretion2040RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2040 | 14.8308 | 17.7454 | 21.4333 | 24.2498 | 27.0648
PembrokeIce Accretion2045RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2045 | 14.8262 | 17.762 | 21.4867 | 24.3176 | 27.1656
PembrokeIce Accretion2050RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2050 | 14.8354 | 17.8229 | 21.6133 | 24.4909 | 27.3924
PembrokeIce Accretion2055RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2055 | 14.8494 | 17.8671 | 21.6867 | 24.5963 | 27.5184
PembrokeIce Accretion2060RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2060 | 14.6592 | 17.6569 | 21.4467 | 24.3477 | 27.2412
PembrokeIce Accretion2065RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2065 | 14.455 | 17.4023 | 21.1333 | 23.9937 | 26.838
PembrokeIce Accretion2070RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2070 | 14.2231 | 17.1367 | 20.8267 | 23.6547 | 26.46
PembrokeIce Accretion2075RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2075 | 14.1953 | 17.1257 | 20.8333 | 23.6697 | 26.4852
PembrokeIce Accretion2080RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2080 | 14.1674 | 17.1146 | 20.84 | 23.6848 | 26.5104
PembrokeIce Accretion2085RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2085 | 13.8891 | 16.8241 | 20.54 | 23.3797 | 26.1954
PembrokeIce Accretion2090RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2090 | 13.6108 | 16.5336 | 20.24 | 23.0746 | 25.8804
PembrokeIce Accretion2095RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2095 | 13.6108 | 16.5336 | 20.24 | 23.0746 | 25.8804
PembrokeIce Accretion2100RCP8.5 | Pembroke | Ice Accretion | RCP8.5 | 2100 | 13.6108 | 16.5336 | 20.24 | 23.0746 | 25.8804
PembrokeWind2023RCP4.5 | Pembroke | Wind | RCP4.5 | 2023 | 76.7577 | 82.6127 | 88.7686 | 94.9348 | 101.0947
PembrokeWind2025RCP4.5 | Pembroke | Wind | RCP4.5 | 2025 | 76.7436 | 82.5962 | 88.7493 | 94.9142 | 101.0728
PembrokeWind2030RCP4.5 | Pembroke | Wind | RCP4.5 | 2030 | 76.7295 | 82.5796 | 88.73 | 94.8935 | 101.0508
PembrokeWind2035RCP4.5 | Pembroke | Wind | RCP4.5 | 2035 | 76.7154 | 82.5631 | 88.7107 | 94.8729 | 101.0288
PembrokeWind2040RCP4.5 | Pembroke | Wind | RCP4.5 | 2040 | 76.7014 | 82.5465 | 88.6915 | 94.8523 | 101.0068
PembrokeWind2045RCP4.5 | Pembroke | Wind | RCP4.5 | 2045 | 76.6873 | 82.53 | 88.6722 | 94.8316 | 100.9848
PembrokeWind2050RCP4.5 | Pembroke | Wind | RCP4.5 | 2050 | 76.747 | 82.5978 | 88.749 | 94.9157 | 101.0785
PembrokeWind2055RCP4.5 | Pembroke | Wind | RCP4.5 | 2055 | 76.8207 | 82.6823 | 88.8451 | 95.0205 | 101.1942
PembrokeWind2060RCP4.5 | Pembroke | Wind | RCP4.5 | 2060 | 76.8945 | 82.7667 | 88.9413 | 95.1252 | 101.3098
PembrokeWind2065RCP4.5 | Pembroke | Wind | RCP4.5 | 2065 | 76.9683 | 82.8511 | 89.0374 | 95.23 | 101.4255
PembrokeWind2070RCP4.5 | Pembroke | Wind | RCP4.5 | 2070 | 77.0421 | 82.9355 | 89.1335 | 95.3348 | 101.5412
PembrokeWind2075RCP4.5 | Pembroke | Wind | RCP4.5 | 2075 | 77.0882 | 82.9949 | 89.2077 | 95.4236 | 101.6426
PembrokeWind2080RCP4.5 | Pembroke | Wind | RCP4.5 | 2080 | 77.1343 | 83.0542 | 89.2818 | 95.5125 | 101.7441
PembrokeWind2085RCP4.5 | Pembroke | Wind | RCP4.5 | 2085 | 77.1804 | 83.1135 | 89.356 | 95.6014 | 101.8455
PembrokeWind2090RCP4.5 | Pembroke | Wind | RCP4.5 | 2090 | 77.2265 | 83.1728 | 89.4302 | 95.6903 | 101.947
PembrokeWind2095RCP4.5 | Pembroke | Wind | RCP4.5 | 2095 | 77.2726 | 83.2321 | 89.5043 | 95.7792 | 102.0485
PembrokeWind2100RCP4.5 | Pembroke | Wind | RCP4.5 | 2100 | 77.3187 | 83.2915 | 89.5785 | 95.868 | 102.1499
PembrokeWind2023RCP6.0 | Pembroke | Wind | RCP6.0 | 2023 | 76.7577 | 82.6127 | 88.7686 | 94.9348 | 101.0947
PembrokeWind2025RCP6.0 | Pembroke | Wind | RCP6.0 | 2025 | 76.7436 | 82.5962 | 88.7493 | 94.9142 | 101.0728
PembrokeWind2030RCP6.0 | Pembroke | Wind | RCP6.0 | 2030 | 76.7295 | 82.5796 | 88.73 | 94.8935 | 101.0508
PembrokeWind2035RCP6.0 | Pembroke | Wind | RCP6.0 | 2035 | 76.7154 | 82.5631 | 88.7107 | 94.8729 | 101.0288
PembrokeWind2040RCP6.0 | Pembroke | Wind | RCP6.0 | 2040 | 76.7014 | 82.5465 | 88.6915 | 94.8523 | 101.0068
PembrokeWind2045RCP6.0 | Pembroke | Wind | RCP6.0 | 2045 | 76.6873 | 82.53 | 88.6722 | 94.8316 | 100.9848
PembrokeWind2050RCP6.0 | Pembroke | Wind | RCP6.0 | 2050 | 76.747 | 82.5978 | 88.749 | 94.9157 | 101.0785
PembrokeWind2055RCP6.0 | Pembroke | Wind | RCP6.0 | 2055 | 76.8207 | 82.6823 | 88.8451 | 95.0205 | 101.1942
PembrokeWind2060RCP6.0 | Pembroke | Wind | RCP6.0 | 2060 | 76.8945 | 82.7667 | 88.9413 | 95.1252 | 101.3098
PembrokeWind2065RCP6.0 | Pembroke | Wind | RCP6.0 | 2065 | 76.9683 | 82.8511 | 89.0374 | 95.23 | 101.4255
PembrokeWind2070RCP6.0 | Pembroke | Wind | RCP6.0 | 2070 | 77.0421 | 82.9355 | 89.1335 | 95.3348 | 101.5412
PembrokeWind2075RCP6.0 | Pembroke | Wind | RCP6.0 | 2075 | 77.1112 | 83.0245 | 89.2447 | 95.4681 | 101.6934
PembrokeWind2080RCP6.0 | Pembroke | Wind | RCP6.0 | 2080 | 77.1804 | 83.1135 | 89.356 | 95.6014 | 101.8455
PembrokeWind2085RCP6.0 | Pembroke | Wind | RCP6.0 | 2085 | 77.2496 | 83.2025 | 89.4672 | 95.7347 | 101.9977
PembrokeWind2090RCP6.0 | Pembroke | Wind | RCP6.0 | 2090 | 77.352 | 83.3246 | 89.6111 | 95.8998 | 102.1804
PembrokeWind2095RCP6.0 | Pembroke | Wind | RCP6.0 | 2095 | 77.3853 | 83.3577 | 89.6438 | 95.9315 | 102.2108
PembrokeWind2100RCP6.0 | Pembroke | Wind | RCP6.0 | 2100 | 77.4186 | 83.3908 | 89.6764 | 95.9633 | 102.2412
PembrokeWind2023RCP8.5 | Pembroke | Wind | RCP8.5 | 2023 | 76.7577 | 82.6127 | 88.7686 | 94.9348 | 101.0947
PembrokeWind2025RCP8.5 | Pembroke | Wind | RCP8.5 | 2025 | 76.7295 | 82.5796 | 88.73 | 94.8935 | 101.0508
PembrokeWind2030RCP8.5 | Pembroke | Wind | RCP8.5 | 2030 | 76.7014 | 82.5465 | 88.6915 | 94.8523 | 101.0068
PembrokeWind2035RCP8.5 | Pembroke | Wind | RCP8.5 | 2035 | 76.6732 | 82.5134 | 88.6529 | 94.811 | 100.9628
PembrokeWind2040RCP8.5 | Pembroke | Wind | RCP8.5 | 2040 | 76.7961 | 82.6541 | 88.8131 | 94.9856 | 101.1556
PembrokeWind2045RCP8.5 | Pembroke | Wind | RCP8.5 | 2045 | 76.9191 | 82.7948 | 88.9733 | 95.1602 | 101.3484
PembrokeWind2050RCP8.5 | Pembroke | Wind | RCP8.5 | 2050 | 77.1343 | 83.0542 | 89.2818 | 95.5125 | 101.7441
PembrokeWind2055RCP8.5 | Pembroke | Wind | RCP8.5 | 2055 | 77.2265 | 83.1728 | 89.4302 | 95.6903 | 101.947
PembrokeWind2060RCP8.5 | Pembroke | Wind | RCP8.5 | 2060 | 77.352 | 83.3246 | 89.6111 | 95.8998 | 102.1804
PembrokeWind2065RCP8.5 | Pembroke | Wind | RCP8.5 | 2065 | 77.3853 | 83.3577 | 89.6438 | 95.9315 | 102.2108
PembrokeWind2070RCP8.5 | Pembroke | Wind | RCP8.5 | 2070 | 77.4109 | 83.3742 | 89.6497 | 95.9284 | 102.2007
PembrokeWind2075RCP8.5 | Pembroke | Wind | RCP8.5 | 2075 | 77.4033 | 83.3577 | 89.623 | 95.8934 | 102.1601
PembrokeWind2080RCP8.5 | Pembroke | Wind | RCP8.5 | 2080 | 77.3956 | 83.3411 | 89.5963 | 95.8585 | 102.1195
PembrokeWind2085RCP8.5 | Pembroke | Wind | RCP8.5 | 2085 | 77.3456 | 83.2666 | 89.4939 | 95.7252 | 101.9622
PembrokeWind2090RCP8.5 | Pembroke | Wind | RCP8.5 | 2090 | 77.2957 | 83.1921 | 89.3916 | 95.5919 | 101.805
PembrokeWind2095RCP8.5 | Pembroke | Wind | RCP8.5 | 2095 | 77.2957 | 83.1921 | 89.3916 | 95.5919 | 101.805
PembrokeWind2100RCP8.5 | Pembroke | Wind | RCP8.5 | 2100 | 77.2957 | 83.1921 | 89.3916 | 95.5919 | 101.805
PenetanguisheneIce Accretion2023RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2023 | 13.6525 | 16.2846 | 19.62 | 22.1706 | 24.7464
PenetanguisheneIce Accretion2025RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2025 | 13.6363 | 16.2735 | 19.6133 | 22.1706 | 24.7464
PenetanguisheneIce Accretion2030RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2030 | 13.62 | 16.2625 | 19.6067 | 22.1706 | 24.7464
PenetanguisheneIce Accretion2035RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2035 | 13.6038 | 16.2514 | 19.6 | 22.1706 | 24.7464
PenetanguisheneIce Accretion2040RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2040 | 13.5876 | 16.2403 | 19.5933 | 22.1706 | 24.7464
PenetanguisheneIce Accretion2045RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2045 | 13.5713 | 16.2293 | 19.5867 | 22.1706 | 24.7464
PenetanguisheneIce Accretion2050RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2050 | 13.5523 | 16.2282 | 19.612 | 22.2113 | 24.8018
PenetanguisheneIce Accretion2055RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2055 | 13.5495 | 16.2381 | 19.644 | 22.252 | 24.8573
PenetanguisheneIce Accretion2060RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2060 | 13.5467 | 16.2481 | 19.676 | 22.2926 | 24.9127
PenetanguisheneIce Accretion2065RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2065 | 13.5439 | 16.258 | 19.708 | 22.3333 | 24.9682
PenetanguisheneIce Accretion2070RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2070 | 13.5412 | 16.268 | 19.74 | 22.374 | 25.0236
PenetanguisheneIce Accretion2075RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2075 | 13.5806 | 16.3316 | 19.83 | 22.4832 | 25.1538
PenetanguisheneIce Accretion2080RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2080 | 13.62 | 16.3953 | 19.92 | 22.5925 | 25.284
PenetanguisheneIce Accretion2085RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2085 | 13.6595 | 16.4589 | 20.01 | 22.7017 | 25.4142
PenetanguisheneIce Accretion2090RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2090 | 13.6989 | 16.5225 | 20.1 | 22.8109 | 25.5444
PenetanguisheneIce Accretion2095RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2095 | 13.7383 | 16.5862 | 20.19 | 22.9202 | 25.6746
PenetanguisheneIce Accretion2100RCP4.5 | Penetanguishene | Ice Accretion | RCP4.5 | 2100 | 13.7778 | 16.6498 | 20.28 | 23.0294 | 25.8048
PenetanguisheneIce Accretion2023RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2023 | 13.6525 | 16.2846 | 19.62 | 22.1706 | 24.7464
PenetanguisheneIce Accretion2025RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2025 | 13.6363 | 16.2735 | 19.6133 | 22.1706 | 24.7464
PenetanguisheneIce Accretion2030RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2030 | 13.62 | 16.2625 | 19.6067 | 22.1706 | 24.7464
PenetanguisheneIce Accretion2035RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2035 | 13.6038 | 16.2514 | 19.6 | 22.1706 | 24.7464
PenetanguisheneIce Accretion2040RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2040 | 13.5876 | 16.2403 | 19.5933 | 22.1706 | 24.7464
PenetanguisheneIce Accretion2045RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2045 | 13.5713 | 16.2293 | 19.5867 | 22.1706 | 24.7464
PenetanguisheneIce Accretion2050RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2050 | 13.5523 | 16.2282 | 19.612 | 22.2113 | 24.8018
PenetanguisheneIce Accretion2055RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2055 | 13.5495 | 16.2381 | 19.644 | 22.252 | 24.8573
PenetanguisheneIce Accretion2060RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2060 | 13.5467 | 16.2481 | 19.676 | 22.2926 | 24.9127
PenetanguisheneIce Accretion2065RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2065 | 13.5439 | 16.258 | 19.708 | 22.3333 | 24.9682
PenetanguisheneIce Accretion2070RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2070 | 13.5412 | 16.268 | 19.74 | 22.374 | 25.0236
PenetanguisheneIce Accretion2075RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2075 | 13.6003 | 16.3634 | 19.875 | 22.5378 | 25.2189
PenetanguisheneIce Accretion2080RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2080 | 13.6595 | 16.4589 | 20.01 | 22.7017 | 25.4142
PenetanguisheneIce Accretion2085RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2085 | 13.7186 | 16.5543 | 20.145 | 22.8655 | 25.6095
PenetanguisheneIce Accretion2090RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2090 | 13.7546 | 16.6609 | 20.3333 | 23.1198 | 25.9224
PenetanguisheneIce Accretion2095RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2095 | 13.7314 | 16.6719 | 20.3867 | 23.2102 | 26.04
PenetanguisheneIce Accretion2100RCP6.0 | Penetanguishene | Ice Accretion | RCP6.0 | 2100 | 13.7082 | 16.683 | 20.44 | 23.3006 | 26.1576
PenetanguisheneIce Accretion2023RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2023 | 13.6525 | 16.2846 | 19.62 | 22.1706 | 24.7464
PenetanguisheneIce Accretion2025RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2025 | 13.62 | 16.2625 | 19.6067 | 22.1706 | 24.7464
PenetanguisheneIce Accretion2030RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2030 | 13.5876 | 16.2403 | 19.5933 | 22.1706 | 24.7464
PenetanguisheneIce Accretion2035RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2035 | 13.5551 | 16.2182 | 19.58 | 22.1706 | 24.7464
PenetanguisheneIce Accretion2040RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2040 | 13.5504 | 16.2348 | 19.6333 | 22.2384 | 24.8388
PenetanguisheneIce Accretion2045RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2045 | 13.5458 | 16.2514 | 19.6867 | 22.3062 | 24.9312
PenetanguisheneIce Accretion2050RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2050 | 13.62 | 16.3953 | 19.92 | 22.5925 | 25.284
PenetanguisheneIce Accretion2055RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2055 | 13.6989 | 16.5225 | 20.1 | 22.8109 | 25.5444
PenetanguisheneIce Accretion2060RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2060 | 13.7546 | 16.6609 | 20.3333 | 23.1198 | 25.9224
PenetanguisheneIce Accretion2065RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2065 | 13.7314 | 16.6719 | 20.3867 | 23.2102 | 26.04
PenetanguisheneIce Accretion2070RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2070 | 13.4577 | 16.4174 | 20.1533 | 22.9917 | 25.83
PenetanguisheneIce Accretion2075RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2075 | 13.2072 | 16.1518 | 19.8667 | 22.6829 | 25.5024
PenetanguisheneIce Accretion2080RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2080 | 12.9567 | 15.8862 | 19.58 | 22.374 | 25.1748
PenetanguisheneIce Accretion2085RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2085 | 12.4348 | 15.2969 | 18.9 | 21.6282 | 24.3558
PenetanguisheneIce Accretion2090RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2090 | 11.9129 | 14.7076 | 18.22 | 20.8824 | 23.5368
PenetanguisheneIce Accretion2095RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2095 | 11.9129 | 14.7076 | 18.22 | 20.8824 | 23.5368
PenetanguisheneIce Accretion2100RCP8.5 | Penetanguishene | Ice Accretion | RCP8.5 | 2100 | 11.9129 | 14.7076 | 18.22 | 20.8824 | 23.5368
PenetanguisheneWind2023RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2023 | 81.6868 | 88.0145 | 94.6862 | 101.3444 | 108.0066
PenetanguisheneWind2025RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2025 | 81.7707 | 88.115 | 94.8053 | 101.4802 | 108.1584
PenetanguisheneWind2030RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2030 | 81.8546 | 88.2155 | 94.9243 | 101.616 | 108.3102
PenetanguisheneWind2035RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2035 | 81.9384 | 88.3161 | 95.0434 | 101.7518 | 108.462
PenetanguisheneWind2040RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2040 | 82.0223 | 88.4166 | 95.1625 | 101.8875 | 108.6138
PenetanguisheneWind2045RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2045 | 82.1062 | 88.5171 | 95.2815 | 102.0233 | 108.7656
PenetanguisheneWind2050RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2050 | 82.3069 | 88.7575 | 95.5698 | 102.3542 | 109.1403
PenetanguisheneWind2055RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2055 | 82.4238 | 88.8974 | 95.739 | 102.5494 | 109.3632
PenetanguisheneWind2060RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2060 | 82.5407 | 89.0373 | 95.9082 | 102.7445 | 109.5861
PenetanguisheneWind2065RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2065 | 82.6576 | 89.1771 | 96.0774 | 102.9396 | 109.809
PenetanguisheneWind2070RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2070 | 82.7745 | 89.317 | 96.2466 | 103.1347 | 110.0319
PenetanguisheneWind2075RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2075 | 82.811 | 89.3695 | 96.3202 | 103.2253 | 110.139
PenetanguisheneWind2080RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2080 | 82.8475 | 89.4219 | 96.3939 | 103.3158 | 110.2462
PenetanguisheneWind2085RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2085 | 82.884 | 89.4744 | 96.4675 | 103.4063 | 110.3534
PenetanguisheneWind2090RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2090 | 82.9206 | 89.5268 | 96.5411 | 103.4968 | 110.4605
PenetanguisheneWind2095RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2095 | 82.9571 | 89.5793 | 96.6148 | 103.5873 | 110.5677
PenetanguisheneWind2100RCP4.5 | Penetanguishene | Wind | RCP4.5 | 2100 | 82.9936 | 89.6317 | 96.6884 | 103.6779 | 110.6748
PenetanguisheneWind2023RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2023 | 81.6868 | 88.0145 | 94.6862 | 101.3444 | 108.0066
PenetanguisheneWind2025RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2025 | 81.7707 | 88.115 | 94.8053 | 101.4802 | 108.1584
PenetanguisheneWind2030RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2030 | 81.8546 | 88.2155 | 94.9243 | 101.616 | 108.3102
PenetanguisheneWind2035RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2035 | 81.9384 | 88.3161 | 95.0434 | 101.7518 | 108.462
PenetanguisheneWind2040RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2040 | 82.0223 | 88.4166 | 95.1625 | 101.8875 | 108.6138
PenetanguisheneWind2045RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2045 | 82.1062 | 88.5171 | 95.2815 | 102.0233 | 108.7656
PenetanguisheneWind2050RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2050 | 82.3069 | 88.7575 | 95.5698 | 102.3542 | 109.1403
PenetanguisheneWind2055RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2055 | 82.4238 | 88.8974 | 95.739 | 102.5494 | 109.3632
PenetanguisheneWind2060RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2060 | 82.5407 | 89.0373 | 95.9082 | 102.7445 | 109.5861
PenetanguisheneWind2065RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2065 | 82.6576 | 89.1771 | 96.0774 | 102.9396 | 109.809
PenetanguisheneWind2070RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2070 | 82.7745 | 89.317 | 96.2466 | 103.1347 | 110.0319
PenetanguisheneWind2075RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2075 | 82.8292 | 89.3957 | 96.3571 | 103.2705 | 110.1926
PenetanguisheneWind2080RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2080 | 82.884 | 89.4744 | 96.4675 | 103.4063 | 110.3534
PenetanguisheneWind2085RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2085 | 82.9388 | 89.553 | 96.578 | 103.5421 | 110.5141
PenetanguisheneWind2090RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2090 | 83.1154 | 89.7949 | 96.8983 | 103.9293 | 110.9678
PenetanguisheneWind2095RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2095 | 83.2371 | 89.9581 | 97.1083 | 104.1808 | 111.2607
PenetanguisheneWind2100RCP6.0 | Penetanguishene | Wind | RCP6.0 | 2100 | 83.3589 | 90.1213 | 97.3182 | 104.4322 | 111.5536
PenetanguisheneWind2023RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2023 | 81.6868 | 88.0145 | 94.6862 | 101.3444 | 108.0066
PenetanguisheneWind2025RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2025 | 81.8546 | 88.2155 | 94.9243 | 101.616 | 108.3102
PenetanguisheneWind2030RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2030 | 82.0223 | 88.4166 | 95.1625 | 101.8875 | 108.6138
PenetanguisheneWind2035RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2035 | 82.1901 | 88.6177 | 95.4006 | 102.1591 | 108.9174
PenetanguisheneWind2040RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2040 | 82.3849 | 88.8508 | 95.6826 | 102.4843 | 109.2889
PenetanguisheneWind2045RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2045 | 82.5797 | 89.0839 | 95.9646 | 102.8095 | 109.6604
PenetanguisheneWind2050RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2050 | 82.8475 | 89.4219 | 96.3939 | 103.3158 | 110.2462
PenetanguisheneWind2055RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2055 | 82.9206 | 89.5268 | 96.5411 | 103.4968 | 110.4605
PenetanguisheneWind2060RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2060 | 83.1154 | 89.7949 | 96.8983 | 103.9293 | 110.9678
PenetanguisheneWind2065RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2065 | 83.2371 | 89.9581 | 97.1083 | 104.1808 | 111.2607
PenetanguisheneWind2070RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2070 | 83.3453 | 90.1154 | 97.3245 | 104.4456 | 111.5786
PenetanguisheneWind2075RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2075 | 83.3318 | 90.1096 | 97.3307 | 104.459 | 111.6036
PenetanguisheneWind2080RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2080 | 83.3183 | 90.1038 | 97.337 | 104.4724 | 111.6286
PenetanguisheneWind2085RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2085 | 83.4238 | 90.2393 | 97.5156 | 104.6837 | 111.875
PenetanguisheneWind2090RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2090 | 83.5293 | 90.3748 | 97.6942 | 104.8949 | 112.1215
PenetanguisheneWind2095RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2095 | 83.5293 | 90.3748 | 97.6942 | 104.8949 | 112.1215
PenetanguisheneWind2100RCP8.5 | Penetanguishene | Wind | RCP8.5 | 2100 | 83.5293 | 90.3748 | 97.6942 | 104.8949 | 112.1215
PerthIce Accretion2023RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2023 | 17.9473 | 21.3426 | 25.636 | 28.9393 | 32.2358
PerthIce Accretion2025RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2025 | 17.9412 | 21.339 | 25.6403 | 28.9491 | 32.2468
PerthIce Accretion2030RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2030 | 17.9352 | 21.3354 | 25.6447 | 28.9589 | 32.2577
PerthIce Accretion2035RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2035 | 17.9292 | 21.3318 | 25.649 | 28.9687 | 32.2686
PerthIce Accretion2040RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2040 | 17.9231 | 21.3282 | 25.6533 | 28.9785 | 32.2795
PerthIce Accretion2045RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2045 | 17.9171 | 21.3246 | 25.6577 | 28.9883 | 32.2904
PerthIce Accretion2050RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2050 | 17.9147 | 21.3426 | 25.7036 | 29.0568 | 32.3734
PerthIce Accretion2055RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2055 | 17.9183 | 21.3642 | 25.7452 | 29.1156 | 32.4455
PerthIce Accretion2060RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2060 | 17.9219 | 21.3858 | 25.7868 | 29.1743 | 32.5176
PerthIce Accretion2065RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2065 | 17.9256 | 21.4074 | 25.8284 | 29.2331 | 32.5896
PerthIce Accretion2070RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2070 | 17.9292 | 21.4289 | 25.87 | 29.2919 | 32.6617
PerthIce Accretion2075RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2075 | 18.0106 | 21.5476 | 26.0347 | 29.4877 | 32.8965
PerthIce Accretion2080RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2080 | 18.092 | 21.6663 | 26.1993 | 29.6836 | 33.1313
PerthIce Accretion2085RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2085 | 18.1734 | 21.785 | 26.364 | 29.8795 | 33.3661
PerthIce Accretion2090RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2090 | 18.2548 | 21.9037 | 26.5287 | 30.0753 | 33.6008
PerthIce Accretion2095RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2095 | 18.3362 | 22.0224 | 26.6933 | 30.2712 | 33.8356
PerthIce Accretion2100RCP4.5 | Perth | Ice Accretion | RCP4.5 | 2100 | 18.4177 | 22.1411 | 26.858 | 30.4671 | 34.0704
PerthIce Accretion2023RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2023 | 17.9473 | 21.3426 | 25.636 | 28.9393 | 32.2358
PerthIce Accretion2025RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2025 | 17.9412 | 21.339 | 25.6403 | 28.9491 | 32.2468
PerthIce Accretion2030RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2030 | 17.9352 | 21.3354 | 25.6447 | 28.9589 | 32.2577
PerthIce Accretion2035RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2035 | 17.9292 | 21.3318 | 25.649 | 28.9687 | 32.2686
PerthIce Accretion2040RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2040 | 17.9231 | 21.3282 | 25.6533 | 28.9785 | 32.2795
PerthIce Accretion2045RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2045 | 17.9171 | 21.3246 | 25.6577 | 28.9883 | 32.2904
PerthIce Accretion2050RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2050 | 17.9147 | 21.3426 | 25.7036 | 29.0568 | 32.3734
PerthIce Accretion2055RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2055 | 17.9183 | 21.3642 | 25.7452 | 29.1156 | 32.4455
PerthIce Accretion2060RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2060 | 17.9219 | 21.3858 | 25.7868 | 29.1743 | 32.5176
PerthIce Accretion2065RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2065 | 17.9256 | 21.4074 | 25.8284 | 29.2331 | 32.5896
PerthIce Accretion2070RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2070 | 17.9292 | 21.4289 | 25.87 | 29.2919 | 32.6617
PerthIce Accretion2075RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2075 | 18.0513 | 21.607 | 26.117 | 29.5857 | 33.0139
PerthIce Accretion2080RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2080 | 18.1734 | 21.785 | 26.364 | 29.8795 | 33.3661
PerthIce Accretion2085RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2085 | 18.2955 | 21.963 | 26.611 | 30.1733 | 33.7182
PerthIce Accretion2090RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2090 | 18.4056 | 22.1627 | 26.9273 | 30.5552 | 34.1905
PerthIce Accretion2095RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2095 | 18.3935 | 22.1842 | 26.9967 | 30.6433 | 34.3106
PerthIce Accretion2100RCP6.0 | Perth | Ice Accretion | RCP6.0 | 2100 | 18.3815 | 22.2058 | 27.066 | 30.7315 | 34.4308
PerthIce Accretion2023RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2023 | 17.9473 | 21.3426 | 25.636 | 28.9393 | 32.2358
PerthIce Accretion2025RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2025 | 17.9352 | 21.3354 | 25.6447 | 28.9589 | 32.2577
PerthIce Accretion2030RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2030 | 17.9231 | 21.3282 | 25.6533 | 28.9785 | 32.2795
PerthIce Accretion2035RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2035 | 17.9111 | 21.321 | 25.662 | 28.9981 | 32.3014
PerthIce Accretion2040RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2040 | 17.9171 | 21.357 | 25.7313 | 29.096 | 32.4215
PerthIce Accretion2045RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2045 | 17.9231 | 21.393 | 25.8007 | 29.1939 | 32.5416
PerthIce Accretion2050RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2050 | 18.092 | 21.6663 | 26.1993 | 29.6836 | 33.1313
PerthIce Accretion2055RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2055 | 18.2548 | 21.9037 | 26.5287 | 30.0753 | 33.6008
PerthIce Accretion2060RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2060 | 18.4056 | 22.1627 | 26.9273 | 30.5552 | 34.1905
PerthIce Accretion2065RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2065 | 18.3935 | 22.1842 | 26.9967 | 30.6433 | 34.3106
PerthIce Accretion2070RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2070 | 18.1885 | 22.0044 | 26.8493 | 30.5062 | 34.1905
PerthIce Accretion2075RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2075 | 17.9955 | 21.803 | 26.6327 | 30.281 | 33.9503
PerthIce Accretion2080RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2080 | 17.8025 | 21.6016 | 26.416 | 30.0557 | 33.71
PerthIce Accretion2085RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2085 | 17.0608 | 20.7492 | 25.415 | 28.954 | 32.4979
PerthIce Accretion2090RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2090 | 16.319 | 19.8968 | 24.414 | 27.8522 | 31.2858
PerthIce Accretion2095RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2095 | 16.319 | 19.8968 | 24.414 | 27.8522 | 31.2858
PerthIce Accretion2100RCP8.5 | Perth | Ice Accretion | RCP8.5 | 2100 | 16.319 | 19.8968 | 24.414 | 27.8522 | 31.2858
PerthWind2023RCP4.5 | Perth | Wind | RCP4.5 | 2023 | 76.5564 | 82.5275 | 88.8272 | 95.1016 | 101.3834
PerthWind2025RCP4.5 | Perth | Wind | RCP4.5 | 2025 | 76.6665 | 82.6598 | 88.9871 | 95.2868 | 101.5941
PerthWind2030RCP4.5 | Perth | Wind | RCP4.5 | 2030 | 76.7767 | 82.7921 | 89.1469 | 95.472 | 101.8047
PerthWind2035RCP4.5 | Perth | Wind | RCP4.5 | 2035 | 76.8869 | 82.9244 | 89.3068 | 95.6571 | 102.0154
PerthWind2040RCP4.5 | Perth | Wind | RCP4.5 | 2040 | 76.9971 | 83.0567 | 89.4667 | 95.8423 | 102.2261
PerthWind2045RCP4.5 | Perth | Wind | RCP4.5 | 2045 | 77.1073 | 83.189 | 89.6265 | 96.0275 | 102.4368
PerthWind2050RCP4.5 | Perth | Wind | RCP4.5 | 2050 | 77.2022 | 83.2984 | 89.7547 | 96.1731 | 102.5993
PerthWind2055RCP4.5 | Perth | Wind | RCP4.5 | 2055 | 77.187 | 83.2755 | 89.723 | 96.1336 | 102.5511
PerthWind2060RCP4.5 | Perth | Wind | RCP4.5 | 2060 | 77.1718 | 83.2526 | 89.6914 | 96.094 | 102.503
PerthWind2065RCP4.5 | Perth | Wind | RCP4.5 | 2065 | 77.1566 | 83.2296 | 89.6597 | 96.0545 | 102.4548
PerthWind2070RCP4.5 | Perth | Wind | RCP4.5 | 2070 | 77.1414 | 83.2067 | 89.628 | 96.015 | 102.4067
PerthWind2075RCP4.5 | Perth | Wind | RCP4.5 | 2075 | 77.1693 | 83.2436 | 89.6779 | 96.0746 | 102.4752
PerthWind2080RCP4.5 | Perth | Wind | RCP4.5 | 2080 | 77.1972 | 83.2804 | 89.7277 | 96.1342 | 102.5438
PerthWind2085RCP4.5 | Perth | Wind | RCP4.5 | 2085 | 77.225 | 83.3172 | 89.7776 | 96.1939 | 102.6123
PerthWind2090RCP4.5 | Perth | Wind | RCP4.5 | 2090 | 77.2529 | 83.354 | 89.8275 | 96.2535 | 102.6809
PerthWind2095RCP4.5 | Perth | Wind | RCP4.5 | 2095 | 77.2808 | 83.3909 | 89.8773 | 96.3131 | 102.7494
PerthWind2100RCP4.5 | Perth | Wind | RCP4.5 | 2100 | 77.3086 | 83.4277 | 89.9272 | 96.3728 | 102.818
PerthWind2023RCP6.0 | Perth | Wind | RCP6.0 | 2023 | 76.5564 | 82.5275 | 88.8272 | 95.1016 | 101.3834
PerthWind2025RCP6.0 | Perth | Wind | RCP6.0 | 2025 | 76.6665 | 82.6598 | 88.9871 | 95.2868 | 101.5941
PerthWind2030RCP6.0 | Perth | Wind | RCP6.0 | 2030 | 76.7767 | 82.7921 | 89.1469 | 95.472 | 101.8047
PerthWind2035RCP6.0 | Perth | Wind | RCP6.0 | 2035 | 76.8869 | 82.9244 | 89.3068 | 95.6571 | 102.0154
PerthWind2040RCP6.0 | Perth | Wind | RCP6.0 | 2040 | 76.9971 | 83.0567 | 89.4667 | 95.8423 | 102.2261
PerthWind2045RCP6.0 | Perth | Wind | RCP6.0 | 2045 | 77.1073 | 83.189 | 89.6265 | 96.0275 | 102.4368
PerthWind2050RCP6.0 | Perth | Wind | RCP6.0 | 2050 | 77.2022 | 83.2984 | 89.7547 | 96.1731 | 102.5993
PerthWind2055RCP6.0 | Perth | Wind | RCP6.0 | 2055 | 77.187 | 83.2755 | 89.723 | 96.1336 | 102.5511
PerthWind2060RCP6.0 | Perth | Wind | RCP6.0 | 2060 | 77.1718 | 83.2526 | 89.6914 | 96.094 | 102.503
PerthWind2065RCP6.0 | Perth | Wind | RCP6.0 | 2065 | 77.1566 | 83.2296 | 89.6597 | 96.0545 | 102.4548
PerthWind2070RCP6.0 | Perth | Wind | RCP6.0 | 2070 | 77.1414 | 83.2067 | 89.628 | 96.015 | 102.4067
PerthWind2075RCP6.0 | Perth | Wind | RCP6.0 | 2075 | 77.1832 | 83.262 | 89.7028 | 96.1044 | 102.5095
PerthWind2080RCP6.0 | Perth | Wind | RCP6.0 | 2080 | 77.225 | 83.3172 | 89.7776 | 96.1939 | 102.6123
PerthWind2085RCP6.0 | Perth | Wind | RCP6.0 | 2085 | 77.2668 | 83.3725 | 89.8524 | 96.2833 | 102.7151
PerthWind2090RCP6.0 | Perth | Wind | RCP6.0 | 2090 | 77.2529 | 83.3431 | 89.7981 | 96.2127 | 102.624
PerthWind2095RCP6.0 | Perth | Wind | RCP6.0 | 2095 | 77.1972 | 83.2586 | 89.6691 | 96.0526 | 102.4301
PerthWind2100RCP6.0 | Perth | Wind | RCP6.0 | 2100 | 77.1414 | 83.174 | 89.54 | 95.8925 | 102.2361
PerthWind2023RCP8.5 | Perth | Wind | RCP8.5 | 2023 | 76.5564 | 82.5275 | 88.8272 | 95.1016 | 101.3834
PerthWind2025RCP8.5 | Perth | Wind | RCP8.5 | 2025 | 76.7767 | 82.7921 | 89.1469 | 95.472 | 101.8047
PerthWind2030RCP8.5 | Perth | Wind | RCP8.5 | 2030 | 76.9971 | 83.0567 | 89.4667 | 95.8423 | 102.2261
PerthWind2035RCP8.5 | Perth | Wind | RCP8.5 | 2035 | 77.2174 | 83.3213 | 89.7864 | 96.2127 | 102.6474
PerthWind2040RCP8.5 | Perth | Wind | RCP8.5 | 2040 | 77.1921 | 83.2831 | 89.7336 | 96.1468 | 102.5672
PerthWind2045RCP8.5 | Perth | Wind | RCP8.5 | 2045 | 77.1668 | 83.2449 | 89.6808 | 96.0809 | 102.4869
PerthWind2050RCP8.5 | Perth | Wind | RCP8.5 | 2050 | 77.1972 | 83.2804 | 89.7277 | 96.1342 | 102.5438
PerthWind2055RCP8.5 | Perth | Wind | RCP8.5 | 2055 | 77.2529 | 83.354 | 89.8275 | 96.2535 | 102.6809
PerthWind2060RCP8.5 | Perth | Wind | RCP8.5 | 2060 | 77.2529 | 83.3431 | 89.7981 | 96.2127 | 102.624
PerthWind2065RCP8.5 | Perth | Wind | RCP8.5 | 2065 | 77.1972 | 83.2586 | 89.6691 | 96.0526 | 102.4301
PerthWind2070RCP8.5 | Perth | Wind | RCP8.5 | 2070 | 77.1744 | 83.204 | 89.5664 | 95.9177 | 102.2595
PerthWind2075RCP8.5 | Perth | Wind | RCP8.5 | 2075 | 77.2073 | 83.234 | 89.5928 | 95.9428 | 102.2829
PerthWind2080RCP8.5 | Perth | Wind | RCP8.5 | 2080 | 77.2402 | 83.264 | 89.6192 | 95.9679 | 102.3063
PerthWind2085RCP8.5 | Perth | Wind | RCP8.5 | 2085 | 77.2668 | 83.3049 | 89.6764 | 96.0338 | 102.3866
PerthWind2090RCP8.5 | Perth | Wind | RCP8.5 | 2090 | 77.2934 | 83.3459 | 89.7336 | 96.0997 | 102.4668
PerthWind2095RCP8.5 | Perth | Wind | RCP8.5 | 2095 | 77.2934 | 83.3459 | 89.7336 | 96.0997 | 102.4668
PerthWind2100RCP8.5 | Perth | Wind | RCP8.5 | 2100 | 77.2934 | 83.3459 | 89.7336 | 96.0997 | 102.4668
PetawawaIce Accretion2023RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2023 | 14.0283 | 16.7162 | 20.12 | 22.713 | 25.326
PetawawaIce Accretion2025RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2025 | 14.1628 | 16.885 | 20.33 | 22.9578 | 25.599
PetawawaIce Accretion2030RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2030 | 14.2973 | 17.0537 | 20.54 | 23.2027 | 25.872
PetawawaIce Accretion2035RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2035 | 14.4318 | 17.2225 | 20.75 | 23.4475 | 26.145
PetawawaIce Accretion2040RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2040 | 14.5664 | 17.3913 | 20.96 | 23.6923 | 26.418
PetawawaIce Accretion2045RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2045 | 14.7009 | 17.56 | 21.17 | 23.9372 | 26.691
PetawawaIce Accretion2050RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2050 | 14.8327 | 17.7388 | 21.412 | 24.2227 | 27.0245
PetawawaIce Accretion2055RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2055 | 14.8299 | 17.7487 | 21.444 | 24.2634 | 27.085
PetawawaIce Accretion2060RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2060 | 14.8271 | 17.7587 | 21.476 | 24.304 | 27.1454
PetawawaIce Accretion2065RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2065 | 14.8243 | 17.7686 | 21.508 | 24.3447 | 27.2059
PetawawaIce Accretion2070RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2070 | 14.8215 | 17.7786 | 21.54 | 24.3854 | 27.2664
PetawawaIce Accretion2075RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2075 | 14.8285 | 17.8007 | 21.5767 | 24.4381 | 27.3294
PetawawaIce Accretion2080RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2080 | 14.8354 | 17.8229 | 21.6133 | 24.4909 | 27.3924
PetawawaIce Accretion2085RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2085 | 14.8424 | 17.845 | 21.65 | 24.5436 | 27.4554
PetawawaIce Accretion2090RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2090 | 14.8494 | 17.8671 | 21.6867 | 24.5963 | 27.5184
PetawawaIce Accretion2095RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2095 | 14.8563 | 17.8893 | 21.7233 | 24.6491 | 27.5814
PetawawaIce Accretion2100RCP4.5 | Petawawa | Ice Accretion | RCP4.5 | 2100 | 14.8633 | 17.9114 | 21.76 | 24.7018 | 27.6444
PetawawaIce Accretion2023RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2023 | 14.0283 | 16.7162 | 20.12 | 22.713 | 25.326
PetawawaIce Accretion2025RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2025 | 14.1628 | 16.885 | 20.33 | 22.9578 | 25.599
PetawawaIce Accretion2030RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2030 | 14.2973 | 17.0537 | 20.54 | 23.2027 | 25.872
PetawawaIce Accretion2035RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2035 | 14.4318 | 17.2225 | 20.75 | 23.4475 | 26.145
PetawawaIce Accretion2040RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2040 | 14.5664 | 17.3913 | 20.96 | 23.6923 | 26.418
PetawawaIce Accretion2045RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2045 | 14.7009 | 17.56 | 21.17 | 23.9372 | 26.691
PetawawaIce Accretion2050RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2050 | 14.8327 | 17.7388 | 21.412 | 24.2227 | 27.0245
PetawawaIce Accretion2055RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2055 | 14.8299 | 17.7487 | 21.444 | 24.2634 | 27.085
PetawawaIce Accretion2060RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2060 | 14.8271 | 17.7587 | 21.476 | 24.304 | 27.1454
PetawawaIce Accretion2065RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2065 | 14.8243 | 17.7686 | 21.508 | 24.3447 | 27.2059
PetawawaIce Accretion2070RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2070 | 14.8215 | 17.7786 | 21.54 | 24.3854 | 27.2664
PetawawaIce Accretion2075RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2075 | 14.832 | 17.8118 | 21.595 | 24.4645 | 27.3609
PetawawaIce Accretion2080RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2080 | 14.8424 | 17.845 | 21.65 | 24.5436 | 27.4554
PetawawaIce Accretion2085RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2085 | 14.8528 | 17.8782 | 21.705 | 24.6227 | 27.5499
PetawawaIce Accretion2090RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2090 | 14.6592 | 17.6569 | 21.4467 | 24.3477 | 27.2412
PetawawaIce Accretion2095RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2095 | 14.455 | 17.4023 | 21.1333 | 23.9937 | 26.838
PetawawaIce Accretion2100RCP6.0 | Petawawa | Ice Accretion | RCP6.0 | 2100 | 14.2509 | 17.1478 | 20.82 | 23.6396 | 26.4348
PetawawaIce Accretion2023RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2023 | 14.0283 | 16.7162 | 20.12 | 22.713 | 25.326
PetawawaIce Accretion2025RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2025 | 14.2973 | 17.0537 | 20.54 | 23.2027 | 25.872
PetawawaIce Accretion2030RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2030 | 14.5664 | 17.3913 | 20.96 | 23.6923 | 26.418
PetawawaIce Accretion2035RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2035 | 14.8354 | 17.7288 | 21.38 | 24.182 | 26.964
PetawawaIce Accretion2040RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2040 | 14.8308 | 17.7454 | 21.4333 | 24.2498 | 27.0648
PetawawaIce Accretion2045RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2045 | 14.8262 | 17.762 | 21.4867 | 24.3176 | 27.1656
PetawawaIce Accretion2050RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2050 | 14.8354 | 17.8229 | 21.6133 | 24.4909 | 27.3924
PetawawaIce Accretion2055RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2055 | 14.8494 | 17.8671 | 21.6867 | 24.5963 | 27.5184
PetawawaIce Accretion2060RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2060 | 14.6592 | 17.6569 | 21.4467 | 24.3477 | 27.2412
PetawawaIce Accretion2065RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2065 | 14.455 | 17.4023 | 21.1333 | 23.9937 | 26.838
PetawawaIce Accretion2070RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2070 | 14.2231 | 17.1367 | 20.8267 | 23.6547 | 26.46
PetawawaIce Accretion2075RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2075 | 14.1953 | 17.1257 | 20.8333 | 23.6697 | 26.4852
PetawawaIce Accretion2080RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2080 | 14.1674 | 17.1146 | 20.84 | 23.6848 | 26.5104
PetawawaIce Accretion2085RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2085 | 13.8891 | 16.8241 | 20.54 | 23.3797 | 26.1954
PetawawaIce Accretion2090RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2090 | 13.6108 | 16.5336 | 20.24 | 23.0746 | 25.8804
PetawawaIce Accretion2095RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2095 | 13.6108 | 16.5336 | 20.24 | 23.0746 | 25.8804
PetawawaIce Accretion2100RCP8.5 | Petawawa | Ice Accretion | RCP8.5 | 2100 | 13.6108 | 16.5336 | 20.24 | 23.0746 | 25.8804
PetawawaWind2023RCP4.5 | Petawawa | Wind | RCP4.5 | 2023 | 76.7577 | 82.6127 | 88.7686 | 94.9348 | 101.0947
PetawawaWind2025RCP4.5 | Petawawa | Wind | RCP4.5 | 2025 | 76.7436 | 82.5962 | 88.7493 | 94.9142 | 101.0728
PetawawaWind2030RCP4.5 | Petawawa | Wind | RCP4.5 | 2030 | 76.7295 | 82.5796 | 88.73 | 94.8935 | 101.0508
PetawawaWind2035RCP4.5 | Petawawa | Wind | RCP4.5 | 2035 | 76.7154 | 82.5631 | 88.7107 | 94.8729 | 101.0288
PetawawaWind2040RCP4.5 | Petawawa | Wind | RCP4.5 | 2040 | 76.7014 | 82.5465 | 88.6915 | 94.8523 | 101.0068
PetawawaWind2045RCP4.5 | Petawawa | Wind | RCP4.5 | 2045 | 76.6873 | 82.53 | 88.6722 | 94.8316 | 100.9848
PetawawaWind2050RCP4.5 | Petawawa | Wind | RCP4.5 | 2050 | 76.747 | 82.5978 | 88.749 | 94.9157 | 101.0785
PetawawaWind2055RCP4.5 | Petawawa | Wind | RCP4.5 | 2055 | 76.8207 | 82.6823 | 88.8451 | 95.0205 | 101.1942
PetawawaWind2060RCP4.5 | Petawawa | Wind | RCP4.5 | 2060 | 76.8945 | 82.7667 | 88.9413 | 95.1252 | 101.3098
PetawawaWind2065RCP4.5 | Petawawa | Wind | RCP4.5 | 2065 | 76.9683 | 82.8511 | 89.0374 | 95.23 | 101.4255
PetawawaWind2070RCP4.5 | Petawawa | Wind | RCP4.5 | 2070 | 77.0421 | 82.9355 | 89.1335 | 95.3348 | 101.5412
PetawawaWind2075RCP4.5 | Petawawa | Wind | RCP4.5 | 2075 | 77.0882 | 82.9949 | 89.2077 | 95.4236 | 101.6426
PetawawaWind2080RCP4.5 | Petawawa | Wind | RCP4.5 | 2080 | 77.1343 | 83.0542 | 89.2818 | 95.5125 | 101.7441
PetawawaWind2085RCP4.5 | Petawawa | Wind | RCP4.5 | 2085 | 77.1804 | 83.1135 | 89.356 | 95.6014 | 101.8455
PetawawaWind2090RCP4.5 | Petawawa | Wind | RCP4.5 | 2090 | 77.2265 | 83.1728 | 89.4302 | 95.6903 | 101.947
PetawawaWind2095RCP4.5 | Petawawa | Wind | RCP4.5 | 2095 | 77.2726 | 83.2321 | 89.5043 | 95.7792 | 102.0485
PetawawaWind2100RCP4.5 | Petawawa | Wind | RCP4.5 | 2100 | 77.3187 | 83.2915 | 89.5785 | 95.868 | 102.1499
PetawawaWind2023RCP6.0 | Petawawa | Wind | RCP6.0 | 2023 | 76.7577 | 82.6127 | 88.7686 | 94.9348 | 101.0947
PetawawaWind2025RCP6.0 | Petawawa | Wind | RCP6.0 | 2025 | 76.7436 | 82.5962 | 88.7493 | 94.9142 | 101.0728
PetawawaWind2030RCP6.0 | Petawawa | Wind | RCP6.0 | 2030 | 76.7295 | 82.5796 | 88.73 | 94.8935 | 101.0508
PetawawaWind2035RCP6.0 | Petawawa | Wind | RCP6.0 | 2035 | 76.7154 | 82.5631 | 88.7107 | 94.8729 | 101.0288
PetawawaWind2040RCP6.0 | Petawawa | Wind | RCP6.0 | 2040 | 76.7014 | 82.5465 | 88.6915 | 94.8523 | 101.0068
PetawawaWind2045RCP6.0 | Petawawa | Wind | RCP6.0 | 2045 | 76.6873 | 82.53 | 88.6722 | 94.8316 | 100.9848
PetawawaWind2050RCP6.0 | Petawawa | Wind | RCP6.0 | 2050 | 76.747 | 82.5978 | 88.749 | 94.9157 | 101.0785
PetawawaWind2055RCP6.0 | Petawawa | Wind | RCP6.0 | 2055 | 76.8207 | 82.6823 | 88.8451 | 95.0205 | 101.1942
PetawawaWind2060RCP6.0 | Petawawa | Wind | RCP6.0 | 2060 | 76.8945 | 82.7667 | 88.9413 | 95.1252 | 101.3098
PetawawaWind2065RCP6.0 | Petawawa | Wind | RCP6.0 | 2065 | 76.9683 | 82.8511 | 89.0374 | 95.23 | 101.4255
PetawawaWind2070RCP6.0 | Petawawa | Wind | RCP6.0 | 2070 | 77.0421 | 82.9355 | 89.1335 | 95.3348 | 101.5412
PetawawaWind2075RCP6.0 | Petawawa | Wind | RCP6.0 | 2075 | 77.1112 | 83.0245 | 89.2447 | 95.4681 | 101.6934
PetawawaWind2080RCP6.0 | Petawawa | Wind | RCP6.0 | 2080 | 77.1804 | 83.1135 | 89.356 | 95.6014 | 101.8455
PetawawaWind2085RCP6.0 | Petawawa | Wind | RCP6.0 | 2085 | 77.2496 | 83.2025 | 89.4672 | 95.7347 | 101.9977
PetawawaWind2090RCP6.0 | Petawawa | Wind | RCP6.0 | 2090 | 77.352 | 83.3246 | 89.6111 | 95.8998 | 102.1804
PetawawaWind2095RCP6.0 | Petawawa | Wind | RCP6.0 | 2095 | 77.3853 | 83.3577 | 89.6438 | 95.9315 | 102.2108
PetawawaWind2100RCP6.0 | Petawawa | Wind | RCP6.0 | 2100 | 77.4186 | 83.3908 | 89.6764 | 95.9633 | 102.2412
PetawawaWind2023RCP8.5 | Petawawa | Wind | RCP8.5 | 2023 | 76.7577 | 82.6127 | 88.7686 | 94.9348 | 101.0947
PetawawaWind2025RCP8.5 | Petawawa | Wind | RCP8.5 | 2025 | 76.7295 | 82.5796 | 88.73 | 94.8935 | 101.0508
PetawawaWind2030RCP8.5 | Petawawa | Wind | RCP8.5 | 2030 | 76.7014 | 82.5465 | 88.6915 | 94.8523 | 101.0068
PetawawaWind2035RCP8.5 | Petawawa | Wind | RCP8.5 | 2035 | 76.6732 | 82.5134 | 88.6529 | 94.811 | 100.9628
PetawawaWind2040RCP8.5 | Petawawa | Wind | RCP8.5 | 2040 | 76.7961 | 82.6541 | 88.8131 | 94.9856 | 101.1556
PetawawaWind2045RCP8.5 | Petawawa | Wind | RCP8.5 | 2045 | 76.9191 | 82.7948 | 88.9733 | 95.1602 | 101.3484
PetawawaWind2050RCP8.5 | Petawawa | Wind | RCP8.5 | 2050 | 77.1343 | 83.0542 | 89.2818 | 95.5125 | 101.7441
PetawawaWind2055RCP8.5 | Petawawa | Wind | RCP8.5 | 2055 | 77.2265 | 83.1728 | 89.4302 | 95.6903 | 101.947
PetawawaWind2060RCP8.5 | Petawawa | Wind | RCP8.5 | 2060 | 77.352 | 83.3246 | 89.6111 | 95.8998 | 102.1804
PetawawaWind2065RCP8.5 | Petawawa | Wind | RCP8.5 | 2065 | 77.3853 | 83.3577 | 89.6438 | 95.9315 | 102.2108
PetawawaWind2070RCP8.5 | Petawawa | Wind | RCP8.5 | 2070 | 77.4109 | 83.3742 | 89.6497 | 95.9284 | 102.2007
PetawawaWind2075RCP8.5 | Petawawa | Wind | RCP8.5 | 2075 | 77.4033 | 83.3577 | 89.623 | 95.8934 | 102.1601
PetawawaWind2080RCP8.5 | Petawawa | Wind | RCP8.5 | 2080 | 77.3956 | 83.3411 | 89.5963 | 95.8585 | 102.1195
PetawawaWind2085RCP8.5 | Petawawa | Wind | RCP8.5 | 2085 | 77.3456 | 83.2666 | 89.4939 | 95.7252 | 101.9622
PetawawaWind2090RCP8.5 | Petawawa | Wind | RCP8.5 | 2090 | 77.2957 | 83.1921 | 89.3916 | 95.5919 | 101.805
PetawawaWind2095RCP8.5 | Petawawa | Wind | RCP8.5 | 2095 | 77.2957 | 83.1921 | 89.3916 | 95.5919 | 101.805
PetawawaWind2100RCP8.5 | Petawawa | Wind | RCP8.5 | 2100 | 77.2957 | 83.1921 | 89.3916 | 95.5919 | 101.805
PeterboroughIce Accretion2023RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2023 | 17.5875 | 20.999 | 25.325 | 28.6172 | 31.941
PeterboroughIce Accretion2025RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2025 | 17.6542 | 21.0958 | 25.4625 | 28.7867 | 32.1352
PeterboroughIce Accretion2030RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2030 | 17.7209 | 21.1927 | 25.6 | 28.9562 | 32.3295
PeterboroughIce Accretion2035RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2035 | 17.7876 | 21.2895 | 25.7375 | 29.1257 | 32.5237
PeterboroughIce Accretion2040RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2040 | 17.8543 | 21.3863 | 25.875 | 29.2952 | 32.718
PeterboroughIce Accretion2045RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2045 | 17.9209 | 21.4832 | 26.0125 | 29.4647 | 32.9123
PeterboroughIce Accretion2050RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2050 | 17.8867 | 21.4804 | 26.045 | 29.5212 | 32.9931
PeterboroughIce Accretion2055RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2055 | 17.7858 | 21.3808 | 25.94 | 29.4082 | 32.8797
PeterboroughIce Accretion2060RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2060 | 17.6849 | 21.2812 | 25.835 | 29.2952 | 32.7663
PeterboroughIce Accretion2065RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2065 | 17.584 | 21.1816 | 25.73 | 29.1822 | 32.6529
PeterboroughIce Accretion2070RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2070 | 17.4831 | 21.082 | 25.625 | 29.0692 | 32.5395
PeterboroughIce Accretion2075RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2075 | 17.5237 | 21.1615 | 25.7542 | 29.2387 | 32.7442
PeterboroughIce Accretion2080RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2080 | 17.5643 | 21.2411 | 25.8833 | 29.4082 | 32.949
PeterboroughIce Accretion2085RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2085 | 17.6049 | 21.3206 | 26.0125 | 29.5777 | 33.1538
PeterboroughIce Accretion2090RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2090 | 17.6455 | 21.4002 | 26.1417 | 29.7472 | 33.3585
PeterboroughIce Accretion2095RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2095 | 17.6861 | 21.4797 | 26.2708 | 29.9167 | 33.5632
PeterboroughIce Accretion2100RCP4.5 | Peterborough | Ice Accretion | RCP4.5 | 2100 | 17.7267 | 21.5592 | 26.4 | 30.0862 | 33.768
PeterboroughIce Accretion2023RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2023 | 17.5875 | 20.999 | 25.325 | 28.6172 | 31.941
PeterboroughIce Accretion2025RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2025 | 17.6542 | 21.0958 | 25.4625 | 28.7867 | 32.1352
PeterboroughIce Accretion2030RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2030 | 17.7209 | 21.1927 | 25.6 | 28.9562 | 32.3295
PeterboroughIce Accretion2035RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2035 | 17.7876 | 21.2895 | 25.7375 | 29.1257 | 32.5237
PeterboroughIce Accretion2040RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2040 | 17.8543 | 21.3863 | 25.875 | 29.2952 | 32.718
PeterboroughIce Accretion2045RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2045 | 17.9209 | 21.4832 | 26.0125 | 29.4647 | 32.9123
PeterboroughIce Accretion2050RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2050 | 17.8867 | 21.4804 | 26.045 | 29.5212 | 32.9931
PeterboroughIce Accretion2055RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2055 | 17.7858 | 21.3808 | 25.94 | 29.4082 | 32.8797
PeterboroughIce Accretion2060RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2060 | 17.6849 | 21.2812 | 25.835 | 29.2952 | 32.7663
PeterboroughIce Accretion2065RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2065 | 17.584 | 21.1816 | 25.73 | 29.1822 | 32.6529
PeterboroughIce Accretion2070RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2070 | 17.4831 | 21.082 | 25.625 | 29.0692 | 32.5395
PeterboroughIce Accretion2075RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2075 | 17.544 | 21.2013 | 25.8187 | 29.3235 | 32.8466
PeterboroughIce Accretion2080RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2080 | 17.6049 | 21.3206 | 26.0125 | 29.5777 | 33.1538
PeterboroughIce Accretion2085RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2085 | 17.6658 | 21.4399 | 26.2063 | 29.832 | 33.4609
PeterboroughIce Accretion2090RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2090 | 17.3498 | 21.1512 | 25.95 | 29.606 | 33.243
PeterboroughIce Accretion2095RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2095 | 16.9728 | 20.7431 | 25.5 | 29.1257 | 32.718
PeterboroughIce Accretion2100RCP6.0 | Peterborough | Ice Accretion | RCP6.0 | 2100 | 16.5959 | 20.335 | 25.05 | 28.6455 | 32.193
PeterboroughIce Accretion2023RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2023 | 17.5875 | 20.999 | 25.325 | 28.6172 | 31.941
PeterboroughIce Accretion2025RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2025 | 17.7209 | 21.1927 | 25.6 | 28.9562 | 32.3295
PeterboroughIce Accretion2030RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2030 | 17.8543 | 21.3863 | 25.875 | 29.2952 | 32.718
PeterboroughIce Accretion2035RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2035 | 17.9876 | 21.58 | 26.15 | 29.6342 | 33.1065
PeterboroughIce Accretion2040RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2040 | 17.8195 | 21.414 | 25.975 | 29.4459 | 32.9175
PeterboroughIce Accretion2045RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2045 | 17.6513 | 21.248 | 25.8 | 29.2576 | 32.7285
PeterboroughIce Accretion2050RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2050 | 17.5643 | 21.2411 | 25.8833 | 29.4082 | 32.949
PeterboroughIce Accretion2055RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2055 | 17.6455 | 21.4002 | 26.1417 | 29.7472 | 33.3585
PeterboroughIce Accretion2060RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2060 | 17.3498 | 21.1512 | 25.95 | 29.606 | 33.243
PeterboroughIce Accretion2065RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2065 | 16.9728 | 20.7431 | 25.5 | 29.1257 | 32.718
PeterboroughIce Accretion2070RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2070 | 16.2306 | 19.9338 | 24.6083 | 28.1558 | 31.6785
PeterboroughIce Accretion2075RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2075 | 15.8653 | 19.5327 | 24.1667 | 27.6662 | 31.164
PeterboroughIce Accretion2080RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2080 | 15.5 | 19.1315 | 23.725 | 27.1765 | 30.6495
PeterboroughIce Accretion2085RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2085 | 14.9259 | 18.4779 | 22.9625 | 26.3431 | 29.736
PeterboroughIce Accretion2090RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2090 | 14.3518 | 17.8242 | 22.2 | 25.5097 | 28.8225
PeterboroughIce Accretion2095RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2095 | 14.3518 | 17.8242 | 22.2 | 25.5097 | 28.8225
PeterboroughIce Accretion2100RCP8.5 | Peterborough | Ice Accretion | RCP8.5 | 2100 | 14.3518 | 17.8242 | 22.2 | 25.5097 | 28.8225
PeterboroughWind2023RCP4.5 | Peterborough | Wind | RCP4.5 | 2023 | 76.184 | 81.9709 | 88.044 | 94.1412 | 100.2297
PeterboroughWind2025RCP4.5 | Peterborough | Wind | RCP4.5 | 2025 | 76.1891 | 81.9832 | 88.0645 | 94.1678 | 100.2632
PeterboroughWind2030RCP4.5 | Peterborough | Wind | RCP4.5 | 2030 | 76.1941 | 81.9955 | 88.0851 | 94.1945 | 100.2966
PeterboroughWind2035RCP4.5 | Peterborough | Wind | RCP4.5 | 2035 | 76.1992 | 82.0078 | 88.1056 | 94.2212 | 100.33
PeterboroughWind2040RCP4.5 | Peterborough | Wind | RCP4.5 | 2040 | 76.2043 | 82.02 | 88.1261 | 94.2479 | 100.3635
PeterboroughWind2045RCP4.5 | Peterborough | Wind | RCP4.5 | 2045 | 76.2093 | 82.0323 | 88.1467 | 94.2746 | 100.3969
PeterboroughWind2050RCP4.5 | Peterborough | Wind | RCP4.5 | 2050 | 76.3208 | 82.1805 | 88.3397 | 94.5046 | 100.6651
PeterboroughWind2055RCP4.5 | Peterborough | Wind | RCP4.5 | 2055 | 76.4272 | 82.3163 | 88.5122 | 94.708 | 100.8998
PeterboroughWind2060RCP4.5 | Peterborough | Wind | RCP4.5 | 2060 | 76.5336 | 82.4522 | 88.6846 | 94.9114 | 101.1346
PeterboroughWind2065RCP4.5 | Peterborough | Wind | RCP4.5 | 2065 | 76.6399 | 82.588 | 88.8571 | 95.1148 | 101.3693
PeterboroughWind2070RCP4.5 | Peterborough | Wind | RCP4.5 | 2070 | 76.7463 | 82.7239 | 89.0296 | 95.3182 | 101.6041
PeterboroughWind2075RCP4.5 | Peterborough | Wind | RCP4.5 | 2075 | 76.8476 | 82.8562 | 89.2012 | 95.5238 | 101.8449
PeterboroughWind2080RCP4.5 | Peterborough | Wind | RCP4.5 | 2080 | 76.9489 | 82.9885 | 89.3728 | 95.7293 | 102.0856
PeterboroughWind2085RCP4.5 | Peterborough | Wind | RCP4.5 | 2085 | 77.0503 | 83.1208 | 89.5444 | 95.9349 | 102.3264
PeterboroughWind2090RCP4.5 | Peterborough | Wind | RCP4.5 | 2090 | 77.1516 | 83.2531 | 89.716 | 96.1405 | 102.5672
PeterboroughWind2095RCP4.5 | Peterborough | Wind | RCP4.5 | 2095 | 77.2529 | 83.3854 | 89.8876 | 96.3461 | 102.8079
PeterboroughWind2100RCP4.5 | Peterborough | Wind | RCP4.5 | 2100 | 77.3542 | 83.5177 | 90.0592 | 96.5517 | 103.0487
PeterboroughWind2023RCP6.0 | Peterborough | Wind | RCP6.0 | 2023 | 76.184 | 81.9709 | 88.044 | 94.1412 | 100.2297
PeterboroughWind2025RCP6.0 | Peterborough | Wind | RCP6.0 | 2025 | 76.1891 | 81.9832 | 88.0645 | 94.1678 | 100.2632
PeterboroughWind2030RCP6.0 | Peterborough | Wind | RCP6.0 | 2030 | 76.1941 | 81.9955 | 88.0851 | 94.1945 | 100.2966
PeterboroughWind2035RCP6.0 | Peterborough | Wind | RCP6.0 | 2035 | 76.1992 | 82.0078 | 88.1056 | 94.2212 | 100.33
PeterboroughWind2040RCP6.0 | Peterborough | Wind | RCP6.0 | 2040 | 76.2043 | 82.02 | 88.1261 | 94.2479 | 100.3635
PeterboroughWind2045RCP6.0 | Peterborough | Wind | RCP6.0 | 2045 | 76.2093 | 82.0323 | 88.1467 | 94.2746 | 100.3969
PeterboroughWind2050RCP6.0 | Peterborough | Wind | RCP6.0 | 2050 | 76.3208 | 82.1805 | 88.3397 | 94.5046 | 100.6651
PeterboroughWind2055RCP6.0 | Peterborough | Wind | RCP6.0 | 2055 | 76.4272 | 82.3163 | 88.5122 | 94.708 | 100.8998
PeterboroughWind2060RCP6.0 | Peterborough | Wind | RCP6.0 | 2060 | 76.5336 | 82.4522 | 88.6846 | 94.9114 | 101.1346
PeterboroughWind2065RCP6.0 | Peterborough | Wind | RCP6.0 | 2065 | 76.6399 | 82.588 | 88.8571 | 95.1148 | 101.3693
PeterboroughWind2070RCP6.0 | Peterborough | Wind | RCP6.0 | 2070 | 76.7463 | 82.7239 | 89.0296 | 95.3182 | 101.6041
PeterboroughWind2075RCP6.0 | Peterborough | Wind | RCP6.0 | 2075 | 76.8983 | 82.9223 | 89.287 | 95.6265 | 101.9652
PeterboroughWind2080RCP6.0 | Peterborough | Wind | RCP6.0 | 2080 | 77.0503 | 83.1208 | 89.5444 | 95.9349 | 102.3264
PeterboroughWind2085RCP6.0 | Peterborough | Wind | RCP6.0 | 2085 | 77.2022 | 83.3193 | 89.8018 | 96.2433 | 102.6876
PeterboroughWind2090RCP6.0 | Peterborough | Wind | RCP6.0 | 2090 | 77.6506 | 83.886 | 90.5197 | 97.0915 | 103.6673
PeterboroughWind2095RCP6.0 | Peterborough | Wind | RCP6.0 | 2095 | 77.9469 | 84.2543 | 90.9803 | 97.6314 | 104.286
PeterboroughWind2100RCP6.0 | Peterborough | Wind | RCP6.0 | 2100 | 78.2433 | 84.6226 | 91.4408 | 98.1712 | 104.9046
PeterboroughWind2023RCP8.5 | Peterborough | Wind | RCP8.5 | 2023 | 76.184 | 81.9709 | 88.044 | 94.1412 | 100.2297
PeterboroughWind2025RCP8.5 | Peterborough | Wind | RCP8.5 | 2025 | 76.1941 | 81.9955 | 88.0851 | 94.1945 | 100.2966
PeterboroughWind2030RCP8.5 | Peterborough | Wind | RCP8.5 | 2030 | 76.2043 | 82.02 | 88.1261 | 94.2479 | 100.3635
PeterboroughWind2035RCP8.5 | Peterborough | Wind | RCP8.5 | 2035 | 76.2144 | 82.0446 | 88.1672 | 94.3012 | 100.4304
PeterboroughWind2040RCP8.5 | Peterborough | Wind | RCP8.5 | 2040 | 76.3917 | 82.271 | 88.4547 | 94.6402 | 100.8216
PeterboroughWind2045RCP8.5 | Peterborough | Wind | RCP8.5 | 2045 | 76.569 | 82.4974 | 88.7421 | 94.9792 | 101.2128
PeterboroughWind2050RCP8.5 | Peterborough | Wind | RCP8.5 | 2050 | 76.9489 | 82.9885 | 89.3728 | 95.7293 | 102.0856
PeterboroughWind2055RCP8.5 | Peterborough | Wind | RCP8.5 | 2055 | 77.1516 | 83.2531 | 89.716 | 96.1405 | 102.5672
PeterboroughWind2060RCP8.5 | Peterborough | Wind | RCP8.5 | 2060 | 77.6506 | 83.886 | 90.5197 | 97.0915 | 103.6673
PeterboroughWind2065RCP8.5 | Peterborough | Wind | RCP8.5 | 2065 | 77.9469 | 84.2543 | 90.9803 | 97.6314 | 104.286
PeterboroughWind2070RCP8.5 | Peterborough | Wind | RCP8.5 | 2070 | 78.2458 | 84.6417 | 91.4789 | 98.2214 | 104.9748
PeterboroughWind2075RCP8.5 | Peterborough | Wind | RCP8.5 | 2075 | 78.2483 | 84.6608 | 91.5171 | 98.2717 | 105.0451
PeterboroughWind2080RCP8.5 | Peterborough | Wind | RCP8.5 | 2080 | 78.2508 | 84.6798 | 91.5552 | 98.3219 | 105.1153
PeterboroughWind2085RCP8.5 | Peterborough | Wind | RCP8.5 | 2085 | 78.4218 | 84.9254 | 91.8984 | 98.7503 | 105.6219
PeterboroughWind2090RCP8.5 | Peterborough | Wind | RCP8.5 | 2090 | 78.5928 | 85.1709 | 92.2416 | 99.1787 | 106.1285
PeterboroughWind2095RCP8.5 | Peterborough | Wind | RCP8.5 | 2095 | 78.5928 | 85.1709 | 92.2416 | 99.1787 | 106.1285
PeterboroughWind2100RCP8.5 | Peterborough | Wind | RCP8.5 | 2100 | 78.5928 | 85.1709 | 92.2416 | 99.1787 | 106.1285
PetroliaIce Accretion2023RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2023 | 14.7422 | 17.6939 | 21.428 | 24.2634 | 27.1102
PetroliaIce Accretion2025RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2025 | 14.6835 | 17.6361 | 21.3693 | 24.2054 | 27.0501
PetroliaIce Accretion2030RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2030 | 14.6248 | 17.5783 | 21.3107 | 24.1473 | 26.99
PetroliaIce Accretion2035RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2035 | 14.5661 | 17.5205 | 21.252 | 24.0893 | 26.93
PetroliaIce Accretion2040RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2040 | 14.5075 | 17.4626 | 21.1933 | 24.0313 | 26.8699
PetroliaIce Accretion2045RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2045 | 14.4488 | 17.4048 | 21.1347 | 23.9733 | 26.8099
PetroliaIce Accretion2050RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2050 | 14.1207 | 17.0475 | 20.7328 | 23.5424 | 26.3451
PetroliaIce Accretion2055RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2055 | 13.8512 | 16.7481 | 20.3896 | 23.1695 | 25.9404
PetroliaIce Accretion2060RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2060 | 13.5818 | 16.4486 | 20.0464 | 22.7966 | 25.5357
PetroliaIce Accretion2065RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2065 | 13.3124 | 16.1491 | 19.7032 | 22.4237 | 25.131
PetroliaIce Accretion2070RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2070 | 13.0429 | 15.8497 | 19.36 | 22.0508 | 24.7262
PetroliaIce Accretion2075RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2075 | 12.9205 | 15.7219 | 19.228 | 21.9099 | 24.5784
PetroliaIce Accretion2080RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2080 | 12.798 | 15.594 | 19.096 | 21.7691 | 24.4306
PetroliaIce Accretion2085RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2085 | 12.6755 | 15.4662 | 18.964 | 21.6282 | 24.2827
PetroliaIce Accretion2090RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2090 | 12.5531 | 15.3384 | 18.832 | 21.4873 | 24.1349
PetroliaIce Accretion2095RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2095 | 12.4306 | 15.2106 | 18.7 | 21.3465 | 23.987
PetroliaIce Accretion2100RCP4.5 | Petrolia | Ice Accretion | RCP4.5 | 2100 | 12.3081 | 15.0828 | 18.568 | 21.2056 | 23.8392
PetroliaIce Accretion2023RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2023 | 14.7422 | 17.6939 | 21.428 | 24.2634 | 27.1102
PetroliaIce Accretion2025RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2025 | 14.6835 | 17.6361 | 21.3693 | 24.2054 | 27.0501
PetroliaIce Accretion2030RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2030 | 14.6248 | 17.5783 | 21.3107 | 24.1473 | 26.99
PetroliaIce Accretion2035RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2035 | 14.5661 | 17.5205 | 21.252 | 24.0893 | 26.93
PetroliaIce Accretion2040RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2040 | 14.5075 | 17.4626 | 21.1933 | 24.0313 | 26.8699
PetroliaIce Accretion2045RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2045 | 14.4488 | 17.4048 | 21.1347 | 23.9733 | 26.8099
PetroliaIce Accretion2050RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2050 | 14.1207 | 17.0475 | 20.7328 | 23.5424 | 26.3451
PetroliaIce Accretion2055RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2055 | 13.8512 | 16.7481 | 20.3896 | 23.1695 | 25.9404
PetroliaIce Accretion2060RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2060 | 13.5818 | 16.4486 | 20.0464 | 22.7966 | 25.5357
PetroliaIce Accretion2065RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2065 | 13.3124 | 16.1491 | 19.7032 | 22.4237 | 25.131
PetroliaIce Accretion2070RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2070 | 13.0429 | 15.8497 | 19.36 | 22.0508 | 24.7262
PetroliaIce Accretion2075RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2075 | 12.8592 | 15.6579 | 19.162 | 21.8395 | 24.5045
PetroliaIce Accretion2080RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2080 | 12.6755 | 15.4662 | 18.964 | 21.6282 | 24.2827
PetroliaIce Accretion2085RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2085 | 12.4918 | 15.2745 | 18.766 | 21.4169 | 24.061
PetroliaIce Accretion2090RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2090 | 11.9356 | 14.6628 | 18.084 | 20.6669 | 23.2478
PetroliaIce Accretion2095RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2095 | 11.5631 | 14.2428 | 17.6 | 20.1283 | 22.6565
PetroliaIce Accretion2100RCP6.0 | Petrolia | Ice Accretion | RCP6.0 | 2100 | 11.1906 | 13.8228 | 17.116 | 19.5897 | 22.0651
PetroliaIce Accretion2023RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2023 | 14.7422 | 17.6939 | 21.428 | 24.2634 | 27.1102
PetroliaIce Accretion2025RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2025 | 14.6248 | 17.5783 | 21.3107 | 24.1473 | 26.99
PetroliaIce Accretion2030RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2030 | 14.5075 | 17.4626 | 21.1933 | 24.0313 | 26.8699
PetroliaIce Accretion2035RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2035 | 14.3901 | 17.347 | 21.076 | 23.9153 | 26.7498
PetroliaIce Accretion2040RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2040 | 13.941 | 16.8479 | 20.504 | 23.2938 | 26.0753
PetroliaIce Accretion2045RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2045 | 13.492 | 16.3488 | 19.932 | 22.6723 | 25.4008
PetroliaIce Accretion2050RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2050 | 12.798 | 15.594 | 19.096 | 21.7691 | 24.4306
PetroliaIce Accretion2055RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2055 | 12.5531 | 15.3384 | 18.832 | 21.4873 | 24.1349
PetroliaIce Accretion2060RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2060 | 11.9356 | 14.6628 | 18.084 | 20.6669 | 23.2478
PetroliaIce Accretion2065RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2065 | 11.5631 | 14.2428 | 17.6 | 20.1283 | 22.6565
PetroliaIce Accretion2070RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2070 | 10.8997 | 13.5063 | 16.7567 | 19.2085 | 21.6493
PetroliaIce Accretion2075RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2075 | 10.6089 | 13.1898 | 16.3973 | 18.8273 | 21.2335
PetroliaIce Accretion2080RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2080 | 10.318 | 12.8733 | 16.038 | 18.4461 | 20.8177
PetroliaIce Accretion2085RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2085 | 9.6138 | 12.0333 | 15.037 | 17.3026 | 19.5565
PetroliaIce Accretion2090RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2090 | 8.9096 | 11.1934 | 14.036 | 16.159 | 18.2952
PetroliaIce Accretion2095RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2095 | 8.9096 | 11.1934 | 14.036 | 16.159 | 18.2952
PetroliaIce Accretion2100RCP8.5 | Petrolia | Ice Accretion | RCP8.5 | 2100 | 8.9096 | 11.1934 | 14.036 | 16.159 | 18.2952
PetroliaWind2023RCP4.5 | Petrolia | Wind | RCP4.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
PetroliaWind2025RCP4.5 | Petrolia | Wind | RCP4.5 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
PetroliaWind2030RCP4.5 | Petrolia | Wind | RCP4.5 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
PetroliaWind2035RCP4.5 | Petrolia | Wind | RCP4.5 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
PetroliaWind2040RCP4.5 | Petrolia | Wind | RCP4.5 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
PetroliaWind2045RCP4.5 | Petrolia | Wind | RCP4.5 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
PetroliaWind2050RCP4.5 | Petrolia | Wind | RCP4.5 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
PetroliaWind2055RCP4.5 | Petrolia | Wind | RCP4.5 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
PetroliaWind2060RCP4.5 | Petrolia | Wind | RCP4.5 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
PetroliaWind2065RCP4.5 | Petrolia | Wind | RCP4.5 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
PetroliaWind2070RCP4.5 | Petrolia | Wind | RCP4.5 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
PetroliaWind2075RCP4.5 | Petrolia | Wind | RCP4.5 | 2075 | 85.7411 | 92.542 | 99.746 | 106.9048 | 114.0736
PetroliaWind2080RCP4.5 | Petrolia | Wind | RCP4.5 | 2080 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
PetroliaWind2085RCP4.5 | Petrolia | Wind | RCP4.5 | 2085 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
PetroliaWind2090RCP4.5 | Petrolia | Wind | RCP4.5 | 2090 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
PetroliaWind2095RCP4.5 | Petrolia | Wind | RCP4.5 | 2095 | 86.3278 | 93.3015 | 100.7326 | 108.0792 | 115.444
PetroliaWind2100RCP4.5 | Petrolia | Wind | RCP4.5 | 2100 | 86.4745 | 93.4914 | 100.9792 | 108.3728 | 115.7866
PetroliaWind2023RCP6.0 | Petrolia | Wind | RCP6.0 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
PetroliaWind2025RCP6.0 | Petrolia | Wind | RCP6.0 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
PetroliaWind2030RCP6.0 | Petrolia | Wind | RCP6.0 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
PetroliaWind2035RCP6.0 | Petrolia | Wind | RCP6.0 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
PetroliaWind2040RCP6.0 | Petrolia | Wind | RCP6.0 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
PetroliaWind2045RCP6.0 | Petrolia | Wind | RCP6.0 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
PetroliaWind2050RCP6.0 | Petrolia | Wind | RCP6.0 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
PetroliaWind2055RCP6.0 | Petrolia | Wind | RCP6.0 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
PetroliaWind2060RCP6.0 | Petrolia | Wind | RCP6.0 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
PetroliaWind2065RCP6.0 | Petrolia | Wind | RCP6.0 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
PetroliaWind2070RCP6.0 | Petrolia | Wind | RCP6.0 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
PetroliaWind2075RCP6.0 | Petrolia | Wind | RCP6.0 | 2075 | 85.8144 | 92.637 | 99.8693 | 107.0516 | 114.2449
PetroliaWind2080RCP6.0 | Petrolia | Wind | RCP6.0 | 2080 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
PetroliaWind2085RCP6.0 | Petrolia | Wind | RCP6.0 | 2085 | 86.2545 | 93.2066 | 100.6093 | 107.9324 | 115.2727
PetroliaWind2090RCP6.0 | Petrolia | Wind | RCP6.0 | 2090 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
PetroliaWind2095RCP6.0 | Petrolia | Wind | RCP6.0 | 2095 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
PetroliaWind2100RCP6.0 | Petrolia | Wind | RCP6.0 | 2100 | 87.5746 | 94.8494 | 102.6452 | 110.3127 | 117.9987
PetroliaWind2023RCP8.5 | Petrolia | Wind | RCP8.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
PetroliaWind2025RCP8.5 | Petrolia | Wind | RCP8.5 | 2025 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
PetroliaWind2030RCP8.5 | Petrolia | Wind | RCP8.5 | 2030 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
PetroliaWind2035RCP8.5 | Petrolia | Wind | RCP8.5 | 2035 | 85.586 | 92.3248 | 99.4504 | 106.5378 | 113.6304
PetroliaWind2040RCP8.5 | Petrolia | Wind | RCP8.5 | 2040 | 85.5888 | 92.3339 | 99.4667 | 106.5622 | 113.6639
PetroliaWind2045RCP8.5 | Petrolia | Wind | RCP8.5 | 2045 | 85.5916 | 92.343 | 99.4831 | 106.5867 | 113.6974
PetroliaWind2050RCP8.5 | Petrolia | Wind | RCP8.5 | 2050 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
PetroliaWind2055RCP8.5 | Petrolia | Wind | RCP8.5 | 2055 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
PetroliaWind2060RCP8.5 | Petrolia | Wind | RCP8.5 | 2060 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
PetroliaWind2065RCP8.5 | Petrolia | Wind | RCP8.5 | 2065 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
PetroliaWind2070RCP8.5 | Petrolia | Wind | RCP8.5 | 2070 | 87.882 | 95.2383 | 103.1385 | 110.8929 | 118.669
PetroliaWind2075RCP8.5 | Petrolia | Wind | RCP8.5 | 2075 | 88.1895 | 95.6271 | 103.6317 | 111.4732 | 119.3393
PetroliaWind2080RCP8.5 | Petrolia | Wind | RCP8.5 | 2080 | 88.4969 | 96.016 | 104.125 | 112.0534 | 120.0096
PetroliaWind2085RCP8.5 | Petrolia | Wind | RCP8.5 | 2085 | 88.8396 | 96.4489 | 104.664 | 112.6826 | 120.7358
PetroliaWind2090RCP8.5 | Petrolia | Wind | RCP8.5 | 2090 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
PetroliaWind2095RCP8.5 | Petrolia | Wind | RCP8.5 | 2095 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
PetroliaWind2100RCP8.5 | Petrolia | Wind | RCP8.5 | 2100 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
Pickering (Dunbarton)Ice Accretion2023RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
Pickering (Dunbarton)Ice Accretion2025RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
Pickering (Dunbarton)Ice Accretion2030RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
Pickering (Dunbarton)Ice Accretion2035RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
Pickering (Dunbarton)Ice Accretion2040RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
Pickering (Dunbarton)Ice Accretion2045RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
Pickering (Dunbarton)Ice Accretion2050RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
Pickering (Dunbarton)Ice Accretion2055RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
Pickering (Dunbarton)Ice Accretion2060RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
Pickering (Dunbarton)Ice Accretion2065RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
Pickering (Dunbarton)Ice Accretion2070RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
Pickering (Dunbarton)Ice Accretion2075RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
Pickering (Dunbarton)Ice Accretion2080RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
Pickering (Dunbarton)Ice Accretion2085RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
Pickering (Dunbarton)Ice Accretion2090RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
Pickering (Dunbarton)Ice Accretion2095RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
Pickering (Dunbarton)Ice Accretion2100RCP4.5 | Pickering (Dunbarton) | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
Pickering (Dunbarton)Ice Accretion2023RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
Pickering (Dunbarton)Ice Accretion2025RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
Pickering (Dunbarton)Ice Accretion2030RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
Pickering (Dunbarton)Ice Accretion2035RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
Pickering (Dunbarton)Ice Accretion2040RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
Pickering (Dunbarton)Ice Accretion2045RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
Pickering (Dunbarton)Ice Accretion2050RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
Pickering (Dunbarton)Ice Accretion2055RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
Pickering (Dunbarton)Ice Accretion2060RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
Pickering (Dunbarton)Ice Accretion2065RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
Pickering (Dunbarton)Ice Accretion2070RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
Pickering (Dunbarton)Ice Accretion2075RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
Pickering (Dunbarton)Ice Accretion2080RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
Pickering (Dunbarton)Ice Accretion2085RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
Pickering (Dunbarton)Ice Accretion2090RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
Pickering (Dunbarton)Ice Accretion2095RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
Pickering (Dunbarton)Ice Accretion2100RCP6.0 | Pickering (Dunbarton) | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
Pickering (Dunbarton)Ice Accretion2023RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
Pickering (Dunbarton)Ice Accretion2025RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
Pickering (Dunbarton)Ice Accretion2030RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
Pickering (Dunbarton)Ice Accretion2035RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
Pickering (Dunbarton)Ice Accretion2040RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
Pickering (Dunbarton)Ice Accretion2045RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
Pickering (Dunbarton)Ice Accretion2050RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
Pickering (Dunbarton)Ice Accretion2055RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
Pickering (Dunbarton)Ice Accretion2060RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
Pickering (Dunbarton)Ice Accretion2065RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
Pickering (Dunbarton)Ice Accretion2070RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
Pickering (Dunbarton)Ice Accretion2075RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
Pickering (Dunbarton)Ice Accretion2080RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
Pickering (Dunbarton)Ice Accretion2085RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
Pickering (Dunbarton)Ice Accretion2090RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
Pickering (Dunbarton)Ice Accretion2095RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
Pickering (Dunbarton)Ice Accretion2100RCP8.5 | Pickering (Dunbarton) | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
Pickering (Dunbarton)Wind2023RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2023 | 84.8244 | 91.3223 | 98.1568 | 104.9963 | 111.8317
Pickering (Dunbarton)Wind2025RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2025 | 84.8399 | 91.3557 | 98.2107 | 105.068 | 111.9211
Pickering (Dunbarton)Wind2030RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2030 | 84.8554 | 91.3891 | 98.2646 | 105.1396 | 112.0105
Pickering (Dunbarton)Wind2035RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2035 | 84.8709 | 91.4225 | 98.3185 | 105.2113 | 112.0998
Pickering (Dunbarton)Wind2040RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2040 | 84.8864 | 91.456 | 98.3724 | 105.2829 | 112.1892
Pickering (Dunbarton)Wind2045RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2045 | 84.9019 | 91.4894 | 98.4263 | 105.3546 | 112.2786
Pickering (Dunbarton)Wind2050RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2050 | 85.0004 | 91.6267 | 98.6115 | 105.5793 | 112.5467
Pickering (Dunbarton)Wind2055RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2055 | 85.0833 | 91.7306 | 98.7428 | 105.7324 | 112.7255
Pickering (Dunbarton)Wind2060RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2060 | 85.1662 | 91.8345 | 98.8742 | 105.8855 | 112.9042
Pickering (Dunbarton)Wind2065RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2065 | 85.2492 | 91.9384 | 99.0055 | 106.0386 | 113.083
Pickering (Dunbarton)Wind2070RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2070 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2617
Pickering (Dunbarton)Wind2075RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2075 | 85.476 | 92.2276 | 99.3736 | 106.4731 | 113.5876
Pickering (Dunbarton)Wind2080RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2080 | 85.6198 | 92.4129 | 99.6105 | 106.7545 | 113.9134
Pickering (Dunbarton)Wind2085RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2085 | 85.7637 | 92.5982 | 99.8473 | 107.0358 | 114.2393
Pickering (Dunbarton)Wind2090RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2090 | 85.9075 | 92.7836 | 100.0841 | 107.3172 | 114.5651
Pickering (Dunbarton)Wind2095RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2095 | 86.0514 | 92.9689 | 100.321 | 107.5986 | 114.891
Pickering (Dunbarton)Wind2100RCP4.5 | Pickering (Dunbarton) | Wind | RCP4.5 | 2100 | 86.1952 | 93.1542 | 100.5578 | 107.88 | 115.2168
Pickering (Dunbarton)Wind2023RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2023 | 84.8244 | 91.3223 | 98.1568 | 104.9963 | 111.8317
Pickering (Dunbarton)Wind2025RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2025 | 84.8399 | 91.3557 | 98.2107 | 105.068 | 111.9211
Pickering (Dunbarton)Wind2030RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2030 | 84.8554 | 91.3891 | 98.2646 | 105.1396 | 112.0105
Pickering (Dunbarton)Wind2035RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2035 | 84.8709 | 91.4225 | 98.3185 | 105.2113 | 112.0998
Pickering (Dunbarton)Wind2040RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2040 | 84.8864 | 91.456 | 98.3724 | 105.2829 | 112.1892
Pickering (Dunbarton)Wind2045RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2045 | 84.9019 | 91.4894 | 98.4263 | 105.3546 | 112.2786
Pickering (Dunbarton)Wind2050RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2050 | 85.0004 | 91.6267 | 98.6115 | 105.5793 | 112.5467
Pickering (Dunbarton)Wind2055RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2055 | 85.0833 | 91.7306 | 98.7428 | 105.7324 | 112.7255
Pickering (Dunbarton)Wind2060RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2060 | 85.1662 | 91.8345 | 98.8742 | 105.8855 | 112.9042
Pickering (Dunbarton)Wind2065RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2065 | 85.2492 | 91.9384 | 99.0055 | 106.0386 | 113.083
Pickering (Dunbarton)Wind2070RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2070 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2617
Pickering (Dunbarton)Wind2075RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2075 | 85.5479 | 92.3203 | 99.4921 | 106.6138 | 113.7505
Pickering (Dunbarton)Wind2080RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2080 | 85.7637 | 92.5982 | 99.8473 | 107.0358 | 114.2393
Pickering (Dunbarton)Wind2085RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2085 | 85.9794 | 92.8762 | 100.2026 | 107.4579 | 114.7281
Pickering (Dunbarton)Wind2090RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2090 | 86.6409 | 93.701 | 101.234 | 108.6664 | 116.118
Pickering (Dunbarton)Wind2095RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2095 | 87.0866 | 94.2479 | 101.9102 | 109.4529 | 117.0193
Pickering (Dunbarton)Wind2100RCP6.0 | Pickering (Dunbarton) | Wind | RCP6.0 | 2100 | 87.5322 | 94.7947 | 102.5864 | 110.2393 | 117.9205
Pickering (Dunbarton)Wind2023RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2023 | 84.8244 | 91.3223 | 98.1568 | 104.9963 | 111.8317
Pickering (Dunbarton)Wind2025RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2025 | 84.8554 | 91.3891 | 98.2646 | 105.1396 | 112.0105
Pickering (Dunbarton)Wind2030RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2030 | 84.8864 | 91.456 | 98.3724 | 105.2829 | 112.1892
Pickering (Dunbarton)Wind2035RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2035 | 84.9175 | 91.5228 | 98.4802 | 105.4262 | 112.368
Pickering (Dunbarton)Wind2040RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2040 | 85.0557 | 91.696 | 98.6991 | 105.6814 | 112.6659
Pickering (Dunbarton)Wind2045RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2045 | 85.1939 | 91.8691 | 98.9179 | 105.9366 | 112.9638
Pickering (Dunbarton)Wind2050RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2050 | 85.6198 | 92.4129 | 99.6105 | 106.7545 | 113.9134
Pickering (Dunbarton)Wind2055RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2055 | 85.9075 | 92.7836 | 100.0841 | 107.3172 | 114.5651
Pickering (Dunbarton)Wind2060RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2060 | 86.6409 | 93.701 | 101.234 | 108.6664 | 116.118
Pickering (Dunbarton)Wind2065RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2065 | 87.0866 | 94.2479 | 101.9102 | 109.4529 | 117.0193
Pickering (Dunbarton)Wind2070RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2070 | 87.6648 | 94.974 | 102.8249 | 110.5329 | 118.2631
Pickering (Dunbarton)Wind2075RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2075 | 87.7974 | 95.1532 | 103.0633 | 110.8265 | 118.6057
Pickering (Dunbarton)Wind2080RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2080 | 87.93 | 95.3324 | 103.3018 | 111.1201 | 118.9483
Pickering (Dunbarton)Wind2085RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2085 | 88.2135 | 95.7335 | 103.8506 | 111.7912 | 119.7471
Pickering (Dunbarton)Wind2090RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2090 | 88.4969 | 96.1345 | 104.3994 | 112.4624 | 120.5459
Pickering (Dunbarton)Wind2095RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2095 | 88.4969 | 96.1345 | 104.3994 | 112.4624 | 120.5459
Pickering (Dunbarton)Wind2100RCP8.5 | Pickering (Dunbarton) | Wind | RCP8.5 | 2100 | 88.4969 | 96.1345 | 104.3994 | 112.4624 | 120.5459
PictonIce Accretion2023RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
PictonIce Accretion2025RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
PictonIce Accretion2030RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
PictonIce Accretion2035RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
PictonIce Accretion2040RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
PictonIce Accretion2045RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
PictonIce Accretion2050RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
PictonIce Accretion2055RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
PictonIce Accretion2060RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
PictonIce Accretion2065RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
PictonIce Accretion2070RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
PictonIce Accretion2075RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2075 | 16.8859 | 20.3972 | 24.8292 | 28.2123 | 31.5682
PictonIce Accretion2080RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2080 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
PictonIce Accretion2085RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2085 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
PictonIce Accretion2090RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2090 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
PictonIce Accretion2095RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2095 | 16.7235 | 20.3142 | 24.8458 | 28.2877 | 31.7152
PictonIce Accretion2100RCP4.5 | Picton | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.2935 | 24.85 | 28.3065 | 31.752
PictonIce Accretion2023RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
PictonIce Accretion2025RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
PictonIce Accretion2030RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
PictonIce Accretion2035RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
PictonIce Accretion2040RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
PictonIce Accretion2045RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
PictonIce Accretion2050RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
PictonIce Accretion2055RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
PictonIce Accretion2060RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
PictonIce Accretion2065RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
PictonIce Accretion2070RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
PictonIce Accretion2075RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2075 | 16.8656 | 20.3869 | 24.8313 | 28.2217 | 31.5866
PictonIce Accretion2080RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2080 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
PictonIce Accretion2085RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2085 | 16.7438 | 20.3246 | 24.8438 | 28.2782 | 31.6969
PictonIce Accretion2090RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2090 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
PictonIce Accretion2095RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2095 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
PictonIce Accretion2100RCP6.0 | Picton | Ice Accretion | RCP6.0 | 2100 | 15.6565 | 19.173 | 23.6 | 26.9505 | 30.2715
PictonIce Accretion2023RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
PictonIce Accretion2025RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2025 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
PictonIce Accretion2030RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2030 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
PictonIce Accretion2035RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2035 | 17.6745 | 21.2272 | 25.725 | 29.154 | 32.571
PictonIce Accretion2040RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2040 | 17.4251 | 20.9575 | 25.425 | 28.8338 | 32.2245
PictonIce Accretion2045RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2045 | 17.1758 | 20.6877 | 25.125 | 28.5137 | 31.878
PictonIce Accretion2050RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2050 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
PictonIce Accretion2055RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2055 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
PictonIce Accretion2060RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2060 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
PictonIce Accretion2065RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2065 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
PictonIce Accretion2070RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2070 | 15.2216 | 18.6888 | 23.05 | 26.3478 | 29.631
PictonIce Accretion2075RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2075 | 14.7867 | 18.2047 | 22.5 | 25.7452 | 28.9905
PictonIce Accretion2080RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2080 | 14.3518 | 17.7205 | 21.95 | 25.1425 | 28.35
PictonIce Accretion2085RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2085 | 13.6908 | 16.9424 | 21.025 | 24.0972 | 27.1845
PictonIce Accretion2090RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2090 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
PictonIce Accretion2095RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2095 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
PictonIce Accretion2100RCP8.5 | Picton | Ice Accretion | RCP8.5 | 2100 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
PictonWind2023RCP4.5 | Picton | Wind | RCP4.5 | 2023 | 91.2096 | 98.2554 | 105.6615 | 113.069 | 120.478
PictonWind2025RCP4.5 | Picton | Wind | RCP4.5 | 2025 | 91.1749 | 98.218 | 105.6248 | 113.0297 | 120.4381
PictonWind2030RCP4.5 | Picton | Wind | RCP4.5 | 2030 | 91.1401 | 98.1806 | 105.588 | 112.9904 | 120.3982
PictonWind2035RCP4.5 | Picton | Wind | RCP4.5 | 2035 | 91.1054 | 98.1431 | 105.5513 | 112.9511 | 120.3583
PictonWind2040RCP4.5 | Picton | Wind | RCP4.5 | 2040 | 91.0706 | 98.1057 | 105.5145 | 112.9117 | 120.3184
PictonWind2045RCP4.5 | Picton | Wind | RCP4.5 | 2045 | 91.0359 | 98.0683 | 105.4778 | 112.8724 | 120.2785
PictonWind2050RCP4.5 | Picton | Wind | RCP4.5 | 2050 | 91.1299 | 98.2027 | 105.6657 | 113.1027 | 120.5547
PictonWind2055RCP4.5 | Picton | Wind | RCP4.5 | 2055 | 91.2586 | 98.3746 | 105.8904 | 113.3724 | 120.8707
PictonWind2060RCP4.5 | Picton | Wind | RCP4.5 | 2060 | 91.3874 | 98.5464 | 106.1151 | 113.642 | 121.1867
PictonWind2065RCP4.5 | Picton | Wind | RCP4.5 | 2065 | 91.5161 | 98.7183 | 106.3398 | 113.9117 | 121.5027
PictonWind2070RCP4.5 | Picton | Wind | RCP4.5 | 2070 | 91.6448 | 98.8902 | 106.5645 | 114.1813 | 121.8187
PictonWind2075RCP4.5 | Picton | Wind | RCP4.5 | 2075 | 91.7098 | 98.9797 | 106.6835 | 114.3255 | 121.9883
PictonWind2080RCP4.5 | Picton | Wind | RCP4.5 | 2080 | 91.7748 | 99.0692 | 106.8025 | 114.4697 | 122.1578
PictonWind2085RCP4.5 | Picton | Wind | RCP4.5 | 2085 | 91.8398 | 99.1587 | 106.9215 | 114.6139 | 122.3274
PictonWind2090RCP4.5 | Picton | Wind | RCP4.5 | 2090 | 91.9048 | 99.2482 | 107.0405 | 114.758 | 122.497
PictonWind2095RCP4.5 | Picton | Wind | RCP4.5 | 2095 | 91.9697 | 99.3377 | 107.1595 | 114.9022 | 122.6666
PictonWind2100RCP4.5 | Picton | Wind | RCP4.5 | 2100 | 92.0347 | 99.4272 | 107.2785 | 115.0464 | 122.8361
PictonWind2023RCP6.0 | Picton | Wind | RCP6.0 | 2023 | 91.2096 | 98.2554 | 105.6615 | 113.069 | 120.478
PictonWind2025RCP6.0 | Picton | Wind | RCP6.0 | 2025 | 91.1749 | 98.218 | 105.6248 | 113.0297 | 120.4381
PictonWind2030RCP6.0 | Picton | Wind | RCP6.0 | 2030 | 91.1401 | 98.1806 | 105.588 | 112.9904 | 120.3982
PictonWind2035RCP6.0 | Picton | Wind | RCP6.0 | 2035 | 91.1054 | 98.1431 | 105.5513 | 112.9511 | 120.3583
PictonWind2040RCP6.0 | Picton | Wind | RCP6.0 | 2040 | 91.0706 | 98.1057 | 105.5145 | 112.9117 | 120.3184
PictonWind2045RCP6.0 | Picton | Wind | RCP6.0 | 2045 | 91.0359 | 98.0683 | 105.4778 | 112.8724 | 120.2785
PictonWind2050RCP6.0 | Picton | Wind | RCP6.0 | 2050 | 91.1299 | 98.2027 | 105.6657 | 113.1027 | 120.5547
PictonWind2055RCP6.0 | Picton | Wind | RCP6.0 | 2055 | 91.2586 | 98.3746 | 105.8904 | 113.3724 | 120.8707
PictonWind2060RCP6.0 | Picton | Wind | RCP6.0 | 2060 | 91.3874 | 98.5464 | 106.1151 | 113.642 | 121.1867
PictonWind2065RCP6.0 | Picton | Wind | RCP6.0 | 2065 | 91.5161 | 98.7183 | 106.3398 | 113.9117 | 121.5027
PictonWind2070RCP6.0 | Picton | Wind | RCP6.0 | 2070 | 91.6448 | 98.8902 | 106.5645 | 114.1813 | 121.8187
PictonWind2075RCP6.0 | Picton | Wind | RCP6.0 | 2075 | 91.7423 | 99.0244 | 106.743 | 114.3976 | 122.0731
PictonWind2080RCP6.0 | Picton | Wind | RCP6.0 | 2080 | 91.8398 | 99.1587 | 106.9215 | 114.6139 | 122.3274
PictonWind2085RCP6.0 | Picton | Wind | RCP6.0 | 2085 | 91.9372 | 99.293 | 107.1 | 114.8301 | 122.5818
PictonWind2090RCP6.0 | Picton | Wind | RCP6.0 | 2090 | 92.346 | 99.8048 | 107.7405 | 115.5857 | 123.4466
PictonWind2095RCP6.0 | Picton | Wind | RCP6.0 | 2095 | 92.6573 | 100.1824 | 108.2025 | 116.125 | 124.0571
PictonWind2100RCP6.0 | Picton | Wind | RCP6.0 | 2100 | 92.9686 | 100.56 | 108.6645 | 116.6642 | 124.6676
PictonWind2023RCP8.5 | Picton | Wind | RCP8.5 | 2023 | 91.2096 | 98.2554 | 105.6615 | 113.069 | 120.478
PictonWind2025RCP8.5 | Picton | Wind | RCP8.5 | 2025 | 91.1401 | 98.1806 | 105.588 | 112.9904 | 120.3982
PictonWind2030RCP8.5 | Picton | Wind | RCP8.5 | 2030 | 91.0706 | 98.1057 | 105.5145 | 112.9117 | 120.3184
PictonWind2035RCP8.5 | Picton | Wind | RCP8.5 | 2035 | 91.0011 | 98.0308 | 105.441 | 112.8331 | 120.2386
PictonWind2040RCP8.5 | Picton | Wind | RCP8.5 | 2040 | 91.2157 | 98.3173 | 105.8155 | 113.2825 | 120.7653
PictonWind2045RCP8.5 | Picton | Wind | RCP8.5 | 2045 | 91.4303 | 98.6037 | 106.19 | 113.7319 | 121.292
PictonWind2050RCP8.5 | Picton | Wind | RCP8.5 | 2050 | 91.7748 | 99.0692 | 106.8025 | 114.4697 | 122.1578
PictonWind2055RCP8.5 | Picton | Wind | RCP8.5 | 2055 | 91.9048 | 99.2482 | 107.0405 | 114.758 | 122.497
PictonWind2060RCP8.5 | Picton | Wind | RCP8.5 | 2060 | 92.346 | 99.8048 | 107.7405 | 115.5857 | 123.4466
PictonWind2065RCP8.5 | Picton | Wind | RCP8.5 | 2065 | 92.6573 | 100.1824 | 108.2025 | 116.125 | 124.0571
PictonWind2070RCP8.5 | Picton | Wind | RCP8.5 | 2070 | 92.8839 | 100.4656 | 108.556 | 116.5444 | 124.5399
PictonWind2075RCP8.5 | Picton | Wind | RCP8.5 | 2075 | 92.7993 | 100.3712 | 108.4475 | 116.4246 | 124.4122
PictonWind2080RCP8.5 | Picton | Wind | RCP8.5 | 2080 | 92.7147 | 100.2768 | 108.339 | 116.3047 | 124.2845
PictonWind2085RCP8.5 | Picton | Wind | RCP8.5 | 2085 | 92.9368 | 100.6137 | 108.822 | 116.9058 | 125.0087
PictonWind2090RCP8.5 | Picton | Wind | RCP8.5 | 2090 | 93.159 | 100.9506 | 109.305 | 117.5069 | 125.7329
PictonWind2095RCP8.5 | Picton | Wind | RCP8.5 | 2095 | 93.159 | 100.9506 | 109.305 | 117.5069 | 125.7329
PictonWind2100RCP8.5 | Picton | Wind | RCP8.5 | 2100 | 93.159 | 100.9506 | 109.305 | 117.5069 | 125.7329
PlattsvilleIce Accretion2023RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2023 | 18.3933 | 22.0514 | 26.676 | 30.2049 | 33.7478
PlattsvilleIce Accretion2025RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2025 | 18.3557 | 22.0178 | 26.6445 | 30.1795 | 33.7195
PlattsvilleIce Accretion2030RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2030 | 18.3181 | 21.9842 | 26.613 | 30.154 | 33.6911
PlattsvilleIce Accretion2035RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2035 | 18.2806 | 21.9506 | 26.5815 | 30.1286 | 33.6628
PlattsvilleIce Accretion2040RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2040 | 18.243 | 21.917 | 26.55 | 30.1032 | 33.6344
PlattsvilleIce Accretion2045RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2045 | 18.2054 | 21.8834 | 26.5185 | 30.0778 | 33.6061
PlattsvilleIce Accretion2050RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2050 | 18.0514 | 21.7377 | 26.3844 | 29.9486 | 33.4825
PlattsvilleIce Accretion2055RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2055 | 17.9349 | 21.6257 | 26.2818 | 29.8449 | 33.3872
PlattsvilleIce Accretion2060RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2060 | 17.8184 | 21.5136 | 26.1792 | 29.7411 | 33.292
PlattsvilleIce Accretion2065RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2065 | 17.7019 | 21.4016 | 26.0766 | 29.6374 | 33.1967
PlattsvilleIce Accretion2070RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2070 | 17.5854 | 21.2895 | 25.974 | 29.5337 | 33.1015
PlattsvilleIce Accretion2075RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2075 | 17.5353 | 21.2522 | 25.956 | 29.5286 | 33.1071
PlattsvilleIce Accretion2080RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2080 | 17.4852 | 21.2148 | 25.938 | 29.5235 | 33.1128
PlattsvilleIce Accretion2085RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2085 | 17.4351 | 21.1775 | 25.92 | 29.5184 | 33.1185
PlattsvilleIce Accretion2090RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2090 | 17.385 | 21.1401 | 25.902 | 29.5133 | 33.1241
PlattsvilleIce Accretion2095RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2095 | 17.3349 | 21.1028 | 25.884 | 29.5083 | 33.1298
PlattsvilleIce Accretion2100RCP4.5 | Plattsville | Ice Accretion | RCP4.5 | 2100 | 17.2848 | 21.0654 | 25.866 | 29.5032 | 33.1355
PlattsvilleIce Accretion2023RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2023 | 18.3933 | 22.0514 | 26.676 | 30.2049 | 33.7478
PlattsvilleIce Accretion2025RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2025 | 18.3557 | 22.0178 | 26.6445 | 30.1795 | 33.7195
PlattsvilleIce Accretion2030RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2030 | 18.3181 | 21.9842 | 26.613 | 30.154 | 33.6911
PlattsvilleIce Accretion2035RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2035 | 18.2806 | 21.9506 | 26.5815 | 30.1286 | 33.6628
PlattsvilleIce Accretion2040RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2040 | 18.243 | 21.917 | 26.55 | 30.1032 | 33.6344
PlattsvilleIce Accretion2045RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2045 | 18.2054 | 21.8834 | 26.5185 | 30.0778 | 33.6061
PlattsvilleIce Accretion2050RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2050 | 18.0514 | 21.7377 | 26.3844 | 29.9486 | 33.4825
PlattsvilleIce Accretion2055RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2055 | 17.9349 | 21.6257 | 26.2818 | 29.8449 | 33.3872
PlattsvilleIce Accretion2060RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2060 | 17.8184 | 21.5136 | 26.1792 | 29.7411 | 33.292
PlattsvilleIce Accretion2065RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2065 | 17.7019 | 21.4016 | 26.0766 | 29.6374 | 33.1967
PlattsvilleIce Accretion2070RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2070 | 17.5854 | 21.2895 | 25.974 | 29.5337 | 33.1015
PlattsvilleIce Accretion2075RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2075 | 17.5103 | 21.2335 | 25.947 | 29.5261 | 33.11
PlattsvilleIce Accretion2080RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2080 | 17.4351 | 21.1775 | 25.92 | 29.5184 | 33.1185
PlattsvilleIce Accretion2085RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2085 | 17.36 | 21.1214 | 25.893 | 29.5108 | 33.127
PlattsvilleIce Accretion2090RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2090 | 16.8965 | 20.6471 | 25.389 | 28.9947 | 32.5798
PlattsvilleIce Accretion2095RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2095 | 16.5083 | 20.2288 | 24.912 | 28.4862 | 32.0242
PlattsvilleIce Accretion2100RCP6.0 | Plattsville | Ice Accretion | RCP6.0 | 2100 | 16.12 | 19.8104 | 24.435 | 27.9777 | 31.4685
PlattsvilleIce Accretion2023RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2023 | 18.3933 | 22.0514 | 26.676 | 30.2049 | 33.7478
PlattsvilleIce Accretion2025RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2025 | 18.3181 | 21.9842 | 26.613 | 30.154 | 33.6911
PlattsvilleIce Accretion2030RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2030 | 18.243 | 21.917 | 26.55 | 30.1032 | 33.6344
PlattsvilleIce Accretion2035RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2035 | 18.1678 | 21.8498 | 26.487 | 30.0523 | 33.5777
PlattsvilleIce Accretion2040RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2040 | 17.9737 | 21.663 | 26.316 | 29.8795 | 33.419
PlattsvilleIce Accretion2045RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2045 | 17.7796 | 21.4763 | 26.145 | 29.7066 | 33.2602
PlattsvilleIce Accretion2050RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2050 | 17.4852 | 21.2148 | 25.938 | 29.5235 | 33.1128
PlattsvilleIce Accretion2055RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2055 | 17.385 | 21.1401 | 25.902 | 29.5133 | 33.1241
PlattsvilleIce Accretion2060RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2060 | 16.8965 | 20.6471 | 25.389 | 28.9947 | 32.5798
PlattsvilleIce Accretion2065RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2065 | 16.5083 | 20.2288 | 24.912 | 28.4862 | 32.0242
PlattsvilleIce Accretion2070RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2070 | 15.7818 | 19.4444 | 24.039 | 27.5505 | 31.0149
PlattsvilleIce Accretion2075RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2075 | 15.4436 | 19.0784 | 23.643 | 27.1234 | 30.5613
PlattsvilleIce Accretion2080RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2080 | 15.1054 | 18.7124 | 23.247 | 26.6962 | 30.1077
PlattsvilleIce Accretion2085RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2085 | 14.2694 | 17.7487 | 22.113 | 25.4148 | 28.7129
PlattsvilleIce Accretion2090RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2090 | 13.4333 | 16.7851 | 20.979 | 24.1334 | 27.3181
PlattsvilleIce Accretion2095RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2095 | 13.4333 | 16.7851 | 20.979 | 24.1334 | 27.3181
PlattsvilleIce Accretion2100RCP8.5 | Plattsville | Ice Accretion | RCP8.5 | 2100 | 13.4333 | 16.7851 | 20.979 | 24.1334 | 27.3181
PlattsvilleWind2023RCP4.5 | Plattsville | Wind | RCP4.5 | 2023 | 85.3829 | 92.1152 | 99.2446 | 106.3385 | 113.4405
PlattsvilleWind2025RCP4.5 | Plattsville | Wind | RCP4.5 | 2025 | 85.4618 | 92.22 | 99.3802 | 106.5011 | 113.6304
PlattsvilleWind2030RCP4.5 | Plattsville | Wind | RCP4.5 | 2030 | 85.5408 | 92.3248 | 99.5157 | 106.6636 | 113.8203
PlattsvilleWind2035RCP4.5 | Plattsville | Wind | RCP4.5 | 2035 | 85.6198 | 92.4296 | 99.6513 | 106.8261 | 114.0103
PlattsvilleWind2040RCP4.5 | Plattsville | Wind | RCP4.5 | 2040 | 85.6988 | 92.5344 | 99.7869 | 106.9887 | 114.2002
PlattsvilleWind2045RCP4.5 | Plattsville | Wind | RCP4.5 | 2045 | 85.7778 | 92.6393 | 99.9224 | 107.1512 | 114.3901
PlattsvilleWind2050RCP4.5 | Plattsville | Wind | RCP4.5 | 2050 | 85.9244 | 92.8261 | 100.1619 | 107.4333 | 114.7163
PlattsvilleWind2055RCP4.5 | Plattsville | Wind | RCP4.5 | 2055 | 85.9921 | 92.9081 | 100.2658 | 107.5528 | 114.8526
PlattsvilleWind2060RCP4.5 | Plattsville | Wind | RCP4.5 | 2060 | 86.0598 | 92.9901 | 100.3696 | 107.6723 | 114.9889
PlattsvilleWind2065RCP4.5 | Plattsville | Wind | RCP4.5 | 2065 | 86.1275 | 93.0722 | 100.4735 | 107.7919 | 115.1252
PlattsvilleWind2070RCP4.5 | Plattsville | Wind | RCP4.5 | 2070 | 86.1952 | 93.1542 | 100.5774 | 107.9114 | 115.2615
PlattsvilleWind2075RCP4.5 | Plattsville | Wind | RCP4.5 | 2075 | 86.2799 | 93.2712 | 100.7358 | 108.1054 | 115.4924
PlattsvilleWind2080RCP4.5 | Plattsville | Wind | RCP4.5 | 2080 | 86.3645 | 93.3881 | 100.8943 | 108.2994 | 115.7233
PlattsvilleWind2085RCP4.5 | Plattsville | Wind | RCP4.5 | 2085 | 86.4491 | 93.5051 | 101.0527 | 108.4934 | 115.9542
PlattsvilleWind2090RCP4.5 | Plattsville | Wind | RCP4.5 | 2090 | 86.5337 | 93.622 | 101.2111 | 108.6874 | 116.1851
PlattsvilleWind2095RCP4.5 | Plattsville | Wind | RCP4.5 | 2095 | 86.6183 | 93.739 | 101.3696 | 108.8814 | 116.416
PlattsvilleWind2100RCP4.5 | Plattsville | Wind | RCP4.5 | 2100 | 86.703 | 93.856 | 101.528 | 109.0754 | 116.6469
PlattsvilleWind2023RCP6.0 | Plattsville | Wind | RCP6.0 | 2023 | 85.3829 | 92.1152 | 99.2446 | 106.3385 | 113.4405
PlattsvilleWind2025RCP6.0 | Plattsville | Wind | RCP6.0 | 2025 | 85.4618 | 92.22 | 99.3802 | 106.5011 | 113.6304
PlattsvilleWind2030RCP6.0 | Plattsville | Wind | RCP6.0 | 2030 | 85.5408 | 92.3248 | 99.5157 | 106.6636 | 113.8203
PlattsvilleWind2035RCP6.0 | Plattsville | Wind | RCP6.0 | 2035 | 85.6198 | 92.4296 | 99.6513 | 106.8261 | 114.0103
PlattsvilleWind2040RCP6.0 | Plattsville | Wind | RCP6.0 | 2040 | 85.6988 | 92.5344 | 99.7869 | 106.9887 | 114.2002
PlattsvilleWind2045RCP6.0 | Plattsville | Wind | RCP6.0 | 2045 | 85.7778 | 92.6393 | 99.9224 | 107.1512 | 114.3901
PlattsvilleWind2050RCP6.0 | Plattsville | Wind | RCP6.0 | 2050 | 85.9244 | 92.8261 | 100.1619 | 107.4333 | 114.7163
PlattsvilleWind2055RCP6.0 | Plattsville | Wind | RCP6.0 | 2055 | 85.9921 | 92.9081 | 100.2658 | 107.5528 | 114.8526
PlattsvilleWind2060RCP6.0 | Plattsville | Wind | RCP6.0 | 2060 | 86.0598 | 92.9901 | 100.3696 | 107.6723 | 114.9889
PlattsvilleWind2065RCP6.0 | Plattsville | Wind | RCP6.0 | 2065 | 86.1275 | 93.0722 | 100.4735 | 107.7919 | 115.1252
PlattsvilleWind2070RCP6.0 | Plattsville | Wind | RCP6.0 | 2070 | 86.1952 | 93.1542 | 100.5774 | 107.9114 | 115.2615
PlattsvilleWind2075RCP6.0 | Plattsville | Wind | RCP6.0 | 2075 | 86.3222 | 93.3296 | 100.815 | 108.2024 | 115.6079
PlattsvilleWind2080RCP6.0 | Plattsville | Wind | RCP6.0 | 2080 | 86.4491 | 93.5051 | 101.0527 | 108.4934 | 115.9542
PlattsvilleWind2085RCP6.0 | Plattsville | Wind | RCP6.0 | 2085 | 86.576 | 93.6805 | 101.2904 | 108.7844 | 116.3005
PlattsvilleWind2090RCP6.0 | Plattsville | Wind | RCP6.0 | 2090 | 87.0499 | 94.3026 | 102.0964 | 109.7465 | 117.4252
PlattsvilleWind2095RCP6.0 | Plattsville | Wind | RCP6.0 | 2095 | 87.3969 | 94.7491 | 102.6648 | 110.4176 | 118.2035
PlattsvilleWind2100RCP6.0 | Plattsville | Wind | RCP6.0 | 2100 | 87.7438 | 95.1957 | 103.2332 | 111.0887 | 118.9818
PlattsvilleWind2023RCP8.5 | Plattsville | Wind | RCP8.5 | 2023 | 85.3829 | 92.1152 | 99.2446 | 106.3385 | 113.4405
PlattsvilleWind2025RCP8.5 | Plattsville | Wind | RCP8.5 | 2025 | 85.5408 | 92.3248 | 99.5157 | 106.6636 | 113.8203
PlattsvilleWind2030RCP8.5 | Plattsville | Wind | RCP8.5 | 2030 | 85.6988 | 92.5344 | 99.7869 | 106.9887 | 114.2002
PlattsvilleWind2035RCP8.5 | Plattsville | Wind | RCP8.5 | 2035 | 85.8567 | 92.7441 | 100.058 | 107.3137 | 114.58
PlattsvilleWind2040RCP8.5 | Plattsville | Wind | RCP8.5 | 2040 | 85.9696 | 92.8808 | 100.2311 | 107.513 | 114.8072
PlattsvilleWind2045RCP8.5 | Plattsville | Wind | RCP8.5 | 2045 | 86.0824 | 93.0175 | 100.4043 | 107.7122 | 115.0344
PlattsvilleWind2050RCP8.5 | Plattsville | Wind | RCP8.5 | 2050 | 86.3645 | 93.3881 | 100.8943 | 108.2994 | 115.7233
PlattsvilleWind2055RCP8.5 | Plattsville | Wind | RCP8.5 | 2055 | 86.5337 | 93.622 | 101.2111 | 108.6874 | 116.1851
PlattsvilleWind2060RCP8.5 | Plattsville | Wind | RCP8.5 | 2060 | 87.0499 | 94.3026 | 102.0964 | 109.7465 | 117.4252
PlattsvilleWind2065RCP8.5 | Plattsville | Wind | RCP8.5 | 2065 | 87.3969 | 94.7491 | 102.6648 | 110.4176 | 118.2035
PlattsvilleWind2070RCP8.5 | Plattsville | Wind | RCP8.5 | 2070 | 87.9638 | 95.4904 | 103.6219 | 111.5571 | 119.533
PlattsvilleWind2075RCP8.5 | Plattsville | Wind | RCP8.5 | 2075 | 88.1838 | 95.7851 | 104.0107 | 112.0254 | 120.0841
PlattsvilleWind2080RCP8.5 | Plattsville | Wind | RCP8.5 | 2080 | 88.4038 | 96.0798 | 104.3994 | 112.4938 | 120.6353
PlattsvilleWind2085RCP8.5 | Plattsville | Wind | RCP8.5 | 2085 | 88.8354 | 96.6449 | 105.1393 | 113.3799 | 121.6687
PlattsvilleWind2090RCP8.5 | Plattsville | Wind | RCP8.5 | 2090 | 89.267 | 97.2099 | 105.8792 | 114.2659 | 122.7021
PlattsvilleWind2095RCP8.5 | Plattsville | Wind | RCP8.5 | 2095 | 89.267 | 97.2099 | 105.8792 | 114.2659 | 122.7021
PlattsvilleWind2100RCP8.5 | Plattsville | Wind | RCP8.5 | 2100 | 89.267 | 97.2099 | 105.8792 | 114.2659 | 122.7021
Point AlexanderIce Accretion2023RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2023 | 14.4458 | 17.2806 | 20.88 | 23.6396 | 26.3844
Point AlexanderIce Accretion2025RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2025 | 14.5014 | 17.347 | 20.9567 | 23.7225 | 26.4768
Point AlexanderIce Accretion2030RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2030 | 14.5571 | 17.4134 | 21.0333 | 23.8053 | 26.5692
Point AlexanderIce Accretion2035RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2035 | 14.6128 | 17.4798 | 21.11 | 23.8882 | 26.6616
Point AlexanderIce Accretion2040RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2040 | 14.6684 | 17.5462 | 21.1867 | 23.9711 | 26.754
Point AlexanderIce Accretion2045RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2045 | 14.7241 | 17.6126 | 21.2633 | 24.0539 | 26.8464
Point AlexanderIce Accretion2050RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2050 | 14.777 | 17.6856 | 21.364 | 24.173 | 26.9892
Point AlexanderIce Accretion2055RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2055 | 14.7742 | 17.6923 | 21.388 | 24.2091 | 27.0396
Point AlexanderIce Accretion2060RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2060 | 14.7714 | 17.6989 | 21.412 | 24.2453 | 27.09
Point AlexanderIce Accretion2065RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2065 | 14.7686 | 17.7056 | 21.436 | 24.2814 | 27.1404
Point AlexanderIce Accretion2070RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2070 | 14.7659 | 17.7122 | 21.46 | 24.3176 | 27.1908
Point AlexanderIce Accretion2075RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2075 | 14.7496 | 17.7011 | 21.4567 | 24.3176 | 27.1908
Point AlexanderIce Accretion2080RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2080 | 14.7334 | 17.6901 | 21.4533 | 24.3176 | 27.1908
Point AlexanderIce Accretion2085RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2085 | 14.7171 | 17.679 | 21.45 | 24.3176 | 27.1908
Point AlexanderIce Accretion2090RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2090 | 14.7009 | 17.6679 | 21.4467 | 24.3176 | 27.1908
Point AlexanderIce Accretion2095RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2095 | 14.6847 | 17.6569 | 21.4433 | 24.3176 | 27.1908
Point AlexanderIce Accretion2100RCP4.5 | Point Alexander | Ice Accretion | RCP4.5 | 2100 | 14.6684 | 17.6458 | 21.44 | 24.3176 | 27.1908
Point AlexanderIce Accretion2023RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2023 | 14.4458 | 17.2806 | 20.88 | 23.6396 | 26.3844
Point AlexanderIce Accretion2025RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2025 | 14.5014 | 17.347 | 20.9567 | 23.7225 | 26.4768
Point AlexanderIce Accretion2030RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2030 | 14.5571 | 17.4134 | 21.0333 | 23.8053 | 26.5692
Point AlexanderIce Accretion2035RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2035 | 14.6128 | 17.4798 | 21.11 | 23.8882 | 26.6616
Point AlexanderIce Accretion2040RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2040 | 14.6684 | 17.5462 | 21.1867 | 23.9711 | 26.754
Point AlexanderIce Accretion2045RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2045 | 14.7241 | 17.6126 | 21.2633 | 24.0539 | 26.8464
Point AlexanderIce Accretion2050RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2050 | 14.777 | 17.6856 | 21.364 | 24.173 | 26.9892
Point AlexanderIce Accretion2055RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2055 | 14.7742 | 17.6923 | 21.388 | 24.2091 | 27.0396
Point AlexanderIce Accretion2060RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2060 | 14.7714 | 17.6989 | 21.412 | 24.2453 | 27.09
Point AlexanderIce Accretion2065RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2065 | 14.7686 | 17.7056 | 21.436 | 24.2814 | 27.1404
Point AlexanderIce Accretion2070RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2070 | 14.7659 | 17.7122 | 21.46 | 24.3176 | 27.1908
Point AlexanderIce Accretion2075RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2075 | 14.7415 | 17.6956 | 21.455 | 24.3176 | 27.1908
Point AlexanderIce Accretion2080RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2080 | 14.7171 | 17.679 | 21.45 | 24.3176 | 27.1908
Point AlexanderIce Accretion2085RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2085 | 14.6928 | 17.6624 | 21.445 | 24.3176 | 27.1908
Point AlexanderIce Accretion2090RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2090 | 14.6777 | 17.6901 | 21.5267 | 24.4457 | 27.3588
Point AlexanderIce Accretion2095RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2095 | 14.687 | 17.7343 | 21.6133 | 24.5737 | 27.5268
Point AlexanderIce Accretion2100RCP6.0 | Point Alexander | Ice Accretion | RCP6.0 | 2100 | 14.6963 | 17.7786 | 21.7 | 24.7018 | 27.6948
Point AlexanderIce Accretion2023RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2023 | 14.4458 | 17.2806 | 20.88 | 23.6396 | 26.3844
Point AlexanderIce Accretion2025RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2025 | 14.5571 | 17.4134 | 21.0333 | 23.8053 | 26.5692
Point AlexanderIce Accretion2030RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2030 | 14.6684 | 17.5462 | 21.1867 | 23.9711 | 26.754
Point AlexanderIce Accretion2035RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2035 | 14.7798 | 17.679 | 21.34 | 24.1368 | 26.9388
Point AlexanderIce Accretion2040RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2040 | 14.7751 | 17.6901 | 21.38 | 24.1971 | 27.0228
Point AlexanderIce Accretion2045RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2045 | 14.7705 | 17.7011 | 21.42 | 24.2573 | 27.1068
Point AlexanderIce Accretion2050RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2050 | 14.7334 | 17.6901 | 21.4533 | 24.3176 | 27.1908
Point AlexanderIce Accretion2055RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2055 | 14.7009 | 17.6679 | 21.4467 | 24.3176 | 27.1908
Point AlexanderIce Accretion2060RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2060 | 14.6777 | 17.6901 | 21.5267 | 24.4457 | 27.3588
Point AlexanderIce Accretion2065RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2065 | 14.687 | 17.7343 | 21.6133 | 24.5737 | 27.5268
Point AlexanderIce Accretion2070RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2070 | 14.6684 | 17.7675 | 21.7 | 24.7093 | 27.7116
Point AlexanderIce Accretion2075RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2075 | 14.6406 | 17.7565 | 21.7 | 24.7169 | 27.7284
Point AlexanderIce Accretion2080RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2080 | 14.6128 | 17.7454 | 21.7 | 24.7244 | 27.7452
Point AlexanderIce Accretion2085RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2085 | 14.3623 | 17.4715 | 21.4 | 24.3967 | 27.3924
Point AlexanderIce Accretion2090RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2090 | 14.1118 | 17.1976 | 21.1 | 24.069 | 27.0396
Point AlexanderIce Accretion2095RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2095 | 14.1118 | 17.1976 | 21.1 | 24.069 | 27.0396
Point AlexanderIce Accretion2100RCP8.5 | Point Alexander | Ice Accretion | RCP8.5 | 2100 | 14.1118 | 17.1976 | 21.1 | 24.069 | 27.0396
Point AlexanderWind2023RCP4.5 | Point Alexander | Wind | RCP4.5 | 2023 | 77.3571 | 83.2997 | 89.5429 | 95.7919 | 102.0383
Point AlexanderWind2025RCP4.5 | Point Alexander | Wind | RCP4.5 | 2025 | 77.4173 | 83.3604 | 89.6037 | 95.8538 | 102.1026
Point AlexanderWind2030RCP4.5 | Point Alexander | Wind | RCP4.5 | 2030 | 77.4775 | 83.4211 | 89.6645 | 95.9157 | 102.1668
Point AlexanderWind2035RCP4.5 | Point Alexander | Wind | RCP4.5 | 2035 | 77.5377 | 83.4818 | 89.7253 | 95.9776 | 102.2311
Point AlexanderWind2040RCP4.5 | Point Alexander | Wind | RCP4.5 | 2040 | 77.5979 | 83.5425 | 89.7862 | 96.0395 | 102.2954
Point AlexanderWind2045RCP4.5 | Point Alexander | Wind | RCP4.5 | 2045 | 77.6581 | 83.6032 | 89.847 | 96.1014 | 102.3596
Point AlexanderWind2050RCP4.5 | Point Alexander | Wind | RCP4.5 | 2050 | 77.7937 | 83.755 | 90.0164 | 96.289 | 102.5639
Point AlexanderWind2055RCP4.5 | Point Alexander | Wind | RCP4.5 | 2055 | 77.869 | 83.846 | 90.125 | 96.4147 | 102.7039
Point AlexanderWind2060RCP4.5 | Point Alexander | Wind | RCP4.5 | 2060 | 77.9443 | 83.9371 | 90.2335 | 96.5404 | 102.8439
Point AlexanderWind2065RCP4.5 | Point Alexander | Wind | RCP4.5 | 2065 | 78.0196 | 84.0281 | 90.3421 | 96.6661 | 102.9839
Point AlexanderWind2070RCP4.5 | Point Alexander | Wind | RCP4.5 | 2070 | 78.0949 | 84.1192 | 90.4507 | 96.7918 | 103.1239
Point AlexanderWind2075RCP4.5 | Point Alexander | Wind | RCP4.5 | 2075 | 78.1884 | 84.2336 | 90.5916 | 96.9537 | 103.31
Point AlexanderWind2080RCP4.5 | Point Alexander | Wind | RCP4.5 | 2080 | 78.2819 | 84.3481 | 90.7325 | 97.1156 | 103.496
Point AlexanderWind2085RCP4.5 | Point Alexander | Wind | RCP4.5 | 2085 | 78.3754 | 84.4626 | 90.8734 | 97.2774 | 103.682
Point AlexanderWind2090RCP4.5 | Point Alexander | Wind | RCP4.5 | 2090 | 78.4689 | 84.5771 | 91.0144 | 97.4393 | 103.868
Point AlexanderWind2095RCP4.5 | Point Alexander | Wind | RCP4.5 | 2095 | 78.5624 | 84.6916 | 91.1553 | 97.6012 | 104.054
Point AlexanderWind2100RCP4.5 | Point Alexander | Wind | RCP4.5 | 2100 | 78.6559 | 84.8061 | 91.2962 | 97.7631 | 104.24
Point AlexanderWind2023RCP6.0 | Point Alexander | Wind | RCP6.0 | 2023 | 77.3571 | 83.2997 | 89.5429 | 95.7919 | 102.0383
Point AlexanderWind2025RCP6.0 | Point Alexander | Wind | RCP6.0 | 2025 | 77.4173 | 83.3604 | 89.6037 | 95.8538 | 102.1026
Point AlexanderWind2030RCP6.0 | Point Alexander | Wind | RCP6.0 | 2030 | 77.4775 | 83.4211 | 89.6645 | 95.9157 | 102.1668
Point AlexanderWind2035RCP6.0 | Point Alexander | Wind | RCP6.0 | 2035 | 77.5377 | 83.4818 | 89.7253 | 95.9776 | 102.2311
Point AlexanderWind2040RCP6.0 | Point Alexander | Wind | RCP6.0 | 2040 | 77.5979 | 83.5425 | 89.7862 | 96.0395 | 102.2954
Point AlexanderWind2045RCP6.0 | Point Alexander | Wind | RCP6.0 | 2045 | 77.6581 | 83.6032 | 89.847 | 96.1014 | 102.3596
Point AlexanderWind2050RCP6.0 | Point Alexander | Wind | RCP6.0 | 2050 | 77.7937 | 83.755 | 90.0164 | 96.289 | 102.5639
Point AlexanderWind2055RCP6.0 | Point Alexander | Wind | RCP6.0 | 2055 | 77.869 | 83.846 | 90.125 | 96.4147 | 102.7039
Point AlexanderWind2060RCP6.0 | Point Alexander | Wind | RCP6.0 | 2060 | 77.9443 | 83.9371 | 90.2335 | 96.5404 | 102.8439
Point AlexanderWind2065RCP6.0 | Point Alexander | Wind | RCP6.0 | 2065 | 78.0196 | 84.0281 | 90.3421 | 96.6661 | 102.9839
Point AlexanderWind2070RCP6.0 | Point Alexander | Wind | RCP6.0 | 2070 | 78.0949 | 84.1192 | 90.4507 | 96.7918 | 103.1239
Point AlexanderWind2075RCP6.0 | Point Alexander | Wind | RCP6.0 | 2075 | 78.2352 | 84.2909 | 90.6621 | 97.0346 | 103.403
Point AlexanderWind2080RCP6.0 | Point Alexander | Wind | RCP6.0 | 2080 | 78.3754 | 84.4626 | 90.8734 | 97.2774 | 103.682
Point AlexanderWind2085RCP6.0 | Point Alexander | Wind | RCP6.0 | 2085 | 78.5157 | 84.6344 | 91.0848 | 97.5203 | 103.961
Point AlexanderWind2090RCP6.0 | Point Alexander | Wind | RCP6.0 | 2090 | 78.7481 | 84.9303 | 91.4653 | 97.9663 | 104.4767
Point AlexanderWind2095RCP6.0 | Point Alexander | Wind | RCP6.0 | 2095 | 78.8403 | 85.0545 | 91.6344 | 98.1694 | 104.7135
Point AlexanderWind2100RCP6.0 | Point Alexander | Wind | RCP6.0 | 2100 | 78.9326 | 85.1786 | 91.8035 | 98.3726 | 104.9502
Point AlexanderWind2023RCP8.5 | Point Alexander | Wind | RCP8.5 | 2023 | 77.3571 | 83.2997 | 89.5429 | 95.7919 | 102.0383
Point AlexanderWind2025RCP8.5 | Point Alexander | Wind | RCP8.5 | 2025 | 77.4775 | 83.4211 | 89.6645 | 95.9157 | 102.1668
Point AlexanderWind2030RCP8.5 | Point Alexander | Wind | RCP8.5 | 2030 | 77.5979 | 83.5425 | 89.7862 | 96.0395 | 102.2954
Point AlexanderWind2035RCP8.5 | Point Alexander | Wind | RCP8.5 | 2035 | 77.7183 | 83.6639 | 89.9078 | 96.1633 | 102.4239
Point AlexanderWind2040RCP8.5 | Point Alexander | Wind | RCP8.5 | 2040 | 77.8439 | 83.8157 | 90.0888 | 96.3728 | 102.6572
Point AlexanderWind2045RCP8.5 | Point Alexander | Wind | RCP8.5 | 2045 | 77.9694 | 83.9674 | 90.2697 | 96.5823 | 102.8906
Point AlexanderWind2050RCP8.5 | Point Alexander | Wind | RCP8.5 | 2050 | 78.2819 | 84.3481 | 90.7325 | 97.1156 | 103.496
Point AlexanderWind2055RCP8.5 | Point Alexander | Wind | RCP8.5 | 2055 | 78.4689 | 84.5771 | 91.0144 | 97.4393 | 103.868
Point AlexanderWind2060RCP8.5 | Point Alexander | Wind | RCP8.5 | 2060 | 78.7481 | 84.9303 | 91.4653 | 97.9663 | 104.4767
Point AlexanderWind2065RCP8.5 | Point Alexander | Wind | RCP8.5 | 2065 | 78.8403 | 85.0545 | 91.6344 | 98.1694 | 104.7135
Point AlexanderWind2070RCP8.5 | Point Alexander | Wind | RCP8.5 | 2070 | 78.9556 | 85.1841 | 91.7798 | 98.3313 | 104.8893
Point AlexanderWind2075RCP8.5 | Point Alexander | Wind | RCP8.5 | 2075 | 78.9787 | 85.1896 | 91.756 | 98.2901 | 104.8285
Point AlexanderWind2080RCP8.5 | Point Alexander | Wind | RCP8.5 | 2080 | 79.0017 | 85.1952 | 91.7323 | 98.2488 | 104.7676
Point AlexanderWind2085RCP8.5 | Point Alexander | Wind | RCP8.5 | 2085 | 79.0517 | 85.2531 | 91.799 | 98.3202 | 104.8488
Point AlexanderWind2090RCP8.5 | Point Alexander | Wind | RCP8.5 | 2090 | 79.1016 | 85.311 | 91.8658 | 98.3916 | 104.9299
Point AlexanderWind2095RCP8.5 | Point Alexander | Wind | RCP8.5 | 2095 | 79.1016 | 85.311 | 91.8658 | 98.3916 | 104.9299
Point AlexanderWind2100RCP8.5 | Point Alexander | Wind | RCP8.5 | 2100 | 79.1016 | 85.311 | 91.8658 | 98.3916 | 104.9299
Port BurwellIce Accretion2023RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2023 | 20.3326 | 24.402 | 29.55 | 33.4932 | 37.422
Port BurwellIce Accretion2025RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2025 | 20.2213 | 24.2816 | 29.42 | 33.352 | 37.2708
Port BurwellIce Accretion2030RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2030 | 20.11 | 24.1613 | 29.29 | 33.2107 | 37.1196
Port BurwellIce Accretion2035RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2035 | 19.9986 | 24.0409 | 29.16 | 33.0695 | 36.9684
Port BurwellIce Accretion2040RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2040 | 19.8873 | 23.9206 | 29.03 | 32.9282 | 36.8172
Port BurwellIce Accretion2045RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2045 | 19.7759 | 23.8002 | 28.9 | 32.7869 | 36.666
Port BurwellIce Accretion2050RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2050 | 19.2304 | 23.2018 | 28.224 | 32.0491 | 35.8646
Port BurwellIce Accretion2055RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2055 | 18.7962 | 22.7237 | 27.678 | 31.4524 | 35.2145
Port BurwellIce Accretion2060RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2060 | 18.362 | 22.2457 | 27.132 | 30.8558 | 34.5643
Port BurwellIce Accretion2065RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2065 | 17.9278 | 21.7676 | 26.586 | 30.2591 | 33.9142
Port BurwellIce Accretion2070RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2070 | 17.4936 | 21.2895 | 26.04 | 29.6625 | 33.264
Port BurwellIce Accretion2075RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2075 | 17.2848 | 21.0571 | 25.775 | 29.3743 | 32.949
Port BurwellIce Accretion2080RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2080 | 17.0761 | 20.8247 | 25.51 | 29.0862 | 32.634
Port BurwellIce Accretion2085RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2085 | 16.8673 | 20.5923 | 25.245 | 28.798 | 32.319
Port BurwellIce Accretion2090RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2090 | 16.6586 | 20.3599 | 24.98 | 28.5099 | 32.004
Port BurwellIce Accretion2095RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2095 | 16.4498 | 20.1275 | 24.715 | 28.2218 | 31.689
Port BurwellIce Accretion2100RCP4.5 | Port Burwell | Ice Accretion | RCP4.5 | 2100 | 16.241 | 19.8951 | 24.45 | 27.9336 | 31.374
Port BurwellIce Accretion2023RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2023 | 20.3326 | 24.402 | 29.55 | 33.4932 | 37.422
Port BurwellIce Accretion2025RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2025 | 20.2213 | 24.2816 | 29.42 | 33.352 | 37.2708
Port BurwellIce Accretion2030RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2030 | 20.11 | 24.1613 | 29.29 | 33.2107 | 37.1196
Port BurwellIce Accretion2035RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2035 | 19.9986 | 24.0409 | 29.16 | 33.0695 | 36.9684
Port BurwellIce Accretion2040RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2040 | 19.8873 | 23.9206 | 29.03 | 32.9282 | 36.8172
Port BurwellIce Accretion2045RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2045 | 19.7759 | 23.8002 | 28.9 | 32.7869 | 36.666
Port BurwellIce Accretion2050RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2050 | 19.2304 | 23.2018 | 28.224 | 32.0491 | 35.8646
Port BurwellIce Accretion2055RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2055 | 18.7962 | 22.7237 | 27.678 | 31.4524 | 35.2145
Port BurwellIce Accretion2060RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2060 | 18.362 | 22.2457 | 27.132 | 30.8558 | 34.5643
Port BurwellIce Accretion2065RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2065 | 17.9278 | 21.7676 | 26.586 | 30.2591 | 33.9142
Port BurwellIce Accretion2070RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2070 | 17.4936 | 21.2895 | 26.04 | 29.6625 | 33.264
Port BurwellIce Accretion2075RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2075 | 17.1804 | 20.9409 | 25.6425 | 29.2303 | 32.7915
Port BurwellIce Accretion2080RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2080 | 16.8673 | 20.5923 | 25.245 | 28.798 | 32.319
Port BurwellIce Accretion2085RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2085 | 16.5542 | 20.2437 | 24.8475 | 28.3658 | 31.8465
Port BurwellIce Accretion2090RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2090 | 15.3852 | 18.8825 | 23.26 | 26.5889 | 29.8872
Port BurwellIce Accretion2095RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2095 | 14.5293 | 17.8699 | 22.07 | 25.2442 | 28.4004
Port BurwellIce Accretion2100RCP6.0 | Port Burwell | Ice Accretion | RCP6.0 | 2100 | 13.6734 | 16.8573 | 20.88 | 23.8995 | 26.9136
Port BurwellIce Accretion2023RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2023 | 20.3326 | 24.402 | 29.55 | 33.4932 | 37.422
Port BurwellIce Accretion2025RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2025 | 20.11 | 24.1613 | 29.29 | 33.2107 | 37.1196
Port BurwellIce Accretion2030RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2030 | 19.8873 | 23.9206 | 29.03 | 32.9282 | 36.8172
Port BurwellIce Accretion2035RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2035 | 19.6646 | 23.6799 | 28.77 | 32.6457 | 36.5148
Port BurwellIce Accretion2040RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2040 | 18.9409 | 22.8831 | 27.86 | 31.6513 | 35.4312
Port BurwellIce Accretion2045RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2045 | 18.2173 | 22.0863 | 26.95 | 30.6569 | 34.3476
Port BurwellIce Accretion2050RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2050 | 17.0761 | 20.8247 | 25.51 | 29.0862 | 32.634
Port BurwellIce Accretion2055RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2055 | 16.6586 | 20.3599 | 24.98 | 28.5099 | 32.004
Port BurwellIce Accretion2060RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2060 | 15.3852 | 18.8825 | 23.26 | 26.5889 | 29.8872
Port BurwellIce Accretion2065RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2065 | 14.5293 | 17.8699 | 22.07 | 25.2442 | 28.4004
Port BurwellIce Accretion2070RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2070 | 13.2628 | 16.4008 | 20.34 | 23.3006 | 26.2584
Port BurwellIce Accretion2075RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2075 | 12.8523 | 15.9443 | 19.8 | 22.7017 | 25.6032
Port BurwellIce Accretion2080RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2080 | 12.4417 | 15.4878 | 19.26 | 22.1028 | 24.948
Port BurwellIce Accretion2085RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2085 | 11.5232 | 14.3797 | 17.94 | 20.6112 | 23.2848
Port BurwellIce Accretion2090RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2090 | 10.6047 | 13.2717 | 16.62 | 19.1196 | 21.6216
Port BurwellIce Accretion2095RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2095 | 10.6047 | 13.2717 | 16.62 | 19.1196 | 21.6216
Port BurwellIce Accretion2100RCP8.5 | Port Burwell | Ice Accretion | RCP8.5 | 2100 | 10.6047 | 13.2717 | 16.62 | 19.1196 | 21.6216
Port BurwellWind2023RCP4.5 | Port Burwell | Wind | RCP4.5 | 2023 | 88.6477 | 95.5809 | 102.8976 | 110.1877 | 117.4893
Port BurwellWind2025RCP4.5 | Port Burwell | Wind | RCP4.5 | 2025 | 88.724 | 95.6821 | 103.0319 | 110.3515 | 117.6792
Port BurwellWind2030RCP4.5 | Port Burwell | Wind | RCP4.5 | 2030 | 88.8004 | 95.7833 | 103.1662 | 110.5152 | 117.8692
Port BurwellWind2035RCP4.5 | Port Burwell | Wind | RCP4.5 | 2035 | 88.8767 | 95.8845 | 103.3005 | 110.6789 | 118.0591
Port BurwellWind2040RCP4.5 | Port Burwell | Wind | RCP4.5 | 2040 | 88.953 | 95.9857 | 103.4348 | 110.8426 | 118.249
Port BurwellWind2045RCP4.5 | Port Burwell | Wind | RCP4.5 | 2045 | 89.0294 | 96.0869 | 103.5691 | 111.0063 | 118.4389
Port BurwellWind2050RCP4.5 | Port Burwell | Wind | RCP4.5 | 2050 | 89.185 | 96.2943 | 103.8442 | 111.3381 | 118.8289
Port BurwellWind2055RCP4.5 | Port Burwell | Wind | RCP4.5 | 2055 | 89.2642 | 96.4005 | 103.9849 | 111.5062 | 119.0289
Port BurwellWind2060RCP4.5 | Port Burwell | Wind | RCP4.5 | 2060 | 89.3435 | 96.5068 | 104.1257 | 111.6742 | 119.2289
Port BurwellWind2065RCP4.5 | Port Burwell | Wind | RCP4.5 | 2065 | 89.4228 | 96.613 | 104.2664 | 111.8423 | 119.4289
Port BurwellWind2070RCP4.5 | Port Burwell | Wind | RCP4.5 | 2070 | 89.502 | 96.7193 | 104.4072 | 112.0104 | 119.6289
Port BurwellWind2075RCP4.5 | Port Burwell | Wind | RCP4.5 | 2075 | 89.6224 | 96.8742 | 104.6061 | 112.2469 | 119.906
Port BurwellWind2080RCP4.5 | Port Burwell | Wind | RCP4.5 | 2080 | 89.7428 | 97.0291 | 104.805 | 112.4833 | 120.1831
Port BurwellWind2085RCP4.5 | Port Burwell | Wind | RCP4.5 | 2085 | 89.8631 | 97.1841 | 105.0039 | 112.7198 | 120.4603
Port BurwellWind2090RCP4.5 | Port Burwell | Wind | RCP4.5 | 2090 | 89.9835 | 97.339 | 105.2028 | 112.9563 | 120.7374
Port BurwellWind2095RCP4.5 | Port Burwell | Wind | RCP4.5 | 2095 | 90.1039 | 97.4939 | 105.4017 | 113.1927 | 121.0145
Port BurwellWind2100RCP4.5 | Port Burwell | Wind | RCP4.5 | 2100 | 90.2242 | 97.6489 | 105.6006 | 113.4292 | 121.2917
Port BurwellWind2023RCP6.0 | Port Burwell | Wind | RCP6.0 | 2023 | 88.6477 | 95.5809 | 102.8976 | 110.1877 | 117.4893
Port BurwellWind2025RCP6.0 | Port Burwell | Wind | RCP6.0 | 2025 | 88.724 | 95.6821 | 103.0319 | 110.3515 | 117.6792
Port BurwellWind2030RCP6.0 | Port Burwell | Wind | RCP6.0 | 2030 | 88.8004 | 95.7833 | 103.1662 | 110.5152 | 117.8692
Port BurwellWind2035RCP6.0 | Port Burwell | Wind | RCP6.0 | 2035 | 88.8767 | 95.8845 | 103.3005 | 110.6789 | 118.0591
Port BurwellWind2040RCP6.0 | Port Burwell | Wind | RCP6.0 | 2040 | 88.953 | 95.9857 | 103.4348 | 110.8426 | 118.249
Port BurwellWind2045RCP6.0 | Port Burwell | Wind | RCP6.0 | 2045 | 89.0294 | 96.0869 | 103.5691 | 111.0063 | 118.4389
Port BurwellWind2050RCP6.0 | Port Burwell | Wind | RCP6.0 | 2050 | 89.185 | 96.2943 | 103.8442 | 111.3381 | 118.8289
Port BurwellWind2055RCP6.0 | Port Burwell | Wind | RCP6.0 | 2055 | 89.2642 | 96.4005 | 103.9849 | 111.5062 | 119.0289
Port BurwellWind2060RCP6.0 | Port Burwell | Wind | RCP6.0 | 2060 | 89.3435 | 96.5068 | 104.1257 | 111.6742 | 119.2289
Port BurwellWind2065RCP6.0 | Port Burwell | Wind | RCP6.0 | 2065 | 89.4228 | 96.613 | 104.2664 | 111.8423 | 119.4289
Port BurwellWind2070RCP6.0 | Port Burwell | Wind | RCP6.0 | 2070 | 89.502 | 96.7193 | 104.4072 | 112.0104 | 119.6289
Port BurwellWind2075RCP6.0 | Port Burwell | Wind | RCP6.0 | 2075 | 89.6826 | 96.9517 | 104.7056 | 112.3651 | 120.0446
Port BurwellWind2080RCP6.0 | Port Burwell | Wind | RCP6.0 | 2080 | 89.8631 | 97.1841 | 105.0039 | 112.7198 | 120.4603
Port BurwellWind2085RCP6.0 | Port Burwell | Wind | RCP6.0 | 2085 | 90.0437 | 97.4165 | 105.3022 | 113.0745 | 120.876
Port BurwellWind2090RCP6.0 | Port Burwell | Wind | RCP6.0 | 2090 | 90.4826 | 97.9841 | 106.0256 | 113.9349 | 121.8731
Port BurwellWind2095RCP6.0 | Port Burwell | Wind | RCP6.0 | 2095 | 90.741 | 98.3192 | 106.4506 | 114.4406 | 122.4545
Port BurwellWind2100RCP6.0 | Port Burwell | Wind | RCP6.0 | 2100 | 90.9993 | 98.6544 | 106.8756 | 114.9462 | 123.0359
Port BurwellWind2023RCP8.5 | Port Burwell | Wind | RCP8.5 | 2023 | 88.6477 | 95.5809 | 102.8976 | 110.1877 | 117.4893
Port BurwellWind2025RCP8.5 | Port Burwell | Wind | RCP8.5 | 2025 | 88.8004 | 95.7833 | 103.1662 | 110.5152 | 117.8692
Port BurwellWind2030RCP8.5 | Port Burwell | Wind | RCP8.5 | 2030 | 88.953 | 95.9857 | 103.4348 | 110.8426 | 118.249
Port BurwellWind2035RCP8.5 | Port Burwell | Wind | RCP8.5 | 2035 | 89.1057 | 96.188 | 103.7034 | 111.17 | 118.6289
Port BurwellWind2040RCP8.5 | Port Burwell | Wind | RCP8.5 | 2040 | 89.2378 | 96.3651 | 103.938 | 111.4501 | 118.9622
Port BurwellWind2045RCP8.5 | Port Burwell | Wind | RCP8.5 | 2045 | 89.3699 | 96.5422 | 104.1726 | 111.7303 | 119.2955
Port BurwellWind2050RCP8.5 | Port Burwell | Wind | RCP8.5 | 2050 | 89.7428 | 97.0291 | 104.805 | 112.4833 | 120.1831
Port BurwellWind2055RCP8.5 | Port Burwell | Wind | RCP8.5 | 2055 | 89.9835 | 97.339 | 105.2028 | 112.9563 | 120.7374
Port BurwellWind2060RCP8.5 | Port Burwell | Wind | RCP8.5 | 2060 | 90.4826 | 97.9841 | 106.0256 | 113.9349 | 121.8731
Port BurwellWind2065RCP8.5 | Port Burwell | Wind | RCP8.5 | 2065 | 90.741 | 98.3192 | 106.4506 | 114.4406 | 122.4545
Port BurwellWind2070RCP8.5 | Port Burwell | Wind | RCP8.5 | 2070 | 91.149 | 98.8663 | 107.168 | 115.3064 | 123.4661
Port BurwellWind2075RCP8.5 | Port Burwell | Wind | RCP8.5 | 2075 | 91.2988 | 99.0781 | 107.4604 | 115.6666 | 123.8963
Port BurwellWind2080RCP8.5 | Port Burwell | Wind | RCP8.5 | 2080 | 91.4485 | 99.29 | 107.7528 | 116.0267 | 124.3266
Port BurwellWind2085RCP8.5 | Port Burwell | Wind | RCP8.5 | 2085 | 91.792 | 99.7405 | 108.3495 | 116.7361 | 125.1638
Port BurwellWind2090RCP8.5 | Port Burwell | Wind | RCP8.5 | 2090 | 92.1355 | 100.1911 | 108.9462 | 117.4456 | 126.001
Port BurwellWind2095RCP8.5 | Port Burwell | Wind | RCP8.5 | 2095 | 92.1355 | 100.1911 | 108.9462 | 117.4456 | 126.001
Port BurwellWind2100RCP8.5 | Port Burwell | Wind | RCP8.5 | 2100 | 92.1355 | 100.1911 | 108.9462 | 117.4456 | 126.001
Port ColborneIce Accretion2023RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2023 | 20.6458 | 24.7755 | 30 | 34.0017 | 37.989
Port ColborneIce Accretion2025RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2025 | 20.5483 | 24.6676 | 29.885 | 33.8717 | 37.8504
Port ColborneIce Accretion2030RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2030 | 20.4509 | 24.5597 | 29.77 | 33.7418 | 37.7118
Port ColborneIce Accretion2035RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2035 | 20.3535 | 24.4518 | 29.655 | 33.6118 | 37.5732
Port ColborneIce Accretion2040RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2040 | 20.2561 | 24.3439 | 29.54 | 33.4819 | 37.4346
Port ColborneIce Accretion2045RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2045 | 20.1587 | 24.236 | 29.425 | 33.352 | 37.296
Port ColborneIce Accretion2050RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2050 | 19.6145 | 23.6251 | 28.722 | 32.5711 | 36.4468
Port ColborneIce Accretion2055RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2055 | 19.1678 | 23.1221 | 28.134 | 31.9202 | 35.7361
Port ColborneIce Accretion2060RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2060 | 18.721 | 22.6192 | 27.546 | 31.2694 | 35.0255
Port ColborneIce Accretion2065RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2065 | 18.2743 | 22.1162 | 26.958 | 30.6185 | 34.3148
Port ColborneIce Accretion2070RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2070 | 17.8276 | 21.6132 | 26.37 | 29.9676 | 33.6042
Port ColborneIce Accretion2075RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2075 | 17.6606 | 21.4389 | 26.185 | 29.7755 | 33.4026
Port ColborneIce Accretion2080RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2080 | 17.4936 | 21.2646 | 26 | 29.5834 | 33.201
Port ColborneIce Accretion2085RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2085 | 17.3266 | 21.0903 | 25.815 | 29.3913 | 32.9994
Port ColborneIce Accretion2090RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2090 | 17.1596 | 20.916 | 25.63 | 29.1992 | 32.7978
Port ColborneIce Accretion2095RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2095 | 16.9926 | 20.7417 | 25.445 | 29.0071 | 32.5962
Port ColborneIce Accretion2100RCP4.5 | Port Colborne | Ice Accretion | RCP4.5 | 2100 | 16.8256 | 20.5674 | 25.26 | 28.815 | 32.3946
Port ColborneIce Accretion2023RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2023 | 20.6458 | 24.7755 | 30 | 34.0017 | 37.989
Port ColborneIce Accretion2025RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2025 | 20.5483 | 24.6676 | 29.885 | 33.8717 | 37.8504
Port ColborneIce Accretion2030RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2030 | 20.4509 | 24.5597 | 29.77 | 33.7418 | 37.7118
Port ColborneIce Accretion2035RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2035 | 20.3535 | 24.4518 | 29.655 | 33.6118 | 37.5732
Port ColborneIce Accretion2040RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2040 | 20.2561 | 24.3439 | 29.54 | 33.4819 | 37.4346
Port ColborneIce Accretion2045RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2045 | 20.1587 | 24.236 | 29.425 | 33.352 | 37.296
Port ColborneIce Accretion2050RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2050 | 19.6145 | 23.6251 | 28.722 | 32.5711 | 36.4468
Port ColborneIce Accretion2055RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2055 | 19.1678 | 23.1221 | 28.134 | 31.9202 | 35.7361
Port ColborneIce Accretion2060RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2060 | 18.721 | 22.6192 | 27.546 | 31.2694 | 35.0255
Port ColborneIce Accretion2065RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2065 | 18.2743 | 22.1162 | 26.958 | 30.6185 | 34.3148
Port ColborneIce Accretion2070RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2070 | 17.8276 | 21.6132 | 26.37 | 29.9676 | 33.6042
Port ColborneIce Accretion2075RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2075 | 17.5771 | 21.3517 | 26.0925 | 29.6794 | 33.3018
Port ColborneIce Accretion2080RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2080 | 17.3266 | 21.0903 | 25.815 | 29.3913 | 32.9994
Port ColborneIce Accretion2085RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2085 | 17.0761 | 20.8288 | 25.5375 | 29.1031 | 32.697
Port ColborneIce Accretion2090RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2090 | 16.1436 | 19.7872 | 24.35 | 27.8093 | 31.2732
Port ColborneIce Accretion2095RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2095 | 15.4617 | 19.007 | 23.44 | 26.8036 | 30.1518
Port ColborneIce Accretion2100RCP6.0 | Port Colborne | Ice Accretion | RCP6.0 | 2100 | 14.7798 | 18.2268 | 22.53 | 25.7979 | 29.0304
Port ColborneIce Accretion2023RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2023 | 20.6458 | 24.7755 | 30 | 34.0017 | 37.989
Port ColborneIce Accretion2025RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2025 | 20.4509 | 24.5597 | 29.77 | 33.7418 | 37.7118
Port ColborneIce Accretion2030RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2030 | 20.2561 | 24.3439 | 29.54 | 33.4819 | 37.4346
Port ColborneIce Accretion2035RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2035 | 20.0612 | 24.1281 | 29.31 | 33.222 | 37.1574
Port ColborneIce Accretion2040RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2040 | 19.3167 | 23.2898 | 28.33 | 32.1372 | 35.973
Port ColborneIce Accretion2045RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2045 | 18.5721 | 22.4515 | 27.35 | 31.0524 | 34.7886
Port ColborneIce Accretion2050RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2050 | 17.4936 | 21.2646 | 26 | 29.5834 | 33.201
Port ColborneIce Accretion2055RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2055 | 17.1596 | 20.916 | 25.63 | 29.1992 | 32.7978
Port ColborneIce Accretion2060RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2060 | 16.1436 | 19.7872 | 24.35 | 27.8093 | 31.2732
Port ColborneIce Accretion2065RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2065 | 15.4617 | 19.007 | 23.44 | 26.8036 | 30.1518
Port ColborneIce Accretion2070RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2070 | 14.4388 | 17.8367 | 22.09 | 25.312 | 28.5012
Port ColborneIce Accretion2075RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2075 | 14.0978 | 17.4466 | 21.65 | 24.8261 | 27.972
Port ColborneIce Accretion2080RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2080 | 13.7569 | 17.0565 | 21.21 | 24.3402 | 27.4428
Port ColborneIce Accretion2085RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2085 | 12.9845 | 16.1476 | 20.115 | 23.1029 | 26.0631
Port ColborneIce Accretion2090RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2090 | 12.2121 | 15.2388 | 19.02 | 21.8655 | 24.6834
Port ColborneIce Accretion2095RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2095 | 12.2121 | 15.2388 | 19.02 | 21.8655 | 24.6834
Port ColborneIce Accretion2100RCP8.5 | Port Colborne | Ice Accretion | RCP8.5 | 2100 | 12.2121 | 15.2388 | 19.02 | 21.8655 | 24.6834
Port ColborneWind2023RCP4.5 | Port Colborne | Wind | RCP4.5 | 2023 | 88.9824 | 96.0647 | 103.581 | 111.05 | 118.5126
Port ColborneWind2025RCP4.5 | Port Colborne | Wind | RCP4.5 | 2025 | 88.953 | 96.0347 | 103.5487 | 111.0154 | 118.4758
Port ColborneWind2030RCP4.5 | Port Colborne | Wind | RCP4.5 | 2030 | 88.9237 | 96.0046 | 103.5164 | 110.9808 | 118.4389
Port ColborneWind2035RCP4.5 | Port Colborne | Wind | RCP4.5 | 2035 | 88.8943 | 95.9746 | 103.4841 | 110.9463 | 118.4021
Port ColborneWind2040RCP4.5 | Port Colborne | Wind | RCP4.5 | 2040 | 88.8649 | 95.9446 | 103.4518 | 110.9117 | 118.3653
Port ColborneWind2045RCP4.5 | Port Colborne | Wind | RCP4.5 | 2045 | 88.8356 | 95.9145 | 103.4195 | 110.8771 | 118.3285
Port ColborneWind2050RCP4.5 | Port Colborne | Wind | RCP4.5 | 2050 | 88.8644 | 95.9585 | 103.4831 | 110.9539 | 118.4219
Port ColborneWind2055RCP4.5 | Port Colborne | Wind | RCP4.5 | 2055 | 88.9225 | 96.0325 | 103.579 | 111.0652 | 118.5521
Port ColborneWind2060RCP4.5 | Port Colborne | Wind | RCP4.5 | 2060 | 88.9806 | 96.1065 | 103.6748 | 111.1766 | 118.6823
Port ColborneWind2065RCP4.5 | Port Colborne | Wind | RCP4.5 | 2065 | 89.0388 | 96.1805 | 103.7707 | 111.2879 | 118.8126
Port ColborneWind2070RCP4.5 | Port Colborne | Wind | RCP4.5 | 2070 | 89.0969 | 96.2544 | 103.8666 | 111.3992 | 118.9428
Port ColborneWind2075RCP4.5 | Port Colborne | Wind | RCP4.5 | 2075 | 89.1791 | 96.3699 | 104.0247 | 111.592 | 119.1734
Port ColborneWind2080RCP4.5 | Port Colborne | Wind | RCP4.5 | 2080 | 89.2613 | 96.4853 | 104.1828 | 111.7848 | 119.4041
Port ColborneWind2085RCP4.5 | Port Colborne | Wind | RCP4.5 | 2085 | 89.3435 | 96.6007 | 104.3409 | 111.9776 | 119.6347
Port ColborneWind2090RCP4.5 | Port Colborne | Wind | RCP4.5 | 2090 | 89.4257 | 96.7161 | 104.499 | 112.1705 | 119.8653
Port ColborneWind2095RCP4.5 | Port Colborne | Wind | RCP4.5 | 2095 | 89.5079 | 96.8315 | 104.6571 | 112.3633 | 120.0959
Port ColborneWind2100RCP4.5 | Port Colborne | Wind | RCP4.5 | 2100 | 89.5901 | 96.9469 | 104.8152 | 112.5561 | 120.3265
Port ColborneWind2023RCP6.0 | Port Colborne | Wind | RCP6.0 | 2023 | 88.9824 | 96.0647 | 103.581 | 111.05 | 118.5126
Port ColborneWind2025RCP6.0 | Port Colborne | Wind | RCP6.0 | 2025 | 88.953 | 96.0347 | 103.5487 | 111.0154 | 118.4758
Port ColborneWind2030RCP6.0 | Port Colborne | Wind | RCP6.0 | 2030 | 88.9237 | 96.0046 | 103.5164 | 110.9808 | 118.4389
Port ColborneWind2035RCP6.0 | Port Colborne | Wind | RCP6.0 | 2035 | 88.8943 | 95.9746 | 103.4841 | 110.9463 | 118.4021
Port ColborneWind2040RCP6.0 | Port Colborne | Wind | RCP6.0 | 2040 | 88.8649 | 95.9446 | 103.4518 | 110.9117 | 118.3653
Port ColborneWind2045RCP6.0 | Port Colborne | Wind | RCP6.0 | 2045 | 88.8356 | 95.9145 | 103.4195 | 110.8771 | 118.3285
Port ColborneWind2050RCP6.0 | Port Colborne | Wind | RCP6.0 | 2050 | 88.8644 | 95.9585 | 103.4831 | 110.9539 | 118.4219
Port ColborneWind2055RCP6.0 | Port Colborne | Wind | RCP6.0 | 2055 | 88.9225 | 96.0325 | 103.579 | 111.0652 | 118.5521
Port ColborneWind2060RCP6.0 | Port Colborne | Wind | RCP6.0 | 2060 | 88.9806 | 96.1065 | 103.6748 | 111.1766 | 118.6823
Port ColborneWind2065RCP6.0 | Port Colborne | Wind | RCP6.0 | 2065 | 89.0388 | 96.1805 | 103.7707 | 111.2879 | 118.8126
Port ColborneWind2070RCP6.0 | Port Colborne | Wind | RCP6.0 | 2070 | 89.0969 | 96.2544 | 103.8666 | 111.3992 | 118.9428
Port ColborneWind2075RCP6.0 | Port Colborne | Wind | RCP6.0 | 2075 | 89.2202 | 96.4276 | 104.1038 | 111.6884 | 119.2887
Port ColborneWind2080RCP6.0 | Port Colborne | Wind | RCP6.0 | 2080 | 89.3435 | 96.6007 | 104.3409 | 111.9776 | 119.6347
Port ColborneWind2085RCP6.0 | Port Colborne | Wind | RCP6.0 | 2085 | 89.4668 | 96.7738 | 104.5781 | 112.2669 | 119.9806
Port ColborneWind2090RCP6.0 | Port Colborne | Wind | RCP6.0 | 2090 | 89.778 | 97.1872 | 105.1178 | 112.9162 | 120.7452
Port ColborneWind2095RCP6.0 | Port Colborne | Wind | RCP6.0 | 2095 | 89.9659 | 97.4275 | 105.4204 | 113.2764 | 121.1638
Port ColborneWind2100RCP6.0 | Port Colborne | Wind | RCP6.0 | 2100 | 90.1538 | 97.6679 | 105.723 | 113.6366 | 121.5824
Port ColborneWind2023RCP8.5 | Port Colborne | Wind | RCP8.5 | 2023 | 88.9824 | 96.0647 | 103.581 | 111.05 | 118.5126
Port ColborneWind2025RCP8.5 | Port Colborne | Wind | RCP8.5 | 2025 | 88.9237 | 96.0046 | 103.5164 | 110.9808 | 118.4389
Port ColborneWind2030RCP8.5 | Port Colborne | Wind | RCP8.5 | 2030 | 88.8649 | 95.9446 | 103.4518 | 110.9117 | 118.3653
Port ColborneWind2035RCP8.5 | Port Colborne | Wind | RCP8.5 | 2035 | 88.8062 | 95.8845 | 103.3872 | 110.8426 | 118.2916
Port ColborneWind2040RCP8.5 | Port Colborne | Wind | RCP8.5 | 2040 | 88.9031 | 96.0078 | 103.547 | 111.0281 | 118.5087
Port ColborneWind2045RCP8.5 | Port Colborne | Wind | RCP8.5 | 2045 | 89 | 96.1311 | 103.7068 | 111.2137 | 118.7258
Port ColborneWind2050RCP8.5 | Port Colborne | Wind | RCP8.5 | 2050 | 89.2613 | 96.4853 | 104.1828 | 111.7848 | 119.4041
Port ColborneWind2055RCP8.5 | Port Colborne | Wind | RCP8.5 | 2055 | 89.4257 | 96.7161 | 104.499 | 112.1705 | 119.8653
Port ColborneWind2060RCP8.5 | Port Colborne | Wind | RCP8.5 | 2060 | 89.778 | 97.1872 | 105.1178 | 112.9162 | 120.7452
Port ColborneWind2065RCP8.5 | Port Colborne | Wind | RCP8.5 | 2065 | 89.9659 | 97.4275 | 105.4204 | 113.2764 | 121.1638
Port ColborneWind2070RCP8.5 | Port Colborne | Wind | RCP8.5 | 2070 | 90.2154 | 97.7722 | 105.8896 | 113.8548 | 121.8459
Port ColborneWind2075RCP8.5 | Port Colborne | Wind | RCP8.5 | 2075 | 90.2771 | 97.8765 | 106.0562 | 114.0731 | 122.1095
Port ColborneWind2080RCP8.5 | Port Colborne | Wind | RCP8.5 | 2080 | 90.3387 | 97.9809 | 106.2228 | 114.2914 | 122.3731
Port ColborneWind2085RCP8.5 | Port Colborne | Wind | RCP8.5 | 2085 | 90.4048 | 98.09 | 106.3809 | 114.4879 | 122.6173
Port ColborneWind2090RCP8.5 | Port Colborne | Wind | RCP8.5 | 2090 | 90.4709 | 98.1991 | 106.539 | 114.6843 | 122.8614
Port ColborneWind2095RCP8.5 | Port Colborne | Wind | RCP8.5 | 2095 | 90.4709 | 98.1991 | 106.539 | 114.6843 | 122.8614
Port ColborneWind2100RCP8.5 | Port Colborne | Wind | RCP8.5 | 2100 | 90.4709 | 98.1991 | 106.539 | 114.6843 | 122.8614
Port ElginIce Accretion2023RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2023 | 13.9865 | 16.7162 | 20.18 | 22.8486 | 25.4772
Port ElginIce Accretion2025RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2025 | 13.9958 | 16.7383 | 20.2167 | 22.8938 | 25.536
Port ElginIce Accretion2030RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2030 | 14.0051 | 16.7605 | 20.2533 | 22.939 | 25.5948
Port ElginIce Accretion2035RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2035 | 14.0143 | 16.7826 | 20.29 | 22.9842 | 25.6536
Port ElginIce Accretion2040RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2040 | 14.0236 | 16.8047 | 20.3267 | 23.0294 | 25.7124
Port ElginIce Accretion2045RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2045 | 14.0329 | 16.8269 | 20.3633 | 23.0746 | 25.7712
Port ElginIce Accretion2050RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2050 | 13.9921 | 16.8025 | 20.36 | 23.0836 | 25.7947
Port ElginIce Accretion2055RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2055 | 13.942 | 16.756 | 20.32 | 23.0475 | 25.7594
Port ElginIce Accretion2060RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2060 | 13.8919 | 16.7096 | 20.28 | 23.0113 | 25.7242
Port ElginIce Accretion2065RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2065 | 13.8418 | 16.6631 | 20.24 | 22.9752 | 25.6889
Port ElginIce Accretion2070RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2070 | 13.7917 | 16.6166 | 20.2 | 22.939 | 25.6536
Port ElginIce Accretion2075RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2075 | 13.7406 | 16.5806 | 20.18 | 22.9277 | 25.6536
Port ElginIce Accretion2080RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2080 | 13.6896 | 16.5447 | 20.16 | 22.9164 | 25.6536
Port ElginIce Accretion2085RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2085 | 13.6386 | 16.5087 | 20.14 | 22.9051 | 25.6536
Port ElginIce Accretion2090RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2090 | 13.5876 | 16.4727 | 20.12 | 22.8938 | 25.6536
Port ElginIce Accretion2095RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2095 | 13.5365 | 16.4368 | 20.1 | 22.8825 | 25.6536
Port ElginIce Accretion2100RCP4.5 | Port Elgin | Ice Accretion | RCP4.5 | 2100 | 13.4855 | 16.4008 | 20.08 | 22.8712 | 25.6536
Port ElginIce Accretion2023RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2023 | 13.9865 | 16.7162 | 20.18 | 22.8486 | 25.4772
Port ElginIce Accretion2025RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2025 | 13.9958 | 16.7383 | 20.2167 | 22.8938 | 25.536
Port ElginIce Accretion2030RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2030 | 14.0051 | 16.7605 | 20.2533 | 22.939 | 25.5948
Port ElginIce Accretion2035RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2035 | 14.0143 | 16.7826 | 20.29 | 22.9842 | 25.6536
Port ElginIce Accretion2040RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2040 | 14.0236 | 16.8047 | 20.3267 | 23.0294 | 25.7124
Port ElginIce Accretion2045RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2045 | 14.0329 | 16.8269 | 20.3633 | 23.0746 | 25.7712
Port ElginIce Accretion2050RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2050 | 13.9921 | 16.8025 | 20.36 | 23.0836 | 25.7947
Port ElginIce Accretion2055RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2055 | 13.942 | 16.756 | 20.32 | 23.0475 | 25.7594
Port ElginIce Accretion2060RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2060 | 13.8919 | 16.7096 | 20.28 | 23.0113 | 25.7242
Port ElginIce Accretion2065RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2065 | 13.8418 | 16.6631 | 20.24 | 22.9752 | 25.6889
Port ElginIce Accretion2070RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2070 | 13.7917 | 16.6166 | 20.2 | 22.939 | 25.6536
Port ElginIce Accretion2075RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2075 | 13.7151 | 16.5626 | 20.17 | 22.922 | 25.6536
Port ElginIce Accretion2080RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2080 | 13.6386 | 16.5087 | 20.14 | 22.9051 | 25.6536
Port ElginIce Accretion2085RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2085 | 13.562 | 16.4547 | 20.11 | 22.8881 | 25.6536
Port ElginIce Accretion2090RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2090 | 13.2489 | 16.1518 | 19.8067 | 22.5849 | 25.3512
Port ElginIce Accretion2095RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2095 | 13.0123 | 15.9028 | 19.5333 | 22.2987 | 25.0488
Port ElginIce Accretion2100RCP6.0 | Port Elgin | Ice Accretion | RCP6.0 | 2100 | 12.7757 | 15.6538 | 19.26 | 22.0124 | 24.7464
Port ElginIce Accretion2023RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2023 | 13.9865 | 16.7162 | 20.18 | 22.8486 | 25.4772
Port ElginIce Accretion2025RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2025 | 14.0051 | 16.7605 | 20.2533 | 22.939 | 25.5948
Port ElginIce Accretion2030RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2030 | 14.0236 | 16.8047 | 20.3267 | 23.0294 | 25.7124
Port ElginIce Accretion2035RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2035 | 14.0422 | 16.849 | 20.4 | 23.1198 | 25.83
Port ElginIce Accretion2040RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2040 | 13.9587 | 16.7715 | 20.3333 | 23.0595 | 25.7712
Port ElginIce Accretion2045RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2045 | 13.8752 | 16.6941 | 20.2667 | 22.9993 | 25.7124
Port ElginIce Accretion2050RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2050 | 13.6896 | 16.5447 | 20.16 | 22.9164 | 25.6536
Port ElginIce Accretion2055RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2055 | 13.5876 | 16.4727 | 20.12 | 22.8938 | 25.6536
Port ElginIce Accretion2060RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2060 | 13.2489 | 16.1518 | 19.8067 | 22.5849 | 25.3512
Port ElginIce Accretion2065RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2065 | 13.0123 | 15.9028 | 19.5333 | 22.2987 | 25.0488
Port ElginIce Accretion2070RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2070 | 12.4232 | 15.2609 | 18.82 | 21.5378 | 24.234
Port ElginIce Accretion2075RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2075 | 12.0706 | 14.8681 | 18.38 | 21.0632 | 23.7216
Port ElginIce Accretion2080RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2080 | 11.718 | 14.4752 | 17.94 | 20.5886 | 23.2092
Port ElginIce Accretion2085RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2085 | 11.1196 | 13.7863 | 17.13 | 19.6733 | 22.2012
Port ElginIce Accretion2090RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2090 | 10.5212 | 13.0974 | 16.32 | 18.758 | 21.1932
Port ElginIce Accretion2095RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2095 | 10.5212 | 13.0974 | 16.32 | 18.758 | 21.1932
Port ElginIce Accretion2100RCP8.5 | Port Elgin | Ice Accretion | RCP8.5 | 2100 | 10.5212 | 13.0974 | 16.32 | 18.758 | 21.1932
Port ElginWind2023RCP4.5 | Port Elgin | Wind | RCP4.5 | 2023 | 85.4848 | 91.9687 | 98.7624 | 105.591 | 112.4086
Port ElginWind2025RCP4.5 | Port Elgin | Wind | RCP4.5 | 2025 | 85.5631 | 92.0654 | 98.8845 | 105.7323 | 112.5722
Port ElginWind2030RCP4.5 | Port Elgin | Wind | RCP4.5 | 2030 | 85.6415 | 92.1621 | 99.0066 | 105.8735 | 112.7359
Port ElginWind2035RCP4.5 | Port Elgin | Wind | RCP4.5 | 2035 | 85.7198 | 92.2587 | 99.1287 | 106.0147 | 112.8995
Port ElginWind2040RCP4.5 | Port Elgin | Wind | RCP4.5 | 2040 | 85.7982 | 92.3554 | 99.2508 | 106.156 | 113.0631
Port ElginWind2045RCP4.5 | Port Elgin | Wind | RCP4.5 | 2045 | 85.8766 | 92.4521 | 99.3729 | 106.2972 | 113.2268
Port ElginWind2050RCP4.5 | Port Elgin | Wind | RCP4.5 | 2050 | 85.9515 | 92.5396 | 99.4752 | 106.413 | 113.3566
Port ElginWind2055RCP4.5 | Port Elgin | Wind | RCP4.5 | 2055 | 85.9481 | 92.5304 | 99.4554 | 106.3876 | 113.3227
Port ElginWind2060RCP4.5 | Port Elgin | Wind | RCP4.5 | 2060 | 85.9447 | 92.5211 | 99.4356 | 106.3622 | 113.2889
Port ElginWind2065RCP4.5 | Port Elgin | Wind | RCP4.5 | 2065 | 85.9412 | 92.5119 | 99.4158 | 106.3368 | 113.255
Port ElginWind2070RCP4.5 | Port Elgin | Wind | RCP4.5 | 2070 | 85.9378 | 92.5027 | 99.396 | 106.3113 | 113.2212
Port ElginWind2075RCP4.5 | Port Elgin | Wind | RCP4.5 | 2075 | 85.9564 | 92.5227 | 99.4175 | 106.3343 | 113.2456
Port ElginWind2080RCP4.5 | Port Elgin | Wind | RCP4.5 | 2080 | 85.9749 | 92.5426 | 99.4389 | 106.3573 | 113.2701
Port ElginWind2085RCP4.5 | Port Elgin | Wind | RCP4.5 | 2085 | 85.9934 | 92.5626 | 99.4604 | 106.3802 | 113.2945
Port ElginWind2090RCP4.5 | Port Elgin | Wind | RCP4.5 | 2090 | 86.0119 | 92.5825 | 99.4818 | 106.4032 | 113.319
Port ElginWind2095RCP4.5 | Port Elgin | Wind | RCP4.5 | 2095 | 86.0304 | 92.6025 | 99.5033 | 106.4261 | 113.3434
Port ElginWind2100RCP4.5 | Port Elgin | Wind | RCP4.5 | 2100 | 86.049 | 92.6224 | 99.5247 | 106.4491 | 113.3679
Port ElginWind2023RCP6.0 | Port Elgin | Wind | RCP6.0 | 2023 | 85.4848 | 91.9687 | 98.7624 | 105.591 | 112.4086
Port ElginWind2025RCP6.0 | Port Elgin | Wind | RCP6.0 | 2025 | 85.5631 | 92.0654 | 98.8845 | 105.7323 | 112.5722
Port ElginWind2030RCP6.0 | Port Elgin | Wind | RCP6.0 | 2030 | 85.6415 | 92.1621 | 99.0066 | 105.8735 | 112.7359
Port ElginWind2035RCP6.0 | Port Elgin | Wind | RCP6.0 | 2035 | 85.7198 | 92.2587 | 99.1287 | 106.0147 | 112.8995
Port ElginWind2040RCP6.0 | Port Elgin | Wind | RCP6.0 | 2040 | 85.7982 | 92.3554 | 99.2508 | 106.156 | 113.0631
Port ElginWind2045RCP6.0 | Port Elgin | Wind | RCP6.0 | 2045 | 85.8766 | 92.4521 | 99.3729 | 106.2972 | 113.2268
Port ElginWind2050RCP6.0 | Port Elgin | Wind | RCP6.0 | 2050 | 85.9515 | 92.5396 | 99.4752 | 106.413 | 113.3566
Port ElginWind2055RCP6.0 | Port Elgin | Wind | RCP6.0 | 2055 | 85.9481 | 92.5304 | 99.4554 | 106.3876 | 113.3227
Port ElginWind2060RCP6.0 | Port Elgin | Wind | RCP6.0 | 2060 | 85.9447 | 92.5211 | 99.4356 | 106.3622 | 113.2889
Port ElginWind2065RCP6.0 | Port Elgin | Wind | RCP6.0 | 2065 | 85.9412 | 92.5119 | 99.4158 | 106.3368 | 113.255
Port ElginWind2070RCP6.0 | Port Elgin | Wind | RCP6.0 | 2070 | 85.9378 | 92.5027 | 99.396 | 106.3113 | 113.2212
Port ElginWind2075RCP6.0 | Port Elgin | Wind | RCP6.0 | 2075 | 85.9656 | 92.5327 | 99.4282 | 106.3458 | 113.2578
Port ElginWind2080RCP6.0 | Port Elgin | Wind | RCP6.0 | 2080 | 85.9934 | 92.5626 | 99.4604 | 106.3802 | 113.2945
Port ElginWind2085RCP6.0 | Port Elgin | Wind | RCP6.0 | 2085 | 86.0212 | 92.5925 | 99.4925 | 106.4146 | 113.3312
Port ElginWind2090RCP6.0 | Port Elgin | Wind | RCP6.0 | 2090 | 86.1857 | 92.7881 | 99.726 | 106.6786 | 113.6237
Port ElginWind2095RCP6.0 | Port Elgin | Wind | RCP6.0 | 2095 | 86.3225 | 92.9539 | 99.9273 | 106.9081 | 113.8795
Port ElginWind2100RCP6.0 | Port Elgin | Wind | RCP6.0 | 2100 | 86.4593 | 93.1196 | 100.1286 | 107.1376 | 114.1353
Port ElginWind2023RCP8.5 | Port Elgin | Wind | RCP8.5 | 2023 | 85.4848 | 91.9687 | 98.7624 | 105.591 | 112.4086
Port ElginWind2025RCP8.5 | Port Elgin | Wind | RCP8.5 | 2025 | 85.6415 | 92.1621 | 99.0066 | 105.8735 | 112.7359
Port ElginWind2030RCP8.5 | Port Elgin | Wind | RCP8.5 | 2030 | 85.7982 | 92.3554 | 99.2508 | 106.156 | 113.0631
Port ElginWind2035RCP8.5 | Port Elgin | Wind | RCP8.5 | 2035 | 85.9549 | 92.5488 | 99.495 | 106.4385 | 113.3904
Port ElginWind2040RCP8.5 | Port Elgin | Wind | RCP8.5 | 2040 | 85.9492 | 92.5334 | 99.462 | 106.3961 | 113.334
Port ElginWind2045RCP8.5 | Port Elgin | Wind | RCP8.5 | 2045 | 85.9435 | 92.5181 | 99.429 | 106.3537 | 113.2776
Port ElginWind2050RCP8.5 | Port Elgin | Wind | RCP8.5 | 2050 | 85.9749 | 92.5426 | 99.4389 | 106.3573 | 113.2701
Port ElginWind2055RCP8.5 | Port Elgin | Wind | RCP8.5 | 2055 | 86.0119 | 92.5825 | 99.4818 | 106.4032 | 113.319
Port ElginWind2060RCP8.5 | Port Elgin | Wind | RCP8.5 | 2060 | 86.1857 | 92.7881 | 99.726 | 106.6786 | 113.6237
Port ElginWind2065RCP8.5 | Port Elgin | Wind | RCP8.5 | 2065 | 86.3225 | 92.9539 | 99.9273 | 106.9081 | 113.8795
Port ElginWind2070RCP8.5 | Port Elgin | Wind | RCP8.5 | 2070 | 86.5305 | 93.2055 | 100.2276 | 107.2506 | 114.267
Port ElginWind2075RCP8.5 | Port Elgin | Wind | RCP8.5 | 2075 | 86.6018 | 93.2915 | 100.3266 | 107.3636 | 114.3987
Port ElginWind2080RCP8.5 | Port Elgin | Wind | RCP8.5 | 2080 | 86.673 | 93.3774 | 100.4256 | 107.4766 | 114.5303
Port ElginWind2085RCP8.5 | Port Elgin | Wind | RCP8.5 | 2085 | 87.0021 | 93.8193 | 101.0147 | 108.1863 | 115.3598
Port ElginWind2090RCP8.5 | Port Elgin | Wind | RCP8.5 | 2090 | 87.3312 | 94.2613 | 101.6037 | 108.896 | 116.1894
Port ElginWind2095RCP8.5 | Port Elgin | Wind | RCP8.5 | 2095 | 87.3312 | 94.2613 | 101.6037 | 108.896 | 116.1894
Port ElginWind2100RCP8.5 | Port Elgin | Wind | RCP8.5 | 2100 | 87.3312 | 94.2613 | 101.6037 | 108.896 | 116.1894
Port HopeIce Accretion2023RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2023 | 17.5875 | 20.999 | 25.325 | 28.6172 | 31.941
Port HopeIce Accretion2025RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2025 | 17.6542 | 21.0958 | 25.4625 | 28.7867 | 32.1352
Port HopeIce Accretion2030RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2030 | 17.7209 | 21.1927 | 25.6 | 28.9562 | 32.3295
Port HopeIce Accretion2035RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2035 | 17.7876 | 21.2895 | 25.7375 | 29.1257 | 32.5237
Port HopeIce Accretion2040RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2040 | 17.8543 | 21.3863 | 25.875 | 29.2952 | 32.718
Port HopeIce Accretion2045RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2045 | 17.9209 | 21.4832 | 26.0125 | 29.4647 | 32.9123
Port HopeIce Accretion2050RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2050 | 17.8867 | 21.4804 | 26.045 | 29.5212 | 32.9931
Port HopeIce Accretion2055RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2055 | 17.7858 | 21.3808 | 25.94 | 29.4082 | 32.8797
Port HopeIce Accretion2060RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2060 | 17.6849 | 21.2812 | 25.835 | 29.2952 | 32.7663
Port HopeIce Accretion2065RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2065 | 17.584 | 21.1816 | 25.73 | 29.1822 | 32.6529
Port HopeIce Accretion2070RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2070 | 17.4831 | 21.082 | 25.625 | 29.0692 | 32.5395
Port HopeIce Accretion2075RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2075 | 17.5237 | 21.1615 | 25.7542 | 29.2387 | 32.7442
Port HopeIce Accretion2080RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2080 | 17.5643 | 21.2411 | 25.8833 | 29.4082 | 32.949
Port HopeIce Accretion2085RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2085 | 17.6049 | 21.3206 | 26.0125 | 29.5777 | 33.1538
Port HopeIce Accretion2090RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2090 | 17.6455 | 21.4002 | 26.1417 | 29.7472 | 33.3585
Port HopeIce Accretion2095RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2095 | 17.6861 | 21.4797 | 26.2708 | 29.9167 | 33.5632
Port HopeIce Accretion2100RCP4.5 | Port Hope | Ice Accretion | RCP4.5 | 2100 | 17.7267 | 21.5592 | 26.4 | 30.0862 | 33.768
Port HopeIce Accretion2023RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2023 | 17.5875 | 20.999 | 25.325 | 28.6172 | 31.941
Port HopeIce Accretion2025RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2025 | 17.6542 | 21.0958 | 25.4625 | 28.7867 | 32.1352
Port HopeIce Accretion2030RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2030 | 17.7209 | 21.1927 | 25.6 | 28.9562 | 32.3295
Port HopeIce Accretion2035RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2035 | 17.7876 | 21.2895 | 25.7375 | 29.1257 | 32.5237
Port HopeIce Accretion2040RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2040 | 17.8543 | 21.3863 | 25.875 | 29.2952 | 32.718
Port HopeIce Accretion2045RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2045 | 17.9209 | 21.4832 | 26.0125 | 29.4647 | 32.9123
Port HopeIce Accretion2050RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2050 | 17.8867 | 21.4804 | 26.045 | 29.5212 | 32.9931
Port HopeIce Accretion2055RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2055 | 17.7858 | 21.3808 | 25.94 | 29.4082 | 32.8797
Port HopeIce Accretion2060RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2060 | 17.6849 | 21.2812 | 25.835 | 29.2952 | 32.7663
Port HopeIce Accretion2065RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2065 | 17.584 | 21.1816 | 25.73 | 29.1822 | 32.6529
Port HopeIce Accretion2070RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2070 | 17.4831 | 21.082 | 25.625 | 29.0692 | 32.5395
Port HopeIce Accretion2075RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2075 | 17.544 | 21.2013 | 25.8187 | 29.3235 | 32.8466
Port HopeIce Accretion2080RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2080 | 17.6049 | 21.3206 | 26.0125 | 29.5777 | 33.1538
Port HopeIce Accretion2085RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2085 | 17.6658 | 21.4399 | 26.2063 | 29.832 | 33.4609
Port HopeIce Accretion2090RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2090 | 17.3498 | 21.1512 | 25.95 | 29.606 | 33.243
Port HopeIce Accretion2095RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2095 | 16.9728 | 20.7431 | 25.5 | 29.1257 | 32.718
Port HopeIce Accretion2100RCP6.0 | Port Hope | Ice Accretion | RCP6.0 | 2100 | 16.5959 | 20.335 | 25.05 | 28.6455 | 32.193
Port HopeIce Accretion2023RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2023 | 17.5875 | 20.999 | 25.325 | 28.6172 | 31.941
Port HopeIce Accretion2025RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2025 | 17.7209 | 21.1927 | 25.6 | 28.9562 | 32.3295
Port HopeIce Accretion2030RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2030 | 17.8543 | 21.3863 | 25.875 | 29.2952 | 32.718
Port HopeIce Accretion2035RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2035 | 17.9876 | 21.58 | 26.15 | 29.6342 | 33.1065
Port HopeIce Accretion2040RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2040 | 17.8195 | 21.414 | 25.975 | 29.4459 | 32.9175
Port HopeIce Accretion2045RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2045 | 17.6513 | 21.248 | 25.8 | 29.2576 | 32.7285
Port HopeIce Accretion2050RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2050 | 17.5643 | 21.2411 | 25.8833 | 29.4082 | 32.949
Port HopeIce Accretion2055RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2055 | 17.6455 | 21.4002 | 26.1417 | 29.7472 | 33.3585
Port HopeIce Accretion2060RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2060 | 17.3498 | 21.1512 | 25.95 | 29.606 | 33.243
Port HopeIce Accretion2065RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2065 | 16.9728 | 20.7431 | 25.5 | 29.1257 | 32.718
Port HopeIce Accretion2070RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2070 | 16.2306 | 19.9338 | 24.6083 | 28.1558 | 31.6785
Port HopeIce Accretion2075RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2075 | 15.8653 | 19.5327 | 24.1667 | 27.6662 | 31.164
Port HopeIce Accretion2080RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2080 | 15.5 | 19.1315 | 23.725 | 27.1765 | 30.6495
Port HopeIce Accretion2085RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2085 | 14.9259 | 18.4779 | 22.9625 | 26.3431 | 29.736
Port HopeIce Accretion2090RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2090 | 14.3518 | 17.8242 | 22.2 | 25.5097 | 28.8225
Port HopeIce Accretion2095RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2095 | 14.3518 | 17.8242 | 22.2 | 25.5097 | 28.8225
Port HopeIce Accretion2100RCP8.5 | Port Hope | Ice Accretion | RCP8.5 | 2100 | 14.3518 | 17.8242 | 22.2 | 25.5097 | 28.8225
Port HopeWind2023RCP4.5 | Port Hope | Wind | RCP4.5 | 2023 | 85.707 | 92.2173 | 99.0495 | 105.9088 | 112.7584
Port HopeWind2025RCP4.5 | Port Hope | Wind | RCP4.5 | 2025 | 85.7127 | 92.2311 | 99.0726 | 105.9388 | 112.796
Port HopeWind2030RCP4.5 | Port Hope | Wind | RCP4.5 | 2030 | 85.7184 | 92.2449 | 99.0957 | 105.9688 | 112.8337
Port HopeWind2035RCP4.5 | Port Hope | Wind | RCP4.5 | 2035 | 85.7241 | 92.2587 | 99.1188 | 105.9989 | 112.8713
Port HopeWind2040RCP4.5 | Port Hope | Wind | RCP4.5 | 2040 | 85.7298 | 92.2726 | 99.1419 | 106.0289 | 112.9089
Port HopeWind2045RCP4.5 | Port Hope | Wind | RCP4.5 | 2045 | 85.7355 | 92.2864 | 99.165 | 106.0589 | 112.9465
Port HopeWind2050RCP4.5 | Port Hope | Wind | RCP4.5 | 2050 | 85.8609 | 92.453 | 99.3821 | 106.3177 | 113.2482
Port HopeWind2055RCP4.5 | Port Hope | Wind | RCP4.5 | 2055 | 85.9806 | 92.6058 | 99.5762 | 106.5465 | 113.5123
Port HopeWind2060RCP4.5 | Port Hope | Wind | RCP4.5 | 2060 | 86.1003 | 92.7587 | 99.7702 | 106.7753 | 113.7764
Port HopeWind2065RCP4.5 | Port Hope | Wind | RCP4.5 | 2065 | 86.2199 | 92.9115 | 99.9643 | 107.0041 | 114.0405
Port HopeWind2070RCP4.5 | Port Hope | Wind | RCP4.5 | 2070 | 86.3396 | 93.0644 | 100.1583 | 107.2329 | 114.3046
Port HopeWind2075RCP4.5 | Port Hope | Wind | RCP4.5 | 2075 | 86.4536 | 93.2132 | 100.3514 | 107.4642 | 114.5755
Port HopeWind2080RCP4.5 | Port Hope | Wind | RCP4.5 | 2080 | 86.5676 | 93.362 | 100.5444 | 107.6955 | 114.8463
Port HopeWind2085RCP4.5 | Port Hope | Wind | RCP4.5 | 2085 | 86.6815 | 93.5109 | 100.7375 | 107.9268 | 115.1172
Port HopeWind2090RCP4.5 | Port Hope | Wind | RCP4.5 | 2090 | 86.7955 | 93.6597 | 100.9305 | 108.1581 | 115.3881
Port HopeWind2095RCP4.5 | Port Hope | Wind | RCP4.5 | 2095 | 86.9095 | 93.8086 | 101.1236 | 108.3893 | 115.6589
Port HopeWind2100RCP4.5 | Port Hope | Wind | RCP4.5 | 2100 | 87.0235 | 93.9574 | 101.3166 | 108.6206 | 115.9298
Port HopeWind2023RCP6.0 | Port Hope | Wind | RCP6.0 | 2023 | 85.707 | 92.2173 | 99.0495 | 105.9088 | 112.7584
Port HopeWind2025RCP6.0 | Port Hope | Wind | RCP6.0 | 2025 | 85.7127 | 92.2311 | 99.0726 | 105.9388 | 112.796
Port HopeWind2030RCP6.0 | Port Hope | Wind | RCP6.0 | 2030 | 85.7184 | 92.2449 | 99.0957 | 105.9688 | 112.8337
Port HopeWind2035RCP6.0 | Port Hope | Wind | RCP6.0 | 2035 | 85.7241 | 92.2587 | 99.1188 | 105.9989 | 112.8713
Port HopeWind2040RCP6.0 | Port Hope | Wind | RCP6.0 | 2040 | 85.7298 | 92.2726 | 99.1419 | 106.0289 | 112.9089
Port HopeWind2045RCP6.0 | Port Hope | Wind | RCP6.0 | 2045 | 85.7355 | 92.2864 | 99.165 | 106.0589 | 112.9465
Port HopeWind2050RCP6.0 | Port Hope | Wind | RCP6.0 | 2050 | 85.8609 | 92.453 | 99.3821 | 106.3177 | 113.2482
Port HopeWind2055RCP6.0 | Port Hope | Wind | RCP6.0 | 2055 | 85.9806 | 92.6058 | 99.5762 | 106.5465 | 113.5123
Port HopeWind2060RCP6.0 | Port Hope | Wind | RCP6.0 | 2060 | 86.1003 | 92.7587 | 99.7702 | 106.7753 | 113.7764
Port HopeWind2065RCP6.0 | Port Hope | Wind | RCP6.0 | 2065 | 86.2199 | 92.9115 | 99.9643 | 107.0041 | 114.0405
Port HopeWind2070RCP6.0 | Port Hope | Wind | RCP6.0 | 2070 | 86.3396 | 93.0644 | 100.1583 | 107.2329 | 114.3046
Port HopeWind2075RCP6.0 | Port Hope | Wind | RCP6.0 | 2075 | 86.5106 | 93.2876 | 100.4479 | 107.5799 | 114.7109
Port HopeWind2080RCP6.0 | Port Hope | Wind | RCP6.0 | 2080 | 86.6815 | 93.5109 | 100.7375 | 107.9268 | 115.1172
Port HopeWind2085RCP6.0 | Port Hope | Wind | RCP6.0 | 2085 | 86.8525 | 93.7342 | 101.027 | 108.2737 | 115.5235
Port HopeWind2090RCP6.0 | Port Hope | Wind | RCP6.0 | 2090 | 87.3569 | 94.3718 | 101.8347 | 109.228 | 116.6258
Port HopeWind2095RCP6.0 | Port Hope | Wind | RCP6.0 | 2095 | 87.6903 | 94.7861 | 102.3528 | 109.8353 | 117.3217
Port HopeWind2100RCP6.0 | Port Hope | Wind | RCP6.0 | 2100 | 88.0237 | 95.2004 | 102.8709 | 110.4426 | 118.0177
Port HopeWind2023RCP8.5 | Port Hope | Wind | RCP8.5 | 2023 | 85.707 | 92.2173 | 99.0495 | 105.9088 | 112.7584
Port HopeWind2025RCP8.5 | Port Hope | Wind | RCP8.5 | 2025 | 85.7184 | 92.2449 | 99.0957 | 105.9688 | 112.8337
Port HopeWind2030RCP8.5 | Port Hope | Wind | RCP8.5 | 2030 | 85.7298 | 92.2726 | 99.1419 | 106.0289 | 112.9089
Port HopeWind2035RCP8.5 | Port Hope | Wind | RCP8.5 | 2035 | 85.7412 | 92.3002 | 99.1881 | 106.0889 | 112.9841
Port HopeWind2040RCP8.5 | Port Hope | Wind | RCP8.5 | 2040 | 85.9407 | 92.5549 | 99.5115 | 106.4702 | 113.4243
Port HopeWind2045RCP8.5 | Port Hope | Wind | RCP8.5 | 2045 | 86.1401 | 92.8096 | 99.8349 | 106.8516 | 113.8645
Port HopeWind2050RCP8.5 | Port Hope | Wind | RCP8.5 | 2050 | 86.5676 | 93.362 | 100.5444 | 107.6955 | 114.8463
Port HopeWind2055RCP8.5 | Port Hope | Wind | RCP8.5 | 2055 | 86.7955 | 93.6597 | 100.9305 | 108.1581 | 115.3881
Port HopeWind2060RCP8.5 | Port Hope | Wind | RCP8.5 | 2060 | 87.3569 | 94.3718 | 101.8347 | 109.228 | 116.6258
Port HopeWind2065RCP8.5 | Port Hope | Wind | RCP8.5 | 2065 | 87.6903 | 94.7861 | 102.3528 | 109.8353 | 117.3217
Port HopeWind2070RCP8.5 | Port Hope | Wind | RCP8.5 | 2070 | 88.0265 | 95.2219 | 102.9138 | 110.4991 | 118.0967
Port HopeWind2075RCP8.5 | Port Hope | Wind | RCP8.5 | 2075 | 88.0294 | 95.2433 | 102.9567 | 110.5556 | 118.1757
Port HopeWind2080RCP8.5 | Port Hope | Wind | RCP8.5 | 2080 | 88.0322 | 95.2648 | 102.9996 | 110.6121 | 118.2547
Port HopeWind2085RCP8.5 | Port Hope | Wind | RCP8.5 | 2085 | 88.2245 | 95.541 | 103.3857 | 111.0941 | 118.8247
Port HopeWind2090RCP8.5 | Port Hope | Wind | RCP8.5 | 2090 | 88.4169 | 95.8172 | 103.7718 | 111.5761 | 119.3946
Port HopeWind2095RCP8.5 | Port Hope | Wind | RCP8.5 | 2095 | 88.4169 | 95.8172 | 103.7718 | 111.5761 | 119.3946
Port HopeWind2100RCP8.5 | Port Hope | Wind | RCP8.5 | 2100 | 88.4169 | 95.8172 | 103.7718 | 111.5761 | 119.3946
Port PerryIce Accretion2023RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
Port PerryIce Accretion2025RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
Port PerryIce Accretion2030RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
Port PerryIce Accretion2035RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
Port PerryIce Accretion2040RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
Port PerryIce Accretion2045RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
Port PerryIce Accretion2050RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
Port PerryIce Accretion2055RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
Port PerryIce Accretion2060RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
Port PerryIce Accretion2065RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
Port PerryIce Accretion2070RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
Port PerryIce Accretion2075RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2075 | 17.2744 | 20.8814 | 25.4167 | 28.8762 | 32.34
Port PerryIce Accretion2080RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2080 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
Port PerryIce Accretion2085RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2085 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
Port PerryIce Accretion2090RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2090 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
Port PerryIce Accretion2095RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2095 | 17.2048 | 20.9091 | 25.5833 | 29.121 | 32.676
Port PerryIce Accretion2100RCP4.5 | Port Perry | Ice Accretion | RCP4.5 | 2100 | 17.1874 | 20.916 | 25.625 | 29.1822 | 32.76
Port PerryIce Accretion2023RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
Port PerryIce Accretion2025RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
Port PerryIce Accretion2030RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
Port PerryIce Accretion2035RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
Port PerryIce Accretion2040RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
Port PerryIce Accretion2045RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
Port PerryIce Accretion2050RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
Port PerryIce Accretion2055RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
Port PerryIce Accretion2060RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
Port PerryIce Accretion2065RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
Port PerryIce Accretion2070RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
Port PerryIce Accretion2075RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2075 | 17.2657 | 20.8849 | 25.4375 | 28.9068 | 32.382
Port PerryIce Accretion2080RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2080 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
Port PerryIce Accretion2085RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2085 | 17.2135 | 20.9056 | 25.5625 | 29.0904 | 32.634
Port PerryIce Accretion2090RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2090 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
Port PerryIce Accretion2095RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2095 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
Port PerryIce Accretion2100RCP6.0 | Port Perry | Ice Accretion | RCP6.0 | 2100 | 16.2654 | 19.8992 | 24.5 | 27.9957 | 31.4685
Port PerryIce Accretion2023RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
Port PerryIce Accretion2025RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2025 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
Port PerryIce Accretion2030RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2030 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
Port PerryIce Accretion2035RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2035 | 17.6919 | 21.2272 | 25.725 | 29.154 | 32.6025
Port PerryIce Accretion2040RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2040 | 17.5585 | 21.1097 | 25.6083 | 29.041 | 32.487
Port PerryIce Accretion2045RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2045 | 17.4251 | 20.9921 | 25.4917 | 28.928 | 32.3715
Port PerryIce Accretion2050RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2050 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
Port PerryIce Accretion2055RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2055 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
Port PerryIce Accretion2060RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2060 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
Port PerryIce Accretion2065RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2065 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
Port PerryIce Accretion2070RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2070 | 15.9987 | 19.6226 | 24.2083 | 27.685 | 31.143
Port PerryIce Accretion2075RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2075 | 15.7319 | 19.3459 | 23.9167 | 27.3742 | 30.8175
Port PerryIce Accretion2080RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2080 | 15.4652 | 19.0693 | 23.625 | 27.0635 | 30.492
Port PerryIce Accretion2085RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2085 | 14.8911 | 18.426 | 22.8875 | 26.2584 | 29.6258
Port PerryIce Accretion2090RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2090 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
Port PerryIce Accretion2095RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2095 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
Port PerryIce Accretion2100RCP8.5 | Port Perry | Ice Accretion | RCP8.5 | 2100 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
Port PerryWind2023RCP4.5 | Port Perry | Wind | RCP4.5 | 2023 | 76.488 | 82.3883 | 88.5896 | 94.7909 | 101.0022
Port PerryWind2025RCP4.5 | Port Perry | Wind | RCP4.5 | 2025 | 76.5222 | 82.4333 | 88.6497 | 94.8646 | 101.0874
Port PerryWind2030RCP4.5 | Port Perry | Wind | RCP4.5 | 2030 | 76.5564 | 82.4784 | 88.7099 | 94.9384 | 101.1727
Port PerryWind2035RCP4.5 | Port Perry | Wind | RCP4.5 | 2035 | 76.5905 | 82.5234 | 88.77 | 95.0121 | 101.258
Port PerryWind2040RCP4.5 | Port Perry | Wind | RCP4.5 | 2040 | 76.6247 | 82.5684 | 88.8301 | 95.0859 | 101.3433
Port PerryWind2045RCP4.5 | Port Perry | Wind | RCP4.5 | 2045 | 76.6589 | 82.6134 | 88.8903 | 95.1597 | 101.4285
Port PerryWind2050RCP4.5 | Port Perry | Wind | RCP4.5 | 2050 | 76.7615 | 82.7386 | 89.0437 | 95.337 | 101.6302
Port PerryWind2055RCP4.5 | Port Perry | Wind | RCP4.5 | 2055 | 76.8299 | 82.8188 | 89.137 | 95.4406 | 101.7466
Port PerryWind2060RCP4.5 | Port Perry | Wind | RCP4.5 | 2060 | 76.8983 | 82.899 | 89.2302 | 95.5442 | 101.8629
Port PerryWind2065RCP4.5 | Port Perry | Wind | RCP4.5 | 2065 | 76.9667 | 82.9792 | 89.3235 | 95.6477 | 101.9793
Port PerryWind2070RCP4.5 | Port Perry | Wind | RCP4.5 | 2070 | 77.0351 | 83.0594 | 89.4168 | 95.7513 | 102.0957
Port PerryWind2075RCP4.5 | Port Perry | Wind | RCP4.5 | 2075 | 77.1098 | 83.1522 | 89.5312 | 95.8863 | 102.2495
Port PerryWind2080RCP4.5 | Port Perry | Wind | RCP4.5 | 2080 | 77.1845 | 83.2449 | 89.6456 | 96.0212 | 102.4033
Port PerryWind2085RCP4.5 | Port Perry | Wind | RCP4.5 | 2085 | 77.2592 | 83.3377 | 89.76 | 96.1562 | 102.5571
Port PerryWind2090RCP4.5 | Port Perry | Wind | RCP4.5 | 2090 | 77.3339 | 83.4304 | 89.8744 | 96.2912 | 102.711
Port PerryWind2095RCP4.5 | Port Perry | Wind | RCP4.5 | 2095 | 77.4087 | 83.5232 | 89.9888 | 96.4261 | 102.8648
Port PerryWind2100RCP4.5 | Port Perry | Wind | RCP4.5 | 2100 | 77.4834 | 83.6159 | 90.1032 | 96.5611 | 103.0186
Port PerryWind2023RCP6.0 | Port Perry | Wind | RCP6.0 | 2023 | 76.488 | 82.3883 | 88.5896 | 94.7909 | 101.0022
Port PerryWind2025RCP6.0 | Port Perry | Wind | RCP6.0 | 2025 | 76.5222 | 82.4333 | 88.6497 | 94.8646 | 101.0874
Port PerryWind2030RCP6.0 | Port Perry | Wind | RCP6.0 | 2030 | 76.5564 | 82.4784 | 88.7099 | 94.9384 | 101.1727
Port PerryWind2035RCP6.0 | Port Perry | Wind | RCP6.0 | 2035 | 76.5905 | 82.5234 | 88.77 | 95.0121 | 101.258
Port PerryWind2040RCP6.0 | Port Perry | Wind | RCP6.0 | 2040 | 76.6247 | 82.5684 | 88.8301 | 95.0859 | 101.3433
Port PerryWind2045RCP6.0 | Port Perry | Wind | RCP6.0 | 2045 | 76.6589 | 82.6134 | 88.8903 | 95.1597 | 101.4285
Port PerryWind2050RCP6.0 | Port Perry | Wind | RCP6.0 | 2050 | 76.7615 | 82.7386 | 89.0437 | 95.337 | 101.6302
Port PerryWind2055RCP6.0 | Port Perry | Wind | RCP6.0 | 2055 | 76.8299 | 82.8188 | 89.137 | 95.4406 | 101.7466
Port PerryWind2060RCP6.0 | Port Perry | Wind | RCP6.0 | 2060 | 76.8983 | 82.899 | 89.2302 | 95.5442 | 101.8629
Port PerryWind2065RCP6.0 | Port Perry | Wind | RCP6.0 | 2065 | 76.9667 | 82.9792 | 89.3235 | 95.6477 | 101.9793
Port PerryWind2070RCP6.0 | Port Perry | Wind | RCP6.0 | 2070 | 77.0351 | 83.0594 | 89.4168 | 95.7513 | 102.0957
Port PerryWind2075RCP6.0 | Port Perry | Wind | RCP6.0 | 2075 | 77.1471 | 83.1985 | 89.5884 | 95.9537 | 102.3264
Port PerryWind2080RCP6.0 | Port Perry | Wind | RCP6.0 | 2080 | 77.2592 | 83.3377 | 89.76 | 96.1562 | 102.5571
Port PerryWind2085RCP6.0 | Port Perry | Wind | RCP6.0 | 2085 | 77.3713 | 83.4768 | 89.9316 | 96.3586 | 102.7879
Port PerryWind2090RCP6.0 | Port Perry | Wind | RCP6.0 | 2090 | 77.7291 | 83.8969 | 90.4317 | 96.9252 | 103.4232
Port PerryWind2095RCP6.0 | Port Perry | Wind | RCP6.0 | 2095 | 77.9748 | 84.1779 | 90.7603 | 97.2893 | 103.8279
Port PerryWind2100RCP6.0 | Port Perry | Wind | RCP6.0 | 2100 | 78.2205 | 84.4589 | 91.0888 | 97.6533 | 104.2325
Port PerryWind2023RCP8.5 | Port Perry | Wind | RCP8.5 | 2023 | 76.488 | 82.3883 | 88.5896 | 94.7909 | 101.0022
Port PerryWind2025RCP8.5 | Port Perry | Wind | RCP8.5 | 2025 | 76.5564 | 82.4784 | 88.7099 | 94.9384 | 101.1727
Port PerryWind2030RCP8.5 | Port Perry | Wind | RCP8.5 | 2030 | 76.6247 | 82.5684 | 88.8301 | 95.0859 | 101.3433
Port PerryWind2035RCP8.5 | Port Perry | Wind | RCP8.5 | 2035 | 76.6931 | 82.6584 | 88.9504 | 95.2334 | 101.5138
Port PerryWind2040RCP8.5 | Port Perry | Wind | RCP8.5 | 2040 | 76.8071 | 82.7921 | 89.1059 | 95.4061 | 101.7078
Port PerryWind2045RCP8.5 | Port Perry | Wind | RCP8.5 | 2045 | 76.9211 | 82.9257 | 89.2613 | 95.5787 | 101.9017
Port PerryWind2050RCP8.5 | Port Perry | Wind | RCP8.5 | 2050 | 77.1845 | 83.2449 | 89.6456 | 96.0212 | 102.4033
Port PerryWind2055RCP8.5 | Port Perry | Wind | RCP8.5 | 2055 | 77.3339 | 83.4304 | 89.8744 | 96.2912 | 102.711
Port PerryWind2060RCP8.5 | Port Perry | Wind | RCP8.5 | 2060 | 77.7291 | 83.8969 | 90.4317 | 96.9252 | 103.4232
Port PerryWind2065RCP8.5 | Port Perry | Wind | RCP8.5 | 2065 | 77.9748 | 84.1779 | 90.7603 | 97.2893 | 103.8279
Port PerryWind2070RCP8.5 | Port Perry | Wind | RCP8.5 | 2070 | 78.3066 | 84.5707 | 91.2267 | 97.8165 | 104.4231
Port PerryWind2075RCP8.5 | Port Perry | Wind | RCP8.5 | 2075 | 78.3927 | 84.6826 | 91.3645 | 97.9798 | 104.6137
Port PerryWind2080RCP8.5 | Port Perry | Wind | RCP8.5 | 2080 | 78.4788 | 84.7944 | 91.5024 | 98.143 | 104.8043
Port PerryWind2085RCP8.5 | Port Perry | Wind | RCP8.5 | 2085 | 78.6802 | 85.0768 | 91.8984 | 98.6279 | 105.3811
Port PerryWind2090RCP8.5 | Port Perry | Wind | RCP8.5 | 2090 | 78.8815 | 85.3591 | 92.2944 | 99.1128 | 105.958
Port PerryWind2095RCP8.5 | Port Perry | Wind | RCP8.5 | 2095 | 78.8815 | 85.3591 | 92.2944 | 99.1128 | 105.958
Port PerryWind2100RCP8.5 | Port Perry | Wind | RCP8.5 | 2100 | 78.8815 | 85.3591 | 92.2944 | 99.1128 | 105.958
Port StanleyIce Accretion2023RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2023 | 20.5831 | 24.7008 | 29.91 | 33.8661 | 37.8378
Port StanleyIce Accretion2025RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2025 | 20.4614 | 24.568 | 29.765 | 33.7135 | 37.674
Port StanleyIce Accretion2030RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2030 | 20.3396 | 24.4352 | 29.62 | 33.561 | 37.5102
Port StanleyIce Accretion2035RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2035 | 20.2178 | 24.3024 | 29.475 | 33.4085 | 37.3464
Port StanleyIce Accretion2040RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2040 | 20.096 | 24.1696 | 29.33 | 33.2559 | 37.1826
Port StanleyIce Accretion2045RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2045 | 19.9743 | 24.0368 | 29.185 | 33.1033 | 37.0188
Port StanleyIce Accretion2050RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2050 | 19.4642 | 23.4757 | 28.554 | 32.422 | 36.2804
Port StanleyIce Accretion2055RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2055 | 19.0759 | 23.0474 | 28.068 | 31.8931 | 35.7059
Port StanleyIce Accretion2060RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2060 | 18.6876 | 22.6192 | 27.582 | 31.3643 | 35.1313
Port StanleyIce Accretion2065RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2065 | 18.2994 | 22.1909 | 27.096 | 30.8354 | 34.5568
Port StanleyIce Accretion2070RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2070 | 17.9111 | 21.7626 | 26.61 | 30.3066 | 33.9822
Port StanleyIce Accretion2075RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2075 | 17.7754 | 21.6257 | 26.47 | 30.1597 | 33.831
Port StanleyIce Accretion2080RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2080 | 17.6397 | 21.4887 | 26.33 | 30.0128 | 33.6798
Port StanleyIce Accretion2085RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2085 | 17.504 | 21.3517 | 26.19 | 29.8659 | 33.5286
Port StanleyIce Accretion2090RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2090 | 17.3683 | 21.2148 | 26.05 | 29.719 | 33.3774
Port StanleyIce Accretion2095RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2095 | 17.2326 | 21.0778 | 25.91 | 29.5721 | 33.2262
Port StanleyIce Accretion2100RCP4.5 | Port Stanley | Ice Accretion | RCP4.5 | 2100 | 17.0969 | 20.9409 | 25.77 | 29.4252 | 33.075
Port StanleyIce Accretion2023RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2023 | 20.5831 | 24.7008 | 29.91 | 33.8661 | 37.8378
Port StanleyIce Accretion2025RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2025 | 20.4614 | 24.568 | 29.765 | 33.7135 | 37.674
Port StanleyIce Accretion2030RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2030 | 20.3396 | 24.4352 | 29.62 | 33.561 | 37.5102
Port StanleyIce Accretion2035RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2035 | 20.2178 | 24.3024 | 29.475 | 33.4085 | 37.3464
Port StanleyIce Accretion2040RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2040 | 20.096 | 24.1696 | 29.33 | 33.2559 | 37.1826
Port StanleyIce Accretion2045RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2045 | 19.9743 | 24.0368 | 29.185 | 33.1033 | 37.0188
Port StanleyIce Accretion2050RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2050 | 19.4642 | 23.4757 | 28.554 | 32.422 | 36.2804
Port StanleyIce Accretion2055RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2055 | 19.0759 | 23.0474 | 28.068 | 31.8931 | 35.7059
Port StanleyIce Accretion2060RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2060 | 18.6876 | 22.6192 | 27.582 | 31.3643 | 35.1313
Port StanleyIce Accretion2065RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2065 | 18.2994 | 22.1909 | 27.096 | 30.8354 | 34.5568
Port StanleyIce Accretion2070RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2070 | 17.9111 | 21.7626 | 26.61 | 30.3066 | 33.9822
Port StanleyIce Accretion2075RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2075 | 17.7075 | 21.5572 | 26.4 | 30.0862 | 33.7554
Port StanleyIce Accretion2080RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2080 | 17.504 | 21.3517 | 26.19 | 29.8659 | 33.5286
Port StanleyIce Accretion2085RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2085 | 17.3005 | 21.1463 | 25.98 | 29.6456 | 33.3018
Port StanleyIce Accretion2090RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2090 | 16.6098 | 20.3931 | 25.15 | 28.7472 | 32.3316
Port StanleyIce Accretion2095RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2095 | 16.1228 | 19.8453 | 24.53 | 28.0692 | 31.5882
Port StanleyIce Accretion2100RCP6.0 | Port Stanley | Ice Accretion | RCP6.0 | 2100 | 15.6357 | 19.2975 | 23.91 | 27.3912 | 30.8448
Port StanleyIce Accretion2023RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2023 | 20.5831 | 24.7008 | 29.91 | 33.8661 | 37.8378
Port StanleyIce Accretion2025RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2025 | 20.3396 | 24.4352 | 29.62 | 33.561 | 37.5102
Port StanleyIce Accretion2030RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2030 | 20.096 | 24.1696 | 29.33 | 33.2559 | 37.1826
Port StanleyIce Accretion2035RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2035 | 19.8525 | 23.904 | 29.04 | 32.9508 | 36.855
Port StanleyIce Accretion2040RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2040 | 19.2054 | 23.1902 | 28.23 | 32.0694 | 35.8974
Port StanleyIce Accretion2045RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2045 | 18.5582 | 22.4764 | 27.42 | 31.188 | 34.9398
Port StanleyIce Accretion2050RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2050 | 17.6397 | 21.4887 | 26.33 | 30.0128 | 33.6798
Port StanleyIce Accretion2055RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2055 | 17.3683 | 21.2148 | 26.05 | 29.719 | 33.3774
Port StanleyIce Accretion2060RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2060 | 16.6098 | 20.3931 | 25.15 | 28.7472 | 32.3316
Port StanleyIce Accretion2065RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2065 | 16.1228 | 19.8453 | 24.53 | 28.0692 | 31.5882
Port StanleyIce Accretion2070RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2070 | 15.3225 | 18.9655 | 23.55 | 26.9957 | 30.429
Port StanleyIce Accretion2075RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2075 | 15.0094 | 18.6335 | 23.19 | 26.6002 | 30.0132
Port StanleyIce Accretion2080RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2080 | 14.6963 | 18.3015 | 22.83 | 26.2047 | 29.5974
Port StanleyIce Accretion2085RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2085 | 13.7673 | 17.2059 | 21.51 | 24.73 | 27.9531
Port StanleyIce Accretion2090RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2090 | 12.8384 | 16.1103 | 20.19 | 23.2554 | 26.3088
Port StanleyIce Accretion2095RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2095 | 12.8384 | 16.1103 | 20.19 | 23.2554 | 26.3088
Port StanleyIce Accretion2100RCP8.5 | Port Stanley | Ice Accretion | RCP8.5 | 2100 | 12.8384 | 16.1103 | 20.19 | 23.2554 | 26.3088
Port StanleyWind2023RCP4.5 | Port Stanley | Wind | RCP4.5 | 2023 | 87.9269 | 94.8505 | 102.1817 | 109.4749 | 116.775
Port StanleyWind2025RCP4.5 | Port Stanley | Wind | RCP4.5 | 2025 | 88.0373 | 94.9977 | 102.3753 | 109.7073 | 117.0475
Port StanleyWind2030RCP4.5 | Port Stanley | Wind | RCP4.5 | 2030 | 88.1478 | 95.1448 | 102.5689 | 109.9396 | 117.32
Port StanleyWind2035RCP4.5 | Port Stanley | Wind | RCP4.5 | 2035 | 88.2583 | 95.292 | 102.7625 | 110.172 | 117.5925
Port StanleyWind2040RCP4.5 | Port Stanley | Wind | RCP4.5 | 2040 | 88.3687 | 95.4391 | 102.956 | 110.4043 | 117.865
Port StanleyWind2045RCP4.5 | Port Stanley | Wind | RCP4.5 | 2045 | 88.4792 | 95.5863 | 103.1496 | 110.6367 | 118.1375
Port StanleyWind2050RCP4.5 | Port Stanley | Wind | RCP4.5 | 2050 | 88.642 | 95.8067 | 103.4442 | 110.9944 | 118.5597
Port StanleyWind2055RCP4.5 | Port Stanley | Wind | RCP4.5 | 2055 | 88.6943 | 95.88 | 103.5452 | 111.1197 | 118.7093
Port StanleyWind2060RCP4.5 | Port Stanley | Wind | RCP4.5 | 2060 | 88.7467 | 95.9533 | 103.6462 | 111.2451 | 118.859
Port StanleyWind2065RCP4.5 | Port Stanley | Wind | RCP4.5 | 2065 | 88.799 | 96.0265 | 103.7472 | 111.3705 | 119.0087
Port StanleyWind2070RCP4.5 | Port Stanley | Wind | RCP4.5 | 2070 | 88.8513 | 96.0998 | 103.8482 | 111.4958 | 119.1584
Port StanleyWind2075RCP4.5 | Port Stanley | Wind | RCP4.5 | 2075 | 89.0054 | 96.3002 | 104.1074 | 111.8038 | 119.5172
Port StanleyWind2080RCP4.5 | Port Stanley | Wind | RCP4.5 | 2080 | 89.1595 | 96.5006 | 104.3667 | 112.1118 | 119.8761
Port StanleyWind2085RCP4.5 | Port Stanley | Wind | RCP4.5 | 2085 | 89.3135 | 96.7009 | 104.6259 | 112.4198 | 120.2349
Port StanleyWind2090RCP4.5 | Port Stanley | Wind | RCP4.5 | 2090 | 89.4676 | 96.9013 | 104.8851 | 112.7278 | 120.5938
Port StanleyWind2095RCP4.5 | Port Stanley | Wind | RCP4.5 | 2095 | 89.6217 | 97.1017 | 105.1444 | 113.0358 | 120.9527
Port StanleyWind2100RCP4.5 | Port Stanley | Wind | RCP4.5 | 2100 | 89.7757 | 97.3021 | 105.4036 | 113.3438 | 121.3115
Port StanleyWind2023RCP6.0 | Port Stanley | Wind | RCP6.0 | 2023 | 87.9269 | 94.8505 | 102.1817 | 109.4749 | 116.775
Port StanleyWind2025RCP6.0 | Port Stanley | Wind | RCP6.0 | 2025 | 88.0373 | 94.9977 | 102.3753 | 109.7073 | 117.0475
Port StanleyWind2030RCP6.0 | Port Stanley | Wind | RCP6.0 | 2030 | 88.1478 | 95.1448 | 102.5689 | 109.9396 | 117.32
Port StanleyWind2035RCP6.0 | Port Stanley | Wind | RCP6.0 | 2035 | 88.2583 | 95.292 | 102.7625 | 110.172 | 117.5925
Port StanleyWind2040RCP6.0 | Port Stanley | Wind | RCP6.0 | 2040 | 88.3687 | 95.4391 | 102.956 | 110.4043 | 117.865
Port StanleyWind2045RCP6.0 | Port Stanley | Wind | RCP6.0 | 2045 | 88.4792 | 95.5863 | 103.1496 | 110.6367 | 118.1375
Port StanleyWind2050RCP6.0 | Port Stanley | Wind | RCP6.0 | 2050 | 88.642 | 95.8067 | 103.4442 | 110.9944 | 118.5597
Port StanleyWind2055RCP6.0 | Port Stanley | Wind | RCP6.0 | 2055 | 88.6943 | 95.88 | 103.5452 | 111.1197 | 118.7093
Port StanleyWind2060RCP6.0 | Port Stanley | Wind | RCP6.0 | 2060 | 88.7467 | 95.9533 | 103.6462 | 111.2451 | 118.859
Port StanleyWind2065RCP6.0 | Port Stanley | Wind | RCP6.0 | 2065 | 88.799 | 96.0265 | 103.7472 | 111.3705 | 119.0087
Port StanleyWind2070RCP6.0 | Port Stanley | Wind | RCP6.0 | 2070 | 88.8513 | 96.0998 | 103.8482 | 111.4958 | 119.1584
Port StanleyWind2075RCP6.0 | Port Stanley | Wind | RCP6.0 | 2075 | 89.0824 | 96.4004 | 104.2371 | 111.9578 | 119.6967
Port StanleyWind2080RCP6.0 | Port Stanley | Wind | RCP6.0 | 2080 | 89.3135 | 96.7009 | 104.6259 | 112.4198 | 120.2349
Port StanleyWind2085RCP6.0 | Port Stanley | Wind | RCP6.0 | 2085 | 89.5446 | 97.0015 | 105.0148 | 112.8818 | 120.7732
Port StanleyWind2090RCP6.0 | Port Stanley | Wind | RCP6.0 | 2090 | 90.1566 | 97.7874 | 106.013 | 114.0607 | 122.1405
Port StanleyWind2095RCP6.0 | Port Stanley | Wind | RCP6.0 | 2095 | 90.5374 | 98.2727 | 106.6223 | 114.7775 | 122.9695
Port StanleyWind2100RCP6.0 | Port Stanley | Wind | RCP6.0 | 2100 | 90.9182 | 98.758 | 107.2317 | 115.4944 | 123.7985
Port StanleyWind2023RCP8.5 | Port Stanley | Wind | RCP8.5 | 2023 | 87.9269 | 94.8505 | 102.1817 | 109.4749 | 116.775
Port StanleyWind2025RCP8.5 | Port Stanley | Wind | RCP8.5 | 2025 | 88.1478 | 95.1448 | 102.5689 | 109.9396 | 117.32
Port StanleyWind2030RCP8.5 | Port Stanley | Wind | RCP8.5 | 2030 | 88.3687 | 95.4391 | 102.956 | 110.4043 | 117.865
Port StanleyWind2035RCP8.5 | Port Stanley | Wind | RCP8.5 | 2035 | 88.5897 | 95.7335 | 103.3432 | 110.869 | 118.41
Port StanleyWind2040RCP8.5 | Port Stanley | Wind | RCP8.5 | 2040 | 88.6769 | 95.8556 | 103.5115 | 111.0779 | 118.6594
Port StanleyWind2045RCP8.5 | Port Stanley | Wind | RCP8.5 | 2045 | 88.7641 | 95.9777 | 103.6799 | 111.2869 | 118.9089
Port StanleyWind2050RCP8.5 | Port Stanley | Wind | RCP8.5 | 2050 | 89.1595 | 96.5006 | 104.3667 | 112.1118 | 119.8761
Port StanleyWind2055RCP8.5 | Port Stanley | Wind | RCP8.5 | 2055 | 89.4676 | 96.9013 | 104.8851 | 112.7278 | 120.5938
Port StanleyWind2060RCP8.5 | Port Stanley | Wind | RCP8.5 | 2060 | 90.1566 | 97.7874 | 106.013 | 114.0607 | 122.1405
Port StanleyWind2065RCP8.5 | Port Stanley | Wind | RCP8.5 | 2065 | 90.5374 | 98.2727 | 106.6223 | 114.7775 | 122.9695
Port StanleyWind2070RCP8.5 | Port Stanley | Wind | RCP8.5 | 2070 | 91.1537 | 99.0523 | 107.6054 | 115.9375 | 124.309
Port StanleyWind2075RCP8.5 | Port Stanley | Wind | RCP8.5 | 2075 | 91.3892 | 99.3466 | 107.9791 | 116.3806 | 124.8194
Port StanleyWind2080RCP8.5 | Port Stanley | Wind | RCP8.5 | 2080 | 91.6246 | 99.6409 | 108.3528 | 116.8237 | 125.3299
Port StanleyWind2085RCP8.5 | Port Stanley | Wind | RCP8.5 | 2085 | 92.0258 | 100.1716 | 109.0497 | 117.6558 | 126.3086
Port StanleyWind2090RCP8.5 | Port Stanley | Wind | RCP8.5 | 2090 | 92.427 | 100.7024 | 109.7466 | 118.4879 | 127.2873
Port StanleyWind2095RCP8.5 | Port Stanley | Wind | RCP8.5 | 2095 | 92.427 | 100.7024 | 109.7466 | 118.4879 | 127.2873
Port StanleyWind2100RCP8.5 | Port Stanley | Wind | RCP8.5 | 2100 | 92.427 | 100.7024 | 109.7466 | 118.4879 | 127.2873
PrescottIce Accretion2023RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2023 | 20.6249 | 24.5763 | 29.61 | 33.4593 | 37.3086
PrescottIce Accretion2025RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2025 | 20.6945 | 24.6801 | 29.755 | 33.6345 | 37.5102
PrescottIce Accretion2030RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2030 | 20.764 | 24.7838 | 29.9 | 33.8096 | 37.7118
PrescottIce Accretion2035RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2035 | 20.8336 | 24.8875 | 30.045 | 33.9847 | 37.9134
PrescottIce Accretion2040RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2040 | 20.9032 | 24.9913 | 30.19 | 34.1599 | 38.115
PrescottIce Accretion2045RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2045 | 20.9728 | 25.0951 | 30.335 | 34.335 | 38.3166
PrescottIce Accretion2050RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2050 | 20.9046 | 25.0544 | 30.318 | 34.3339 | 38.3368
PrescottIce Accretion2055RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2055 | 20.7668 | 24.91 | 30.156 | 34.1576 | 38.1553
PrescottIce Accretion2060RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2060 | 20.6291 | 24.7655 | 29.994 | 33.9814 | 37.9739
PrescottIce Accretion2065RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2065 | 20.4913 | 24.6211 | 29.832 | 33.8051 | 37.7924
PrescottIce Accretion2070RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2070 | 20.3535 | 24.4767 | 29.67 | 33.6288 | 37.611
PrescottIce Accretion2075RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2075 | 20.4231 | 24.5846 | 29.825 | 33.8209 | 37.8378
PrescottIce Accretion2080RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2080 | 20.4927 | 24.6925 | 29.98 | 34.013 | 38.0646
PrescottIce Accretion2085RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2085 | 20.5623 | 24.8004 | 30.135 | 34.2051 | 38.2914
PrescottIce Accretion2090RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2090 | 20.6318 | 24.9083 | 30.29 | 34.3972 | 38.5182
PrescottIce Accretion2095RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2095 | 20.7014 | 25.0162 | 30.445 | 34.5893 | 38.745
PrescottIce Accretion2100RCP4.5 | Prescott | Ice Accretion | RCP4.5 | 2100 | 20.771 | 25.1241 | 30.6 | 34.7814 | 38.9718
PrescottIce Accretion2023RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2023 | 20.6249 | 24.5763 | 29.61 | 33.4593 | 37.3086
PrescottIce Accretion2025RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2025 | 20.6945 | 24.6801 | 29.755 | 33.6345 | 37.5102
PrescottIce Accretion2030RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2030 | 20.764 | 24.7838 | 29.9 | 33.8096 | 37.7118
PrescottIce Accretion2035RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2035 | 20.8336 | 24.8875 | 30.045 | 33.9847 | 37.9134
PrescottIce Accretion2040RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2040 | 20.9032 | 24.9913 | 30.19 | 34.1599 | 38.115
PrescottIce Accretion2045RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2045 | 20.9728 | 25.0951 | 30.335 | 34.335 | 38.3166
PrescottIce Accretion2050RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2050 | 20.9046 | 25.0544 | 30.318 | 34.3339 | 38.3368
PrescottIce Accretion2055RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2055 | 20.7668 | 24.91 | 30.156 | 34.1576 | 38.1553
PrescottIce Accretion2060RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2060 | 20.6291 | 24.7655 | 29.994 | 33.9814 | 37.9739
PrescottIce Accretion2065RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2065 | 20.4913 | 24.6211 | 29.832 | 33.8051 | 37.7924
PrescottIce Accretion2070RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2070 | 20.3535 | 24.4767 | 29.67 | 33.6288 | 37.611
PrescottIce Accretion2075RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2075 | 20.4579 | 24.6385 | 29.9025 | 33.9169 | 37.9512
PrescottIce Accretion2080RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2080 | 20.5623 | 24.8004 | 30.135 | 34.2051 | 38.2914
PrescottIce Accretion2085RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2085 | 20.6666 | 24.9622 | 30.3675 | 34.4932 | 38.6316
PrescottIce Accretion2090RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2090 | 20.6249 | 24.9913 | 30.49 | 34.6797 | 38.8836
PrescottIce Accretion2095RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2095 | 20.4788 | 24.8585 | 30.38 | 34.578 | 38.7954
PrescottIce Accretion2100RCP6.0 | Prescott | Ice Accretion | RCP6.0 | 2100 | 20.3326 | 24.7257 | 30.27 | 34.4763 | 38.7072
PrescottIce Accretion2023RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2023 | 20.6249 | 24.5763 | 29.61 | 33.4593 | 37.3086
PrescottIce Accretion2025RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2025 | 20.764 | 24.7838 | 29.9 | 33.8096 | 37.7118
PrescottIce Accretion2030RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2030 | 20.9032 | 24.9913 | 30.19 | 34.1599 | 38.115
PrescottIce Accretion2035RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2035 | 21.0424 | 25.1988 | 30.48 | 34.5102 | 38.5182
PrescottIce Accretion2040RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2040 | 20.8128 | 24.9581 | 30.21 | 34.2164 | 38.2158
PrescottIce Accretion2045RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2045 | 20.5831 | 24.7174 | 29.94 | 33.9226 | 37.9134
PrescottIce Accretion2050RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2050 | 20.4927 | 24.6925 | 29.98 | 34.013 | 38.0646
PrescottIce Accretion2055RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2055 | 20.6318 | 24.9083 | 30.29 | 34.3972 | 38.5182
PrescottIce Accretion2060RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2060 | 20.6249 | 24.9913 | 30.49 | 34.6797 | 38.8836
PrescottIce Accretion2065RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2065 | 20.4788 | 24.8585 | 30.38 | 34.578 | 38.7954
PrescottIce Accretion2070RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2070 | 20.0473 | 24.4103 | 29.91 | 34.0808 | 38.2662
PrescottIce Accretion2075RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2075 | 19.762 | 24.0949 | 29.55 | 33.6853 | 37.8252
PrescottIce Accretion2080RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2080 | 19.4767 | 23.7795 | 29.19 | 33.2898 | 37.3842
PrescottIce Accretion2085RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2085 | 18.7148 | 22.8831 | 28.14 | 32.1202 | 36.0801
PrescottIce Accretion2090RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2090 | 17.9528 | 21.9867 | 27.09 | 30.9507 | 34.776
PrescottIce Accretion2095RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2095 | 17.9528 | 21.9867 | 27.09 | 30.9507 | 34.776
PrescottIce Accretion2100RCP8.5 | Prescott | Ice Accretion | RCP8.5 | 2100 | 17.9528 | 21.9867 | 27.09 | 30.9507 | 34.776
PrescottWind2023RCP4.5 | Prescott | Wind | RCP4.5 | 2023 | 81.0025 | 87.3376 | 94.0323 | 100.7041 | 107.3771
PrescottWind2025RCP4.5 | Prescott | Wind | RCP4.5 | 2025 | 81.0065 | 87.3333 | 94.0153 | 100.6759 | 107.3399
PrescottWind2030RCP4.5 | Prescott | Wind | RCP4.5 | 2030 | 81.0105 | 87.329 | 93.9982 | 100.6477 | 107.3028
PrescottWind2035RCP4.5 | Prescott | Wind | RCP4.5 | 2035 | 81.0146 | 87.3246 | 93.9812 | 100.6195 | 107.2657
PrescottWind2040RCP4.5 | Prescott | Wind | RCP4.5 | 2040 | 81.0186 | 87.3203 | 93.9641 | 100.5913 | 107.2286
PrescottWind2045RCP4.5 | Prescott | Wind | RCP4.5 | 2045 | 81.0226 | 87.316 | 93.9471 | 100.5631 | 107.1915
PrescottWind2050RCP4.5 | Prescott | Wind | RCP4.5 | 2050 | 80.9447 | 87.1871 | 93.7514 | 100.314 | 106.8851
PrescottWind2055RCP4.5 | Prescott | Wind | RCP4.5 | 2055 | 80.8628 | 87.0626 | 93.5729 | 100.0931 | 106.6158
PrescottWind2060RCP4.5 | Prescott | Wind | RCP4.5 | 2060 | 80.7809 | 86.938 | 93.3943 | 99.8722 | 106.3465
PrescottWind2065RCP4.5 | Prescott | Wind | RCP4.5 | 2065 | 80.699 | 86.8135 | 93.2158 | 99.6513 | 106.0773
PrescottWind2070RCP4.5 | Prescott | Wind | RCP4.5 | 2070 | 80.6171 | 86.6889 | 93.0372 | 99.4304 | 105.808
PrescottWind2075RCP4.5 | Prescott | Wind | RCP4.5 | 2075 | 80.5836 | 86.6457 | 92.9845 | 99.369 | 105.739
PrescottWind2080RCP4.5 | Prescott | Wind | RCP4.5 | 2080 | 80.5501 | 86.6024 | 92.9318 | 99.3077 | 105.6701
PrescottWind2085RCP4.5 | Prescott | Wind | RCP4.5 | 2085 | 80.5167 | 86.5592 | 92.8791 | 99.2463 | 105.6012
PrescottWind2090RCP4.5 | Prescott | Wind | RCP4.5 | 2090 | 80.4832 | 86.5159 | 92.8264 | 99.1849 | 105.5323
PrescottWind2095RCP4.5 | Prescott | Wind | RCP4.5 | 2095 | 80.4498 | 86.4727 | 92.7737 | 99.1236 | 105.4634
PrescottWind2100RCP4.5 | Prescott | Wind | RCP4.5 | 2100 | 80.4163 | 86.4295 | 92.721 | 99.0622 | 105.3945
PrescottWind2023RCP6.0 | Prescott | Wind | RCP6.0 | 2023 | 81.0025 | 87.3376 | 94.0323 | 100.7041 | 107.3771
PrescottWind2025RCP6.0 | Prescott | Wind | RCP6.0 | 2025 | 81.0065 | 87.3333 | 94.0153 | 100.6759 | 107.3399
PrescottWind2030RCP6.0 | Prescott | Wind | RCP6.0 | 2030 | 81.0105 | 87.329 | 93.9982 | 100.6477 | 107.3028
PrescottWind2035RCP6.0 | Prescott | Wind | RCP6.0 | 2035 | 81.0146 | 87.3246 | 93.9812 | 100.6195 | 107.2657
PrescottWind2040RCP6.0 | Prescott | Wind | RCP6.0 | 2040 | 81.0186 | 87.3203 | 93.9641 | 100.5913 | 107.2286
PrescottWind2045RCP6.0 | Prescott | Wind | RCP6.0 | 2045 | 81.0226 | 87.316 | 93.9471 | 100.5631 | 107.1915
PrescottWind2050RCP6.0 | Prescott | Wind | RCP6.0 | 2050 | 80.9447 | 87.1871 | 93.7514 | 100.314 | 106.8851
PrescottWind2055RCP6.0 | Prescott | Wind | RCP6.0 | 2055 | 80.8628 | 87.0626 | 93.5729 | 100.0931 | 106.6158
PrescottWind2060RCP6.0 | Prescott | Wind | RCP6.0 | 2060 | 80.7809 | 86.938 | 93.3943 | 99.8722 | 106.3465
PrescottWind2065RCP6.0 | Prescott | Wind | RCP6.0 | 2065 | 80.699 | 86.8135 | 93.2158 | 99.6513 | 106.0773
PrescottWind2070RCP6.0 | Prescott | Wind | RCP6.0 | 2070 | 80.6171 | 86.6889 | 93.0372 | 99.4304 | 105.808
PrescottWind2075RCP6.0 | Prescott | Wind | RCP6.0 | 2075 | 80.5669 | 86.6241 | 92.9582 | 99.3383 | 105.7046
PrescottWind2080RCP6.0 | Prescott | Wind | RCP6.0 | 2080 | 80.5167 | 86.5592 | 92.8791 | 99.2463 | 105.6012
PrescottWind2085RCP6.0 | Prescott | Wind | RCP6.0 | 2085 | 80.4665 | 86.4943 | 92.8 | 99.1543 | 105.4979
PrescottWind2090RCP6.0 | Prescott | Wind | RCP6.0 | 2090 | 80.3467 | 86.3343 | 92.5877 | 98.8964 | 105.193
PrescottWind2095RCP6.0 | Prescott | Wind | RCP6.0 | 2095 | 80.2771 | 86.2392 | 92.4544 | 98.7305 | 104.9916
PrescottWind2100RCP6.0 | Prescott | Wind | RCP6.0 | 2100 | 80.2075 | 86.144 | 92.3211 | 98.5647 | 104.7902
PrescottWind2023RCP8.5 | Prescott | Wind | RCP8.5 | 2023 | 81.0025 | 87.3376 | 94.0323 | 100.7041 | 107.3771
PrescottWind2025RCP8.5 | Prescott | Wind | RCP8.5 | 2025 | 81.0105 | 87.329 | 93.9982 | 100.6477 | 107.3028
PrescottWind2030RCP8.5 | Prescott | Wind | RCP8.5 | 2030 | 81.0186 | 87.3203 | 93.9641 | 100.5913 | 107.2286
PrescottWind2035RCP8.5 | Prescott | Wind | RCP8.5 | 2035 | 81.0266 | 87.3117 | 93.93 | 100.535 | 107.1544
PrescottWind2040RCP8.5 | Prescott | Wind | RCP8.5 | 2040 | 80.8901 | 87.1041 | 93.6324 | 100.1668 | 106.7056
PrescottWind2045RCP8.5 | Prescott | Wind | RCP8.5 | 2045 | 80.7536 | 86.8965 | 93.3348 | 99.7986 | 106.2568
PrescottWind2050RCP8.5 | Prescott | Wind | RCP8.5 | 2050 | 80.5501 | 86.6024 | 92.9318 | 99.3077 | 105.6701
PrescottWind2055RCP8.5 | Prescott | Wind | RCP8.5 | 2055 | 80.4832 | 86.5159 | 92.8264 | 99.1849 | 105.5323
PrescottWind2060RCP8.5 | Prescott | Wind | RCP8.5 | 2060 | 80.3467 | 86.3343 | 92.5877 | 98.8964 | 105.193
PrescottWind2065RCP8.5 | Prescott | Wind | RCP8.5 | 2065 | 80.2771 | 86.2392 | 92.4544 | 98.7305 | 104.9916
PrescottWind2070RCP8.5 | Prescott | Wind | RCP8.5 | 2070 | 80.336 | 86.3141 | 92.5443 | 98.8333 | 105.1118
PrescottWind2075RCP8.5 | Prescott | Wind | RCP8.5 | 2075 | 80.4645 | 86.4842 | 92.7675 | 99.102 | 105.4334
PrescottWind2080RCP8.5 | Prescott | Wind | RCP8.5 | 2080 | 80.593 | 86.6543 | 92.9907 | 99.3707 | 105.755
PrescottWind2085RCP8.5 | Prescott | Wind | RCP8.5 | 2085 | 80.5769 | 86.6543 | 93.0093 | 99.4055 | 105.8027
PrescottWind2090RCP8.5 | Prescott | Wind | RCP8.5 | 2090 | 80.5608 | 86.6543 | 93.0279 | 99.4403 | 105.8504
PrescottWind2095RCP8.5 | Prescott | Wind | RCP8.5 | 2095 | 80.5608 | 86.6543 | 93.0279 | 99.4403 | 105.8504
PrescottWind2100RCP8.5 | Prescott | Wind | RCP8.5 | 2100 | 80.5608 | 86.6543 | 93.0279 | 99.4403 | 105.8504
PrincetonIce Accretion2023RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
PrincetonIce Accretion2025RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2025 | 20.3952 | 24.4642 | 29.605 | 33.5328 | 37.4661
PrincetonIce Accretion2030RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2030 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
PrincetonIce Accretion2035RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2035 | 20.3117 | 24.3895 | 29.535 | 33.4763 | 37.4031
PrincetonIce Accretion2040RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2040 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
PrincetonIce Accretion2045RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2045 | 20.2282 | 24.3148 | 29.465 | 33.4198 | 37.3401
PrincetonIce Accretion2050RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2050 | 20.0571 | 24.153 | 29.316 | 33.2762 | 37.2028
PrincetonIce Accretion2055RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2055 | 19.9276 | 24.0285 | 29.202 | 33.161 | 37.0969
PrincetonIce Accretion2060RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2060 | 19.7982 | 23.904 | 29.088 | 33.0457 | 36.9911
PrincetonIce Accretion2065RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2065 | 19.6688 | 23.7795 | 28.974 | 32.9305 | 36.8852
PrincetonIce Accretion2070RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2070 | 19.5394 | 23.655 | 28.86 | 32.8152 | 36.7794
PrincetonIce Accretion2075RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2075 | 19.4837 | 23.6135 | 28.84 | 32.8095 | 36.7857
PrincetonIce Accretion2080RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2080 | 19.428 | 23.572 | 28.82 | 32.8039 | 36.792
PrincetonIce Accretion2085RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2085 | 19.3724 | 23.5305 | 28.8 | 32.7982 | 36.7983
PrincetonIce Accretion2090RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2090 | 19.3167 | 23.489 | 28.78 | 32.7926 | 36.8046
PrincetonIce Accretion2095RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2095 | 19.261 | 23.4475 | 28.76 | 32.7869 | 36.8109
PrincetonIce Accretion2100RCP4.5 | Princeton | Ice Accretion | RCP4.5 | 2100 | 19.2054 | 23.406 | 28.74 | 32.7813 | 36.8172
PrincetonIce Accretion2023RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
PrincetonIce Accretion2025RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2025 | 20.3952 | 24.4642 | 29.605 | 33.5328 | 37.4661
PrincetonIce Accretion2030RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2030 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
PrincetonIce Accretion2035RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2035 | 20.3117 | 24.3895 | 29.535 | 33.4763 | 37.4031
PrincetonIce Accretion2040RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2040 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
PrincetonIce Accretion2045RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2045 | 20.2282 | 24.3148 | 29.465 | 33.4198 | 37.3401
PrincetonIce Accretion2050RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2050 | 20.0571 | 24.153 | 29.316 | 33.2762 | 37.2028
PrincetonIce Accretion2055RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2055 | 19.9276 | 24.0285 | 29.202 | 33.161 | 37.0969
PrincetonIce Accretion2060RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2060 | 19.7982 | 23.904 | 29.088 | 33.0457 | 36.9911
PrincetonIce Accretion2065RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2065 | 19.6688 | 23.7795 | 28.974 | 32.9305 | 36.8852
PrincetonIce Accretion2070RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2070 | 19.5394 | 23.655 | 28.86 | 32.8152 | 36.7794
PrincetonIce Accretion2075RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2075 | 19.4559 | 23.5927 | 28.83 | 32.8067 | 36.7888
PrincetonIce Accretion2080RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2080 | 19.3724 | 23.5305 | 28.8 | 32.7982 | 36.7983
PrincetonIce Accretion2085RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2085 | 19.2889 | 23.4682 | 28.77 | 32.7898 | 36.8077
PrincetonIce Accretion2090RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2090 | 18.7739 | 22.9412 | 28.21 | 32.2163 | 36.1998
PrincetonIce Accretion2095RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2095 | 18.3425 | 22.4764 | 27.68 | 31.6513 | 35.5824
PrincetonIce Accretion2100RCP6.0 | Princeton | Ice Accretion | RCP6.0 | 2100 | 17.9111 | 22.0116 | 27.15 | 31.0863 | 34.965
PrincetonIce Accretion2023RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
PrincetonIce Accretion2025RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2025 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
PrincetonIce Accretion2030RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2030 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
PrincetonIce Accretion2035RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2035 | 20.1865 | 24.2775 | 29.43 | 33.3915 | 37.3086
PrincetonIce Accretion2040RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2040 | 19.9708 | 24.07 | 29.24 | 33.1994 | 37.1322
PrincetonIce Accretion2045RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2045 | 19.7551 | 23.8625 | 29.05 | 33.0073 | 36.9558
PrincetonIce Accretion2050RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2050 | 19.428 | 23.572 | 28.82 | 32.8039 | 36.792
PrincetonIce Accretion2055RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2055 | 19.3167 | 23.489 | 28.78 | 32.7926 | 36.8046
PrincetonIce Accretion2060RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2060 | 18.7739 | 22.9412 | 28.21 | 32.2163 | 36.1998
PrincetonIce Accretion2065RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2065 | 18.3425 | 22.4764 | 27.68 | 31.6513 | 35.5824
PrincetonIce Accretion2070RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2070 | 17.5353 | 21.6049 | 26.71 | 30.6117 | 34.461
PrincetonIce Accretion2075RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2075 | 17.1596 | 21.1982 | 26.27 | 30.1371 | 33.957
PrincetonIce Accretion2080RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2080 | 16.7838 | 20.7915 | 25.83 | 29.6625 | 33.453
PrincetonIce Accretion2085RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2085 | 15.8549 | 19.7208 | 24.57 | 28.2387 | 31.9032
PrincetonIce Accretion2090RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2090 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
PrincetonIce Accretion2095RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2095 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
PrincetonIce Accretion2100RCP8.5 | Princeton | Ice Accretion | RCP8.5 | 2100 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
PrincetonWind2023RCP4.5 | Princeton | Wind | RCP4.5 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
PrincetonWind2025RCP4.5 | Princeton | Wind | RCP4.5 | 2025 | 87.206 | 94.102 | 101.4083 | 108.6746 | 115.9494
PrincetonWind2030RCP4.5 | Princeton | Wind | RCP4.5 | 2030 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
PrincetonWind2035RCP4.5 | Princeton | Wind | RCP4.5 | 2035 | 87.3672 | 94.316 | 101.685 | 109.0063 | 116.337
PrincetonWind2040RCP4.5 | Princeton | Wind | RCP4.5 | 2040 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
PrincetonWind2045RCP4.5 | Princeton | Wind | RCP4.5 | 2045 | 87.5283 | 94.5299 | 101.9617 | 109.338 | 116.7246
PrincetonWind2050RCP4.5 | Princeton | Wind | RCP4.5 | 2050 | 87.678 | 94.7205 | 102.206 | 109.6258 | 117.0575
PrincetonWind2055RCP4.5 | Princeton | Wind | RCP4.5 | 2055 | 87.7471 | 94.8042 | 102.312 | 109.7478 | 117.1966
PrincetonWind2060RCP4.5 | Princeton | Wind | RCP4.5 | 2060 | 87.8162 | 94.8879 | 102.418 | 109.8697 | 117.3356
PrincetonWind2065RCP4.5 | Princeton | Wind | RCP4.5 | 2065 | 87.8852 | 94.9716 | 102.524 | 109.9917 | 117.4747
PrincetonWind2070RCP4.5 | Princeton | Wind | RCP4.5 | 2070 | 87.9543 | 95.0553 | 102.63 | 110.1137 | 117.6138
PrincetonWind2075RCP4.5 | Princeton | Wind | RCP4.5 | 2075 | 88.0407 | 95.1746 | 102.7917 | 110.3117 | 117.8494
PrincetonWind2080RCP4.5 | Princeton | Wind | RCP4.5 | 2080 | 88.127 | 95.294 | 102.9533 | 110.5096 | 118.085
PrincetonWind2085RCP4.5 | Princeton | Wind | RCP4.5 | 2085 | 88.2134 | 95.4134 | 103.115 | 110.7075 | 118.3206
PrincetonWind2090RCP4.5 | Princeton | Wind | RCP4.5 | 2090 | 88.2997 | 95.5327 | 103.2767 | 110.9055 | 118.5562
PrincetonWind2095RCP4.5 | Princeton | Wind | RCP4.5 | 2095 | 88.3861 | 95.6521 | 103.4383 | 111.1034 | 118.7918
PrincetonWind2100RCP4.5 | Princeton | Wind | RCP4.5 | 2100 | 88.4724 | 95.7714 | 103.6 | 111.3014 | 119.0274
PrincetonWind2023RCP6.0 | Princeton | Wind | RCP6.0 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
PrincetonWind2025RCP6.0 | Princeton | Wind | RCP6.0 | 2025 | 87.206 | 94.102 | 101.4083 | 108.6746 | 115.9494
PrincetonWind2030RCP6.0 | Princeton | Wind | RCP6.0 | 2030 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
PrincetonWind2035RCP6.0 | Princeton | Wind | RCP6.0 | 2035 | 87.3672 | 94.316 | 101.685 | 109.0063 | 116.337
PrincetonWind2040RCP6.0 | Princeton | Wind | RCP6.0 | 2040 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
PrincetonWind2045RCP6.0 | Princeton | Wind | RCP6.0 | 2045 | 87.5283 | 94.5299 | 101.9617 | 109.338 | 116.7246
PrincetonWind2050RCP6.0 | Princeton | Wind | RCP6.0 | 2050 | 87.678 | 94.7205 | 102.206 | 109.6258 | 117.0575
PrincetonWind2055RCP6.0 | Princeton | Wind | RCP6.0 | 2055 | 87.7471 | 94.8042 | 102.312 | 109.7478 | 117.1966
PrincetonWind2060RCP6.0 | Princeton | Wind | RCP6.0 | 2060 | 87.8162 | 94.8879 | 102.418 | 109.8697 | 117.3356
PrincetonWind2065RCP6.0 | Princeton | Wind | RCP6.0 | 2065 | 87.8852 | 94.9716 | 102.524 | 109.9917 | 117.4747
PrincetonWind2070RCP6.0 | Princeton | Wind | RCP6.0 | 2070 | 87.9543 | 95.0553 | 102.63 | 110.1137 | 117.6138
PrincetonWind2075RCP6.0 | Princeton | Wind | RCP6.0 | 2075 | 88.0838 | 95.2343 | 102.8725 | 110.4106 | 117.9672
PrincetonWind2080RCP6.0 | Princeton | Wind | RCP6.0 | 2080 | 88.2134 | 95.4134 | 103.115 | 110.7075 | 118.3206
PrincetonWind2085RCP6.0 | Princeton | Wind | RCP6.0 | 2085 | 88.3429 | 95.5924 | 103.3575 | 111.0045 | 118.674
PrincetonWind2090RCP6.0 | Princeton | Wind | RCP6.0 | 2090 | 88.8264 | 96.2271 | 104.18 | 111.9862 | 119.8216
PrincetonWind2095RCP6.0 | Princeton | Wind | RCP6.0 | 2095 | 89.1805 | 96.6828 | 104.76 | 112.671 | 120.6158
PrincetonWind2100RCP6.0 | Princeton | Wind | RCP6.0 | 2100 | 89.5345 | 97.1385 | 105.34 | 113.3558 | 121.41
PrincetonWind2023RCP8.5 | Princeton | Wind | RCP8.5 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
PrincetonWind2025RCP8.5 | Princeton | Wind | RCP8.5 | 2025 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
PrincetonWind2030RCP8.5 | Princeton | Wind | RCP8.5 | 2030 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
PrincetonWind2035RCP8.5 | Princeton | Wind | RCP8.5 | 2035 | 87.6089 | 94.6368 | 102.1 | 109.5038 | 116.9184
PrincetonWind2040RCP8.5 | Princeton | Wind | RCP8.5 | 2040 | 87.7241 | 94.7763 | 102.2767 | 109.7071 | 117.1502
PrincetonWind2045RCP8.5 | Princeton | Wind | RCP8.5 | 2045 | 87.8392 | 94.9158 | 102.4533 | 109.9104 | 117.382
PrincetonWind2050RCP8.5 | Princeton | Wind | RCP8.5 | 2050 | 88.127 | 95.294 | 102.9533 | 110.5096 | 118.085
PrincetonWind2055RCP8.5 | Princeton | Wind | RCP8.5 | 2055 | 88.2997 | 95.5327 | 103.2767 | 110.9055 | 118.5562
PrincetonWind2060RCP8.5 | Princeton | Wind | RCP8.5 | 2060 | 88.8264 | 96.2271 | 104.18 | 111.9862 | 119.8216
PrincetonWind2065RCP8.5 | Princeton | Wind | RCP8.5 | 2065 | 89.1805 | 96.6828 | 104.76 | 112.671 | 120.6158
PrincetonWind2070RCP8.5 | Princeton | Wind | RCP8.5 | 2070 | 89.759 | 97.4392 | 105.7367 | 113.8337 | 121.9724
PrincetonWind2075RCP8.5 | Princeton | Wind | RCP8.5 | 2075 | 89.9835 | 97.7399 | 106.1333 | 114.3117 | 122.5348
PrincetonWind2080RCP8.5 | Princeton | Wind | RCP8.5 | 2080 | 90.208 | 98.0406 | 106.53 | 114.7896 | 123.0972
PrincetonWind2085RCP8.5 | Princeton | Wind | RCP8.5 | 2085 | 90.6484 | 98.6172 | 107.285 | 115.6937 | 124.1517
PrincetonWind2090RCP8.5 | Princeton | Wind | RCP8.5 | 2090 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
PrincetonWind2095RCP8.5 | Princeton | Wind | RCP8.5 | 2095 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
PrincetonWind2100RCP8.5 | Princeton | Wind | RCP8.5 | 2100 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
RaithIce Accretion2023RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2023 | 10.6464 | 12.7239 | 15.345 | 17.3568 | 19.3536
RaithIce Accretion2025RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2025 | 10.6952 | 12.782 | 15.4175 | 17.4387 | 19.4481
RaithIce Accretion2030RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2030 | 10.7439 | 12.8401 | 15.49 | 17.5206 | 19.5426
RaithIce Accretion2035RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2035 | 10.7926 | 12.8982 | 15.5625 | 17.6026 | 19.6371
RaithIce Accretion2040RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2040 | 10.8413 | 12.9563 | 15.635 | 17.6845 | 19.7316
RaithIce Accretion2045RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2045 | 10.89 | 13.0144 | 15.7075 | 17.7664 | 19.8261
RaithIce Accretion2050RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2050 | 10.922 | 13.0501 | 15.747 | 17.8077 | 19.8715
RaithIce Accretion2055RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2055 | 10.9053 | 13.0277 | 15.714 | 17.767 | 19.8223
RaithIce Accretion2060RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2060 | 10.8886 | 13.0053 | 15.681 | 17.7263 | 19.7732
RaithIce Accretion2065RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2065 | 10.8719 | 12.9829 | 15.648 | 17.6856 | 19.724
RaithIce Accretion2070RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2070 | 10.8552 | 12.9604 | 15.615 | 17.6449 | 19.6749
RaithIce Accretion2075RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2075 | 10.923 | 13.0455 | 15.7225 | 17.7692 | 19.8135
RaithIce Accretion2080RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2080 | 10.9909 | 13.1306 | 15.83 | 17.8935 | 19.9521
RaithIce Accretion2085RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2085 | 11.0587 | 13.2157 | 15.9375 | 18.0178 | 20.0907
RaithIce Accretion2090RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2090 | 11.1266 | 13.3007 | 16.045 | 18.1421 | 20.2293
RaithIce Accretion2095RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2095 | 11.1944 | 13.3858 | 16.1525 | 18.2664 | 20.3679
RaithIce Accretion2100RCP4.5 | Raith | Ice Accretion | RCP4.5 | 2100 | 11.2623 | 13.4709 | 16.26 | 18.3907 | 20.5065
RaithIce Accretion2023RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2023 | 10.6464 | 12.7239 | 15.345 | 17.3568 | 19.3536
RaithIce Accretion2025RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2025 | 10.6952 | 12.782 | 15.4175 | 17.4387 | 19.4481
RaithIce Accretion2030RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2030 | 10.7439 | 12.8401 | 15.49 | 17.5206 | 19.5426
RaithIce Accretion2035RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2035 | 10.7926 | 12.8982 | 15.5625 | 17.6026 | 19.6371
RaithIce Accretion2040RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2040 | 10.8413 | 12.9563 | 15.635 | 17.6845 | 19.7316
RaithIce Accretion2045RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2045 | 10.89 | 13.0144 | 15.7075 | 17.7664 | 19.8261
RaithIce Accretion2050RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2050 | 10.922 | 13.0501 | 15.747 | 17.8077 | 19.8715
RaithIce Accretion2055RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2055 | 10.9053 | 13.0277 | 15.714 | 17.767 | 19.8223
RaithIce Accretion2060RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2060 | 10.8886 | 13.0053 | 15.681 | 17.7263 | 19.7732
RaithIce Accretion2065RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2065 | 10.8719 | 12.9829 | 15.648 | 17.6856 | 19.724
RaithIce Accretion2070RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2070 | 10.8552 | 12.9604 | 15.615 | 17.6449 | 19.6749
RaithIce Accretion2075RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2075 | 10.957 | 13.0881 | 15.7762 | 17.8314 | 19.8828
RaithIce Accretion2080RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2080 | 11.0587 | 13.2157 | 15.9375 | 18.0178 | 20.0907
RaithIce Accretion2085RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2085 | 11.1605 | 13.3433 | 16.0988 | 18.2043 | 20.2986
RaithIce Accretion2090RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2090 | 11.2727 | 13.4833 | 16.275 | 18.4133 | 20.538
RaithIce Accretion2095RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2095 | 11.2831 | 13.4958 | 16.29 | 18.4359 | 20.5695
RaithIce Accretion2100RCP6.0 | Raith | Ice Accretion | RCP6.0 | 2100 | 11.2936 | 13.5082 | 16.305 | 18.4585 | 20.601
RaithIce Accretion2023RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2023 | 10.6464 | 12.7239 | 15.345 | 17.3568 | 19.3536
RaithIce Accretion2025RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2025 | 10.7439 | 12.8401 | 15.49 | 17.5206 | 19.5426
RaithIce Accretion2030RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2030 | 10.8413 | 12.9563 | 15.635 | 17.6845 | 19.7316
RaithIce Accretion2035RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2035 | 10.9387 | 13.0725 | 15.78 | 17.8483 | 19.9206
RaithIce Accretion2040RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2040 | 10.9109 | 13.0351 | 15.725 | 17.7805 | 19.8387
RaithIce Accretion2045RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2045 | 10.883 | 12.9978 | 15.67 | 17.7127 | 19.7568
RaithIce Accretion2050RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2050 | 10.9909 | 13.1306 | 15.83 | 17.8935 | 19.9521
RaithIce Accretion2055RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2055 | 11.1266 | 13.3007 | 16.045 | 18.1421 | 20.2293
RaithIce Accretion2060RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2060 | 11.2727 | 13.4833 | 16.275 | 18.4133 | 20.538
RaithIce Accretion2065RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2065 | 11.2831 | 13.4958 | 16.29 | 18.4359 | 20.5695
RaithIce Accretion2070RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2070 | 11.3423 | 13.5746 | 16.4 | 18.5659 | 20.7207
RaithIce Accretion2075RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2075 | 11.391 | 13.641 | 16.495 | 18.6732 | 20.8404
RaithIce Accretion2080RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2080 | 11.4397 | 13.7074 | 16.59 | 18.7806 | 20.9601
RaithIce Accretion2085RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2085 | 11.231 | 13.4647 | 16.2975 | 18.4586 | 20.6105
RaithIce Accretion2090RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2090 | 11.0222 | 13.2219 | 16.005 | 18.1365 | 20.2608
RaithIce Accretion2095RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2095 | 11.0222 | 13.2219 | 16.005 | 18.1365 | 20.2608
RaithIce Accretion2100RCP8.5 | Raith | Ice Accretion | RCP8.5 | 2100 | 11.0222 | 13.2219 | 16.005 | 18.1365 | 20.2608
RaithWind2023RCP4.5 | Raith | Wind | RCP4.5 | 2023 | 70.9401 | 76.4125 | 82.1804 | 87.9418 | 93.7044
RaithWind2025RCP4.5 | Raith | Wind | RCP4.5 | 2025 | 71.0097 | 76.4901 | 82.2665 | 88.0369 | 93.8072
RaithWind2030RCP4.5 | Raith | Wind | RCP4.5 | 2030 | 71.0793 | 76.5676 | 82.3526 | 88.1319 | 93.91
RaithWind2035RCP4.5 | Raith | Wind | RCP4.5 | 2035 | 71.149 | 76.6451 | 82.4387 | 88.227 | 94.0128
RaithWind2040RCP4.5 | Raith | Wind | RCP4.5 | 2040 | 71.2186 | 76.7226 | 82.5248 | 88.322 | 94.1157
RaithWind2045RCP4.5 | Raith | Wind | RCP4.5 | 2045 | 71.2882 | 76.8002 | 82.6109 | 88.4171 | 94.2185
RaithWind2050RCP4.5 | Raith | Wind | RCP4.5 | 2050 | 71.3947 | 76.9189 | 82.7429 | 88.5612 | 94.3755
RaithWind2055RCP4.5 | Raith | Wind | RCP4.5 | 2055 | 71.4315 | 76.9601 | 82.7888 | 88.6104 | 94.4298
RaithWind2060RCP4.5 | Raith | Wind | RCP4.5 | 2060 | 71.4683 | 77.0012 | 82.8348 | 88.6595 | 94.484
RaithWind2065RCP4.5 | Raith | Wind | RCP4.5 | 2065 | 71.5051 | 77.0424 | 82.8807 | 88.7086 | 94.5382
RaithWind2070RCP4.5 | Raith | Wind | RCP4.5 | 2070 | 71.5419 | 77.0836 | 82.9266 | 88.7578 | 94.5924
RaithWind2075RCP4.5 | Raith | Wind | RCP4.5 | 2075 | 71.6328 | 77.1929 | 83.0578 | 88.9084 | 94.7622
RaithWind2080RCP4.5 | Raith | Wind | RCP4.5 | 2080 | 71.7237 | 77.3022 | 83.189 | 89.059 | 94.9321
RaithWind2085RCP4.5 | Raith | Wind | RCP4.5 | 2085 | 71.8145 | 77.4115 | 83.3202 | 89.2096 | 95.1019
RaithWind2090RCP4.5 | Raith | Wind | RCP4.5 | 2090 | 71.9054 | 77.5208 | 83.4514 | 89.3603 | 95.2717
RaithWind2095RCP4.5 | Raith | Wind | RCP4.5 | 2095 | 71.9963 | 77.6301 | 83.5826 | 89.5109 | 95.4415
RaithWind2100RCP4.5 | Raith | Wind | RCP4.5 | 2100 | 72.0871 | 77.7394 | 83.7138 | 89.6615 | 95.6113
RaithWind2023RCP6.0 | Raith | Wind | RCP6.0 | 2023 | 70.9401 | 76.4125 | 82.1804 | 87.9418 | 93.7044
RaithWind2025RCP6.0 | Raith | Wind | RCP6.0 | 2025 | 71.0097 | 76.4901 | 82.2665 | 88.0369 | 93.8072
RaithWind2030RCP6.0 | Raith | Wind | RCP6.0 | 2030 | 71.0793 | 76.5676 | 82.3526 | 88.1319 | 93.91
RaithWind2035RCP6.0 | Raith | Wind | RCP6.0 | 2035 | 71.149 | 76.6451 | 82.4387 | 88.227 | 94.0128
RaithWind2040RCP6.0 | Raith | Wind | RCP6.0 | 2040 | 71.2186 | 76.7226 | 82.5248 | 88.322 | 94.1157
RaithWind2045RCP6.0 | Raith | Wind | RCP6.0 | 2045 | 71.2882 | 76.8002 | 82.6109 | 88.4171 | 94.2185
RaithWind2050RCP6.0 | Raith | Wind | RCP6.0 | 2050 | 71.3947 | 76.9189 | 82.7429 | 88.5612 | 94.3755
RaithWind2055RCP6.0 | Raith | Wind | RCP6.0 | 2055 | 71.4315 | 76.9601 | 82.7888 | 88.6104 | 94.4298
RaithWind2060RCP6.0 | Raith | Wind | RCP6.0 | 2060 | 71.4683 | 77.0012 | 82.8348 | 88.6595 | 94.484
RaithWind2065RCP6.0 | Raith | Wind | RCP6.0 | 2065 | 71.5051 | 77.0424 | 82.8807 | 88.7086 | 94.5382
RaithWind2070RCP6.0 | Raith | Wind | RCP6.0 | 2070 | 71.5419 | 77.0836 | 82.9266 | 88.7578 | 94.5924
RaithWind2075RCP6.0 | Raith | Wind | RCP6.0 | 2075 | 71.6782 | 77.2476 | 83.1234 | 88.9837 | 94.8471
RaithWind2080RCP6.0 | Raith | Wind | RCP6.0 | 2080 | 71.8145 | 77.4115 | 83.3202 | 89.2096 | 95.1019
RaithWind2085RCP6.0 | Raith | Wind | RCP6.0 | 2085 | 71.9508 | 77.5755 | 83.517 | 89.4356 | 95.3566
RaithWind2090RCP6.0 | Raith | Wind | RCP6.0 | 2090 | 72.1296 | 77.8132 | 83.8259 | 89.8048 | 95.7858
RaithWind2095RCP6.0 | Raith | Wind | RCP6.0 | 2095 | 72.1721 | 77.8869 | 83.9379 | 89.9481 | 95.9603
RaithWind2100RCP6.0 | Raith | Wind | RCP6.0 | 2100 | 72.2146 | 77.9606 | 84.05 | 90.0914 | 96.1348
RaithWind2023RCP8.5 | Raith | Wind | RCP8.5 | 2023 | 70.9401 | 76.4125 | 82.1804 | 87.9418 | 93.7044
RaithWind2025RCP8.5 | Raith | Wind | RCP8.5 | 2025 | 71.0793 | 76.5676 | 82.3526 | 88.1319 | 93.91
RaithWind2030RCP8.5 | Raith | Wind | RCP8.5 | 2030 | 71.2186 | 76.7226 | 82.5248 | 88.322 | 94.1157
RaithWind2035RCP8.5 | Raith | Wind | RCP8.5 | 2035 | 71.3578 | 76.8777 | 82.697 | 88.5121 | 94.3213
RaithWind2040RCP8.5 | Raith | Wind | RCP8.5 | 2040 | 71.4192 | 76.9463 | 82.7735 | 88.594 | 94.4117
RaithWind2045RCP8.5 | Raith | Wind | RCP8.5 | 2045 | 71.4806 | 77.015 | 82.8501 | 88.6759 | 94.502
RaithWind2050RCP8.5 | Raith | Wind | RCP8.5 | 2050 | 71.7237 | 77.3022 | 83.189 | 89.059 | 94.9321
RaithWind2055RCP8.5 | Raith | Wind | RCP8.5 | 2055 | 71.9054 | 77.5208 | 83.4514 | 89.3603 | 95.2717
RaithWind2060RCP8.5 | Raith | Wind | RCP8.5 | 2060 | 72.1296 | 77.8132 | 83.8259 | 89.8048 | 95.7858
RaithWind2065RCP8.5 | Raith | Wind | RCP8.5 | 2065 | 72.1721 | 77.8869 | 83.9379 | 89.9481 | 95.9603
RaithWind2070RCP8.5 | Raith | Wind | RCP8.5 | 2070 | 72.4058 | 78.1919 | 84.3288 | 90.4131 | 96.5025
RaithWind2075RCP8.5 | Raith | Wind | RCP8.5 | 2075 | 72.5969 | 78.4232 | 84.6076 | 90.7349 | 96.8702
RaithWind2080RCP8.5 | Raith | Wind | RCP8.5 | 2080 | 72.7881 | 78.6546 | 84.8864 | 91.0566 | 97.2379
RaithWind2085RCP8.5 | Raith | Wind | RCP8.5 | 2085 | 72.7669 | 78.6279 | 84.8577 | 91.0259 | 97.2052
RaithWind2090RCP8.5 | Raith | Wind | RCP8.5 | 2090 | 72.7456 | 78.6012 | 84.829 | 90.9952 | 97.1725
RaithWind2095RCP8.5 | Raith | Wind | RCP8.5 | 2095 | 72.7456 | 78.6012 | 84.829 | 90.9952 | 97.1725
RaithWind2100RCP8.5 | Raith | Wind | RCP8.5 | 2100 | 72.7456 | 78.6012 | 84.829 | 90.9952 | 97.1725
Rayside-Balfour (Chelmsford)Ice Accretion2023RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2023 | 16.0587 | 19.1913 | 23.166 | 26.2024 | 29.2446
Rayside-Balfour (Chelmsford)Ice Accretion2025RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2025 | 16.1353 | 19.2826 | 23.2797 | 26.3309 | 29.3878
Rayside-Balfour (Chelmsford)Ice Accretion2030RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2030 | 16.2118 | 19.3739 | 23.3933 | 26.4593 | 29.531
Rayside-Balfour (Chelmsford)Ice Accretion2035RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2035 | 16.2884 | 19.4652 | 23.507 | 26.5878 | 29.6743
Rayside-Balfour (Chelmsford)Ice Accretion2040RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2040 | 16.3649 | 19.5565 | 23.6207 | 26.7162 | 29.8175
Rayside-Balfour (Chelmsford)Ice Accretion2045RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2045 | 16.4415 | 19.6478 | 23.7343 | 26.8447 | 29.9607
Rayside-Balfour (Chelmsford)Ice Accretion2050RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2050 | 16.5945 | 19.845 | 23.9888 | 27.1421 | 30.298
Rayside-Balfour (Chelmsford)Ice Accretion2055RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2055 | 16.6711 | 19.9509 | 24.1296 | 27.3112 | 30.492
Rayside-Balfour (Chelmsford)Ice Accretion2060RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2060 | 16.7476 | 20.0568 | 24.2704 | 27.4802 | 30.686
Rayside-Balfour (Chelmsford)Ice Accretion2065RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2065 | 16.8242 | 20.1627 | 24.4112 | 27.6493 | 30.8801
Rayside-Balfour (Chelmsford)Ice Accretion2070RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2070 | 16.9007 | 20.2686 | 24.552 | 27.8183 | 31.0741
Rayside-Balfour (Chelmsford)Ice Accretion2075RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2075 | 16.814 | 20.1773 | 24.4493 | 27.7106 | 30.9586
Rayside-Balfour (Chelmsford)Ice Accretion2080RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2080 | 16.7272 | 20.086 | 24.3467 | 27.6029 | 30.8431
Rayside-Balfour (Chelmsford)Ice Accretion2085RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2085 | 16.6405 | 19.9947 | 24.244 | 27.4952 | 30.7276
Rayside-Balfour (Chelmsford)Ice Accretion2090RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2090 | 16.5537 | 19.9034 | 24.1413 | 27.3874 | 30.6121
Rayside-Balfour (Chelmsford)Ice Accretion2095RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2095 | 16.467 | 19.8121 | 24.0387 | 27.2797 | 30.4966
Rayside-Balfour (Chelmsford)Ice Accretion2100RCP4.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP4.5 | 2100 | 16.3802 | 19.7208 | 23.936 | 27.172 | 30.3811
Rayside-Balfour (Chelmsford)Ice Accretion2023RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2023 | 16.0587 | 19.1913 | 23.166 | 26.2024 | 29.2446
Rayside-Balfour (Chelmsford)Ice Accretion2025RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2025 | 16.1353 | 19.2826 | 23.2797 | 26.3309 | 29.3878
Rayside-Balfour (Chelmsford)Ice Accretion2030RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2030 | 16.2118 | 19.3739 | 23.3933 | 26.4593 | 29.531
Rayside-Balfour (Chelmsford)Ice Accretion2035RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2035 | 16.2884 | 19.4652 | 23.507 | 26.5878 | 29.6743
Rayside-Balfour (Chelmsford)Ice Accretion2040RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2040 | 16.3649 | 19.5565 | 23.6207 | 26.7162 | 29.8175
Rayside-Balfour (Chelmsford)Ice Accretion2045RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2045 | 16.4415 | 19.6478 | 23.7343 | 26.8447 | 29.9607
Rayside-Balfour (Chelmsford)Ice Accretion2050RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2050 | 16.5945 | 19.845 | 23.9888 | 27.1421 | 30.298
Rayside-Balfour (Chelmsford)Ice Accretion2055RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2055 | 16.6711 | 19.9509 | 24.1296 | 27.3112 | 30.492
Rayside-Balfour (Chelmsford)Ice Accretion2060RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2060 | 16.7476 | 20.0568 | 24.2704 | 27.4802 | 30.686
Rayside-Balfour (Chelmsford)Ice Accretion2065RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2065 | 16.8242 | 20.1627 | 24.4112 | 27.6493 | 30.8801
Rayside-Balfour (Chelmsford)Ice Accretion2070RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2070 | 16.9007 | 20.2686 | 24.552 | 27.8183 | 31.0741
Rayside-Balfour (Chelmsford)Ice Accretion2075RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2075 | 16.7706 | 20.1317 | 24.398 | 27.6567 | 30.9009
Rayside-Balfour (Chelmsford)Ice Accretion2080RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2080 | 16.6405 | 19.9947 | 24.244 | 27.4952 | 30.7276
Rayside-Balfour (Chelmsford)Ice Accretion2085RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2085 | 16.5103 | 19.8577 | 24.09 | 27.3336 | 30.5544
Rayside-Balfour (Chelmsford)Ice Accretion2090RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2090 | 16.3853 | 19.7512 | 24.0093 | 27.2631 | 30.5012
Rayside-Balfour (Chelmsford)Ice Accretion2095RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2095 | 16.3904 | 19.7817 | 24.0827 | 27.3543 | 30.6214
Rayside-Balfour (Chelmsford)Ice Accretion2100RCP6.0 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP6.0 | 2100 | 16.3955 | 19.8121 | 24.156 | 27.4454 | 30.7415
Rayside-Balfour (Chelmsford)Ice Accretion2023RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2023 | 16.0587 | 19.1913 | 23.166 | 26.2024 | 29.2446
Rayside-Balfour (Chelmsford)Ice Accretion2025RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2025 | 16.2118 | 19.3739 | 23.3933 | 26.4593 | 29.531
Rayside-Balfour (Chelmsford)Ice Accretion2030RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2030 | 16.3649 | 19.5565 | 23.6207 | 26.7162 | 29.8175
Rayside-Balfour (Chelmsford)Ice Accretion2035RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2035 | 16.518 | 19.7391 | 23.848 | 26.9731 | 30.1039
Rayside-Balfour (Chelmsford)Ice Accretion2040RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2040 | 16.6456 | 19.9156 | 24.0827 | 27.2548 | 30.4273
Rayside-Balfour (Chelmsford)Ice Accretion2045RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2045 | 16.7731 | 20.0921 | 24.3173 | 27.5366 | 30.7507
Rayside-Balfour (Chelmsford)Ice Accretion2050RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2050 | 16.7272 | 20.086 | 24.3467 | 27.6029 | 30.8431
Rayside-Balfour (Chelmsford)Ice Accretion2055RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2055 | 16.5537 | 19.9034 | 24.1413 | 27.3874 | 30.6121
Rayside-Balfour (Chelmsford)Ice Accretion2060RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2060 | 16.3853 | 19.7512 | 24.0093 | 27.2631 | 30.5012
Rayside-Balfour (Chelmsford)Ice Accretion2065RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2065 | 16.3904 | 19.7817 | 24.0827 | 27.3543 | 30.6214
Rayside-Balfour (Chelmsford)Ice Accretion2070RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2070 | 16.0996 | 19.4895 | 23.782 | 27.0394 | 30.298
Rayside-Balfour (Chelmsford)Ice Accretion2075RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2075 | 15.8036 | 19.1669 | 23.408 | 26.6333 | 29.8544
Rayside-Balfour (Chelmsford)Ice Accretion2080RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2080 | 15.5076 | 18.8443 | 23.034 | 26.2273 | 29.4109
Rayside-Balfour (Chelmsford)Ice Accretion2085RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2085 | 15.4464 | 18.8169 | 23.067 | 26.2895 | 29.5079
Rayside-Balfour (Chelmsford)Ice Accretion2090RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2090 | 15.3852 | 18.7895 | 23.1 | 26.3516 | 29.605
Rayside-Balfour (Chelmsford)Ice Accretion2095RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2095 | 15.3852 | 18.7895 | 23.1 | 26.3516 | 29.605
Rayside-Balfour (Chelmsford)Ice Accretion2100RCP8.5 | Rayside-Balfour (Chelmsford) | Ice Accretion | RCP8.5 | 2100 | 15.3852 | 18.7895 | 23.1 | 26.3516 | 29.605
Rayside-Balfour (Chelmsford)Wind2023RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2023 | 79.1819 | 85.2901 | 91.7189 | 98.149 | 104.5803
Rayside-Balfour (Chelmsford)Wind2025RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2025 | 79.288 | 85.4114 | 91.8569 | 98.3015 | 104.748
Rayside-Balfour (Chelmsford)Wind2030RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2030 | 79.3941 | 85.5327 | 91.9949 | 98.4541 | 104.9157
Rayside-Balfour (Chelmsford)Wind2035RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2035 | 79.5002 | 85.654 | 92.1329 | 98.6066 | 105.0834
Rayside-Balfour (Chelmsford)Wind2040RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2040 | 79.6063 | 85.7753 | 92.271 | 98.7591 | 105.2511
Rayside-Balfour (Chelmsford)Wind2045RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2045 | 79.7123 | 85.8966 | 92.409 | 98.9117 | 105.4189
Rayside-Balfour (Chelmsford)Wind2050RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2050 | 79.8608 | 86.0552 | 92.5779 | 99.0896 | 105.6073
Rayside-Balfour (Chelmsford)Wind2055RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2055 | 79.9033 | 86.0924 | 92.6089 | 99.1149 | 105.6281
Rayside-Balfour (Chelmsford)Wind2060RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2060 | 79.9457 | 86.1296 | 92.6398 | 99.1402 | 105.6488
Rayside-Balfour (Chelmsford)Wind2065RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2065 | 79.9881 | 86.1669 | 92.6708 | 99.1655 | 105.6696
Rayside-Balfour (Chelmsford)Wind2070RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2070 | 80.0306 | 86.2041 | 92.7017 | 99.1908 | 105.6903
Rayside-Balfour (Chelmsford)Wind2075RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2075 | 80.1144 | 86.3113 | 92.8382 | 99.3547 | 105.8788
Rayside-Balfour (Chelmsford)Wind2080RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2080 | 80.1982 | 86.4185 | 92.9747 | 99.5186 | 106.0672
Rayside-Balfour (Chelmsford)Wind2085RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2085 | 80.282 | 86.5257 | 93.1112 | 99.6825 | 106.2557
Rayside-Balfour (Chelmsford)Wind2090RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2090 | 80.3658 | 86.6329 | 93.2477 | 99.8464 | 106.4442
Rayside-Balfour (Chelmsford)Wind2095RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2095 | 80.4497 | 86.7401 | 93.3842 | 100.0103 | 106.6326
Rayside-Balfour (Chelmsford)Wind2100RCP4.5 | Rayside-Balfour (Chelmsford) | Wind | RCP4.5 | 2100 | 80.5335 | 86.8473 | 93.5207 | 100.1743 | 106.8211
Rayside-Balfour (Chelmsford)Wind2023RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2023 | 79.1819 | 85.2901 | 91.7189 | 98.149 | 104.5803
Rayside-Balfour (Chelmsford)Wind2025RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2025 | 79.288 | 85.4114 | 91.8569 | 98.3015 | 104.748
Rayside-Balfour (Chelmsford)Wind2030RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2030 | 79.3941 | 85.5327 | 91.9949 | 98.4541 | 104.9157
Rayside-Balfour (Chelmsford)Wind2035RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2035 | 79.5002 | 85.654 | 92.1329 | 98.6066 | 105.0834
Rayside-Balfour (Chelmsford)Wind2040RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2040 | 79.6063 | 85.7753 | 92.271 | 98.7591 | 105.2511
Rayside-Balfour (Chelmsford)Wind2045RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2045 | 79.7123 | 85.8966 | 92.409 | 98.9117 | 105.4189
Rayside-Balfour (Chelmsford)Wind2050RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2050 | 79.8608 | 86.0552 | 92.5779 | 99.0896 | 105.6073
Rayside-Balfour (Chelmsford)Wind2055RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2055 | 79.9033 | 86.0924 | 92.6089 | 99.1149 | 105.6281
Rayside-Balfour (Chelmsford)Wind2060RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2060 | 79.9457 | 86.1296 | 92.6398 | 99.1402 | 105.6488
Rayside-Balfour (Chelmsford)Wind2065RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2065 | 79.9881 | 86.1669 | 92.6708 | 99.1655 | 105.6696
Rayside-Balfour (Chelmsford)Wind2070RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2070 | 80.0306 | 86.2041 | 92.7017 | 99.1908 | 105.6903
Rayside-Balfour (Chelmsford)Wind2075RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2075 | 80.1563 | 86.3649 | 92.9064 | 99.4367 | 105.973
Rayside-Balfour (Chelmsford)Wind2080RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2080 | 80.282 | 86.5257 | 93.1112 | 99.6825 | 106.2557
Rayside-Balfour (Chelmsford)Wind2085RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2085 | 80.4077 | 86.6865 | 93.316 | 99.9284 | 106.5384
Rayside-Balfour (Chelmsford)Wind2090RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2090 | 80.8425 | 87.2422 | 94.0212 | 100.7617 | 107.5023
Rayside-Balfour (Chelmsford)Wind2095RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2095 | 81.1516 | 87.6372 | 94.5217 | 101.3492 | 108.1835
Rayside-Balfour (Chelmsford)Wind2100RCP6.0 | Rayside-Balfour (Chelmsford) | Wind | RCP6.0 | 2100 | 81.4607 | 88.0321 | 95.0222 | 101.9367 | 108.8648
Rayside-Balfour (Chelmsford)Wind2023RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2023 | 79.1819 | 85.2901 | 91.7189 | 98.149 | 104.5803
Rayside-Balfour (Chelmsford)Wind2025RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2025 | 79.3941 | 85.5327 | 91.9949 | 98.4541 | 104.9157
Rayside-Balfour (Chelmsford)Wind2030RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2030 | 79.6063 | 85.7753 | 92.271 | 98.7591 | 105.2511
Rayside-Balfour (Chelmsford)Wind2035RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2035 | 79.8184 | 86.0179 | 92.547 | 99.0642 | 105.5866
Rayside-Balfour (Chelmsford)Wind2040RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2040 | 79.8891 | 86.08 | 92.5986 | 99.1064 | 105.6212
Rayside-Balfour (Chelmsford)Wind2045RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2045 | 79.9599 | 86.1421 | 92.6501 | 99.1486 | 105.6557
Rayside-Balfour (Chelmsford)Wind2050RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2050 | 80.1982 | 86.4185 | 92.9747 | 99.5186 | 106.0672
Rayside-Balfour (Chelmsford)Wind2055RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2055 | 80.3658 | 86.6329 | 93.2477 | 99.8464 | 106.4442
Rayside-Balfour (Chelmsford)Wind2060RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2060 | 80.8425 | 87.2422 | 94.0212 | 100.7617 | 107.5023
Rayside-Balfour (Chelmsford)Wind2065RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2065 | 81.1516 | 87.6372 | 94.5217 | 101.3492 | 108.1835
Rayside-Balfour (Chelmsford)Wind2070RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2070 | 81.6807 | 88.3058 | 95.365 | 102.3359 | 109.3178
Rayside-Balfour (Chelmsford)Wind2075RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2075 | 81.9007 | 88.5794 | 95.7077 | 102.7351 | 109.7708
Rayside-Balfour (Chelmsford)Wind2080RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2080 | 82.1207 | 88.853 | 96.0505 | 103.1343 | 110.2237
Rayside-Balfour (Chelmsford)Wind2085RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2085 | 82.3486 | 89.1323 | 96.3872 | 103.5238 | 110.675
Rayside-Balfour (Chelmsford)Wind2090RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2090 | 82.5765 | 89.4116 | 96.7239 | 103.9133 | 111.1263
Rayside-Balfour (Chelmsford)Wind2095RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2095 | 82.5765 | 89.4116 | 96.7239 | 103.9133 | 111.1263
Rayside-Balfour (Chelmsford)Wind2100RCP8.5 | Rayside-Balfour (Chelmsford) | Wind | RCP8.5 | 2100 | 82.5765 | 89.4116 | 96.7239 | 103.9133 | 111.1263
Red LakeIce Accretion2023RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2023 | 9.3619 | 11.132 | 13.37 | 15.0923 | 16.8109
Red LakeIce Accretion2025RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2025 | 9.5519 | 11.3508 | 13.6267 | 15.3797 | 17.1284
Red LakeIce Accretion2030RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2030 | 9.7418 | 11.5696 | 13.8833 | 15.6671 | 17.446
Red LakeIce Accretion2035RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2035 | 9.9318 | 11.7885 | 14.14 | 15.9545 | 17.7635
Red LakeIce Accretion2040RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2040 | 10.1218 | 12.0073 | 14.3967 | 16.2419 | 18.081
Red LakeIce Accretion2045RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2045 | 10.3117 | 12.2262 | 14.6533 | 16.5293 | 18.3985
Red LakeIce Accretion2050RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2050 | 10.605 | 12.5635 | 15.05 | 16.9717 | 18.8854
Red LakeIce Accretion2055RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2055 | 10.7082 | 12.6821 | 15.19 | 17.1267 | 19.0547
Red LakeIce Accretion2060RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2060 | 10.8115 | 12.8006 | 15.33 | 17.2818 | 19.2241
Red LakeIce Accretion2065RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2065 | 10.9148 | 12.9191 | 15.47 | 17.4368 | 19.3934
Red LakeIce Accretion2070RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2070 | 11.018 | 13.0376 | 15.61 | 17.5918 | 19.5628
Red LakeIce Accretion2075RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2075 | 11.0911 | 13.1248 | 15.715 | 17.7079 | 19.6921
Red LakeIce Accretion2080RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2080 | 11.1642 | 13.2119 | 15.82 | 17.8239 | 19.8215
Red LakeIce Accretion2085RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2085 | 11.2372 | 13.2991 | 15.925 | 17.9399 | 19.9508
Red LakeIce Accretion2090RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2090 | 11.3103 | 13.3862 | 16.03 | 18.0559 | 20.0802
Red LakeIce Accretion2095RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2095 | 11.3833 | 13.4734 | 16.135 | 18.1719 | 20.2096
Red LakeIce Accretion2100RCP4.5 | Red Lake | Ice Accretion | RCP4.5 | 2100 | 11.4564 | 13.5605 | 16.24 | 18.2879 | 20.3389
Red LakeIce Accretion2023RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2023 | 9.3619 | 11.132 | 13.37 | 15.0923 | 16.8109
Red LakeIce Accretion2025RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2025 | 9.5519 | 11.3508 | 13.6267 | 15.3797 | 17.1284
Red LakeIce Accretion2030RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2030 | 9.7418 | 11.5696 | 13.8833 | 15.6671 | 17.446
Red LakeIce Accretion2035RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2035 | 9.9318 | 11.7885 | 14.14 | 15.9545 | 17.7635
Red LakeIce Accretion2040RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2040 | 10.1218 | 12.0073 | 14.3967 | 16.2419 | 18.081
Red LakeIce Accretion2045RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2045 | 10.3117 | 12.2262 | 14.6533 | 16.5293 | 18.3985
Red LakeIce Accretion2050RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2050 | 10.605 | 12.5635 | 15.05 | 16.9717 | 18.8854
Red LakeIce Accretion2055RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2055 | 10.7082 | 12.6821 | 15.19 | 17.1267 | 19.0547
Red LakeIce Accretion2060RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2060 | 10.8115 | 12.8006 | 15.33 | 17.2818 | 19.2241
Red LakeIce Accretion2065RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2065 | 10.9148 | 12.9191 | 15.47 | 17.4368 | 19.3934
Red LakeIce Accretion2070RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2070 | 11.018 | 13.0376 | 15.61 | 17.5918 | 19.5628
Red LakeIce Accretion2075RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2075 | 11.1276 | 13.1684 | 15.7675 | 17.7659 | 19.7568
Red LakeIce Accretion2080RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2080 | 11.2372 | 13.2991 | 15.925 | 17.9399 | 19.9508
Red LakeIce Accretion2085RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2085 | 11.3468 | 13.4298 | 16.0825 | 18.1139 | 20.1449
Red LakeIce Accretion2090RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2090 | 11.307 | 13.3862 | 16.0347 | 18.0559 | 20.0861
Red LakeIce Accretion2095RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2095 | 11.1577 | 13.2119 | 15.8293 | 17.8239 | 19.8332
Red LakeIce Accretion2100RCP6.0 | Red Lake | Ice Accretion | RCP6.0 | 2100 | 11.0083 | 13.0376 | 15.624 | 17.5918 | 19.5804
Red LakeIce Accretion2023RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2023 | 9.3619 | 11.132 | 13.37 | 15.0923 | 16.8109
Red LakeIce Accretion2025RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2025 | 9.7418 | 11.5696 | 13.8833 | 15.6671 | 17.446
Red LakeIce Accretion2030RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2030 | 10.1218 | 12.0073 | 14.3967 | 16.2419 | 18.081
Red LakeIce Accretion2035RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2035 | 10.5017 | 12.445 | 14.91 | 16.8167 | 18.716
Red LakeIce Accretion2040RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2040 | 10.6738 | 12.6426 | 15.1433 | 17.0751 | 18.9983
Red LakeIce Accretion2045RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2045 | 10.8459 | 12.8401 | 15.3767 | 17.3334 | 19.2805
Red LakeIce Accretion2050RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2050 | 11.1642 | 13.2119 | 15.82 | 17.8239 | 19.8215
Red LakeIce Accretion2055RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2055 | 11.3103 | 13.3862 | 16.03 | 18.0559 | 20.0802
Red LakeIce Accretion2060RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2060 | 11.307 | 13.3862 | 16.0347 | 18.0559 | 20.0861
Red LakeIce Accretion2065RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2065 | 11.1577 | 13.2119 | 15.8293 | 17.8239 | 19.8332
Red LakeIce Accretion2070RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2070 | 10.9239 | 12.9331 | 15.4933 | 17.4495 | 19.4158
Red LakeIce Accretion2075RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2075 | 10.8394 | 12.8285 | 15.3627 | 17.3071 | 19.2511
Red LakeIce Accretion2080RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2080 | 10.755 | 12.7239 | 15.232 | 17.1647 | 19.0865
Red LakeIce Accretion2085RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2085 | 10.6284 | 12.567 | 15.043 | 16.9432 | 18.8395
Red LakeIce Accretion2090RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2090 | 10.5017 | 12.4102 | 14.854 | 16.7217 | 18.5926
Red LakeIce Accretion2095RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2095 | 10.5017 | 12.4102 | 14.854 | 16.7217 | 18.5926
Red LakeIce Accretion2100RCP8.5 | Red Lake | Ice Accretion | RCP8.5 | 2100 | 10.5017 | 12.4102 | 14.854 | 16.7217 | 18.5926
Red LakeWind2023RCP4.5 | Red Lake | Wind | RCP4.5 | 2023 | 69.1408 | 74.4 | 79.928 | 85.463 | 90.9994
Red LakeWind2025RCP4.5 | Red Lake | Wind | RCP4.5 | 2025 | 69.2432 | 74.5153 | 80.0573 | 85.6071 | 91.1574
Red LakeWind2030RCP4.5 | Red Lake | Wind | RCP4.5 | 2030 | 69.3457 | 74.6306 | 80.1867 | 85.7512 | 91.3155
Red LakeWind2035RCP4.5 | Red Lake | Wind | RCP4.5 | 2035 | 69.4482 | 74.746 | 80.316 | 85.8953 | 91.4736
Red LakeWind2040RCP4.5 | Red Lake | Wind | RCP4.5 | 2040 | 69.5506 | 74.8613 | 80.4453 | 86.0394 | 91.6317
Red LakeWind2045RCP4.5 | Red Lake | Wind | RCP4.5 | 2045 | 69.6531 | 74.9766 | 80.5747 | 86.1835 | 91.7898
Red LakeWind2050RCP4.5 | Red Lake | Wind | RCP4.5 | 2050 | 69.8454 | 75.1946 | 80.8192 | 86.4543 | 92.0865
Red LakeWind2055RCP4.5 | Red Lake | Wind | RCP4.5 | 2055 | 69.9352 | 75.2973 | 80.9344 | 86.581 | 92.2251
Red LakeWind2060RCP4.5 | Red Lake | Wind | RCP4.5 | 2060 | 70.025 | 75.3999 | 81.0496 | 86.7077 | 92.3637
Red LakeWind2065RCP4.5 | Red Lake | Wind | RCP4.5 | 2065 | 70.1148 | 75.5026 | 81.1648 | 86.8344 | 92.5023
Red LakeWind2070RCP4.5 | Red Lake | Wind | RCP4.5 | 2070 | 70.2046 | 75.6053 | 81.28 | 86.961 | 92.641
Red LakeWind2075RCP4.5 | Red Lake | Wind | RCP4.5 | 2075 | 70.2598 | 75.6561 | 81.324 | 87.001 | 92.6759
Red LakeWind2080RCP4.5 | Red Lake | Wind | RCP4.5 | 2080 | 70.3151 | 75.707 | 81.368 | 87.0409 | 92.7109
Red LakeWind2085RCP4.5 | Red Lake | Wind | RCP4.5 | 2085 | 70.3704 | 75.7578 | 81.412 | 87.0809 | 92.7458
Red LakeWind2090RCP4.5 | Red Lake | Wind | RCP4.5 | 2090 | 70.4256 | 75.8086 | 81.456 | 87.1208 | 92.7808
Red LakeWind2095RCP4.5 | Red Lake | Wind | RCP4.5 | 2095 | 70.4809 | 75.8595 | 81.5 | 87.1608 | 92.8158
Red LakeWind2100RCP4.5 | Red Lake | Wind | RCP4.5 | 2100 | 70.5362 | 75.9103 | 81.544 | 87.2007 | 92.8507
Red LakeWind2023RCP6.0 | Red Lake | Wind | RCP6.0 | 2023 | 69.1408 | 74.4 | 79.928 | 85.463 | 90.9994
Red LakeWind2025RCP6.0 | Red Lake | Wind | RCP6.0 | 2025 | 69.2432 | 74.5153 | 80.0573 | 85.6071 | 91.1574
Red LakeWind2030RCP6.0 | Red Lake | Wind | RCP6.0 | 2030 | 69.3457 | 74.6306 | 80.1867 | 85.7512 | 91.3155
Red LakeWind2035RCP6.0 | Red Lake | Wind | RCP6.0 | 2035 | 69.4482 | 74.746 | 80.316 | 85.8953 | 91.4736
Red LakeWind2040RCP6.0 | Red Lake | Wind | RCP6.0 | 2040 | 69.5506 | 74.8613 | 80.4453 | 86.0394 | 91.6317
Red LakeWind2045RCP6.0 | Red Lake | Wind | RCP6.0 | 2045 | 69.6531 | 74.9766 | 80.5747 | 86.1835 | 91.7898
Red LakeWind2050RCP6.0 | Red Lake | Wind | RCP6.0 | 2050 | 69.8454 | 75.1946 | 80.8192 | 86.4543 | 92.0865
Red LakeWind2055RCP6.0 | Red Lake | Wind | RCP6.0 | 2055 | 69.9352 | 75.2973 | 80.9344 | 86.581 | 92.2251
Red LakeWind2060RCP6.0 | Red Lake | Wind | RCP6.0 | 2060 | 70.025 | 75.3999 | 81.0496 | 86.7077 | 92.3637
Red LakeWind2065RCP6.0 | Red Lake | Wind | RCP6.0 | 2065 | 70.1148 | 75.5026 | 81.1648 | 86.8344 | 92.5023
Red LakeWind2070RCP6.0 | Red Lake | Wind | RCP6.0 | 2070 | 70.2046 | 75.6053 | 81.28 | 86.961 | 92.641
Red LakeWind2075RCP6.0 | Red Lake | Wind | RCP6.0 | 2075 | 70.2875 | 75.6815 | 81.346 | 87.021 | 92.6934
Red LakeWind2080RCP6.0 | Red Lake | Wind | RCP6.0 | 2080 | 70.3704 | 75.7578 | 81.412 | 87.0809 | 92.7458
Red LakeWind2085RCP6.0 | Red Lake | Wind | RCP6.0 | 2085 | 70.4533 | 75.8341 | 81.478 | 87.1408 | 92.7983
Red LakeWind2090RCP6.0 | Red Lake | Wind | RCP6.0 | 2090 | 70.6858 | 76.1038 | 81.7947 | 87.4946 | 93.1942
Red LakeWind2095RCP6.0 | Red Lake | Wind | RCP6.0 | 2095 | 70.8355 | 76.2972 | 82.0453 | 87.7885 | 93.5378
Red LakeWind2100RCP6.0 | Red Lake | Wind | RCP6.0 | 2100 | 70.9852 | 76.4906 | 82.296 | 88.0824 | 93.8813
Red LakeWind2023RCP8.5 | Red Lake | Wind | RCP8.5 | 2023 | 69.1408 | 74.4 | 79.928 | 85.463 | 90.9994
Red LakeWind2025RCP8.5 | Red Lake | Wind | RCP8.5 | 2025 | 69.3457 | 74.6306 | 80.1867 | 85.7512 | 91.3155
Red LakeWind2030RCP8.5 | Red Lake | Wind | RCP8.5 | 2030 | 69.5506 | 74.8613 | 80.4453 | 86.0394 | 91.6317
Red LakeWind2035RCP8.5 | Red Lake | Wind | RCP8.5 | 2035 | 69.7556 | 75.0919 | 80.704 | 86.3276 | 91.9478
Red LakeWind2040RCP8.5 | Red Lake | Wind | RCP8.5 | 2040 | 69.9052 | 75.263 | 80.896 | 86.5387 | 92.1789
Red LakeWind2045RCP8.5 | Red Lake | Wind | RCP8.5 | 2045 | 70.0549 | 75.4342 | 81.088 | 86.7499 | 92.4099
Red LakeWind2050RCP8.5 | Red Lake | Wind | RCP8.5 | 2050 | 70.3151 | 75.707 | 81.368 | 87.0409 | 92.7109
Red LakeWind2055RCP8.5 | Red Lake | Wind | RCP8.5 | 2055 | 70.4256 | 75.8086 | 81.456 | 87.1208 | 92.7808
Red LakeWind2060RCP8.5 | Red Lake | Wind | RCP8.5 | 2060 | 70.6858 | 76.1038 | 81.7947 | 87.4946 | 93.1942
Red LakeWind2065RCP8.5 | Red Lake | Wind | RCP8.5 | 2065 | 70.8355 | 76.2972 | 82.0453 | 87.7885 | 93.5378
Red LakeWind2070RCP8.5 | Red Lake | Wind | RCP8.5 | 2070 | 71.0819 | 76.5898 | 82.3973 | 88.188 | 93.9877
Red LakeWind2075RCP8.5 | Red Lake | Wind | RCP8.5 | 2075 | 71.1786 | 76.689 | 82.4987 | 88.2935 | 94.0941
Red LakeWind2080RCP8.5 | Red Lake | Wind | RCP8.5 | 2080 | 71.2753 | 76.7882 | 82.6 | 88.3991 | 94.2005
Red LakeWind2085RCP8.5 | Red Lake | Wind | RCP8.5 | 2085 | 71.3996 | 76.9519 | 82.812 | 88.6559 | 94.5014
Red LakeWind2090RCP8.5 | Red Lake | Wind | RCP8.5 | 2090 | 71.524 | 77.1156 | 83.024 | 88.9127 | 94.8024
Red LakeWind2095RCP8.5 | Red Lake | Wind | RCP8.5 | 2095 | 71.524 | 77.1156 | 83.024 | 88.9127 | 94.8024
Red LakeWind2100RCP8.5 | Red Lake | Wind | RCP8.5 | 2100 | 71.524 | 77.1156 | 83.024 | 88.9127 | 94.8024
RenfrewIce Accretion2023RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2023 | 15.2933 | 18.2052 | 21.868 | 24.686 | 27.4982
RenfrewIce Accretion2025RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2025 | 15.375 | 18.3056 | 22 | 24.8393 | 27.6692
RenfrewIce Accretion2030RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2030 | 15.4566 | 18.4061 | 22.132 | 24.9926 | 27.8401
RenfrewIce Accretion2035RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2035 | 15.5382 | 18.5065 | 22.264 | 25.1459 | 28.0111
RenfrewIce Accretion2040RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2040 | 15.6199 | 18.6069 | 22.396 | 25.2992 | 28.182
RenfrewIce Accretion2045RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2045 | 15.7015 | 18.7074 | 22.528 | 25.4525 | 28.3529
RenfrewIce Accretion2050RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2050 | 15.7862 | 18.8261 | 22.6952 | 25.6555 | 28.5904
RenfrewIce Accretion2055RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2055 | 15.7893 | 18.8443 | 22.7304 | 25.7052 | 28.6569
RenfrewIce Accretion2060RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2060 | 15.7924 | 18.8626 | 22.7656 | 25.755 | 28.7235
RenfrewIce Accretion2065RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2065 | 15.7954 | 18.8808 | 22.8008 | 25.8047 | 28.79
RenfrewIce Accretion2070RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2070 | 15.7985 | 18.8991 | 22.836 | 25.8544 | 28.8565
RenfrewIce Accretion2075RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2075 | 15.8189 | 18.9387 | 22.8983 | 25.9331 | 28.9489
RenfrewIce Accretion2080RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2080 | 15.8393 | 18.9782 | 22.9607 | 26.0118 | 29.0413
RenfrewIce Accretion2085RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2085 | 15.8597 | 19.0178 | 23.023 | 26.0906 | 29.1337
RenfrewIce Accretion2090RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2090 | 15.8801 | 19.0574 | 23.0853 | 26.1693 | 29.2261
RenfrewIce Accretion2095RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2095 | 15.9005 | 19.0969 | 23.1477 | 26.248 | 29.3185
RenfrewIce Accretion2100RCP4.5 | Renfrew | Ice Accretion | RCP4.5 | 2100 | 15.921 | 19.1365 | 23.21 | 26.3267 | 29.4109
RenfrewIce Accretion2023RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2023 | 15.2933 | 18.2052 | 21.868 | 24.686 | 27.4982
RenfrewIce Accretion2025RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2025 | 15.375 | 18.3056 | 22 | 24.8393 | 27.6692
RenfrewIce Accretion2030RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2030 | 15.4566 | 18.4061 | 22.132 | 24.9926 | 27.8401
RenfrewIce Accretion2035RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2035 | 15.5382 | 18.5065 | 22.264 | 25.1459 | 28.0111
RenfrewIce Accretion2040RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2040 | 15.6199 | 18.6069 | 22.396 | 25.2992 | 28.182
RenfrewIce Accretion2045RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2045 | 15.7015 | 18.7074 | 22.528 | 25.4525 | 28.3529
RenfrewIce Accretion2050RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2050 | 15.7862 | 18.8261 | 22.6952 | 25.6555 | 28.5904
RenfrewIce Accretion2055RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2055 | 15.7893 | 18.8443 | 22.7304 | 25.7052 | 28.6569
RenfrewIce Accretion2060RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2060 | 15.7924 | 18.8626 | 22.7656 | 25.755 | 28.7235
RenfrewIce Accretion2065RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2065 | 15.7954 | 18.8808 | 22.8008 | 25.8047 | 28.79
RenfrewIce Accretion2070RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2070 | 15.7985 | 18.8991 | 22.836 | 25.8544 | 28.8565
RenfrewIce Accretion2075RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2075 | 15.8291 | 18.9584 | 22.9295 | 25.9725 | 28.9951
RenfrewIce Accretion2080RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2080 | 15.8597 | 19.0178 | 23.023 | 26.0906 | 29.1337
RenfrewIce Accretion2085RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2085 | 15.8903 | 19.0771 | 23.1165 | 26.2087 | 29.2723
RenfrewIce Accretion2090RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2090 | 15.8291 | 19.0452 | 23.1147 | 26.2273 | 29.3093
RenfrewIce Accretion2095RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2095 | 15.7373 | 18.9539 | 23.0193 | 26.1279 | 29.2076
RenfrewIce Accretion2100RCP6.0 | Renfrew | Ice Accretion | RCP6.0 | 2100 | 15.6454 | 18.8626 | 22.924 | 26.0284 | 29.106
RenfrewIce Accretion2023RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2023 | 15.2933 | 18.2052 | 21.868 | 24.686 | 27.4982
RenfrewIce Accretion2025RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2025 | 15.4566 | 18.4061 | 22.132 | 24.9926 | 27.8401
RenfrewIce Accretion2030RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2030 | 15.6199 | 18.6069 | 22.396 | 25.2992 | 28.182
RenfrewIce Accretion2035RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2035 | 15.7832 | 18.8078 | 22.66 | 25.6058 | 28.5239
RenfrewIce Accretion2040RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2040 | 15.7883 | 18.8382 | 22.7187 | 25.6887 | 28.6348
RenfrewIce Accretion2045RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2045 | 15.7934 | 18.8687 | 22.7773 | 25.7715 | 28.7456
RenfrewIce Accretion2050RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2050 | 15.8393 | 18.9782 | 22.9607 | 26.0118 | 29.0413
RenfrewIce Accretion2055RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2055 | 15.8801 | 19.0574 | 23.0853 | 26.1693 | 29.2261
RenfrewIce Accretion2060RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2060 | 15.8291 | 19.0452 | 23.1147 | 26.2273 | 29.3093
RenfrewIce Accretion2065RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2065 | 15.7373 | 18.9539 | 23.0193 | 26.1279 | 29.2076
RenfrewIce Accretion2070RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2070 | 15.6352 | 18.8869 | 22.9973 | 26.1361 | 29.2538
RenfrewIce Accretion2075RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2075 | 15.625 | 18.9113 | 23.0707 | 26.2439 | 29.4017
RenfrewIce Accretion2080RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2080 | 15.6148 | 18.9356 | 23.144 | 26.3516 | 29.5495
RenfrewIce Accretion2085RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2085 | 15.0943 | 18.3513 | 22.484 | 25.6182 | 28.7595
RenfrewIce Accretion2090RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2090 | 14.5738 | 17.767 | 21.824 | 24.8849 | 27.9695
RenfrewIce Accretion2095RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2095 | 14.5738 | 17.767 | 21.824 | 24.8849 | 27.9695
RenfrewIce Accretion2100RCP8.5 | Renfrew | Ice Accretion | RCP8.5 | 2100 | 14.5738 | 17.767 | 21.824 | 24.8849 | 27.9695
RenfrewWind2023RCP4.5 | Renfrew | Wind | RCP4.5 | 2023 | 75.9257 | 81.7418 | 87.8504 | 93.9717 | 100.0893
RenfrewWind2025RCP4.5 | Renfrew | Wind | RCP4.5 | 2025 | 75.9244 | 81.7404 | 87.8504 | 93.9717 | 100.0909
RenfrewWind2030RCP4.5 | Renfrew | Wind | RCP4.5 | 2030 | 75.9231 | 81.7391 | 87.8504 | 93.9717 | 100.0926
RenfrewWind2035RCP4.5 | Renfrew | Wind | RCP4.5 | 2035 | 75.9219 | 81.7377 | 87.8504 | 93.9717 | 100.0943
RenfrewWind2040RCP4.5 | Renfrew | Wind | RCP4.5 | 2040 | 75.9206 | 81.7363 | 87.8504 | 93.9717 | 100.096
RenfrewWind2045RCP4.5 | Renfrew | Wind | RCP4.5 | 2045 | 75.9193 | 81.735 | 87.8504 | 93.9717 | 100.0976
RenfrewWind2050RCP4.5 | Renfrew | Wind | RCP4.5 | 2050 | 75.8998 | 81.7123 | 87.824 | 93.9434 | 100.0652
RenfrewWind2055RCP4.5 | Renfrew | Wind | RCP4.5 | 2055 | 75.8816 | 81.6911 | 87.7976 | 93.9152 | 100.0311
RenfrewWind2060RCP4.5 | Renfrew | Wind | RCP4.5 | 2060 | 75.8634 | 81.6698 | 87.7712 | 93.8869 | 99.997
RenfrewWind2065RCP4.5 | Renfrew | Wind | RCP4.5 | 2065 | 75.8451 | 81.6485 | 87.7448 | 93.8587 | 99.9629
RenfrewWind2070RCP4.5 | Renfrew | Wind | RCP4.5 | 2070 | 75.8269 | 81.6272 | 87.7184 | 93.8304 | 99.9288
RenfrewWind2075RCP4.5 | Renfrew | Wind | RCP4.5 | 2075 | 75.8687 | 81.6831 | 87.7917 | 93.9168 | 100.0307
RenfrewWind2080RCP4.5 | Renfrew | Wind | RCP4.5 | 2080 | 75.9105 | 81.7391 | 87.8651 | 94.0031 | 100.1327
RenfrewWind2085RCP4.5 | Renfrew | Wind | RCP4.5 | 2085 | 75.9523 | 81.795 | 87.9384 | 94.0894 | 100.2347
RenfrewWind2090RCP4.5 | Renfrew | Wind | RCP4.5 | 2090 | 75.9941 | 81.8509 | 88.0117 | 94.1757 | 100.3367
RenfrewWind2095RCP4.5 | Renfrew | Wind | RCP4.5 | 2095 | 76.0358 | 81.9068 | 88.0851 | 94.262 | 100.4387
RenfrewWind2100RCP4.5 | Renfrew | Wind | RCP4.5 | 2100 | 76.0776 | 81.9628 | 88.1584 | 94.3483 | 100.5407
RenfrewWind2023RCP6.0 | Renfrew | Wind | RCP6.0 | 2023 | 75.9257 | 81.7418 | 87.8504 | 93.9717 | 100.0893
RenfrewWind2025RCP6.0 | Renfrew | Wind | RCP6.0 | 2025 | 75.9244 | 81.7404 | 87.8504 | 93.9717 | 100.0909
RenfrewWind2030RCP6.0 | Renfrew | Wind | RCP6.0 | 2030 | 75.9231 | 81.7391 | 87.8504 | 93.9717 | 100.0926
RenfrewWind2035RCP6.0 | Renfrew | Wind | RCP6.0 | 2035 | 75.9219 | 81.7377 | 87.8504 | 93.9717 | 100.0943
RenfrewWind2040RCP6.0 | Renfrew | Wind | RCP6.0 | 2040 | 75.9206 | 81.7363 | 87.8504 | 93.9717 | 100.096
RenfrewWind2045RCP6.0 | Renfrew | Wind | RCP6.0 | 2045 | 75.9193 | 81.735 | 87.8504 | 93.9717 | 100.0976
RenfrewWind2050RCP6.0 | Renfrew | Wind | RCP6.0 | 2050 | 75.8998 | 81.7123 | 87.824 | 93.9434 | 100.0652
RenfrewWind2055RCP6.0 | Renfrew | Wind | RCP6.0 | 2055 | 75.8816 | 81.6911 | 87.7976 | 93.9152 | 100.0311
RenfrewWind2060RCP6.0 | Renfrew | Wind | RCP6.0 | 2060 | 75.8634 | 81.6698 | 87.7712 | 93.8869 | 99.997
RenfrewWind2065RCP6.0 | Renfrew | Wind | RCP6.0 | 2065 | 75.8451 | 81.6485 | 87.7448 | 93.8587 | 99.9629
RenfrewWind2070RCP6.0 | Renfrew | Wind | RCP6.0 | 2070 | 75.8269 | 81.6272 | 87.7184 | 93.8304 | 99.9288
RenfrewWind2075RCP6.0 | Renfrew | Wind | RCP6.0 | 2075 | 75.8896 | 81.7111 | 87.8284 | 93.9599 | 100.0817
RenfrewWind2080RCP6.0 | Renfrew | Wind | RCP6.0 | 2080 | 75.9523 | 81.795 | 87.9384 | 94.0894 | 100.2347
RenfrewWind2085RCP6.0 | Renfrew | Wind | RCP6.0 | 2085 | 76.0149 | 81.8789 | 88.0484 | 94.2189 | 100.3877
RenfrewWind2090RCP6.0 | Renfrew | Wind | RCP6.0 | 2090 | 75.9738 | 81.8209 | 87.9707 | 94.1223 | 100.2765
RenfrewWind2095RCP6.0 | Renfrew | Wind | RCP6.0 | 2095 | 75.8699 | 81.679 | 87.7829 | 93.8964 | 100.0124
RenfrewWind2100RCP6.0 | Renfrew | Wind | RCP6.0 | 2100 | 75.7661 | 81.5372 | 87.5952 | 93.6704 | 99.7482
RenfrewWind2023RCP8.5 | Renfrew | Wind | RCP8.5 | 2023 | 75.9257 | 81.7418 | 87.8504 | 93.9717 | 100.0893
RenfrewWind2025RCP8.5 | Renfrew | Wind | RCP8.5 | 2025 | 75.9231 | 81.7391 | 87.8504 | 93.9717 | 100.0926
RenfrewWind2030RCP8.5 | Renfrew | Wind | RCP8.5 | 2030 | 75.9206 | 81.7363 | 87.8504 | 93.9717 | 100.096
RenfrewWind2035RCP8.5 | Renfrew | Wind | RCP8.5 | 2035 | 75.9181 | 81.7336 | 87.8504 | 93.9717 | 100.0993
RenfrewWind2040RCP8.5 | Renfrew | Wind | RCP8.5 | 2040 | 75.8877 | 81.6981 | 87.8064 | 93.9246 | 100.0424
RenfrewWind2045RCP8.5 | Renfrew | Wind | RCP8.5 | 2045 | 75.8573 | 81.6627 | 87.7624 | 93.8775 | 99.9856
RenfrewWind2050RCP8.5 | Renfrew | Wind | RCP8.5 | 2050 | 75.9105 | 81.7391 | 87.8651 | 94.0031 | 100.1327
RenfrewWind2055RCP8.5 | Renfrew | Wind | RCP8.5 | 2055 | 75.9941 | 81.8509 | 88.0117 | 94.1757 | 100.3367
RenfrewWind2060RCP8.5 | Renfrew | Wind | RCP8.5 | 2060 | 75.9738 | 81.8209 | 87.9707 | 94.1223 | 100.2765
RenfrewWind2065RCP8.5 | Renfrew | Wind | RCP8.5 | 2065 | 75.8699 | 81.679 | 87.7829 | 93.8964 | 100.0124
RenfrewWind2070RCP8.5 | Renfrew | Wind | RCP8.5 | 2070 | 75.7053 | 81.4499 | 87.4749 | 93.5229 | 99.5709
RenfrewWind2075RCP8.5 | Renfrew | Wind | RCP8.5 | 2075 | 75.6445 | 81.3626 | 87.3547 | 93.3753 | 99.3937
RenfrewWind2080RCP8.5 | Renfrew | Wind | RCP8.5 | 2080 | 75.5837 | 81.2753 | 87.2344 | 93.2278 | 99.2165
RenfrewWind2085RCP8.5 | Renfrew | Wind | RCP8.5 | 2085 | 75.5989 | 81.3244 | 87.3268 | 93.3502 | 99.377
RenfrewWind2090RCP8.5 | Renfrew | Wind | RCP8.5 | 2090 | 75.6141 | 81.3735 | 87.4192 | 93.4726 | 99.5375
RenfrewWind2095RCP8.5 | Renfrew | Wind | RCP8.5 | 2095 | 75.6141 | 81.3735 | 87.4192 | 93.4726 | 99.5375
RenfrewWind2100RCP8.5 | Renfrew | Wind | RCP8.5 | 2100 | 75.6141 | 81.3735 | 87.4192 | 93.4726 | 99.5375
Richmond HillIce Accretion2023RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
Richmond HillIce Accretion2025RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
Richmond HillIce Accretion2030RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
Richmond HillIce Accretion2035RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
Richmond HillIce Accretion2040RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
Richmond HillIce Accretion2045RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
Richmond HillIce Accretion2050RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
Richmond HillIce Accretion2055RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
Richmond HillIce Accretion2060RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
Richmond HillIce Accretion2065RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
Richmond HillIce Accretion2070RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
Richmond HillIce Accretion2075RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
Richmond HillIce Accretion2080RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
Richmond HillIce Accretion2085RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
Richmond HillIce Accretion2090RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
Richmond HillIce Accretion2095RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
Richmond HillIce Accretion2100RCP4.5 | Richmond Hill | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
Richmond HillIce Accretion2023RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
Richmond HillIce Accretion2025RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
Richmond HillIce Accretion2030RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
Richmond HillIce Accretion2035RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
Richmond HillIce Accretion2040RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
Richmond HillIce Accretion2045RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
Richmond HillIce Accretion2050RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
Richmond HillIce Accretion2055RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
Richmond HillIce Accretion2060RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
Richmond HillIce Accretion2065RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
Richmond HillIce Accretion2070RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
Richmond HillIce Accretion2075RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
Richmond HillIce Accretion2080RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
Richmond HillIce Accretion2085RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
Richmond HillIce Accretion2090RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
Richmond HillIce Accretion2095RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
Richmond HillIce Accretion2100RCP6.0 | Richmond Hill | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
Richmond HillIce Accretion2023RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
Richmond HillIce Accretion2025RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
Richmond HillIce Accretion2030RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
Richmond HillIce Accretion2035RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
Richmond HillIce Accretion2040RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
Richmond HillIce Accretion2045RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
Richmond HillIce Accretion2050RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
Richmond HillIce Accretion2055RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
Richmond HillIce Accretion2060RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
Richmond HillIce Accretion2065RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
Richmond HillIce Accretion2070RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
Richmond HillIce Accretion2075RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
Richmond HillIce Accretion2080RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
Richmond HillIce Accretion2085RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
Richmond HillIce Accretion2090RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
Richmond HillIce Accretion2095RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
Richmond HillIce Accretion2100RCP8.5 | Richmond Hill | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
Richmond HillWind2023RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2023 | 79.631 | 85.7311 | 92.1472 | 98.568 | 104.9849
Richmond HillWind2025RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2025 | 79.6456 | 85.7625 | 92.1978 | 98.6352 | 105.0688
Richmond HillWind2030RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2030 | 79.6602 | 85.7939 | 92.2484 | 98.7025 | 105.1527
Richmond HillWind2035RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2035 | 79.6747 | 85.8252 | 92.299 | 98.7698 | 105.2366
Richmond HillWind2040RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2040 | 79.6893 | 85.8566 | 92.3496 | 98.837 | 105.3205
Richmond HillWind2045RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2045 | 79.7039 | 85.888 | 92.4002 | 98.9043 | 105.4044
Richmond HillWind2050RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2050 | 79.7963 | 86.0169 | 92.5741 | 99.1153 | 105.6561
Richmond HillWind2055RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2055 | 79.8741 | 86.1144 | 92.6974 | 99.259 | 105.8239
Richmond HillWind2060RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2060 | 79.952 | 86.212 | 92.8206 | 99.4027 | 105.9917
Richmond HillWind2065RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2065 | 80.0298 | 86.3095 | 92.9439 | 99.5465 | 106.1595
Richmond HillWind2070RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2070 | 80.1077 | 86.407 | 93.0672 | 99.6902 | 106.3273
Richmond HillWind2075RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2075 | 80.2427 | 86.581 | 93.2895 | 99.9543 | 106.6332
Richmond HillWind2080RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2080 | 80.3778 | 86.755 | 93.5119 | 100.2185 | 106.9391
Richmond HillWind2085RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2085 | 80.5128 | 86.929 | 93.7342 | 100.4826 | 107.245
Richmond HillWind2090RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2090 | 80.6479 | 87.1029 | 93.9565 | 100.7468 | 107.5509
Richmond HillWind2095RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2095 | 80.7829 | 87.2769 | 94.1789 | 101.0109 | 107.8568
Richmond HillWind2100RCP4.5 | Richmond Hill | Wind | RCP4.5 | 2100 | 80.918 | 87.4509 | 94.4012 | 101.2751 | 108.1627
Richmond HillWind2023RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2023 | 79.631 | 85.7311 | 92.1472 | 98.568 | 104.9849
Richmond HillWind2025RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2025 | 79.6456 | 85.7625 | 92.1978 | 98.6352 | 105.0688
Richmond HillWind2030RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2030 | 79.6602 | 85.7939 | 92.2484 | 98.7025 | 105.1527
Richmond HillWind2035RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2035 | 79.6747 | 85.8252 | 92.299 | 98.7698 | 105.2366
Richmond HillWind2040RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2040 | 79.6893 | 85.8566 | 92.3496 | 98.837 | 105.3205
Richmond HillWind2045RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2045 | 79.7039 | 85.888 | 92.4002 | 98.9043 | 105.4044
Richmond HillWind2050RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2050 | 79.7963 | 86.0169 | 92.5741 | 99.1153 | 105.6561
Richmond HillWind2055RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2055 | 79.8741 | 86.1144 | 92.6974 | 99.259 | 105.8239
Richmond HillWind2060RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2060 | 79.952 | 86.212 | 92.8206 | 99.4027 | 105.9917
Richmond HillWind2065RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2065 | 80.0298 | 86.3095 | 92.9439 | 99.5465 | 106.1595
Richmond HillWind2070RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2070 | 80.1077 | 86.407 | 93.0672 | 99.6902 | 106.3273
Richmond HillWind2075RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2075 | 80.3103 | 86.668 | 93.4007 | 100.0864 | 106.7862
Richmond HillWind2080RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2080 | 80.5128 | 86.929 | 93.7342 | 100.4826 | 107.245
Richmond HillWind2085RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2085 | 80.7154 | 87.1899 | 94.0677 | 100.8789 | 107.7039
Richmond HillWind2090RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2090 | 81.3364 | 87.9642 | 95.036 | 102.0134 | 109.0088
Richmond HillWind2095RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2095 | 81.7547 | 88.4776 | 95.6708 | 102.7517 | 109.8548
Richmond HillWind2100RCP6.0 | Richmond Hill | Wind | RCP6.0 | 2100 | 82.1731 | 88.991 | 96.3056 | 103.49 | 110.7008
Richmond HillWind2023RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2023 | 79.631 | 85.7311 | 92.1472 | 98.568 | 104.9849
Richmond HillWind2025RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2025 | 79.6602 | 85.7939 | 92.2484 | 98.7025 | 105.1527
Richmond HillWind2030RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2030 | 79.6893 | 85.8566 | 92.3496 | 98.837 | 105.3205
Richmond HillWind2035RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2035 | 79.7184 | 85.9194 | 92.4508 | 98.9716 | 105.4883
Richmond HillWind2040RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2040 | 79.8482 | 86.0819 | 92.6563 | 99.2111 | 105.768
Richmond HillWind2045RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2045 | 79.9779 | 86.2445 | 92.8617 | 99.4507 | 106.0477
Richmond HillWind2050RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2050 | 80.3778 | 86.755 | 93.5119 | 100.2185 | 106.9391
Richmond HillWind2055RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2055 | 80.6479 | 87.1029 | 93.9565 | 100.7468 | 107.5509
Richmond HillWind2060RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2060 | 81.3364 | 87.9642 | 95.036 | 102.0134 | 109.0088
Richmond HillWind2065RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2065 | 81.7547 | 88.4776 | 95.6708 | 102.7517 | 109.8548
Richmond HillWind2070RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2070 | 82.2976 | 89.1592 | 96.5295 | 103.7656 | 111.0225
Richmond HillWind2075RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2075 | 82.422 | 89.3275 | 96.7533 | 104.0412 | 111.3441
Richmond HillWind2080RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2080 | 82.5465 | 89.4958 | 96.9772 | 104.3169 | 111.6657
Richmond HillWind2085RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2085 | 82.8126 | 89.8722 | 97.4924 | 104.9469 | 112.4156
Richmond HillWind2090RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2090 | 83.0788 | 90.2487 | 98.0076 | 105.5769 | 113.1655
Richmond HillWind2095RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2095 | 83.0788 | 90.2487 | 98.0076 | 105.5769 | 113.1655
Richmond HillWind2100RCP8.5 | Richmond Hill | Wind | RCP8.5 | 2100 | 83.0788 | 90.2487 | 98.0076 | 105.5769 | 113.1655
RocklandIce Accretion2023RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
RocklandIce Accretion2025RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
RocklandIce Accretion2030RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
RocklandIce Accretion2035RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
RocklandIce Accretion2040RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
RocklandIce Accretion2045RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
RocklandIce Accretion2050RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
RocklandIce Accretion2055RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
RocklandIce Accretion2060RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
RocklandIce Accretion2065RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
RocklandIce Accretion2070RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
RocklandIce Accretion2075RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2075 | 20.6423 | 24.7215 | 29.87 | 33.8039 | 37.7496
RocklandIce Accretion2080RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2080 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
RocklandIce Accretion2085RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2085 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
RocklandIce Accretion2090RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2090 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
RocklandIce Accretion2095RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2095 | 20.9624 | 25.2029 | 30.55 | 34.6401 | 38.7576
RocklandIce Accretion2100RCP4.5 | Rockland | Ice Accretion | RCP4.5 | 2100 | 21.0424 | 25.3233 | 30.72 | 34.8492 | 39.0096
RocklandIce Accretion2023RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
RocklandIce Accretion2025RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2025 | 20.3639 | 24.1945 | 29.035 | 32.7474 | 36.4455
RocklandIce Accretion2030RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2030 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
RocklandIce Accretion2035RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2035 | 20.3013 | 24.1281 | 28.965 | 32.6796 | 36.3825
RocklandIce Accretion2040RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2040 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
RocklandIce Accretion2045RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2045 | 20.2387 | 24.0617 | 28.895 | 32.6118 | 36.3195
RocklandIce Accretion2050RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2050 | 20.2783 | 24.143 | 29.028 | 32.7813 | 36.5299
RocklandIce Accretion2055RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2055 | 20.3493 | 24.2576 | 29.196 | 32.9847 | 36.7718
RocklandIce Accretion2060RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2060 | 20.4203 | 24.3721 | 29.364 | 33.1881 | 37.0138
RocklandIce Accretion2065RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2065 | 20.4913 | 24.4867 | 29.532 | 33.3915 | 37.2557
RocklandIce Accretion2070RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2070 | 20.5623 | 24.6012 | 29.7 | 33.5949 | 37.4976
RocklandIce Accretion2075RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2075 | 20.6823 | 24.7817 | 29.955 | 33.9085 | 37.8756
RocklandIce Accretion2080RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2080 | 20.8023 | 24.9622 | 30.21 | 34.222 | 38.2536
RocklandIce Accretion2085RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2085 | 20.9224 | 25.1428 | 30.465 | 34.5356 | 38.6316
RocklandIce Accretion2090RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2090 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
RocklandIce Accretion2095RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2095 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
RocklandIce Accretion2100RCP6.0 | Rockland | Ice Accretion | RCP6.0 | 2100 | 21.439 | 25.9458 | 31.65 | 36.0018 | 40.3326
RocklandIce Accretion2023RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2023 | 20.3952 | 24.2277 | 29.07 | 32.7813 | 36.477
RocklandIce Accretion2025RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2025 | 20.3326 | 24.1613 | 29 | 32.7135 | 36.414
RocklandIce Accretion2030RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2030 | 20.27 | 24.0949 | 28.93 | 32.6457 | 36.351
RocklandIce Accretion2035RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2035 | 20.2074 | 24.0285 | 28.86 | 32.5779 | 36.288
RocklandIce Accretion2040RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2040 | 20.3257 | 24.2194 | 29.14 | 32.9169 | 36.6912
RocklandIce Accretion2045RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2045 | 20.444 | 24.4103 | 29.42 | 33.2559 | 37.0944
RocklandIce Accretion2050RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2050 | 20.7223 | 24.8419 | 30.04 | 34.013 | 38.0016
RocklandIce Accretion2055RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2055 | 20.8823 | 25.0826 | 30.38 | 34.4311 | 38.5056
RocklandIce Accretion2060RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2060 | 21.1746 | 25.5308 | 31.03 | 35.2334 | 39.4506
RocklandIce Accretion2065RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2065 | 21.3068 | 25.7383 | 31.34 | 35.6176 | 39.8916
RocklandIce Accretion2070RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2070 | 21.2372 | 25.7383 | 31.44 | 35.7871 | 40.1184
RocklandIce Accretion2075RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2075 | 21.0354 | 25.5308 | 31.23 | 35.5724 | 39.9042
RocklandIce Accretion2080RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2080 | 20.8336 | 25.3233 | 31.02 | 35.3577 | 39.69
RocklandIce Accretion2085RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2085 | 20.0926 | 24.5016 | 30.09 | 34.3237 | 38.5749
RocklandIce Accretion2090RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2090 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
RocklandIce Accretion2095RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2095 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
RocklandIce Accretion2100RCP8.5 | Rockland | Ice Accretion | RCP8.5 | 2100 | 19.3515 | 23.6799 | 29.16 | 33.2898 | 37.4598
RocklandWind2023RCP4.5 | Rockland | Wind | RCP4.5 | 2023 | 82.1949 | 88.6062 | 95.3705 | 102.1176 | 108.8632
RocklandWind2025RCP4.5 | Rockland | Wind | RCP4.5 | 2025 | 82.2263 | 88.643 | 95.4133 | 102.1667 | 108.9173
RocklandWind2030RCP4.5 | Rockland | Wind | RCP4.5 | 2030 | 82.2578 | 88.6798 | 95.456 | 102.2159 | 108.9715
RocklandWind2035RCP4.5 | Rockland | Wind | RCP4.5 | 2035 | 82.2892 | 88.7167 | 95.4988 | 102.265 | 109.0256
RocklandWind2040RCP4.5 | Rockland | Wind | RCP4.5 | 2040 | 82.3207 | 88.7535 | 95.5415 | 102.3141 | 109.0798
RocklandWind2045RCP4.5 | Rockland | Wind | RCP4.5 | 2045 | 82.3521 | 88.7903 | 95.5842 | 102.3632 | 109.1339
RocklandWind2050RCP4.5 | Rockland | Wind | RCP4.5 | 2050 | 82.3065 | 88.7211 | 95.4883 | 102.2436 | 108.991
RocklandWind2055RCP4.5 | Rockland | Wind | RCP4.5 | 2055 | 82.2293 | 88.6151 | 95.3496 | 102.0749 | 108.7938
RocklandWind2060RCP4.5 | Rockland | Wind | RCP4.5 | 2060 | 82.1522 | 88.509 | 95.2109 | 101.9062 | 108.5967
RocklandWind2065RCP4.5 | Rockland | Wind | RCP4.5 | 2065 | 82.0751 | 88.403 | 95.0722 | 101.7374 | 108.3996
RocklandWind2070RCP4.5 | Rockland | Wind | RCP4.5 | 2070 | 81.998 | 88.297 | 94.9335 | 101.5687 | 108.2025
RocklandWind2075RCP4.5 | Rockland | Wind | RCP4.5 | 2075 | 82.0185 | 88.3309 | 94.9826 | 101.6314 | 108.2801
RocklandWind2080RCP4.5 | Rockland | Wind | RCP4.5 | 2080 | 82.039 | 88.3647 | 95.0317 | 101.694 | 108.3578
RocklandWind2085RCP4.5 | Rockland | Wind | RCP4.5 | 2085 | 82.0595 | 88.3986 | 95.0807 | 101.7567 | 108.4354
RocklandWind2090RCP4.5 | Rockland | Wind | RCP4.5 | 2090 | 82.08 | 88.4325 | 95.1298 | 101.8194 | 108.513
RocklandWind2095RCP4.5 | Rockland | Wind | RCP4.5 | 2095 | 82.1006 | 88.4663 | 95.1789 | 101.8821 | 108.5906
RocklandWind2100RCP4.5 | Rockland | Wind | RCP4.5 | 2100 | 82.1211 | 88.5002 | 95.228 | 101.9448 | 108.6682
RocklandWind2023RCP6.0 | Rockland | Wind | RCP6.0 | 2023 | 82.1949 | 88.6062 | 95.3705 | 102.1176 | 108.8632
RocklandWind2025RCP6.0 | Rockland | Wind | RCP6.0 | 2025 | 82.2263 | 88.643 | 95.4133 | 102.1667 | 108.9173
RocklandWind2030RCP6.0 | Rockland | Wind | RCP6.0 | 2030 | 82.2578 | 88.6798 | 95.456 | 102.2159 | 108.9715
RocklandWind2035RCP6.0 | Rockland | Wind | RCP6.0 | 2035 | 82.2892 | 88.7167 | 95.4988 | 102.265 | 109.0256
RocklandWind2040RCP6.0 | Rockland | Wind | RCP6.0 | 2040 | 82.3207 | 88.7535 | 95.5415 | 102.3141 | 109.0798
RocklandWind2045RCP6.0 | Rockland | Wind | RCP6.0 | 2045 | 82.3521 | 88.7903 | 95.5842 | 102.3632 | 109.1339
RocklandWind2050RCP6.0 | Rockland | Wind | RCP6.0 | 2050 | 82.3065 | 88.7211 | 95.4883 | 102.2436 | 108.991
RocklandWind2055RCP6.0 | Rockland | Wind | RCP6.0 | 2055 | 82.2293 | 88.6151 | 95.3496 | 102.0749 | 108.7938
RocklandWind2060RCP6.0 | Rockland | Wind | RCP6.0 | 2060 | 82.1522 | 88.509 | 95.2109 | 101.9062 | 108.5967
RocklandWind2065RCP6.0 | Rockland | Wind | RCP6.0 | 2065 | 82.0751 | 88.403 | 95.0722 | 101.7374 | 108.3996
RocklandWind2070RCP6.0 | Rockland | Wind | RCP6.0 | 2070 | 81.998 | 88.297 | 94.9335 | 101.5687 | 108.2025
RocklandWind2075RCP6.0 | Rockland | Wind | RCP6.0 | 2075 | 82.0288 | 88.3478 | 95.0071 | 101.6627 | 108.319
RocklandWind2080RCP6.0 | Rockland | Wind | RCP6.0 | 2080 | 82.0595 | 88.3986 | 95.0807 | 101.7567 | 108.4354
RocklandWind2085RCP6.0 | Rockland | Wind | RCP6.0 | 2085 | 82.0903 | 88.4494 | 95.1544 | 101.8508 | 108.5518
RocklandWind2090RCP6.0 | Rockland | Wind | RCP6.0 | 2090 | 81.9953 | 88.3412 | 95.0317 | 101.7144 | 108.4011
RocklandWind2095RCP6.0 | Rockland | Wind | RCP6.0 | 2095 | 81.8695 | 88.1821 | 94.8353 | 101.484 | 108.1339
RocklandWind2100RCP6.0 | Rockland | Wind | RCP6.0 | 2100 | 81.7437 | 88.0231 | 94.639 | 101.2536 | 107.8668
RocklandWind2023RCP8.5 | Rockland | Wind | RCP8.5 | 2023 | 82.1949 | 88.6062 | 95.3705 | 102.1176 | 108.8632
RocklandWind2025RCP8.5 | Rockland | Wind | RCP8.5 | 2025 | 82.2578 | 88.6798 | 95.456 | 102.2159 | 108.9715
RocklandWind2030RCP8.5 | Rockland | Wind | RCP8.5 | 2030 | 82.3207 | 88.7535 | 95.5415 | 102.3141 | 109.0798
RocklandWind2035RCP8.5 | Rockland | Wind | RCP8.5 | 2035 | 82.3836 | 88.8271 | 95.627 | 102.4124 | 109.1881
RocklandWind2040RCP8.5 | Rockland | Wind | RCP8.5 | 2040 | 82.255 | 88.6504 | 95.3958 | 102.1311 | 108.8595
RocklandWind2045RCP8.5 | Rockland | Wind | RCP8.5 | 2045 | 82.1265 | 88.4737 | 95.1647 | 101.8499 | 108.531
RocklandWind2050RCP8.5 | Rockland | Wind | RCP8.5 | 2050 | 82.039 | 88.3647 | 95.0317 | 101.694 | 108.3578
RocklandWind2055RCP8.5 | Rockland | Wind | RCP8.5 | 2055 | 82.08 | 88.4325 | 95.1298 | 101.8194 | 108.513
RocklandWind2060RCP8.5 | Rockland | Wind | RCP8.5 | 2060 | 81.9953 | 88.3412 | 95.0317 | 101.7144 | 108.4011
RocklandWind2065RCP8.5 | Rockland | Wind | RCP8.5 | 2065 | 81.8695 | 88.1821 | 94.8353 | 101.484 | 108.1339
RocklandWind2070RCP8.5 | Rockland | Wind | RCP8.5 | 2070 | 81.823 | 88.1291 | 94.772 | 101.4094 | 108.0509
RocklandWind2075RCP8.5 | Rockland | Wind | RCP8.5 | 2075 | 81.9023 | 88.2351 | 94.905 | 101.5653 | 108.235
RocklandWind2080RCP8.5 | Rockland | Wind | RCP8.5 | 2080 | 81.9816 | 88.3412 | 95.038 | 101.7212 | 108.4191
RocklandWind2085RCP8.5 | Rockland | Wind | RCP8.5 | 2085 | 81.957 | 88.297 | 94.9762 | 101.6449 | 108.3217
RocklandWind2090RCP8.5 | Rockland | Wind | RCP8.5 | 2090 | 81.9324 | 88.2528 | 94.9145 | 101.5687 | 108.2242
RocklandWind2095RCP8.5 | Rockland | Wind | RCP8.5 | 2095 | 81.9324 | 88.2528 | 94.9145 | 101.5687 | 108.2242
RocklandWind2100RCP8.5 | Rockland | Wind | RCP8.5 | 2100 | 81.9324 | 88.2528 | 94.9145 | 101.5687 | 108.2242
SarniaIce Accretion2023RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2023 | 14.5432 | 17.4931 | 21.208 | 24.0396 | 26.8607
SarniaIce Accretion2025RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2025 | 14.5917 | 17.56 | 21.3033 | 24.1515 | 26.9947
SarniaIce Accretion2030RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2030 | 14.6401 | 17.627 | 21.3987 | 24.2634 | 27.1286
SarniaIce Accretion2035RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2035 | 14.6886 | 17.6939 | 21.494 | 24.3752 | 27.2626
SarniaIce Accretion2040RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2040 | 14.7371 | 17.7609 | 21.5893 | 24.4871 | 27.3966
SarniaIce Accretion2045RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2045 | 14.7856 | 17.8278 | 21.6847 | 24.599 | 27.5306
SarniaIce Accretion2050RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2050 | 14.6167 | 17.6647 | 21.5248 | 24.4374 | 27.3707
SarniaIce Accretion2055RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2055 | 14.3993 | 17.4346 | 21.2696 | 24.1639 | 27.0769
SarniaIce Accretion2060RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2060 | 14.1819 | 17.2046 | 21.0144 | 23.8905 | 26.7831
SarniaIce Accretion2065RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2065 | 13.9645 | 16.9745 | 20.7592 | 23.617 | 26.4892
SarniaIce Accretion2070RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2070 | 13.7471 | 16.7444 | 20.504 | 23.3435 | 26.1954
SarniaIce Accretion2075RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2075 | 13.5047 | 16.4675 | 20.1813 | 22.9914 | 25.8073
SarniaIce Accretion2080RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2080 | 13.2624 | 16.1905 | 19.8587 | 22.6392 | 25.4192
SarniaIce Accretion2085RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2085 | 13.02 | 15.9136 | 19.536 | 22.287 | 25.0312
SarniaIce Accretion2090RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2090 | 12.7776 | 15.6366 | 19.2133 | 21.9348 | 24.6431
SarniaIce Accretion2095RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2095 | 12.5352 | 15.3597 | 18.8907 | 21.5826 | 24.255
SarniaIce Accretion2100RCP4.5 | Sarnia | Ice Accretion | RCP4.5 | 2100 | 12.2928 | 15.0828 | 18.568 | 21.2304 | 23.8669
SarniaIce Accretion2023RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2023 | 14.5432 | 17.4931 | 21.208 | 24.0396 | 26.8607
SarniaIce Accretion2025RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2025 | 14.5917 | 17.56 | 21.3033 | 24.1515 | 26.9947
SarniaIce Accretion2030RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2030 | 14.6401 | 17.627 | 21.3987 | 24.2634 | 27.1286
SarniaIce Accretion2035RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2035 | 14.6886 | 17.6939 | 21.494 | 24.3752 | 27.2626
SarniaIce Accretion2040RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2040 | 14.7371 | 17.7609 | 21.5893 | 24.4871 | 27.3966
SarniaIce Accretion2045RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2045 | 14.7856 | 17.8278 | 21.6847 | 24.599 | 27.5306
SarniaIce Accretion2050RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2050 | 14.6167 | 17.6647 | 21.5248 | 24.4374 | 27.3707
SarniaIce Accretion2055RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2055 | 14.3993 | 17.4346 | 21.2696 | 24.1639 | 27.0769
SarniaIce Accretion2060RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2060 | 14.1819 | 17.2046 | 21.0144 | 23.8905 | 26.7831
SarniaIce Accretion2065RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2065 | 13.9645 | 16.9745 | 20.7592 | 23.617 | 26.4892
SarniaIce Accretion2070RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2070 | 13.7471 | 16.7444 | 20.504 | 23.3435 | 26.1954
SarniaIce Accretion2075RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2075 | 13.3836 | 16.329 | 20.02 | 22.8153 | 25.6133
SarniaIce Accretion2080RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2080 | 13.02 | 15.9136 | 19.536 | 22.287 | 25.0312
SarniaIce Accretion2085RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2085 | 12.6564 | 15.4982 | 19.052 | 21.7587 | 24.449
SarniaIce Accretion2090RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2090 | 11.7774 | 14.4802 | 17.864 | 20.4349 | 22.9891
SarniaIce Accretion2095RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2095 | 11.262 | 13.8776 | 17.16 | 19.6394 | 22.1113
SarniaIce Accretion2100RCP6.0 | Sarnia | Ice Accretion | RCP6.0 | 2100 | 10.7466 | 13.275 | 16.456 | 18.8439 | 21.2335
SarniaIce Accretion2023RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2023 | 14.5432 | 17.4931 | 21.208 | 24.0396 | 26.8607
SarniaIce Accretion2025RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2025 | 14.6401 | 17.627 | 21.3987 | 24.2634 | 27.1286
SarniaIce Accretion2030RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2030 | 14.7371 | 17.7609 | 21.5893 | 24.4871 | 27.3966
SarniaIce Accretion2035RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2035 | 14.834 | 17.8948 | 21.78 | 24.7108 | 27.6646
SarniaIce Accretion2040RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2040 | 14.4717 | 17.5113 | 21.3547 | 24.2551 | 27.1748
SarniaIce Accretion2045RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2045 | 14.1094 | 17.1279 | 20.9293 | 23.7993 | 26.6851
SarniaIce Accretion2050RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2050 | 13.2624 | 16.1905 | 19.8587 | 22.6392 | 25.4192
SarniaIce Accretion2055RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2055 | 12.7776 | 15.6366 | 19.2133 | 21.9348 | 24.6431
SarniaIce Accretion2060RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2060 | 11.7774 | 14.4802 | 17.864 | 20.4349 | 22.9891
SarniaIce Accretion2065RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2065 | 11.262 | 13.8776 | 17.16 | 19.6394 | 22.1113
SarniaIce Accretion2070RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2070 | 10.3231 | 12.7942 | 15.8987 | 18.2307 | 20.559
SarniaIce Accretion2075RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2075 | 9.8996 | 12.3133 | 15.3413 | 17.6175 | 19.8845
SarniaIce Accretion2080RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2080 | 9.476 | 11.8325 | 14.784 | 17.0042 | 19.21
SarniaIce Accretion2085RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2085 | 8.6647 | 10.8647 | 13.596 | 15.6618 | 17.7131
SarniaIce Accretion2090RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2090 | 7.8533 | 9.8969 | 12.408 | 14.3194 | 16.2162
SarniaIce Accretion2095RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2095 | 7.8533 | 9.8969 | 12.408 | 14.3194 | 16.2162
SarniaIce Accretion2100RCP8.5 | Sarnia | Ice Accretion | RCP8.5 | 2100 | 7.8533 | 9.8969 | 12.408 | 14.3194 | 16.2162
SarniaWind2023RCP4.5 | Sarnia | Wind | RCP4.5 | 2023 | 85.0444 | 91.6139 | 98.5292 | 105.4367 | 112.3456
SarniaWind2025RCP4.5 | Sarnia | Wind | RCP4.5 | 2025 | 85.105 | 91.6838 | 98.6109 | 105.5311 | 112.4499
SarniaWind2030RCP4.5 | Sarnia | Wind | RCP4.5 | 2030 | 85.1657 | 91.7537 | 98.6925 | 105.6255 | 112.5542
SarniaWind2035RCP4.5 | Sarnia | Wind | RCP4.5 | 2035 | 85.2263 | 91.8236 | 98.7742 | 105.7199 | 112.6584
SarniaWind2040RCP4.5 | Sarnia | Wind | RCP4.5 | 2040 | 85.287 | 91.8934 | 98.8559 | 105.8142 | 112.7627
SarniaWind2045RCP4.5 | Sarnia | Wind | RCP4.5 | 2045 | 85.3476 | 91.9633 | 98.9375 | 105.9086 | 112.867
SarniaWind2050RCP4.5 | Sarnia | Wind | RCP4.5 | 2050 | 85.4083 | 92.0332 | 99.0192 | 106.0009 | 112.9713
SarniaWind2055RCP4.5 | Sarnia | Wind | RCP4.5 | 2055 | 85.4083 | 92.0332 | 99.0192 | 105.9988 | 112.9713
SarniaWind2060RCP4.5 | Sarnia | Wind | RCP4.5 | 2060 | 85.4083 | 92.0332 | 99.0192 | 105.9967 | 112.9713
SarniaWind2065RCP4.5 | Sarnia | Wind | RCP4.5 | 2065 | 85.4083 | 92.0332 | 99.0192 | 105.9946 | 112.9713
SarniaWind2070RCP4.5 | Sarnia | Wind | RCP4.5 | 2070 | 85.4083 | 92.0332 | 99.0192 | 105.9925 | 112.9713
SarniaWind2075RCP4.5 | Sarnia | Wind | RCP4.5 | 2075 | 85.538 | 92.1957 | 99.2201 | 106.2284 | 113.2413
SarniaWind2080RCP4.5 | Sarnia | Wind | RCP4.5 | 2080 | 85.6678 | 92.3582 | 99.421 | 106.4644 | 113.5112
SarniaWind2085RCP4.5 | Sarnia | Wind | RCP4.5 | 2085 | 85.7975 | 92.5208 | 99.6219 | 106.7003 | 113.7812
SarniaWind2090RCP4.5 | Sarnia | Wind | RCP4.5 | 2090 | 85.9273 | 92.6833 | 99.8228 | 106.9362 | 114.0512
SarniaWind2095RCP4.5 | Sarnia | Wind | RCP4.5 | 2095 | 86.057 | 92.8458 | 100.0237 | 107.1722 | 114.3212
SarniaWind2100RCP4.5 | Sarnia | Wind | RCP4.5 | 2100 | 86.1868 | 93.0084 | 100.2246 | 107.4081 | 114.5912
SarniaWind2023RCP6.0 | Sarnia | Wind | RCP6.0 | 2023 | 85.0444 | 91.6139 | 98.5292 | 105.4367 | 112.3456
SarniaWind2025RCP6.0 | Sarnia | Wind | RCP6.0 | 2025 | 85.105 | 91.6838 | 98.6109 | 105.5311 | 112.4499
SarniaWind2030RCP6.0 | Sarnia | Wind | RCP6.0 | 2030 | 85.1657 | 91.7537 | 98.6925 | 105.6255 | 112.5542
SarniaWind2035RCP6.0 | Sarnia | Wind | RCP6.0 | 2035 | 85.2263 | 91.8236 | 98.7742 | 105.7199 | 112.6584
SarniaWind2040RCP6.0 | Sarnia | Wind | RCP6.0 | 2040 | 85.287 | 91.8934 | 98.8559 | 105.8142 | 112.7627
SarniaWind2045RCP6.0 | Sarnia | Wind | RCP6.0 | 2045 | 85.3476 | 91.9633 | 98.9375 | 105.9086 | 112.867
SarniaWind2050RCP6.0 | Sarnia | Wind | RCP6.0 | 2050 | 85.4083 | 92.0332 | 99.0192 | 106.0009 | 112.9713
SarniaWind2055RCP6.0 | Sarnia | Wind | RCP6.0 | 2055 | 85.4083 | 92.0332 | 99.0192 | 105.9988 | 112.9713
SarniaWind2060RCP6.0 | Sarnia | Wind | RCP6.0 | 2060 | 85.4083 | 92.0332 | 99.0192 | 105.9967 | 112.9713
SarniaWind2065RCP6.0 | Sarnia | Wind | RCP6.0 | 2065 | 85.4083 | 92.0332 | 99.0192 | 105.9946 | 112.9713
SarniaWind2070RCP6.0 | Sarnia | Wind | RCP6.0 | 2070 | 85.4083 | 92.0332 | 99.0192 | 105.9925 | 112.9713
SarniaWind2075RCP6.0 | Sarnia | Wind | RCP6.0 | 2075 | 85.6029 | 92.277 | 99.3205 | 106.3464 | 113.3762
SarniaWind2080RCP6.0 | Sarnia | Wind | RCP6.0 | 2080 | 85.7975 | 92.5208 | 99.6219 | 106.7003 | 113.7812
SarniaWind2085RCP6.0 | Sarnia | Wind | RCP6.0 | 2085 | 85.9921 | 92.7646 | 99.9232 | 107.0542 | 114.1862
SarniaWind2090RCP6.0 | Sarnia | Wind | RCP6.0 | 2090 | 86.4463 | 93.3304 | 100.6264 | 107.8765 | 115.1275
SarniaWind2095RCP6.0 | Sarnia | Wind | RCP6.0 | 2095 | 86.7058 | 93.6524 | 101.0282 | 108.3448 | 115.6637
SarniaWind2100RCP6.0 | Sarnia | Wind | RCP6.0 | 2100 | 86.9653 | 93.9745 | 101.43 | 108.8132 | 116.2
SarniaWind2023RCP8.5 | Sarnia | Wind | RCP8.5 | 2023 | 85.0444 | 91.6139 | 98.5292 | 105.4367 | 112.3456
SarniaWind2025RCP8.5 | Sarnia | Wind | RCP8.5 | 2025 | 85.1657 | 91.7537 | 98.6925 | 105.6255 | 112.5542
SarniaWind2030RCP8.5 | Sarnia | Wind | RCP8.5 | 2030 | 85.287 | 91.8934 | 98.8559 | 105.8142 | 112.7627
SarniaWind2035RCP8.5 | Sarnia | Wind | RCP8.5 | 2035 | 85.4083 | 92.0332 | 99.0192 | 106.003 | 112.9713
SarniaWind2040RCP8.5 | Sarnia | Wind | RCP8.5 | 2040 | 85.4083 | 92.0332 | 99.0192 | 105.9995 | 112.9713
SarniaWind2045RCP8.5 | Sarnia | Wind | RCP8.5 | 2045 | 85.4083 | 92.0332 | 99.0192 | 105.996 | 112.9713
SarniaWind2050RCP8.5 | Sarnia | Wind | RCP8.5 | 2050 | 85.6678 | 92.3582 | 99.421 | 106.4644 | 113.5112
SarniaWind2055RCP8.5 | Sarnia | Wind | RCP8.5 | 2055 | 85.9273 | 92.6833 | 99.8228 | 106.9362 | 114.0512
SarniaWind2060RCP8.5 | Sarnia | Wind | RCP8.5 | 2060 | 86.4463 | 93.3304 | 100.6264 | 107.8765 | 115.1275
SarniaWind2065RCP8.5 | Sarnia | Wind | RCP8.5 | 2065 | 86.7058 | 93.6524 | 101.0282 | 108.3448 | 115.6637
SarniaWind2070RCP8.5 | Sarnia | Wind | RCP8.5 | 2070 | 87.2474 | 94.3238 | 101.8612 | 109.3131 | 116.7697
SarniaWind2075RCP8.5 | Sarnia | Wind | RCP8.5 | 2075 | 87.5294 | 94.6732 | 102.2924 | 109.8129 | 117.3395
SarniaWind2080RCP8.5 | Sarnia | Wind | RCP8.5 | 2080 | 87.8115 | 95.0226 | 102.7236 | 110.3127 | 117.9093
SarniaWind2085RCP8.5 | Sarnia | Wind | RCP8.5 | 2085 | 87.968 | 95.2367 | 103.0176 | 110.6692 | 118.3394
SarniaWind2090RCP8.5 | Sarnia | Wind | RCP8.5 | 2090 | 88.1246 | 95.4509 | 103.3116 | 111.0258 | 118.7695
SarniaWind2095RCP8.5 | Sarnia | Wind | RCP8.5 | 2095 | 88.1246 | 95.4509 | 103.3116 | 111.0258 | 118.7695
SarniaWind2100RCP8.5 | Sarnia | Wind | RCP8.5 | 2100 | 88.1246 | 95.4509 | 103.3116 | 111.0258 | 118.7695
Sault Ste. MarieIce Accretion2023RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2023 | 14.8647 | 17.8218 | 21.582 | 24.4374 | 27.3042
Sault Ste. MarieIce Accretion2025RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2025 | 14.8111 | 17.77 | 21.5307 | 24.3877 | 27.258
Sault Ste. MarieIce Accretion2030RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2030 | 14.7575 | 17.7183 | 21.4793 | 24.3379 | 27.2118
Sault Ste. MarieIce Accretion2035RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2035 | 14.7039 | 17.6665 | 21.428 | 24.2882 | 27.1656
Sault Ste. MarieIce Accretion2040RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2040 | 14.6503 | 17.6148 | 21.3767 | 24.2385 | 27.1194
Sault Ste. MarieIce Accretion2045RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2045 | 14.5968 | 17.5631 | 21.3253 | 24.1888 | 27.0732
Sault Ste. MarieIce Accretion2050RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2050 | 14.6473 | 17.6574 | 21.4676 | 24.3727 | 27.2876
Sault Ste. MarieIce Accretion2055RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2055 | 14.7514 | 17.8035 | 21.6612 | 24.6064 | 27.5481
Sault Ste. MarieIce Accretion2060RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2060 | 14.8555 | 17.9496 | 21.8548 | 24.8401 | 27.8087
Sault Ste. MarieIce Accretion2065RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2065 | 14.9596 | 18.0957 | 22.0484 | 25.0738 | 28.0693
Sault Ste. MarieIce Accretion2070RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2070 | 15.0637 | 18.2417 | 22.242 | 25.3075 | 28.3298
Sault Ste. MarieIce Accretion2075RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2075 | 15.028 | 18.2265 | 22.2493 | 25.3241 | 28.3668
Sault Ste. MarieIce Accretion2080RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2080 | 14.9922 | 18.2113 | 22.2567 | 25.3406 | 28.4038
Sault Ste. MarieIce Accretion2085RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2085 | 14.9565 | 18.1961 | 22.264 | 25.3572 | 28.4407
Sault Ste. MarieIce Accretion2090RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2090 | 14.9208 | 18.1809 | 22.2713 | 25.3738 | 28.4777
Sault Ste. MarieIce Accretion2095RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2095 | 14.8851 | 18.1657 | 22.2787 | 25.3903 | 28.5146
Sault Ste. MarieIce Accretion2100RCP4.5 | Sault Ste. Marie | Ice Accretion | RCP4.5 | 2100 | 14.8494 | 18.1504 | 22.286 | 25.4069 | 28.5516
Sault Ste. MarieIce Accretion2023RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2023 | 14.8647 | 17.8218 | 21.582 | 24.4374 | 27.3042
Sault Ste. MarieIce Accretion2025RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2025 | 14.8111 | 17.77 | 21.5307 | 24.3877 | 27.258
Sault Ste. MarieIce Accretion2030RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2030 | 14.7575 | 17.7183 | 21.4793 | 24.3379 | 27.2118
Sault Ste. MarieIce Accretion2035RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2035 | 14.7039 | 17.6665 | 21.428 | 24.2882 | 27.1656
Sault Ste. MarieIce Accretion2040RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2040 | 14.6503 | 17.6148 | 21.3767 | 24.2385 | 27.1194
Sault Ste. MarieIce Accretion2045RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2045 | 14.5968 | 17.5631 | 21.3253 | 24.1888 | 27.0732
Sault Ste. MarieIce Accretion2050RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2050 | 14.6473 | 17.6574 | 21.4676 | 24.3727 | 27.2876
Sault Ste. MarieIce Accretion2055RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2055 | 14.7514 | 17.8035 | 21.6612 | 24.6064 | 27.5481
Sault Ste. MarieIce Accretion2060RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2060 | 14.8555 | 17.9496 | 21.8548 | 24.8401 | 27.8087
Sault Ste. MarieIce Accretion2065RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2065 | 14.9596 | 18.0957 | 22.0484 | 25.0738 | 28.0693
Sault Ste. MarieIce Accretion2070RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2070 | 15.0637 | 18.2417 | 22.242 | 25.3075 | 28.3298
Sault Ste. MarieIce Accretion2075RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2075 | 15.0101 | 18.2189 | 22.253 | 25.3323 | 28.3853
Sault Ste. MarieIce Accretion2080RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2080 | 14.9565 | 18.1961 | 22.264 | 25.3572 | 28.4407
Sault Ste. MarieIce Accretion2085RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2085 | 14.9029 | 18.1733 | 22.275 | 25.3821 | 28.4962
Sault Ste. MarieIce Accretion2090RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2090 | 14.8494 | 18.193 | 22.3813 | 25.5478 | 28.7179
Sault Ste. MarieIce Accretion2095RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2095 | 14.8494 | 18.2357 | 22.4767 | 25.6887 | 28.8842
Sault Ste. MarieIce Accretion2100RCP6.0 | Sault Ste. Marie | Ice Accretion | RCP6.0 | 2100 | 14.8494 | 18.2783 | 22.572 | 25.8295 | 29.0506
Sault Ste. MarieIce Accretion2023RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2023 | 14.8647 | 17.8218 | 21.582 | 24.4374 | 27.3042
Sault Ste. MarieIce Accretion2025RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2025 | 14.7575 | 17.7183 | 21.4793 | 24.3379 | 27.2118
Sault Ste. MarieIce Accretion2030RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2030 | 14.6503 | 17.6148 | 21.3767 | 24.2385 | 27.1194
Sault Ste. MarieIce Accretion2035RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2035 | 14.5432 | 17.5113 | 21.274 | 24.1391 | 27.027
Sault Ste. MarieIce Accretion2040RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2040 | 14.7167 | 17.7548 | 21.5967 | 24.5285 | 27.4613
Sault Ste. MarieIce Accretion2045RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2045 | 14.8902 | 17.9983 | 21.9193 | 24.918 | 27.8956
Sault Ste. MarieIce Accretion2050RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2050 | 14.9922 | 18.2113 | 22.2567 | 25.3406 | 28.4038
Sault Ste. MarieIce Accretion2055RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2055 | 14.9208 | 18.1809 | 22.2713 | 25.3738 | 28.4777
Sault Ste. MarieIce Accretion2060RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2060 | 14.8494 | 18.193 | 22.3813 | 25.5478 | 28.7179
Sault Ste. MarieIce Accretion2065RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2065 | 14.8494 | 18.2357 | 22.4767 | 25.6887 | 28.8842
Sault Ste. MarieIce Accretion2070RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2070 | 14.3442 | 17.6757 | 21.8533 | 25.0257 | 28.1635
Sault Ste. MarieIce Accretion2075RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2075 | 13.839 | 17.0731 | 21.1347 | 24.2219 | 27.2765
Sault Ste. MarieIce Accretion2080RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2080 | 13.3338 | 16.4705 | 20.416 | 23.4181 | 26.3894
Sault Ste. MarieIce Accretion2085RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2085 | 13.1348 | 16.2605 | 20.185 | 23.1695 | 26.1261
Sault Ste. MarieIce Accretion2090RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2090 | 12.9358 | 16.0505 | 19.954 | 22.9209 | 25.8628
Sault Ste. MarieIce Accretion2095RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2095 | 12.9358 | 16.0505 | 19.954 | 22.9209 | 25.8628
Sault Ste. MarieIce Accretion2100RCP8.5 | Sault Ste. Marie | Ice Accretion | RCP8.5 | 2100 | 12.9358 | 16.0505 | 19.954 | 22.9209 | 25.8628
Sault Ste. MarieWind2023RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2023 | 85.4252 | 92.097 | 99.1466 | 106.1707 | 113.1947
Sault Ste. MarieWind2025RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2025 | 85.4689 | 92.1486 | 99.2087 | 106.2424 | 113.2748
Sault Ste. MarieWind2030RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2030 | 85.5126 | 92.2003 | 99.2707 | 106.3141 | 113.3548
Sault Ste. MarieWind2035RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2035 | 85.5563 | 92.2519 | 99.3328 | 106.3857 | 113.4349
Sault Ste. MarieWind2040RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2040 | 85.6001 | 92.3036 | 99.3949 | 106.4574 | 113.515
Sault Ste. MarieWind2045RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2045 | 85.6438 | 92.3552 | 99.4569 | 106.529 | 113.595
Sault Ste. MarieWind2050RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2050 | 85.6655 | 92.3649 | 99.4484 | 106.5063 | 113.5589
Sault Ste. MarieWind2055RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2055 | 85.6435 | 92.323 | 99.3779 | 106.4119 | 113.4427
Sault Ste. MarieWind2060RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2060 | 85.6215 | 92.2811 | 99.3073 | 106.3176 | 113.3265
Sault Ste. MarieWind2065RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2065 | 85.5995 | 92.2391 | 99.2368 | 106.2232 | 113.2103
Sault Ste. MarieWind2070RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2070 | 85.5775 | 92.1972 | 99.1662 | 106.1288 | 113.0942
Sault Ste. MarieWind2075RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2075 | 85.6156 | 92.2443 | 99.2266 | 106.1987 | 113.1761
Sault Ste. MarieWind2080RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2080 | 85.6537 | 92.2914 | 99.2871 | 106.2686 | 113.258
Sault Ste. MarieWind2085RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2085 | 85.6917 | 92.3385 | 99.3475 | 106.3385 | 113.3399
Sault Ste. MarieWind2090RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2090 | 85.7298 | 92.3856 | 99.4079 | 106.4084 | 113.4219
Sault Ste. MarieWind2095RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2095 | 85.7679 | 92.4327 | 99.4684 | 106.4783 | 113.5038
Sault Ste. MarieWind2100RCP4.5 | Sault Ste. Marie | Wind | RCP4.5 | 2100 | 85.806 | 92.4798 | 99.5288 | 106.5482 | 113.5857
Sault Ste. MarieWind2023RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2023 | 85.4252 | 92.097 | 99.1466 | 106.1707 | 113.1947
Sault Ste. MarieWind2025RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2025 | 85.4689 | 92.1486 | 99.2087 | 106.2424 | 113.2748
Sault Ste. MarieWind2030RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2030 | 85.5126 | 92.2003 | 99.2707 | 106.3141 | 113.3548
Sault Ste. MarieWind2035RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2035 | 85.5563 | 92.2519 | 99.3328 | 106.3857 | 113.4349
Sault Ste. MarieWind2040RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2040 | 85.6001 | 92.3036 | 99.3949 | 106.4574 | 113.515
Sault Ste. MarieWind2045RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2045 | 85.6438 | 92.3552 | 99.4569 | 106.529 | 113.595
Sault Ste. MarieWind2050RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2050 | 85.6655 | 92.3649 | 99.4484 | 106.5063 | 113.5589
Sault Ste. MarieWind2055RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2055 | 85.6435 | 92.323 | 99.3779 | 106.4119 | 113.4427
Sault Ste. MarieWind2060RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2060 | 85.6215 | 92.2811 | 99.3073 | 106.3176 | 113.3265
Sault Ste. MarieWind2065RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2065 | 85.5995 | 92.2391 | 99.2368 | 106.2232 | 113.2103
Sault Ste. MarieWind2070RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2070 | 85.5775 | 92.1972 | 99.1662 | 106.1288 | 113.0942
Sault Ste. MarieWind2075RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2075 | 85.6346 | 92.2679 | 99.2569 | 106.2337 | 113.217
Sault Ste. MarieWind2080RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2080 | 85.6917 | 92.3385 | 99.3475 | 106.3385 | 113.3399
Sault Ste. MarieWind2085RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2085 | 85.7489 | 92.4091 | 99.4382 | 106.4434 | 113.4628
Sault Ste. MarieWind2090RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2090 | 86.184 | 92.9324 | 100.0678 | 107.1669 | 114.2784
Sault Ste. MarieWind2095RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2095 | 86.5619 | 93.3851 | 100.6068 | 107.7856 | 114.9711
Sault Ste. MarieWind2100RCP6.0 | Sault Ste. Marie | Wind | RCP6.0 | 2100 | 86.9399 | 93.8377 | 101.1458 | 108.4043 | 115.6637
Sault Ste. MarieWind2023RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2023 | 85.4252 | 92.097 | 99.1466 | 106.1707 | 113.1947
Sault Ste. MarieWind2025RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2025 | 85.5126 | 92.2003 | 99.2707 | 106.3141 | 113.3548
Sault Ste. MarieWind2030RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2030 | 85.6001 | 92.3036 | 99.3949 | 106.4574 | 113.515
Sault Ste. MarieWind2035RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2035 | 85.6875 | 92.4068 | 99.519 | 106.6007 | 113.6751
Sault Ste. MarieWind2040RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2040 | 85.6508 | 92.337 | 99.4014 | 106.4434 | 113.4815
Sault Ste. MarieWind2045RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2045 | 85.6142 | 92.2671 | 99.2838 | 106.2861 | 113.2878
Sault Ste. MarieWind2050RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2050 | 85.6537 | 92.2914 | 99.2871 | 106.2686 | 113.258
Sault Ste. MarieWind2055RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2055 | 85.7298 | 92.3856 | 99.4079 | 106.4084 | 113.4219
Sault Ste. MarieWind2060RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2060 | 86.184 | 92.9324 | 100.0678 | 107.1669 | 114.2784
Sault Ste. MarieWind2065RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2065 | 86.5619 | 93.3851 | 100.6068 | 107.7856 | 114.9711
Sault Ste. MarieWind2070RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2070 | 87.1007 | 94.0261 | 101.3679 | 108.6559 | 115.9467
Sault Ste. MarieWind2075RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2075 | 87.2615 | 94.2145 | 101.5901 | 108.9076 | 116.2298
Sault Ste. MarieWind2080RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2080 | 87.4222 | 94.4028 | 101.8122 | 109.1593 | 116.5128
Sault Ste. MarieWind2085RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2085 | 87.5576 | 94.5623 | 102.0033 | 109.3742 | 116.753
Sault Ste. MarieWind2090RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2090 | 87.693 | 94.7218 | 102.1944 | 109.5892 | 116.9932
Sault Ste. MarieWind2095RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2095 | 87.693 | 94.7218 | 102.1944 | 109.5892 | 116.9932
Sault Ste. MarieWind2100RCP8.5 | Sault Ste. Marie | Wind | RCP8.5 | 2100 | 87.693 | 94.7218 | 102.1944 | 109.5892 | 116.9932
ScarboroughIce Accretion2023RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
ScarboroughIce Accretion2025RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
ScarboroughIce Accretion2030RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
ScarboroughIce Accretion2035RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
ScarboroughIce Accretion2040RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
ScarboroughIce Accretion2045RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
ScarboroughIce Accretion2050RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
ScarboroughIce Accretion2055RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
ScarboroughIce Accretion2060RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
ScarboroughIce Accretion2065RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
ScarboroughIce Accretion2070RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
ScarboroughIce Accretion2075RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
ScarboroughIce Accretion2080RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
ScarboroughIce Accretion2085RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
ScarboroughIce Accretion2090RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
ScarboroughIce Accretion2095RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
ScarboroughIce Accretion2100RCP4.5 | Scarborough | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
ScarboroughIce Accretion2023RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
ScarboroughIce Accretion2025RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
ScarboroughIce Accretion2030RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
ScarboroughIce Accretion2035RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
ScarboroughIce Accretion2040RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
ScarboroughIce Accretion2045RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
ScarboroughIce Accretion2050RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
ScarboroughIce Accretion2055RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
ScarboroughIce Accretion2060RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
ScarboroughIce Accretion2065RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
ScarboroughIce Accretion2070RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
ScarboroughIce Accretion2075RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
ScarboroughIce Accretion2080RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
ScarboroughIce Accretion2085RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
ScarboroughIce Accretion2090RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
ScarboroughIce Accretion2095RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
ScarboroughIce Accretion2100RCP6.0 | Scarborough | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
ScarboroughIce Accretion2023RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
ScarboroughIce Accretion2025RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
ScarboroughIce Accretion2030RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
ScarboroughIce Accretion2035RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
ScarboroughIce Accretion2040RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
ScarboroughIce Accretion2045RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
ScarboroughIce Accretion2050RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
ScarboroughIce Accretion2055RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
ScarboroughIce Accretion2060RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
ScarboroughIce Accretion2065RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
ScarboroughIce Accretion2070RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
ScarboroughIce Accretion2075RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
ScarboroughIce Accretion2080RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
ScarboroughIce Accretion2085RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
ScarboroughIce Accretion2090RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
ScarboroughIce Accretion2095RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
ScarboroughIce Accretion2100RCP8.5 | Scarborough | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
ScarboroughWind2023RCP4.5 | Scarborough | Wind | RCP4.5 | 2023 | 83.0933 | 89.4586 | 96.1536 | 102.8535 | 109.5494
ScarboroughWind2025RCP4.5 | Scarborough | Wind | RCP4.5 | 2025 | 83.1085 | 89.4913 | 96.2064 | 102.9237 | 109.637
ScarboroughWind2030RCP4.5 | Scarborough | Wind | RCP4.5 | 2030 | 83.1237 | 89.524 | 96.2592 | 102.9939 | 109.7245
ScarboroughWind2035RCP4.5 | Scarborough | Wind | RCP4.5 | 2035 | 83.1389 | 89.5568 | 96.312 | 103.0641 | 109.8121
ScarboroughWind2040RCP4.5 | Scarborough | Wind | RCP4.5 | 2040 | 83.154 | 89.5895 | 96.3648 | 103.1343 | 109.8996
ScarboroughWind2045RCP4.5 | Scarborough | Wind | RCP4.5 | 2045 | 83.1692 | 89.6222 | 96.4176 | 103.2045 | 109.9872
ScarboroughWind2050RCP4.5 | Scarborough | Wind | RCP4.5 | 2050 | 83.2657 | 89.7568 | 96.599 | 103.4247 | 110.2499
ScarboroughWind2055RCP4.5 | Scarborough | Wind | RCP4.5 | 2055 | 83.3469 | 89.8585 | 96.7277 | 103.5746 | 110.425
ScarboroughWind2060RCP4.5 | Scarborough | Wind | RCP4.5 | 2060 | 83.4282 | 89.9603 | 96.8563 | 103.7246 | 110.6001
ScarboroughWind2065RCP4.5 | Scarborough | Wind | RCP4.5 | 2065 | 83.5094 | 90.0621 | 96.985 | 103.8746 | 110.7752
ScarboroughWind2070RCP4.5 | Scarborough | Wind | RCP4.5 | 2070 | 83.5906 | 90.1639 | 97.1136 | 104.0245 | 110.9503
ScarboroughWind2075RCP4.5 | Scarborough | Wind | RCP4.5 | 2075 | 83.7315 | 90.3454 | 97.3456 | 104.3002 | 111.2695
ScarboroughWind2080RCP4.5 | Scarborough | Wind | RCP4.5 | 2080 | 83.8725 | 90.5269 | 97.5776 | 104.5758 | 111.5887
ScarboroughWind2085RCP4.5 | Scarborough | Wind | RCP4.5 | 2085 | 84.0134 | 90.7085 | 97.8096 | 104.8514 | 111.9079
ScarboroughWind2090RCP4.5 | Scarborough | Wind | RCP4.5 | 2090 | 84.1543 | 90.89 | 98.0416 | 105.1271 | 112.2271
ScarboroughWind2095RCP4.5 | Scarborough | Wind | RCP4.5 | 2095 | 84.2952 | 91.0716 | 98.2736 | 105.4027 | 112.5463
ScarboroughWind2100RCP4.5 | Scarborough | Wind | RCP4.5 | 2100 | 84.4361 | 91.2531 | 98.5056 | 105.6783 | 112.8655
ScarboroughWind2023RCP6.0 | Scarborough | Wind | RCP6.0 | 2023 | 83.0933 | 89.4586 | 96.1536 | 102.8535 | 109.5494
ScarboroughWind2025RCP6.0 | Scarborough | Wind | RCP6.0 | 2025 | 83.1085 | 89.4913 | 96.2064 | 102.9237 | 109.637
ScarboroughWind2030RCP6.0 | Scarborough | Wind | RCP6.0 | 2030 | 83.1237 | 89.524 | 96.2592 | 102.9939 | 109.7245
ScarboroughWind2035RCP6.0 | Scarborough | Wind | RCP6.0 | 2035 | 83.1389 | 89.5568 | 96.312 | 103.0641 | 109.8121
ScarboroughWind2040RCP6.0 | Scarborough | Wind | RCP6.0 | 2040 | 83.154 | 89.5895 | 96.3648 | 103.1343 | 109.8996
ScarboroughWind2045RCP6.0 | Scarborough | Wind | RCP6.0 | 2045 | 83.1692 | 89.6222 | 96.4176 | 103.2045 | 109.9872
ScarboroughWind2050RCP6.0 | Scarborough | Wind | RCP6.0 | 2050 | 83.2657 | 89.7568 | 96.599 | 103.4247 | 110.2499
ScarboroughWind2055RCP6.0 | Scarborough | Wind | RCP6.0 | 2055 | 83.3469 | 89.8585 | 96.7277 | 103.5746 | 110.425
ScarboroughWind2060RCP6.0 | Scarborough | Wind | RCP6.0 | 2060 | 83.4282 | 89.9603 | 96.8563 | 103.7246 | 110.6001
ScarboroughWind2065RCP6.0 | Scarborough | Wind | RCP6.0 | 2065 | 83.5094 | 90.0621 | 96.985 | 103.8746 | 110.7752
ScarboroughWind2070RCP6.0 | Scarborough | Wind | RCP6.0 | 2070 | 83.5906 | 90.1639 | 97.1136 | 104.0245 | 110.9503
ScarboroughWind2075RCP6.0 | Scarborough | Wind | RCP6.0 | 2075 | 83.802 | 90.4362 | 97.4616 | 104.438 | 111.4291
ScarboroughWind2080RCP6.0 | Scarborough | Wind | RCP6.0 | 2080 | 84.0134 | 90.7085 | 97.8096 | 104.8514 | 111.9079
ScarboroughWind2085RCP6.0 | Scarborough | Wind | RCP6.0 | 2085 | 84.2248 | 90.9808 | 98.1576 | 105.2649 | 112.3867
ScarboroughWind2090RCP6.0 | Scarborough | Wind | RCP6.0 | 2090 | 84.8727 | 91.7888 | 99.168 | 106.4487 | 113.7483
ScarboroughWind2095RCP6.0 | Scarborough | Wind | RCP6.0 | 2095 | 85.3093 | 92.3244 | 99.8304 | 107.2191 | 114.6311
ScarboroughWind2100RCP6.0 | Scarborough | Wind | RCP6.0 | 2100 | 85.7459 | 92.8601 | 100.4928 | 107.9895 | 115.5139
ScarboroughWind2023RCP8.5 | Scarborough | Wind | RCP8.5 | 2023 | 83.0933 | 89.4586 | 96.1536 | 102.8535 | 109.5494
ScarboroughWind2025RCP8.5 | Scarborough | Wind | RCP8.5 | 2025 | 83.1237 | 89.524 | 96.2592 | 102.9939 | 109.7245
ScarboroughWind2030RCP8.5 | Scarborough | Wind | RCP8.5 | 2030 | 83.154 | 89.5895 | 96.3648 | 103.1343 | 109.8996
ScarboroughWind2035RCP8.5 | Scarborough | Wind | RCP8.5 | 2035 | 83.1844 | 89.655 | 96.4704 | 103.2747 | 110.0748
ScarboroughWind2040RCP8.5 | Scarborough | Wind | RCP8.5 | 2040 | 83.3198 | 89.8246 | 96.6848 | 103.5246 | 110.3666
ScarboroughWind2045RCP8.5 | Scarborough | Wind | RCP8.5 | 2045 | 83.4552 | 89.9942 | 96.8992 | 103.7746 | 110.6584
ScarboroughWind2050RCP8.5 | Scarborough | Wind | RCP8.5 | 2050 | 83.8725 | 90.5269 | 97.5776 | 104.5758 | 111.5887
ScarboroughWind2055RCP8.5 | Scarborough | Wind | RCP8.5 | 2055 | 84.1543 | 90.89 | 98.0416 | 105.1271 | 112.2271
ScarboroughWind2060RCP8.5 | Scarborough | Wind | RCP8.5 | 2060 | 84.8727 | 91.7888 | 99.168 | 106.4487 | 113.7483
ScarboroughWind2065RCP8.5 | Scarborough | Wind | RCP8.5 | 2065 | 85.3093 | 92.3244 | 99.8304 | 107.2191 | 114.6311
ScarboroughWind2070RCP8.5 | Scarborough | Wind | RCP8.5 | 2070 | 85.8757 | 93.0357 | 100.7264 | 108.2772 | 115.8495
ScarboroughWind2075RCP8.5 | Scarborough | Wind | RCP8.5 | 2075 | 86.0056 | 93.2113 | 100.96 | 108.5648 | 116.1852
ScarboroughWind2080RCP8.5 | Scarborough | Wind | RCP8.5 | 2080 | 86.1355 | 93.3869 | 101.1936 | 108.8524 | 116.5208
ScarboroughWind2085RCP8.5 | Scarborough | Wind | RCP8.5 | 2085 | 86.4132 | 93.7797 | 101.7312 | 109.5098 | 117.3033
ScarboroughWind2090RCP8.5 | Scarborough | Wind | RCP8.5 | 2090 | 86.6909 | 94.1725 | 102.2688 | 110.1672 | 118.0858
ScarboroughWind2095RCP8.5 | Scarborough | Wind | RCP8.5 | 2095 | 86.6909 | 94.1725 | 102.2688 | 110.1672 | 118.0858
ScarboroughWind2100RCP8.5 | Scarborough | Wind | RCP8.5 | 2100 | 86.6909 | 94.1725 | 102.2688 | 110.1672 | 118.0858
SchreiberIce Accretion2023RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2023 | 13.0889 | 15.6272 | 18.846 | 21.3163 | 23.7686
SchreiberIce Accretion2025RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2025 | 13.1035 | 15.6472 | 18.873 | 21.3468 | 23.8064
SchreiberIce Accretion2030RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2030 | 13.1181 | 15.6671 | 18.9 | 21.3773 | 23.8442
SchreiberIce Accretion2035RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2035 | 13.1327 | 15.687 | 18.927 | 21.4078 | 23.882
SchreiberIce Accretion2040RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2040 | 13.1473 | 15.7069 | 18.954 | 21.4384 | 23.9198
SchreiberIce Accretion2045RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2045 | 13.1619 | 15.7268 | 18.981 | 21.4689 | 23.9576
SchreiberIce Accretion2050RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2050 | 13.2317 | 15.8185 | 19.098 | 21.6051 | 24.1134
SchreiberIce Accretion2055RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2055 | 13.2868 | 15.8902 | 19.188 | 21.7109 | 24.2313
SchreiberIce Accretion2060RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2060 | 13.3419 | 15.9619 | 19.278 | 21.8167 | 24.3492
SchreiberIce Accretion2065RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2065 | 13.397 | 16.0336 | 19.368 | 21.9225 | 24.4672
SchreiberIce Accretion2070RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2070 | 13.4521 | 16.1053 | 19.458 | 22.0282 | 24.5851
SchreiberIce Accretion2075RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2075 | 13.4333 | 16.0879 | 19.44 | 22.0113 | 24.57
SchreiberIce Accretion2080RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2080 | 13.4145 | 16.0705 | 19.422 | 21.9943 | 24.5549
SchreiberIce Accretion2085RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2085 | 13.3957 | 16.053 | 19.404 | 21.9774 | 24.5398
SchreiberIce Accretion2090RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2090 | 13.3769 | 16.0356 | 19.386 | 21.9604 | 24.5246
SchreiberIce Accretion2095RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2095 | 13.3582 | 16.0182 | 19.368 | 21.9435 | 24.5095
SchreiberIce Accretion2100RCP4.5 | Schreiber | Ice Accretion | RCP4.5 | 2100 | 13.3394 | 16.0007 | 19.35 | 21.9265 | 24.4944
SchreiberIce Accretion2023RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2023 | 13.0889 | 15.6272 | 18.846 | 21.3163 | 23.7686
SchreiberIce Accretion2025RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2025 | 13.1035 | 15.6472 | 18.873 | 21.3468 | 23.8064
SchreiberIce Accretion2030RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2030 | 13.1181 | 15.6671 | 18.9 | 21.3773 | 23.8442
SchreiberIce Accretion2035RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2035 | 13.1327 | 15.687 | 18.927 | 21.4078 | 23.882
SchreiberIce Accretion2040RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2040 | 13.1473 | 15.7069 | 18.954 | 21.4384 | 23.9198
SchreiberIce Accretion2045RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2045 | 13.1619 | 15.7268 | 18.981 | 21.4689 | 23.9576
SchreiberIce Accretion2050RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2050 | 13.2317 | 15.8185 | 19.098 | 21.6051 | 24.1134
SchreiberIce Accretion2055RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2055 | 13.2868 | 15.8902 | 19.188 | 21.7109 | 24.2313
SchreiberIce Accretion2060RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2060 | 13.3419 | 15.9619 | 19.278 | 21.8167 | 24.3492
SchreiberIce Accretion2065RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2065 | 13.397 | 16.0336 | 19.368 | 21.9225 | 24.4672
SchreiberIce Accretion2070RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2070 | 13.4521 | 16.1053 | 19.458 | 22.0282 | 24.5851
SchreiberIce Accretion2075RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2075 | 13.4239 | 16.0792 | 19.431 | 22.0028 | 24.5624
SchreiberIce Accretion2080RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2080 | 13.3957 | 16.053 | 19.404 | 21.9774 | 24.5398
SchreiberIce Accretion2085RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2085 | 13.3676 | 16.0269 | 19.377 | 21.9519 | 24.5171
SchreiberIce Accretion2090RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2090 | 13.2016 | 15.8414 | 19.164 | 21.7163 | 24.26
SchreiberIce Accretion2095RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2095 | 13.0638 | 15.682 | 18.978 | 21.5062 | 24.0257
SchreiberIce Accretion2100RCP6.0 | Schreiber | Ice Accretion | RCP6.0 | 2100 | 12.926 | 15.5227 | 18.792 | 21.296 | 23.7913
SchreiberIce Accretion2023RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2023 | 13.0889 | 15.6272 | 18.846 | 21.3163 | 23.7686
SchreiberIce Accretion2025RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2025 | 13.1181 | 15.6671 | 18.9 | 21.3773 | 23.8442
SchreiberIce Accretion2030RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2030 | 13.1473 | 15.7069 | 18.954 | 21.4384 | 23.9198
SchreiberIce Accretion2035RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2035 | 13.1765 | 15.7468 | 19.008 | 21.4994 | 23.9954
SchreiberIce Accretion2040RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2040 | 13.2684 | 15.8663 | 19.158 | 21.6757 | 24.192
SchreiberIce Accretion2045RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2045 | 13.3602 | 15.9858 | 19.308 | 21.8519 | 24.3886
SchreiberIce Accretion2050RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2050 | 13.4145 | 16.0705 | 19.422 | 21.9943 | 24.5549
SchreiberIce Accretion2055RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2055 | 13.3769 | 16.0356 | 19.386 | 21.9604 | 24.5246
SchreiberIce Accretion2060RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2060 | 13.2016 | 15.8414 | 19.164 | 21.7163 | 24.26
SchreiberIce Accretion2065RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2065 | 13.0638 | 15.682 | 18.978 | 21.5062 | 24.0257
SchreiberIce Accretion2070RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2070 | 12.8968 | 15.5027 | 18.792 | 21.3028 | 23.814
SchreiberIce Accretion2075RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2075 | 12.8676 | 15.4828 | 18.792 | 21.3095 | 23.8367
SchreiberIce Accretion2080RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2080 | 12.8384 | 15.4629 | 18.792 | 21.3163 | 23.8594
SchreiberIce Accretion2085RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2085 | 12.7194 | 15.3359 | 18.639 | 21.1536 | 23.6779
SchreiberIce Accretion2090RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2090 | 12.6004 | 15.2089 | 18.486 | 20.9909 | 23.4965
SchreiberIce Accretion2095RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2095 | 12.6004 | 15.2089 | 18.486 | 20.9909 | 23.4965
SchreiberIce Accretion2100RCP8.5 | Schreiber | Ice Accretion | RCP8.5 | 2100 | 12.6004 | 15.2089 | 18.486 | 20.9909 | 23.4965
SchreiberWind2023RCP4.5 | Schreiber | Wind | RCP4.5 | 2023 | 81.3134 | 87.4987 | 93.9812 | 100.4895 | 106.9885
SchreiberWind2025RCP4.5 | Schreiber | Wind | RCP4.5 | 2025 | 81.4568 | 87.6808 | 94.2099 | 100.7577 | 107.2993
SchreiberWind2030RCP4.5 | Schreiber | Wind | RCP4.5 | 2030 | 81.6002 | 87.8629 | 94.4387 | 101.0259 | 107.6101
SchreiberWind2035RCP4.5 | Schreiber | Wind | RCP4.5 | 2035 | 81.7436 | 88.0451 | 94.6674 | 101.2941 | 107.9208
SchreiberWind2040RCP4.5 | Schreiber | Wind | RCP4.5 | 2040 | 81.887 | 88.2272 | 94.8961 | 101.5623 | 108.2316
SchreiberWind2045RCP4.5 | Schreiber | Wind | RCP4.5 | 2045 | 82.0304 | 88.4093 | 95.1249 | 101.8305 | 108.5424
SchreiberWind2050RCP4.5 | Schreiber | Wind | RCP4.5 | 2050 | 82.3751 | 88.838 | 95.66 | 102.4548 | 109.2582
SchreiberWind2055RCP4.5 | Schreiber | Wind | RCP4.5 | 2055 | 82.5764 | 89.0845 | 95.9665 | 102.8109 | 109.6633
SchreiberWind2060RCP4.5 | Schreiber | Wind | RCP4.5 | 2060 | 82.7777 | 89.331 | 96.2729 | 103.1669 | 110.0683
SchreiberWind2065RCP4.5 | Schreiber | Wind | RCP4.5 | 2065 | 82.979 | 89.5775 | 96.5794 | 103.523 | 110.4734
SchreiberWind2070RCP4.5 | Schreiber | Wind | RCP4.5 | 2070 | 83.1803 | 89.8241 | 96.8858 | 103.879 | 110.8785
SchreiberWind2075RCP4.5 | Schreiber | Wind | RCP4.5 | 2075 | 83.2804 | 89.9362 | 97.0096 | 104.0148 | 111.0267
SchreiberWind2080RCP4.5 | Schreiber | Wind | RCP4.5 | 2080 | 83.3805 | 90.0484 | 97.1333 | 104.1506 | 111.1749
SchreiberWind2085RCP4.5 | Schreiber | Wind | RCP4.5 | 2085 | 83.4806 | 90.1606 | 97.2571 | 104.2864 | 111.3232
SchreiberWind2090RCP4.5 | Schreiber | Wind | RCP4.5 | 2090 | 83.5807 | 90.2728 | 97.3809 | 104.4222 | 111.4714
SchreiberWind2095RCP4.5 | Schreiber | Wind | RCP4.5 | 2095 | 83.6808 | 90.385 | 97.5046 | 104.5579 | 111.6196
SchreiberWind2100RCP4.5 | Schreiber | Wind | RCP4.5 | 2100 | 83.7809 | 90.4972 | 97.6284 | 104.6937 | 111.7679
SchreiberWind2023RCP6.0 | Schreiber | Wind | RCP6.0 | 2023 | 81.3134 | 87.4987 | 93.9812 | 100.4895 | 106.9885
SchreiberWind2025RCP6.0 | Schreiber | Wind | RCP6.0 | 2025 | 81.4568 | 87.6808 | 94.2099 | 100.7577 | 107.2993
SchreiberWind2030RCP6.0 | Schreiber | Wind | RCP6.0 | 2030 | 81.6002 | 87.8629 | 94.4387 | 101.0259 | 107.6101
SchreiberWind2035RCP6.0 | Schreiber | Wind | RCP6.0 | 2035 | 81.7436 | 88.0451 | 94.6674 | 101.2941 | 107.9208
SchreiberWind2040RCP6.0 | Schreiber | Wind | RCP6.0 | 2040 | 81.887 | 88.2272 | 94.8961 | 101.5623 | 108.2316
SchreiberWind2045RCP6.0 | Schreiber | Wind | RCP6.0 | 2045 | 82.0304 | 88.4093 | 95.1249 | 101.8305 | 108.5424
SchreiberWind2050RCP6.0 | Schreiber | Wind | RCP6.0 | 2050 | 82.3751 | 88.838 | 95.66 | 102.4548 | 109.2582
SchreiberWind2055RCP6.0 | Schreiber | Wind | RCP6.0 | 2055 | 82.5764 | 89.0845 | 95.9665 | 102.8109 | 109.6633
SchreiberWind2060RCP6.0 | Schreiber | Wind | RCP6.0 | 2060 | 82.7777 | 89.331 | 96.2729 | 103.1669 | 110.0683
SchreiberWind2065RCP6.0 | Schreiber | Wind | RCP6.0 | 2065 | 82.979 | 89.5775 | 96.5794 | 103.523 | 110.4734
SchreiberWind2070RCP6.0 | Schreiber | Wind | RCP6.0 | 2070 | 83.1803 | 89.8241 | 96.8858 | 103.879 | 110.8785
SchreiberWind2075RCP6.0 | Schreiber | Wind | RCP6.0 | 2075 | 83.3305 | 89.9923 | 97.0714 | 104.0827 | 111.1008
SchreiberWind2080RCP6.0 | Schreiber | Wind | RCP6.0 | 2080 | 83.4806 | 90.1606 | 97.2571 | 104.2864 | 111.3232
SchreiberWind2085RCP6.0 | Schreiber | Wind | RCP6.0 | 2085 | 83.6308 | 90.3289 | 97.4427 | 104.49 | 111.5455
SchreiberWind2090RCP6.0 | Schreiber | Wind | RCP6.0 | 2090 | 83.8702 | 90.57 | 97.6817 | 104.7306 | 111.7857
SchreiberWind2095RCP6.0 | Schreiber | Wind | RCP6.0 | 2095 | 83.9595 | 90.6429 | 97.7349 | 104.7675 | 111.8036
SchreiberWind2100RCP6.0 | Schreiber | Wind | RCP6.0 | 2100 | 84.0488 | 90.7157 | 97.7882 | 104.8044 | 111.8215
SchreiberWind2023RCP8.5 | Schreiber | Wind | RCP8.5 | 2023 | 81.3134 | 87.4987 | 93.9812 | 100.4895 | 106.9885
SchreiberWind2025RCP8.5 | Schreiber | Wind | RCP8.5 | 2025 | 81.6002 | 87.8629 | 94.4387 | 101.0259 | 107.6101
SchreiberWind2030RCP8.5 | Schreiber | Wind | RCP8.5 | 2030 | 81.887 | 88.2272 | 94.8961 | 101.5623 | 108.2316
SchreiberWind2035RCP8.5 | Schreiber | Wind | RCP8.5 | 2035 | 82.1738 | 88.5914 | 95.3536 | 102.0988 | 108.8531
SchreiberWind2040RCP8.5 | Schreiber | Wind | RCP8.5 | 2040 | 82.5093 | 89.0023 | 95.8643 | 102.6922 | 109.5282
SchreiberWind2045RCP8.5 | Schreiber | Wind | RCP8.5 | 2045 | 82.8448 | 89.4132 | 96.3751 | 103.2856 | 110.2033
SchreiberWind2050RCP8.5 | Schreiber | Wind | RCP8.5 | 2050 | 83.3805 | 90.0484 | 97.1333 | 104.1506 | 111.1749
SchreiberWind2055RCP8.5 | Schreiber | Wind | RCP8.5 | 2055 | 83.5807 | 90.2728 | 97.3809 | 104.4222 | 111.4714
SchreiberWind2060RCP8.5 | Schreiber | Wind | RCP8.5 | 2060 | 83.8702 | 90.57 | 97.6817 | 104.7306 | 111.7857
SchreiberWind2065RCP8.5 | Schreiber | Wind | RCP8.5 | 2065 | 83.9595 | 90.6429 | 97.7349 | 104.7675 | 111.8036
SchreiberWind2070RCP8.5 | Schreiber | Wind | RCP8.5 | 2070 | 84.3058 | 91.013 | 98.1329 | 105.1933 | 112.2572
SchreiberWind2075RCP8.5 | Schreiber | Wind | RCP8.5 | 2075 | 84.5628 | 91.3102 | 98.4775 | 105.5822 | 112.693
SchreiberWind2080RCP8.5 | Schreiber | Wind | RCP8.5 | 2080 | 84.8199 | 91.6074 | 98.8222 | 105.9711 | 113.1288
SchreiberWind2085RCP8.5 | Schreiber | Wind | RCP8.5 | 2085 | 85.2338 | 92.1451 | 99.5131 | 106.7908 | 114.0772
SchreiberWind2090RCP8.5 | Schreiber | Wind | RCP8.5 | 2090 | 85.6478 | 92.6827 | 100.204 | 107.6105 | 115.0255
SchreiberWind2095RCP8.5 | Schreiber | Wind | RCP8.5 | 2095 | 85.6478 | 92.6827 | 100.204 | 107.6105 | 115.0255
SchreiberWind2100RCP8.5 | Schreiber | Wind | RCP8.5 | 2100 | 85.6478 | 92.6827 | 100.204 | 107.6105 | 115.0255
SeaforthIce Accretion2023RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2023 | 15.278 | 18.3513 | 22.242 | 25.208 | 28.1635
SeaforthIce Accretion2025RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2025 | 15.352 | 18.4456 | 22.363 | 25.3531 | 28.3298
SeaforthIce Accretion2030RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2030 | 15.426 | 18.54 | 22.484 | 25.4981 | 28.4962
SeaforthIce Accretion2035RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2035 | 15.5 | 18.6343 | 22.605 | 25.6431 | 28.6625
SeaforthIce Accretion2040RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2040 | 15.574 | 18.7287 | 22.726 | 25.7881 | 28.8288
SeaforthIce Accretion2045RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2045 | 15.648 | 18.823 | 22.847 | 25.9331 | 28.9951
SeaforthIce Accretion2050RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2050 | 15.7281 | 18.9466 | 23.0296 | 26.1527 | 29.2612
SeaforthIce Accretion2055RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2055 | 15.7342 | 18.9758 | 23.0912 | 26.2273 | 29.361
SeaforthIce Accretion2060RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2060 | 15.7403 | 19.005 | 23.1528 | 26.3019 | 29.4608
SeaforthIce Accretion2065RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2065 | 15.7464 | 19.0342 | 23.2144 | 26.3765 | 29.5606
SeaforthIce Accretion2070RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2070 | 15.7526 | 19.0634 | 23.276 | 26.451 | 29.6604
SeaforthIce Accretion2075RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2075 | 15.7041 | 19.033 | 23.2613 | 26.4552 | 29.6743
SeaforthIce Accretion2080RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2080 | 15.6556 | 19.0026 | 23.2467 | 26.4593 | 29.6881
SeaforthIce Accretion2085RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2085 | 15.6071 | 18.9721 | 23.232 | 26.4635 | 29.702
SeaforthIce Accretion2090RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2090 | 15.5587 | 18.9417 | 23.2173 | 26.4676 | 29.7158
SeaforthIce Accretion2095RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2095 | 15.5102 | 18.9113 | 23.2027 | 26.4718 | 29.7297
SeaforthIce Accretion2100RCP4.5 | Seaforth | Ice Accretion | RCP4.5 | 2100 | 15.4617 | 18.8808 | 23.188 | 26.4759 | 29.7436
SeaforthIce Accretion2023RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2023 | 15.278 | 18.3513 | 22.242 | 25.208 | 28.1635
SeaforthIce Accretion2025RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2025 | 15.352 | 18.4456 | 22.363 | 25.3531 | 28.3298
SeaforthIce Accretion2030RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2030 | 15.426 | 18.54 | 22.484 | 25.4981 | 28.4962
SeaforthIce Accretion2035RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2035 | 15.5 | 18.6343 | 22.605 | 25.6431 | 28.6625
SeaforthIce Accretion2040RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2040 | 15.574 | 18.7287 | 22.726 | 25.7881 | 28.8288
SeaforthIce Accretion2045RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2045 | 15.648 | 18.823 | 22.847 | 25.9331 | 28.9951
SeaforthIce Accretion2050RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2050 | 15.7281 | 18.9466 | 23.0296 | 26.1527 | 29.2612
SeaforthIce Accretion2055RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2055 | 15.7342 | 18.9758 | 23.0912 | 26.2273 | 29.361
SeaforthIce Accretion2060RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2060 | 15.7403 | 19.005 | 23.1528 | 26.3019 | 29.4608
SeaforthIce Accretion2065RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2065 | 15.7464 | 19.0342 | 23.2144 | 26.3765 | 29.5606
SeaforthIce Accretion2070RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2070 | 15.7526 | 19.0634 | 23.276 | 26.451 | 29.6604
SeaforthIce Accretion2075RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2075 | 15.6798 | 19.0178 | 23.254 | 26.4573 | 29.6812
SeaforthIce Accretion2080RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2080 | 15.6071 | 18.9721 | 23.232 | 26.4635 | 29.702
SeaforthIce Accretion2085RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2085 | 15.5344 | 18.9265 | 23.21 | 26.4697 | 29.7228
SeaforthIce Accretion2090RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2090 | 15.2066 | 18.6191 | 22.9167 | 26.1859 | 29.4479
SeaforthIce Accretion2095RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2095 | 14.9514 | 18.3574 | 22.6453 | 25.8958 | 29.1522
SeaforthIce Accretion2100RCP6.0 | Seaforth | Ice Accretion | RCP6.0 | 2100 | 14.6963 | 18.0957 | 22.374 | 25.6058 | 28.8565
SeaforthIce Accretion2023RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2023 | 15.278 | 18.3513 | 22.242 | 25.208 | 28.1635
SeaforthIce Accretion2025RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2025 | 15.426 | 18.54 | 22.484 | 25.4981 | 28.4962
SeaforthIce Accretion2030RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2030 | 15.574 | 18.7287 | 22.726 | 25.7881 | 28.8288
SeaforthIce Accretion2035RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2035 | 15.7219 | 18.9174 | 22.968 | 26.0781 | 29.1614
SeaforthIce Accretion2040RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2040 | 15.7322 | 18.9661 | 23.0707 | 26.2024 | 29.3278
SeaforthIce Accretion2045RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2045 | 15.7424 | 19.0147 | 23.1733 | 26.3267 | 29.4941
SeaforthIce Accretion2050RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2050 | 15.6556 | 19.0026 | 23.2467 | 26.4593 | 29.6881
SeaforthIce Accretion2055RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2055 | 15.5587 | 18.9417 | 23.2173 | 26.4676 | 29.7158
SeaforthIce Accretion2060RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2060 | 15.2066 | 18.6191 | 22.9167 | 26.1859 | 29.4479
SeaforthIce Accretion2065RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2065 | 14.9514 | 18.3574 | 22.6453 | 25.8958 | 29.1522
SeaforthIce Accretion2070RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2070 | 14.2268 | 17.5661 | 21.7727 | 24.9512 | 28.1358
SeaforthIce Accretion2075RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2075 | 13.7573 | 17.0366 | 21.1713 | 24.2965 | 27.4151
SeaforthIce Accretion2080RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2080 | 13.2879 | 16.507 | 20.57 | 23.6419 | 26.6944
SeaforthIce Accretion2085RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2085 | 12.599 | 15.6945 | 19.602 | 22.548 | 25.4885
SeaforthIce Accretion2090RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2090 | 11.9101 | 14.8819 | 18.634 | 21.4542 | 24.2827
SeaforthIce Accretion2095RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2095 | 11.9101 | 14.8819 | 18.634 | 21.4542 | 24.2827
SeaforthIce Accretion2100RCP8.5 | Seaforth | Ice Accretion | RCP8.5 | 2100 | 11.9101 | 14.8819 | 18.634 | 21.4542 | 24.2827
SeaforthWind2023RCP4.5 | Seaforth | Wind | RCP4.5 | 2023 | 85.2136 | 91.8691 | 98.8918 | 105.8981 | 112.9042
SeaforthWind2025RCP4.5 | Seaforth | Wind | RCP4.5 | 2025 | 85.2588 | 91.9223 | 98.9555 | 105.9698 | 112.9862
SeaforthWind2030RCP4.5 | Seaforth | Wind | RCP4.5 | 2030 | 85.3039 | 91.9754 | 99.0192 | 106.0414 | 113.0681
SeaforthWind2035RCP4.5 | Seaforth | Wind | RCP4.5 | 2035 | 85.349 | 92.0286 | 99.0829 | 106.1131 | 113.15
SeaforthWind2040RCP4.5 | Seaforth | Wind | RCP4.5 | 2040 | 85.3942 | 92.0818 | 99.1466 | 106.1847 | 113.2319
SeaforthWind2045RCP4.5 | Seaforth | Wind | RCP4.5 | 2045 | 85.4393 | 92.1349 | 99.2103 | 106.2564 | 113.3139
SeaforthWind2050RCP4.5 | Seaforth | Wind | RCP4.5 | 2050 | 85.4929 | 92.1936 | 99.274 | 106.3259 | 113.3869
SeaforthWind2055RCP4.5 | Seaforth | Wind | RCP4.5 | 2055 | 85.5013 | 92.199 | 99.274 | 106.3238 | 113.3779
SeaforthWind2060RCP4.5 | Seaforth | Wind | RCP4.5 | 2060 | 85.5098 | 92.2045 | 99.274 | 106.3217 | 113.369
SeaforthWind2065RCP4.5 | Seaforth | Wind | RCP4.5 | 2065 | 85.5183 | 92.21 | 99.274 | 106.3197 | 113.36
SeaforthWind2070RCP4.5 | Seaforth | Wind | RCP4.5 | 2070 | 85.5267 | 92.2155 | 99.274 | 106.3176 | 113.3511
SeaforthWind2075RCP4.5 | Seaforth | Wind | RCP4.5 | 2075 | 85.6212 | 92.3446 | 99.4488 | 106.5308 | 113.6043
SeaforthWind2080RCP4.5 | Seaforth | Wind | RCP4.5 | 2080 | 85.7157 | 92.4737 | 99.6235 | 106.744 | 113.8576
SeaforthWind2085RCP4.5 | Seaforth | Wind | RCP4.5 | 2085 | 85.8102 | 92.6028 | 99.7983 | 106.9572 | 114.1108
SeaforthWind2090RCP4.5 | Seaforth | Wind | RCP4.5 | 2090 | 85.9047 | 92.7319 | 99.9731 | 107.1704 | 114.364
SeaforthWind2095RCP4.5 | Seaforth | Wind | RCP4.5 | 2095 | 85.9992 | 92.861 | 100.1478 | 107.3836 | 114.6173
SeaforthWind2100RCP4.5 | Seaforth | Wind | RCP4.5 | 2100 | 86.0937 | 92.9901 | 100.3226 | 107.5968 | 114.8705
SeaforthWind2023RCP6.0 | Seaforth | Wind | RCP6.0 | 2023 | 85.2136 | 91.8691 | 98.8918 | 105.8981 | 112.9042
SeaforthWind2025RCP6.0 | Seaforth | Wind | RCP6.0 | 2025 | 85.2588 | 91.9223 | 98.9555 | 105.9698 | 112.9862
SeaforthWind2030RCP6.0 | Seaforth | Wind | RCP6.0 | 2030 | 85.3039 | 91.9754 | 99.0192 | 106.0414 | 113.0681
SeaforthWind2035RCP6.0 | Seaforth | Wind | RCP6.0 | 2035 | 85.349 | 92.0286 | 99.0829 | 106.1131 | 113.15
SeaforthWind2040RCP6.0 | Seaforth | Wind | RCP6.0 | 2040 | 85.3942 | 92.0818 | 99.1466 | 106.1847 | 113.2319
SeaforthWind2045RCP6.0 | Seaforth | Wind | RCP6.0 | 2045 | 85.4393 | 92.1349 | 99.2103 | 106.2564 | 113.3139
SeaforthWind2050RCP6.0 | Seaforth | Wind | RCP6.0 | 2050 | 85.4929 | 92.1936 | 99.274 | 106.3259 | 113.3869
SeaforthWind2055RCP6.0 | Seaforth | Wind | RCP6.0 | 2055 | 85.5013 | 92.199 | 99.274 | 106.3238 | 113.3779
SeaforthWind2060RCP6.0 | Seaforth | Wind | RCP6.0 | 2060 | 85.5098 | 92.2045 | 99.274 | 106.3217 | 113.369
SeaforthWind2065RCP6.0 | Seaforth | Wind | RCP6.0 | 2065 | 85.5183 | 92.21 | 99.274 | 106.3197 | 113.36
SeaforthWind2070RCP6.0 | Seaforth | Wind | RCP6.0 | 2070 | 85.5267 | 92.2155 | 99.274 | 106.3176 | 113.3511
SeaforthWind2075RCP6.0 | Seaforth | Wind | RCP6.0 | 2075 | 85.6685 | 92.4091 | 99.5361 | 106.6374 | 113.731
SeaforthWind2080RCP6.0 | Seaforth | Wind | RCP6.0 | 2080 | 85.8102 | 92.6028 | 99.7983 | 106.9572 | 114.1108
SeaforthWind2085RCP6.0 | Seaforth | Wind | RCP6.0 | 2085 | 85.9519 | 92.7965 | 100.0605 | 107.277 | 114.4907
SeaforthWind2090RCP6.0 | Seaforth | Wind | RCP6.0 | 2090 | 86.4688 | 93.4519 | 100.8877 | 108.2505 | 115.619
SeaforthWind2095RCP6.0 | Seaforth | Wind | RCP6.0 | 2095 | 86.844 | 93.9137 | 101.4529 | 108.9041 | 116.3676
SeaforthWind2100RCP6.0 | Seaforth | Wind | RCP6.0 | 2100 | 87.2192 | 94.3755 | 102.018 | 109.5577 | 117.1161
SeaforthWind2023RCP8.5 | Seaforth | Wind | RCP8.5 | 2023 | 85.2136 | 91.8691 | 98.8918 | 105.8981 | 112.9042
SeaforthWind2025RCP8.5 | Seaforth | Wind | RCP8.5 | 2025 | 85.3039 | 91.9754 | 99.0192 | 106.0414 | 113.0681
SeaforthWind2030RCP8.5 | Seaforth | Wind | RCP8.5 | 2030 | 85.3942 | 92.0818 | 99.1466 | 106.1847 | 113.2319
SeaforthWind2035RCP8.5 | Seaforth | Wind | RCP8.5 | 2035 | 85.4844 | 92.1881 | 99.274 | 106.328 | 113.3958
SeaforthWind2040RCP8.5 | Seaforth | Wind | RCP8.5 | 2040 | 85.4985 | 92.1972 | 99.274 | 106.3245 | 113.3809
SeaforthWind2045RCP8.5 | Seaforth | Wind | RCP8.5 | 2045 | 85.5126 | 92.2063 | 99.274 | 106.321 | 113.366
SeaforthWind2050RCP8.5 | Seaforth | Wind | RCP8.5 | 2050 | 85.7157 | 92.4737 | 99.6235 | 106.744 | 113.8576
SeaforthWind2055RCP8.5 | Seaforth | Wind | RCP8.5 | 2055 | 85.9047 | 92.7319 | 99.9731 | 107.1704 | 114.364
SeaforthWind2060RCP8.5 | Seaforth | Wind | RCP8.5 | 2060 | 86.4688 | 93.4519 | 100.8877 | 108.2505 | 115.619
SeaforthWind2065RCP8.5 | Seaforth | Wind | RCP8.5 | 2065 | 86.844 | 93.9137 | 101.4529 | 108.9041 | 116.3676
SeaforthWind2070RCP8.5 | Seaforth | Wind | RCP8.5 | 2070 | 87.4956 | 94.737 | 102.4917 | 110.124 | 117.7789
SeaforthWind2075RCP8.5 | Seaforth | Wind | RCP8.5 | 2075 | 87.772 | 95.0985 | 102.9653 | 110.6902 | 118.4418
SeaforthWind2080RCP8.5 | Seaforth | Wind | RCP8.5 | 2080 | 88.0484 | 95.46 | 103.439 | 111.2565 | 119.1047
SeaforthWind2085RCP8.5 | Seaforth | Wind | RCP8.5 | 2085 | 88.2642 | 95.7471 | 103.8163 | 111.7074 | 119.6298
SeaforthWind2090RCP8.5 | Seaforth | Wind | RCP8.5 | 2090 | 88.48 | 96.0342 | 104.1936 | 112.1583 | 120.1549
SeaforthWind2095RCP8.5 | Seaforth | Wind | RCP8.5 | 2095 | 88.48 | 96.0342 | 104.1936 | 112.1583 | 120.1549
SeaforthWind2100RCP8.5 | Seaforth | Wind | RCP8.5 | 2100 | 88.48 | 96.0342 | 104.1936 | 112.1583 | 120.1549
ShelburneIce Accretion2023RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2023 | 15.4005 | 18.4791 | 22.396 | 25.3821 | 28.3576
ShelburneIce Accretion2025RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2025 | 15.4209 | 18.5156 | 22.451 | 25.4525 | 28.4407
ShelburneIce Accretion2030RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2030 | 15.4413 | 18.5522 | 22.506 | 25.5229 | 28.5239
ShelburneIce Accretion2035RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2035 | 15.4617 | 18.5887 | 22.561 | 25.5934 | 28.607
ShelburneIce Accretion2040RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2040 | 15.4821 | 18.6252 | 22.616 | 25.6638 | 28.6902
ShelburneIce Accretion2045RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2045 | 15.5025 | 18.6617 | 22.671 | 25.7342 | 28.7734
ShelburneIce Accretion2050RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2050 | 15.4893 | 18.6727 | 22.7128 | 25.7997 | 28.8676
ShelburneIce Accretion2055RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2055 | 15.4556 | 18.6471 | 22.6996 | 25.7947 | 28.8787
ShelburneIce Accretion2060RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2060 | 15.4219 | 18.6215 | 22.6864 | 25.7898 | 28.8898
ShelburneIce Accretion2065RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2065 | 15.3882 | 18.596 | 22.6732 | 25.7848 | 28.9009
ShelburneIce Accretion2070RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2070 | 15.3545 | 18.5704 | 22.66 | 25.7798 | 28.912
ShelburneIce Accretion2075RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2075 | 15.3341 | 18.5735 | 22.6893 | 25.8295 | 28.9813
ShelburneIce Accretion2080RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2080 | 15.3137 | 18.5765 | 22.7187 | 25.8793 | 29.0506
ShelburneIce Accretion2085RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2085 | 15.2933 | 18.5795 | 22.748 | 25.929 | 29.1199
ShelburneIce Accretion2090RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2090 | 15.2729 | 18.5826 | 22.7773 | 25.9787 | 29.1892
ShelburneIce Accretion2095RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2095 | 15.2525 | 18.5856 | 22.8067 | 26.0284 | 29.2585
ShelburneIce Accretion2100RCP4.5 | Shelburne | Ice Accretion | RCP4.5 | 2100 | 15.2321 | 18.5887 | 22.836 | 26.0781 | 29.3278
ShelburneIce Accretion2023RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2023 | 15.4005 | 18.4791 | 22.396 | 25.3821 | 28.3576
ShelburneIce Accretion2025RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2025 | 15.4209 | 18.5156 | 22.451 | 25.4525 | 28.4407
ShelburneIce Accretion2030RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2030 | 15.4413 | 18.5522 | 22.506 | 25.5229 | 28.5239
ShelburneIce Accretion2035RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2035 | 15.4617 | 18.5887 | 22.561 | 25.5934 | 28.607
ShelburneIce Accretion2040RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2040 | 15.4821 | 18.6252 | 22.616 | 25.6638 | 28.6902
ShelburneIce Accretion2045RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2045 | 15.5025 | 18.6617 | 22.671 | 25.7342 | 28.7734
ShelburneIce Accretion2050RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2050 | 15.4893 | 18.6727 | 22.7128 | 25.7997 | 28.8676
ShelburneIce Accretion2055RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2055 | 15.4556 | 18.6471 | 22.6996 | 25.7947 | 28.8787
ShelburneIce Accretion2060RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2060 | 15.4219 | 18.6215 | 22.6864 | 25.7898 | 28.8898
ShelburneIce Accretion2065RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2065 | 15.3882 | 18.596 | 22.6732 | 25.7848 | 28.9009
ShelburneIce Accretion2070RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2070 | 15.3545 | 18.5704 | 22.66 | 25.7798 | 28.912
ShelburneIce Accretion2075RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2075 | 15.3239 | 18.575 | 22.704 | 25.8544 | 29.0159
ShelburneIce Accretion2080RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2080 | 15.2933 | 18.5795 | 22.748 | 25.929 | 29.1199
ShelburneIce Accretion2085RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2085 | 15.2627 | 18.5841 | 22.792 | 26.0036 | 29.2238
ShelburneIce Accretion2090RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2090 | 15.0331 | 18.3939 | 22.6453 | 25.8875 | 29.1245
ShelburneIce Accretion2095RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2095 | 14.834 | 18.1991 | 22.4547 | 25.697 | 28.9212
ShelburneIce Accretion2100RCP6.0 | Shelburne | Ice Accretion | RCP6.0 | 2100 | 14.635 | 18.0044 | 22.264 | 25.5064 | 28.7179
ShelburneIce Accretion2023RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2023 | 15.4005 | 18.4791 | 22.396 | 25.3821 | 28.3576
ShelburneIce Accretion2025RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2025 | 15.4413 | 18.5522 | 22.506 | 25.5229 | 28.5239
ShelburneIce Accretion2030RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2030 | 15.4821 | 18.6252 | 22.616 | 25.6638 | 28.6902
ShelburneIce Accretion2035RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2035 | 15.5229 | 18.6982 | 22.726 | 25.8047 | 28.8565
ShelburneIce Accretion2040RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2040 | 15.4668 | 18.6556 | 22.704 | 25.7964 | 28.875
ShelburneIce Accretion2045RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2045 | 15.4107 | 18.613 | 22.682 | 25.7881 | 28.8935
ShelburneIce Accretion2050RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2050 | 15.3137 | 18.5765 | 22.7187 | 25.8793 | 29.0506
ShelburneIce Accretion2055RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2055 | 15.2729 | 18.5826 | 22.7773 | 25.9787 | 29.1892
ShelburneIce Accretion2060RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2060 | 15.0331 | 18.3939 | 22.6453 | 25.8875 | 29.1245
ShelburneIce Accretion2065RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2065 | 14.834 | 18.1991 | 22.4547 | 25.697 | 28.9212
ShelburneIce Accretion2070RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2070 | 14.2778 | 17.6087 | 21.8167 | 25.0174 | 28.2005
ShelburneIce Accretion2075RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2075 | 13.9206 | 17.2131 | 21.3693 | 24.5285 | 27.683
ShelburneIce Accretion2080RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2080 | 13.5634 | 16.8175 | 20.922 | 24.0396 | 27.1656
ShelburneIce Accretion2085RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2085 | 12.9817 | 16.1601 | 20.174 | 23.2192 | 26.2647
ShelburneIce Accretion2090RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2090 | 12.4 | 15.5027 | 19.426 | 22.3989 | 25.3638
ShelburneIce Accretion2095RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2095 | 12.4 | 15.5027 | 19.426 | 22.3989 | 25.3638
ShelburneIce Accretion2100RCP8.5 | Shelburne | Ice Accretion | RCP8.5 | 2100 | 12.4 | 15.5027 | 19.426 | 22.3989 | 25.3638
ShelburneWind2023RCP4.5 | Shelburne | Wind | RCP4.5 | 2023 | 80.5608 | 86.7841 | 93.3348 | 99.8782 | 106.4229
ShelburneWind2025RCP4.5 | Shelburne | Wind | RCP4.5 | 2025 | 80.5689 | 86.7985 | 93.3581 | 99.908 | 106.4617
ShelburneWind2030RCP4.5 | Shelburne | Wind | RCP4.5 | 2030 | 80.5769 | 86.8129 | 93.3813 | 99.9379 | 106.5006
ShelburneWind2035RCP4.5 | Shelburne | Wind | RCP4.5 | 2035 | 80.5849 | 86.8273 | 93.4046 | 99.9677 | 106.5395
ShelburneWind2040RCP4.5 | Shelburne | Wind | RCP4.5 | 2040 | 80.593 | 86.8417 | 93.4278 | 99.9976 | 106.5784
ShelburneWind2045RCP4.5 | Shelburne | Wind | RCP4.5 | 2045 | 80.601 | 86.8561 | 93.4511 | 100.0275 | 106.6172
ShelburneWind2050RCP4.5 | Shelburne | Wind | RCP4.5 | 2050 | 80.6636 | 86.9294 | 93.5375 | 100.125 | 106.7282
ShelburneWind2055RCP4.5 | Shelburne | Wind | RCP4.5 | 2055 | 80.7182 | 86.9882 | 93.6008 | 100.1926 | 106.8003
ShelburneWind2060RCP4.5 | Shelburne | Wind | RCP4.5 | 2060 | 80.7728 | 87.047 | 93.664 | 100.2603 | 106.8724
ShelburneWind2065RCP4.5 | Shelburne | Wind | RCP4.5 | 2065 | 80.8274 | 87.1058 | 93.7273 | 100.328 | 106.9445
ShelburneWind2070RCP4.5 | Shelburne | Wind | RCP4.5 | 2070 | 80.8821 | 87.1646 | 93.7905 | 100.3956 | 107.0166
ShelburneWind2075RCP4.5 | Shelburne | Wind | RCP4.5 | 2075 | 80.9503 | 87.2569 | 93.9145 | 100.5482 | 107.1951
ShelburneWind2080RCP4.5 | Shelburne | Wind | RCP4.5 | 2080 | 81.0186 | 87.3491 | 94.0385 | 100.7008 | 107.3735
ShelburneWind2085RCP4.5 | Shelburne | Wind | RCP4.5 | 2085 | 81.0868 | 87.4414 | 94.1625 | 100.8534 | 107.552
ShelburneWind2090RCP4.5 | Shelburne | Wind | RCP4.5 | 2090 | 81.1551 | 87.5336 | 94.2865 | 101.006 | 107.7305
ShelburneWind2095RCP4.5 | Shelburne | Wind | RCP4.5 | 2095 | 81.2233 | 87.6259 | 94.4105 | 101.1585 | 107.9089
ShelburneWind2100RCP4.5 | Shelburne | Wind | RCP4.5 | 2100 | 81.2916 | 87.7182 | 94.5345 | 101.3111 | 108.0874
ShelburneWind2023RCP6.0 | Shelburne | Wind | RCP6.0 | 2023 | 80.5608 | 86.7841 | 93.3348 | 99.8782 | 106.4229
ShelburneWind2025RCP6.0 | Shelburne | Wind | RCP6.0 | 2025 | 80.5689 | 86.7985 | 93.3581 | 99.908 | 106.4617
ShelburneWind2030RCP6.0 | Shelburne | Wind | RCP6.0 | 2030 | 80.5769 | 86.8129 | 93.3813 | 99.9379 | 106.5006
ShelburneWind2035RCP6.0 | Shelburne | Wind | RCP6.0 | 2035 | 80.5849 | 86.8273 | 93.4046 | 99.9677 | 106.5395
ShelburneWind2040RCP6.0 | Shelburne | Wind | RCP6.0 | 2040 | 80.593 | 86.8417 | 93.4278 | 99.9976 | 106.5784
ShelburneWind2045RCP6.0 | Shelburne | Wind | RCP6.0 | 2045 | 80.601 | 86.8561 | 93.4511 | 100.0275 | 106.6172
ShelburneWind2050RCP6.0 | Shelburne | Wind | RCP6.0 | 2050 | 80.6636 | 86.9294 | 93.5375 | 100.125 | 106.7282
ShelburneWind2055RCP6.0 | Shelburne | Wind | RCP6.0 | 2055 | 80.7182 | 86.9882 | 93.6008 | 100.1926 | 106.8003
ShelburneWind2060RCP6.0 | Shelburne | Wind | RCP6.0 | 2060 | 80.7728 | 87.047 | 93.664 | 100.2603 | 106.8724
ShelburneWind2065RCP6.0 | Shelburne | Wind | RCP6.0 | 2065 | 80.8274 | 87.1058 | 93.7273 | 100.328 | 106.9445
ShelburneWind2070RCP6.0 | Shelburne | Wind | RCP6.0 | 2070 | 80.8821 | 87.1646 | 93.7905 | 100.3956 | 107.0166
ShelburneWind2075RCP6.0 | Shelburne | Wind | RCP6.0 | 2075 | 80.9844 | 87.303 | 93.9765 | 100.6245 | 107.2843
ShelburneWind2080RCP6.0 | Shelburne | Wind | RCP6.0 | 2080 | 81.0868 | 87.4414 | 94.1625 | 100.8534 | 107.552
ShelburneWind2085RCP6.0 | Shelburne | Wind | RCP6.0 | 2085 | 81.1892 | 87.5798 | 94.3485 | 101.0823 | 107.8197
ShelburneWind2090RCP6.0 | Shelburne | Wind | RCP6.0 | 2090 | 81.6744 | 88.191 | 95.1142 | 101.9845 | 108.8543
ShelburneWind2095RCP6.0 | Shelburne | Wind | RCP6.0 | 2095 | 82.0572 | 88.6638 | 95.6939 | 102.6578 | 109.6211
ShelburneWind2100RCP6.0 | Shelburne | Wind | RCP6.0 | 2100 | 82.4399 | 89.1366 | 96.2736 | 103.3312 | 110.388
ShelburneWind2023RCP8.5 | Shelburne | Wind | RCP8.5 | 2023 | 80.5608 | 86.7841 | 93.3348 | 99.8782 | 106.4229
ShelburneWind2025RCP8.5 | Shelburne | Wind | RCP8.5 | 2025 | 80.5769 | 86.8129 | 93.3813 | 99.9379 | 106.5006
ShelburneWind2030RCP8.5 | Shelburne | Wind | RCP8.5 | 2030 | 80.593 | 86.8417 | 93.4278 | 99.9976 | 106.5784
ShelburneWind2035RCP8.5 | Shelburne | Wind | RCP8.5 | 2035 | 80.609 | 86.8706 | 93.4743 | 100.0573 | 106.6561
ShelburneWind2040RCP8.5 | Shelburne | Wind | RCP8.5 | 2040 | 80.7 | 86.9686 | 93.5797 | 100.1701 | 106.7763
ShelburneWind2045RCP8.5 | Shelburne | Wind | RCP8.5 | 2045 | 80.791 | 87.0666 | 93.6851 | 100.2829 | 106.8964
ShelburneWind2050RCP8.5 | Shelburne | Wind | RCP8.5 | 2050 | 81.0186 | 87.3491 | 94.0385 | 100.7008 | 107.3735
ShelburneWind2055RCP8.5 | Shelburne | Wind | RCP8.5 | 2055 | 81.1551 | 87.5336 | 94.2865 | 101.006 | 107.7305
ShelburneWind2060RCP8.5 | Shelburne | Wind | RCP8.5 | 2060 | 81.6744 | 88.191 | 95.1142 | 101.9845 | 108.8543
ShelburneWind2065RCP8.5 | Shelburne | Wind | RCP8.5 | 2065 | 82.0572 | 88.6638 | 95.6939 | 102.6578 | 109.6211
ShelburneWind2070RCP8.5 | Shelburne | Wind | RCP8.5 | 2070 | 82.6514 | 89.4076 | 96.6208 | 103.7359 | 110.858
ShelburneWind2075RCP8.5 | Shelburne | Wind | RCP8.5 | 2075 | 82.8629 | 89.6786 | 96.968 | 104.1405 | 111.3281
ShelburneWind2080RCP8.5 | Shelburne | Wind | RCP8.5 | 2080 | 83.0743 | 89.9496 | 97.3152 | 104.5452 | 111.7981
ShelburneWind2085RCP8.5 | Shelburne | Wind | RCP8.5 | 2085 | 83.251 | 90.1658 | 97.5803 | 104.8537 | 112.1533
ShelburneWind2090RCP8.5 | Shelburne | Wind | RCP8.5 | 2090 | 83.4277 | 90.3821 | 97.8453 | 105.1622 | 112.5084
ShelburneWind2095RCP8.5 | Shelburne | Wind | RCP8.5 | 2095 | 83.4277 | 90.3821 | 97.8453 | 105.1622 | 112.5084
ShelburneWind2100RCP8.5 | Shelburne | Wind | RCP8.5 | 2100 | 83.4277 | 90.3821 | 97.8453 | 105.1622 | 112.5084
SimcoeIce Accretion2023RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
SimcoeIce Accretion2025RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2025 | 22.9175 | 27.5192 | 33.3427 | 37.7989 | 42.2402
SimcoeIce Accretion2030RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2030 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
SimcoeIce Accretion2035RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2035 | 22.6651 | 27.2464 | 33.048 | 37.4787 | 41.8975
SimcoeIce Accretion2040RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2040 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
SimcoeIce Accretion2045RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2045 | 22.4127 | 26.9736 | 32.7533 | 37.1585 | 41.5548
SimcoeIce Accretion2050RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2050 | 21.7945 | 26.2954 | 31.9872 | 36.3223 | 40.6466
SimcoeIce Accretion2055RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2055 | 21.3024 | 25.7536 | 31.3684 | 35.6461 | 39.9097
SimcoeIce Accretion2060RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2060 | 20.8103 | 25.2117 | 30.7496 | 34.9699 | 39.1729
SimcoeIce Accretion2065RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2065 | 20.3181 | 24.6699 | 30.1308 | 34.2937 | 38.436
SimcoeIce Accretion2070RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2070 | 19.826 | 24.1281 | 29.512 | 33.6175 | 37.6992
SimcoeIce Accretion2075RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2075 | 19.5895 | 23.8647 | 29.2117 | 33.2909 | 37.3422
SimcoeIce Accretion2080RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2080 | 19.3529 | 23.6013 | 28.9113 | 32.9644 | 36.9852
SimcoeIce Accretion2085RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2085 | 19.1163 | 23.3379 | 28.611 | 32.6378 | 36.6282
SimcoeIce Accretion2090RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2090 | 18.8797 | 23.0746 | 28.3107 | 32.3112 | 36.2712
SimcoeIce Accretion2095RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2095 | 18.6431 | 22.8112 | 28.0103 | 31.9846 | 35.9142
SimcoeIce Accretion2100RCP4.5 | Simcoe | Ice Accretion | RCP4.5 | 2100 | 18.4065 | 22.5478 | 27.71 | 31.6581 | 35.5572
SimcoeIce Accretion2023RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
SimcoeIce Accretion2025RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2025 | 22.9175 | 27.5192 | 33.3427 | 37.7989 | 42.2402
SimcoeIce Accretion2030RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2030 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
SimcoeIce Accretion2035RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2035 | 22.6651 | 27.2464 | 33.048 | 37.4787 | 41.8975
SimcoeIce Accretion2040RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2040 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
SimcoeIce Accretion2045RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2045 | 22.4127 | 26.9736 | 32.7533 | 37.1585 | 41.5548
SimcoeIce Accretion2050RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2050 | 21.7945 | 26.2954 | 31.9872 | 36.3223 | 40.6466
SimcoeIce Accretion2055RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2055 | 21.3024 | 25.7536 | 31.3684 | 35.6461 | 39.9097
SimcoeIce Accretion2060RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2060 | 20.8103 | 25.2117 | 30.7496 | 34.9699 | 39.1729
SimcoeIce Accretion2065RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2065 | 20.3181 | 24.6699 | 30.1308 | 34.2937 | 38.436
SimcoeIce Accretion2070RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2070 | 19.826 | 24.1281 | 29.512 | 33.6175 | 37.6992
SimcoeIce Accretion2075RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2075 | 19.4712 | 23.733 | 29.0615 | 33.1276 | 37.1637
SimcoeIce Accretion2080RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2080 | 19.1163 | 23.3379 | 28.611 | 32.6378 | 36.6282
SimcoeIce Accretion2085RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2085 | 18.7614 | 22.9429 | 28.1605 | 32.1479 | 36.0927
SimcoeIce Accretion2090RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2090 | 17.4365 | 21.4002 | 26.3613 | 30.1341 | 33.8722
SimcoeIce Accretion2095RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2095 | 16.4665 | 20.2526 | 25.0127 | 28.6101 | 32.1871
SimcoeIce Accretion2100RCP6.0 | Simcoe | Ice Accretion | RCP6.0 | 2100 | 15.4965 | 19.1049 | 23.664 | 27.0861 | 30.5021
SimcoeIce Accretion2023RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
SimcoeIce Accretion2025RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2025 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
SimcoeIce Accretion2030RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2030 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
SimcoeIce Accretion2035RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2035 | 22.2866 | 26.8372 | 32.606 | 36.9985 | 41.3834
SimcoeIce Accretion2040RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2040 | 21.4664 | 25.9342 | 31.5747 | 35.8715 | 40.1554
SimcoeIce Accretion2045RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2045 | 20.6462 | 25.0311 | 30.5433 | 34.7445 | 38.9273
SimcoeIce Accretion2050RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2050 | 19.3529 | 23.6013 | 28.9113 | 32.9644 | 36.9852
SimcoeIce Accretion2055RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2055 | 18.8797 | 23.0746 | 28.3107 | 32.3112 | 36.2712
SimcoeIce Accretion2060RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2060 | 17.4365 | 21.4002 | 26.3613 | 30.1341 | 33.8722
SimcoeIce Accretion2065RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2065 | 16.4665 | 20.2526 | 25.0127 | 28.6101 | 32.1871
SimcoeIce Accretion2070RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2070 | 15.0312 | 18.5876 | 23.052 | 26.4073 | 29.7595
SimcoeIce Accretion2075RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2075 | 14.5659 | 18.0702 | 22.44 | 25.7286 | 29.017
SimcoeIce Accretion2080RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2080 | 14.1006 | 17.5528 | 21.828 | 25.0498 | 28.2744
SimcoeIce Accretion2085RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2085 | 13.0596 | 16.297 | 20.332 | 23.3594 | 26.3894
SimcoeIce Accretion2090RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2090 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
SimcoeIce Accretion2095RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2095 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
SimcoeIce Accretion2100RCP8.5 | Simcoe | Ice Accretion | RCP8.5 | 2100 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
SimcoeWind2023RCP4.5 | Simcoe | Wind | RCP4.5 | 2023 | 87.7786 | 94.6439 | 101.8888 | 109.1075 | 116.3375
SimcoeWind2025RCP4.5 | Simcoe | Wind | RCP4.5 | 2025 | 87.8542 | 94.7441 | 102.0218 | 109.2696 | 116.5255
SimcoeWind2030RCP4.5 | Simcoe | Wind | RCP4.5 | 2030 | 87.9298 | 94.8443 | 102.1548 | 109.4317 | 116.7136
SimcoeWind2035RCP4.5 | Simcoe | Wind | RCP4.5 | 2035 | 88.0054 | 94.9444 | 102.2877 | 109.5938 | 116.9016
SimcoeWind2040RCP4.5 | Simcoe | Wind | RCP4.5 | 2040 | 88.0809 | 95.0446 | 102.4207 | 109.7559 | 117.0897
SimcoeWind2045RCP4.5 | Simcoe | Wind | RCP4.5 | 2045 | 88.1565 | 95.1448 | 102.5537 | 109.918 | 117.2778
SimcoeWind2050RCP4.5 | Simcoe | Wind | RCP4.5 | 2050 | 88.3106 | 95.3502 | 102.8261 | 110.2465 | 117.6639
SimcoeWind2055RCP4.5 | Simcoe | Wind | RCP4.5 | 2055 | 88.3891 | 95.4554 | 102.9655 | 110.413 | 117.8619
SimcoeWind2060RCP4.5 | Simcoe | Wind | RCP4.5 | 2060 | 88.4676 | 95.5606 | 103.1048 | 110.5794 | 118.06
SimcoeWind2065RCP4.5 | Simcoe | Wind | RCP4.5 | 2065 | 88.5461 | 95.6658 | 103.2442 | 110.7458 | 118.258
SimcoeWind2070RCP4.5 | Simcoe | Wind | RCP4.5 | 2070 | 88.6246 | 95.771 | 103.3836 | 110.9122 | 118.456
SimcoeWind2075RCP4.5 | Simcoe | Wind | RCP4.5 | 2075 | 88.7437 | 95.9244 | 103.5806 | 111.1464 | 118.7304
SimcoeWind2080RCP4.5 | Simcoe | Wind | RCP4.5 | 2080 | 88.8629 | 96.0779 | 103.7775 | 111.3805 | 119.0049
SimcoeWind2085RCP4.5 | Simcoe | Wind | RCP4.5 | 2085 | 88.9821 | 96.2313 | 103.9744 | 111.6147 | 119.2793
SimcoeWind2090RCP4.5 | Simcoe | Wind | RCP4.5 | 2090 | 89.1013 | 96.3847 | 104.1714 | 111.8488 | 119.5537
SimcoeWind2095RCP4.5 | Simcoe | Wind | RCP4.5 | 2095 | 89.2205 | 96.5381 | 104.3683 | 112.083 | 119.8281
SimcoeWind2100RCP4.5 | Simcoe | Wind | RCP4.5 | 2100 | 89.3397 | 96.6915 | 104.5653 | 112.3172 | 120.1025
SimcoeWind2023RCP6.0 | Simcoe | Wind | RCP6.0 | 2023 | 87.7786 | 94.6439 | 101.8888 | 109.1075 | 116.3375
SimcoeWind2025RCP6.0 | Simcoe | Wind | RCP6.0 | 2025 | 87.8542 | 94.7441 | 102.0218 | 109.2696 | 116.5255
SimcoeWind2030RCP6.0 | Simcoe | Wind | RCP6.0 | 2030 | 87.9298 | 94.8443 | 102.1548 | 109.4317 | 116.7136
SimcoeWind2035RCP6.0 | Simcoe | Wind | RCP6.0 | 2035 | 88.0054 | 94.9444 | 102.2877 | 109.5938 | 116.9016
SimcoeWind2040RCP6.0 | Simcoe | Wind | RCP6.0 | 2040 | 88.0809 | 95.0446 | 102.4207 | 109.7559 | 117.0897
SimcoeWind2045RCP6.0 | Simcoe | Wind | RCP6.0 | 2045 | 88.1565 | 95.1448 | 102.5537 | 109.918 | 117.2778
SimcoeWind2050RCP6.0 | Simcoe | Wind | RCP6.0 | 2050 | 88.3106 | 95.3502 | 102.8261 | 110.2465 | 117.6639
SimcoeWind2055RCP6.0 | Simcoe | Wind | RCP6.0 | 2055 | 88.3891 | 95.4554 | 102.9655 | 110.413 | 117.8619
SimcoeWind2060RCP6.0 | Simcoe | Wind | RCP6.0 | 2060 | 88.4676 | 95.5606 | 103.1048 | 110.5794 | 118.06
SimcoeWind2065RCP6.0 | Simcoe | Wind | RCP6.0 | 2065 | 88.5461 | 95.6658 | 103.2442 | 110.7458 | 118.258
SimcoeWind2070RCP6.0 | Simcoe | Wind | RCP6.0 | 2070 | 88.6246 | 95.771 | 103.3836 | 110.9122 | 118.456
SimcoeWind2075RCP6.0 | Simcoe | Wind | RCP6.0 | 2075 | 88.8033 | 96.0012 | 103.679 | 111.2635 | 118.8677
SimcoeWind2080RCP6.0 | Simcoe | Wind | RCP6.0 | 2080 | 88.9821 | 96.2313 | 103.9744 | 111.6147 | 119.2793
SimcoeWind2085RCP6.0 | Simcoe | Wind | RCP6.0 | 2085 | 89.1609 | 96.4614 | 104.2699 | 111.9659 | 119.6909
SimcoeWind2090RCP6.0 | Simcoe | Wind | RCP6.0 | 2090 | 89.5955 | 97.0234 | 104.9861 | 112.8179 | 120.6782
SimcoeWind2095RCP6.0 | Simcoe | Wind | RCP6.0 | 2095 | 89.8513 | 97.3553 | 105.407 | 113.3186 | 121.2539
SimcoeWind2100RCP6.0 | Simcoe | Wind | RCP6.0 | 2100 | 90.1072 | 97.6872 | 105.8278 | 113.8193 | 121.8296
SimcoeWind2023RCP8.5 | Simcoe | Wind | RCP8.5 | 2023 | 87.7786 | 94.6439 | 101.8888 | 109.1075 | 116.3375
SimcoeWind2025RCP8.5 | Simcoe | Wind | RCP8.5 | 2025 | 87.9298 | 94.8443 | 102.1548 | 109.4317 | 116.7136
SimcoeWind2030RCP8.5 | Simcoe | Wind | RCP8.5 | 2030 | 88.0809 | 95.0446 | 102.4207 | 109.7559 | 117.0897
SimcoeWind2035RCP8.5 | Simcoe | Wind | RCP8.5 | 2035 | 88.2321 | 95.245 | 102.6867 | 110.0801 | 117.4658
SimcoeWind2040RCP8.5 | Simcoe | Wind | RCP8.5 | 2040 | 88.3629 | 95.4204 | 102.919 | 110.3575 | 117.7959
SimcoeWind2045RCP8.5 | Simcoe | Wind | RCP8.5 | 2045 | 88.4937 | 95.5957 | 103.1513 | 110.6349 | 118.126
SimcoeWind2050RCP8.5 | Simcoe | Wind | RCP8.5 | 2050 | 88.8629 | 96.0779 | 103.7775 | 111.3805 | 119.0049
SimcoeWind2055RCP8.5 | Simcoe | Wind | RCP8.5 | 2055 | 89.1013 | 96.3847 | 104.1714 | 111.8488 | 119.5537
SimcoeWind2060RCP8.5 | Simcoe | Wind | RCP8.5 | 2060 | 89.5955 | 97.0234 | 104.9861 | 112.8179 | 120.6782
SimcoeWind2065RCP8.5 | Simcoe | Wind | RCP8.5 | 2065 | 89.8513 | 97.3553 | 105.407 | 113.3186 | 121.2539
SimcoeWind2070RCP8.5 | Simcoe | Wind | RCP8.5 | 2070 | 90.2554 | 97.897 | 106.1173 | 114.176 | 122.2557
SimcoeWind2075RCP8.5 | Simcoe | Wind | RCP8.5 | 2075 | 90.4037 | 98.1068 | 106.4069 | 114.5326 | 122.6817
SimcoeWind2080RCP8.5 | Simcoe | Wind | RCP8.5 | 2080 | 90.5519 | 98.3165 | 106.6964 | 114.8892 | 123.1077
SimcoeWind2085RCP8.5 | Simcoe | Wind | RCP8.5 | 2085 | 90.8921 | 98.7627 | 107.2873 | 115.5917 | 123.9367
SimcoeWind2090RCP8.5 | Simcoe | Wind | RCP8.5 | 2090 | 91.2322 | 99.2089 | 107.8781 | 116.2941 | 124.7657
SimcoeWind2095RCP8.5 | Simcoe | Wind | RCP8.5 | 2095 | 91.2322 | 99.2089 | 107.8781 | 116.2941 | 124.7657
SimcoeWind2100RCP8.5 | Simcoe | Wind | RCP8.5 | 2100 | 91.2322 | 99.2089 | 107.8781 | 116.2941 | 124.7657
Sioux LookoutIce Accretion2023RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2023 | 9.245 | 11.0274 | 13.286 | 15.0132 | 16.7404
Sioux LookoutIce Accretion2025RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2025 | 9.3053 | 11.0939 | 13.3575 | 15.0915 | 16.825
Sioux LookoutIce Accretion2030RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2030 | 9.3656 | 11.1605 | 13.429 | 15.1699 | 16.9096
Sioux LookoutIce Accretion2035RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2035 | 9.4259 | 11.227 | 13.5005 | 15.2482 | 16.9943
Sioux LookoutIce Accretion2040RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2040 | 9.4862 | 11.2935 | 13.572 | 15.3266 | 17.0789
Sioux LookoutIce Accretion2045RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2045 | 9.5465 | 11.3601 | 13.6435 | 15.4049 | 17.1635
Sioux LookoutIce Accretion2050RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2050 | 9.6412 | 11.4633 | 13.7592 | 15.5303 | 17.2973
Sioux LookoutIce Accretion2055RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2055 | 9.6756 | 11.5 | 13.8034 | 15.5773 | 17.3464
Sioux LookoutIce Accretion2060RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2060 | 9.71 | 11.5367 | 13.8476 | 15.6243 | 17.3956
Sioux LookoutIce Accretion2065RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2065 | 9.7444 | 11.5734 | 13.8918 | 15.6713 | 17.4447
Sioux LookoutIce Accretion2070RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2070 | 9.7787 | 11.61 | 13.936 | 15.7183 | 17.4938
Sioux LookoutIce Accretion2075RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2075 | 9.7908 | 11.6262 | 13.9598 | 15.7477 | 17.5293
Sioux LookoutIce Accretion2080RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2080 | 9.8028 | 11.6424 | 13.9837 | 15.7771 | 17.5648
Sioux LookoutIce Accretion2085RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2085 | 9.8149 | 11.6586 | 14.0075 | 15.8064 | 17.6003
Sioux LookoutIce Accretion2090RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2090 | 9.827 | 11.6748 | 14.0313 | 15.8358 | 17.6358
Sioux LookoutIce Accretion2095RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2095 | 9.839 | 11.691 | 14.0552 | 15.8652 | 17.6713
Sioux LookoutIce Accretion2100RCP4.5 | Sioux Lookout | Ice Accretion | RCP4.5 | 2100 | 9.8511 | 11.7071 | 14.079 | 15.8946 | 17.7068
Sioux LookoutIce Accretion2023RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2023 | 9.245 | 11.0274 | 13.286 | 15.0132 | 16.7404
Sioux LookoutIce Accretion2025RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2025 | 9.3053 | 11.0939 | 13.3575 | 15.0915 | 16.825
Sioux LookoutIce Accretion2030RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2030 | 9.3656 | 11.1605 | 13.429 | 15.1699 | 16.9096
Sioux LookoutIce Accretion2035RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2035 | 9.4259 | 11.227 | 13.5005 | 15.2482 | 16.9943
Sioux LookoutIce Accretion2040RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2040 | 9.4862 | 11.2935 | 13.572 | 15.3266 | 17.0789
Sioux LookoutIce Accretion2045RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2045 | 9.5465 | 11.3601 | 13.6435 | 15.4049 | 17.1635
Sioux LookoutIce Accretion2050RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2050 | 9.6412 | 11.4633 | 13.7592 | 15.5303 | 17.2973
Sioux LookoutIce Accretion2055RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2055 | 9.6756 | 11.5 | 13.8034 | 15.5773 | 17.3464
Sioux LookoutIce Accretion2060RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2060 | 9.71 | 11.5367 | 13.8476 | 15.6243 | 17.3956
Sioux LookoutIce Accretion2065RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2065 | 9.7444 | 11.5734 | 13.8918 | 15.6713 | 17.4447
Sioux LookoutIce Accretion2070RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2070 | 9.7787 | 11.61 | 13.936 | 15.7183 | 17.4938
Sioux LookoutIce Accretion2075RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2075 | 9.7968 | 11.6343 | 13.9718 | 15.7624 | 17.5471
Sioux LookoutIce Accretion2080RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2080 | 9.8149 | 11.6586 | 14.0075 | 15.8064 | 17.6003
Sioux LookoutIce Accretion2085RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2085 | 9.833 | 11.6829 | 14.0432 | 15.8505 | 17.6535
Sioux LookoutIce Accretion2090RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2090 | 9.7636 | 11.61 | 13.9663 | 15.7673 | 17.5648
Sioux LookoutIce Accretion2095RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2095 | 9.6762 | 11.5129 | 13.8537 | 15.64 | 17.4229
Sioux LookoutIce Accretion2100RCP6.0 | Sioux Lookout | Ice Accretion | RCP6.0 | 2100 | 9.5888 | 11.4158 | 13.741 | 15.5126 | 17.2809
Sioux LookoutIce Accretion2023RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2023 | 9.245 | 11.0274 | 13.286 | 15.0132 | 16.7404
Sioux LookoutIce Accretion2025RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2025 | 9.3656 | 11.1605 | 13.429 | 15.1699 | 16.9096
Sioux LookoutIce Accretion2030RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2030 | 9.4862 | 11.2935 | 13.572 | 15.3266 | 17.0789
Sioux LookoutIce Accretion2035RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2035 | 9.6069 | 11.4266 | 13.715 | 15.4833 | 17.2481
Sioux LookoutIce Accretion2040RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2040 | 9.6641 | 11.4878 | 13.7887 | 15.5616 | 17.33
Sioux LookoutIce Accretion2045RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2045 | 9.7214 | 11.5489 | 13.8623 | 15.64 | 17.4119
Sioux LookoutIce Accretion2050RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2050 | 9.8028 | 11.6424 | 13.9837 | 15.7771 | 17.5648
Sioux LookoutIce Accretion2055RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2055 | 9.827 | 11.6748 | 14.0313 | 15.8358 | 17.6358
Sioux LookoutIce Accretion2060RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2060 | 9.7636 | 11.61 | 13.9663 | 15.7673 | 17.5648
Sioux LookoutIce Accretion2065RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2065 | 9.6762 | 11.5129 | 13.8537 | 15.64 | 17.4229
Sioux LookoutIce Accretion2070RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2070 | 9.7335 | 11.5992 | 13.9663 | 15.7771 | 17.5812
Sioux LookoutIce Accretion2075RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2075 | 9.8782 | 11.7827 | 14.1917 | 16.0415 | 17.8815
Sioux LookoutIce Accretion2080RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2080 | 10.023 | 11.9661 | 14.417 | 16.3059 | 18.1818
Sioux LookoutIce Accretion2085RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2085 | 9.7516 | 11.6316 | 14.014 | 15.8432 | 17.6658
Sioux LookoutIce Accretion2090RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2090 | 9.4802 | 11.2971 | 13.611 | 15.3804 | 17.1499
Sioux LookoutIce Accretion2095RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2095 | 9.4802 | 11.2971 | 13.611 | 15.3804 | 17.1499
Sioux LookoutIce Accretion2100RCP8.5 | Sioux Lookout | Ice Accretion | RCP8.5 | 2100 | 9.4802 | 11.2971 | 13.611 | 15.3804 | 17.1499
Sioux LookoutWind2023RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2023 | 71.2304 | 76.7633 | 82.5986 | 88.4156 | 94.2372
Sioux LookoutWind2025RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2025 | 71.2481 | 76.7671 | 82.5849 | 88.3878 | 94.1951
Sioux LookoutWind2030RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2030 | 71.2658 | 76.7709 | 82.5713 | 88.36 | 94.1531
Sioux LookoutWind2035RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2035 | 71.2835 | 76.7748 | 82.5576 | 88.3322 | 94.111
Sioux LookoutWind2040RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2040 | 71.3012 | 76.7786 | 82.5439 | 88.3045 | 94.0689
Sioux LookoutWind2045RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2045 | 71.3189 | 76.7824 | 82.5303 | 88.2767 | 94.0269
Sioux LookoutWind2050RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2050 | 71.3961 | 76.8625 | 82.6117 | 88.3612 | 94.1138
Sioux LookoutWind2055RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2055 | 71.4556 | 76.9387 | 82.7068 | 88.4735 | 94.2428
Sioux LookoutWind2060RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2060 | 71.515 | 77.015 | 82.802 | 88.5858 | 94.3718
Sioux LookoutWind2065RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2065 | 71.5745 | 77.0912 | 82.8971 | 88.6981 | 94.5008
Sioux LookoutWind2070RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2070 | 71.634 | 77.1675 | 82.9922 | 88.8104 | 94.6298
Sioux LookoutWind2075RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2075 | 71.7437 | 77.3022 | 83.1576 | 89.0035 | 94.851
Sioux LookoutWind2080RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2080 | 71.8535 | 77.4369 | 83.3229 | 89.1965 | 95.0723
Sioux LookoutWind2085RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2085 | 71.9632 | 77.5717 | 83.4883 | 89.3895 | 95.2935
Sioux LookoutWind2090RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2090 | 72.073 | 77.7064 | 83.6537 | 89.5825 | 95.5147
Sioux LookoutWind2095RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2095 | 72.1827 | 77.8411 | 83.819 | 89.7756 | 95.736
Sioux LookoutWind2100RCP4.5 | Sioux Lookout | Wind | RCP4.5 | 2100 | 72.2925 | 77.9759 | 83.9844 | 89.9686 | 95.9572
Sioux LookoutWind2023RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2023 | 71.2304 | 76.7633 | 82.5986 | 88.4156 | 94.2372
Sioux LookoutWind2025RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2025 | 71.2481 | 76.7671 | 82.5849 | 88.3878 | 94.1951
Sioux LookoutWind2030RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2030 | 71.2658 | 76.7709 | 82.5713 | 88.36 | 94.1531
Sioux LookoutWind2035RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2035 | 71.2835 | 76.7748 | 82.5576 | 88.3322 | 94.111
Sioux LookoutWind2040RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2040 | 71.3012 | 76.7786 | 82.5439 | 88.3045 | 94.0689
Sioux LookoutWind2045RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2045 | 71.3189 | 76.7824 | 82.5303 | 88.2767 | 94.0269
Sioux LookoutWind2050RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2050 | 71.3961 | 76.8625 | 82.6117 | 88.3612 | 94.1138
Sioux LookoutWind2055RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2055 | 71.4556 | 76.9387 | 82.7068 | 88.4735 | 94.2428
Sioux LookoutWind2060RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2060 | 71.515 | 77.015 | 82.802 | 88.5858 | 94.3718
Sioux LookoutWind2065RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2065 | 71.5745 | 77.0912 | 82.8971 | 88.6981 | 94.5008
Sioux LookoutWind2070RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2070 | 71.634 | 77.1675 | 82.9922 | 88.8104 | 94.6298
Sioux LookoutWind2075RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2075 | 71.7986 | 77.3696 | 83.2403 | 89.1 | 94.9617
Sioux LookoutWind2080RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2080 | 71.9632 | 77.5717 | 83.4883 | 89.3895 | 95.2935
Sioux LookoutWind2085RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2085 | 72.1279 | 77.7738 | 83.7363 | 89.6791 | 95.6254
Sioux LookoutWind2090RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2090 | 72.4341 | 78.164 | 84.2331 | 90.2669 | 96.3031
Sioux LookoutWind2095RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2095 | 72.5757 | 78.3521 | 84.4819 | 90.5652 | 96.649
Sioux LookoutWind2100RCP6.0 | Sioux Lookout | Wind | RCP6.0 | 2100 | 72.7173 | 78.5402 | 84.7306 | 90.8635 | 96.9948
Sioux LookoutWind2023RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2023 | 71.2304 | 76.7633 | 82.5986 | 88.4156 | 94.2372
Sioux LookoutWind2025RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2025 | 71.2658 | 76.7709 | 82.5713 | 88.36 | 94.1531
Sioux LookoutWind2030RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2030 | 71.3012 | 76.7786 | 82.5439 | 88.3045 | 94.0689
Sioux LookoutWind2035RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2035 | 71.3366 | 76.7862 | 82.5166 | 88.2489 | 93.9848
Sioux LookoutWind2040RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2040 | 71.4357 | 76.9133 | 82.6751 | 88.4361 | 94.1998
Sioux LookoutWind2045RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2045 | 71.5349 | 77.0404 | 82.8337 | 88.6232 | 94.4148
Sioux LookoutWind2050RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2050 | 71.8535 | 77.4369 | 83.3229 | 89.1965 | 95.0723
Sioux LookoutWind2055RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2055 | 72.073 | 77.7064 | 83.6537 | 89.5825 | 95.5147
Sioux LookoutWind2060RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2060 | 72.4341 | 78.164 | 84.2331 | 90.2669 | 96.3031
Sioux LookoutWind2065RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2065 | 72.5757 | 78.3521 | 84.4819 | 90.5652 | 96.649
Sioux LookoutWind2070RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2070 | 72.8448 | 78.6749 | 84.8727 | 91.0098 | 97.1506
Sioux LookoutWind2075RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2075 | 72.9722 | 78.8096 | 85.0149 | 91.156 | 97.3064
Sioux LookoutWind2080RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2080 | 73.0997 | 78.9444 | 85.157 | 91.3022 | 97.4622
Sioux LookoutWind2085RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2085 | 73.2625 | 79.135 | 85.3784 | 91.5611 | 97.7474
Sioux LookoutWind2090RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2090 | 73.4254 | 79.3257 | 85.5998 | 91.8199 | 98.0325
Sioux LookoutWind2095RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2095 | 73.4254 | 79.3257 | 85.5998 | 91.8199 | 98.0325
Sioux LookoutWind2100RCP8.5 | Sioux Lookout | Wind | RCP8.5 | 2100 | 73.4254 | 79.3257 | 85.5998 | 91.8199 | 98.0325
Smiths FallsIce Accretion2023RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2023 | 17.9473 | 21.3426 | 25.636 | 28.9393 | 32.2358
Smiths FallsIce Accretion2025RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2025 | 17.9412 | 21.339 | 25.6403 | 28.9491 | 32.2468
Smiths FallsIce Accretion2030RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2030 | 17.9352 | 21.3354 | 25.6447 | 28.9589 | 32.2577
Smiths FallsIce Accretion2035RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2035 | 17.9292 | 21.3318 | 25.649 | 28.9687 | 32.2686
Smiths FallsIce Accretion2040RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2040 | 17.9231 | 21.3282 | 25.6533 | 28.9785 | 32.2795
Smiths FallsIce Accretion2045RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2045 | 17.9171 | 21.3246 | 25.6577 | 28.9883 | 32.2904
Smiths FallsIce Accretion2050RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2050 | 17.9147 | 21.3426 | 25.7036 | 29.0568 | 32.3734
Smiths FallsIce Accretion2055RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2055 | 17.9183 | 21.3642 | 25.7452 | 29.1156 | 32.4455
Smiths FallsIce Accretion2060RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2060 | 17.9219 | 21.3858 | 25.7868 | 29.1743 | 32.5176
Smiths FallsIce Accretion2065RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2065 | 17.9256 | 21.4074 | 25.8284 | 29.2331 | 32.5896
Smiths FallsIce Accretion2070RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2070 | 17.9292 | 21.4289 | 25.87 | 29.2919 | 32.6617
Smiths FallsIce Accretion2075RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2075 | 18.0106 | 21.5476 | 26.0347 | 29.4877 | 32.8965
Smiths FallsIce Accretion2080RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2080 | 18.092 | 21.6663 | 26.1993 | 29.6836 | 33.1313
Smiths FallsIce Accretion2085RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2085 | 18.1734 | 21.785 | 26.364 | 29.8795 | 33.3661
Smiths FallsIce Accretion2090RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2090 | 18.2548 | 21.9037 | 26.5287 | 30.0753 | 33.6008
Smiths FallsIce Accretion2095RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2095 | 18.3362 | 22.0224 | 26.6933 | 30.2712 | 33.8356
Smiths FallsIce Accretion2100RCP4.5 | Smiths Falls | Ice Accretion | RCP4.5 | 2100 | 18.4177 | 22.1411 | 26.858 | 30.4671 | 34.0704
Smiths FallsIce Accretion2023RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2023 | 17.9473 | 21.3426 | 25.636 | 28.9393 | 32.2358
Smiths FallsIce Accretion2025RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2025 | 17.9412 | 21.339 | 25.6403 | 28.9491 | 32.2468
Smiths FallsIce Accretion2030RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2030 | 17.9352 | 21.3354 | 25.6447 | 28.9589 | 32.2577
Smiths FallsIce Accretion2035RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2035 | 17.9292 | 21.3318 | 25.649 | 28.9687 | 32.2686
Smiths FallsIce Accretion2040RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2040 | 17.9231 | 21.3282 | 25.6533 | 28.9785 | 32.2795
Smiths FallsIce Accretion2045RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2045 | 17.9171 | 21.3246 | 25.6577 | 28.9883 | 32.2904
Smiths FallsIce Accretion2050RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2050 | 17.9147 | 21.3426 | 25.7036 | 29.0568 | 32.3734
Smiths FallsIce Accretion2055RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2055 | 17.9183 | 21.3642 | 25.7452 | 29.1156 | 32.4455
Smiths FallsIce Accretion2060RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2060 | 17.9219 | 21.3858 | 25.7868 | 29.1743 | 32.5176
Smiths FallsIce Accretion2065RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2065 | 17.9256 | 21.4074 | 25.8284 | 29.2331 | 32.5896
Smiths FallsIce Accretion2070RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2070 | 17.9292 | 21.4289 | 25.87 | 29.2919 | 32.6617
Smiths FallsIce Accretion2075RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2075 | 18.0513 | 21.607 | 26.117 | 29.5857 | 33.0139
Smiths FallsIce Accretion2080RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2080 | 18.1734 | 21.785 | 26.364 | 29.8795 | 33.3661
Smiths FallsIce Accretion2085RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2085 | 18.2955 | 21.963 | 26.611 | 30.1733 | 33.7182
Smiths FallsIce Accretion2090RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2090 | 18.4056 | 22.1627 | 26.9273 | 30.5552 | 34.1905
Smiths FallsIce Accretion2095RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2095 | 18.3935 | 22.1842 | 26.9967 | 30.6433 | 34.3106
Smiths FallsIce Accretion2100RCP6.0 | Smiths Falls | Ice Accretion | RCP6.0 | 2100 | 18.3815 | 22.2058 | 27.066 | 30.7315 | 34.4308
Smiths FallsIce Accretion2023RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2023 | 17.9473 | 21.3426 | 25.636 | 28.9393 | 32.2358
Smiths FallsIce Accretion2025RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2025 | 17.9352 | 21.3354 | 25.6447 | 28.9589 | 32.2577
Smiths FallsIce Accretion2030RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2030 | 17.9231 | 21.3282 | 25.6533 | 28.9785 | 32.2795
Smiths FallsIce Accretion2035RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2035 | 17.9111 | 21.321 | 25.662 | 28.9981 | 32.3014
Smiths FallsIce Accretion2040RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2040 | 17.9171 | 21.357 | 25.7313 | 29.096 | 32.4215
Smiths FallsIce Accretion2045RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2045 | 17.9231 | 21.393 | 25.8007 | 29.1939 | 32.5416
Smiths FallsIce Accretion2050RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2050 | 18.092 | 21.6663 | 26.1993 | 29.6836 | 33.1313
Smiths FallsIce Accretion2055RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2055 | 18.2548 | 21.9037 | 26.5287 | 30.0753 | 33.6008
Smiths FallsIce Accretion2060RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2060 | 18.4056 | 22.1627 | 26.9273 | 30.5552 | 34.1905
Smiths FallsIce Accretion2065RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2065 | 18.3935 | 22.1842 | 26.9967 | 30.6433 | 34.3106
Smiths FallsIce Accretion2070RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2070 | 18.1885 | 22.0044 | 26.8493 | 30.5062 | 34.1905
Smiths FallsIce Accretion2075RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2075 | 17.9955 | 21.803 | 26.6327 | 30.281 | 33.9503
Smiths FallsIce Accretion2080RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2080 | 17.8025 | 21.6016 | 26.416 | 30.0557 | 33.71
Smiths FallsIce Accretion2085RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2085 | 17.0608 | 20.7492 | 25.415 | 28.954 | 32.4979
Smiths FallsIce Accretion2090RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2090 | 16.319 | 19.8968 | 24.414 | 27.8522 | 31.2858
Smiths FallsIce Accretion2095RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2095 | 16.319 | 19.8968 | 24.414 | 27.8522 | 31.2858
Smiths FallsIce Accretion2100RCP8.5 | Smiths Falls | Ice Accretion | RCP8.5 | 2100 | 16.319 | 19.8968 | 24.414 | 27.8522 | 31.2858
Smiths FallsWind2023RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2023 | 76.5564 | 82.5275 | 88.8272 | 95.1016 | 101.3834
Smiths FallsWind2025RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2025 | 76.6665 | 82.6598 | 88.9871 | 95.2868 | 101.5941
Smiths FallsWind2030RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2030 | 76.7767 | 82.7921 | 89.1469 | 95.472 | 101.8047
Smiths FallsWind2035RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2035 | 76.8869 | 82.9244 | 89.3068 | 95.6571 | 102.0154
Smiths FallsWind2040RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2040 | 76.9971 | 83.0567 | 89.4667 | 95.8423 | 102.2261
Smiths FallsWind2045RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2045 | 77.1073 | 83.189 | 89.6265 | 96.0275 | 102.4368
Smiths FallsWind2050RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2050 | 77.2022 | 83.2984 | 89.7547 | 96.1731 | 102.5993
Smiths FallsWind2055RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2055 | 77.187 | 83.2755 | 89.723 | 96.1336 | 102.5511
Smiths FallsWind2060RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2060 | 77.1718 | 83.2526 | 89.6914 | 96.094 | 102.503
Smiths FallsWind2065RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2065 | 77.1566 | 83.2296 | 89.6597 | 96.0545 | 102.4548
Smiths FallsWind2070RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2070 | 77.1414 | 83.2067 | 89.628 | 96.015 | 102.4067
Smiths FallsWind2075RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2075 | 77.1693 | 83.2436 | 89.6779 | 96.0746 | 102.4752
Smiths FallsWind2080RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2080 | 77.1972 | 83.2804 | 89.7277 | 96.1342 | 102.5438
Smiths FallsWind2085RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2085 | 77.225 | 83.3172 | 89.7776 | 96.1939 | 102.6123
Smiths FallsWind2090RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2090 | 77.2529 | 83.354 | 89.8275 | 96.2535 | 102.6809
Smiths FallsWind2095RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2095 | 77.2808 | 83.3909 | 89.8773 | 96.3131 | 102.7494
Smiths FallsWind2100RCP4.5 | Smiths Falls | Wind | RCP4.5 | 2100 | 77.3086 | 83.4277 | 89.9272 | 96.3728 | 102.818
Smiths FallsWind2023RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2023 | 76.5564 | 82.5275 | 88.8272 | 95.1016 | 101.3834
Smiths FallsWind2025RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2025 | 76.6665 | 82.6598 | 88.9871 | 95.2868 | 101.5941
Smiths FallsWind2030RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2030 | 76.7767 | 82.7921 | 89.1469 | 95.472 | 101.8047
Smiths FallsWind2035RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2035 | 76.8869 | 82.9244 | 89.3068 | 95.6571 | 102.0154
Smiths FallsWind2040RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2040 | 76.9971 | 83.0567 | 89.4667 | 95.8423 | 102.2261
Smiths FallsWind2045RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2045 | 77.1073 | 83.189 | 89.6265 | 96.0275 | 102.4368
Smiths FallsWind2050RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2050 | 77.2022 | 83.2984 | 89.7547 | 96.1731 | 102.5993
Smiths FallsWind2055RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2055 | 77.187 | 83.2755 | 89.723 | 96.1336 | 102.5511
Smiths FallsWind2060RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2060 | 77.1718 | 83.2526 | 89.6914 | 96.094 | 102.503
Smiths FallsWind2065RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2065 | 77.1566 | 83.2296 | 89.6597 | 96.0545 | 102.4548
Smiths FallsWind2070RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2070 | 77.1414 | 83.2067 | 89.628 | 96.015 | 102.4067
Smiths FallsWind2075RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2075 | 77.1832 | 83.262 | 89.7028 | 96.1044 | 102.5095
Smiths FallsWind2080RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2080 | 77.225 | 83.3172 | 89.7776 | 96.1939 | 102.6123
Smiths FallsWind2085RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2085 | 77.2668 | 83.3725 | 89.8524 | 96.2833 | 102.7151
Smiths FallsWind2090RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2090 | 77.2529 | 83.3431 | 89.7981 | 96.2127 | 102.624
Smiths FallsWind2095RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2095 | 77.1972 | 83.2586 | 89.6691 | 96.0526 | 102.4301
Smiths FallsWind2100RCP6.0 | Smiths Falls | Wind | RCP6.0 | 2100 | 77.1414 | 83.174 | 89.54 | 95.8925 | 102.2361
Smiths FallsWind2023RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2023 | 76.5564 | 82.5275 | 88.8272 | 95.1016 | 101.3834
Smiths FallsWind2025RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2025 | 76.7767 | 82.7921 | 89.1469 | 95.472 | 101.8047
Smiths FallsWind2030RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2030 | 76.9971 | 83.0567 | 89.4667 | 95.8423 | 102.2261
Smiths FallsWind2035RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2035 | 77.2174 | 83.3213 | 89.7864 | 96.2127 | 102.6474
Smiths FallsWind2040RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2040 | 77.1921 | 83.2831 | 89.7336 | 96.1468 | 102.5672
Smiths FallsWind2045RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2045 | 77.1668 | 83.2449 | 89.6808 | 96.0809 | 102.4869
Smiths FallsWind2050RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2050 | 77.1972 | 83.2804 | 89.7277 | 96.1342 | 102.5438
Smiths FallsWind2055RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2055 | 77.2529 | 83.354 | 89.8275 | 96.2535 | 102.6809
Smiths FallsWind2060RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2060 | 77.2529 | 83.3431 | 89.7981 | 96.2127 | 102.624
Smiths FallsWind2065RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2065 | 77.1972 | 83.2586 | 89.6691 | 96.0526 | 102.4301
Smiths FallsWind2070RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2070 | 77.1744 | 83.204 | 89.5664 | 95.9177 | 102.2595
Smiths FallsWind2075RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2075 | 77.2073 | 83.234 | 89.5928 | 95.9428 | 102.2829
Smiths FallsWind2080RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2080 | 77.2402 | 83.264 | 89.6192 | 95.9679 | 102.3063
Smiths FallsWind2085RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2085 | 77.2668 | 83.3049 | 89.6764 | 96.0338 | 102.3866
Smiths FallsWind2090RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2090 | 77.2934 | 83.3459 | 89.7336 | 96.0997 | 102.4668
Smiths FallsWind2095RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2095 | 77.2934 | 83.3459 | 89.7336 | 96.0997 | 102.4668
Smiths FallsWind2100RCP8.5 | Smiths Falls | Wind | RCP8.5 | 2100 | 77.2934 | 83.3459 | 89.7336 | 96.0997 | 102.4668
SmithvilleIce Accretion2023RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
SmithvilleIce Accretion2025RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2025 | 21.9182 | 26.3121 | 31.8773 | 36.1299 | 40.3738
SmithvilleIce Accretion2030RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2030 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
SmithvilleIce Accretion2035RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2035 | 21.7104 | 26.0819 | 31.632 | 35.8526 | 40.0781
SmithvilleIce Accretion2040RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2040 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
SmithvilleIce Accretion2045RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2045 | 21.5026 | 25.8517 | 31.3867 | 35.5754 | 39.7824
SmithvilleIce Accretion2050RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2050 | 20.9221 | 25.2001 | 30.6368 | 34.7425 | 38.8765
SmithvilleIce Accretion2055RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2055 | 20.4456 | 24.6636 | 30.0096 | 34.0483 | 38.1185
SmithvilleIce Accretion2060RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2060 | 19.9691 | 24.1271 | 29.3824 | 33.354 | 37.3605
SmithvilleIce Accretion2065RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2065 | 19.4926 | 23.5906 | 28.7552 | 32.6597 | 36.6025
SmithvilleIce Accretion2070RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2070 | 19.0161 | 23.0541 | 28.128 | 31.9654 | 35.8445
SmithvilleIce Accretion2075RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2075 | 18.8379 | 22.8682 | 27.9307 | 31.7605 | 35.6294
SmithvilleIce Accretion2080RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2080 | 18.6598 | 22.6822 | 27.7333 | 31.5556 | 35.4144
SmithvilleIce Accretion2085RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2085 | 18.4817 | 22.4963 | 27.536 | 31.3507 | 35.1994
SmithvilleIce Accretion2090RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2090 | 18.3035 | 22.3104 | 27.3387 | 31.1458 | 34.9843
SmithvilleIce Accretion2095RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2095 | 18.1254 | 22.1245 | 27.1413 | 30.9409 | 34.7693
SmithvilleIce Accretion2100RCP4.5 | Smithville | Ice Accretion | RCP4.5 | 2100 | 17.9473 | 21.9386 | 26.944 | 30.736 | 34.5542
SmithvilleIce Accretion2023RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
SmithvilleIce Accretion2025RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2025 | 21.9182 | 26.3121 | 31.8773 | 36.1299 | 40.3738
SmithvilleIce Accretion2030RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2030 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
SmithvilleIce Accretion2035RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2035 | 21.7104 | 26.0819 | 31.632 | 35.8526 | 40.0781
SmithvilleIce Accretion2040RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2040 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
SmithvilleIce Accretion2045RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2045 | 21.5026 | 25.8517 | 31.3867 | 35.5754 | 39.7824
SmithvilleIce Accretion2050RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2050 | 20.9221 | 25.2001 | 30.6368 | 34.7425 | 38.8765
SmithvilleIce Accretion2055RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2055 | 20.4456 | 24.6636 | 30.0096 | 34.0483 | 38.1185
SmithvilleIce Accretion2060RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2060 | 19.9691 | 24.1271 | 29.3824 | 33.354 | 37.3605
SmithvilleIce Accretion2065RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2065 | 19.4926 | 23.5906 | 28.7552 | 32.6597 | 36.6025
SmithvilleIce Accretion2070RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2070 | 19.0161 | 23.0541 | 28.128 | 31.9654 | 35.8445
SmithvilleIce Accretion2075RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2075 | 18.7489 | 22.7752 | 27.832 | 31.6581 | 35.5219
SmithvilleIce Accretion2080RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2080 | 18.4817 | 22.4963 | 27.536 | 31.3507 | 35.1994
SmithvilleIce Accretion2085RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2085 | 18.2145 | 22.2174 | 27.24 | 31.0434 | 34.8768
SmithvilleIce Accretion2090RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2090 | 17.2199 | 21.1063 | 25.9733 | 29.6633 | 33.3581
SmithvilleIce Accretion2095RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2095 | 16.4925 | 20.2741 | 25.0027 | 28.5905 | 32.1619
SmithvilleIce Accretion2100RCP6.0 | Smithville | Ice Accretion | RCP6.0 | 2100 | 15.7651 | 19.4419 | 24.032 | 27.5178 | 30.9658
SmithvilleIce Accretion2023RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
SmithvilleIce Accretion2025RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2025 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
SmithvilleIce Accretion2030RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2030 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
SmithvilleIce Accretion2035RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2035 | 21.3987 | 25.7366 | 31.264 | 35.4368 | 39.6346
SmithvilleIce Accretion2040RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2040 | 20.6045 | 24.8425 | 30.2187 | 34.2797 | 38.3712
SmithvilleIce Accretion2045RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2045 | 19.8103 | 23.9483 | 29.1733 | 33.1226 | 37.1078
SmithvilleIce Accretion2050RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2050 | 18.6598 | 22.6822 | 27.7333 | 31.5556 | 35.4144
SmithvilleIce Accretion2055RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2055 | 18.3035 | 22.3104 | 27.3387 | 31.1458 | 34.9843
SmithvilleIce Accretion2060RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2060 | 17.2199 | 21.1063 | 25.9733 | 29.6633 | 33.3581
SmithvilleIce Accretion2065RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2065 | 16.4925 | 20.2741 | 25.0027 | 28.5905 | 32.1619
SmithvilleIce Accretion2070RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2070 | 15.4014 | 19.0258 | 23.5627 | 26.9995 | 30.4013
SmithvilleIce Accretion2075RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2075 | 15.0377 | 18.6097 | 23.0933 | 26.4812 | 29.8368
SmithvilleIce Accretion2080RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2080 | 14.674 | 18.1936 | 22.624 | 25.9629 | 29.2723
SmithvilleIce Accretion2085RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2085 | 13.8501 | 17.2242 | 21.456 | 24.643 | 27.8006
SmithvilleIce Accretion2090RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2090 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
SmithvilleIce Accretion2095RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2095 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
SmithvilleIce Accretion2100RCP8.5 | Smithville | Ice Accretion | RCP8.5 | 2100 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
SmithvilleWind2023RCP4.5 | Smithville | Wind | RCP4.5 | 2023 | 88.11 | 95.1229 | 102.5655 | 109.9612 | 117.3507
SmithvilleWind2025RCP4.5 | Smithville | Wind | RCP4.5 | 2025 | 88.0809 | 95.0932 | 102.5335 | 109.927 | 117.3142
SmithvilleWind2030RCP4.5 | Smithville | Wind | RCP4.5 | 2030 | 88.0519 | 95.0634 | 102.5015 | 109.8928 | 117.2778
SmithvilleWind2035RCP4.5 | Smithville | Wind | RCP4.5 | 2035 | 88.0228 | 95.0337 | 102.4695 | 109.8586 | 117.2413
SmithvilleWind2040RCP4.5 | Smithville | Wind | RCP4.5 | 2040 | 87.9937 | 95.0039 | 102.4376 | 109.8243 | 117.2048
SmithvilleWind2045RCP4.5 | Smithville | Wind | RCP4.5 | 2045 | 87.9647 | 94.9742 | 102.4056 | 109.7901 | 117.1684
SmithvilleWind2050RCP4.5 | Smithville | Wind | RCP4.5 | 2050 | 87.9931 | 95.0177 | 102.4685 | 109.8661 | 117.2609
SmithvilleWind2055RCP4.5 | Smithville | Wind | RCP4.5 | 2055 | 88.0507 | 95.091 | 102.5635 | 109.9764 | 117.3898
SmithvilleWind2060RCP4.5 | Smithville | Wind | RCP4.5 | 2060 | 88.1083 | 95.1642 | 102.6584 | 110.0866 | 117.5188
SmithvilleWind2065RCP4.5 | Smithville | Wind | RCP4.5 | 2065 | 88.1658 | 95.2375 | 102.7534 | 110.1968 | 117.6477
SmithvilleWind2070RCP4.5 | Smithville | Wind | RCP4.5 | 2070 | 88.2234 | 95.3108 | 102.8483 | 110.307 | 117.7767
SmithvilleWind2075RCP4.5 | Smithville | Wind | RCP4.5 | 2075 | 88.3048 | 95.4251 | 103.0049 | 110.498 | 118.0051
SmithvilleWind2080RCP4.5 | Smithville | Wind | RCP4.5 | 2080 | 88.3862 | 95.5393 | 103.1614 | 110.6889 | 118.2334
SmithvilleWind2085RCP4.5 | Smithville | Wind | RCP4.5 | 2085 | 88.4676 | 95.6536 | 103.3179 | 110.8798 | 118.4618
SmithvilleWind2090RCP4.5 | Smithville | Wind | RCP4.5 | 2090 | 88.549 | 95.7679 | 103.4745 | 111.0707 | 118.6901
SmithvilleWind2095RCP4.5 | Smithville | Wind | RCP4.5 | 2095 | 88.6304 | 95.8822 | 103.6311 | 111.2617 | 118.9185
SmithvilleWind2100RCP4.5 | Smithville | Wind | RCP4.5 | 2100 | 88.7118 | 95.9965 | 103.7876 | 111.4526 | 119.1469
SmithvilleWind2023RCP6.0 | Smithville | Wind | RCP6.0 | 2023 | 88.11 | 95.1229 | 102.5655 | 109.9612 | 117.3507
SmithvilleWind2025RCP6.0 | Smithville | Wind | RCP6.0 | 2025 | 88.0809 | 95.0932 | 102.5335 | 109.927 | 117.3142
SmithvilleWind2030RCP6.0 | Smithville | Wind | RCP6.0 | 2030 | 88.0519 | 95.0634 | 102.5015 | 109.8928 | 117.2778
SmithvilleWind2035RCP6.0 | Smithville | Wind | RCP6.0 | 2035 | 88.0228 | 95.0337 | 102.4695 | 109.8586 | 117.2413
SmithvilleWind2040RCP6.0 | Smithville | Wind | RCP6.0 | 2040 | 87.9937 | 95.0039 | 102.4376 | 109.8243 | 117.2048
SmithvilleWind2045RCP6.0 | Smithville | Wind | RCP6.0 | 2045 | 87.9647 | 94.9742 | 102.4056 | 109.7901 | 117.1684
SmithvilleWind2050RCP6.0 | Smithville | Wind | RCP6.0 | 2050 | 87.9931 | 95.0177 | 102.4685 | 109.8661 | 117.2609
SmithvilleWind2055RCP6.0 | Smithville | Wind | RCP6.0 | 2055 | 88.0507 | 95.091 | 102.5635 | 109.9764 | 117.3898
SmithvilleWind2060RCP6.0 | Smithville | Wind | RCP6.0 | 2060 | 88.1083 | 95.1642 | 102.6584 | 110.0866 | 117.5188
SmithvilleWind2065RCP6.0 | Smithville | Wind | RCP6.0 | 2065 | 88.1658 | 95.2375 | 102.7534 | 110.1968 | 117.6477
SmithvilleWind2070RCP6.0 | Smithville | Wind | RCP6.0 | 2070 | 88.2234 | 95.3108 | 102.8483 | 110.307 | 117.7767
SmithvilleWind2075RCP6.0 | Smithville | Wind | RCP6.0 | 2075 | 88.3455 | 95.4822 | 103.0831 | 110.5934 | 118.1192
SmithvilleWind2080RCP6.0 | Smithville | Wind | RCP6.0 | 2080 | 88.4676 | 95.6536 | 103.3179 | 110.8798 | 118.4618
SmithvilleWind2085RCP6.0 | Smithville | Wind | RCP6.0 | 2085 | 88.5897 | 95.825 | 103.5528 | 111.1662 | 118.8043
SmithvilleWind2090RCP6.0 | Smithville | Wind | RCP6.0 | 2090 | 88.8978 | 96.2344 | 104.0872 | 111.8092 | 119.5614
SmithvilleWind2095RCP6.0 | Smithville | Wind | RCP6.0 | 2095 | 89.0839 | 96.4724 | 104.3869 | 112.1659 | 119.9759
SmithvilleWind2100RCP6.0 | Smithville | Wind | RCP6.0 | 2100 | 89.2699 | 96.7103 | 104.6865 | 112.5225 | 120.3904
SmithvilleWind2023RCP8.5 | Smithville | Wind | RCP8.5 | 2023 | 88.11 | 95.1229 | 102.5655 | 109.9612 | 117.3507
SmithvilleWind2025RCP8.5 | Smithville | Wind | RCP8.5 | 2025 | 88.0519 | 95.0634 | 102.5015 | 109.8928 | 117.2778
SmithvilleWind2030RCP8.5 | Smithville | Wind | RCP8.5 | 2030 | 87.9937 | 95.0039 | 102.4376 | 109.8243 | 117.2048
SmithvilleWind2035RCP8.5 | Smithville | Wind | RCP8.5 | 2035 | 87.9356 | 94.9444 | 102.3736 | 109.7559 | 117.1319
SmithvilleWind2040RCP8.5 | Smithville | Wind | RCP8.5 | 2040 | 88.0315 | 95.0666 | 102.5318 | 109.9396 | 117.3468
SmithvilleWind2045RCP8.5 | Smithville | Wind | RCP8.5 | 2045 | 88.1274 | 95.1887 | 102.6901 | 110.1233 | 117.5618
SmithvilleWind2050RCP8.5 | Smithville | Wind | RCP8.5 | 2050 | 88.3862 | 95.5393 | 103.1614 | 110.6889 | 118.2334
SmithvilleWind2055RCP8.5 | Smithville | Wind | RCP8.5 | 2055 | 88.549 | 95.7679 | 103.4745 | 111.0707 | 118.6901
SmithvilleWind2060RCP8.5 | Smithville | Wind | RCP8.5 | 2060 | 88.8978 | 96.2344 | 104.0872 | 111.8092 | 119.5614
SmithvilleWind2065RCP8.5 | Smithville | Wind | RCP8.5 | 2065 | 89.0839 | 96.4724 | 104.3869 | 112.1659 | 119.9759
SmithvilleWind2070RCP8.5 | Smithville | Wind | RCP8.5 | 2070 | 89.331 | 96.8137 | 104.8515 | 112.7386 | 120.6514
SmithvilleWind2075RCP8.5 | Smithville | Wind | RCP8.5 | 2075 | 89.392 | 96.917 | 105.0164 | 112.9548 | 120.9124
SmithvilleWind2080RCP8.5 | Smithville | Wind | RCP8.5 | 2080 | 89.4531 | 97.0203 | 105.1814 | 113.1709 | 121.1733
SmithvilleWind2085RCP8.5 | Smithville | Wind | RCP8.5 | 2085 | 89.5185 | 97.1283 | 105.338 | 113.3654 | 121.4151
SmithvilleWind2090RCP8.5 | Smithville | Wind | RCP8.5 | 2090 | 89.5839 | 97.2363 | 105.4945 | 113.56 | 121.6569
SmithvilleWind2095RCP8.5 | Smithville | Wind | RCP8.5 | 2095 | 89.5839 | 97.2363 | 105.4945 | 113.56 | 121.6569
SmithvilleWind2100RCP8.5 | Smithville | Wind | RCP8.5 | 2100 | 89.5839 | 97.2363 | 105.4945 | 113.56 | 121.6569
Smooth Rock FallsIce Accretion2023RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2023 | 11.256 | 13.4128 | 16.144 | 18.2246 | 20.3213
Smooth Rock FallsIce Accretion2025RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2025 | 11.2542 | 13.4084 | 16.136 | 18.2156 | 20.3078
Smooth Rock FallsIce Accretion2030RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2030 | 11.2523 | 13.4039 | 16.128 | 18.2066 | 20.2944
Smooth Rock FallsIce Accretion2035RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2035 | 11.2504 | 13.3995 | 16.12 | 18.1975 | 20.281
Smooth Rock FallsIce Accretion2040RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2040 | 11.2486 | 13.3951 | 16.112 | 18.1885 | 20.2675
Smooth Rock FallsIce Accretion2045RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2045 | 11.2467 | 13.3907 | 16.104 | 18.1794 | 20.2541
Smooth Rock FallsIce Accretion2050RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2050 | 11.3495 | 13.5164 | 16.2592 | 18.3584 | 20.4543
Smooth Rock FallsIce Accretion2055RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2055 | 11.4542 | 13.6465 | 16.4224 | 18.5465 | 20.668
Smooth Rock FallsIce Accretion2060RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2060 | 11.5588 | 13.7767 | 16.5856 | 18.7345 | 20.8817
Smooth Rock FallsIce Accretion2065RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2065 | 11.6635 | 13.9068 | 16.7488 | 18.9225 | 21.0954
Smooth Rock FallsIce Accretion2070RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2070 | 11.7681 | 14.037 | 16.912 | 19.1106 | 21.3091
Smooth Rock FallsIce Accretion2075RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2075 | 11.8034 | 14.079 | 16.9627 | 19.1678 | 21.373
Smooth Rock FallsIce Accretion2080RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2080 | 11.8387 | 14.1211 | 17.0133 | 19.2251 | 21.4368
Smooth Rock FallsIce Accretion2085RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2085 | 11.8739 | 14.1631 | 17.064 | 19.2823 | 21.5006
Smooth Rock FallsIce Accretion2090RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2090 | 11.9092 | 14.2052 | 17.1147 | 19.3396 | 21.5645
Smooth Rock FallsIce Accretion2095RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2095 | 11.9444 | 14.2472 | 17.1653 | 19.3968 | 21.6283
Smooth Rock FallsIce Accretion2100RCP4.5 | Smooth Rock Falls | Ice Accretion | RCP4.5 | 2100 | 11.9797 | 14.2893 | 17.216 | 19.4541 | 21.6922
Smooth Rock FallsIce Accretion2023RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2023 | 11.256 | 13.4128 | 16.144 | 18.2246 | 20.3213
Smooth Rock FallsIce Accretion2025RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2025 | 11.2542 | 13.4084 | 16.136 | 18.2156 | 20.3078
Smooth Rock FallsIce Accretion2030RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2030 | 11.2523 | 13.4039 | 16.128 | 18.2066 | 20.2944
Smooth Rock FallsIce Accretion2035RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2035 | 11.2504 | 13.3995 | 16.12 | 18.1975 | 20.281
Smooth Rock FallsIce Accretion2040RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2040 | 11.2486 | 13.3951 | 16.112 | 18.1885 | 20.2675
Smooth Rock FallsIce Accretion2045RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2045 | 11.2467 | 13.3907 | 16.104 | 18.1794 | 20.2541
Smooth Rock FallsIce Accretion2050RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2050 | 11.3495 | 13.5164 | 16.2592 | 18.3584 | 20.4543
Smooth Rock FallsIce Accretion2055RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2055 | 11.4542 | 13.6465 | 16.4224 | 18.5465 | 20.668
Smooth Rock FallsIce Accretion2060RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2060 | 11.5588 | 13.7767 | 16.5856 | 18.7345 | 20.8817
Smooth Rock FallsIce Accretion2065RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2065 | 11.6635 | 13.9068 | 16.7488 | 18.9225 | 21.0954
Smooth Rock FallsIce Accretion2070RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2070 | 11.7681 | 14.037 | 16.912 | 19.1106 | 21.3091
Smooth Rock FallsIce Accretion2075RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2075 | 11.821 | 14.1 | 16.988 | 19.1964 | 21.4049
Smooth Rock FallsIce Accretion2080RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2080 | 11.8739 | 14.1631 | 17.064 | 19.2823 | 21.5006
Smooth Rock FallsIce Accretion2085RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2085 | 11.9268 | 14.2262 | 17.14 | 19.3682 | 21.5964
Smooth Rock FallsIce Accretion2090RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2090 | 11.9277 | 14.2583 | 17.2053 | 19.4601 | 21.7123
Smooth Rock FallsIce Accretion2095RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2095 | 11.8758 | 14.2273 | 17.1947 | 19.4661 | 21.7325
Smooth Rock FallsIce Accretion2100RCP6.0 | Smooth Rock Falls | Ice Accretion | RCP6.0 | 2100 | 11.8238 | 14.1963 | 17.184 | 19.4722 | 21.7526
Smooth Rock FallsIce Accretion2023RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2023 | 11.256 | 13.4128 | 16.144 | 18.2246 | 20.3213
Smooth Rock FallsIce Accretion2025RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2025 | 11.2523 | 13.4039 | 16.128 | 18.2066 | 20.2944
Smooth Rock FallsIce Accretion2030RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2030 | 11.2486 | 13.3951 | 16.112 | 18.1885 | 20.2675
Smooth Rock FallsIce Accretion2035RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2035 | 11.2449 | 13.3862 | 16.096 | 18.1704 | 20.2406
Smooth Rock FallsIce Accretion2040RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2040 | 11.4193 | 13.6031 | 16.368 | 18.4838 | 20.5968
Smooth Rock FallsIce Accretion2045RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2045 | 11.5937 | 13.8201 | 16.64 | 18.7972 | 20.953
Smooth Rock FallsIce Accretion2050RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2050 | 11.8387 | 14.1211 | 17.0133 | 19.2251 | 21.4368
Smooth Rock FallsIce Accretion2055RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2055 | 11.9092 | 14.2052 | 17.1147 | 19.3396 | 21.5645
Smooth Rock FallsIce Accretion2060RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2060 | 11.9277 | 14.2583 | 17.2053 | 19.4601 | 21.7123
Smooth Rock FallsIce Accretion2065RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2065 | 11.8758 | 14.2273 | 17.1947 | 19.4661 | 21.7325
Smooth Rock FallsIce Accretion2070RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2070 | 11.7978 | 14.1742 | 17.1787 | 19.4722 | 21.7594
Smooth Rock FallsIce Accretion2075RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2075 | 11.7719 | 14.1521 | 17.1733 | 19.4722 | 21.7661
Smooth Rock FallsIce Accretion2080RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2080 | 11.7459 | 14.1299 | 17.168 | 19.4722 | 21.7728
Smooth Rock FallsIce Accretion2085RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2085 | 11.5789 | 13.9706 | 17 | 19.3094 | 21.6115
Smooth Rock FallsIce Accretion2090RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2090 | 11.4119 | 13.8112 | 16.832 | 19.1467 | 21.4502
Smooth Rock FallsIce Accretion2095RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2095 | 11.4119 | 13.8112 | 16.832 | 19.1467 | 21.4502
Smooth Rock FallsIce Accretion2100RCP8.5 | Smooth Rock Falls | Ice Accretion | RCP8.5 | 2100 | 11.4119 | 13.8112 | 16.832 | 19.1467 | 21.4502
Smooth Rock FallsWind2023RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2023 | 73.0185 | 78.6278 | 84.5292 | 90.4283 | 96.3346
Smooth Rock FallsWind2025RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2025 | 73.1152 | 78.7371 | 84.6524 | 90.5646 | 96.483
Smooth Rock FallsWind2030RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2030 | 73.2119 | 78.8465 | 84.7756 | 90.7009 | 96.6314
Smooth Rock FallsWind2035RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2035 | 73.3086 | 78.9559 | 84.8988 | 90.8372 | 96.7798
Smooth Rock FallsWind2040RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2040 | 73.4053 | 79.0653 | 85.022 | 90.9735 | 96.9283
Smooth Rock FallsWind2045RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2045 | 73.502 | 79.1746 | 85.1452 | 91.1099 | 97.0767
Smooth Rock FallsWind2050RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2050 | 73.6292 | 79.3152 | 85.3003 | 91.2803 | 97.2615
Smooth Rock FallsWind2055RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2055 | 73.6597 | 79.3465 | 85.3322 | 91.3145 | 97.2979
Smooth Rock FallsWind2060RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2060 | 73.6901 | 79.3777 | 85.3642 | 91.3486 | 97.3343
Smooth Rock FallsWind2065RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2065 | 73.7206 | 79.409 | 85.3961 | 91.3828 | 97.3707
Smooth Rock FallsWind2070RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2070 | 73.7511 | 79.4402 | 85.428 | 91.4169 | 97.4071
Smooth Rock FallsWind2075RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2075 | 73.7499 | 79.4142 | 85.3706 | 91.3331 | 97.2954
Smooth Rock FallsWind2080RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2080 | 73.7487 | 79.3881 | 85.3132 | 91.2492 | 97.1836
Smooth Rock FallsWind2085RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2085 | 73.7474 | 79.3621 | 85.2558 | 91.1653 | 97.0719
Smooth Rock FallsWind2090RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2090 | 73.7462 | 79.3361 | 85.1984 | 91.0814 | 96.9602
Smooth Rock FallsWind2095RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2095 | 73.745 | 79.31 | 85.141 | 90.9975 | 96.8485
Smooth Rock FallsWind2100RCP4.5 | Smooth Rock Falls | Wind | RCP4.5 | 2100 | 73.7438 | 79.284 | 85.0836 | 90.9136 | 96.7368
Smooth Rock FallsWind2023RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2023 | 73.0185 | 78.6278 | 84.5292 | 90.4283 | 96.3346
Smooth Rock FallsWind2025RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2025 | 73.1152 | 78.7371 | 84.6524 | 90.5646 | 96.483
Smooth Rock FallsWind2030RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2030 | 73.2119 | 78.8465 | 84.7756 | 90.7009 | 96.6314
Smooth Rock FallsWind2035RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2035 | 73.3086 | 78.9559 | 84.8988 | 90.8372 | 96.7798
Smooth Rock FallsWind2040RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2040 | 73.4053 | 79.0653 | 85.022 | 90.9735 | 96.9283
Smooth Rock FallsWind2045RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2045 | 73.502 | 79.1746 | 85.1452 | 91.1099 | 97.0767
Smooth Rock FallsWind2050RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2050 | 73.6292 | 79.3152 | 85.3003 | 91.2803 | 97.2615
Smooth Rock FallsWind2055RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2055 | 73.6597 | 79.3465 | 85.3322 | 91.3145 | 97.2979
Smooth Rock FallsWind2060RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2060 | 73.6901 | 79.3777 | 85.3642 | 91.3486 | 97.3343
Smooth Rock FallsWind2065RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2065 | 73.7206 | 79.409 | 85.3961 | 91.3828 | 97.3707
Smooth Rock FallsWind2070RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2070 | 73.7511 | 79.4402 | 85.428 | 91.4169 | 97.4071
Smooth Rock FallsWind2075RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2075 | 73.7493 | 79.4012 | 85.3419 | 91.2911 | 97.2395
Smooth Rock FallsWind2080RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2080 | 73.7474 | 79.3621 | 85.2558 | 91.1653 | 97.0719
Smooth Rock FallsWind2085RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2085 | 73.7456 | 79.323 | 85.1697 | 91.0395 | 96.9043
Smooth Rock FallsWind2090RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2090 | 73.8913 | 79.4559 | 85.2824 | 91.1383 | 96.9889
Smooth Rock FallsWind2095RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2095 | 74.0388 | 79.6277 | 85.4812 | 91.363 | 97.2411
Smooth Rock FallsWind2100RCP6.0 | Smooth Rock Falls | Wind | RCP6.0 | 2100 | 74.1863 | 79.7996 | 85.68 | 91.5877 | 97.4933
Smooth Rock FallsWind2023RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2023 | 73.0185 | 78.6278 | 84.5292 | 90.4283 | 96.3346
Smooth Rock FallsWind2025RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2025 | 73.2119 | 78.8465 | 84.7756 | 90.7009 | 96.6314
Smooth Rock FallsWind2030RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2030 | 73.4053 | 79.0653 | 85.022 | 90.9735 | 96.9283
Smooth Rock FallsWind2035RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2035 | 73.5988 | 79.284 | 85.2684 | 91.2462 | 97.2251
Smooth Rock FallsWind2040RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2040 | 73.6495 | 79.3361 | 85.3216 | 91.3031 | 97.2858
Smooth Rock FallsWind2045RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2045 | 73.7003 | 79.3881 | 85.3748 | 91.36 | 97.3464
Smooth Rock FallsWind2050RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2050 | 73.7487 | 79.3881 | 85.3132 | 91.2492 | 97.1836
Smooth Rock FallsWind2055RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2055 | 73.7462 | 79.3361 | 85.1984 | 91.0814 | 96.9602
Smooth Rock FallsWind2060RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2060 | 73.8913 | 79.4559 | 85.2824 | 91.1383 | 96.9889
Smooth Rock FallsWind2065RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2065 | 74.0388 | 79.6277 | 85.4812 | 91.363 | 97.2411
Smooth Rock FallsWind2070RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2070 | 74.3337 | 79.9584 | 85.8536 | 91.7735 | 97.6944
Smooth Rock FallsWind2075RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2075 | 74.4812 | 80.1173 | 86.0272 | 91.9592 | 97.8954
Smooth Rock FallsWind2080RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2080 | 74.6287 | 80.2761 | 86.2008 | 92.145 | 98.0965
Smooth Rock FallsWind2085RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2085 | 74.7919 | 80.4831 | 86.4612 | 92.4506 | 98.4461
Smooth Rock FallsWind2090RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2090 | 74.9551 | 80.6901 | 86.7216 | 92.7562 | 98.7956
Smooth Rock FallsWind2095RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2095 | 74.9551 | 80.6901 | 86.7216 | 92.7562 | 98.7956
Smooth Rock FallsWind2100RCP8.5 | Smooth Rock Falls | Wind | RCP8.5 | 2100 | 74.9551 | 80.6901 | 86.7216 | 92.7562 | 98.7956
South RiverIce Accretion2023RCP4.5 | South River | Ice Accretion | RCP4.5 | 2023 | 15.2321 | 18.1504 | 21.868 | 24.7108 | 27.526
South RiverIce Accretion2025RCP4.5 | South River | Ice Accretion | RCP4.5 | 2025 | 15.3086 | 18.2509 | 22 | 24.8641 | 27.7061
South RiverIce Accretion2030RCP4.5 | South River | Ice Accretion | RCP4.5 | 2030 | 15.3852 | 18.3513 | 22.132 | 25.0174 | 27.8863
South RiverIce Accretion2035RCP4.5 | South River | Ice Accretion | RCP4.5 | 2035 | 15.4617 | 18.4517 | 22.264 | 25.1707 | 28.0665
South RiverIce Accretion2040RCP4.5 | South River | Ice Accretion | RCP4.5 | 2040 | 15.5382 | 18.5522 | 22.396 | 25.3241 | 28.2467
South RiverIce Accretion2045RCP4.5 | South River | Ice Accretion | RCP4.5 | 2045 | 15.6148 | 18.6526 | 22.528 | 25.4774 | 28.4269
South RiverIce Accretion2050RCP4.5 | South River | Ice Accretion | RCP4.5 | 2050 | 15.7373 | 18.8261 | 22.7612 | 25.755 | 28.7512
South RiverIce Accretion2055RCP4.5 | South River | Ice Accretion | RCP4.5 | 2055 | 15.7832 | 18.8991 | 22.8624 | 25.8793 | 28.8953
South RiverIce Accretion2060RCP4.5 | South River | Ice Accretion | RCP4.5 | 2060 | 15.8291 | 18.9721 | 22.9636 | 26.0036 | 29.0395
South RiverIce Accretion2065RCP4.5 | South River | Ice Accretion | RCP4.5 | 2065 | 15.875 | 19.0452 | 23.0648 | 26.1279 | 29.1836
South RiverIce Accretion2070RCP4.5 | South River | Ice Accretion | RCP4.5 | 2070 | 15.921 | 19.1182 | 23.166 | 26.2522 | 29.3278
South RiverIce Accretion2075RCP4.5 | South River | Ice Accretion | RCP4.5 | 2075 | 15.9235 | 19.1395 | 23.21 | 26.3143 | 29.4109
South RiverIce Accretion2080RCP4.5 | South River | Ice Accretion | RCP4.5 | 2080 | 15.9261 | 19.1608 | 23.254 | 26.3765 | 29.4941
South RiverIce Accretion2085RCP4.5 | South River | Ice Accretion | RCP4.5 | 2085 | 15.9286 | 19.1821 | 23.298 | 26.4386 | 29.5772
South RiverIce Accretion2090RCP4.5 | South River | Ice Accretion | RCP4.5 | 2090 | 15.9312 | 19.2034 | 23.342 | 26.5008 | 29.6604
South RiverIce Accretion2095RCP4.5 | South River | Ice Accretion | RCP4.5 | 2095 | 15.9337 | 19.2247 | 23.386 | 26.5629 | 29.7436
South RiverIce Accretion2100RCP4.5 | South River | Ice Accretion | RCP4.5 | 2100 | 15.9363 | 19.246 | 23.43 | 26.6251 | 29.8267
South RiverIce Accretion2023RCP6.0 | South River | Ice Accretion | RCP6.0 | 2023 | 15.2321 | 18.1504 | 21.868 | 24.7108 | 27.526
South RiverIce Accretion2025RCP6.0 | South River | Ice Accretion | RCP6.0 | 2025 | 15.3086 | 18.2509 | 22 | 24.8641 | 27.7061
South RiverIce Accretion2030RCP6.0 | South River | Ice Accretion | RCP6.0 | 2030 | 15.3852 | 18.3513 | 22.132 | 25.0174 | 27.8863
South RiverIce Accretion2035RCP6.0 | South River | Ice Accretion | RCP6.0 | 2035 | 15.4617 | 18.4517 | 22.264 | 25.1707 | 28.0665
South RiverIce Accretion2040RCP6.0 | South River | Ice Accretion | RCP6.0 | 2040 | 15.5382 | 18.5522 | 22.396 | 25.3241 | 28.2467
South RiverIce Accretion2045RCP6.0 | South River | Ice Accretion | RCP6.0 | 2045 | 15.6148 | 18.6526 | 22.528 | 25.4774 | 28.4269
South RiverIce Accretion2050RCP6.0 | South River | Ice Accretion | RCP6.0 | 2050 | 15.7373 | 18.8261 | 22.7612 | 25.755 | 28.7512
South RiverIce Accretion2055RCP6.0 | South River | Ice Accretion | RCP6.0 | 2055 | 15.7832 | 18.8991 | 22.8624 | 25.8793 | 28.8953
South RiverIce Accretion2060RCP6.0 | South River | Ice Accretion | RCP6.0 | 2060 | 15.8291 | 18.9721 | 22.9636 | 26.0036 | 29.0395
South RiverIce Accretion2065RCP6.0 | South River | Ice Accretion | RCP6.0 | 2065 | 15.875 | 19.0452 | 23.0648 | 26.1279 | 29.1836
South RiverIce Accretion2070RCP6.0 | South River | Ice Accretion | RCP6.0 | 2070 | 15.921 | 19.1182 | 23.166 | 26.2522 | 29.3278
South RiverIce Accretion2075RCP6.0 | South River | Ice Accretion | RCP6.0 | 2075 | 15.9248 | 19.1502 | 23.232 | 26.3454 | 29.4525
South RiverIce Accretion2080RCP6.0 | South River | Ice Accretion | RCP6.0 | 2080 | 15.9286 | 19.1821 | 23.298 | 26.4386 | 29.5772
South RiverIce Accretion2085RCP6.0 | South River | Ice Accretion | RCP6.0 | 2085 | 15.9324 | 19.2141 | 23.364 | 26.5318 | 29.702
South RiverIce Accretion2090RCP6.0 | South River | Ice Accretion | RCP6.0 | 2090 | 15.9618 | 19.2947 | 23.5107 | 26.7328 | 29.9468
South RiverIce Accretion2095RCP6.0 | South River | Ice Accretion | RCP6.0 | 2095 | 15.9873 | 19.3434 | 23.5913 | 26.8405 | 30.067
South RiverIce Accretion2100RCP6.0 | South River | Ice Accretion | RCP6.0 | 2100 | 16.0128 | 19.3921 | 23.672 | 26.9482 | 30.1871
South RiverIce Accretion2023RCP8.5 | South River | Ice Accretion | RCP8.5 | 2023 | 15.2321 | 18.1504 | 21.868 | 24.7108 | 27.526
South RiverIce Accretion2025RCP8.5 | South River | Ice Accretion | RCP8.5 | 2025 | 15.3852 | 18.3513 | 22.132 | 25.0174 | 27.8863
South RiverIce Accretion2030RCP8.5 | South River | Ice Accretion | RCP8.5 | 2030 | 15.5382 | 18.5522 | 22.396 | 25.3241 | 28.2467
South RiverIce Accretion2035RCP8.5 | South River | Ice Accretion | RCP8.5 | 2035 | 15.6913 | 18.753 | 22.66 | 25.6307 | 28.607
South RiverIce Accretion2040RCP8.5 | South River | Ice Accretion | RCP8.5 | 2040 | 15.7679 | 18.8748 | 22.8287 | 25.8378 | 28.8473
South RiverIce Accretion2045RCP8.5 | South River | Ice Accretion | RCP8.5 | 2045 | 15.8444 | 18.9965 | 22.9973 | 26.045 | 29.0875
South RiverIce Accretion2050RCP8.5 | South River | Ice Accretion | RCP8.5 | 2050 | 15.9261 | 19.1608 | 23.254 | 26.3765 | 29.4941
South RiverIce Accretion2055RCP8.5 | South River | Ice Accretion | RCP8.5 | 2055 | 15.9312 | 19.2034 | 23.342 | 26.5008 | 29.6604
South RiverIce Accretion2060RCP8.5 | South River | Ice Accretion | RCP8.5 | 2060 | 15.9618 | 19.2947 | 23.5107 | 26.7328 | 29.9468
South RiverIce Accretion2065RCP8.5 | South River | Ice Accretion | RCP8.5 | 2065 | 15.9873 | 19.3434 | 23.5913 | 26.8405 | 30.067
South RiverIce Accretion2070RCP8.5 | South River | Ice Accretion | RCP8.5 | 2070 | 15.8801 | 19.2521 | 23.5253 | 26.7908 | 30.03
South RiverIce Accretion2075RCP8.5 | South River | Ice Accretion | RCP8.5 | 2075 | 15.7475 | 19.1121 | 23.3787 | 26.6333 | 29.8729
South RiverIce Accretion2080RCP8.5 | South River | Ice Accretion | RCP8.5 | 2080 | 15.6148 | 18.9721 | 23.232 | 26.4759 | 29.7158
South RiverIce Accretion2085RCP8.5 | South River | Ice Accretion | RCP8.5 | 2085 | 15.2091 | 18.5248 | 22.715 | 25.9166 | 29.106
South RiverIce Accretion2090RCP8.5 | South River | Ice Accretion | RCP8.5 | 2090 | 14.8034 | 18.0774 | 22.198 | 25.3572 | 28.4962
South RiverIce Accretion2095RCP8.5 | South River | Ice Accretion | RCP8.5 | 2095 | 14.8034 | 18.0774 | 22.198 | 25.3572 | 28.4962
South RiverIce Accretion2100RCP8.5 | South River | Ice Accretion | RCP8.5 | 2100 | 14.8034 | 18.0774 | 22.198 | 25.3572 | 28.4962
South RiverWind2023RCP4.5 | South River | Wind | RCP4.5 | 2023 | 69.3273 | 74.6976 | 80.36 | 86.0109 | 91.6651
South RiverWind2025RCP4.5 | South River | Wind | RCP4.5 | 2025 | 69.371 | 74.7559 | 80.436 | 86.1008 | 91.77
South RiverWind2030RCP4.5 | South River | Wind | RCP4.5 | 2030 | 69.4148 | 74.8142 | 80.512 | 86.1906 | 91.8749
South RiverWind2035RCP4.5 | South River | Wind | RCP4.5 | 2035 | 69.4585 | 74.8724 | 80.588 | 86.2805 | 91.9798
South RiverWind2040RCP4.5 | South River | Wind | RCP4.5 | 2040 | 69.5023 | 74.9307 | 80.664 | 86.3704 | 92.0846
South RiverWind2045RCP4.5 | South River | Wind | RCP4.5 | 2045 | 69.546 | 74.989 | 80.74 | 86.4603 | 92.1895
South RiverWind2050RCP4.5 | South River | Wind | RCP4.5 | 2050 | 69.5842 | 75.0309 | 80.784 | 86.5091 | 92.2397
South RiverWind2055RCP4.5 | South River | Wind | RCP4.5 | 2055 | 69.5787 | 75.0145 | 80.752 | 86.468 | 92.185
South RiverWind2060RCP4.5 | South River | Wind | RCP4.5 | 2060 | 69.5732 | 74.9982 | 80.72 | 86.4269 | 92.1302
South RiverWind2065RCP4.5 | South River | Wind | RCP4.5 | 2065 | 69.5677 | 74.9818 | 80.688 | 86.3858 | 92.0755
South RiverWind2070RCP4.5 | South River | Wind | RCP4.5 | 2070 | 69.5621 | 74.9654 | 80.656 | 86.3447 | 92.0208
South RiverWind2075RCP4.5 | South River | Wind | RCP4.5 | 2075 | 69.6347 | 75.0485 | 80.7533 | 86.4531 | 92.1424
South RiverWind2080RCP4.5 | South River | Wind | RCP4.5 | 2080 | 69.7072 | 75.1316 | 80.8507 | 86.5616 | 92.264
South RiverWind2085RCP4.5 | South River | Wind | RCP4.5 | 2085 | 69.7797 | 75.2147 | 80.948 | 86.67 | 92.3856
South RiverWind2090RCP4.5 | South River | Wind | RCP4.5 | 2090 | 69.8523 | 75.2978 | 81.0453 | 86.7784 | 92.5072
South RiverWind2095RCP4.5 | South River | Wind | RCP4.5 | 2095 | 69.9248 | 75.3808 | 81.1427 | 86.8869 | 92.6288
South RiverWind2100RCP4.5 | South River | Wind | RCP4.5 | 2100 | 69.9973 | 75.4639 | 81.24 | 86.9953 | 92.7504
South RiverWind2023RCP6.0 | South River | Wind | RCP6.0 | 2023 | 69.3273 | 74.6976 | 80.36 | 86.0109 | 91.6651
South RiverWind2025RCP6.0 | South River | Wind | RCP6.0 | 2025 | 69.371 | 74.7559 | 80.436 | 86.1008 | 91.77
South RiverWind2030RCP6.0 | South River | Wind | RCP6.0 | 2030 | 69.4148 | 74.8142 | 80.512 | 86.1906 | 91.8749
South RiverWind2035RCP6.0 | South River | Wind | RCP6.0 | 2035 | 69.4585 | 74.8724 | 80.588 | 86.2805 | 91.9798
South RiverWind2040RCP6.0 | South River | Wind | RCP6.0 | 2040 | 69.5023 | 74.9307 | 80.664 | 86.3704 | 92.0846
South RiverWind2045RCP6.0 | South River | Wind | RCP6.0 | 2045 | 69.546 | 74.989 | 80.74 | 86.4603 | 92.1895
South RiverWind2050RCP6.0 | South River | Wind | RCP6.0 | 2050 | 69.5842 | 75.0309 | 80.784 | 86.5091 | 92.2397
South RiverWind2055RCP6.0 | South River | Wind | RCP6.0 | 2055 | 69.5787 | 75.0145 | 80.752 | 86.468 | 92.185
South RiverWind2060RCP6.0 | South River | Wind | RCP6.0 | 2060 | 69.5732 | 74.9982 | 80.72 | 86.4269 | 92.1302
South RiverWind2065RCP6.0 | South River | Wind | RCP6.0 | 2065 | 69.5677 | 74.9818 | 80.688 | 86.3858 | 92.0755
South RiverWind2070RCP6.0 | South River | Wind | RCP6.0 | 2070 | 69.5621 | 74.9654 | 80.656 | 86.3447 | 92.0208
South RiverWind2075RCP6.0 | South River | Wind | RCP6.0 | 2075 | 69.6709 | 75.0901 | 80.802 | 86.5074 | 92.2032
South RiverWind2080RCP6.0 | South River | Wind | RCP6.0 | 2080 | 69.7797 | 75.2147 | 80.948 | 86.67 | 92.3856
South RiverWind2085RCP6.0 | South River | Wind | RCP6.0 | 2085 | 69.8885 | 75.3393 | 81.094 | 86.8326 | 92.568
South RiverWind2090RCP6.0 | South River | Wind | RCP6.0 | 2090 | 69.8638 | 75.2978 | 81.0293 | 86.7499 | 92.4677
South RiverWind2095RCP6.0 | South River | Wind | RCP6.0 | 2095 | 69.7302 | 75.1316 | 80.8187 | 86.5045 | 92.185
South RiverWind2100RCP6.0 | South River | Wind | RCP6.0 | 2100 | 69.5967 | 74.9654 | 80.608 | 86.2591 | 91.9022
South RiverWind2023RCP8.5 | South River | Wind | RCP8.5 | 2023 | 69.3273 | 74.6976 | 80.36 | 86.0109 | 91.6651
South RiverWind2025RCP8.5 | South River | Wind | RCP8.5 | 2025 | 69.4148 | 74.8142 | 80.512 | 86.1906 | 91.8749
South RiverWind2030RCP8.5 | South River | Wind | RCP8.5 | 2030 | 69.5023 | 74.9307 | 80.664 | 86.3704 | 92.0846
South RiverWind2035RCP8.5 | South River | Wind | RCP8.5 | 2035 | 69.5898 | 75.0473 | 80.816 | 86.5502 | 92.2944
South RiverWind2040RCP8.5 | South River | Wind | RCP8.5 | 2040 | 69.5806 | 75.02 | 80.7627 | 86.4817 | 92.2032
South RiverWind2045RCP8.5 | South River | Wind | RCP8.5 | 2045 | 69.5714 | 74.9927 | 80.7093 | 86.4132 | 92.112
South RiverWind2050RCP8.5 | South River | Wind | RCP8.5 | 2050 | 69.7072 | 75.1316 | 80.8507 | 86.5616 | 92.264
South RiverWind2055RCP8.5 | South River | Wind | RCP8.5 | 2055 | 69.8523 | 75.2978 | 81.0453 | 86.7784 | 92.5072
South RiverWind2060RCP8.5 | South River | Wind | RCP8.5 | 2060 | 69.8638 | 75.2978 | 81.0293 | 86.7499 | 92.4677
South RiverWind2065RCP8.5 | South River | Wind | RCP8.5 | 2065 | 69.7302 | 75.1316 | 80.8187 | 86.5045 | 92.185
South RiverWind2070RCP8.5 | South River | Wind | RCP8.5 | 2070 | 69.7302 | 75.1266 | 80.808 | 86.4874 | 92.1637
South RiverWind2075RCP8.5 | South River | Wind | RCP8.5 | 2075 | 69.8638 | 75.2878 | 81.008 | 86.7157 | 92.4251
South RiverWind2080RCP8.5 | South River | Wind | RCP8.5 | 2080 | 69.9973 | 75.449 | 81.208 | 86.9439 | 92.6866
South RiverWind2085RCP8.5 | South River | Wind | RCP8.5 | 2085 | 70.0284 | 75.4676 | 81.208 | 86.9311 | 92.6592
South RiverWind2090RCP8.5 | South River | Wind | RCP8.5 | 2090 | 70.0595 | 75.4862 | 81.208 | 86.9182 | 92.6318
South RiverWind2095RCP8.5 | South River | Wind | RCP8.5 | 2095 | 70.0595 | 75.4862 | 81.208 | 86.9182 | 92.6318
South RiverWind2100RCP8.5 | South River | Wind | RCP8.5 | 2100 | 70.0595 | 75.4862 | 81.208 | 86.9182 | 92.6318
SouthamptonIce Accretion2023RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2023 | 13.9865 | 16.7162 | 20.18 | 22.8486 | 25.4772
SouthamptonIce Accretion2025RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2025 | 13.9958 | 16.7383 | 20.2167 | 22.8938 | 25.536
SouthamptonIce Accretion2030RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2030 | 14.0051 | 16.7605 | 20.2533 | 22.939 | 25.5948
SouthamptonIce Accretion2035RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2035 | 14.0143 | 16.7826 | 20.29 | 22.9842 | 25.6536
SouthamptonIce Accretion2040RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2040 | 14.0236 | 16.8047 | 20.3267 | 23.0294 | 25.7124
SouthamptonIce Accretion2045RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2045 | 14.0329 | 16.8269 | 20.3633 | 23.0746 | 25.7712
SouthamptonIce Accretion2050RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2050 | 13.9921 | 16.8025 | 20.36 | 23.0836 | 25.7947
SouthamptonIce Accretion2055RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2055 | 13.942 | 16.756 | 20.32 | 23.0475 | 25.7594
SouthamptonIce Accretion2060RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2060 | 13.8919 | 16.7096 | 20.28 | 23.0113 | 25.7242
SouthamptonIce Accretion2065RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2065 | 13.8418 | 16.6631 | 20.24 | 22.9752 | 25.6889
SouthamptonIce Accretion2070RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2070 | 13.7917 | 16.6166 | 20.2 | 22.939 | 25.6536
SouthamptonIce Accretion2075RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2075 | 13.7406 | 16.5806 | 20.18 | 22.9277 | 25.6536
SouthamptonIce Accretion2080RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2080 | 13.6896 | 16.5447 | 20.16 | 22.9164 | 25.6536
SouthamptonIce Accretion2085RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2085 | 13.6386 | 16.5087 | 20.14 | 22.9051 | 25.6536
SouthamptonIce Accretion2090RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2090 | 13.5876 | 16.4727 | 20.12 | 22.8938 | 25.6536
SouthamptonIce Accretion2095RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2095 | 13.5365 | 16.4368 | 20.1 | 22.8825 | 25.6536
SouthamptonIce Accretion2100RCP4.5 | Southampton | Ice Accretion | RCP4.5 | 2100 | 13.4855 | 16.4008 | 20.08 | 22.8712 | 25.6536
SouthamptonIce Accretion2023RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2023 | 13.9865 | 16.7162 | 20.18 | 22.8486 | 25.4772
SouthamptonIce Accretion2025RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2025 | 13.9958 | 16.7383 | 20.2167 | 22.8938 | 25.536
SouthamptonIce Accretion2030RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2030 | 14.0051 | 16.7605 | 20.2533 | 22.939 | 25.5948
SouthamptonIce Accretion2035RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2035 | 14.0143 | 16.7826 | 20.29 | 22.9842 | 25.6536
SouthamptonIce Accretion2040RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2040 | 14.0236 | 16.8047 | 20.3267 | 23.0294 | 25.7124
SouthamptonIce Accretion2045RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2045 | 14.0329 | 16.8269 | 20.3633 | 23.0746 | 25.7712
SouthamptonIce Accretion2050RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2050 | 13.9921 | 16.8025 | 20.36 | 23.0836 | 25.7947
SouthamptonIce Accretion2055RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2055 | 13.942 | 16.756 | 20.32 | 23.0475 | 25.7594
SouthamptonIce Accretion2060RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2060 | 13.8919 | 16.7096 | 20.28 | 23.0113 | 25.7242
SouthamptonIce Accretion2065RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2065 | 13.8418 | 16.6631 | 20.24 | 22.9752 | 25.6889
SouthamptonIce Accretion2070RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2070 | 13.7917 | 16.6166 | 20.2 | 22.939 | 25.6536
SouthamptonIce Accretion2075RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2075 | 13.7151 | 16.5626 | 20.17 | 22.922 | 25.6536
SouthamptonIce Accretion2080RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2080 | 13.6386 | 16.5087 | 20.14 | 22.9051 | 25.6536
SouthamptonIce Accretion2085RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2085 | 13.562 | 16.4547 | 20.11 | 22.8881 | 25.6536
SouthamptonIce Accretion2090RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2090 | 13.2489 | 16.1518 | 19.8067 | 22.5849 | 25.3512
SouthamptonIce Accretion2095RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2095 | 13.0123 | 15.9028 | 19.5333 | 22.2987 | 25.0488
SouthamptonIce Accretion2100RCP6.0 | Southampton | Ice Accretion | RCP6.0 | 2100 | 12.7757 | 15.6538 | 19.26 | 22.0124 | 24.7464
SouthamptonIce Accretion2023RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2023 | 13.9865 | 16.7162 | 20.18 | 22.8486 | 25.4772
SouthamptonIce Accretion2025RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2025 | 14.0051 | 16.7605 | 20.2533 | 22.939 | 25.5948
SouthamptonIce Accretion2030RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2030 | 14.0236 | 16.8047 | 20.3267 | 23.0294 | 25.7124
SouthamptonIce Accretion2035RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2035 | 14.0422 | 16.849 | 20.4 | 23.1198 | 25.83
SouthamptonIce Accretion2040RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2040 | 13.9587 | 16.7715 | 20.3333 | 23.0595 | 25.7712
SouthamptonIce Accretion2045RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2045 | 13.8752 | 16.6941 | 20.2667 | 22.9993 | 25.7124
SouthamptonIce Accretion2050RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2050 | 13.6896 | 16.5447 | 20.16 | 22.9164 | 25.6536
SouthamptonIce Accretion2055RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2055 | 13.5876 | 16.4727 | 20.12 | 22.8938 | 25.6536
SouthamptonIce Accretion2060RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2060 | 13.2489 | 16.1518 | 19.8067 | 22.5849 | 25.3512
SouthamptonIce Accretion2065RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2065 | 13.0123 | 15.9028 | 19.5333 | 22.2987 | 25.0488
SouthamptonIce Accretion2070RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2070 | 12.4232 | 15.2609 | 18.82 | 21.5378 | 24.234
SouthamptonIce Accretion2075RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2075 | 12.0706 | 14.8681 | 18.38 | 21.0632 | 23.7216
SouthamptonIce Accretion2080RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2080 | 11.718 | 14.4752 | 17.94 | 20.5886 | 23.2092
SouthamptonIce Accretion2085RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2085 | 11.1196 | 13.7863 | 17.13 | 19.6733 | 22.2012
SouthamptonIce Accretion2090RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2090 | 10.5212 | 13.0974 | 16.32 | 18.758 | 21.1932
SouthamptonIce Accretion2095RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2095 | 10.5212 | 13.0974 | 16.32 | 18.758 | 21.1932
SouthamptonIce Accretion2100RCP8.5 | Southampton | Ice Accretion | RCP8.5 | 2100 | 10.5212 | 13.0974 | 16.32 | 18.758 | 21.1932
SouthamptonWind2023RCP4.5 | Southampton | Wind | RCP4.5 | 2023 | 85.4848 | 91.9687 | 98.7624 | 105.591 | 112.4086
SouthamptonWind2025RCP4.5 | Southampton | Wind | RCP4.5 | 2025 | 85.5631 | 92.0654 | 98.8845 | 105.7323 | 112.5722
SouthamptonWind2030RCP4.5 | Southampton | Wind | RCP4.5 | 2030 | 85.6415 | 92.1621 | 99.0066 | 105.8735 | 112.7359
SouthamptonWind2035RCP4.5 | Southampton | Wind | RCP4.5 | 2035 | 85.7198 | 92.2587 | 99.1287 | 106.0147 | 112.8995
SouthamptonWind2040RCP4.5 | Southampton | Wind | RCP4.5 | 2040 | 85.7982 | 92.3554 | 99.2508 | 106.156 | 113.0631
SouthamptonWind2045RCP4.5 | Southampton | Wind | RCP4.5 | 2045 | 85.8766 | 92.4521 | 99.3729 | 106.2972 | 113.2268
SouthamptonWind2050RCP4.5 | Southampton | Wind | RCP4.5 | 2050 | 85.9515 | 92.5396 | 99.4752 | 106.413 | 113.3566
SouthamptonWind2055RCP4.5 | Southampton | Wind | RCP4.5 | 2055 | 85.9481 | 92.5304 | 99.4554 | 106.3876 | 113.3227
SouthamptonWind2060RCP4.5 | Southampton | Wind | RCP4.5 | 2060 | 85.9447 | 92.5211 | 99.4356 | 106.3622 | 113.2889
SouthamptonWind2065RCP4.5 | Southampton | Wind | RCP4.5 | 2065 | 85.9412 | 92.5119 | 99.4158 | 106.3368 | 113.255
SouthamptonWind2070RCP4.5 | Southampton | Wind | RCP4.5 | 2070 | 85.9378 | 92.5027 | 99.396 | 106.3113 | 113.2212
SouthamptonWind2075RCP4.5 | Southampton | Wind | RCP4.5 | 2075 | 85.9564 | 92.5227 | 99.4175 | 106.3343 | 113.2456
SouthamptonWind2080RCP4.5 | Southampton | Wind | RCP4.5 | 2080 | 85.9749 | 92.5426 | 99.4389 | 106.3573 | 113.2701
SouthamptonWind2085RCP4.5 | Southampton | Wind | RCP4.5 | 2085 | 85.9934 | 92.5626 | 99.4604 | 106.3802 | 113.2945
SouthamptonWind2090RCP4.5 | Southampton | Wind | RCP4.5 | 2090 | 86.0119 | 92.5825 | 99.4818 | 106.4032 | 113.319
SouthamptonWind2095RCP4.5 | Southampton | Wind | RCP4.5 | 2095 | 86.0304 | 92.6025 | 99.5033 | 106.4261 | 113.3434
SouthamptonWind2100RCP4.5 | Southampton | Wind | RCP4.5 | 2100 | 86.049 | 92.6224 | 99.5247 | 106.4491 | 113.3679
SouthamptonWind2023RCP6.0 | Southampton | Wind | RCP6.0 | 2023 | 85.4848 | 91.9687 | 98.7624 | 105.591 | 112.4086
SouthamptonWind2025RCP6.0 | Southampton | Wind | RCP6.0 | 2025 | 85.5631 | 92.0654 | 98.8845 | 105.7323 | 112.5722
SouthamptonWind2030RCP6.0 | Southampton | Wind | RCP6.0 | 2030 | 85.6415 | 92.1621 | 99.0066 | 105.8735 | 112.7359
SouthamptonWind2035RCP6.0 | Southampton | Wind | RCP6.0 | 2035 | 85.7198 | 92.2587 | 99.1287 | 106.0147 | 112.8995
SouthamptonWind2040RCP6.0 | Southampton | Wind | RCP6.0 | 2040 | 85.7982 | 92.3554 | 99.2508 | 106.156 | 113.0631
SouthamptonWind2045RCP6.0 | Southampton | Wind | RCP6.0 | 2045 | 85.8766 | 92.4521 | 99.3729 | 106.2972 | 113.2268
SouthamptonWind2050RCP6.0 | Southampton | Wind | RCP6.0 | 2050 | 85.9515 | 92.5396 | 99.4752 | 106.413 | 113.3566
SouthamptonWind2055RCP6.0 | Southampton | Wind | RCP6.0 | 2055 | 85.9481 | 92.5304 | 99.4554 | 106.3876 | 113.3227
SouthamptonWind2060RCP6.0 | Southampton | Wind | RCP6.0 | 2060 | 85.9447 | 92.5211 | 99.4356 | 106.3622 | 113.2889
SouthamptonWind2065RCP6.0 | Southampton | Wind | RCP6.0 | 2065 | 85.9412 | 92.5119 | 99.4158 | 106.3368 | 113.255
SouthamptonWind2070RCP6.0 | Southampton | Wind | RCP6.0 | 2070 | 85.9378 | 92.5027 | 99.396 | 106.3113 | 113.2212
SouthamptonWind2075RCP6.0 | Southampton | Wind | RCP6.0 | 2075 | 85.9656 | 92.5327 | 99.4282 | 106.3458 | 113.2578
SouthamptonWind2080RCP6.0 | Southampton | Wind | RCP6.0 | 2080 | 85.9934 | 92.5626 | 99.4604 | 106.3802 | 113.2945
SouthamptonWind2085RCP6.0 | Southampton | Wind | RCP6.0 | 2085 | 86.0212 | 92.5925 | 99.4925 | 106.4146 | 113.3312
SouthamptonWind2090RCP6.0 | Southampton | Wind | RCP6.0 | 2090 | 86.1857 | 92.7881 | 99.726 | 106.6786 | 113.6237
SouthamptonWind2095RCP6.0 | Southampton | Wind | RCP6.0 | 2095 | 86.3225 | 92.9539 | 99.9273 | 106.9081 | 113.8795
SouthamptonWind2100RCP6.0 | Southampton | Wind | RCP6.0 | 2100 | 86.4593 | 93.1196 | 100.1286 | 107.1376 | 114.1353
SouthamptonWind2023RCP8.5 | Southampton | Wind | RCP8.5 | 2023 | 85.4848 | 91.9687 | 98.7624 | 105.591 | 112.4086
SouthamptonWind2025RCP8.5 | Southampton | Wind | RCP8.5 | 2025 | 85.6415 | 92.1621 | 99.0066 | 105.8735 | 112.7359
SouthamptonWind2030RCP8.5 | Southampton | Wind | RCP8.5 | 2030 | 85.7982 | 92.3554 | 99.2508 | 106.156 | 113.0631
SouthamptonWind2035RCP8.5 | Southampton | Wind | RCP8.5 | 2035 | 85.9549 | 92.5488 | 99.495 | 106.4385 | 113.3904
SouthamptonWind2040RCP8.5 | Southampton | Wind | RCP8.5 | 2040 | 85.9492 | 92.5334 | 99.462 | 106.3961 | 113.334
SouthamptonWind2045RCP8.5 | Southampton | Wind | RCP8.5 | 2045 | 85.9435 | 92.5181 | 99.429 | 106.3537 | 113.2776
SouthamptonWind2050RCP8.5 | Southampton | Wind | RCP8.5 | 2050 | 85.9749 | 92.5426 | 99.4389 | 106.3573 | 113.2701
SouthamptonWind2055RCP8.5 | Southampton | Wind | RCP8.5 | 2055 | 86.0119 | 92.5825 | 99.4818 | 106.4032 | 113.319
SouthamptonWind2060RCP8.5 | Southampton | Wind | RCP8.5 | 2060 | 86.1857 | 92.7881 | 99.726 | 106.6786 | 113.6237
SouthamptonWind2065RCP8.5 | Southampton | Wind | RCP8.5 | 2065 | 86.3225 | 92.9539 | 99.9273 | 106.9081 | 113.8795
SouthamptonWind2070RCP8.5 | Southampton | Wind | RCP8.5 | 2070 | 86.5305 | 93.2055 | 100.2276 | 107.2506 | 114.267
SouthamptonWind2075RCP8.5 | Southampton | Wind | RCP8.5 | 2075 | 86.6018 | 93.2915 | 100.3266 | 107.3636 | 114.3987
SouthamptonWind2080RCP8.5 | Southampton | Wind | RCP8.5 | 2080 | 86.673 | 93.3774 | 100.4256 | 107.4766 | 114.5303
SouthamptonWind2085RCP8.5 | Southampton | Wind | RCP8.5 | 2085 | 87.0021 | 93.8193 | 101.0147 | 108.1863 | 115.3598
SouthamptonWind2090RCP8.5 | Southampton | Wind | RCP8.5 | 2090 | 87.3312 | 94.2613 | 101.6037 | 108.896 | 116.1894
SouthamptonWind2095RCP8.5 | Southampton | Wind | RCP8.5 | 2095 | 87.3312 | 94.2613 | 101.6037 | 108.896 | 116.1894
SouthamptonWind2100RCP8.5 | Southampton | Wind | RCP8.5 | 2100 | 87.3312 | 94.2613 | 101.6037 | 108.896 | 116.1894
St. CatharinesIce Accretion2023RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2023 | 19.9576 | 23.9497 | 29 | 32.8683 | 36.7227
St. CatharinesIce Accretion2025RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2025 | 19.8634 | 23.8453 | 28.8888 | 32.7427 | 36.5887
St. CatharinesIce Accretion2030RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2030 | 19.7692 | 23.741 | 28.7777 | 32.6171 | 36.4547
St. CatharinesIce Accretion2035RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2035 | 19.675 | 23.6367 | 28.6665 | 32.4915 | 36.3208
St. CatharinesIce Accretion2040RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2040 | 19.5809 | 23.5324 | 28.5553 | 32.3658 | 36.1868
St. CatharinesIce Accretion2045RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2045 | 19.4867 | 23.4281 | 28.4442 | 32.2402 | 36.0528
St. CatharinesIce Accretion2050RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2050 | 18.9607 | 22.8376 | 27.7646 | 31.4854 | 35.2319
St. CatharinesIce Accretion2055RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2055 | 18.5289 | 22.3514 | 27.1962 | 30.8562 | 34.5449
St. CatharinesIce Accretion2060RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2060 | 18.097 | 21.8652 | 26.6278 | 30.227 | 33.858
St. CatharinesIce Accretion2065RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2065 | 17.6652 | 21.379 | 26.0594 | 29.5979 | 33.171
St. CatharinesIce Accretion2070RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2070 | 17.2333 | 20.8928 | 25.491 | 28.9687 | 32.4841
St. CatharinesIce Accretion2075RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2075 | 17.0719 | 20.7243 | 25.3122 | 28.783 | 32.2892
St. CatharinesIce Accretion2080RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2080 | 16.9105 | 20.5558 | 25.1333 | 28.5973 | 32.0943
St. CatharinesIce Accretion2085RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2085 | 16.749 | 20.3873 | 24.9545 | 28.4116 | 31.8994
St. CatharinesIce Accretion2090RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2090 | 16.5876 | 20.2188 | 24.7757 | 28.2259 | 31.7045
St. CatharinesIce Accretion2095RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2095 | 16.4261 | 20.0503 | 24.5968 | 28.0402 | 31.5097
St. CatharinesIce Accretion2100RCP4.5 | St. Catharines | Ice Accretion | RCP4.5 | 2100 | 16.2647 | 19.8818 | 24.418 | 27.8545 | 31.3148
St. CatharinesIce Accretion2023RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2023 | 19.9576 | 23.9497 | 29 | 32.8683 | 36.7227
St. CatharinesIce Accretion2025RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2025 | 19.8634 | 23.8453 | 28.8888 | 32.7427 | 36.5887
St. CatharinesIce Accretion2030RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2030 | 19.7692 | 23.741 | 28.7777 | 32.6171 | 36.4547
St. CatharinesIce Accretion2035RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2035 | 19.675 | 23.6367 | 28.6665 | 32.4915 | 36.3208
St. CatharinesIce Accretion2040RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2040 | 19.5809 | 23.5324 | 28.5553 | 32.3658 | 36.1868
St. CatharinesIce Accretion2045RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2045 | 19.4867 | 23.4281 | 28.4442 | 32.2402 | 36.0528
St. CatharinesIce Accretion2050RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2050 | 18.9607 | 22.8376 | 27.7646 | 31.4854 | 35.2319
St. CatharinesIce Accretion2055RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2055 | 18.5289 | 22.3514 | 27.1962 | 30.8562 | 34.5449
St. CatharinesIce Accretion2060RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2060 | 18.097 | 21.8652 | 26.6278 | 30.227 | 33.858
St. CatharinesIce Accretion2065RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2065 | 17.6652 | 21.379 | 26.0594 | 29.5979 | 33.171
St. CatharinesIce Accretion2070RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2070 | 17.2333 | 20.8928 | 25.491 | 28.9687 | 32.4841
St. CatharinesIce Accretion2075RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2075 | 16.9912 | 20.64 | 25.2227 | 28.6901 | 32.1917
St. CatharinesIce Accretion2080RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2080 | 16.749 | 20.3873 | 24.9545 | 28.4116 | 31.8994
St. CatharinesIce Accretion2085RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2085 | 16.5069 | 20.1346 | 24.6863 | 28.133 | 31.6071
St. CatharinesIce Accretion2090RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2090 | 15.6055 | 19.1276 | 23.5383 | 26.8823 | 30.2308
St. CatharinesIce Accretion2095RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2095 | 14.9463 | 18.3734 | 22.6587 | 25.9101 | 29.1467
St. CatharinesIce Accretion2100RCP6.0 | St. Catharines | Ice Accretion | RCP6.0 | 2100 | 14.2871 | 17.6192 | 21.779 | 24.938 | 28.0627
St. CatharinesIce Accretion2023RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2023 | 19.9576 | 23.9497 | 29 | 32.8683 | 36.7227
St. CatharinesIce Accretion2025RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2025 | 19.7692 | 23.741 | 28.7777 | 32.6171 | 36.4547
St. CatharinesIce Accretion2030RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2030 | 19.5809 | 23.5324 | 28.5553 | 32.3658 | 36.1868
St. CatharinesIce Accretion2035RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2035 | 19.3925 | 23.3238 | 28.333 | 32.1146 | 35.9188
St. CatharinesIce Accretion2040RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2040 | 18.6728 | 22.5135 | 27.3857 | 31.066 | 34.7739
St. CatharinesIce Accretion2045RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2045 | 17.9531 | 21.7031 | 26.4383 | 30.0173 | 33.629
St. CatharinesIce Accretion2050RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2050 | 16.9105 | 20.5558 | 25.1333 | 28.5973 | 32.0943
St. CatharinesIce Accretion2055RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2055 | 16.5876 | 20.2188 | 24.7757 | 28.2259 | 31.7045
St. CatharinesIce Accretion2060RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2060 | 15.6055 | 19.1276 | 23.5383 | 26.8823 | 30.2308
St. CatharinesIce Accretion2065RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2065 | 14.9463 | 18.3734 | 22.6587 | 25.9101 | 29.1467
St. CatharinesIce Accretion2070RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2070 | 13.9575 | 17.2421 | 21.3537 | 24.4683 | 27.5512
St. CatharinesIce Accretion2075RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2075 | 13.6279 | 16.865 | 20.9283 | 23.9986 | 27.0396
St. CatharinesIce Accretion2080RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2080 | 13.2983 | 16.488 | 20.503 | 23.5289 | 26.528
St. CatharinesIce Accretion2085RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2085 | 12.5517 | 15.6094 | 19.4445 | 22.3328 | 25.1943
St. CatharinesIce Accretion2090RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2090 | 11.805 | 14.7308 | 18.386 | 21.1366 | 23.8606
St. CatharinesIce Accretion2095RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2095 | 11.805 | 14.7308 | 18.386 | 21.1366 | 23.8606
St. CatharinesIce Accretion2100RCP8.5 | St. Catharines | Ice Accretion | RCP8.5 | 2100 | 11.805 | 14.7308 | 18.386 | 21.1366 | 23.8606
St. CatharinesWind2023RCP4.5 | St. Catharines | Wind | RCP4.5 | 2023 | 88.9824 | 96.0647 | 103.581 | 111.05 | 118.5126
St. CatharinesWind2025RCP4.5 | St. Catharines | Wind | RCP4.5 | 2025 | 88.953 | 96.0347 | 103.5487 | 111.0154 | 118.4758
St. CatharinesWind2030RCP4.5 | St. Catharines | Wind | RCP4.5 | 2030 | 88.9237 | 96.0046 | 103.5164 | 110.9808 | 118.4389
St. CatharinesWind2035RCP4.5 | St. Catharines | Wind | RCP4.5 | 2035 | 88.8943 | 95.9746 | 103.4841 | 110.9463 | 118.4021
St. CatharinesWind2040RCP4.5 | St. Catharines | Wind | RCP4.5 | 2040 | 88.8649 | 95.9446 | 103.4518 | 110.9117 | 118.3653
St. CatharinesWind2045RCP4.5 | St. Catharines | Wind | RCP4.5 | 2045 | 88.8356 | 95.9145 | 103.4195 | 110.8771 | 118.3285
St. CatharinesWind2050RCP4.5 | St. Catharines | Wind | RCP4.5 | 2050 | 88.8644 | 95.9585 | 103.4831 | 110.9539 | 118.4219
St. CatharinesWind2055RCP4.5 | St. Catharines | Wind | RCP4.5 | 2055 | 88.9225 | 96.0325 | 103.579 | 111.0652 | 118.5521
St. CatharinesWind2060RCP4.5 | St. Catharines | Wind | RCP4.5 | 2060 | 88.9806 | 96.1065 | 103.6748 | 111.1766 | 118.6823
St. CatharinesWind2065RCP4.5 | St. Catharines | Wind | RCP4.5 | 2065 | 89.0388 | 96.1805 | 103.7707 | 111.2879 | 118.8126
St. CatharinesWind2070RCP4.5 | St. Catharines | Wind | RCP4.5 | 2070 | 89.0969 | 96.2544 | 103.8666 | 111.3992 | 118.9428
St. CatharinesWind2075RCP4.5 | St. Catharines | Wind | RCP4.5 | 2075 | 89.1791 | 96.3699 | 104.0247 | 111.592 | 119.1734
St. CatharinesWind2080RCP4.5 | St. Catharines | Wind | RCP4.5 | 2080 | 89.2613 | 96.4853 | 104.1828 | 111.7848 | 119.4041
St. CatharinesWind2085RCP4.5 | St. Catharines | Wind | RCP4.5 | 2085 | 89.3435 | 96.6007 | 104.3409 | 111.9776 | 119.6347
St. CatharinesWind2090RCP4.5 | St. Catharines | Wind | RCP4.5 | 2090 | 89.4257 | 96.7161 | 104.499 | 112.1705 | 119.8653
St. CatharinesWind2095RCP4.5 | St. Catharines | Wind | RCP4.5 | 2095 | 89.5079 | 96.8315 | 104.6571 | 112.3633 | 120.0959
St. CatharinesWind2100RCP4.5 | St. Catharines | Wind | RCP4.5 | 2100 | 89.5901 | 96.9469 | 104.8152 | 112.5561 | 120.3265
St. CatharinesWind2023RCP6.0 | St. Catharines | Wind | RCP6.0 | 2023 | 88.9824 | 96.0647 | 103.581 | 111.05 | 118.5126
St. CatharinesWind2025RCP6.0 | St. Catharines | Wind | RCP6.0 | 2025 | 88.953 | 96.0347 | 103.5487 | 111.0154 | 118.4758
St. CatharinesWind2030RCP6.0 | St. Catharines | Wind | RCP6.0 | 2030 | 88.9237 | 96.0046 | 103.5164 | 110.9808 | 118.4389
St. CatharinesWind2035RCP6.0 | St. Catharines | Wind | RCP6.0 | 2035 | 88.8943 | 95.9746 | 103.4841 | 110.9463 | 118.4021
St. CatharinesWind2040RCP6.0 | St. Catharines | Wind | RCP6.0 | 2040 | 88.8649 | 95.9446 | 103.4518 | 110.9117 | 118.3653
St. CatharinesWind2045RCP6.0 | St. Catharines | Wind | RCP6.0 | 2045 | 88.8356 | 95.9145 | 103.4195 | 110.8771 | 118.3285
St. CatharinesWind2050RCP6.0 | St. Catharines | Wind | RCP6.0 | 2050 | 88.8644 | 95.9585 | 103.4831 | 110.9539 | 118.4219
St. CatharinesWind2055RCP6.0 | St. Catharines | Wind | RCP6.0 | 2055 | 88.9225 | 96.0325 | 103.579 | 111.0652 | 118.5521
St. CatharinesWind2060RCP6.0 | St. Catharines | Wind | RCP6.0 | 2060 | 88.9806 | 96.1065 | 103.6748 | 111.1766 | 118.6823
St. CatharinesWind2065RCP6.0 | St. Catharines | Wind | RCP6.0 | 2065 | 89.0388 | 96.1805 | 103.7707 | 111.2879 | 118.8126
St. CatharinesWind2070RCP6.0 | St. Catharines | Wind | RCP6.0 | 2070 | 89.0969 | 96.2544 | 103.8666 | 111.3992 | 118.9428
St. CatharinesWind2075RCP6.0 | St. Catharines | Wind | RCP6.0 | 2075 | 89.2202 | 96.4276 | 104.1038 | 111.6884 | 119.2887
St. CatharinesWind2080RCP6.0 | St. Catharines | Wind | RCP6.0 | 2080 | 89.3435 | 96.6007 | 104.3409 | 111.9776 | 119.6347
St. CatharinesWind2085RCP6.0 | St. Catharines | Wind | RCP6.0 | 2085 | 89.4668 | 96.7738 | 104.5781 | 112.2669 | 119.9806
St. CatharinesWind2090RCP6.0 | St. Catharines | Wind | RCP6.0 | 2090 | 89.778 | 97.1872 | 105.1178 | 112.9162 | 120.7452
St. CatharinesWind2095RCP6.0 | St. Catharines | Wind | RCP6.0 | 2095 | 89.9659 | 97.4275 | 105.4204 | 113.2764 | 121.1638
St. CatharinesWind2100RCP6.0 | St. Catharines | Wind | RCP6.0 | 2100 | 90.1538 | 97.6679 | 105.723 | 113.6366 | 121.5824
St. CatharinesWind2023RCP8.5 | St. Catharines | Wind | RCP8.5 | 2023 | 88.9824 | 96.0647 | 103.581 | 111.05 | 118.5126
St. CatharinesWind2025RCP8.5 | St. Catharines | Wind | RCP8.5 | 2025 | 88.9237 | 96.0046 | 103.5164 | 110.9808 | 118.4389
St. CatharinesWind2030RCP8.5 | St. Catharines | Wind | RCP8.5 | 2030 | 88.8649 | 95.9446 | 103.4518 | 110.9117 | 118.3653
St. CatharinesWind2035RCP8.5 | St. Catharines | Wind | RCP8.5 | 2035 | 88.8062 | 95.8845 | 103.3872 | 110.8426 | 118.2916
St. CatharinesWind2040RCP8.5 | St. Catharines | Wind | RCP8.5 | 2040 | 88.9031 | 96.0078 | 103.547 | 111.0281 | 118.5087
St. CatharinesWind2045RCP8.5 | St. Catharines | Wind | RCP8.5 | 2045 | 89 | 96.1311 | 103.7068 | 111.2137 | 118.7258
St. CatharinesWind2050RCP8.5 | St. Catharines | Wind | RCP8.5 | 2050 | 89.2613 | 96.4853 | 104.1828 | 111.7848 | 119.4041
St. CatharinesWind2055RCP8.5 | St. Catharines | Wind | RCP8.5 | 2055 | 89.4257 | 96.7161 | 104.499 | 112.1705 | 119.8653
St. CatharinesWind2060RCP8.5 | St. Catharines | Wind | RCP8.5 | 2060 | 89.778 | 97.1872 | 105.1178 | 112.9162 | 120.7452
St. CatharinesWind2065RCP8.5 | St. Catharines | Wind | RCP8.5 | 2065 | 89.9659 | 97.4275 | 105.4204 | 113.2764 | 121.1638
St. CatharinesWind2070RCP8.5 | St. Catharines | Wind | RCP8.5 | 2070 | 90.2154 | 97.7722 | 105.8896 | 113.8548 | 121.8459
St. CatharinesWind2075RCP8.5 | St. Catharines | Wind | RCP8.5 | 2075 | 90.2771 | 97.8765 | 106.0562 | 114.0731 | 122.1095
St. CatharinesWind2080RCP8.5 | St. Catharines | Wind | RCP8.5 | 2080 | 90.3387 | 97.9809 | 106.2228 | 114.2914 | 122.3731
St. CatharinesWind2085RCP8.5 | St. Catharines | Wind | RCP8.5 | 2085 | 90.4048 | 98.09 | 106.3809 | 114.4879 | 122.6173
St. CatharinesWind2090RCP8.5 | St. Catharines | Wind | RCP8.5 | 2090 | 90.4709 | 98.1991 | 106.539 | 114.6843 | 122.8614
St. CatharinesWind2095RCP8.5 | St. Catharines | Wind | RCP8.5 | 2095 | 90.4709 | 98.1991 | 106.539 | 114.6843 | 122.8614
St. CatharinesWind2100RCP8.5 | St. Catharines | Wind | RCP8.5 | 2100 | 90.4709 | 98.1991 | 106.539 | 114.6843 | 122.8614
St. Mary'sIce Accretion2023RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425
St. Mary'sIce Accretion2025RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2025 | 17.1352 | 20.5563 | 24.8625 | 28.1605 | 31.4423
St. Mary'sIce Accretion2030RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2030 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542
St. Mary'sIce Accretion2035RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2035 | 17.17 | 20.6255 | 24.9875 | 28.3206 | 31.6418
St. Mary'sIce Accretion2040RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2040 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415
St. Mary'sIce Accretion2045RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2045 | 17.2048 | 20.6947 | 25.1125 | 28.4807 | 31.8412
St. Mary'sIce Accretion2050RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2050 | 17.1526 | 20.6794 | 25.145 | 28.5438 | 31.941
St. Mary'sIce Accretion2055RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2055 | 17.083 | 20.6296 | 25.115 | 28.5268 | 31.941
St. Mary'sIce Accretion2060RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2060 | 17.0134 | 20.5799 | 25.085 | 28.5099 | 31.941
St. Mary'sIce Accretion2065RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2065 | 16.9439 | 20.53 | 25.055 | 28.4929 | 31.941
St. Mary'sIce Accretion2070RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2070 | 16.8743 | 20.4802 | 25.025 | 28.476 | 31.941
St. Mary'sIce Accretion2075RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2075 | 16.8424 | 20.4664 | 25.0375 | 28.5042 | 31.9883
St. Mary'sIce Accretion2080RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2080 | 16.8105 | 20.4526 | 25.05 | 28.5325 | 32.0355
St. Mary'sIce Accretion2085RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2085 | 16.7786 | 20.4387 | 25.0625 | 28.5607 | 32.0827
St. Mary'sIce Accretion2090RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2090 | 16.7467 | 20.4249 | 25.075 | 28.589 | 32.13
St. Mary'sIce Accretion2095RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2095 | 16.7148 | 20.4111 | 25.0875 | 28.6172 | 32.1773
St. Mary'sIce Accretion2100RCP4.5 | St. Mary's | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.3972 | 25.1 | 28.6455 | 32.2245
St. Mary'sIce Accretion2023RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425
St. Mary'sIce Accretion2025RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2025 | 17.1352 | 20.5563 | 24.8625 | 28.1605 | 31.4423
St. Mary'sIce Accretion2030RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2030 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542
St. Mary'sIce Accretion2035RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2035 | 17.17 | 20.6255 | 24.9875 | 28.3206 | 31.6418
St. Mary'sIce Accretion2040RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2040 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415
St. Mary'sIce Accretion2045RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2045 | 17.2048 | 20.6947 | 25.1125 | 28.4807 | 31.8412
St. Mary'sIce Accretion2050RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2050 | 17.1526 | 20.6794 | 25.145 | 28.5438 | 31.941
St. Mary'sIce Accretion2055RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2055 | 17.083 | 20.6296 | 25.115 | 28.5268 | 31.941
St. Mary'sIce Accretion2060RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2060 | 17.0134 | 20.5799 | 25.085 | 28.5099 | 31.941
St. Mary'sIce Accretion2065RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2065 | 16.9439 | 20.53 | 25.055 | 28.4929 | 31.941
St. Mary'sIce Accretion2070RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2070 | 16.8743 | 20.4802 | 25.025 | 28.476 | 31.941
St. Mary'sIce Accretion2075RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2075 | 16.8264 | 20.4595 | 25.0437 | 28.5184 | 32.0119
St. Mary'sIce Accretion2080RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2080 | 16.7786 | 20.4387 | 25.0625 | 28.5607 | 32.0827
St. Mary'sIce Accretion2085RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2085 | 16.7308 | 20.418 | 25.0813 | 28.6031 | 32.1536
St. Mary'sIce Accretion2090RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2090 | 16.4742 | 20.1898 | 24.8833 | 28.4289 | 31.9935
St. Mary'sIce Accretion2095RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2095 | 16.2654 | 19.9822 | 24.6667 | 28.2123 | 31.7625
St. Mary'sIce Accretion2100RCP6.0 | St. Mary's | Ice Accretion | RCP6.0 | 2100 | 16.0566 | 19.7747 | 24.45 | 27.9957 | 31.5315
St. Mary'sIce Accretion2023RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425
St. Mary'sIce Accretion2025RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2025 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542
St. Mary'sIce Accretion2030RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2030 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415
St. Mary'sIce Accretion2035RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2035 | 17.2222 | 20.7293 | 25.175 | 28.5607 | 31.941
St. Mary'sIce Accretion2040RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2040 | 17.1062 | 20.6462 | 25.125 | 28.5325 | 31.941
St. Mary'sIce Accretion2045RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2045 | 16.9902 | 20.5633 | 25.075 | 28.5042 | 31.941
St. Mary'sIce Accretion2050RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2050 | 16.8105 | 20.4526 | 25.05 | 28.5325 | 32.0355
St. Mary'sIce Accretion2055RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2055 | 16.7467 | 20.4249 | 25.075 | 28.589 | 32.13
St. Mary'sIce Accretion2060RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2060 | 16.4742 | 20.1898 | 24.8833 | 28.4289 | 31.9935
St. Mary'sIce Accretion2065RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2065 | 16.2654 | 19.9822 | 24.6667 | 28.2123 | 31.7625
St. Mary'sIce Accretion2070RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2070 | 15.6797 | 19.3528 | 23.975 | 27.4778 | 30.9645
St. Mary'sIce Accretion2075RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2075 | 15.3028 | 18.9309 | 23.5 | 26.9599 | 30.3975
St. Mary'sIce Accretion2080RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2080 | 14.9259 | 18.509 | 23.025 | 26.442 | 29.8305
St. Mary'sIce Accretion2085RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2085 | 14.1431 | 17.5856 | 21.925 | 25.2131 | 28.476
St. Mary'sIce Accretion2090RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2090 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215
St. Mary'sIce Accretion2095RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2095 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215
St. Mary'sIce Accretion2100RCP8.5 | St. Mary's | Ice Accretion | RCP8.5 | 2100 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215
St. Mary'sWind2023RCP4.5 | St. Mary's | Wind | RCP4.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
St. Mary'sWind2025RCP4.5 | St. Mary's | Wind | RCP4.5 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
St. Mary'sWind2030RCP4.5 | St. Mary's | Wind | RCP4.5 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
St. Mary'sWind2035RCP4.5 | St. Mary's | Wind | RCP4.5 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
St. Mary'sWind2040RCP4.5 | St. Mary's | Wind | RCP4.5 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
St. Mary'sWind2045RCP4.5 | St. Mary's | Wind | RCP4.5 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
St. Mary'sWind2050RCP4.5 | St. Mary's | Wind | RCP4.5 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
St. Mary'sWind2055RCP4.5 | St. Mary's | Wind | RCP4.5 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
St. Mary'sWind2060RCP4.5 | St. Mary's | Wind | RCP4.5 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
St. Mary'sWind2065RCP4.5 | St. Mary's | Wind | RCP4.5 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
St. Mary'sWind2070RCP4.5 | St. Mary's | Wind | RCP4.5 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
St. Mary'sWind2075RCP4.5 | St. Mary's | Wind | RCP4.5 | 2075 | 86.3504 | 93.3577 | 100.8387 | 108.226 | 115.6228
St. Mary'sWind2080RCP4.5 | St. Mary's | Wind | RCP4.5 | 2080 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
St. Mary'sWind2085RCP4.5 | St. Mary's | Wind | RCP4.5 | 2085 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
St. Mary'sWind2090RCP4.5 | St. Mary's | Wind | RCP4.5 | 2090 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
St. Mary'sWind2095RCP4.5 | St. Mary's | Wind | RCP4.5 | 2095 | 86.7678 | 93.9167 | 101.5705 | 109.1068 | 116.6655
St. Mary'sWind2100RCP4.5 | St. Mary's | Wind | RCP4.5 | 2100 | 86.8722 | 94.0565 | 101.7534 | 109.327 | 116.9262
St. Mary'sWind2023RCP6.0 | St. Mary's | Wind | RCP6.0 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
St. Mary'sWind2025RCP6.0 | St. Mary's | Wind | RCP6.0 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
St. Mary'sWind2030RCP6.0 | St. Mary's | Wind | RCP6.0 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
St. Mary'sWind2035RCP6.0 | St. Mary's | Wind | RCP6.0 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
St. Mary'sWind2040RCP6.0 | St. Mary's | Wind | RCP6.0 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
St. Mary'sWind2045RCP6.0 | St. Mary's | Wind | RCP6.0 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
St. Mary'sWind2050RCP6.0 | St. Mary's | Wind | RCP6.0 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
St. Mary'sWind2055RCP6.0 | St. Mary's | Wind | RCP6.0 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
St. Mary'sWind2060RCP6.0 | St. Mary's | Wind | RCP6.0 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
St. Mary'sWind2065RCP6.0 | St. Mary's | Wind | RCP6.0 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
St. Mary'sWind2070RCP6.0 | St. Mary's | Wind | RCP6.0 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
St. Mary'sWind2075RCP6.0 | St. Mary's | Wind | RCP6.0 | 2075 | 86.4026 | 93.4276 | 100.9302 | 108.3361 | 115.7531
St. Mary'sWind2080RCP6.0 | St. Mary's | Wind | RCP6.0 | 2080 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
St. Mary'sWind2085RCP6.0 | St. Mary's | Wind | RCP6.0 | 2085 | 86.7157 | 93.8469 | 101.479 | 108.9967 | 116.5351
St. Mary'sWind2090RCP6.0 | St. Mary's | Wind | RCP6.0 | 2090 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
St. Mary'sWind2095RCP6.0 | St. Mary's | Wind | RCP6.0 | 2095 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
St. Mary'sWind2100RCP6.0 | St. Mary's | Wind | RCP6.0 | 2100 | 87.7861 | 95.1502 | 103.0568 | 110.8265 | 118.6131
St. Mary'sWind2023RCP8.5 | St. Mary's | Wind | RCP8.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
St. Mary'sWind2025RCP8.5 | St. Mary's | Wind | RCP8.5 | 2025 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
St. Mary'sWind2030RCP8.5 | St. Mary's | Wind | RCP8.5 | 2030 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
St. Mary'sWind2035RCP8.5 | St. Mary's | Wind | RCP8.5 | 2035 | 86.0768 | 93.0084 | 100.3912 | 107.7017 | 115.0269
St. Mary'sWind2040RCP8.5 | St. Mary's | Wind | RCP8.5 | 2040 | 86.1332 | 93.0782 | 100.4794 | 107.8031 | 115.1386
St. Mary'sWind2045RCP8.5 | St. Mary's | Wind | RCP8.5 | 2045 | 86.1896 | 93.1481 | 100.5676 | 107.9044 | 115.2504
St. Mary'sWind2050RCP8.5 | St. Mary's | Wind | RCP8.5 | 2050 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
St. Mary'sWind2055RCP8.5 | St. Mary's | Wind | RCP8.5 | 2055 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
St. Mary'sWind2060RCP8.5 | St. Mary's | Wind | RCP8.5 | 2060 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
St. Mary'sWind2065RCP8.5 | St. Mary's | Wind | RCP8.5 | 2065 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
St. Mary'sWind2070RCP8.5 | St. Mary's | Wind | RCP8.5 | 2070 | 88.0541 | 95.5026 | 103.5207 | 111.3788 | 119.2611
St. Mary'sWind2075RCP8.5 | St. Mary's | Wind | RCP8.5 | 2075 | 88.322 | 95.855 | 103.9845 | 111.9311 | 119.9091
St. Mary'sWind2080RCP8.5 | St. Mary's | Wind | RCP8.5 | 2080 | 88.59 | 96.2074 | 104.4484 | 112.4833 | 120.5571
St. Mary'sWind2085RCP8.5 | St. Mary's | Wind | RCP8.5 | 2085 | 88.9454 | 96.6585 | 105.0217 | 113.1649 | 121.3447
St. Mary'sWind2090RCP8.5 | St. Mary's | Wind | RCP8.5 | 2090 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
St. Mary'sWind2095RCP8.5 | St. Mary's | Wind | RCP8.5 | 2095 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
St. Mary'sWind2100RCP8.5 | St. Mary's | Wind | RCP8.5 | 2100 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
St. ThomasIce Accretion2023RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2023 | 21.9553 | 26.3475 | 31.904 | 36.1238 | 40.3603
St. ThomasIce Accretion2025RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2025 | 21.8254 | 26.2059 | 31.7493 | 35.9611 | 40.1856
St. ThomasIce Accretion2030RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2030 | 21.6956 | 26.0642 | 31.5947 | 35.7984 | 40.0109
St. ThomasIce Accretion2035RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2035 | 21.5657 | 25.9226 | 31.44 | 35.6357 | 39.8362
St. ThomasIce Accretion2040RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2040 | 21.4358 | 25.7809 | 31.2853 | 35.473 | 39.6614
St. ThomasIce Accretion2045RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2045 | 21.3059 | 25.6393 | 31.1307 | 35.3102 | 39.4867
St. ThomasIce Accretion2050RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2050 | 20.7618 | 25.0408 | 30.4576 | 34.5834 | 38.6991
St. ThomasIce Accretion2055RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2055 | 20.3477 | 24.5839 | 29.9392 | 34.0193 | 38.0863
St. ThomasIce Accretion2060RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2060 | 19.9335 | 24.1271 | 29.4208 | 33.4552 | 37.4734
St. ThomasIce Accretion2065RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2065 | 19.5193 | 23.6703 | 28.9024 | 32.8911 | 36.8605
St. ThomasIce Accretion2070RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2070 | 19.1052 | 23.2134 | 28.384 | 32.327 | 36.2477
St. ThomasIce Accretion2075RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2075 | 18.9604 | 23.0674 | 28.2347 | 32.1703 | 36.0864
St. ThomasIce Accretion2080RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2080 | 18.8157 | 22.9213 | 28.0853 | 32.0137 | 35.9251
St. ThomasIce Accretion2085RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2085 | 18.6709 | 22.7752 | 27.936 | 31.857 | 35.7638
St. ThomasIce Accretion2090RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2090 | 18.5262 | 22.6291 | 27.7867 | 31.7003 | 35.6026
St. ThomasIce Accretion2095RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2095 | 18.3815 | 22.483 | 27.6373 | 31.5436 | 35.4413
St. ThomasIce Accretion2100RCP4.5 | St. Thomas | Ice Accretion | RCP4.5 | 2100 | 18.2367 | 22.337 | 27.488 | 31.3869 | 35.28
St. ThomasIce Accretion2023RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2023 | 21.9553 | 26.3475 | 31.904 | 36.1238 | 40.3603
St. ThomasIce Accretion2025RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2025 | 21.8254 | 26.2059 | 31.7493 | 35.9611 | 40.1856
St. ThomasIce Accretion2030RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2030 | 21.6956 | 26.0642 | 31.5947 | 35.7984 | 40.0109
St. ThomasIce Accretion2035RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2035 | 21.5657 | 25.9226 | 31.44 | 35.6357 | 39.8362
St. ThomasIce Accretion2040RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2040 | 21.4358 | 25.7809 | 31.2853 | 35.473 | 39.6614
St. ThomasIce Accretion2045RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2045 | 21.3059 | 25.6393 | 31.1307 | 35.3102 | 39.4867
St. ThomasIce Accretion2050RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2050 | 20.7618 | 25.0408 | 30.4576 | 34.5834 | 38.6991
St. ThomasIce Accretion2055RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2055 | 20.3477 | 24.5839 | 29.9392 | 34.0193 | 38.0863
St. ThomasIce Accretion2060RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2060 | 19.9335 | 24.1271 | 29.4208 | 33.4552 | 37.4734
St. ThomasIce Accretion2065RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2065 | 19.5193 | 23.6703 | 28.9024 | 32.8911 | 36.8605
St. ThomasIce Accretion2070RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2070 | 19.1052 | 23.2134 | 28.384 | 32.327 | 36.2477
St. ThomasIce Accretion2075RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2075 | 18.888 | 22.9943 | 28.16 | 32.092 | 36.0058
St. ThomasIce Accretion2080RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2080 | 18.6709 | 22.7752 | 27.936 | 31.857 | 35.7638
St. ThomasIce Accretion2085RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2085 | 18.4538 | 22.5561 | 27.712 | 31.6219 | 35.5219
St. ThomasIce Accretion2090RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2090 | 17.7172 | 21.7526 | 26.8267 | 30.6637 | 34.487
St. ThomasIce Accretion2095RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2095 | 17.1976 | 21.1683 | 26.1653 | 29.9405 | 33.6941
St. ThomasIce Accretion2100RCP6.0 | St. Thomas | Ice Accretion | RCP6.0 | 2100 | 16.678 | 20.584 | 25.504 | 29.2173 | 32.9011
St. ThomasIce Accretion2023RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2023 | 21.9553 | 26.3475 | 31.904 | 36.1238 | 40.3603
St. ThomasIce Accretion2025RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2025 | 21.6956 | 26.0642 | 31.5947 | 35.7984 | 40.0109
St. ThomasIce Accretion2030RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2030 | 21.4358 | 25.7809 | 31.2853 | 35.473 | 39.6614
St. ThomasIce Accretion2035RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2035 | 21.176 | 25.4976 | 30.976 | 35.1475 | 39.312
St. ThomasIce Accretion2040RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2040 | 20.4857 | 24.7362 | 30.112 | 34.2074 | 38.2906
St. ThomasIce Accretion2045RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2045 | 19.7954 | 23.9748 | 29.248 | 33.2672 | 37.2691
St. ThomasIce Accretion2050RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2050 | 18.8157 | 22.9213 | 28.0853 | 32.0137 | 35.9251
St. ThomasIce Accretion2055RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2055 | 18.5262 | 22.6291 | 27.7867 | 31.7003 | 35.6026
St. ThomasIce Accretion2060RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2060 | 17.7172 | 21.7526 | 26.8267 | 30.6637 | 34.487
St. ThomasIce Accretion2065RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2065 | 17.1976 | 21.1683 | 26.1653 | 29.9405 | 33.6941
St. ThomasIce Accretion2070RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2070 | 16.344 | 20.2299 | 25.12 | 28.7954 | 32.4576
St. ThomasIce Accretion2075RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2075 | 16.01 | 19.8757 | 24.736 | 28.3735 | 32.0141
St. ThomasIce Accretion2080RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2080 | 15.676 | 19.5216 | 24.352 | 27.9517 | 31.5706
St. ThomasIce Accretion2085RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2085 | 14.6851 | 18.353 | 22.944 | 26.3787 | 29.8166
St. ThomasIce Accretion2090RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2090 | 13.6943 | 17.1843 | 21.536 | 24.8058 | 28.0627
St. ThomasIce Accretion2095RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2095 | 13.6943 | 17.1843 | 21.536 | 24.8058 | 28.0627
St. ThomasIce Accretion2100RCP8.5 | St. Thomas | Ice Accretion | RCP8.5 | 2100 | 13.6943 | 17.1843 | 21.536 | 24.8058 | 28.0627
St. ThomasWind2023RCP4.5 | St. Thomas | Wind | RCP4.5 | 2023 | 87.9269 | 94.8505 | 102.1817 | 109.4749 | 116.775
St. ThomasWind2025RCP4.5 | St. Thomas | Wind | RCP4.5 | 2025 | 88.0373 | 94.9977 | 102.3753 | 109.7073 | 117.0475
St. ThomasWind2030RCP4.5 | St. Thomas | Wind | RCP4.5 | 2030 | 88.1478 | 95.1448 | 102.5689 | 109.9396 | 117.32
St. ThomasWind2035RCP4.5 | St. Thomas | Wind | RCP4.5 | 2035 | 88.2583 | 95.292 | 102.7625 | 110.172 | 117.5925
St. ThomasWind2040RCP4.5 | St. Thomas | Wind | RCP4.5 | 2040 | 88.3687 | 95.4391 | 102.956 | 110.4043 | 117.865
St. ThomasWind2045RCP4.5 | St. Thomas | Wind | RCP4.5 | 2045 | 88.4792 | 95.5863 | 103.1496 | 110.6367 | 118.1375
St. ThomasWind2050RCP4.5 | St. Thomas | Wind | RCP4.5 | 2050 | 88.642 | 95.8067 | 103.4442 | 110.9944 | 118.5597
St. ThomasWind2055RCP4.5 | St. Thomas | Wind | RCP4.5 | 2055 | 88.6943 | 95.88 | 103.5452 | 111.1197 | 118.7093
St. ThomasWind2060RCP4.5 | St. Thomas | Wind | RCP4.5 | 2060 | 88.7467 | 95.9533 | 103.6462 | 111.2451 | 118.859
St. ThomasWind2065RCP4.5 | St. Thomas | Wind | RCP4.5 | 2065 | 88.799 | 96.0265 | 103.7472 | 111.3705 | 119.0087
St. ThomasWind2070RCP4.5 | St. Thomas | Wind | RCP4.5 | 2070 | 88.8513 | 96.0998 | 103.8482 | 111.4958 | 119.1584
St. ThomasWind2075RCP4.5 | St. Thomas | Wind | RCP4.5 | 2075 | 89.0054 | 96.3002 | 104.1074 | 111.8038 | 119.5172
St. ThomasWind2080RCP4.5 | St. Thomas | Wind | RCP4.5 | 2080 | 89.1595 | 96.5006 | 104.3667 | 112.1118 | 119.8761
St. ThomasWind2085RCP4.5 | St. Thomas | Wind | RCP4.5 | 2085 | 89.3135 | 96.7009 | 104.6259 | 112.4198 | 120.2349
St. ThomasWind2090RCP4.5 | St. Thomas | Wind | RCP4.5 | 2090 | 89.4676 | 96.9013 | 104.8851 | 112.7278 | 120.5938
St. ThomasWind2095RCP4.5 | St. Thomas | Wind | RCP4.5 | 2095 | 89.6217 | 97.1017 | 105.1444 | 113.0358 | 120.9527
St. ThomasWind2100RCP4.5 | St. Thomas | Wind | RCP4.5 | 2100 | 89.7757 | 97.3021 | 105.4036 | 113.3438 | 121.3115
St. ThomasWind2023RCP6.0 | St. Thomas | Wind | RCP6.0 | 2023 | 87.9269 | 94.8505 | 102.1817 | 109.4749 | 116.775
St. ThomasWind2025RCP6.0 | St. Thomas | Wind | RCP6.0 | 2025 | 88.0373 | 94.9977 | 102.3753 | 109.7073 | 117.0475
St. ThomasWind2030RCP6.0 | St. Thomas | Wind | RCP6.0 | 2030 | 88.1478 | 95.1448 | 102.5689 | 109.9396 | 117.32
St. ThomasWind2035RCP6.0 | St. Thomas | Wind | RCP6.0 | 2035 | 88.2583 | 95.292 | 102.7625 | 110.172 | 117.5925
St. ThomasWind2040RCP6.0 | St. Thomas | Wind | RCP6.0 | 2040 | 88.3687 | 95.4391 | 102.956 | 110.4043 | 117.865
St. ThomasWind2045RCP6.0 | St. Thomas | Wind | RCP6.0 | 2045 | 88.4792 | 95.5863 | 103.1496 | 110.6367 | 118.1375
St. ThomasWind2050RCP6.0 | St. Thomas | Wind | RCP6.0 | 2050 | 88.642 | 95.8067 | 103.4442 | 110.9944 | 118.5597
St. ThomasWind2055RCP6.0 | St. Thomas | Wind | RCP6.0 | 2055 | 88.6943 | 95.88 | 103.5452 | 111.1197 | 118.7093
St. ThomasWind2060RCP6.0 | St. Thomas | Wind | RCP6.0 | 2060 | 88.7467 | 95.9533 | 103.6462 | 111.2451 | 118.859
St. ThomasWind2065RCP6.0 | St. Thomas | Wind | RCP6.0 | 2065 | 88.799 | 96.0265 | 103.7472 | 111.3705 | 119.0087
St. ThomasWind2070RCP6.0 | St. Thomas | Wind | RCP6.0 | 2070 | 88.8513 | 96.0998 | 103.8482 | 111.4958 | 119.1584
St. ThomasWind2075RCP6.0 | St. Thomas | Wind | RCP6.0 | 2075 | 89.0824 | 96.4004 | 104.2371 | 111.9578 | 119.6967
St. ThomasWind2080RCP6.0 | St. Thomas | Wind | RCP6.0 | 2080 | 89.3135 | 96.7009 | 104.6259 | 112.4198 | 120.2349
St. ThomasWind2085RCP6.0 | St. Thomas | Wind | RCP6.0 | 2085 | 89.5446 | 97.0015 | 105.0148 | 112.8818 | 120.7732
St. ThomasWind2090RCP6.0 | St. Thomas | Wind | RCP6.0 | 2090 | 90.1566 | 97.7874 | 106.013 | 114.0607 | 122.1405
St. ThomasWind2095RCP6.0 | St. Thomas | Wind | RCP6.0 | 2095 | 90.5374 | 98.2727 | 106.6223 | 114.7775 | 122.9695
St. ThomasWind2100RCP6.0 | St. Thomas | Wind | RCP6.0 | 2100 | 90.9182 | 98.758 | 107.2317 | 115.4944 | 123.7985
St. ThomasWind2023RCP8.5 | St. Thomas | Wind | RCP8.5 | 2023 | 87.9269 | 94.8505 | 102.1817 | 109.4749 | 116.775
St. ThomasWind2025RCP8.5 | St. Thomas | Wind | RCP8.5 | 2025 | 88.1478 | 95.1448 | 102.5689 | 109.9396 | 117.32
St. ThomasWind2030RCP8.5 | St. Thomas | Wind | RCP8.5 | 2030 | 88.3687 | 95.4391 | 102.956 | 110.4043 | 117.865
St. ThomasWind2035RCP8.5 | St. Thomas | Wind | RCP8.5 | 2035 | 88.5897 | 95.7335 | 103.3432 | 110.869 | 118.41
St. ThomasWind2040RCP8.5 | St. Thomas | Wind | RCP8.5 | 2040 | 88.6769 | 95.8556 | 103.5115 | 111.0779 | 118.6594
St. ThomasWind2045RCP8.5 | St. Thomas | Wind | RCP8.5 | 2045 | 88.7641 | 95.9777 | 103.6799 | 111.2869 | 118.9089
St. ThomasWind2050RCP8.5 | St. Thomas | Wind | RCP8.5 | 2050 | 89.1595 | 96.5006 | 104.3667 | 112.1118 | 119.8761
St. ThomasWind2055RCP8.5 | St. Thomas | Wind | RCP8.5 | 2055 | 89.4676 | 96.9013 | 104.8851 | 112.7278 | 120.5938
St. ThomasWind2060RCP8.5 | St. Thomas | Wind | RCP8.5 | 2060 | 90.1566 | 97.7874 | 106.013 | 114.0607 | 122.1405
St. ThomasWind2065RCP8.5 | St. Thomas | Wind | RCP8.5 | 2065 | 90.5374 | 98.2727 | 106.6223 | 114.7775 | 122.9695
St. ThomasWind2070RCP8.5 | St. Thomas | Wind | RCP8.5 | 2070 | 91.1537 | 99.0523 | 107.6054 | 115.9375 | 124.309
St. ThomasWind2075RCP8.5 | St. Thomas | Wind | RCP8.5 | 2075 | 91.3892 | 99.3466 | 107.9791 | 116.3806 | 124.8194
St. ThomasWind2080RCP8.5 | St. Thomas | Wind | RCP8.5 | 2080 | 91.6246 | 99.6409 | 108.3528 | 116.8237 | 125.3299
St. ThomasWind2085RCP8.5 | St. Thomas | Wind | RCP8.5 | 2085 | 92.0258 | 100.1716 | 109.0497 | 117.6558 | 126.3086
St. ThomasWind2090RCP8.5 | St. Thomas | Wind | RCP8.5 | 2090 | 92.427 | 100.7024 | 109.7466 | 118.4879 | 127.2873
St. ThomasWind2095RCP8.5 | St. Thomas | Wind | RCP8.5 | 2095 | 92.427 | 100.7024 | 109.7466 | 118.4879 | 127.2873
St. ThomasWind2100RCP8.5 | St. Thomas | Wind | RCP8.5 | 2100 | 92.427 | 100.7024 | 109.7466 | 118.4879 | 127.2873
StirlingIce Accretion2023RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3065 | 31.563
StirlingIce Accretion2025RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2025 | 17.544 | 20.9091 | 25.1667 | 28.4148 | 31.6837
StirlingIce Accretion2030RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2030 | 17.6049 | 20.9852 | 25.2583 | 28.5231 | 31.8045
StirlingIce Accretion2035RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2035 | 17.6658 | 21.0613 | 25.35 | 28.6314 | 31.9252
StirlingIce Accretion2040RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2040 | 17.7267 | 21.1373 | 25.4417 | 28.7397 | 32.046
StirlingIce Accretion2045RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2045 | 17.7876 | 21.2134 | 25.5333 | 28.848 | 32.1667
StirlingIce Accretion2050RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2050 | 17.8032 | 21.248 | 25.595 | 28.928 | 32.2623
StirlingIce Accretion2055RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2055 | 17.758 | 21.2065 | 25.565 | 28.8997 | 32.2371
StirlingIce Accretion2060RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2060 | 17.7128 | 21.165 | 25.535 | 28.8715 | 32.2119
StirlingIce Accretion2065RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2065 | 17.6675 | 21.1235 | 25.505 | 28.8432 | 32.1867
StirlingIce Accretion2070RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2070 | 17.6223 | 21.082 | 25.475 | 28.815 | 32.1615
StirlingIce Accretion2075RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2075 | 17.6919 | 21.1927 | 25.6375 | 29.0175 | 32.403
StirlingIce Accretion2080RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2080 | 17.7615 | 21.3033 | 25.8 | 29.2199 | 32.6445
StirlingIce Accretion2085RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2085 | 17.8311 | 21.414 | 25.9625 | 29.4224 | 32.886
StirlingIce Accretion2090RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2090 | 17.9006 | 21.5247 | 26.125 | 29.6248 | 33.1275
StirlingIce Accretion2095RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2095 | 17.9702 | 21.6353 | 26.2875 | 29.8273 | 33.369
StirlingIce Accretion2100RCP4.5 | Stirling | Ice Accretion | RCP4.5 | 2100 | 18.0398 | 21.746 | 26.45 | 30.0297 | 33.6105
StirlingIce Accretion2023RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3065 | 31.563
StirlingIce Accretion2025RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2025 | 17.544 | 20.9091 | 25.1667 | 28.4148 | 31.6837
StirlingIce Accretion2030RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2030 | 17.6049 | 20.9852 | 25.2583 | 28.5231 | 31.8045
StirlingIce Accretion2035RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2035 | 17.6658 | 21.0613 | 25.35 | 28.6314 | 31.9252
StirlingIce Accretion2040RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2040 | 17.7267 | 21.1373 | 25.4417 | 28.7397 | 32.046
StirlingIce Accretion2045RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2045 | 17.7876 | 21.2134 | 25.5333 | 28.848 | 32.1667
StirlingIce Accretion2050RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2050 | 17.8032 | 21.248 | 25.595 | 28.928 | 32.2623
StirlingIce Accretion2055RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2055 | 17.758 | 21.2065 | 25.565 | 28.8997 | 32.2371
StirlingIce Accretion2060RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2060 | 17.7128 | 21.165 | 25.535 | 28.8715 | 32.2119
StirlingIce Accretion2065RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2065 | 17.6675 | 21.1235 | 25.505 | 28.8432 | 32.1867
StirlingIce Accretion2070RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2070 | 17.6223 | 21.082 | 25.475 | 28.815 | 32.1615
StirlingIce Accretion2075RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2075 | 17.7267 | 21.248 | 25.7188 | 29.1187 | 32.5237
StirlingIce Accretion2080RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2080 | 17.8311 | 21.414 | 25.9625 | 29.4224 | 32.886
StirlingIce Accretion2085RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2085 | 17.9354 | 21.58 | 26.2063 | 29.7261 | 33.2482
StirlingIce Accretion2090RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2090 | 17.7499 | 21.4486 | 26.1333 | 29.7002 | 33.264
StirlingIce Accretion2095RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2095 | 17.4599 | 21.1512 | 25.8167 | 29.3706 | 32.9175
StirlingIce Accretion2100RCP6.0 | Stirling | Ice Accretion | RCP6.0 | 2100 | 17.17 | 20.8537 | 25.5 | 29.041 | 32.571
StirlingIce Accretion2023RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2023 | 17.4831 | 20.833 | 25.075 | 28.3065 | 31.563
StirlingIce Accretion2025RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2025 | 17.6049 | 20.9852 | 25.2583 | 28.5231 | 31.8045
StirlingIce Accretion2030RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2030 | 17.7267 | 21.1373 | 25.4417 | 28.7397 | 32.046
StirlingIce Accretion2035RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2035 | 17.8485 | 21.2895 | 25.625 | 28.9562 | 32.2875
StirlingIce Accretion2040RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2040 | 17.7731 | 21.2203 | 25.575 | 28.9092 | 32.2455
StirlingIce Accretion2045RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2045 | 17.6977 | 21.1512 | 25.525 | 28.8621 | 32.2035
StirlingIce Accretion2050RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2050 | 17.7615 | 21.3033 | 25.8 | 29.2199 | 32.6445
StirlingIce Accretion2055RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2055 | 17.9006 | 21.5247 | 26.125 | 29.6248 | 33.1275
StirlingIce Accretion2060RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2060 | 17.7499 | 21.4486 | 26.1333 | 29.7002 | 33.264
StirlingIce Accretion2065RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2065 | 17.4599 | 21.1512 | 25.8167 | 29.3706 | 32.9175
StirlingIce Accretion2070RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2070 | 16.8801 | 20.5287 | 25.1417 | 28.6455 | 32.151
StirlingIce Accretion2075RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2075 | 16.5901 | 20.2036 | 24.7833 | 28.25 | 31.731
StirlingIce Accretion2080RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2080 | 16.3002 | 19.8785 | 24.425 | 27.8545 | 31.311
StirlingIce Accretion2085RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2085 | 15.6826 | 19.1626 | 23.5875 | 26.9222 | 30.2715
StirlingIce Accretion2090RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2090 | 15.0651 | 18.4468 | 22.75 | 25.99 | 29.232
StirlingIce Accretion2095RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2095 | 15.0651 | 18.4468 | 22.75 | 25.99 | 29.232
StirlingIce Accretion2100RCP8.5 | Stirling | Ice Accretion | RCP8.5 | 2100 | 15.0651 | 18.4468 | 22.75 | 25.99 | 29.232
StirlingWind2023RCP4.5 | Stirling | Wind | RCP4.5 | 2023 | 76.1688 | 82.0773 | 88.308 | 94.5178 | 100.7413
StirlingWind2025RCP4.5 | Stirling | Wind | RCP4.5 | 2025 | 76.1992 | 82.1223 | 88.3696 | 94.5963 | 100.835
StirlingWind2030RCP4.5 | Stirling | Wind | RCP4.5 | 2030 | 76.2296 | 82.1674 | 88.4312 | 94.6747 | 100.9286
StirlingWind2035RCP4.5 | Stirling | Wind | RCP4.5 | 2035 | 76.26 | 82.2124 | 88.4928 | 94.7532 | 101.0222
StirlingWind2040RCP4.5 | Stirling | Wind | RCP4.5 | 2040 | 76.2904 | 82.2574 | 88.5544 | 94.8317 | 101.1159
StirlingWind2045RCP4.5 | Stirling | Wind | RCP4.5 | 2045 | 76.3208 | 82.3024 | 88.616 | 94.9101 | 101.2095
StirlingWind2050RCP4.5 | Stirling | Wind | RCP4.5 | 2050 | 76.3269 | 82.3016 | 88.609 | 94.8982 | 101.1908
StirlingWind2055RCP4.5 | Stirling | Wind | RCP4.5 | 2055 | 76.3026 | 82.2557 | 88.5403 | 94.8078 | 101.0784
StirlingWind2060RCP4.5 | Stirling | Wind | RCP4.5 | 2060 | 76.2782 | 82.2099 | 88.4717 | 94.7174 | 100.9661
StirlingWind2065RCP4.5 | Stirling | Wind | RCP4.5 | 2065 | 76.2539 | 82.1641 | 88.403 | 94.627 | 100.8537
StirlingWind2070RCP4.5 | Stirling | Wind | RCP4.5 | 2070 | 76.2296 | 82.1183 | 88.3344 | 94.5366 | 100.7413
StirlingWind2075RCP4.5 | Stirling | Wind | RCP4.5 | 2075 | 76.2068 | 82.0923 | 88.3036 | 94.5021 | 100.7046
StirlingWind2080RCP4.5 | Stirling | Wind | RCP4.5 | 2080 | 76.184 | 82.0664 | 88.2728 | 94.4676 | 100.6678
StirlingWind2085RCP4.5 | Stirling | Wind | RCP4.5 | 2085 | 76.1612 | 82.0405 | 88.242 | 94.4331 | 100.631
StirlingWind2090RCP4.5 | Stirling | Wind | RCP4.5 | 2090 | 76.1384 | 82.0146 | 88.2112 | 94.3985 | 100.5942
StirlingWind2095RCP4.5 | Stirling | Wind | RCP4.5 | 2095 | 76.1156 | 81.9887 | 88.1804 | 94.364 | 100.5574
StirlingWind2100RCP4.5 | Stirling | Wind | RCP4.5 | 2100 | 76.0928 | 81.9628 | 88.1496 | 94.3295 | 100.5206
StirlingWind2023RCP6.0 | Stirling | Wind | RCP6.0 | 2023 | 76.1688 | 82.0773 | 88.308 | 94.5178 | 100.7413
StirlingWind2025RCP6.0 | Stirling | Wind | RCP6.0 | 2025 | 76.1992 | 82.1223 | 88.3696 | 94.5963 | 100.835
StirlingWind2030RCP6.0 | Stirling | Wind | RCP6.0 | 2030 | 76.2296 | 82.1674 | 88.4312 | 94.6747 | 100.9286
StirlingWind2035RCP6.0 | Stirling | Wind | RCP6.0 | 2035 | 76.26 | 82.2124 | 88.4928 | 94.7532 | 101.0222
StirlingWind2040RCP6.0 | Stirling | Wind | RCP6.0 | 2040 | 76.2904 | 82.2574 | 88.5544 | 94.8317 | 101.1159
StirlingWind2045RCP6.0 | Stirling | Wind | RCP6.0 | 2045 | 76.3208 | 82.3024 | 88.616 | 94.9101 | 101.2095
StirlingWind2050RCP6.0 | Stirling | Wind | RCP6.0 | 2050 | 76.3269 | 82.3016 | 88.609 | 94.8982 | 101.1908
StirlingWind2055RCP6.0 | Stirling | Wind | RCP6.0 | 2055 | 76.3026 | 82.2557 | 88.5403 | 94.8078 | 101.0784
StirlingWind2060RCP6.0 | Stirling | Wind | RCP6.0 | 2060 | 76.2782 | 82.2099 | 88.4717 | 94.7174 | 100.9661
StirlingWind2065RCP6.0 | Stirling | Wind | RCP6.0 | 2065 | 76.2539 | 82.1641 | 88.403 | 94.627 | 100.8537
StirlingWind2070RCP6.0 | Stirling | Wind | RCP6.0 | 2070 | 76.2296 | 82.1183 | 88.3344 | 94.5366 | 100.7413
StirlingWind2075RCP6.0 | Stirling | Wind | RCP6.0 | 2075 | 76.1954 | 82.0794 | 88.2882 | 94.4849 | 100.6862
StirlingWind2080RCP6.0 | Stirling | Wind | RCP6.0 | 2080 | 76.1612 | 82.0405 | 88.242 | 94.4331 | 100.631
StirlingWind2085RCP6.0 | Stirling | Wind | RCP6.0 | 2085 | 76.127 | 82.0016 | 88.1958 | 94.3813 | 100.5758
StirlingWind2090RCP6.0 | Stirling | Wind | RCP6.0 | 2090 | 76.0802 | 81.9382 | 88.1085 | 94.273 | 100.4471
StirlingWind2095RCP6.0 | Stirling | Wind | RCP6.0 | 2095 | 76.0675 | 81.9137 | 88.0675 | 94.2165 | 100.3735
StirlingWind2100RCP6.0 | Stirling | Wind | RCP6.0 | 2100 | 76.0548 | 81.8891 | 88.0264 | 94.16 | 100.2999
StirlingWind2023RCP8.5 | Stirling | Wind | RCP8.5 | 2023 | 76.1688 | 82.0773 | 88.308 | 94.5178 | 100.7413
StirlingWind2025RCP8.5 | Stirling | Wind | RCP8.5 | 2025 | 76.2296 | 82.1674 | 88.4312 | 94.6747 | 100.9286
StirlingWind2030RCP8.5 | Stirling | Wind | RCP8.5 | 2030 | 76.2904 | 82.2574 | 88.5544 | 94.8317 | 101.1159
StirlingWind2035RCP8.5 | Stirling | Wind | RCP8.5 | 2035 | 76.3512 | 82.3474 | 88.6776 | 94.9886 | 101.3031
StirlingWind2040RCP8.5 | Stirling | Wind | RCP8.5 | 2040 | 76.3107 | 82.271 | 88.5632 | 94.838 | 101.1159
StirlingWind2045RCP8.5 | Stirling | Wind | RCP8.5 | 2045 | 76.2701 | 82.1946 | 88.4488 | 94.6873 | 100.9286
StirlingWind2050RCP8.5 | Stirling | Wind | RCP8.5 | 2050 | 76.184 | 82.0664 | 88.2728 | 94.4676 | 100.6678
StirlingWind2055RCP8.5 | Stirling | Wind | RCP8.5 | 2055 | 76.1384 | 82.0146 | 88.2112 | 94.3985 | 100.5942
StirlingWind2060RCP8.5 | Stirling | Wind | RCP8.5 | 2060 | 76.0802 | 81.9382 | 88.1085 | 94.273 | 100.4471
StirlingWind2065RCP8.5 | Stirling | Wind | RCP8.5 | 2065 | 76.0675 | 81.9137 | 88.0675 | 94.2165 | 100.3735
StirlingWind2070RCP8.5 | Stirling | Wind | RCP8.5 | 2070 | 76.0219 | 81.8455 | 87.9707 | 94.0941 | 100.223
StirlingWind2075RCP8.5 | Stirling | Wind | RCP8.5 | 2075 | 75.989 | 81.8018 | 87.9149 | 94.0282 | 100.1461
StirlingWind2080RCP8.5 | Stirling | Wind | RCP8.5 | 2080 | 75.9561 | 81.7582 | 87.8592 | 93.9623 | 100.0692
StirlingWind2085RCP8.5 | Stirling | Wind | RCP8.5 | 2085 | 75.9143 | 81.7295 | 87.846 | 93.967 | 100.0842
StirlingWind2090RCP8.5 | Stirling | Wind | RCP8.5 | 2090 | 75.8725 | 81.7009 | 87.8328 | 93.9717 | 100.0993
StirlingWind2095RCP8.5 | Stirling | Wind | RCP8.5 | 2095 | 75.8725 | 81.7009 | 87.8328 | 93.9717 | 100.0993
StirlingWind2100RCP8.5 | Stirling | Wind | RCP8.5 | 2100 | 75.8725 | 81.7009 | 87.8328 | 93.9717 | 100.0993
StratfordIce Accretion2023RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425
StratfordIce Accretion2025RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2025 | 17.1352 | 20.5563 | 24.8625 | 28.1605 | 31.4423
StratfordIce Accretion2030RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2030 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542
StratfordIce Accretion2035RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2035 | 17.17 | 20.6255 | 24.9875 | 28.3206 | 31.6418
StratfordIce Accretion2040RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2040 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415
StratfordIce Accretion2045RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2045 | 17.2048 | 20.6947 | 25.1125 | 28.4807 | 31.8412
StratfordIce Accretion2050RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2050 | 17.1526 | 20.6794 | 25.145 | 28.5438 | 31.941
StratfordIce Accretion2055RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2055 | 17.083 | 20.6296 | 25.115 | 28.5268 | 31.941
StratfordIce Accretion2060RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2060 | 17.0134 | 20.5799 | 25.085 | 28.5099 | 31.941
StratfordIce Accretion2065RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2065 | 16.9439 | 20.53 | 25.055 | 28.4929 | 31.941
StratfordIce Accretion2070RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2070 | 16.8743 | 20.4802 | 25.025 | 28.476 | 31.941
StratfordIce Accretion2075RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2075 | 16.8424 | 20.4664 | 25.0375 | 28.5042 | 31.9883
StratfordIce Accretion2080RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2080 | 16.8105 | 20.4526 | 25.05 | 28.5325 | 32.0355
StratfordIce Accretion2085RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2085 | 16.7786 | 20.4387 | 25.0625 | 28.5607 | 32.0827
StratfordIce Accretion2090RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2090 | 16.7467 | 20.4249 | 25.075 | 28.589 | 32.13
StratfordIce Accretion2095RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2095 | 16.7148 | 20.4111 | 25.0875 | 28.6172 | 32.1773
StratfordIce Accretion2100RCP4.5 | Stratford | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.3972 | 25.1 | 28.6455 | 32.2245
StratfordIce Accretion2023RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425
StratfordIce Accretion2025RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2025 | 17.1352 | 20.5563 | 24.8625 | 28.1605 | 31.4423
StratfordIce Accretion2030RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2030 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542
StratfordIce Accretion2035RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2035 | 17.17 | 20.6255 | 24.9875 | 28.3206 | 31.6418
StratfordIce Accretion2040RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2040 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415
StratfordIce Accretion2045RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2045 | 17.2048 | 20.6947 | 25.1125 | 28.4807 | 31.8412
StratfordIce Accretion2050RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2050 | 17.1526 | 20.6794 | 25.145 | 28.5438 | 31.941
StratfordIce Accretion2055RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2055 | 17.083 | 20.6296 | 25.115 | 28.5268 | 31.941
StratfordIce Accretion2060RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2060 | 17.0134 | 20.5799 | 25.085 | 28.5099 | 31.941
StratfordIce Accretion2065RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2065 | 16.9439 | 20.53 | 25.055 | 28.4929 | 31.941
StratfordIce Accretion2070RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2070 | 16.8743 | 20.4802 | 25.025 | 28.476 | 31.941
StratfordIce Accretion2075RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2075 | 16.8264 | 20.4595 | 25.0437 | 28.5184 | 32.0119
StratfordIce Accretion2080RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2080 | 16.7786 | 20.4387 | 25.0625 | 28.5607 | 32.0827
StratfordIce Accretion2085RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2085 | 16.7308 | 20.418 | 25.0813 | 28.6031 | 32.1536
StratfordIce Accretion2090RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2090 | 16.4742 | 20.1898 | 24.8833 | 28.4289 | 31.9935
StratfordIce Accretion2095RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2095 | 16.2654 | 19.9822 | 24.6667 | 28.2123 | 31.7625
StratfordIce Accretion2100RCP6.0 | Stratford | Ice Accretion | RCP6.0 | 2100 | 16.0566 | 19.7747 | 24.45 | 27.9957 | 31.5315
StratfordIce Accretion2023RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2023 | 17.1178 | 20.5218 | 24.8 | 28.0805 | 31.3425
StratfordIce Accretion2025RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2025 | 17.1526 | 20.5909 | 24.925 | 28.2406 | 31.542
StratfordIce Accretion2030RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2030 | 17.1874 | 20.6601 | 25.05 | 28.4007 | 31.7415
StratfordIce Accretion2035RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2035 | 17.2222 | 20.7293 | 25.175 | 28.5607 | 31.941
StratfordIce Accretion2040RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2040 | 17.1062 | 20.6462 | 25.125 | 28.5325 | 31.941
StratfordIce Accretion2045RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2045 | 16.9902 | 20.5633 | 25.075 | 28.5042 | 31.941
StratfordIce Accretion2050RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2050 | 16.8105 | 20.4526 | 25.05 | 28.5325 | 32.0355
StratfordIce Accretion2055RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2055 | 16.7467 | 20.4249 | 25.075 | 28.589 | 32.13
StratfordIce Accretion2060RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2060 | 16.4742 | 20.1898 | 24.8833 | 28.4289 | 31.9935
StratfordIce Accretion2065RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2065 | 16.2654 | 19.9822 | 24.6667 | 28.2123 | 31.7625
StratfordIce Accretion2070RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2070 | 15.6797 | 19.3528 | 23.975 | 27.4778 | 30.9645
StratfordIce Accretion2075RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2075 | 15.3028 | 18.9309 | 23.5 | 26.9599 | 30.3975
StratfordIce Accretion2080RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2080 | 14.9259 | 18.509 | 23.025 | 26.442 | 29.8305
StratfordIce Accretion2085RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2085 | 14.1431 | 17.5856 | 21.925 | 25.2131 | 28.476
StratfordIce Accretion2090RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2090 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215
StratfordIce Accretion2095RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2095 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215
StratfordIce Accretion2100RCP8.5 | Stratford | Ice Accretion | RCP8.5 | 2100 | 13.3602 | 16.6623 | 20.825 | 23.9842 | 27.1215
StratfordWind2023RCP4.5 | Stratford | Wind | RCP4.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
StratfordWind2025RCP4.5 | Stratford | Wind | RCP4.5 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
StratfordWind2030RCP4.5 | Stratford | Wind | RCP4.5 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
StratfordWind2035RCP4.5 | Stratford | Wind | RCP4.5 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
StratfordWind2040RCP4.5 | Stratford | Wind | RCP4.5 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
StratfordWind2045RCP4.5 | Stratford | Wind | RCP4.5 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
StratfordWind2050RCP4.5 | Stratford | Wind | RCP4.5 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
StratfordWind2055RCP4.5 | Stratford | Wind | RCP4.5 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
StratfordWind2060RCP4.5 | Stratford | Wind | RCP4.5 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
StratfordWind2065RCP4.5 | Stratford | Wind | RCP4.5 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
StratfordWind2070RCP4.5 | Stratford | Wind | RCP4.5 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
StratfordWind2075RCP4.5 | Stratford | Wind | RCP4.5 | 2075 | 86.3504 | 93.3577 | 100.8387 | 108.226 | 115.6228
StratfordWind2080RCP4.5 | Stratford | Wind | RCP4.5 | 2080 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
StratfordWind2085RCP4.5 | Stratford | Wind | RCP4.5 | 2085 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
StratfordWind2090RCP4.5 | Stratford | Wind | RCP4.5 | 2090 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
StratfordWind2095RCP4.5 | Stratford | Wind | RCP4.5 | 2095 | 86.7678 | 93.9167 | 101.5705 | 109.1068 | 116.6655
StratfordWind2100RCP4.5 | Stratford | Wind | RCP4.5 | 2100 | 86.8722 | 94.0565 | 101.7534 | 109.327 | 116.9262
StratfordWind2023RCP6.0 | Stratford | Wind | RCP6.0 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
StratfordWind2025RCP6.0 | Stratford | Wind | RCP6.0 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
StratfordWind2030RCP6.0 | Stratford | Wind | RCP6.0 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
StratfordWind2035RCP6.0 | Stratford | Wind | RCP6.0 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
StratfordWind2040RCP6.0 | Stratford | Wind | RCP6.0 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
StratfordWind2045RCP6.0 | Stratford | Wind | RCP6.0 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
StratfordWind2050RCP6.0 | Stratford | Wind | RCP6.0 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
StratfordWind2055RCP6.0 | Stratford | Wind | RCP6.0 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
StratfordWind2060RCP6.0 | Stratford | Wind | RCP6.0 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
StratfordWind2065RCP6.0 | Stratford | Wind | RCP6.0 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
StratfordWind2070RCP6.0 | Stratford | Wind | RCP6.0 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
StratfordWind2075RCP6.0 | Stratford | Wind | RCP6.0 | 2075 | 86.4026 | 93.4276 | 100.9302 | 108.3361 | 115.7531
StratfordWind2080RCP6.0 | Stratford | Wind | RCP6.0 | 2080 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
StratfordWind2085RCP6.0 | Stratford | Wind | RCP6.0 | 2085 | 86.7157 | 93.8469 | 101.479 | 108.9967 | 116.5351
StratfordWind2090RCP6.0 | Stratford | Wind | RCP6.0 | 2090 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
StratfordWind2095RCP6.0 | Stratford | Wind | RCP6.0 | 2095 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
StratfordWind2100RCP6.0 | Stratford | Wind | RCP6.0 | 2100 | 87.7861 | 95.1502 | 103.0568 | 110.8265 | 118.6131
StratfordWind2023RCP8.5 | Stratford | Wind | RCP8.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
StratfordWind2025RCP8.5 | Stratford | Wind | RCP8.5 | 2025 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
StratfordWind2030RCP8.5 | Stratford | Wind | RCP8.5 | 2030 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
StratfordWind2035RCP8.5 | Stratford | Wind | RCP8.5 | 2035 | 86.0768 | 93.0084 | 100.3912 | 107.7017 | 115.0269
StratfordWind2040RCP8.5 | Stratford | Wind | RCP8.5 | 2040 | 86.1332 | 93.0782 | 100.4794 | 107.8031 | 115.1386
StratfordWind2045RCP8.5 | Stratford | Wind | RCP8.5 | 2045 | 86.1896 | 93.1481 | 100.5676 | 107.9044 | 115.2504
StratfordWind2050RCP8.5 | Stratford | Wind | RCP8.5 | 2050 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
StratfordWind2055RCP8.5 | Stratford | Wind | RCP8.5 | 2055 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
StratfordWind2060RCP8.5 | Stratford | Wind | RCP8.5 | 2060 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
StratfordWind2065RCP8.5 | Stratford | Wind | RCP8.5 | 2065 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
StratfordWind2070RCP8.5 | Stratford | Wind | RCP8.5 | 2070 | 88.0541 | 95.5026 | 103.5207 | 111.3788 | 119.2611
StratfordWind2075RCP8.5 | Stratford | Wind | RCP8.5 | 2075 | 88.322 | 95.855 | 103.9845 | 111.9311 | 119.9091
StratfordWind2080RCP8.5 | Stratford | Wind | RCP8.5 | 2080 | 88.59 | 96.2074 | 104.4484 | 112.4833 | 120.5571
StratfordWind2085RCP8.5 | Stratford | Wind | RCP8.5 | 2085 | 88.9454 | 96.6585 | 105.0217 | 113.1649 | 121.3447
StratfordWind2090RCP8.5 | Stratford | Wind | RCP8.5 | 2090 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
StratfordWind2095RCP8.5 | Stratford | Wind | RCP8.5 | 2095 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
StratfordWind2100RCP8.5 | Stratford | Wind | RCP8.5 | 2100 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
StrathroyIce Accretion2023RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2023 | 16.7525 | 20.1067 | 24.35 | 27.572 | 30.807
StrathroyIce Accretion2025RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2025 | 16.6858 | 20.041 | 24.2833 | 27.5061 | 30.7387
StrathroyIce Accretion2030RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2030 | 16.6191 | 19.9753 | 24.2167 | 27.4402 | 30.6705
StrathroyIce Accretion2035RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2035 | 16.5524 | 19.9096 | 24.15 | 27.3742 | 30.6022
StrathroyIce Accretion2040RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2040 | 16.4858 | 19.8439 | 24.0833 | 27.3083 | 30.534
StrathroyIce Accretion2045RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2045 | 16.4191 | 19.7782 | 24.0167 | 27.2424 | 30.4657
StrathroyIce Accretion2050RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2050 | 16.0462 | 19.3722 | 23.56 | 26.7527 | 29.9376
StrathroyIce Accretion2055RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2055 | 15.74 | 19.0319 | 23.17 | 26.329 | 29.4777
StrathroyIce Accretion2060RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2060 | 15.4339 | 18.6916 | 22.78 | 25.9052 | 29.0178
StrathroyIce Accretion2065RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2065 | 15.1277 | 18.3513 | 22.39 | 25.4815 | 28.5579
StrathroyIce Accretion2070RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2070 | 14.8215 | 18.011 | 22 | 25.0577 | 28.098
StrathroyIce Accretion2075RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2075 | 14.6824 | 17.8657 | 21.85 | 24.8977 | 27.93
StrathroyIce Accretion2080RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2080 | 14.5432 | 17.7205 | 21.7 | 24.7376 | 27.762
StrathroyIce Accretion2085RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2085 | 14.404 | 17.5753 | 21.55 | 24.5775 | 27.594
StrathroyIce Accretion2090RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2090 | 14.2648 | 17.43 | 21.4 | 24.4174 | 27.426
StrathroyIce Accretion2095RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2095 | 14.1257 | 17.2848 | 21.25 | 24.2573 | 27.258
StrathroyIce Accretion2100RCP4.5 | Strathroy | Ice Accretion | RCP4.5 | 2100 | 13.9865 | 17.1395 | 21.1 | 24.0972 | 27.09
StrathroyIce Accretion2023RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2023 | 16.7525 | 20.1067 | 24.35 | 27.572 | 30.807
StrathroyIce Accretion2025RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2025 | 16.6858 | 20.041 | 24.2833 | 27.5061 | 30.7387
StrathroyIce Accretion2030RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2030 | 16.6191 | 19.9753 | 24.2167 | 27.4402 | 30.6705
StrathroyIce Accretion2035RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2035 | 16.5524 | 19.9096 | 24.15 | 27.3742 | 30.6022
StrathroyIce Accretion2040RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2040 | 16.4858 | 19.8439 | 24.0833 | 27.3083 | 30.534
StrathroyIce Accretion2045RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2045 | 16.4191 | 19.7782 | 24.0167 | 27.2424 | 30.4657
StrathroyIce Accretion2050RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2050 | 16.0462 | 19.3722 | 23.56 | 26.7527 | 29.9376
StrathroyIce Accretion2055RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2055 | 15.74 | 19.0319 | 23.17 | 26.329 | 29.4777
StrathroyIce Accretion2060RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2060 | 15.4339 | 18.6916 | 22.78 | 25.9052 | 29.0178
StrathroyIce Accretion2065RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2065 | 15.1277 | 18.3513 | 22.39 | 25.4815 | 28.5579
StrathroyIce Accretion2070RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2070 | 14.8215 | 18.011 | 22 | 25.0577 | 28.098
StrathroyIce Accretion2075RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2075 | 14.6128 | 17.7931 | 21.775 | 24.8176 | 27.846
StrathroyIce Accretion2080RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2080 | 14.404 | 17.5753 | 21.55 | 24.5775 | 27.594
StrathroyIce Accretion2085RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2085 | 14.1953 | 17.3574 | 21.325 | 24.3374 | 27.342
StrathroyIce Accretion2090RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2090 | 13.5632 | 16.6623 | 20.55 | 23.4852 | 26.418
StrathroyIce Accretion2095RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2095 | 13.1399 | 16.185 | 20 | 22.8731 | 25.746
StrathroyIce Accretion2100RCP6.0 | Strathroy | Ice Accretion | RCP6.0 | 2100 | 12.7166 | 15.7078 | 19.45 | 22.261 | 25.074
StrathroyIce Accretion2023RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2023 | 16.7525 | 20.1067 | 24.35 | 27.572 | 30.807
StrathroyIce Accretion2025RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2025 | 16.6191 | 19.9753 | 24.2167 | 27.4402 | 30.6705
StrathroyIce Accretion2030RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2030 | 16.4858 | 19.8439 | 24.0833 | 27.3083 | 30.534
StrathroyIce Accretion2035RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2035 | 16.3524 | 19.7125 | 23.95 | 27.1765 | 30.3975
StrathroyIce Accretion2040RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2040 | 15.8421 | 19.1453 | 23.3 | 26.4702 | 29.631
StrathroyIce Accretion2045RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2045 | 15.3318 | 18.5782 | 22.65 | 25.764 | 28.8645
StrathroyIce Accretion2050RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2050 | 14.5432 | 17.7205 | 21.7 | 24.7376 | 27.762
StrathroyIce Accretion2055RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2055 | 14.2648 | 17.43 | 21.4 | 24.4174 | 27.426
StrathroyIce Accretion2060RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2060 | 13.5632 | 16.6623 | 20.55 | 23.4852 | 26.418
StrathroyIce Accretion2065RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2065 | 13.1399 | 16.185 | 20 | 22.8731 | 25.746
StrathroyIce Accretion2070RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2070 | 12.3861 | 15.3481 | 19.0417 | 21.8278 | 24.6015
StrathroyIce Accretion2075RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2075 | 12.0555 | 14.9884 | 18.6333 | 21.3947 | 24.129
StrathroyIce Accretion2080RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2080 | 11.725 | 14.6288 | 18.225 | 20.9615 | 23.6565
StrathroyIce Accretion2085RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2085 | 10.9248 | 13.6743 | 17.0875 | 19.662 | 22.2233
StrathroyIce Accretion2090RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2090 | 10.1246 | 12.7197 | 15.95 | 18.3625 | 20.79
StrathroyIce Accretion2095RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2095 | 10.1246 | 12.7197 | 15.95 | 18.3625 | 20.79
StrathroyIce Accretion2100RCP8.5 | Strathroy | Ice Accretion | RCP8.5 | 2100 | 10.1246 | 12.7197 | 15.95 | 18.3625 | 20.79
StrathroyWind2023RCP4.5 | Strathroy | Wind | RCP4.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
StrathroyWind2025RCP4.5 | Strathroy | Wind | RCP4.5 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
StrathroyWind2030RCP4.5 | Strathroy | Wind | RCP4.5 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
StrathroyWind2035RCP4.5 | Strathroy | Wind | RCP4.5 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
StrathroyWind2040RCP4.5 | Strathroy | Wind | RCP4.5 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
StrathroyWind2045RCP4.5 | Strathroy | Wind | RCP4.5 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
StrathroyWind2050RCP4.5 | Strathroy | Wind | RCP4.5 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
StrathroyWind2055RCP4.5 | Strathroy | Wind | RCP4.5 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
StrathroyWind2060RCP4.5 | Strathroy | Wind | RCP4.5 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
StrathroyWind2065RCP4.5 | Strathroy | Wind | RCP4.5 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
StrathroyWind2070RCP4.5 | Strathroy | Wind | RCP4.5 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
StrathroyWind2075RCP4.5 | Strathroy | Wind | RCP4.5 | 2075 | 85.7411 | 92.542 | 99.746 | 106.9048 | 114.0736
StrathroyWind2080RCP4.5 | Strathroy | Wind | RCP4.5 | 2080 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
StrathroyWind2085RCP4.5 | Strathroy | Wind | RCP4.5 | 2085 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
StrathroyWind2090RCP4.5 | Strathroy | Wind | RCP4.5 | 2090 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
StrathroyWind2095RCP4.5 | Strathroy | Wind | RCP4.5 | 2095 | 86.3278 | 93.3015 | 100.7326 | 108.0792 | 115.444
StrathroyWind2100RCP4.5 | Strathroy | Wind | RCP4.5 | 2100 | 86.4745 | 93.4914 | 100.9792 | 108.3728 | 115.7866
StrathroyWind2023RCP6.0 | Strathroy | Wind | RCP6.0 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
StrathroyWind2025RCP6.0 | Strathroy | Wind | RCP6.0 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
StrathroyWind2030RCP6.0 | Strathroy | Wind | RCP6.0 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
StrathroyWind2035RCP6.0 | Strathroy | Wind | RCP6.0 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
StrathroyWind2040RCP6.0 | Strathroy | Wind | RCP6.0 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
StrathroyWind2045RCP6.0 | Strathroy | Wind | RCP6.0 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
StrathroyWind2050RCP6.0 | Strathroy | Wind | RCP6.0 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
StrathroyWind2055RCP6.0 | Strathroy | Wind | RCP6.0 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
StrathroyWind2060RCP6.0 | Strathroy | Wind | RCP6.0 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
StrathroyWind2065RCP6.0 | Strathroy | Wind | RCP6.0 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
StrathroyWind2070RCP6.0 | Strathroy | Wind | RCP6.0 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
StrathroyWind2075RCP6.0 | Strathroy | Wind | RCP6.0 | 2075 | 85.8144 | 92.637 | 99.8693 | 107.0516 | 114.2449
StrathroyWind2080RCP6.0 | Strathroy | Wind | RCP6.0 | 2080 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
StrathroyWind2085RCP6.0 | Strathroy | Wind | RCP6.0 | 2085 | 86.2545 | 93.2066 | 100.6093 | 107.9324 | 115.2727
StrathroyWind2090RCP6.0 | Strathroy | Wind | RCP6.0 | 2090 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
StrathroyWind2095RCP6.0 | Strathroy | Wind | RCP6.0 | 2095 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
StrathroyWind2100RCP6.0 | Strathroy | Wind | RCP6.0 | 2100 | 87.5746 | 94.8494 | 102.6452 | 110.3127 | 117.9987
StrathroyWind2023RCP8.5 | Strathroy | Wind | RCP8.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
StrathroyWind2025RCP8.5 | Strathroy | Wind | RCP8.5 | 2025 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
StrathroyWind2030RCP8.5 | Strathroy | Wind | RCP8.5 | 2030 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
StrathroyWind2035RCP8.5 | Strathroy | Wind | RCP8.5 | 2035 | 85.586 | 92.3248 | 99.4504 | 106.5378 | 113.6304
StrathroyWind2040RCP8.5 | Strathroy | Wind | RCP8.5 | 2040 | 85.5888 | 92.3339 | 99.4667 | 106.5622 | 113.6639
StrathroyWind2045RCP8.5 | Strathroy | Wind | RCP8.5 | 2045 | 85.5916 | 92.343 | 99.4831 | 106.5867 | 113.6974
StrathroyWind2050RCP8.5 | Strathroy | Wind | RCP8.5 | 2050 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
StrathroyWind2055RCP8.5 | Strathroy | Wind | RCP8.5 | 2055 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
StrathroyWind2060RCP8.5 | Strathroy | Wind | RCP8.5 | 2060 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
StrathroyWind2065RCP8.5 | Strathroy | Wind | RCP8.5 | 2065 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
StrathroyWind2070RCP8.5 | Strathroy | Wind | RCP8.5 | 2070 | 87.882 | 95.2383 | 103.1385 | 110.8929 | 118.669
StrathroyWind2075RCP8.5 | Strathroy | Wind | RCP8.5 | 2075 | 88.1895 | 95.6271 | 103.6317 | 111.4732 | 119.3393
StrathroyWind2080RCP8.5 | Strathroy | Wind | RCP8.5 | 2080 | 88.4969 | 96.016 | 104.125 | 112.0534 | 120.0096
StrathroyWind2085RCP8.5 | Strathroy | Wind | RCP8.5 | 2085 | 88.8396 | 96.4489 | 104.664 | 112.6826 | 120.7358
StrathroyWind2090RCP8.5 | Strathroy | Wind | RCP8.5 | 2090 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
StrathroyWind2095RCP8.5 | Strathroy | Wind | RCP8.5 | 2095 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
StrathroyWind2100RCP8.5 | Strathroy | Wind | RCP8.5 | 2100 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
Sturgeon FallsIce Accretion2023RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2023 | 16.4046 | 19.6054 | 23.667 | 26.7437 | 29.8494
Sturgeon FallsIce Accretion2025RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2025 | 16.5086 | 19.7359 | 23.8357 | 26.943 | 30.0716
Sturgeon FallsIce Accretion2030RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2030 | 16.6126 | 19.8663 | 24.0043 | 27.1422 | 30.2938
Sturgeon FallsIce Accretion2035RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2035 | 16.7167 | 19.9968 | 24.173 | 27.3415 | 30.5159
Sturgeon FallsIce Accretion2040RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2040 | 16.8207 | 20.1272 | 24.3417 | 27.5407 | 30.7381
Sturgeon FallsIce Accretion2045RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2045 | 16.9247 | 20.2577 | 24.5103 | 27.74 | 30.9603
Sturgeon FallsIce Accretion2050RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2050 | 17.16 | 20.5752 | 24.932 | 28.2407 | 31.5418
Sturgeon FallsIce Accretion2055RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2055 | 17.2912 | 20.7623 | 25.185 | 28.5422 | 31.9012
Sturgeon FallsIce Accretion2060RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2060 | 17.4225 | 20.9494 | 25.438 | 28.8437 | 32.2605
Sturgeon FallsIce Accretion2065RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2065 | 17.5537 | 21.1364 | 25.691 | 29.1452 | 32.6199
Sturgeon FallsIce Accretion2070RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2070 | 17.6849 | 21.3235 | 25.944 | 29.4467 | 32.9792
Sturgeon FallsIce Accretion2075RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2075 | 17.6209 | 21.2599 | 25.8827 | 29.386 | 32.9164
Sturgeon FallsIce Accretion2080RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2080 | 17.5569 | 21.1963 | 25.8213 | 29.3254 | 32.8537
Sturgeon FallsIce Accretion2085RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2085 | 17.4929 | 21.1326 | 25.76 | 29.2647 | 32.7909
Sturgeon FallsIce Accretion2090RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2090 | 17.4289 | 21.069 | 25.6987 | 29.2041 | 32.7281
Sturgeon FallsIce Accretion2095RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2095 | 17.3648 | 21.0054 | 25.6373 | 29.1435 | 32.6653
Sturgeon FallsIce Accretion2100RCP4.5 | Sturgeon Falls | Ice Accretion | RCP4.5 | 2100 | 17.3008 | 20.9417 | 25.576 | 29.0828 | 32.6025
Sturgeon FallsIce Accretion2023RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2023 | 16.4046 | 19.6054 | 23.667 | 26.7437 | 29.8494
Sturgeon FallsIce Accretion2025RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2025 | 16.5086 | 19.7359 | 23.8357 | 26.943 | 30.0716
Sturgeon FallsIce Accretion2030RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2030 | 16.6126 | 19.8663 | 24.0043 | 27.1422 | 30.2938
Sturgeon FallsIce Accretion2035RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2035 | 16.7167 | 19.9968 | 24.173 | 27.3415 | 30.5159
Sturgeon FallsIce Accretion2040RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2040 | 16.8207 | 20.1272 | 24.3417 | 27.5407 | 30.7381
Sturgeon FallsIce Accretion2045RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2045 | 16.9247 | 20.2577 | 24.5103 | 27.74 | 30.9603
Sturgeon FallsIce Accretion2050RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2050 | 17.16 | 20.5752 | 24.932 | 28.2407 | 31.5418
Sturgeon FallsIce Accretion2055RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2055 | 17.2912 | 20.7623 | 25.185 | 28.5422 | 31.9012
Sturgeon FallsIce Accretion2060RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2060 | 17.4225 | 20.9494 | 25.438 | 28.8437 | 32.2605
Sturgeon FallsIce Accretion2065RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2065 | 17.5537 | 21.1364 | 25.691 | 29.1452 | 32.6199
Sturgeon FallsIce Accretion2070RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2070 | 17.6849 | 21.3235 | 25.944 | 29.4467 | 32.9792
Sturgeon FallsIce Accretion2075RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2075 | 17.5889 | 21.2281 | 25.852 | 29.3557 | 32.8851
Sturgeon FallsIce Accretion2080RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2080 | 17.4929 | 21.1326 | 25.76 | 29.2647 | 32.7909
Sturgeon FallsIce Accretion2085RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2085 | 17.3968 | 21.0372 | 25.668 | 29.1738 | 32.6967
Sturgeon FallsIce Accretion2090RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2090 | 17.2795 | 20.9354 | 25.5837 | 29.1088 | 32.6411
Sturgeon FallsIce Accretion2095RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2095 | 17.2581 | 20.929 | 25.5913 | 29.1348 | 32.6798
Sturgeon FallsIce Accretion2100RCP6.0 | Sturgeon Falls | Ice Accretion | RCP6.0 | 2100 | 17.2368 | 20.9226 | 25.599 | 29.1608 | 32.7184
Sturgeon FallsIce Accretion2023RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2023 | 16.4046 | 19.6054 | 23.667 | 26.7437 | 29.8494
Sturgeon FallsIce Accretion2025RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2025 | 16.6126 | 19.8663 | 24.0043 | 27.1422 | 30.2938
Sturgeon FallsIce Accretion2030RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2030 | 16.8207 | 20.1272 | 24.3417 | 27.5407 | 30.7381
Sturgeon FallsIce Accretion2035RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2035 | 17.0287 | 20.3881 | 24.679 | 27.9392 | 31.1825
Sturgeon FallsIce Accretion2040RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2040 | 17.2475 | 20.6999 | 25.1007 | 28.4417 | 31.7814
Sturgeon FallsIce Accretion2045RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2045 | 17.4662 | 21.0117 | 25.5223 | 28.9442 | 32.3803
Sturgeon FallsIce Accretion2050RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2050 | 17.5569 | 21.1963 | 25.8213 | 29.3254 | 32.8537
Sturgeon FallsIce Accretion2055RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2055 | 17.4289 | 21.069 | 25.6987 | 29.2041 | 32.7281
Sturgeon FallsIce Accretion2060RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2060 | 17.2795 | 20.9354 | 25.5837 | 29.1088 | 32.6411
Sturgeon FallsIce Accretion2065RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2065 | 17.2581 | 20.929 | 25.5913 | 29.1348 | 32.6798
Sturgeon FallsIce Accretion2070RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2070 | 16.7993 | 20.4072 | 24.9703 | 28.4504 | 31.9263
Sturgeon FallsIce Accretion2075RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2075 | 16.3619 | 19.8918 | 24.3417 | 27.74 | 31.1342
Sturgeon FallsIce Accretion2080RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2080 | 15.9244 | 19.3763 | 23.713 | 27.0296 | 30.3421
Sturgeon FallsIce Accretion2085RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2085 | 15.6764 | 19.1186 | 23.46 | 26.7567 | 30.0667
Sturgeon FallsIce Accretion2090RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2090 | 15.4283 | 18.8609 | 23.207 | 26.4838 | 29.7914
Sturgeon FallsIce Accretion2095RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2095 | 15.4283 | 18.8609 | 23.207 | 26.4838 | 29.7914
Sturgeon FallsIce Accretion2100RCP8.5 | Sturgeon Falls | Ice Accretion | RCP8.5 | 2100 | 15.4283 | 18.8609 | 23.207 | 26.4838 | 29.7914
Sturgeon FallsWind2023RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2023 | 76.6095 | 82.4947 | 88.6864 | 94.885 | 101.0824
Sturgeon FallsWind2025RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2025 | 76.6349 | 82.522 | 88.7143 | 94.9148 | 101.1125
Sturgeon FallsWind2030RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2030 | 76.6602 | 82.5493 | 88.7421 | 94.9447 | 101.1426
Sturgeon FallsWind2035RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2035 | 76.6855 | 82.5766 | 88.77 | 94.9745 | 101.1727
Sturgeon FallsWind2040RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2040 | 76.7109 | 82.6038 | 88.7979 | 95.0043 | 101.2028
Sturgeon FallsWind2045RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2045 | 76.7362 | 82.6311 | 88.8257 | 95.0341 | 101.2329
Sturgeon FallsWind2050RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2050 | 76.7007 | 82.5749 | 88.7427 | 94.9302 | 101.1065
Sturgeon FallsWind2055RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2055 | 76.6399 | 82.4914 | 88.6318 | 94.7965 | 100.95
Sturgeon FallsWind2060RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2060 | 76.5791 | 82.408 | 88.521 | 94.6628 | 100.7935
Sturgeon FallsWind2065RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2065 | 76.5184 | 82.3245 | 88.4101 | 94.5291 | 100.637
Sturgeon FallsWind2070RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2070 | 76.4576 | 82.241 | 88.2992 | 94.3954 | 100.4805
Sturgeon FallsWind2075RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2075 | 76.5222 | 82.3242 | 88.4048 | 94.5194 | 100.6243
Sturgeon FallsWind2080RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2080 | 76.5867 | 82.4074 | 88.5104 | 94.6434 | 100.7681
Sturgeon FallsWind2085RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2085 | 76.6513 | 82.4906 | 88.616 | 94.7673 | 100.9119
Sturgeon FallsWind2090RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2090 | 76.7159 | 82.5738 | 88.7216 | 94.8913 | 101.0557
Sturgeon FallsWind2095RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2095 | 76.7805 | 82.657 | 88.8272 | 95.0153 | 101.1995
Sturgeon FallsWind2100RCP4.5 | Sturgeon Falls | Wind | RCP4.5 | 2100 | 76.8451 | 82.7402 | 88.9328 | 95.1393 | 101.3433
Sturgeon FallsWind2023RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2023 | 76.6095 | 82.4947 | 88.6864 | 94.885 | 101.0824
Sturgeon FallsWind2025RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2025 | 76.6349 | 82.522 | 88.7143 | 94.9148 | 101.1125
Sturgeon FallsWind2030RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2030 | 76.6602 | 82.5493 | 88.7421 | 94.9447 | 101.1426
Sturgeon FallsWind2035RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2035 | 76.6855 | 82.5766 | 88.77 | 94.9745 | 101.1727
Sturgeon FallsWind2040RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2040 | 76.7109 | 82.6038 | 88.7979 | 95.0043 | 101.2028
Sturgeon FallsWind2045RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2045 | 76.7362 | 82.6311 | 88.8257 | 95.0341 | 101.2329
Sturgeon FallsWind2050RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2050 | 76.7007 | 82.5749 | 88.7427 | 94.9302 | 101.1065
Sturgeon FallsWind2055RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2055 | 76.6399 | 82.4914 | 88.6318 | 94.7965 | 100.95
Sturgeon FallsWind2060RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2060 | 76.5791 | 82.408 | 88.521 | 94.6628 | 100.7935
Sturgeon FallsWind2065RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2065 | 76.5184 | 82.3245 | 88.4101 | 94.5291 | 100.637
Sturgeon FallsWind2070RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2070 | 76.4576 | 82.241 | 88.2992 | 94.3954 | 100.4805
Sturgeon FallsWind2075RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2075 | 76.5545 | 82.3658 | 88.4576 | 94.5814 | 100.6962
Sturgeon FallsWind2080RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2080 | 76.6513 | 82.4906 | 88.616 | 94.7673 | 100.9119
Sturgeon FallsWind2085RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2085 | 76.7482 | 82.6154 | 88.7744 | 94.9533 | 101.1276
Sturgeon FallsWind2090RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2090 | 76.8426 | 82.7348 | 88.924 | 95.1267 | 101.3265
Sturgeon FallsWind2095RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2095 | 76.84 | 82.7293 | 88.9152 | 95.1142 | 101.3098
Sturgeon FallsWind2100RCP6.0 | Sturgeon Falls | Wind | RCP6.0 | 2100 | 76.8375 | 82.7239 | 88.9064 | 95.1016 | 101.2931
Sturgeon FallsWind2023RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2023 | 76.6095 | 82.4947 | 88.6864 | 94.885 | 101.0824
Sturgeon FallsWind2025RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2025 | 76.6602 | 82.5493 | 88.7421 | 94.9447 | 101.1426
Sturgeon FallsWind2030RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2030 | 76.7109 | 82.6038 | 88.7979 | 95.0043 | 101.2028
Sturgeon FallsWind2035RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2035 | 76.7615 | 82.6584 | 88.8536 | 95.0639 | 101.263
Sturgeon FallsWind2040RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2040 | 76.6602 | 82.5193 | 88.6688 | 94.8411 | 101.0022
Sturgeon FallsWind2045RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2045 | 76.5589 | 82.3801 | 88.484 | 94.6182 | 100.7413
Sturgeon FallsWind2050RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2050 | 76.5867 | 82.4074 | 88.5104 | 94.6434 | 100.7681
Sturgeon FallsWind2055RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2055 | 76.7159 | 82.5738 | 88.7216 | 94.8913 | 101.0557
Sturgeon FallsWind2060RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2060 | 76.8426 | 82.7348 | 88.924 | 95.1267 | 101.3265
Sturgeon FallsWind2065RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2065 | 76.84 | 82.7293 | 88.9152 | 95.1142 | 101.3098
Sturgeon FallsWind2070RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2070 | 77.1288 | 83.0949 | 89.3787 | 95.654 | 101.9318
Sturgeon FallsWind2075RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2075 | 77.4201 | 83.4659 | 89.8509 | 96.2064 | 102.5705
Sturgeon FallsWind2080RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2080 | 77.7113 | 83.8369 | 90.3232 | 96.7588 | 103.2092
Sturgeon FallsWind2085RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2085 | 77.9811 | 84.1274 | 90.6312 | 97.0931 | 103.5603
Sturgeon FallsWind2090RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2090 | 78.2508 | 84.418 | 90.9392 | 97.4274 | 103.9115
Sturgeon FallsWind2095RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2095 | 78.2508 | 84.418 | 90.9392 | 97.4274 | 103.9115
Sturgeon FallsWind2100RCP8.5 | Sturgeon Falls | Wind | RCP8.5 | 2100 | 78.2508 | 84.418 | 90.9392 | 97.4274 | 103.9115
SudburyIce Accretion2023RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2023 | 16.0587 | 19.1913 | 23.166 | 26.2024 | 29.2446
SudburyIce Accretion2025RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2025 | 16.1353 | 19.2826 | 23.2797 | 26.3309 | 29.3878
SudburyIce Accretion2030RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2030 | 16.2118 | 19.3739 | 23.3933 | 26.4593 | 29.531
SudburyIce Accretion2035RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2035 | 16.2884 | 19.4652 | 23.507 | 26.5878 | 29.6743
SudburyIce Accretion2040RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2040 | 16.3649 | 19.5565 | 23.6207 | 26.7162 | 29.8175
SudburyIce Accretion2045RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2045 | 16.4415 | 19.6478 | 23.7343 | 26.8447 | 29.9607
SudburyIce Accretion2050RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2050 | 16.5945 | 19.845 | 23.9888 | 27.1421 | 30.298
SudburyIce Accretion2055RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2055 | 16.6711 | 19.9509 | 24.1296 | 27.3112 | 30.492
SudburyIce Accretion2060RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2060 | 16.7476 | 20.0568 | 24.2704 | 27.4802 | 30.686
SudburyIce Accretion2065RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2065 | 16.8242 | 20.1627 | 24.4112 | 27.6493 | 30.8801
SudburyIce Accretion2070RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2070 | 16.9007 | 20.2686 | 24.552 | 27.8183 | 31.0741
SudburyIce Accretion2075RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2075 | 16.814 | 20.1773 | 24.4493 | 27.7106 | 30.9586
SudburyIce Accretion2080RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2080 | 16.7272 | 20.086 | 24.3467 | 27.6029 | 30.8431
SudburyIce Accretion2085RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2085 | 16.6405 | 19.9947 | 24.244 | 27.4952 | 30.7276
SudburyIce Accretion2090RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2090 | 16.5537 | 19.9034 | 24.1413 | 27.3874 | 30.6121
SudburyIce Accretion2095RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2095 | 16.467 | 19.8121 | 24.0387 | 27.2797 | 30.4966
SudburyIce Accretion2100RCP4.5 | Sudbury | Ice Accretion | RCP4.5 | 2100 | 16.3802 | 19.7208 | 23.936 | 27.172 | 30.3811
SudburyIce Accretion2023RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2023 | 16.0587 | 19.1913 | 23.166 | 26.2024 | 29.2446
SudburyIce Accretion2025RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2025 | 16.1353 | 19.2826 | 23.2797 | 26.3309 | 29.3878
SudburyIce Accretion2030RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2030 | 16.2118 | 19.3739 | 23.3933 | 26.4593 | 29.531
SudburyIce Accretion2035RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2035 | 16.2884 | 19.4652 | 23.507 | 26.5878 | 29.6743
SudburyIce Accretion2040RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2040 | 16.3649 | 19.5565 | 23.6207 | 26.7162 | 29.8175
SudburyIce Accretion2045RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2045 | 16.4415 | 19.6478 | 23.7343 | 26.8447 | 29.9607
SudburyIce Accretion2050RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2050 | 16.5945 | 19.845 | 23.9888 | 27.1421 | 30.298
SudburyIce Accretion2055RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2055 | 16.6711 | 19.9509 | 24.1296 | 27.3112 | 30.492
SudburyIce Accretion2060RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2060 | 16.7476 | 20.0568 | 24.2704 | 27.4802 | 30.686
SudburyIce Accretion2065RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2065 | 16.8242 | 20.1627 | 24.4112 | 27.6493 | 30.8801
SudburyIce Accretion2070RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2070 | 16.9007 | 20.2686 | 24.552 | 27.8183 | 31.0741
SudburyIce Accretion2075RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2075 | 16.7706 | 20.1317 | 24.398 | 27.6567 | 30.9009
SudburyIce Accretion2080RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2080 | 16.6405 | 19.9947 | 24.244 | 27.4952 | 30.7276
SudburyIce Accretion2085RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2085 | 16.5103 | 19.8577 | 24.09 | 27.3336 | 30.5544
SudburyIce Accretion2090RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2090 | 16.3853 | 19.7512 | 24.0093 | 27.2631 | 30.5012
SudburyIce Accretion2095RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2095 | 16.3904 | 19.7817 | 24.0827 | 27.3543 | 30.6214
SudburyIce Accretion2100RCP6.0 | Sudbury | Ice Accretion | RCP6.0 | 2100 | 16.3955 | 19.8121 | 24.156 | 27.4454 | 30.7415
SudburyIce Accretion2023RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2023 | 16.0587 | 19.1913 | 23.166 | 26.2024 | 29.2446
SudburyIce Accretion2025RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2025 | 16.2118 | 19.3739 | 23.3933 | 26.4593 | 29.531
SudburyIce Accretion2030RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2030 | 16.3649 | 19.5565 | 23.6207 | 26.7162 | 29.8175
SudburyIce Accretion2035RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2035 | 16.518 | 19.7391 | 23.848 | 26.9731 | 30.1039
SudburyIce Accretion2040RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2040 | 16.6456 | 19.9156 | 24.0827 | 27.2548 | 30.4273
SudburyIce Accretion2045RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2045 | 16.7731 | 20.0921 | 24.3173 | 27.5366 | 30.7507
SudburyIce Accretion2050RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2050 | 16.7272 | 20.086 | 24.3467 | 27.6029 | 30.8431
SudburyIce Accretion2055RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2055 | 16.5537 | 19.9034 | 24.1413 | 27.3874 | 30.6121
SudburyIce Accretion2060RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2060 | 16.3853 | 19.7512 | 24.0093 | 27.2631 | 30.5012
SudburyIce Accretion2065RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2065 | 16.3904 | 19.7817 | 24.0827 | 27.3543 | 30.6214
SudburyIce Accretion2070RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2070 | 16.0996 | 19.4895 | 23.782 | 27.0394 | 30.298
SudburyIce Accretion2075RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2075 | 15.8036 | 19.1669 | 23.408 | 26.6333 | 29.8544
SudburyIce Accretion2080RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2080 | 15.5076 | 18.8443 | 23.034 | 26.2273 | 29.4109
SudburyIce Accretion2085RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2085 | 15.4464 | 18.8169 | 23.067 | 26.2895 | 29.5079
SudburyIce Accretion2090RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2090 | 15.3852 | 18.7895 | 23.1 | 26.3516 | 29.605
SudburyIce Accretion2095RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2095 | 15.3852 | 18.7895 | 23.1 | 26.3516 | 29.605
SudburyIce Accretion2100RCP8.5 | Sudbury | Ice Accretion | RCP8.5 | 2100 | 15.3852 | 18.7895 | 23.1 | 26.3516 | 29.605
SudburyWind2023RCP4.5 | Sudbury | Wind | RCP4.5 | 2023 | 80.0521 | 86.2274 | 92.7268 | 99.2275 | 105.7295
SudburyWind2025RCP4.5 | Sudbury | Wind | RCP4.5 | 2025 | 80.1593 | 86.35 | 92.8663 | 99.3817 | 105.8991
SudburyWind2030RCP4.5 | Sudbury | Wind | RCP4.5 | 2030 | 80.2666 | 86.4726 | 93.0059 | 99.536 | 106.0686
SudburyWind2035RCP4.5 | Sudbury | Wind | RCP4.5 | 2035 | 80.3738 | 86.5953 | 93.1454 | 99.6902 | 106.2382
SudburyWind2040RCP4.5 | Sudbury | Wind | RCP4.5 | 2040 | 80.4811 | 86.7179 | 93.2849 | 99.8444 | 106.4078
SudburyWind2045RCP4.5 | Sudbury | Wind | RCP4.5 | 2045 | 80.5883 | 86.8405 | 93.4245 | 99.9986 | 106.5773
SudburyWind2050RCP4.5 | Sudbury | Wind | RCP4.5 | 2050 | 80.7384 | 87.0008 | 93.5953 | 100.1785 | 106.7678
SudburyWind2055RCP4.5 | Sudbury | Wind | RCP4.5 | 2055 | 80.7813 | 87.0385 | 93.6266 | 100.204 | 106.7888
SudburyWind2060RCP4.5 | Sudbury | Wind | RCP4.5 | 2060 | 80.8242 | 87.0761 | 93.6578 | 100.2296 | 106.8098
SudburyWind2065RCP4.5 | Sudbury | Wind | RCP4.5 | 2065 | 80.8671 | 87.1138 | 93.6891 | 100.2552 | 106.8308
SudburyWind2070RCP4.5 | Sudbury | Wind | RCP4.5 | 2070 | 80.91 | 87.1514 | 93.7204 | 100.2808 | 106.8517
SudburyWind2075RCP4.5 | Sudbury | Wind | RCP4.5 | 2075 | 80.9948 | 87.2598 | 93.8584 | 100.4465 | 107.0423
SudburyWind2080RCP4.5 | Sudbury | Wind | RCP4.5 | 2080 | 81.0795 | 87.3682 | 93.9964 | 100.6122 | 107.2328
SudburyWind2085RCP4.5 | Sudbury | Wind | RCP4.5 | 2085 | 81.1642 | 87.4765 | 94.1344 | 100.778 | 107.4233
SudburyWind2090RCP4.5 | Sudbury | Wind | RCP4.5 | 2090 | 81.249 | 87.5849 | 94.2724 | 100.9437 | 107.6139
SudburyWind2095RCP4.5 | Sudbury | Wind | RCP4.5 | 2095 | 81.3337 | 87.6933 | 94.4104 | 101.1094 | 107.8044
SudburyWind2100RCP4.5 | Sudbury | Wind | RCP4.5 | 2100 | 81.4184 | 87.8017 | 94.5484 | 101.2751 | 107.9949
SudburyWind2023RCP6.0 | Sudbury | Wind | RCP6.0 | 2023 | 80.0521 | 86.2274 | 92.7268 | 99.2275 | 105.7295
SudburyWind2025RCP6.0 | Sudbury | Wind | RCP6.0 | 2025 | 80.1593 | 86.35 | 92.8663 | 99.3817 | 105.8991
SudburyWind2030RCP6.0 | Sudbury | Wind | RCP6.0 | 2030 | 80.2666 | 86.4726 | 93.0059 | 99.536 | 106.0686
SudburyWind2035RCP6.0 | Sudbury | Wind | RCP6.0 | 2035 | 80.3738 | 86.5953 | 93.1454 | 99.6902 | 106.2382
SudburyWind2040RCP6.0 | Sudbury | Wind | RCP6.0 | 2040 | 80.4811 | 86.7179 | 93.2849 | 99.8444 | 106.4078
SudburyWind2045RCP6.0 | Sudbury | Wind | RCP6.0 | 2045 | 80.5883 | 86.8405 | 93.4245 | 99.9986 | 106.5773
SudburyWind2050RCP6.0 | Sudbury | Wind | RCP6.0 | 2050 | 80.7384 | 87.0008 | 93.5953 | 100.1785 | 106.7678
SudburyWind2055RCP6.0 | Sudbury | Wind | RCP6.0 | 2055 | 80.7813 | 87.0385 | 93.6266 | 100.204 | 106.7888
SudburyWind2060RCP6.0 | Sudbury | Wind | RCP6.0 | 2060 | 80.8242 | 87.0761 | 93.6578 | 100.2296 | 106.8098
SudburyWind2065RCP6.0 | Sudbury | Wind | RCP6.0 | 2065 | 80.8671 | 87.1138 | 93.6891 | 100.2552 | 106.8308
SudburyWind2070RCP6.0 | Sudbury | Wind | RCP6.0 | 2070 | 80.91 | 87.1514 | 93.7204 | 100.2808 | 106.8517
SudburyWind2075RCP6.0 | Sudbury | Wind | RCP6.0 | 2075 | 81.0371 | 87.314 | 93.9274 | 100.5294 | 107.1375
SudburyWind2080RCP6.0 | Sudbury | Wind | RCP6.0 | 2080 | 81.1642 | 87.4765 | 94.1344 | 100.778 | 107.4233
SudburyWind2085RCP6.0 | Sudbury | Wind | RCP6.0 | 2085 | 81.2913 | 87.6391 | 94.3414 | 101.0265 | 107.7091
SudburyWind2090RCP6.0 | Sudbury | Wind | RCP6.0 | 2090 | 81.7309 | 88.201 | 95.0544 | 101.869 | 108.6836
SudburyWind2095RCP6.0 | Sudbury | Wind | RCP6.0 | 2095 | 82.0434 | 88.6002 | 95.5604 | 102.4629 | 109.3724
SudburyWind2100RCP6.0 | Sudbury | Wind | RCP6.0 | 2100 | 82.3558 | 88.9995 | 96.0664 | 103.0568 | 110.0611
SudburyWind2023RCP8.5 | Sudbury | Wind | RCP8.5 | 2023 | 80.0521 | 86.2274 | 92.7268 | 99.2275 | 105.7295
SudburyWind2025RCP8.5 | Sudbury | Wind | RCP8.5 | 2025 | 80.2666 | 86.4726 | 93.0059 | 99.536 | 106.0686
SudburyWind2030RCP8.5 | Sudbury | Wind | RCP8.5 | 2030 | 80.4811 | 86.7179 | 93.2849 | 99.8444 | 106.4078
SudburyWind2035RCP8.5 | Sudbury | Wind | RCP8.5 | 2035 | 80.6955 | 86.9632 | 93.564 | 100.1529 | 106.7469
SudburyWind2040RCP8.5 | Sudbury | Wind | RCP8.5 | 2040 | 80.767 | 87.0259 | 93.6161 | 100.1955 | 106.7818
SudburyWind2045RCP8.5 | Sudbury | Wind | RCP8.5 | 2045 | 80.8385 | 87.0887 | 93.6683 | 100.2382 | 106.8168
SudburyWind2050RCP8.5 | Sudbury | Wind | RCP8.5 | 2050 | 81.0795 | 87.3682 | 93.9964 | 100.6122 | 107.2328
SudburyWind2055RCP8.5 | Sudbury | Wind | RCP8.5 | 2055 | 81.249 | 87.5849 | 94.2724 | 100.9437 | 107.6139
SudburyWind2060RCP8.5 | Sudbury | Wind | RCP8.5 | 2060 | 81.7309 | 88.201 | 95.0544 | 101.869 | 108.6836
SudburyWind2065RCP8.5 | Sudbury | Wind | RCP8.5 | 2065 | 82.0434 | 88.6002 | 95.5604 | 102.4629 | 109.3724
SudburyWind2070RCP8.5 | Sudbury | Wind | RCP8.5 | 2070 | 82.5783 | 89.2762 | 96.4129 | 103.4604 | 110.519
SudburyWind2075RCP8.5 | Sudbury | Wind | RCP8.5 | 2075 | 82.8007 | 89.5528 | 96.7595 | 103.864 | 110.977
SudburyWind2080RCP8.5 | Sudbury | Wind | RCP8.5 | 2080 | 83.0231 | 89.8294 | 97.106 | 104.2676 | 111.435
SudburyWind2085RCP8.5 | Sudbury | Wind | RCP8.5 | 2085 | 83.2535 | 90.1118 | 97.4464 | 104.6614 | 111.8912
SudburyWind2090RCP8.5 | Sudbury | Wind | RCP8.5 | 2090 | 83.4839 | 90.3941 | 97.7868 | 105.0552 | 112.3475
SudburyWind2095RCP8.5 | Sudbury | Wind | RCP8.5 | 2095 | 83.4839 | 90.3941 | 97.7868 | 105.0552 | 112.3475
SudburyWind2100RCP8.5 | Sudbury | Wind | RCP8.5 | 2100 | 83.4839 | 90.3941 | 97.7868 | 105.0552 | 112.3475
SundridgeIce Accretion2023RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2023 | 15.2321 | 18.1504 | 21.868 | 24.7108 | 27.526
SundridgeIce Accretion2025RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2025 | 15.3086 | 18.2509 | 22 | 24.8641 | 27.7061
SundridgeIce Accretion2030RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2030 | 15.3852 | 18.3513 | 22.132 | 25.0174 | 27.8863
SundridgeIce Accretion2035RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2035 | 15.4617 | 18.4517 | 22.264 | 25.1707 | 28.0665
SundridgeIce Accretion2040RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2040 | 15.5382 | 18.5522 | 22.396 | 25.3241 | 28.2467
SundridgeIce Accretion2045RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2045 | 15.6148 | 18.6526 | 22.528 | 25.4774 | 28.4269
SundridgeIce Accretion2050RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2050 | 15.7373 | 18.8261 | 22.7612 | 25.755 | 28.7512
SundridgeIce Accretion2055RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2055 | 15.7832 | 18.8991 | 22.8624 | 25.8793 | 28.8953
SundridgeIce Accretion2060RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2060 | 15.8291 | 18.9721 | 22.9636 | 26.0036 | 29.0395
SundridgeIce Accretion2065RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2065 | 15.875 | 19.0452 | 23.0648 | 26.1279 | 29.1836
SundridgeIce Accretion2070RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2070 | 15.921 | 19.1182 | 23.166 | 26.2522 | 29.3278
SundridgeIce Accretion2075RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2075 | 15.9235 | 19.1395 | 23.21 | 26.3143 | 29.4109
SundridgeIce Accretion2080RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2080 | 15.9261 | 19.1608 | 23.254 | 26.3765 | 29.4941
SundridgeIce Accretion2085RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2085 | 15.9286 | 19.1821 | 23.298 | 26.4386 | 29.5772
SundridgeIce Accretion2090RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2090 | 15.9312 | 19.2034 | 23.342 | 26.5008 | 29.6604
SundridgeIce Accretion2095RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2095 | 15.9337 | 19.2247 | 23.386 | 26.5629 | 29.7436
SundridgeIce Accretion2100RCP4.5 | Sundridge | Ice Accretion | RCP4.5 | 2100 | 15.9363 | 19.246 | 23.43 | 26.6251 | 29.8267
SundridgeIce Accretion2023RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2023 | 15.2321 | 18.1504 | 21.868 | 24.7108 | 27.526
SundridgeIce Accretion2025RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2025 | 15.3086 | 18.2509 | 22 | 24.8641 | 27.7061
SundridgeIce Accretion2030RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2030 | 15.3852 | 18.3513 | 22.132 | 25.0174 | 27.8863
SundridgeIce Accretion2035RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2035 | 15.4617 | 18.4517 | 22.264 | 25.1707 | 28.0665
SundridgeIce Accretion2040RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2040 | 15.5382 | 18.5522 | 22.396 | 25.3241 | 28.2467
SundridgeIce Accretion2045RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2045 | 15.6148 | 18.6526 | 22.528 | 25.4774 | 28.4269
SundridgeIce Accretion2050RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2050 | 15.7373 | 18.8261 | 22.7612 | 25.755 | 28.7512
SundridgeIce Accretion2055RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2055 | 15.7832 | 18.8991 | 22.8624 | 25.8793 | 28.8953
SundridgeIce Accretion2060RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2060 | 15.8291 | 18.9721 | 22.9636 | 26.0036 | 29.0395
SundridgeIce Accretion2065RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2065 | 15.875 | 19.0452 | 23.0648 | 26.1279 | 29.1836
SundridgeIce Accretion2070RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2070 | 15.921 | 19.1182 | 23.166 | 26.2522 | 29.3278
SundridgeIce Accretion2075RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2075 | 15.9248 | 19.1502 | 23.232 | 26.3454 | 29.4525
SundridgeIce Accretion2080RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2080 | 15.9286 | 19.1821 | 23.298 | 26.4386 | 29.5772
SundridgeIce Accretion2085RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2085 | 15.9324 | 19.2141 | 23.364 | 26.5318 | 29.702
SundridgeIce Accretion2090RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2090 | 15.9618 | 19.2947 | 23.5107 | 26.7328 | 29.9468
SundridgeIce Accretion2095RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2095 | 15.9873 | 19.3434 | 23.5913 | 26.8405 | 30.067
SundridgeIce Accretion2100RCP6.0 | Sundridge | Ice Accretion | RCP6.0 | 2100 | 16.0128 | 19.3921 | 23.672 | 26.9482 | 30.1871
SundridgeIce Accretion2023RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2023 | 15.2321 | 18.1504 | 21.868 | 24.7108 | 27.526
SundridgeIce Accretion2025RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2025 | 15.3852 | 18.3513 | 22.132 | 25.0174 | 27.8863
SundridgeIce Accretion2030RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2030 | 15.5382 | 18.5522 | 22.396 | 25.3241 | 28.2467
SundridgeIce Accretion2035RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2035 | 15.6913 | 18.753 | 22.66 | 25.6307 | 28.607
SundridgeIce Accretion2040RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2040 | 15.7679 | 18.8748 | 22.8287 | 25.8378 | 28.8473
SundridgeIce Accretion2045RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2045 | 15.8444 | 18.9965 | 22.9973 | 26.045 | 29.0875
SundridgeIce Accretion2050RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2050 | 15.9261 | 19.1608 | 23.254 | 26.3765 | 29.4941
SundridgeIce Accretion2055RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2055 | 15.9312 | 19.2034 | 23.342 | 26.5008 | 29.6604
SundridgeIce Accretion2060RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2060 | 15.9618 | 19.2947 | 23.5107 | 26.7328 | 29.9468
SundridgeIce Accretion2065RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2065 | 15.9873 | 19.3434 | 23.5913 | 26.8405 | 30.067
SundridgeIce Accretion2070RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2070 | 15.8801 | 19.2521 | 23.5253 | 26.7908 | 30.03
SundridgeIce Accretion2075RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2075 | 15.7475 | 19.1121 | 23.3787 | 26.6333 | 29.8729
SundridgeIce Accretion2080RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2080 | 15.6148 | 18.9721 | 23.232 | 26.4759 | 29.7158
SundridgeIce Accretion2085RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2085 | 15.2091 | 18.5248 | 22.715 | 25.9166 | 29.106
SundridgeIce Accretion2090RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2090 | 14.8034 | 18.0774 | 22.198 | 25.3572 | 28.4962
SundridgeIce Accretion2095RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2095 | 14.8034 | 18.0774 | 22.198 | 25.3572 | 28.4962
SundridgeIce Accretion2100RCP8.5 | Sundridge | Ice Accretion | RCP8.5 | 2100 | 14.8034 | 18.0774 | 22.198 | 25.3572 | 28.4962
SundridgeWind2023RCP4.5 | Sundridge | Wind | RCP4.5 | 2023 | 69.3273 | 74.6976 | 80.36 | 86.0109 | 91.6651
SundridgeWind2025RCP4.5 | Sundridge | Wind | RCP4.5 | 2025 | 69.371 | 74.7559 | 80.436 | 86.1008 | 91.77
SundridgeWind2030RCP4.5 | Sundridge | Wind | RCP4.5 | 2030 | 69.4148 | 74.8142 | 80.512 | 86.1906 | 91.8749
SundridgeWind2035RCP4.5 | Sundridge | Wind | RCP4.5 | 2035 | 69.4585 | 74.8724 | 80.588 | 86.2805 | 91.9798
SundridgeWind2040RCP4.5 | Sundridge | Wind | RCP4.5 | 2040 | 69.5023 | 74.9307 | 80.664 | 86.3704 | 92.0846
SundridgeWind2045RCP4.5 | Sundridge | Wind | RCP4.5 | 2045 | 69.546 | 74.989 | 80.74 | 86.4603 | 92.1895
SundridgeWind2050RCP4.5 | Sundridge | Wind | RCP4.5 | 2050 | 69.5842 | 75.0309 | 80.784 | 86.5091 | 92.2397
SundridgeWind2055RCP4.5 | Sundridge | Wind | RCP4.5 | 2055 | 69.5787 | 75.0145 | 80.752 | 86.468 | 92.185
SundridgeWind2060RCP4.5 | Sundridge | Wind | RCP4.5 | 2060 | 69.5732 | 74.9982 | 80.72 | 86.4269 | 92.1302
SundridgeWind2065RCP4.5 | Sundridge | Wind | RCP4.5 | 2065 | 69.5677 | 74.9818 | 80.688 | 86.3858 | 92.0755
SundridgeWind2070RCP4.5 | Sundridge | Wind | RCP4.5 | 2070 | 69.5621 | 74.9654 | 80.656 | 86.3447 | 92.0208
SundridgeWind2075RCP4.5 | Sundridge | Wind | RCP4.5 | 2075 | 69.6347 | 75.0485 | 80.7533 | 86.4531 | 92.1424
SundridgeWind2080RCP4.5 | Sundridge | Wind | RCP4.5 | 2080 | 69.7072 | 75.1316 | 80.8507 | 86.5616 | 92.264
SundridgeWind2085RCP4.5 | Sundridge | Wind | RCP4.5 | 2085 | 69.7797 | 75.2147 | 80.948 | 86.67 | 92.3856
SundridgeWind2090RCP4.5 | Sundridge | Wind | RCP4.5 | 2090 | 69.8523 | 75.2978 | 81.0453 | 86.7784 | 92.5072
SundridgeWind2095RCP4.5 | Sundridge | Wind | RCP4.5 | 2095 | 69.9248 | 75.3808 | 81.1427 | 86.8869 | 92.6288
SundridgeWind2100RCP4.5 | Sundridge | Wind | RCP4.5 | 2100 | 69.9973 | 75.4639 | 81.24 | 86.9953 | 92.7504
SundridgeWind2023RCP6.0 | Sundridge | Wind | RCP6.0 | 2023 | 69.3273 | 74.6976 | 80.36 | 86.0109 | 91.6651
SundridgeWind2025RCP6.0 | Sundridge | Wind | RCP6.0 | 2025 | 69.371 | 74.7559 | 80.436 | 86.1008 | 91.77
SundridgeWind2030RCP6.0 | Sundridge | Wind | RCP6.0 | 2030 | 69.4148 | 74.8142 | 80.512 | 86.1906 | 91.8749
SundridgeWind2035RCP6.0 | Sundridge | Wind | RCP6.0 | 2035 | 69.4585 | 74.8724 | 80.588 | 86.2805 | 91.9798
SundridgeWind2040RCP6.0 | Sundridge | Wind | RCP6.0 | 2040 | 69.5023 | 74.9307 | 80.664 | 86.3704 | 92.0846
SundridgeWind2045RCP6.0 | Sundridge | Wind | RCP6.0 | 2045 | 69.546 | 74.989 | 80.74 | 86.4603 | 92.1895
SundridgeWind2050RCP6.0 | Sundridge | Wind | RCP6.0 | 2050 | 69.5842 | 75.0309 | 80.784 | 86.5091 | 92.2397
SundridgeWind2055RCP6.0 | Sundridge | Wind | RCP6.0 | 2055 | 69.5787 | 75.0145 | 80.752 | 86.468 | 92.185
SundridgeWind2060RCP6.0 | Sundridge | Wind | RCP6.0 | 2060 | 69.5732 | 74.9982 | 80.72 | 86.4269 | 92.1302
SundridgeWind2065RCP6.0 | Sundridge | Wind | RCP6.0 | 2065 | 69.5677 | 74.9818 | 80.688 | 86.3858 | 92.0755
SundridgeWind2070RCP6.0 | Sundridge | Wind | RCP6.0 | 2070 | 69.5621 | 74.9654 | 80.656 | 86.3447 | 92.0208
SundridgeWind2075RCP6.0 | Sundridge | Wind | RCP6.0 | 2075 | 69.6709 | 75.0901 | 80.802 | 86.5074 | 92.2032
SundridgeWind2080RCP6.0 | Sundridge | Wind | RCP6.0 | 2080 | 69.7797 | 75.2147 | 80.948 | 86.67 | 92.3856
SundridgeWind2085RCP6.0 | Sundridge | Wind | RCP6.0 | 2085 | 69.8885 | 75.3393 | 81.094 | 86.8326 | 92.568
SundridgeWind2090RCP6.0 | Sundridge | Wind | RCP6.0 | 2090 | 69.8638 | 75.2978 | 81.0293 | 86.7499 | 92.4677
SundridgeWind2095RCP6.0 | Sundridge | Wind | RCP6.0 | 2095 | 69.7302 | 75.1316 | 80.8187 | 86.5045 | 92.185
SundridgeWind2100RCP6.0 | Sundridge | Wind | RCP6.0 | 2100 | 69.5967 | 74.9654 | 80.608 | 86.2591 | 91.9022
SundridgeWind2023RCP8.5 | Sundridge | Wind | RCP8.5 | 2023 | 69.3273 | 74.6976 | 80.36 | 86.0109 | 91.6651
SundridgeWind2025RCP8.5 | Sundridge | Wind | RCP8.5 | 2025 | 69.4148 | 74.8142 | 80.512 | 86.1906 | 91.8749
SundridgeWind2030RCP8.5 | Sundridge | Wind | RCP8.5 | 2030 | 69.5023 | 74.9307 | 80.664 | 86.3704 | 92.0846
SundridgeWind2035RCP8.5 | Sundridge | Wind | RCP8.5 | 2035 | 69.5898 | 75.0473 | 80.816 | 86.5502 | 92.2944
SundridgeWind2040RCP8.5 | Sundridge | Wind | RCP8.5 | 2040 | 69.5806 | 75.02 | 80.7627 | 86.4817 | 92.2032
SundridgeWind2045RCP8.5 | Sundridge | Wind | RCP8.5 | 2045 | 69.5714 | 74.9927 | 80.7093 | 86.4132 | 92.112
SundridgeWind2050RCP8.5 | Sundridge | Wind | RCP8.5 | 2050 | 69.7072 | 75.1316 | 80.8507 | 86.5616 | 92.264
SundridgeWind2055RCP8.5 | Sundridge | Wind | RCP8.5 | 2055 | 69.8523 | 75.2978 | 81.0453 | 86.7784 | 92.5072
SundridgeWind2060RCP8.5 | Sundridge | Wind | RCP8.5 | 2060 | 69.8638 | 75.2978 | 81.0293 | 86.7499 | 92.4677
SundridgeWind2065RCP8.5 | Sundridge | Wind | RCP8.5 | 2065 | 69.7302 | 75.1316 | 80.8187 | 86.5045 | 92.185
SundridgeWind2070RCP8.5 | Sundridge | Wind | RCP8.5 | 2070 | 69.7302 | 75.1266 | 80.808 | 86.4874 | 92.1637
SundridgeWind2075RCP8.5 | Sundridge | Wind | RCP8.5 | 2075 | 69.8638 | 75.2878 | 81.008 | 86.7157 | 92.4251
SundridgeWind2080RCP8.5 | Sundridge | Wind | RCP8.5 | 2080 | 69.9973 | 75.449 | 81.208 | 86.9439 | 92.6866
SundridgeWind2085RCP8.5 | Sundridge | Wind | RCP8.5 | 2085 | 70.0284 | 75.4676 | 81.208 | 86.9311 | 92.6592
SundridgeWind2090RCP8.5 | Sundridge | Wind | RCP8.5 | 2090 | 70.0595 | 75.4862 | 81.208 | 86.9182 | 92.6318
SundridgeWind2095RCP8.5 | Sundridge | Wind | RCP8.5 | 2095 | 70.0595 | 75.4862 | 81.208 | 86.9182 | 92.6318
SundridgeWind2100RCP8.5 | Sundridge | Wind | RCP8.5 | 2100 | 70.0595 | 75.4862 | 81.208 | 86.9182 | 92.6318
TavistockIce Accretion2023RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2023 | 18.3933 | 22.0514 | 26.676 | 30.2049 | 33.7478
TavistockIce Accretion2025RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2025 | 18.3557 | 22.0178 | 26.6445 | 30.1795 | 33.7195
TavistockIce Accretion2030RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2030 | 18.3181 | 21.9842 | 26.613 | 30.154 | 33.6911
TavistockIce Accretion2035RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2035 | 18.2806 | 21.9506 | 26.5815 | 30.1286 | 33.6628
TavistockIce Accretion2040RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2040 | 18.243 | 21.917 | 26.55 | 30.1032 | 33.6344
TavistockIce Accretion2045RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2045 | 18.2054 | 21.8834 | 26.5185 | 30.0778 | 33.6061
TavistockIce Accretion2050RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2050 | 18.0514 | 21.7377 | 26.3844 | 29.9486 | 33.4825
TavistockIce Accretion2055RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2055 | 17.9349 | 21.6257 | 26.2818 | 29.8449 | 33.3872
TavistockIce Accretion2060RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2060 | 17.8184 | 21.5136 | 26.1792 | 29.7411 | 33.292
TavistockIce Accretion2065RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2065 | 17.7019 | 21.4016 | 26.0766 | 29.6374 | 33.1967
TavistockIce Accretion2070RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2070 | 17.5854 | 21.2895 | 25.974 | 29.5337 | 33.1015
TavistockIce Accretion2075RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2075 | 17.5353 | 21.2522 | 25.956 | 29.5286 | 33.1071
TavistockIce Accretion2080RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2080 | 17.4852 | 21.2148 | 25.938 | 29.5235 | 33.1128
TavistockIce Accretion2085RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2085 | 17.4351 | 21.1775 | 25.92 | 29.5184 | 33.1185
TavistockIce Accretion2090RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2090 | 17.385 | 21.1401 | 25.902 | 29.5133 | 33.1241
TavistockIce Accretion2095RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2095 | 17.3349 | 21.1028 | 25.884 | 29.5083 | 33.1298
TavistockIce Accretion2100RCP4.5 | Tavistock | Ice Accretion | RCP4.5 | 2100 | 17.2848 | 21.0654 | 25.866 | 29.5032 | 33.1355
TavistockIce Accretion2023RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2023 | 18.3933 | 22.0514 | 26.676 | 30.2049 | 33.7478
TavistockIce Accretion2025RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2025 | 18.3557 | 22.0178 | 26.6445 | 30.1795 | 33.7195
TavistockIce Accretion2030RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2030 | 18.3181 | 21.9842 | 26.613 | 30.154 | 33.6911
TavistockIce Accretion2035RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2035 | 18.2806 | 21.9506 | 26.5815 | 30.1286 | 33.6628
TavistockIce Accretion2040RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2040 | 18.243 | 21.917 | 26.55 | 30.1032 | 33.6344
TavistockIce Accretion2045RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2045 | 18.2054 | 21.8834 | 26.5185 | 30.0778 | 33.6061
TavistockIce Accretion2050RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2050 | 18.0514 | 21.7377 | 26.3844 | 29.9486 | 33.4825
TavistockIce Accretion2055RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2055 | 17.9349 | 21.6257 | 26.2818 | 29.8449 | 33.3872
TavistockIce Accretion2060RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2060 | 17.8184 | 21.5136 | 26.1792 | 29.7411 | 33.292
TavistockIce Accretion2065RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2065 | 17.7019 | 21.4016 | 26.0766 | 29.6374 | 33.1967
TavistockIce Accretion2070RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2070 | 17.5854 | 21.2895 | 25.974 | 29.5337 | 33.1015
TavistockIce Accretion2075RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2075 | 17.5103 | 21.2335 | 25.947 | 29.5261 | 33.11
TavistockIce Accretion2080RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2080 | 17.4351 | 21.1775 | 25.92 | 29.5184 | 33.1185
TavistockIce Accretion2085RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2085 | 17.36 | 21.1214 | 25.893 | 29.5108 | 33.127
TavistockIce Accretion2090RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2090 | 16.8965 | 20.6471 | 25.389 | 28.9947 | 32.5798
TavistockIce Accretion2095RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2095 | 16.5083 | 20.2288 | 24.912 | 28.4862 | 32.0242
TavistockIce Accretion2100RCP6.0 | Tavistock | Ice Accretion | RCP6.0 | 2100 | 16.12 | 19.8104 | 24.435 | 27.9777 | 31.4685
TavistockIce Accretion2023RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2023 | 18.3933 | 22.0514 | 26.676 | 30.2049 | 33.7478
TavistockIce Accretion2025RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2025 | 18.3181 | 21.9842 | 26.613 | 30.154 | 33.6911
TavistockIce Accretion2030RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2030 | 18.243 | 21.917 | 26.55 | 30.1032 | 33.6344
TavistockIce Accretion2035RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2035 | 18.1678 | 21.8498 | 26.487 | 30.0523 | 33.5777
TavistockIce Accretion2040RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2040 | 17.9737 | 21.663 | 26.316 | 29.8795 | 33.419
TavistockIce Accretion2045RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2045 | 17.7796 | 21.4763 | 26.145 | 29.7066 | 33.2602
TavistockIce Accretion2050RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2050 | 17.4852 | 21.2148 | 25.938 | 29.5235 | 33.1128
TavistockIce Accretion2055RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2055 | 17.385 | 21.1401 | 25.902 | 29.5133 | 33.1241
TavistockIce Accretion2060RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2060 | 16.8965 | 20.6471 | 25.389 | 28.9947 | 32.5798
TavistockIce Accretion2065RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2065 | 16.5083 | 20.2288 | 24.912 | 28.4862 | 32.0242
TavistockIce Accretion2070RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2070 | 15.7818 | 19.4444 | 24.039 | 27.5505 | 31.0149
TavistockIce Accretion2075RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2075 | 15.4436 | 19.0784 | 23.643 | 27.1234 | 30.5613
TavistockIce Accretion2080RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2080 | 15.1054 | 18.7124 | 23.247 | 26.6962 | 30.1077
TavistockIce Accretion2085RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2085 | 14.2694 | 17.7487 | 22.113 | 25.4148 | 28.7129
TavistockIce Accretion2090RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2090 | 13.4333 | 16.7851 | 20.979 | 24.1334 | 27.3181
TavistockIce Accretion2095RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2095 | 13.4333 | 16.7851 | 20.979 | 24.1334 | 27.3181
TavistockIce Accretion2100RCP8.5 | Tavistock | Ice Accretion | RCP8.5 | 2100 | 13.4333 | 16.7851 | 20.979 | 24.1334 | 27.3181
TavistockWind2023RCP4.5 | Tavistock | Wind | RCP4.5 | 2023 | 85.3829 | 92.1152 | 99.2446 | 106.3385 | 113.4405
TavistockWind2025RCP4.5 | Tavistock | Wind | RCP4.5 | 2025 | 85.4618 | 92.22 | 99.3802 | 106.5011 | 113.6304
TavistockWind2030RCP4.5 | Tavistock | Wind | RCP4.5 | 2030 | 85.5408 | 92.3248 | 99.5157 | 106.6636 | 113.8203
TavistockWind2035RCP4.5 | Tavistock | Wind | RCP4.5 | 2035 | 85.6198 | 92.4296 | 99.6513 | 106.8261 | 114.0103
TavistockWind2040RCP4.5 | Tavistock | Wind | RCP4.5 | 2040 | 85.6988 | 92.5344 | 99.7869 | 106.9887 | 114.2002
TavistockWind2045RCP4.5 | Tavistock | Wind | RCP4.5 | 2045 | 85.7778 | 92.6393 | 99.9224 | 107.1512 | 114.3901
TavistockWind2050RCP4.5 | Tavistock | Wind | RCP4.5 | 2050 | 85.9244 | 92.8261 | 100.1619 | 107.4333 | 114.7163
TavistockWind2055RCP4.5 | Tavistock | Wind | RCP4.5 | 2055 | 85.9921 | 92.9081 | 100.2658 | 107.5528 | 114.8526
TavistockWind2060RCP4.5 | Tavistock | Wind | RCP4.5 | 2060 | 86.0598 | 92.9901 | 100.3696 | 107.6723 | 114.9889
TavistockWind2065RCP4.5 | Tavistock | Wind | RCP4.5 | 2065 | 86.1275 | 93.0722 | 100.4735 | 107.7919 | 115.1252
TavistockWind2070RCP4.5 | Tavistock | Wind | RCP4.5 | 2070 | 86.1952 | 93.1542 | 100.5774 | 107.9114 | 115.2615
TavistockWind2075RCP4.5 | Tavistock | Wind | RCP4.5 | 2075 | 86.2799 | 93.2712 | 100.7358 | 108.1054 | 115.4924
TavistockWind2080RCP4.5 | Tavistock | Wind | RCP4.5 | 2080 | 86.3645 | 93.3881 | 100.8943 | 108.2994 | 115.7233
TavistockWind2085RCP4.5 | Tavistock | Wind | RCP4.5 | 2085 | 86.4491 | 93.5051 | 101.0527 | 108.4934 | 115.9542
TavistockWind2090RCP4.5 | Tavistock | Wind | RCP4.5 | 2090 | 86.5337 | 93.622 | 101.2111 | 108.6874 | 116.1851
TavistockWind2095RCP4.5 | Tavistock | Wind | RCP4.5 | 2095 | 86.6183 | 93.739 | 101.3696 | 108.8814 | 116.416
TavistockWind2100RCP4.5 | Tavistock | Wind | RCP4.5 | 2100 | 86.703 | 93.856 | 101.528 | 109.0754 | 116.6469
TavistockWind2023RCP6.0 | Tavistock | Wind | RCP6.0 | 2023 | 85.3829 | 92.1152 | 99.2446 | 106.3385 | 113.4405
TavistockWind2025RCP6.0 | Tavistock | Wind | RCP6.0 | 2025 | 85.4618 | 92.22 | 99.3802 | 106.5011 | 113.6304
TavistockWind2030RCP6.0 | Tavistock | Wind | RCP6.0 | 2030 | 85.5408 | 92.3248 | 99.5157 | 106.6636 | 113.8203
TavistockWind2035RCP6.0 | Tavistock | Wind | RCP6.0 | 2035 | 85.6198 | 92.4296 | 99.6513 | 106.8261 | 114.0103
TavistockWind2040RCP6.0 | Tavistock | Wind | RCP6.0 | 2040 | 85.6988 | 92.5344 | 99.7869 | 106.9887 | 114.2002
TavistockWind2045RCP6.0 | Tavistock | Wind | RCP6.0 | 2045 | 85.7778 | 92.6393 | 99.9224 | 107.1512 | 114.3901
TavistockWind2050RCP6.0 | Tavistock | Wind | RCP6.0 | 2050 | 85.9244 | 92.8261 | 100.1619 | 107.4333 | 114.7163
TavistockWind2055RCP6.0 | Tavistock | Wind | RCP6.0 | 2055 | 85.9921 | 92.9081 | 100.2658 | 107.5528 | 114.8526
TavistockWind2060RCP6.0 | Tavistock | Wind | RCP6.0 | 2060 | 86.0598 | 92.9901 | 100.3696 | 107.6723 | 114.9889
TavistockWind2065RCP6.0 | Tavistock | Wind | RCP6.0 | 2065 | 86.1275 | 93.0722 | 100.4735 | 107.7919 | 115.1252
TavistockWind2070RCP6.0 | Tavistock | Wind | RCP6.0 | 2070 | 86.1952 | 93.1542 | 100.5774 | 107.9114 | 115.2615
TavistockWind2075RCP6.0 | Tavistock | Wind | RCP6.0 | 2075 | 86.3222 | 93.3296 | 100.815 | 108.2024 | 115.6079
TavistockWind2080RCP6.0 | Tavistock | Wind | RCP6.0 | 2080 | 86.4491 | 93.5051 | 101.0527 | 108.4934 | 115.9542
TavistockWind2085RCP6.0 | Tavistock | Wind | RCP6.0 | 2085 | 86.576 | 93.6805 | 101.2904 | 108.7844 | 116.3005
TavistockWind2090RCP6.0 | Tavistock | Wind | RCP6.0 | 2090 | 87.0499 | 94.3026 | 102.0964 | 109.7465 | 117.4252
TavistockWind2095RCP6.0 | Tavistock | Wind | RCP6.0 | 2095 | 87.3969 | 94.7491 | 102.6648 | 110.4176 | 118.2035
TavistockWind2100RCP6.0 | Tavistock | Wind | RCP6.0 | 2100 | 87.7438 | 95.1957 | 103.2332 | 111.0887 | 118.9818
TavistockWind2023RCP8.5 | Tavistock | Wind | RCP8.5 | 2023 | 85.3829 | 92.1152 | 99.2446 | 106.3385 | 113.4405
TavistockWind2025RCP8.5 | Tavistock | Wind | RCP8.5 | 2025 | 85.5408 | 92.3248 | 99.5157 | 106.6636 | 113.8203
TavistockWind2030RCP8.5 | Tavistock | Wind | RCP8.5 | 2030 | 85.6988 | 92.5344 | 99.7869 | 106.9887 | 114.2002
TavistockWind2035RCP8.5 | Tavistock | Wind | RCP8.5 | 2035 | 85.8567 | 92.7441 | 100.058 | 107.3137 | 114.58
TavistockWind2040RCP8.5 | Tavistock | Wind | RCP8.5 | 2040 | 85.9696 | 92.8808 | 100.2311 | 107.513 | 114.8072
TavistockWind2045RCP8.5 | Tavistock | Wind | RCP8.5 | 2045 | 86.0824 | 93.0175 | 100.4043 | 107.7122 | 115.0344
TavistockWind2050RCP8.5 | Tavistock | Wind | RCP8.5 | 2050 | 86.3645 | 93.3881 | 100.8943 | 108.2994 | 115.7233
TavistockWind2055RCP8.5 | Tavistock | Wind | RCP8.5 | 2055 | 86.5337 | 93.622 | 101.2111 | 108.6874 | 116.1851
TavistockWind2060RCP8.5 | Tavistock | Wind | RCP8.5 | 2060 | 87.0499 | 94.3026 | 102.0964 | 109.7465 | 117.4252
TavistockWind2065RCP8.5 | Tavistock | Wind | RCP8.5 | 2065 | 87.3969 | 94.7491 | 102.6648 | 110.4176 | 118.2035
TavistockWind2070RCP8.5 | Tavistock | Wind | RCP8.5 | 2070 | 87.9638 | 95.4904 | 103.6219 | 111.5571 | 119.533
TavistockWind2075RCP8.5 | Tavistock | Wind | RCP8.5 | 2075 | 88.1838 | 95.7851 | 104.0107 | 112.0254 | 120.0841
TavistockWind2080RCP8.5 | Tavistock | Wind | RCP8.5 | 2080 | 88.4038 | 96.0798 | 104.3994 | 112.4938 | 120.6353
TavistockWind2085RCP8.5 | Tavistock | Wind | RCP8.5 | 2085 | 88.8354 | 96.6449 | 105.1393 | 113.3799 | 121.6687
TavistockWind2090RCP8.5 | Tavistock | Wind | RCP8.5 | 2090 | 89.267 | 97.2099 | 105.8792 | 114.2659 | 122.7021
TavistockWind2095RCP8.5 | Tavistock | Wind | RCP8.5 | 2095 | 89.267 | 97.2099 | 105.8792 | 114.2659 | 122.7021
TavistockWind2100RCP8.5 | Tavistock | Wind | RCP8.5 | 2100 | 89.267 | 97.2099 | 105.8792 | 114.2659 | 122.7021
TemagamiIce Accretion2023RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2023 | 15.3726 | 18.3886 | 22.218 | 25.1538 | 28.0741
TemagamiIce Accretion2025RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2025 | 15.3556 | 18.3683 | 22.1935 | 25.1222 | 28.0388
TemagamiIce Accretion2030RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2030 | 15.3385 | 18.348 | 22.169 | 25.0905 | 28.0035
TemagamiIce Accretion2035RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2035 | 15.3215 | 18.3276 | 22.1445 | 25.0589 | 27.9682
TemagamiIce Accretion2040RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2040 | 15.3044 | 18.3073 | 22.12 | 25.0272 | 27.9329
TemagamiIce Accretion2045RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2045 | 15.2874 | 18.287 | 22.0955 | 24.9956 | 27.8977
TemagamiIce Accretion2050RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2050 | 15.2937 | 18.2945 | 22.1046 | 25.0067 | 27.91
TemagamiIce Accretion2055RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2055 | 15.3171 | 18.3224 | 22.1382 | 25.0494 | 27.9576
TemagamiIce Accretion2060RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2060 | 15.3405 | 18.3503 | 22.1718 | 25.0921 | 28.0053
TemagamiIce Accretion2065RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2065 | 15.3639 | 18.3782 | 22.2054 | 25.1348 | 28.0529
TemagamiIce Accretion2070RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2070 | 15.3872 | 18.4061 | 22.239 | 25.1775 | 28.1005
TemagamiIce Accretion2075RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2075 | 15.3848 | 18.4032 | 22.2355 | 25.1736 | 28.0961
TemagamiIce Accretion2080RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2080 | 15.3824 | 18.4003 | 22.232 | 25.1696 | 28.0917
TemagamiIce Accretion2085RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2085 | 15.3799 | 18.3974 | 22.2285 | 25.1657 | 28.0873
TemagamiIce Accretion2090RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2090 | 15.3775 | 18.3945 | 22.225 | 25.1617 | 28.0829
TemagamiIce Accretion2095RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2095 | 15.3751 | 18.3916 | 22.2215 | 25.1578 | 28.0785
TemagamiIce Accretion2100RCP4.5 | Temagami | Ice Accretion | RCP4.5 | 2100 | 15.3726 | 18.3886 | 22.218 | 25.1538 | 28.0741
TemagamiIce Accretion2023RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2023 | 15.3726 | 18.3886 | 22.218 | 25.1538 | 28.0741
TemagamiIce Accretion2025RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2025 | 15.3556 | 18.3683 | 22.1935 | 25.1222 | 28.0388
TemagamiIce Accretion2030RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2030 | 15.3385 | 18.348 | 22.169 | 25.0905 | 28.0035
TemagamiIce Accretion2035RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2035 | 15.3215 | 18.3276 | 22.1445 | 25.0589 | 27.9682
TemagamiIce Accretion2040RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2040 | 15.3044 | 18.3073 | 22.12 | 25.0272 | 27.9329
TemagamiIce Accretion2045RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2045 | 15.2874 | 18.287 | 22.0955 | 24.9956 | 27.8977
TemagamiIce Accretion2050RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2050 | 15.2937 | 18.2945 | 22.1046 | 25.0067 | 27.91
TemagamiIce Accretion2055RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2055 | 15.3171 | 18.3224 | 22.1382 | 25.0494 | 27.9576
TemagamiIce Accretion2060RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2060 | 15.3405 | 18.3503 | 22.1718 | 25.0921 | 28.0053
TemagamiIce Accretion2065RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2065 | 15.3639 | 18.3782 | 22.2054 | 25.1348 | 28.0529
TemagamiIce Accretion2070RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2070 | 15.3872 | 18.4061 | 22.239 | 25.1775 | 28.1005
TemagamiIce Accretion2075RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2075 | 15.3836 | 18.4017 | 22.2337 | 25.1716 | 28.0939
TemagamiIce Accretion2080RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2080 | 15.3799 | 18.3974 | 22.2285 | 25.1657 | 28.0873
TemagamiIce Accretion2085RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2085 | 15.3763 | 18.393 | 22.2233 | 25.1597 | 28.0807
TemagamiIce Accretion2090RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2090 | 15.436 | 18.4874 | 22.358 | 25.3199 | 28.2769
TemagamiIce Accretion2095RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2095 | 15.4993 | 18.5862 | 22.498 | 25.486 | 28.4798
TemagamiIce Accretion2100RCP6.0 | Temagami | Ice Accretion | RCP6.0 | 2100 | 15.5626 | 18.685 | 22.638 | 25.6521 | 28.6826
TemagamiIce Accretion2023RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2023 | 15.3726 | 18.3886 | 22.218 | 25.1538 | 28.0741
TemagamiIce Accretion2025RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2025 | 15.3385 | 18.348 | 22.169 | 25.0905 | 28.0035
TemagamiIce Accretion2030RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2030 | 15.3044 | 18.3073 | 22.12 | 25.0272 | 27.9329
TemagamiIce Accretion2035RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2035 | 15.2703 | 18.2666 | 22.071 | 24.964 | 27.8624
TemagamiIce Accretion2040RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2040 | 15.3093 | 18.3131 | 22.127 | 25.0351 | 27.9418
TemagamiIce Accretion2045RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2045 | 15.3483 | 18.3596 | 22.183 | 25.1063 | 28.0211
TemagamiIce Accretion2050RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2050 | 15.3824 | 18.4003 | 22.232 | 25.1696 | 28.0917
TemagamiIce Accretion2055RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2055 | 15.3775 | 18.3945 | 22.225 | 25.1617 | 28.0829
TemagamiIce Accretion2060RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2060 | 15.436 | 18.4874 | 22.358 | 25.3199 | 28.2769
TemagamiIce Accretion2065RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2065 | 15.4993 | 18.5862 | 22.498 | 25.486 | 28.4798
TemagamiIce Accretion2070RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2070 | 15.3726 | 18.47 | 22.4 | 25.3911 | 28.3916
TemagamiIce Accretion2075RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2075 | 15.1827 | 18.255 | 22.162 | 25.1301 | 28.1005
TemagamiIce Accretion2080RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2080 | 14.9927 | 18.04 | 21.924 | 24.869 | 27.8095
TemagamiIce Accretion2085RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2085 | 14.832 | 17.8919 | 21.7665 | 24.7267 | 27.6639
TemagamiIce Accretion2090RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2090 | 14.6712 | 17.7437 | 21.609 | 24.5843 | 27.5184
TemagamiIce Accretion2095RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2095 | 14.6712 | 17.7437 | 21.609 | 24.5843 | 27.5184
TemagamiIce Accretion2100RCP8.5 | Temagami | Ice Accretion | RCP8.5 | 2100 | 14.6712 | 17.7437 | 21.609 | 24.5843 | 27.5184
TemagamiWind2023RCP4.5 | Temagami | Wind | RCP4.5 | 2023 | 75.0929 | 80.7725 | 86.7129 | 92.6804 | 98.6543
TemagamiWind2025RCP4.5 | Temagami | Wind | RCP4.5 | 2025 | 75.0228 | 80.6727 | 86.5781 | 92.5175 | 98.4609
TemagamiWind2030RCP4.5 | Temagami | Wind | RCP4.5 | 2030 | 74.9527 | 80.5729 | 86.4432 | 92.3546 | 98.2675
TemagamiWind2035RCP4.5 | Temagami | Wind | RCP4.5 | 2035 | 74.8826 | 80.4731 | 86.3084 | 92.1917 | 98.0741
TemagamiWind2040RCP4.5 | Temagami | Wind | RCP4.5 | 2040 | 74.8125 | 80.3733 | 86.1735 | 92.0288 | 97.8807
TemagamiWind2045RCP4.5 | Temagami | Wind | RCP4.5 | 2045 | 74.7423 | 80.2735 | 86.0387 | 91.8659 | 97.6873
TemagamiWind2050RCP4.5 | Temagami | Wind | RCP4.5 | 2050 | 74.6677 | 80.1575 | 85.8725 | 91.6601 | 97.4384
TemagamiWind2055RCP4.5 | Temagami | Wind | RCP4.5 | 2055 | 74.6632 | 80.1414 | 85.8412 | 91.6173 | 97.3829
TemagamiWind2060RCP4.5 | Temagami | Wind | RCP4.5 | 2060 | 74.6587 | 80.1252 | 85.8098 | 91.5745 | 97.3273
TemagamiWind2065RCP4.5 | Temagami | Wind | RCP4.5 | 2065 | 74.6542 | 80.109 | 85.7785 | 91.5317 | 97.2718
TemagamiWind2070RCP4.5 | Temagami | Wind | RCP4.5 | 2070 | 74.6497 | 80.0928 | 85.7472 | 91.4889 | 97.2162
TemagamiWind2075RCP4.5 | Temagami | Wind | RCP4.5 | 2075 | 74.7774 | 80.2479 | 85.9343 | 91.703 | 97.4592
TemagamiWind2080RCP4.5 | Temagami | Wind | RCP4.5 | 2080 | 74.9051 | 80.403 | 86.1213 | 91.9171 | 97.7022
TemagamiWind2085RCP4.5 | Temagami | Wind | RCP4.5 | 2085 | 75.0328 | 80.558 | 86.3084 | 92.1312 | 97.9452
TemagamiWind2090RCP4.5 | Temagami | Wind | RCP4.5 | 2090 | 75.1605 | 80.7131 | 86.4954 | 92.3453 | 98.1882
TemagamiWind2095RCP4.5 | Temagami | Wind | RCP4.5 | 2095 | 75.2882 | 80.8682 | 86.6825 | 92.5594 | 98.4312
TemagamiWind2100RCP4.5 | Temagami | Wind | RCP4.5 | 2100 | 75.416 | 81.0233 | 86.8695 | 92.7735 | 98.6742
TemagamiWind2023RCP6.0 | Temagami | Wind | RCP6.0 | 2023 | 75.0929 | 80.7725 | 86.7129 | 92.6804 | 98.6543
TemagamiWind2025RCP6.0 | Temagami | Wind | RCP6.0 | 2025 | 75.0228 | 80.6727 | 86.5781 | 92.5175 | 98.4609
TemagamiWind2030RCP6.0 | Temagami | Wind | RCP6.0 | 2030 | 74.9527 | 80.5729 | 86.4432 | 92.3546 | 98.2675
TemagamiWind2035RCP6.0 | Temagami | Wind | RCP6.0 | 2035 | 74.8826 | 80.4731 | 86.3084 | 92.1917 | 98.0741
TemagamiWind2040RCP6.0 | Temagami | Wind | RCP6.0 | 2040 | 74.8125 | 80.3733 | 86.1735 | 92.0288 | 97.8807
TemagamiWind2045RCP6.0 | Temagami | Wind | RCP6.0 | 2045 | 74.7423 | 80.2735 | 86.0387 | 91.8659 | 97.6873
TemagamiWind2050RCP6.0 | Temagami | Wind | RCP6.0 | 2050 | 74.6677 | 80.1575 | 85.8725 | 91.6601 | 97.4384
TemagamiWind2055RCP6.0 | Temagami | Wind | RCP6.0 | 2055 | 74.6632 | 80.1414 | 85.8412 | 91.6173 | 97.3829
TemagamiWind2060RCP6.0 | Temagami | Wind | RCP6.0 | 2060 | 74.6587 | 80.1252 | 85.8098 | 91.5745 | 97.3273
TemagamiWind2065RCP6.0 | Temagami | Wind | RCP6.0 | 2065 | 74.6542 | 80.109 | 85.7785 | 91.5317 | 97.2718
TemagamiWind2070RCP6.0 | Temagami | Wind | RCP6.0 | 2070 | 74.6497 | 80.0928 | 85.7472 | 91.4889 | 97.2162
TemagamiWind2075RCP6.0 | Temagami | Wind | RCP6.0 | 2075 | 74.8413 | 80.3254 | 86.0278 | 91.81 | 97.5807
TemagamiWind2080RCP6.0 | Temagami | Wind | RCP6.0 | 2080 | 75.0328 | 80.558 | 86.3084 | 92.1312 | 97.9452
TemagamiWind2085RCP6.0 | Temagami | Wind | RCP6.0 | 2085 | 75.2244 | 80.7907 | 86.5889 | 92.4523 | 98.3097
TemagamiWind2090RCP6.0 | Temagami | Wind | RCP6.0 | 2090 | 75.6664 | 81.3442 | 87.2784 | 93.2545 | 99.2296
TemagamiWind2095RCP6.0 | Temagami | Wind | RCP6.0 | 2095 | 75.9168 | 81.6652 | 87.6873 | 93.7354 | 99.785
TemagamiWind2100RCP6.0 | Temagami | Wind | RCP6.0 | 2100 | 76.1672 | 81.9861 | 88.0962 | 94.2164 | 100.3404
TemagamiWind2023RCP8.5 | Temagami | Wind | RCP8.5 | 2023 | 75.0929 | 80.7725 | 86.7129 | 92.6804 | 98.6543
TemagamiWind2025RCP8.5 | Temagami | Wind | RCP8.5 | 2025 | 74.9527 | 80.5729 | 86.4432 | 92.3546 | 98.2675
TemagamiWind2030RCP8.5 | Temagami | Wind | RCP8.5 | 2030 | 74.8125 | 80.3733 | 86.1735 | 92.0288 | 97.8807
TemagamiWind2035RCP8.5 | Temagami | Wind | RCP8.5 | 2035 | 74.6722 | 80.1737 | 85.9038 | 91.703 | 97.4939
TemagamiWind2040RCP8.5 | Temagami | Wind | RCP8.5 | 2040 | 74.6647 | 80.1467 | 85.8516 | 91.6316 | 97.4014
TemagamiWind2045RCP8.5 | Temagami | Wind | RCP8.5 | 2045 | 74.6572 | 80.1198 | 85.7994 | 91.5602 | 97.3088
TemagamiWind2050RCP8.5 | Temagami | Wind | RCP8.5 | 2050 | 74.9051 | 80.403 | 86.1213 | 91.9171 | 97.7022
TemagamiWind2055RCP8.5 | Temagami | Wind | RCP8.5 | 2055 | 75.1605 | 80.7131 | 86.4954 | 92.3453 | 98.1882
TemagamiWind2060RCP8.5 | Temagami | Wind | RCP8.5 | 2060 | 75.6664 | 81.3442 | 87.2784 | 93.2545 | 99.2296
TemagamiWind2065RCP8.5 | Temagami | Wind | RCP8.5 | 2065 | 75.9168 | 81.6652 | 87.6873 | 93.7354 | 99.785
TemagamiWind2070RCP8.5 | Temagami | Wind | RCP8.5 | 2070 | 76.3074 | 82.1425 | 88.2731 | 94.415 | 100.5553
TemagamiWind2075RCP8.5 | Temagami | Wind | RCP8.5 | 2075 | 76.4476 | 82.299 | 88.45 | 94.6136 | 100.7702
TemagamiWind2080RCP8.5 | Temagami | Wind | RCP8.5 | 2080 | 76.5879 | 82.4554 | 88.6269 | 94.8122 | 100.9851
TemagamiWind2085RCP8.5 | Temagami | Wind | RCP8.5 | 2085 | 76.5503 | 82.3987 | 88.5399 | 94.7005 | 100.8512
TemagamiWind2090RCP8.5 | Temagami | Wind | RCP8.5 | 2090 | 76.5127 | 82.3421 | 88.4529 | 94.5887 | 100.7173
TemagamiWind2095RCP8.5 | Temagami | Wind | RCP8.5 | 2095 | 76.5127 | 82.3421 | 88.4529 | 94.5887 | 100.7173
TemagamiWind2100RCP8.5 | Temagami | Wind | RCP8.5 | 2100 | 76.5127 | 82.3421 | 88.4529 | 94.5887 | 100.7173
ThamesfordIce Accretion2023RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2023 | 20.5414 | 24.6261 | 29.76 | 33.6966 | 37.611
ThamesfordIce Accretion2025RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2025 | 20.5623 | 24.6676 | 29.835 | 33.7926 | 37.7307
ThamesfordIce Accretion2030RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2030 | 20.5831 | 24.7091 | 29.91 | 33.8887 | 37.8504
ThamesfordIce Accretion2035RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2035 | 20.604 | 24.7506 | 29.985 | 33.9847 | 37.9701
ThamesfordIce Accretion2040RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2040 | 20.6249 | 24.7921 | 30.06 | 34.0808 | 38.0898
ThamesfordIce Accretion2045RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2045 | 20.6458 | 24.8336 | 30.135 | 34.1768 | 38.2095
ThamesfordIce Accretion2050RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2050 | 20.5831 | 24.8153 | 30.174 | 34.2526 | 38.3292
ThamesfordIce Accretion2055RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2055 | 20.4996 | 24.7556 | 30.138 | 34.2322 | 38.3292
ThamesfordIce Accretion2060RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2060 | 20.4161 | 24.6958 | 30.102 | 34.2119 | 38.3292
ThamesfordIce Accretion2065RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2065 | 20.3326 | 24.6361 | 30.066 | 34.1915 | 38.3292
ThamesfordIce Accretion2070RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2070 | 20.2491 | 24.5763 | 30.03 | 34.1712 | 38.3292
ThamesfordIce Accretion2075RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2075 | 20.2109 | 24.5597 | 30.045 | 34.2051 | 38.3859
ThamesfordIce Accretion2080RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2080 | 20.1726 | 24.5431 | 30.06 | 34.239 | 38.4426
ThamesfordIce Accretion2085RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2085 | 20.1343 | 24.5265 | 30.075 | 34.2729 | 38.4993
ThamesfordIce Accretion2090RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2090 | 20.096 | 24.5099 | 30.09 | 34.3068 | 38.556
ThamesfordIce Accretion2095RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2095 | 20.0578 | 24.4933 | 30.105 | 34.3407 | 38.6127
ThamesfordIce Accretion2100RCP4.5 | Thamesford | Ice Accretion | RCP4.5 | 2100 | 20.0195 | 24.4767 | 30.12 | 34.3746 | 38.6694
ThamesfordIce Accretion2023RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2023 | 20.5414 | 24.6261 | 29.76 | 33.6966 | 37.611
ThamesfordIce Accretion2025RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2025 | 20.5623 | 24.6676 | 29.835 | 33.7926 | 37.7307
ThamesfordIce Accretion2030RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2030 | 20.5831 | 24.7091 | 29.91 | 33.8887 | 37.8504
ThamesfordIce Accretion2035RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2035 | 20.604 | 24.7506 | 29.985 | 33.9847 | 37.9701
ThamesfordIce Accretion2040RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2040 | 20.6249 | 24.7921 | 30.06 | 34.0808 | 38.0898
ThamesfordIce Accretion2045RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2045 | 20.6458 | 24.8336 | 30.135 | 34.1768 | 38.2095
ThamesfordIce Accretion2050RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2050 | 20.5831 | 24.8153 | 30.174 | 34.2526 | 38.3292
ThamesfordIce Accretion2055RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2055 | 20.4996 | 24.7556 | 30.138 | 34.2322 | 38.3292
ThamesfordIce Accretion2060RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2060 | 20.4161 | 24.6958 | 30.102 | 34.2119 | 38.3292
ThamesfordIce Accretion2065RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2065 | 20.3326 | 24.6361 | 30.066 | 34.1915 | 38.3292
ThamesfordIce Accretion2070RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2070 | 20.2491 | 24.5763 | 30.03 | 34.1712 | 38.3292
ThamesfordIce Accretion2075RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2075 | 20.1917 | 24.5514 | 30.0525 | 34.222 | 38.4142
ThamesfordIce Accretion2080RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2080 | 20.1343 | 24.5265 | 30.075 | 34.2729 | 38.4993
ThamesfordIce Accretion2085RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2085 | 20.0769 | 24.5016 | 30.0975 | 34.3238 | 38.5844
ThamesfordIce Accretion2090RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2090 | 19.769 | 24.2277 | 29.86 | 34.1147 | 38.3922
ThamesfordIce Accretion2095RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2095 | 19.5185 | 23.9787 | 29.6 | 33.8548 | 38.115
ThamesfordIce Accretion2100RCP6.0 | Thamesford | Ice Accretion | RCP6.0 | 2100 | 19.268 | 23.7297 | 29.34 | 33.5949 | 37.8378
ThamesfordIce Accretion2023RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2023 | 20.5414 | 24.6261 | 29.76 | 33.6966 | 37.611
ThamesfordIce Accretion2025RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2025 | 20.5831 | 24.7091 | 29.91 | 33.8887 | 37.8504
ThamesfordIce Accretion2030RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2030 | 20.6249 | 24.7921 | 30.06 | 34.0808 | 38.0898
ThamesfordIce Accretion2035RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2035 | 20.6666 | 24.8751 | 30.21 | 34.2729 | 38.3292
ThamesfordIce Accretion2040RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2040 | 20.5275 | 24.7755 | 30.15 | 34.239 | 38.3292
ThamesfordIce Accretion2045RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2045 | 20.3883 | 24.6759 | 30.09 | 34.2051 | 38.3292
ThamesfordIce Accretion2050RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2050 | 20.1726 | 24.5431 | 30.06 | 34.239 | 38.4426
ThamesfordIce Accretion2055RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2055 | 20.096 | 24.5099 | 30.09 | 34.3068 | 38.556
ThamesfordIce Accretion2060RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2060 | 19.769 | 24.2277 | 29.86 | 34.1147 | 38.3922
ThamesfordIce Accretion2065RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2065 | 19.5185 | 23.9787 | 29.6 | 33.8548 | 38.115
ThamesfordIce Accretion2070RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2070 | 18.8157 | 23.2234 | 28.77 | 32.9734 | 37.1574
ThamesfordIce Accretion2075RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2075 | 18.3634 | 22.7171 | 28.2 | 32.3519 | 36.477
ThamesfordIce Accretion2080RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2080 | 17.9111 | 22.2108 | 27.63 | 31.7304 | 35.7966
ThamesfordIce Accretion2085RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2085 | 16.9717 | 21.1028 | 26.31 | 30.2557 | 34.1712
ThamesfordIce Accretion2090RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2090 | 16.0323 | 19.9947 | 24.99 | 28.7811 | 32.5458
ThamesfordIce Accretion2095RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2095 | 16.0323 | 19.9947 | 24.99 | 28.7811 | 32.5458
ThamesfordIce Accretion2100RCP8.5 | Thamesford | Ice Accretion | RCP8.5 | 2100 | 16.0323 | 19.9947 | 24.99 | 28.7811 | 32.5458
ThamesfordWind2023RCP4.5 | Thamesford | Wind | RCP4.5 | 2023 | 88.1536 | 95.1229 | 102.5049 | 109.8423 | 117.1895
ThamesfordWind2025RCP4.5 | Thamesford | Wind | RCP4.5 | 2025 | 88.2466 | 95.245 | 102.6648 | 110.0351 | 117.4159
ThamesfordWind2030RCP4.5 | Thamesford | Wind | RCP4.5 | 2030 | 88.3397 | 95.3671 | 102.8247 | 110.2278 | 117.6424
ThamesfordWind2035RCP4.5 | Thamesford | Wind | RCP4.5 | 2035 | 88.4327 | 95.4892 | 102.9846 | 110.4205 | 117.8688
ThamesfordWind2040RCP4.5 | Thamesford | Wind | RCP4.5 | 2040 | 88.5257 | 95.6113 | 103.1446 | 110.6132 | 118.0953
ThamesfordWind2045RCP4.5 | Thamesford | Wind | RCP4.5 | 2045 | 88.6187 | 95.7335 | 103.3045 | 110.806 | 118.3217
ThamesfordWind2050RCP4.5 | Thamesford | Wind | RCP4.5 | 2050 | 88.7467 | 95.8988 | 103.5189 | 111.0614 | 118.6172
ThamesfordWind2055RCP4.5 | Thamesford | Wind | RCP4.5 | 2055 | 88.7815 | 95.942 | 103.5735 | 111.1241 | 118.6863
ThamesfordWind2060RCP4.5 | Thamesford | Wind | RCP4.5 | 2060 | 88.8164 | 95.9852 | 103.628 | 111.1867 | 118.7554
ThamesfordWind2065RCP4.5 | Thamesford | Wind | RCP4.5 | 2065 | 88.8513 | 96.0284 | 103.6826 | 111.2494 | 118.8245
ThamesfordWind2070RCP4.5 | Thamesford | Wind | RCP4.5 | 2070 | 88.8862 | 96.0716 | 103.7371 | 111.3121 | 118.8936
ThamesfordWind2075RCP4.5 | Thamesford | Wind | RCP4.5 | 2075 | 88.9938 | 96.2156 | 103.9256 | 111.539 | 119.1622
ThamesfordWind2080RCP4.5 | Thamesford | Wind | RCP4.5 | 2080 | 89.1013 | 96.3597 | 104.1142 | 111.766 | 119.4309
ThamesfordWind2085RCP4.5 | Thamesford | Wind | RCP4.5 | 2085 | 89.2089 | 96.5037 | 104.3027 | 111.9929 | 119.6995
ThamesfordWind2090RCP4.5 | Thamesford | Wind | RCP4.5 | 2090 | 89.3164 | 96.6477 | 104.4912 | 112.2199 | 119.9682
ThamesfordWind2095RCP4.5 | Thamesford | Wind | RCP4.5 | 2095 | 89.424 | 96.7917 | 104.6798 | 112.4468 | 120.2369
ThamesfordWind2100RCP4.5 | Thamesford | Wind | RCP4.5 | 2100 | 89.5316 | 96.9358 | 104.8683 | 112.6738 | 120.5055
ThamesfordWind2023RCP6.0 | Thamesford | Wind | RCP6.0 | 2023 | 88.1536 | 95.1229 | 102.5049 | 109.8423 | 117.1895
ThamesfordWind2025RCP6.0 | Thamesford | Wind | RCP6.0 | 2025 | 88.2466 | 95.245 | 102.6648 | 110.0351 | 117.4159
ThamesfordWind2030RCP6.0 | Thamesford | Wind | RCP6.0 | 2030 | 88.3397 | 95.3671 | 102.8247 | 110.2278 | 117.6424
ThamesfordWind2035RCP6.0 | Thamesford | Wind | RCP6.0 | 2035 | 88.4327 | 95.4892 | 102.9846 | 110.4205 | 117.8688
ThamesfordWind2040RCP6.0 | Thamesford | Wind | RCP6.0 | 2040 | 88.5257 | 95.6113 | 103.1446 | 110.6132 | 118.0953
ThamesfordWind2045RCP6.0 | Thamesford | Wind | RCP6.0 | 2045 | 88.6187 | 95.7335 | 103.3045 | 110.806 | 118.3217
ThamesfordWind2050RCP6.0 | Thamesford | Wind | RCP6.0 | 2050 | 88.7467 | 95.8988 | 103.5189 | 111.0614 | 118.6172
ThamesfordWind2055RCP6.0 | Thamesford | Wind | RCP6.0 | 2055 | 88.7815 | 95.942 | 103.5735 | 111.1241 | 118.6863
ThamesfordWind2060RCP6.0 | Thamesford | Wind | RCP6.0 | 2060 | 88.8164 | 95.9852 | 103.628 | 111.1867 | 118.7554
ThamesfordWind2065RCP6.0 | Thamesford | Wind | RCP6.0 | 2065 | 88.8513 | 96.0284 | 103.6826 | 111.2494 | 118.8245
ThamesfordWind2070RCP6.0 | Thamesford | Wind | RCP6.0 | 2070 | 88.8862 | 96.0716 | 103.7371 | 111.3121 | 118.8936
ThamesfordWind2075RCP6.0 | Thamesford | Wind | RCP6.0 | 2075 | 89.0475 | 96.2876 | 104.0199 | 111.6525 | 119.2966
ThamesfordWind2080RCP6.0 | Thamesford | Wind | RCP6.0 | 2080 | 89.2089 | 96.5037 | 104.3027 | 111.9929 | 119.6995
ThamesfordWind2085RCP6.0 | Thamesford | Wind | RCP6.0 | 2085 | 89.3702 | 96.7197 | 104.5855 | 112.3334 | 120.1025
ThamesfordWind2090RCP6.0 | Thamesford | Wind | RCP6.0 | 2090 | 89.8455 | 97.3115 | 105.3161 | 113.1889 | 121.0851
ThamesfordWind2095RCP6.0 | Thamesford | Wind | RCP6.0 | 2095 | 90.1595 | 97.6872 | 105.7638 | 113.704 | 121.6646
ThamesfordWind2100RCP6.0 | Thamesford | Wind | RCP6.0 | 2100 | 90.4734 | 98.0629 | 106.2116 | 114.2192 | 122.2441
ThamesfordWind2023RCP8.5 | Thamesford | Wind | RCP8.5 | 2023 | 88.1536 | 95.1229 | 102.5049 | 109.8423 | 117.1895
ThamesfordWind2025RCP8.5 | Thamesford | Wind | RCP8.5 | 2025 | 88.3397 | 95.3671 | 102.8247 | 110.2278 | 117.6424
ThamesfordWind2030RCP8.5 | Thamesford | Wind | RCP8.5 | 2030 | 88.5257 | 95.6113 | 103.1446 | 110.6132 | 118.0953
ThamesfordWind2035RCP8.5 | Thamesford | Wind | RCP8.5 | 2035 | 88.7118 | 95.8556 | 103.4644 | 110.9987 | 118.5481
ThamesfordWind2040RCP8.5 | Thamesford | Wind | RCP8.5 | 2040 | 88.7699 | 95.9276 | 103.5553 | 111.1032 | 118.6633
ThamesfordWind2045RCP8.5 | Thamesford | Wind | RCP8.5 | 2045 | 88.828 | 95.9996 | 103.6462 | 111.2076 | 118.7784
ThamesfordWind2050RCP8.5 | Thamesford | Wind | RCP8.5 | 2050 | 89.1013 | 96.3597 | 104.1142 | 111.766 | 119.4309
ThamesfordWind2055RCP8.5 | Thamesford | Wind | RCP8.5 | 2055 | 89.3164 | 96.6477 | 104.4912 | 112.2199 | 119.9682
ThamesfordWind2060RCP8.5 | Thamesford | Wind | RCP8.5 | 2060 | 89.8455 | 97.3115 | 105.3161 | 113.1889 | 121.0851
ThamesfordWind2065RCP8.5 | Thamesford | Wind | RCP8.5 | 2065 | 90.1595 | 97.6872 | 105.7638 | 113.704 | 121.6646
ThamesfordWind2070RCP8.5 | Thamesford | Wind | RCP8.5 | 2070 | 90.7496 | 98.4261 | 106.6897 | 114.7884 | 122.9119
ThamesfordWind2075RCP8.5 | Thamesford | Wind | RCP8.5 | 2075 | 91.0258 | 98.7893 | 107.1677 | 115.3575 | 123.5798
ThamesfordWind2080RCP8.5 | Thamesford | Wind | RCP8.5 | 2080 | 91.302 | 99.1525 | 107.6458 | 115.9267 | 124.2476
ThamesfordWind2085RCP8.5 | Thamesford | Wind | RCP8.5 | 2085 | 91.6682 | 99.6175 | 108.2366 | 116.6291 | 125.0593
ThamesfordWind2090RCP8.5 | Thamesford | Wind | RCP8.5 | 2090 | 92.0345 | 100.0824 | 108.8275 | 117.3316 | 125.871
ThamesfordWind2095RCP8.5 | Thamesford | Wind | RCP8.5 | 2095 | 92.0345 | 100.0824 | 108.8275 | 117.3316 | 125.871
ThamesfordWind2100RCP8.5 | Thamesford | Wind | RCP8.5 | 2100 | 92.0345 | 100.0824 | 108.8275 | 117.3316 | 125.871
ThedfordIce Accretion2023RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2023 | 15.0637 | 18.0591 | 21.824 | 24.7108 | 27.5814
ThedfordIce Accretion2025RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2025 | 15.079 | 18.0896 | 21.879 | 24.7813 | 27.6692
ThedfordIce Accretion2030RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2030 | 15.0943 | 18.12 | 21.934 | 24.8517 | 27.757
ThedfordIce Accretion2035RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2035 | 15.1096 | 18.1504 | 21.989 | 24.9221 | 27.8447
ThedfordIce Accretion2040RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2040 | 15.1249 | 18.1809 | 22.044 | 24.9926 | 27.9325
ThedfordIce Accretion2045RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2045 | 15.1402 | 18.2113 | 22.099 | 25.063 | 28.0203
ThedfordIce Accretion2050RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2050 | 15.0943 | 18.1979 | 22.1276 | 25.1185 | 28.1081
ThedfordIce Accretion2055RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2055 | 15.0331 | 18.1541 | 22.1012 | 25.1036 | 28.1081
ThedfordIce Accretion2060RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2060 | 14.9718 | 18.1103 | 22.0748 | 25.0887 | 28.1081
ThedfordIce Accretion2065RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2065 | 14.9106 | 18.0664 | 22.0484 | 25.0738 | 28.1081
ThedfordIce Accretion2070RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2070 | 14.8494 | 18.0226 | 22.022 | 25.0589 | 28.1081
ThedfordIce Accretion2075RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2075 | 14.8213 | 18.0104 | 22.033 | 25.0837 | 28.1497
ThedfordIce Accretion2080RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2080 | 14.7932 | 17.9983 | 22.044 | 25.1086 | 28.1912
ThedfordIce Accretion2085RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2085 | 14.7652 | 17.9861 | 22.055 | 25.1335 | 28.2328
ThedfordIce Accretion2090RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2090 | 14.7371 | 17.9739 | 22.066 | 25.1583 | 28.2744
ThedfordIce Accretion2095RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2095 | 14.709 | 17.9618 | 22.077 | 25.1832 | 28.316
ThedfordIce Accretion2100RCP4.5 | Thedford | Ice Accretion | RCP4.5 | 2100 | 14.681 | 17.9496 | 22.088 | 25.208 | 28.3576
ThedfordIce Accretion2023RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2023 | 15.0637 | 18.0591 | 21.824 | 24.7108 | 27.5814
ThedfordIce Accretion2025RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2025 | 15.079 | 18.0896 | 21.879 | 24.7813 | 27.6692
ThedfordIce Accretion2030RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2030 | 15.0943 | 18.12 | 21.934 | 24.8517 | 27.757
ThedfordIce Accretion2035RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2035 | 15.1096 | 18.1504 | 21.989 | 24.9221 | 27.8447
ThedfordIce Accretion2040RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2040 | 15.1249 | 18.1809 | 22.044 | 24.9926 | 27.9325
ThedfordIce Accretion2045RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2045 | 15.1402 | 18.2113 | 22.099 | 25.063 | 28.0203
ThedfordIce Accretion2050RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2050 | 15.0943 | 18.1979 | 22.1276 | 25.1185 | 28.1081
ThedfordIce Accretion2055RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2055 | 15.0331 | 18.1541 | 22.1012 | 25.1036 | 28.1081
ThedfordIce Accretion2060RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2060 | 14.9718 | 18.1103 | 22.0748 | 25.0887 | 28.1081
ThedfordIce Accretion2065RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2065 | 14.9106 | 18.0664 | 22.0484 | 25.0738 | 28.1081
ThedfordIce Accretion2070RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2070 | 14.8494 | 18.0226 | 22.022 | 25.0589 | 28.1081
ThedfordIce Accretion2075RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2075 | 14.8073 | 18.0044 | 22.0385 | 25.0962 | 28.1704
ThedfordIce Accretion2080RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2080 | 14.7652 | 17.9861 | 22.055 | 25.1335 | 28.2328
ThedfordIce Accretion2085RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2085 | 14.7231 | 17.9678 | 22.0715 | 25.1707 | 28.2952
ThedfordIce Accretion2090RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2090 | 14.4973 | 17.767 | 21.8973 | 25.0174 | 28.1543
ThedfordIce Accretion2095RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2095 | 14.3136 | 17.5844 | 21.7067 | 24.8269 | 27.951
ThedfordIce Accretion2100RCP6.0 | Thedford | Ice Accretion | RCP6.0 | 2100 | 14.1299 | 17.4018 | 21.516 | 24.6363 | 27.7477
ThedfordIce Accretion2023RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2023 | 15.0637 | 18.0591 | 21.824 | 24.7108 | 27.5814
ThedfordIce Accretion2025RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2025 | 15.0943 | 18.12 | 21.934 | 24.8517 | 27.757
ThedfordIce Accretion2030RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2030 | 15.1249 | 18.1809 | 22.044 | 24.9926 | 27.9325
ThedfordIce Accretion2035RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2035 | 15.1555 | 18.2417 | 22.154 | 25.1335 | 28.1081
ThedfordIce Accretion2040RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2040 | 15.0535 | 18.1687 | 22.11 | 25.1086 | 28.1081
ThedfordIce Accretion2045RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2045 | 14.9514 | 18.0957 | 22.066 | 25.0837 | 28.1081
ThedfordIce Accretion2050RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2050 | 14.7932 | 17.9983 | 22.044 | 25.1086 | 28.1912
ThedfordIce Accretion2055RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2055 | 14.7371 | 17.9739 | 22.066 | 25.1583 | 28.2744
ThedfordIce Accretion2060RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2060 | 14.4973 | 17.767 | 21.8973 | 25.0174 | 28.1543
ThedfordIce Accretion2065RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2065 | 14.3136 | 17.5844 | 21.7067 | 24.8269 | 27.951
ThedfordIce Accretion2070RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2070 | 13.7982 | 17.0305 | 21.098 | 24.1805 | 27.2488
ThedfordIce Accretion2075RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2075 | 13.4665 | 16.6592 | 20.68 | 23.7247 | 26.7498
ThedfordIce Accretion2080RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2080 | 13.1348 | 16.2879 | 20.262 | 23.269 | 26.2508
ThedfordIce Accretion2085RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2085 | 12.4459 | 15.4753 | 19.294 | 22.1875 | 25.0589
ThedfordIce Accretion2090RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2090 | 11.757 | 14.6628 | 18.326 | 21.1061 | 23.8669
ThedfordIce Accretion2095RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2095 | 11.757 | 14.6628 | 18.326 | 21.1061 | 23.8669
ThedfordIce Accretion2100RCP8.5 | Thedford | Ice Accretion | RCP8.5 | 2100 | 11.757 | 14.6628 | 18.326 | 21.1061 | 23.8669
ThedfordWind2023RCP4.5 | Thedford | Wind | RCP4.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
ThedfordWind2025RCP4.5 | Thedford | Wind | RCP4.5 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
ThedfordWind2030RCP4.5 | Thedford | Wind | RCP4.5 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
ThedfordWind2035RCP4.5 | Thedford | Wind | RCP4.5 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
ThedfordWind2040RCP4.5 | Thedford | Wind | RCP4.5 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
ThedfordWind2045RCP4.5 | Thedford | Wind | RCP4.5 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
ThedfordWind2050RCP4.5 | Thedford | Wind | RCP4.5 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
ThedfordWind2055RCP4.5 | Thedford | Wind | RCP4.5 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
ThedfordWind2060RCP4.5 | Thedford | Wind | RCP4.5 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
ThedfordWind2065RCP4.5 | Thedford | Wind | RCP4.5 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
ThedfordWind2070RCP4.5 | Thedford | Wind | RCP4.5 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
ThedfordWind2075RCP4.5 | Thedford | Wind | RCP4.5 | 2075 | 86.3504 | 93.3577 | 100.8387 | 108.226 | 115.6228
ThedfordWind2080RCP4.5 | Thedford | Wind | RCP4.5 | 2080 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
ThedfordWind2085RCP4.5 | Thedford | Wind | RCP4.5 | 2085 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
ThedfordWind2090RCP4.5 | Thedford | Wind | RCP4.5 | 2090 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
ThedfordWind2095RCP4.5 | Thedford | Wind | RCP4.5 | 2095 | 86.7678 | 93.9167 | 101.5705 | 109.1068 | 116.6655
ThedfordWind2100RCP4.5 | Thedford | Wind | RCP4.5 | 2100 | 86.8722 | 94.0565 | 101.7534 | 109.327 | 116.9262
ThedfordWind2023RCP6.0 | Thedford | Wind | RCP6.0 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
ThedfordWind2025RCP6.0 | Thedford | Wind | RCP6.0 | 2025 | 85.6255 | 92.416 | 99.6154 | 106.7667 | 113.9283
ThedfordWind2030RCP6.0 | Thedford | Wind | RCP6.0 | 2030 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
ThedfordWind2035RCP6.0 | Thedford | Wind | RCP6.0 | 2035 | 85.806 | 92.6529 | 99.9257 | 107.1407 | 114.3678
ThedfordWind2040RCP6.0 | Thedford | Wind | RCP6.0 | 2040 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
ThedfordWind2045RCP6.0 | Thedford | Wind | RCP6.0 | 2045 | 85.9865 | 92.8899 | 100.236 | 107.5147 | 114.8072
ThedfordWind2050RCP6.0 | Thedford | Wind | RCP6.0 | 2050 | 86.1106 | 93.0503 | 100.4441 | 107.7625 | 115.0939
ThedfordWind2055RCP6.0 | Thedford | Wind | RCP6.0 | 2055 | 86.1445 | 93.0922 | 100.497 | 107.8233 | 115.161
ThedfordWind2060RCP6.0 | Thedford | Wind | RCP6.0 | 2060 | 86.1783 | 93.1341 | 100.55 | 107.8842 | 115.228
ThedfordWind2065RCP6.0 | Thedford | Wind | RCP6.0 | 2065 | 86.2122 | 93.1761 | 100.6029 | 107.945 | 115.295
ThedfordWind2070RCP6.0 | Thedford | Wind | RCP6.0 | 2070 | 86.246 | 93.218 | 100.6558 | 108.0058 | 115.3621
ThedfordWind2075RCP6.0 | Thedford | Wind | RCP6.0 | 2075 | 86.4026 | 93.4276 | 100.9302 | 108.3361 | 115.7531
ThedfordWind2080RCP6.0 | Thedford | Wind | RCP6.0 | 2080 | 86.5591 | 93.6372 | 101.2046 | 108.6664 | 116.1441
ThedfordWind2085RCP6.0 | Thedford | Wind | RCP6.0 | 2085 | 86.7157 | 93.8469 | 101.479 | 108.9967 | 116.5351
ThedfordWind2090RCP6.0 | Thedford | Wind | RCP6.0 | 2090 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
ThedfordWind2095RCP6.0 | Thedford | Wind | RCP6.0 | 2095 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
ThedfordWind2100RCP6.0 | Thedford | Wind | RCP6.0 | 2100 | 87.7861 | 95.1502 | 103.0568 | 110.8265 | 118.6131
ThedfordWind2023RCP8.5 | Thedford | Wind | RCP8.5 | 2023 | 85.5352 | 92.2975 | 99.4602 | 106.5797 | 113.7086
ThedfordWind2025RCP8.5 | Thedford | Wind | RCP8.5 | 2025 | 85.7157 | 92.5344 | 99.7705 | 106.9537 | 114.148
ThedfordWind2030RCP8.5 | Thedford | Wind | RCP8.5 | 2030 | 85.8962 | 92.7714 | 100.0809 | 107.3277 | 114.5875
ThedfordWind2035RCP8.5 | Thedford | Wind | RCP8.5 | 2035 | 86.0768 | 93.0084 | 100.3912 | 107.7017 | 115.0269
ThedfordWind2040RCP8.5 | Thedford | Wind | RCP8.5 | 2040 | 86.1332 | 93.0782 | 100.4794 | 107.8031 | 115.1386
ThedfordWind2045RCP8.5 | Thedford | Wind | RCP8.5 | 2045 | 86.1896 | 93.1481 | 100.5676 | 107.9044 | 115.2504
ThedfordWind2050RCP8.5 | Thedford | Wind | RCP8.5 | 2050 | 86.4547 | 93.4975 | 101.0217 | 108.4462 | 115.8834
ThedfordWind2055RCP8.5 | Thedford | Wind | RCP8.5 | 2055 | 86.6635 | 93.777 | 101.3875 | 108.8866 | 116.4048
ThedfordWind2060RCP8.5 | Thedford | Wind | RCP8.5 | 2060 | 87.1768 | 94.421 | 102.1879 | 109.8269 | 117.4885
ThedfordWind2065RCP8.5 | Thedford | Wind | RCP8.5 | 2065 | 87.4815 | 94.7856 | 102.6223 | 110.3267 | 118.0508
ThedfordWind2070RCP8.5 | Thedford | Wind | RCP8.5 | 2070 | 88.0541 | 95.5026 | 103.5207 | 111.3788 | 119.2611
ThedfordWind2075RCP8.5 | Thedford | Wind | RCP8.5 | 2075 | 88.322 | 95.855 | 103.9845 | 111.9311 | 119.9091
ThedfordWind2080RCP8.5 | Thedford | Wind | RCP8.5 | 2080 | 88.59 | 96.2074 | 104.4484 | 112.4833 | 120.5571
ThedfordWind2085RCP8.5 | Thedford | Wind | RCP8.5 | 2085 | 88.9454 | 96.6585 | 105.0217 | 113.1649 | 121.3447
ThedfordWind2090RCP8.5 | Thedford | Wind | RCP8.5 | 2090 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
ThedfordWind2095RCP8.5 | Thedford | Wind | RCP8.5 | 2095 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
ThedfordWind2100RCP8.5 | Thedford | Wind | RCP8.5 | 2100 | 89.3008 | 97.1097 | 105.595 | 113.8465 | 122.1323
Thunder BayIce Accretion2023RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2023 | 11.7013 | 14.0104 | 16.928 | 19.1467 | 21.3696
Thunder BayIce Accretion2025RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2025 | 11.6531 | 13.9551 | 16.8667 | 19.0804 | 21.2957
Thunder BayIce Accretion2030RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2030 | 11.6049 | 13.8997 | 16.8053 | 19.0141 | 21.2218
Thunder BayIce Accretion2035RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2035 | 11.5566 | 13.8444 | 16.744 | 18.9478 | 21.1478
Thunder BayIce Accretion2040RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2040 | 11.5084 | 13.7891 | 16.6827 | 18.8815 | 21.0739
Thunder BayIce Accretion2045RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2045 | 11.4601 | 13.7337 | 16.6213 | 18.8153 | 21
Thunder BayIce Accretion2050RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2050 | 11.3762 | 13.6439 | 16.5248 | 18.7128 | 20.8938
Thunder BayIce Accretion2055RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2055 | 11.3406 | 13.6093 | 16.4896 | 18.6766 | 20.8616
Thunder BayIce Accretion2060RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2060 | 11.305 | 13.5748 | 16.4544 | 18.6405 | 20.8293
Thunder BayIce Accretion2065RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2065 | 11.2694 | 13.5403 | 16.4192 | 18.6043 | 20.7971
Thunder BayIce Accretion2070RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2070 | 11.2337 | 13.5058 | 16.384 | 18.5682 | 20.7648
Thunder BayIce Accretion2075RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2075 | 11.2504 | 13.5323 | 16.4213 | 18.6134 | 20.8186
Thunder BayIce Accretion2080RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2080 | 11.2671 | 13.5589 | 16.4587 | 18.6586 | 20.8723
Thunder BayIce Accretion2085RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2085 | 11.2838 | 13.5854 | 16.496 | 18.7038 | 20.9261
Thunder BayIce Accretion2090RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2090 | 11.3005 | 13.612 | 16.5333 | 18.749 | 20.9798
Thunder BayIce Accretion2095RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2095 | 11.3172 | 13.6386 | 16.5707 | 18.7942 | 21.0336
Thunder BayIce Accretion2100RCP4.5 | Thunder Bay | Ice Accretion | RCP4.5 | 2100 | 11.3339 | 13.6651 | 16.608 | 18.8394 | 21.0874
Thunder BayIce Accretion2023RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2023 | 11.7013 | 14.0104 | 16.928 | 19.1467 | 21.3696
Thunder BayIce Accretion2025RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2025 | 11.6531 | 13.9551 | 16.8667 | 19.0804 | 21.2957
Thunder BayIce Accretion2030RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2030 | 11.6049 | 13.8997 | 16.8053 | 19.0141 | 21.2218
Thunder BayIce Accretion2035RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2035 | 11.5566 | 13.8444 | 16.744 | 18.9478 | 21.1478
Thunder BayIce Accretion2040RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2040 | 11.5084 | 13.7891 | 16.6827 | 18.8815 | 21.0739
Thunder BayIce Accretion2045RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2045 | 11.4601 | 13.7337 | 16.6213 | 18.8153 | 21
Thunder BayIce Accretion2050RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2050 | 11.3762 | 13.6439 | 16.5248 | 18.7128 | 20.8938
Thunder BayIce Accretion2055RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2055 | 11.3406 | 13.6093 | 16.4896 | 18.6766 | 20.8616
Thunder BayIce Accretion2060RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2060 | 11.305 | 13.5748 | 16.4544 | 18.6405 | 20.8293
Thunder BayIce Accretion2065RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2065 | 11.2694 | 13.5403 | 16.4192 | 18.6043 | 20.7971
Thunder BayIce Accretion2070RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2070 | 11.2337 | 13.5058 | 16.384 | 18.5682 | 20.7648
Thunder BayIce Accretion2075RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2075 | 11.2588 | 13.5456 | 16.44 | 18.636 | 20.8454
Thunder BayIce Accretion2080RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2080 | 11.2838 | 13.5854 | 16.496 | 18.7038 | 20.9261
Thunder BayIce Accretion2085RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2085 | 11.3089 | 13.6253 | 16.552 | 18.7716 | 21.0067
Thunder BayIce Accretion2090RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2090 | 11.3005 | 13.6341 | 16.576 | 18.8092 | 21.0538
Thunder BayIce Accretion2095RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2095 | 11.2671 | 13.6031 | 16.544 | 18.7791 | 21.0202
Thunder BayIce Accretion2100RCP6.0 | Thunder Bay | Ice Accretion | RCP6.0 | 2100 | 11.2337 | 13.5722 | 16.512 | 18.749 | 20.9866
Thunder BayIce Accretion2023RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2023 | 11.7013 | 14.0104 | 16.928 | 19.1467 | 21.3696
Thunder BayIce Accretion2025RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2025 | 11.6049 | 13.8997 | 16.8053 | 19.0141 | 21.2218
Thunder BayIce Accretion2030RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2030 | 11.5084 | 13.7891 | 16.6827 | 18.8815 | 21.0739
Thunder BayIce Accretion2035RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2035 | 11.4119 | 13.6784 | 16.56 | 18.749 | 20.9261
Thunder BayIce Accretion2040RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2040 | 11.3525 | 13.6209 | 16.5013 | 18.6887 | 20.8723
Thunder BayIce Accretion2045RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2045 | 11.2931 | 13.5633 | 16.4427 | 18.6284 | 20.8186
Thunder BayIce Accretion2050RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2050 | 11.2671 | 13.5589 | 16.4587 | 18.6586 | 20.8723
Thunder BayIce Accretion2055RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2055 | 11.3005 | 13.612 | 16.5333 | 18.749 | 20.9798
Thunder BayIce Accretion2060RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2060 | 11.3005 | 13.6341 | 16.576 | 18.8092 | 21.0538
Thunder BayIce Accretion2065RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2065 | 11.2671 | 13.6031 | 16.544 | 18.7791 | 21.0202
Thunder BayIce Accretion2070RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2070 | 11.141 | 13.4659 | 16.3947 | 18.6224 | 20.8522
Thunder BayIce Accretion2075RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2075 | 11.0482 | 13.3597 | 16.2773 | 18.4958 | 20.7178
Thunder BayIce Accretion2080RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2080 | 10.9554 | 13.2534 | 16.16 | 18.3693 | 20.5834
Thunder BayIce Accretion2085RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2085 | 10.6492 | 12.8949 | 15.736 | 17.8902 | 20.039
Thunder BayIce Accretion2090RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2090 | 10.3431 | 12.5363 | 15.312 | 17.411 | 19.4947
Thunder BayIce Accretion2095RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2095 | 10.3431 | 12.5363 | 15.312 | 17.411 | 19.4947
Thunder BayIce Accretion2100RCP8.5 | Thunder Bay | Ice Accretion | RCP8.5 | 2100 | 10.3431 | 12.5363 | 15.312 | 17.411 | 19.4947
Thunder BayWind2023RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2023 | 81.2566 | 87.4987 | 94.0564 | 100.6202 | 107.1814
Thunder BayWind2025RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2025 | 81.3175 | 87.5672 | 94.1363 | 100.7108 | 107.2814
Thunder BayWind2030RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2030 | 81.3784 | 87.6356 | 94.2162 | 100.8013 | 107.3815
Thunder BayWind2035RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2035 | 81.4393 | 87.7041 | 94.2961 | 100.8918 | 107.4815
Thunder BayWind2040RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2040 | 81.5001 | 87.7726 | 94.376 | 100.9823 | 107.5815
Thunder BayWind2045RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2045 | 81.561 | 87.8411 | 94.4559 | 101.0728 | 107.6815
Thunder BayWind2050RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2050 | 81.7566 | 88.0739 | 94.7351 | 101.3927 | 108.043
Thunder BayWind2055RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2055 | 81.8914 | 88.2383 | 94.9344 | 101.622 | 108.3045
Thunder BayWind2060RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2060 | 82.0261 | 88.4026 | 95.1336 | 101.8513 | 108.5659
Thunder BayWind2065RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2065 | 82.1608 | 88.567 | 95.3329 | 102.0807 | 108.8274
Thunder BayWind2070RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2070 | 82.2956 | 88.7313 | 95.5322 | 102.31 | 109.0889
Thunder BayWind2075RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2075 | 82.3835 | 88.8333 | 95.6481 | 102.4391 | 109.2318
Thunder BayWind2080RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2080 | 82.4714 | 88.9353 | 95.7641 | 102.5681 | 109.3746
Thunder BayWind2085RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2085 | 82.5594 | 89.0373 | 95.88 | 102.6972 | 109.5175
Thunder BayWind2090RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2090 | 82.6473 | 89.1393 | 95.9959 | 102.8263 | 109.6604
Thunder BayWind2095RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2095 | 82.7352 | 89.2413 | 96.1119 | 102.9554 | 109.8033
Thunder BayWind2100RCP4.5 | Thunder Bay | Wind | RCP4.5 | 2100 | 82.8232 | 89.3432 | 96.2278 | 103.0844 | 109.9462
Thunder BayWind2023RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2023 | 81.2566 | 87.4987 | 94.0564 | 100.6202 | 107.1814
Thunder BayWind2025RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2025 | 81.3175 | 87.5672 | 94.1363 | 100.7108 | 107.2814
Thunder BayWind2030RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2030 | 81.3784 | 87.6356 | 94.2162 | 100.8013 | 107.3815
Thunder BayWind2035RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2035 | 81.4393 | 87.7041 | 94.2961 | 100.8918 | 107.4815
Thunder BayWind2040RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2040 | 81.5001 | 87.7726 | 94.376 | 100.9823 | 107.5815
Thunder BayWind2045RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2045 | 81.561 | 87.8411 | 94.4559 | 101.0728 | 107.6815
Thunder BayWind2050RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2050 | 81.7566 | 88.0739 | 94.7351 | 101.3927 | 108.043
Thunder BayWind2055RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2055 | 81.8914 | 88.2383 | 94.9344 | 101.622 | 108.3045
Thunder BayWind2060RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2060 | 82.0261 | 88.4026 | 95.1336 | 101.8513 | 108.5659
Thunder BayWind2065RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2065 | 82.1608 | 88.567 | 95.3329 | 102.0807 | 108.8274
Thunder BayWind2070RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2070 | 82.2956 | 88.7313 | 95.5322 | 102.31 | 109.0889
Thunder BayWind2075RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2075 | 82.4275 | 88.8843 | 95.7061 | 102.5036 | 109.3032
Thunder BayWind2080RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2080 | 82.5594 | 89.0373 | 95.88 | 102.6972 | 109.5175
Thunder BayWind2085RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2085 | 82.6913 | 89.1903 | 96.0539 | 102.8908 | 109.7318
Thunder BayWind2090RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2090 | 83.0423 | 89.6084 | 96.5537 | 103.4599 | 110.3712
Thunder BayWind2095RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2095 | 83.2615 | 89.8736 | 96.8795 | 103.8354 | 110.7963
Thunder BayWind2100RCP6.0 | Thunder Bay | Wind | RCP6.0 | 2100 | 83.4806 | 90.1388 | 97.2054 | 104.2109 | 111.2214
Thunder BayWind2023RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2023 | 81.2566 | 87.4987 | 94.0564 | 100.6202 | 107.1814
Thunder BayWind2025RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2025 | 81.3784 | 87.6356 | 94.2162 | 100.8013 | 107.3815
Thunder BayWind2030RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2030 | 81.5001 | 87.7726 | 94.376 | 100.9823 | 107.5815
Thunder BayWind2035RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2035 | 81.6219 | 87.9096 | 94.5358 | 101.1634 | 107.7815
Thunder BayWind2040RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2040 | 81.8464 | 88.1835 | 94.8679 | 101.5456 | 108.2173
Thunder BayWind2045RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2045 | 82.071 | 88.4574 | 95.2001 | 101.9278 | 108.6531
Thunder BayWind2050RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2050 | 82.4714 | 88.9353 | 95.7641 | 102.5681 | 109.3746
Thunder BayWind2055RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2055 | 82.6473 | 89.1393 | 95.9959 | 102.8263 | 109.6604
Thunder BayWind2060RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2060 | 83.0423 | 89.6084 | 96.5537 | 103.4599 | 110.3712
Thunder BayWind2065RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2065 | 83.2615 | 89.8736 | 96.8795 | 103.8354 | 110.7963
Thunder BayWind2070RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2070 | 83.6132 | 90.2874 | 97.3683 | 104.392 | 111.4178
Thunder BayWind2075RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2075 | 83.7458 | 90.436 | 97.5313 | 104.573 | 111.6143
Thunder BayWind2080RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2080 | 83.8783 | 90.5846 | 97.6942 | 104.7541 | 111.8107
Thunder BayWind2085RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2085 | 84.1218 | 90.8687 | 98.0373 | 105.1413 | 112.2501
Thunder BayWind2090RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2090 | 84.3653 | 91.1528 | 98.3804 | 105.5285 | 112.6895
Thunder BayWind2095RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2095 | 84.3653 | 91.1528 | 98.3804 | 105.5285 | 112.6895
Thunder BayWind2100RCP8.5 | Thunder Bay | Wind | RCP8.5 | 2100 | 84.3653 | 91.1528 | 98.3804 | 105.5285 | 112.6895
TillsonburgIce Accretion2023RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
TillsonburgIce Accretion2025RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2025 | 22.9175 | 27.5192 | 33.3427 | 37.7989 | 42.2402
TillsonburgIce Accretion2030RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2030 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
TillsonburgIce Accretion2035RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2035 | 22.6651 | 27.2464 | 33.048 | 37.4787 | 41.8975
TillsonburgIce Accretion2040RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2040 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
TillsonburgIce Accretion2045RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2045 | 22.4127 | 26.9736 | 32.7533 | 37.1585 | 41.5548
TillsonburgIce Accretion2050RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2050 | 21.7945 | 26.2954 | 31.9872 | 36.3223 | 40.6466
TillsonburgIce Accretion2055RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2055 | 21.3024 | 25.7536 | 31.3684 | 35.6461 | 39.9097
TillsonburgIce Accretion2060RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2060 | 20.8103 | 25.2117 | 30.7496 | 34.9699 | 39.1729
TillsonburgIce Accretion2065RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2065 | 20.3181 | 24.6699 | 30.1308 | 34.2937 | 38.436
TillsonburgIce Accretion2070RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2070 | 19.826 | 24.1281 | 29.512 | 33.6175 | 37.6992
TillsonburgIce Accretion2075RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2075 | 19.5895 | 23.8647 | 29.2117 | 33.2909 | 37.3422
TillsonburgIce Accretion2080RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2080 | 19.3529 | 23.6013 | 28.9113 | 32.9644 | 36.9852
TillsonburgIce Accretion2085RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2085 | 19.1163 | 23.3379 | 28.611 | 32.6378 | 36.6282
TillsonburgIce Accretion2090RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2090 | 18.8797 | 23.0746 | 28.3107 | 32.3112 | 36.2712
TillsonburgIce Accretion2095RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2095 | 18.6431 | 22.8112 | 28.0103 | 31.9846 | 35.9142
TillsonburgIce Accretion2100RCP4.5 | Tillsonburg | Ice Accretion | RCP4.5 | 2100 | 18.4065 | 22.5478 | 27.71 | 31.6581 | 35.5572
TillsonburgIce Accretion2023RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
TillsonburgIce Accretion2025RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2025 | 22.9175 | 27.5192 | 33.3427 | 37.7989 | 42.2402
TillsonburgIce Accretion2030RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2030 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
TillsonburgIce Accretion2035RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2035 | 22.6651 | 27.2464 | 33.048 | 37.4787 | 41.8975
TillsonburgIce Accretion2040RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2040 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
TillsonburgIce Accretion2045RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2045 | 22.4127 | 26.9736 | 32.7533 | 37.1585 | 41.5548
TillsonburgIce Accretion2050RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2050 | 21.7945 | 26.2954 | 31.9872 | 36.3223 | 40.6466
TillsonburgIce Accretion2055RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2055 | 21.3024 | 25.7536 | 31.3684 | 35.6461 | 39.9097
TillsonburgIce Accretion2060RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2060 | 20.8103 | 25.2117 | 30.7496 | 34.9699 | 39.1729
TillsonburgIce Accretion2065RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2065 | 20.3181 | 24.6699 | 30.1308 | 34.2937 | 38.436
TillsonburgIce Accretion2070RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2070 | 19.826 | 24.1281 | 29.512 | 33.6175 | 37.6992
TillsonburgIce Accretion2075RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2075 | 19.4712 | 23.733 | 29.0615 | 33.1276 | 37.1637
TillsonburgIce Accretion2080RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2080 | 19.1163 | 23.3379 | 28.611 | 32.6378 | 36.6282
TillsonburgIce Accretion2085RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2085 | 18.7614 | 22.9429 | 28.1605 | 32.1479 | 36.0927
TillsonburgIce Accretion2090RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2090 | 17.4365 | 21.4002 | 26.3613 | 30.1341 | 33.8722
TillsonburgIce Accretion2095RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2095 | 16.4665 | 20.2526 | 25.0127 | 28.6101 | 32.1871
TillsonburgIce Accretion2100RCP6.0 | Tillsonburg | Ice Accretion | RCP6.0 | 2100 | 15.4965 | 19.1049 | 23.664 | 27.0861 | 30.5021
TillsonburgIce Accretion2023RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
TillsonburgIce Accretion2025RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2025 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
TillsonburgIce Accretion2030RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2030 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
TillsonburgIce Accretion2035RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2035 | 22.2866 | 26.8372 | 32.606 | 36.9985 | 41.3834
TillsonburgIce Accretion2040RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2040 | 21.4664 | 25.9342 | 31.5747 | 35.8715 | 40.1554
TillsonburgIce Accretion2045RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2045 | 20.6462 | 25.0311 | 30.5433 | 34.7445 | 38.9273
TillsonburgIce Accretion2050RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2050 | 19.3529 | 23.6013 | 28.9113 | 32.9644 | 36.9852
TillsonburgIce Accretion2055RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2055 | 18.8797 | 23.0746 | 28.3107 | 32.3112 | 36.2712
TillsonburgIce Accretion2060RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2060 | 17.4365 | 21.4002 | 26.3613 | 30.1341 | 33.8722
TillsonburgIce Accretion2065RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2065 | 16.4665 | 20.2526 | 25.0127 | 28.6101 | 32.1871
TillsonburgIce Accretion2070RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2070 | 15.0312 | 18.5876 | 23.052 | 26.4073 | 29.7595
TillsonburgIce Accretion2075RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2075 | 14.5659 | 18.0702 | 22.44 | 25.7286 | 29.017
TillsonburgIce Accretion2080RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2080 | 14.1006 | 17.5528 | 21.828 | 25.0498 | 28.2744
TillsonburgIce Accretion2085RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2085 | 13.0596 | 16.297 | 20.332 | 23.3594 | 26.3894
TillsonburgIce Accretion2090RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2090 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
TillsonburgIce Accretion2095RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2095 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
TillsonburgIce Accretion2100RCP8.5 | Tillsonburg | Ice Accretion | RCP8.5 | 2100 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
TillsonburgWind2023RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2023 | 87.7786 | 94.6439 | 101.8888 | 109.1075 | 116.3375
TillsonburgWind2025RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2025 | 87.8542 | 94.7441 | 102.0218 | 109.2696 | 116.5255
TillsonburgWind2030RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2030 | 87.9298 | 94.8443 | 102.1548 | 109.4317 | 116.7136
TillsonburgWind2035RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2035 | 88.0054 | 94.9444 | 102.2877 | 109.5938 | 116.9016
TillsonburgWind2040RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2040 | 88.0809 | 95.0446 | 102.4207 | 109.7559 | 117.0897
TillsonburgWind2045RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2045 | 88.1565 | 95.1448 | 102.5537 | 109.918 | 117.2778
TillsonburgWind2050RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2050 | 88.3106 | 95.3502 | 102.8261 | 110.2465 | 117.6639
TillsonburgWind2055RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2055 | 88.3891 | 95.4554 | 102.9655 | 110.413 | 117.8619
TillsonburgWind2060RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2060 | 88.4676 | 95.5606 | 103.1048 | 110.5794 | 118.06
TillsonburgWind2065RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2065 | 88.5461 | 95.6658 | 103.2442 | 110.7458 | 118.258
TillsonburgWind2070RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2070 | 88.6246 | 95.771 | 103.3836 | 110.9122 | 118.456
TillsonburgWind2075RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2075 | 88.7437 | 95.9244 | 103.5806 | 111.1464 | 118.7304
TillsonburgWind2080RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2080 | 88.8629 | 96.0779 | 103.7775 | 111.3805 | 119.0049
TillsonburgWind2085RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2085 | 88.9821 | 96.2313 | 103.9744 | 111.6147 | 119.2793
TillsonburgWind2090RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2090 | 89.1013 | 96.3847 | 104.1714 | 111.8488 | 119.5537
TillsonburgWind2095RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2095 | 89.2205 | 96.5381 | 104.3683 | 112.083 | 119.8281
TillsonburgWind2100RCP4.5 | Tillsonburg | Wind | RCP4.5 | 2100 | 89.3397 | 96.6915 | 104.5653 | 112.3172 | 120.1025
TillsonburgWind2023RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2023 | 87.7786 | 94.6439 | 101.8888 | 109.1075 | 116.3375
TillsonburgWind2025RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2025 | 87.8542 | 94.7441 | 102.0218 | 109.2696 | 116.5255
TillsonburgWind2030RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2030 | 87.9298 | 94.8443 | 102.1548 | 109.4317 | 116.7136
TillsonburgWind2035RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2035 | 88.0054 | 94.9444 | 102.2877 | 109.5938 | 116.9016
TillsonburgWind2040RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2040 | 88.0809 | 95.0446 | 102.4207 | 109.7559 | 117.0897
TillsonburgWind2045RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2045 | 88.1565 | 95.1448 | 102.5537 | 109.918 | 117.2778
TillsonburgWind2050RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2050 | 88.3106 | 95.3502 | 102.8261 | 110.2465 | 117.6639
TillsonburgWind2055RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2055 | 88.3891 | 95.4554 | 102.9655 | 110.413 | 117.8619
TillsonburgWind2060RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2060 | 88.4676 | 95.5606 | 103.1048 | 110.5794 | 118.06
TillsonburgWind2065RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2065 | 88.5461 | 95.6658 | 103.2442 | 110.7458 | 118.258
TillsonburgWind2070RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2070 | 88.6246 | 95.771 | 103.3836 | 110.9122 | 118.456
TillsonburgWind2075RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2075 | 88.8033 | 96.0012 | 103.679 | 111.2635 | 118.8677
TillsonburgWind2080RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2080 | 88.9821 | 96.2313 | 103.9744 | 111.6147 | 119.2793
TillsonburgWind2085RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2085 | 89.1609 | 96.4614 | 104.2699 | 111.9659 | 119.6909
TillsonburgWind2090RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2090 | 89.5955 | 97.0234 | 104.9861 | 112.8179 | 120.6782
TillsonburgWind2095RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2095 | 89.8513 | 97.3553 | 105.407 | 113.3186 | 121.2539
TillsonburgWind2100RCP6.0 | Tillsonburg | Wind | RCP6.0 | 2100 | 90.1072 | 97.6872 | 105.8278 | 113.8193 | 121.8296
TillsonburgWind2023RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2023 | 87.7786 | 94.6439 | 101.8888 | 109.1075 | 116.3375
TillsonburgWind2025RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2025 | 87.9298 | 94.8443 | 102.1548 | 109.4317 | 116.7136
TillsonburgWind2030RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2030 | 88.0809 | 95.0446 | 102.4207 | 109.7559 | 117.0897
TillsonburgWind2035RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2035 | 88.2321 | 95.245 | 102.6867 | 110.0801 | 117.4658
TillsonburgWind2040RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2040 | 88.3629 | 95.4204 | 102.919 | 110.3575 | 117.7959
TillsonburgWind2045RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2045 | 88.4937 | 95.5957 | 103.1513 | 110.6349 | 118.126
TillsonburgWind2050RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2050 | 88.8629 | 96.0779 | 103.7775 | 111.3805 | 119.0049
TillsonburgWind2055RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2055 | 89.1013 | 96.3847 | 104.1714 | 111.8488 | 119.5537
TillsonburgWind2060RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2060 | 89.5955 | 97.0234 | 104.9861 | 112.8179 | 120.6782
TillsonburgWind2065RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2065 | 89.8513 | 97.3553 | 105.407 | 113.3186 | 121.2539
TillsonburgWind2070RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2070 | 90.2554 | 97.897 | 106.1173 | 114.176 | 122.2557
TillsonburgWind2075RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2075 | 90.4037 | 98.1068 | 106.4069 | 114.5326 | 122.6817
TillsonburgWind2080RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2080 | 90.5519 | 98.3165 | 106.6964 | 114.8892 | 123.1077
TillsonburgWind2085RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2085 | 90.8921 | 98.7627 | 107.2873 | 115.5917 | 123.9367
TillsonburgWind2090RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2090 | 91.2322 | 99.2089 | 107.8781 | 116.2941 | 124.7657
TillsonburgWind2095RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2095 | 91.2322 | 99.2089 | 107.8781 | 116.2941 | 124.7657
TillsonburgWind2100RCP8.5 | Tillsonburg | Wind | RCP8.5 | 2100 | 91.2322 | 99.2089 | 107.8781 | 116.2941 | 124.7657
TimminsIce Accretion2023RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2023 | 13.2211 | 15.7069 | 18.867 | 21.2982 | 23.7006
TimminsIce Accretion2025RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2025 | 13.2057 | 15.6885 | 18.8448 | 21.2696 | 23.6727
TimminsIce Accretion2030RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2030 | 13.1902 | 15.6701 | 18.8227 | 21.241 | 23.6447
TimminsIce Accretion2035RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2035 | 13.1748 | 15.6517 | 18.8005 | 21.2124 | 23.6168
TimminsIce Accretion2040RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2040 | 13.1594 | 15.6333 | 18.7783 | 21.1837 | 23.5889
TimminsIce Accretion2045RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2045 | 13.144 | 15.6149 | 18.7562 | 21.1551 | 23.561
TimminsIce Accretion2050RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2050 | 13.2343 | 15.7353 | 18.9126 | 21.3369 | 23.7724
TimminsIce Accretion2055RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2055 | 13.3401 | 15.8741 | 19.0912 | 21.5473 | 24.0118
TimminsIce Accretion2060RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2060 | 13.4458 | 16.0129 | 19.2698 | 21.7577 | 24.2512
TimminsIce Accretion2065RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2065 | 13.5516 | 16.1516 | 19.4484 | 21.9681 | 24.4906
TimminsIce Accretion2070RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2070 | 13.6574 | 16.2904 | 19.627 | 22.1785 | 24.73
TimminsIce Accretion2075RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2075 | 13.686 | 16.3272 | 19.6713 | 22.2322 | 24.7899
TimminsIce Accretion2080RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2080 | 13.7147 | 16.364 | 19.7157 | 22.2859 | 24.8497
TimminsIce Accretion2085RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2085 | 13.7433 | 16.4008 | 19.76 | 22.3395 | 24.9096
TimminsIce Accretion2090RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2090 | 13.772 | 16.4376 | 19.8043 | 22.3932 | 24.9694
TimminsIce Accretion2095RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2095 | 13.8006 | 16.4744 | 19.8487 | 22.4469 | 25.0293
TimminsIce Accretion2100RCP4.5 | Timmins | Ice Accretion | RCP4.5 | 2100 | 13.8292 | 16.5112 | 19.893 | 22.5006 | 25.0891
TimminsIce Accretion2023RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2023 | 13.2211 | 15.7069 | 18.867 | 21.2982 | 23.7006
TimminsIce Accretion2025RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2025 | 13.2057 | 15.6885 | 18.8448 | 21.2696 | 23.6727
TimminsIce Accretion2030RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2030 | 13.1902 | 15.6701 | 18.8227 | 21.241 | 23.6447
TimminsIce Accretion2035RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2035 | 13.1748 | 15.6517 | 18.8005 | 21.2124 | 23.6168
TimminsIce Accretion2040RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2040 | 13.1594 | 15.6333 | 18.7783 | 21.1837 | 23.5889
TimminsIce Accretion2045RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2045 | 13.144 | 15.6149 | 18.7562 | 21.1551 | 23.561
TimminsIce Accretion2050RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2050 | 13.2343 | 15.7353 | 18.9126 | 21.3369 | 23.7724
TimminsIce Accretion2055RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2055 | 13.3401 | 15.8741 | 19.0912 | 21.5473 | 24.0118
TimminsIce Accretion2060RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2060 | 13.4458 | 16.0129 | 19.2698 | 21.7577 | 24.2512
TimminsIce Accretion2065RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2065 | 13.5516 | 16.1516 | 19.4484 | 21.9681 | 24.4906
TimminsIce Accretion2070RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2070 | 13.6574 | 16.2904 | 19.627 | 22.1785 | 24.73
TimminsIce Accretion2075RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2075 | 13.7003 | 16.3456 | 19.6935 | 22.259 | 24.8198
TimminsIce Accretion2080RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2080 | 13.7433 | 16.4008 | 19.76 | 22.3395 | 24.9096
TimminsIce Accretion2085RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2085 | 13.7863 | 16.456 | 19.8265 | 22.42 | 24.9993
TimminsIce Accretion2090RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2090 | 13.7499 | 16.4323 | 19.817 | 22.4218 | 25.0093
TimminsIce Accretion2095RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2095 | 13.6706 | 16.3535 | 19.741 | 22.3431 | 24.9295
TimminsIce Accretion2100RCP6.0 | Timmins | Ice Accretion | RCP6.0 | 2100 | 13.5913 | 16.2746 | 19.665 | 22.2644 | 24.8497
TimminsIce Accretion2023RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2023 | 13.2211 | 15.7069 | 18.867 | 21.2982 | 23.7006
TimminsIce Accretion2025RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2025 | 13.1902 | 15.6701 | 18.8227 | 21.241 | 23.6447
TimminsIce Accretion2030RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2030 | 13.1594 | 15.6333 | 18.7783 | 21.1837 | 23.5889
TimminsIce Accretion2035RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2035 | 13.1285 | 15.5965 | 18.734 | 21.1265 | 23.533
TimminsIce Accretion2040RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2040 | 13.3048 | 15.8278 | 19.0317 | 21.4772 | 23.932
TimminsIce Accretion2045RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2045 | 13.4811 | 16.0591 | 19.3293 | 21.8278 | 24.331
TimminsIce Accretion2050RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2050 | 13.7147 | 16.364 | 19.7157 | 22.2859 | 24.8497
TimminsIce Accretion2055RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2055 | 13.772 | 16.4376 | 19.8043 | 22.3932 | 24.9694
TimminsIce Accretion2060RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2060 | 13.7499 | 16.4323 | 19.817 | 22.4218 | 25.0093
TimminsIce Accretion2065RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2065 | 13.6706 | 16.3535 | 19.741 | 22.3431 | 24.9295
TimminsIce Accretion2070RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2070 | 13.534 | 16.2116 | 19.6017 | 22.1928 | 24.7779
TimminsIce Accretion2075RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2075 | 13.4767 | 16.1485 | 19.5383 | 22.1213 | 24.7061
TimminsIce Accretion2080RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2080 | 13.4194 | 16.0854 | 19.475 | 22.0497 | 24.6343
TimminsIce Accretion2085RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2085 | 13.3731 | 16.0854 | 19.5225 | 22.1356 | 24.754
TimminsIce Accretion2090RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2090 | 13.3268 | 16.0854 | 19.57 | 22.2214 | 24.8737
TimminsIce Accretion2095RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2095 | 13.3268 | 16.0854 | 19.57 | 22.2214 | 24.8737
TimminsIce Accretion2100RCP8.5 | Timmins | Ice Accretion | RCP8.5 | 2100 | 13.3268 | 16.0854 | 19.57 | 22.2214 | 24.8737
TimminsWind2023RCP4.5 | Timmins | Wind | RCP4.5 | 2023 | 74.1446 | 79.9195 | 86.003 | 92.0687 | 98.15
TimminsWind2025RCP4.5 | Timmins | Wind | RCP4.5 | 2025 | 74.1471 | 79.9103 | 85.9803 | 92.0353 | 98.1032
TimminsWind2030RCP4.5 | Timmins | Wind | RCP4.5 | 2030 | 74.1495 | 79.9011 | 85.9577 | 92.002 | 98.0563
TimminsWind2035RCP4.5 | Timmins | Wind | RCP4.5 | 2035 | 74.152 | 79.8919 | 85.935 | 91.9686 | 98.0095
TimminsWind2040RCP4.5 | Timmins | Wind | RCP4.5 | 2040 | 74.1544 | 79.8827 | 85.9123 | 91.9353 | 97.9627
TimminsWind2045RCP4.5 | Timmins | Wind | RCP4.5 | 2045 | 74.1569 | 79.8734 | 85.8897 | 91.9019 | 97.9158
TimminsWind2050RCP4.5 | Timmins | Wind | RCP4.5 | 2050 | 74.1784 | 79.8895 | 85.901 | 91.9086 | 97.9174
TimminsWind2055RCP4.5 | Timmins | Wind | RCP4.5 | 2055 | 74.1975 | 79.9148 | 85.935 | 91.9486 | 97.9659
TimminsWind2060RCP4.5 | Timmins | Wind | RCP4.5 | 2060 | 74.2166 | 79.9401 | 85.969 | 91.9886 | 98.0143
TimminsWind2065RCP4.5 | Timmins | Wind | RCP4.5 | 2065 | 74.2357 | 79.9654 | 86.003 | 92.0287 | 98.0628
TimminsWind2070RCP4.5 | Timmins | Wind | RCP4.5 | 2070 | 74.2547 | 79.9907 | 86.037 | 92.0687 | 98.1112
TimminsWind2075RCP4.5 | Timmins | Wind | RCP4.5 | 2075 | 74.3024 | 80.0355 | 86.0767 | 92.1051 | 98.1435
TimminsWind2080RCP4.5 | Timmins | Wind | RCP4.5 | 2080 | 74.3502 | 80.0803 | 86.1163 | 92.1414 | 98.1758
TimminsWind2085RCP4.5 | Timmins | Wind | RCP4.5 | 2085 | 74.3979 | 80.1251 | 86.156 | 92.1778 | 98.2081
TimminsWind2090RCP4.5 | Timmins | Wind | RCP4.5 | 2090 | 74.4456 | 80.1699 | 86.1957 | 92.2142 | 98.2404
TimminsWind2095RCP4.5 | Timmins | Wind | RCP4.5 | 2095 | 74.4933 | 80.2147 | 86.2353 | 92.2506 | 98.2727
TimminsWind2100RCP4.5 | Timmins | Wind | RCP4.5 | 2100 | 74.541 | 80.2595 | 86.275 | 92.287 | 98.305
TimminsWind2023RCP6.0 | Timmins | Wind | RCP6.0 | 2023 | 74.1446 | 79.9195 | 86.003 | 92.0687 | 98.15
TimminsWind2025RCP6.0 | Timmins | Wind | RCP6.0 | 2025 | 74.1471 | 79.9103 | 85.9803 | 92.0353 | 98.1032
TimminsWind2030RCP6.0 | Timmins | Wind | RCP6.0 | 2030 | 74.1495 | 79.9011 | 85.9577 | 92.002 | 98.0563
TimminsWind2035RCP6.0 | Timmins | Wind | RCP6.0 | 2035 | 74.152 | 79.8919 | 85.935 | 91.9686 | 98.0095
TimminsWind2040RCP6.0 | Timmins | Wind | RCP6.0 | 2040 | 74.1544 | 79.8827 | 85.9123 | 91.9353 | 97.9627
TimminsWind2045RCP6.0 | Timmins | Wind | RCP6.0 | 2045 | 74.1569 | 79.8734 | 85.8897 | 91.9019 | 97.9158
TimminsWind2050RCP6.0 | Timmins | Wind | RCP6.0 | 2050 | 74.1784 | 79.8895 | 85.901 | 91.9086 | 97.9174
TimminsWind2055RCP6.0 | Timmins | Wind | RCP6.0 | 2055 | 74.1975 | 79.9148 | 85.935 | 91.9486 | 97.9659
TimminsWind2060RCP6.0 | Timmins | Wind | RCP6.0 | 2060 | 74.2166 | 79.9401 | 85.969 | 91.9886 | 98.0143
TimminsWind2065RCP6.0 | Timmins | Wind | RCP6.0 | 2065 | 74.2357 | 79.9654 | 86.003 | 92.0287 | 98.0628
TimminsWind2070RCP6.0 | Timmins | Wind | RCP6.0 | 2070 | 74.2547 | 79.9907 | 86.037 | 92.0687 | 98.1112
TimminsWind2075RCP6.0 | Timmins | Wind | RCP6.0 | 2075 | 74.3263 | 80.0579 | 86.0965 | 92.1233 | 98.1597
TimminsWind2080RCP6.0 | Timmins | Wind | RCP6.0 | 2080 | 74.3979 | 80.1251 | 86.156 | 92.1778 | 98.2081
TimminsWind2085RCP6.0 | Timmins | Wind | RCP6.0 | 2085 | 74.4694 | 80.1923 | 86.2155 | 92.2324 | 98.2566
TimminsWind2090RCP6.0 | Timmins | Wind | RCP6.0 | 2090 | 74.6755 | 80.4018 | 86.4252 | 92.4507 | 98.4762
TimminsWind2095RCP6.0 | Timmins | Wind | RCP6.0 | 2095 | 74.8101 | 80.544 | 86.5753 | 92.6144 | 98.6474
TimminsWind2100RCP6.0 | Timmins | Wind | RCP6.0 | 2100 | 74.9447 | 80.6863 | 86.7255 | 92.7781 | 98.8186
TimminsWind2023RCP8.5 | Timmins | Wind | RCP8.5 | 2023 | 74.1446 | 79.9195 | 86.003 | 92.0687 | 98.15
TimminsWind2025RCP8.5 | Timmins | Wind | RCP8.5 | 2025 | 74.1495 | 79.9011 | 85.9577 | 92.002 | 98.0563
TimminsWind2030RCP8.5 | Timmins | Wind | RCP8.5 | 2030 | 74.1544 | 79.8827 | 85.9123 | 91.9353 | 97.9627
TimminsWind2035RCP8.5 | Timmins | Wind | RCP8.5 | 2035 | 74.1593 | 79.8642 | 85.867 | 91.8686 | 97.869
TimminsWind2040RCP8.5 | Timmins | Wind | RCP8.5 | 2040 | 74.1911 | 79.9064 | 85.9237 | 91.9353 | 97.9497
TimminsWind2045RCP8.5 | Timmins | Wind | RCP8.5 | 2045 | 74.2229 | 79.9485 | 85.9803 | 92.002 | 98.0305
TimminsWind2050RCP8.5 | Timmins | Wind | RCP8.5 | 2050 | 74.3502 | 80.0803 | 86.1163 | 92.1414 | 98.1758
TimminsWind2055RCP8.5 | Timmins | Wind | RCP8.5 | 2055 | 74.4456 | 80.1699 | 86.1957 | 92.2142 | 98.2404
TimminsWind2060RCP8.5 | Timmins | Wind | RCP8.5 | 2060 | 74.6755 | 80.4018 | 86.4252 | 92.4507 | 98.4762
TimminsWind2065RCP8.5 | Timmins | Wind | RCP8.5 | 2065 | 74.8101 | 80.544 | 86.5753 | 92.6144 | 98.6474
TimminsWind2070RCP8.5 | Timmins | Wind | RCP8.5 | 2070 | 75.1282 | 80.884 | 86.938 | 93.0024 | 99.0576
TimminsWind2075RCP8.5 | Timmins | Wind | RCP8.5 | 2075 | 75.3116 | 81.0816 | 87.1505 | 93.2268 | 99.2967
TimminsWind2080RCP8.5 | Timmins | Wind | RCP8.5 | 2080 | 75.4951 | 81.2792 | 87.363 | 93.4511 | 99.5357
TimminsWind2085RCP8.5 | Timmins | Wind | RCP8.5 | 2085 | 75.5612 | 81.3622 | 87.4607 | 93.5603 | 99.6616
TimminsWind2090RCP8.5 | Timmins | Wind | RCP8.5 | 2090 | 75.6272 | 81.4452 | 87.5585 | 93.6694 | 99.7876
TimminsWind2095RCP8.5 | Timmins | Wind | RCP8.5 | 2095 | 75.6272 | 81.4452 | 87.5585 | 93.6694 | 99.7876
TimminsWind2100RCP8.5 | Timmins | Wind | RCP8.5 | 2100 | 75.6272 | 81.4452 | 87.5585 | 93.6694 | 99.7876
Timmins (Porcupine)Ice Accretion2023RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2023 | 13.1682 | 15.6596 | 18.829 | 21.2553 | 23.6767
Timmins (Porcupine)Ice Accretion2025RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2025 | 13.2189 | 15.7227 | 18.9082 | 21.3448 | 23.7764
Timmins (Porcupine)Ice Accretion2030RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2030 | 13.2696 | 15.7858 | 18.9873 | 21.4342 | 23.8762
Timmins (Porcupine)Ice Accretion2035RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2035 | 13.3202 | 15.8488 | 19.0665 | 21.5237 | 23.9759
Timmins (Porcupine)Ice Accretion2040RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2040 | 13.3709 | 15.9119 | 19.1457 | 21.6131 | 24.0757
Timmins (Porcupine)Ice Accretion2045RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2045 | 13.4216 | 15.975 | 19.2248 | 21.7026 | 24.1754
Timmins (Porcupine)Ice Accretion2050RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2050 | 13.5516 | 16.1422 | 19.437 | 21.9509 | 24.4571
Timmins (Porcupine)Ice Accretion2055RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2055 | 13.6309 | 16.2463 | 19.57 | 22.1098 | 24.639
Timmins (Porcupine)Ice Accretion2060RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2060 | 13.7103 | 16.3503 | 19.703 | 22.2687 | 24.821
Timmins (Porcupine)Ice Accretion2065RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2065 | 13.7896 | 16.4544 | 19.836 | 22.4276 | 25.0029
Timmins (Porcupine)Ice Accretion2070RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2070 | 13.8689 | 16.5585 | 19.969 | 22.5864 | 25.1849
Timmins (Porcupine)Ice Accretion2075RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2075 | 13.8513 | 16.5427 | 19.9532 | 22.5721 | 25.1689
Timmins (Porcupine)Ice Accretion2080RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2080 | 13.8337 | 16.527 | 19.9373 | 22.5578 | 25.153
Timmins (Porcupine)Ice Accretion2085RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2085 | 13.816 | 16.5112 | 19.9215 | 22.5435 | 25.137
Timmins (Porcupine)Ice Accretion2090RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2090 | 13.7984 | 16.4954 | 19.9057 | 22.5292 | 25.121
Timmins (Porcupine)Ice Accretion2095RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2095 | 13.7808 | 16.4796 | 19.8898 | 22.5149 | 25.1051
Timmins (Porcupine)Ice Accretion2100RCP4.5 | Timmins (Porcupine) | Ice Accretion | RCP4.5 | 2100 | 13.7631 | 16.4639 | 19.874 | 22.5006 | 25.0891
Timmins (Porcupine)Ice Accretion2023RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2023 | 13.1682 | 15.6596 | 18.829 | 21.2553 | 23.6767
Timmins (Porcupine)Ice Accretion2025RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2025 | 13.2189 | 15.7227 | 18.9082 | 21.3448 | 23.7764
Timmins (Porcupine)Ice Accretion2030RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2030 | 13.2696 | 15.7858 | 18.9873 | 21.4342 | 23.8762
Timmins (Porcupine)Ice Accretion2035RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2035 | 13.3202 | 15.8488 | 19.0665 | 21.5237 | 23.9759
Timmins (Porcupine)Ice Accretion2040RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2040 | 13.3709 | 15.9119 | 19.1457 | 21.6131 | 24.0757
Timmins (Porcupine)Ice Accretion2045RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2045 | 13.4216 | 15.975 | 19.2248 | 21.7026 | 24.1754
Timmins (Porcupine)Ice Accretion2050RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2050 | 13.5516 | 16.1422 | 19.437 | 21.9509 | 24.4571
Timmins (Porcupine)Ice Accretion2055RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2055 | 13.6309 | 16.2463 | 19.57 | 22.1098 | 24.639
Timmins (Porcupine)Ice Accretion2060RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2060 | 13.7103 | 16.3503 | 19.703 | 22.2687 | 24.821
Timmins (Porcupine)Ice Accretion2065RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2065 | 13.7896 | 16.4544 | 19.836 | 22.4276 | 25.0029
Timmins (Porcupine)Ice Accretion2070RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2070 | 13.8689 | 16.5585 | 19.969 | 22.5864 | 25.1849
Timmins (Porcupine)Ice Accretion2075RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2075 | 13.8425 | 16.5348 | 19.9452 | 22.565 | 25.1609
Timmins (Porcupine)Ice Accretion2080RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2080 | 13.816 | 16.5112 | 19.9215 | 22.5435 | 25.137
Timmins (Porcupine)Ice Accretion2085RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2085 | 13.7896 | 16.4875 | 19.8978 | 22.522 | 25.1131
Timmins (Porcupine)Ice Accretion2090RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2090 | 13.6442 | 16.3325 | 19.7347 | 22.3431 | 24.9295
Timmins (Porcupine)Ice Accretion2095RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2095 | 13.5252 | 16.201 | 19.5953 | 22.1857 | 24.7699
Timmins (Porcupine)Ice Accretion2100RCP6.0 | Timmins (Porcupine) | Ice Accretion | RCP6.0 | 2100 | 13.4062 | 16.0696 | 19.456 | 22.0282 | 24.6103
Timmins (Porcupine)Ice Accretion2023RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2023 | 13.1682 | 15.6596 | 18.829 | 21.2553 | 23.6767
Timmins (Porcupine)Ice Accretion2025RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2025 | 13.2696 | 15.7858 | 18.9873 | 21.4342 | 23.8762
Timmins (Porcupine)Ice Accretion2030RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2030 | 13.3709 | 15.9119 | 19.1457 | 21.6131 | 24.0757
Timmins (Porcupine)Ice Accretion2035RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2035 | 13.4723 | 16.0381 | 19.304 | 21.792 | 24.2752
Timmins (Porcupine)Ice Accretion2040RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2040 | 13.6045 | 16.2116 | 19.5257 | 22.0568 | 24.5784
Timmins (Porcupine)Ice Accretion2045RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2045 | 13.7367 | 16.385 | 19.7473 | 22.3216 | 24.8816
Timmins (Porcupine)Ice Accretion2050RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2050 | 13.8337 | 16.527 | 19.9373 | 22.5578 | 25.153
Timmins (Porcupine)Ice Accretion2055RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2055 | 13.7984 | 16.4954 | 19.9057 | 22.5292 | 25.121
Timmins (Porcupine)Ice Accretion2060RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2060 | 13.6442 | 16.3325 | 19.7347 | 22.3431 | 24.9295
Timmins (Porcupine)Ice Accretion2065RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2065 | 13.5252 | 16.201 | 19.5953 | 22.1857 | 24.7699
Timmins (Porcupine)Ice Accretion2070RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2070 | 13.3268 | 15.9908 | 19.3737 | 21.9495 | 24.5225
Timmins (Porcupine)Ice Accretion2075RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2075 | 13.2475 | 15.9119 | 19.2913 | 21.8708 | 24.4348
Timmins (Porcupine)Ice Accretion2080RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2080 | 13.1682 | 15.8331 | 19.209 | 21.792 | 24.347
Timmins (Porcupine)Ice Accretion2085RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2085 | 13.0228 | 15.699 | 19.076 | 21.6632 | 24.2273
Timmins (Porcupine)Ice Accretion2090RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2090 | 12.8773 | 15.565 | 18.943 | 21.5344 | 24.1076
Timmins (Porcupine)Ice Accretion2095RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2095 | 12.8773 | 15.565 | 18.943 | 21.5344 | 24.1076
Timmins (Porcupine)Ice Accretion2100RCP8.5 | Timmins (Porcupine) | Ice Accretion | RCP8.5 | 2100 | 12.8773 | 15.565 | 18.943 | 21.5344 | 24.1076
Timmins (Porcupine)Wind2023RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2023 | 74.1667 | 79.9195 | 85.986 | 92.0414 | 98.1016
Timmins (Porcupine)Wind2025RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2025 | 74.1581 | 79.8932 | 85.935 | 91.9717 | 98.0111
Timmins (Porcupine)Wind2030RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2030 | 74.1495 | 79.8668 | 85.884 | 91.9019 | 97.9207
Timmins (Porcupine)Wind2035RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2035 | 74.141 | 79.8405 | 85.833 | 91.8322 | 97.8302
Timmins (Porcupine)Wind2040RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2040 | 74.1324 | 79.8141 | 85.782 | 91.7625 | 97.7398
Timmins (Porcupine)Wind2045RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2045 | 74.1239 | 79.7878 | 85.731 | 91.6928 | 97.6494
Timmins (Porcupine)Wind2050RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2050 | 74.1476 | 79.8089 | 85.7446 | 91.7031 | 97.6539
Timmins (Porcupine)Wind2055RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2055 | 74.1799 | 79.8563 | 85.8092 | 91.7831 | 97.7488
Timmins (Porcupine)Wind2060RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2060 | 74.2122 | 79.9037 | 85.8738 | 91.8631 | 97.8438
Timmins (Porcupine)Wind2065RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2065 | 74.2445 | 79.9512 | 85.9384 | 91.9432 | 97.9388
Timmins (Porcupine)Wind2070RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2070 | 74.2768 | 79.9986 | 86.003 | 92.0232 | 98.0337
Timmins (Porcupine)Wind2075RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2075 | 74.3061 | 80.017 | 86.0115 | 92.0217 | 98.024
Timmins (Porcupine)Wind2080RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2080 | 74.3355 | 80.0355 | 86.02 | 92.0202 | 98.0143
Timmins (Porcupine)Wind2085RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2085 | 74.3648 | 80.0539 | 86.0285 | 92.0187 | 98.0047
Timmins (Porcupine)Wind2090RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2090 | 74.3942 | 80.0724 | 86.037 | 92.0171 | 97.995
Timmins (Porcupine)Wind2095RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2095 | 74.4236 | 80.0908 | 86.0455 | 92.0156 | 97.9853
Timmins (Porcupine)Wind2100RCP4.5 | Timmins (Porcupine) | Wind | RCP4.5 | 2100 | 74.4529 | 80.1093 | 86.054 | 92.0141 | 97.9756
Timmins (Porcupine)Wind2023RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2023 | 74.1667 | 79.9195 | 85.986 | 92.0414 | 98.1016
Timmins (Porcupine)Wind2025RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2025 | 74.1581 | 79.8932 | 85.935 | 91.9717 | 98.0111
Timmins (Porcupine)Wind2030RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2030 | 74.1495 | 79.8668 | 85.884 | 91.9019 | 97.9207
Timmins (Porcupine)Wind2035RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2035 | 74.141 | 79.8405 | 85.833 | 91.8322 | 97.8302
Timmins (Porcupine)Wind2040RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2040 | 74.1324 | 79.8141 | 85.782 | 91.7625 | 97.7398
Timmins (Porcupine)Wind2045RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2045 | 74.1239 | 79.7878 | 85.731 | 91.6928 | 97.6494
Timmins (Porcupine)Wind2050RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2050 | 74.1476 | 79.8089 | 85.7446 | 91.7031 | 97.6539
Timmins (Porcupine)Wind2055RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2055 | 74.1799 | 79.8563 | 85.8092 | 91.7831 | 97.7488
Timmins (Porcupine)Wind2060RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2060 | 74.2122 | 79.9037 | 85.8738 | 91.8631 | 97.8438
Timmins (Porcupine)Wind2065RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2065 | 74.2445 | 79.9512 | 85.9384 | 91.9432 | 97.9388
Timmins (Porcupine)Wind2070RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2070 | 74.2768 | 79.9986 | 86.003 | 92.0232 | 98.0337
Timmins (Porcupine)Wind2075RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2075 | 74.3208 | 80.0263 | 86.0157 | 92.0209 | 98.0192
Timmins (Porcupine)Wind2080RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2080 | 74.3648 | 80.0539 | 86.0285 | 92.0187 | 98.0047
Timmins (Porcupine)Wind2085RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2085 | 74.4089 | 80.0816 | 86.0413 | 92.0164 | 97.9901
Timmins (Porcupine)Wind2090RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2090 | 74.7073 | 80.4281 | 86.4478 | 92.4719 | 98.4989
Timmins (Porcupine)Wind2095RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2095 | 74.9618 | 80.7469 | 86.8417 | 92.9297 | 99.0221
Timmins (Porcupine)Wind2100RCP6.0 | Timmins (Porcupine) | Wind | RCP6.0 | 2100 | 75.2162 | 81.0658 | 87.2355 | 93.3875 | 99.5454
Timmins (Porcupine)Wind2023RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2023 | 74.1667 | 79.9195 | 85.986 | 92.0414 | 98.1016
Timmins (Porcupine)Wind2025RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2025 | 74.1495 | 79.8668 | 85.884 | 91.9019 | 97.9207
Timmins (Porcupine)Wind2030RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2030 | 74.1324 | 79.8141 | 85.782 | 91.7625 | 97.7398
Timmins (Porcupine)Wind2035RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2035 | 74.1153 | 79.7614 | 85.68 | 91.623 | 97.5589
Timmins (Porcupine)Wind2040RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2040 | 74.1691 | 79.8405 | 85.7877 | 91.7564 | 97.7172
Timmins (Porcupine)Wind2045RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2045 | 74.2229 | 79.9195 | 85.8953 | 91.8898 | 97.8755
Timmins (Porcupine)Wind2050RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2050 | 74.3355 | 80.0355 | 86.02 | 92.0202 | 98.0143
Timmins (Porcupine)Wind2055RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2055 | 74.3942 | 80.0724 | 86.037 | 92.0171 | 97.995
Timmins (Porcupine)Wind2060RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2060 | 74.7073 | 80.4281 | 86.4478 | 92.4719 | 98.4989
Timmins (Porcupine)Wind2065RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2065 | 74.9618 | 80.7469 | 86.8417 | 92.9297 | 99.0221
Timmins (Porcupine)Wind2070RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2070 | 75.3997 | 81.2555 | 87.4338 | 93.5936 | 99.7618
Timmins (Porcupine)Wind2075RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2075 | 75.5832 | 81.4452 | 87.6322 | 93.7998 | 99.9782
Timmins (Porcupine)Wind2080RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2080 | 75.7667 | 81.6349 | 87.8305 | 94.0059 | 100.1946
Timmins (Porcupine)Wind2085RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2085 | 75.8988 | 81.8247 | 88.0813 | 94.3152 | 100.558
Timmins (Porcupine)Wind2090RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2090 | 76.0309 | 82.0144 | 88.332 | 94.6244 | 100.9214
Timmins (Porcupine)Wind2095RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2095 | 76.0309 | 82.0144 | 88.332 | 94.6244 | 100.9214
Timmins (Porcupine)Wind2100RCP8.5 | Timmins (Porcupine) | Wind | RCP8.5 | 2100 | 76.0309 | 82.0144 | 88.332 | 94.6244 | 100.9214
Toronto (LBP Int'l Airport)Ice Accretion2023RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
Toronto (LBP Int'l Airport)Ice Accretion2025RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
Toronto (LBP Int'l Airport)Ice Accretion2030RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
Toronto (LBP Int'l Airport)Ice Accretion2035RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
Toronto (LBP Int'l Airport)Ice Accretion2040RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
Toronto (LBP Int'l Airport)Ice Accretion2045RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
Toronto (LBP Int'l Airport)Ice Accretion2050RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
Toronto (LBP Int'l Airport)Ice Accretion2055RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
Toronto (LBP Int'l Airport)Ice Accretion2060RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
Toronto (LBP Int'l Airport)Ice Accretion2065RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
Toronto (LBP Int'l Airport)Ice Accretion2070RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
Toronto (LBP Int'l Airport)Ice Accretion2075RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2075 | 15.5377 | 18.8894 | 23.1125 | 26.329 | 29.5313
Toronto (LBP Int'l Airport)Ice Accretion2080RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2080 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
Toronto (LBP Int'l Airport)Ice Accretion2085RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2085 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
Toronto (LBP Int'l Airport)Ice Accretion2090RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2090 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
Toronto (LBP Int'l Airport)Ice Accretion2095RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2095 | 15.3405 | 18.7511 | 23.0625 | 26.329 | 29.5942
Toronto (LBP Int'l Airport)Ice Accretion2100RCP4.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP4.5 | 2100 | 15.2912 | 18.7165 | 23.05 | 26.329 | 29.61
Toronto (LBP Int'l Airport)Ice Accretion2023RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
Toronto (LBP Int'l Airport)Ice Accretion2025RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2025 | 16.8598 | 20.2728 | 24.5708 | 27.8592 | 31.164
Toronto (LBP Int'l Airport)Ice Accretion2030RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2030 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
Toronto (LBP Int'l Airport)Ice Accretion2035RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2035 | 16.7612 | 20.1898 | 24.5125 | 27.8121 | 31.122
Toronto (LBP Int'l Airport)Ice Accretion2040RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2040 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
Toronto (LBP Int'l Airport)Ice Accretion2045RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2045 | 16.6626 | 20.1067 | 24.4542 | 27.765 | 31.08
Toronto (LBP Int'l Airport)Ice Accretion2050RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2050 | 16.4081 | 19.837 | 24.165 | 27.459 | 30.7503
Toronto (LBP Int'l Airport)Ice Accretion2055RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2055 | 16.2028 | 19.6088 | 23.905 | 27.1765 | 30.4416
Toronto (LBP Int'l Airport)Ice Accretion2060RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2060 | 15.9975 | 19.3805 | 23.645 | 26.894 | 30.1329
Toronto (LBP Int'l Airport)Ice Accretion2065RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2065 | 15.7922 | 19.1522 | 23.385 | 26.6115 | 29.8242
Toronto (LBP Int'l Airport)Ice Accretion2070RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2070 | 15.587 | 18.924 | 23.125 | 26.329 | 29.5155
Toronto (LBP Int'l Airport)Ice Accretion2075RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2075 | 15.513 | 18.8721 | 23.1062 | 26.329 | 29.5391
Toronto (LBP Int'l Airport)Ice Accretion2080RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2080 | 15.4391 | 18.8203 | 23.0875 | 26.329 | 29.5628
Toronto (LBP Int'l Airport)Ice Accretion2085RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2085 | 15.3652 | 18.7684 | 23.0688 | 26.329 | 29.5864
Toronto (LBP Int'l Airport)Ice Accretion2090RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2090 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
Toronto (LBP Int'l Airport)Ice Accretion2095RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2095 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
Toronto (LBP Int'l Airport)Ice Accretion2100RCP6.0 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP6.0 | 2100 | 14.2127 | 17.596 | 21.825 | 25.0577 | 28.2555
Toronto (LBP Int'l Airport)Ice Accretion2023RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2023 | 16.9091 | 20.3143 | 24.6 | 27.8827 | 31.185
Toronto (LBP Int'l Airport)Ice Accretion2025RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2025 | 16.8105 | 20.2312 | 24.5417 | 27.8357 | 31.143
Toronto (LBP Int'l Airport)Ice Accretion2030RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2030 | 16.7119 | 20.1483 | 24.4833 | 27.7886 | 31.101
Toronto (LBP Int'l Airport)Ice Accretion2035RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2035 | 16.6133 | 20.0652 | 24.425 | 27.7415 | 31.059
Toronto (LBP Int'l Airport)Ice Accretion2040RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2040 | 16.2712 | 19.6848 | 23.9917 | 27.2707 | 30.5445
Toronto (LBP Int'l Airport)Ice Accretion2045RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2045 | 15.9291 | 19.3044 | 23.5583 | 26.7998 | 30.03
Toronto (LBP Int'l Airport)Ice Accretion2050RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2050 | 15.4884 | 18.8548 | 23.1 | 26.329 | 29.547
Toronto (LBP Int'l Airport)Ice Accretion2055RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2055 | 15.3898 | 18.7857 | 23.075 | 26.329 | 29.5785
Toronto (LBP Int'l Airport)Ice Accretion2060RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2060 | 14.9317 | 18.343 | 22.6417 | 25.9052 | 29.1585
Toronto (LBP Int'l Airport)Ice Accretion2065RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2065 | 14.5722 | 17.9695 | 22.2333 | 25.4815 | 28.707
Toronto (LBP Int'l Airport)Ice Accretion2070RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2070 | 13.8125 | 17.1464 | 21.325 | 24.5022 | 27.657
Toronto (LBP Int'l Airport)Ice Accretion2075RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2075 | 13.4124 | 16.6968 | 20.825 | 23.9466 | 27.0585
Toronto (LBP Int'l Airport)Ice Accretion2080RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2080 | 13.0123 | 16.2473 | 20.325 | 23.391 | 26.46
Toronto (LBP Int'l Airport)Ice Accretion2085RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2085 | 12.1338 | 15.1994 | 19.0625 | 21.9785 | 24.885
Toronto (LBP Int'l Airport)Ice Accretion2090RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2090 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
Toronto (LBP Int'l Airport)Ice Accretion2095RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2095 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
Toronto (LBP Int'l Airport)Ice Accretion2100RCP8.5 | Toronto (LBP Int'l Airport) | Ice Accretion | RCP8.5 | 2100 | 11.2553 | 14.1515 | 17.8 | 20.566 | 23.31
Toronto (LBP Int'l Airport)Wind2023RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2023 | 85.9036 | 92.5764 | 99.6138 | 106.6397 | 113.6613
Toronto (LBP Int'l Airport)Wind2025RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2025 | 85.935 | 92.6224 | 99.6798 | 106.7227 | 113.761
Toronto (LBP Int'l Airport)Wind2030RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2030 | 85.9663 | 92.6685 | 99.7458 | 106.8057 | 113.8607
Toronto (LBP Int'l Airport)Wind2035RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2035 | 85.9977 | 92.7145 | 99.8118 | 106.8887 | 113.9604
Toronto (LBP Int'l Airport)Wind2040RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2040 | 86.029 | 92.7605 | 99.8778 | 106.9716 | 114.0601
Toronto (LBP Int'l Airport)Wind2045RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2045 | 86.0604 | 92.8066 | 99.9438 | 107.0546 | 114.1598
Toronto (LBP Int'l Airport)Wind2050RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2050 | 86.1601 | 92.9355 | 100.1108 | 107.2541 | 114.3926
Toronto (LBP Int'l Airport)Wind2055RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2055 | 86.2285 | 93.0183 | 100.2118 | 107.3706 | 114.5258
Toronto (LBP Int'l Airport)Wind2060RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2060 | 86.2969 | 93.1012 | 100.3127 | 107.4872 | 114.659
Toronto (LBP Int'l Airport)Wind2065RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2065 | 86.3653 | 93.184 | 100.4137 | 107.6037 | 114.7922
Toronto (LBP Int'l Airport)Wind2070RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2070 | 86.4336 | 93.2669 | 100.5147 | 107.7202 | 114.9253
Toronto (LBP Int'l Airport)Wind2075RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2075 | 86.5277 | 93.3989 | 100.6946 | 107.9391 | 115.1849
Toronto (LBP Int'l Airport)Wind2080RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2080 | 86.6217 | 93.5308 | 100.8744 | 108.1581 | 115.4445
Toronto (LBP Int'l Airport)Wind2085RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2085 | 86.7157 | 93.6628 | 101.0542 | 108.377 | 115.7041
Toronto (LBP Int'l Airport)Wind2090RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2090 | 86.8098 | 93.7948 | 101.2341 | 108.5959 | 115.9636
Toronto (LBP Int'l Airport)Wind2095RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2095 | 86.9038 | 93.9267 | 101.4139 | 108.8148 | 116.2232
Toronto (LBP Int'l Airport)Wind2100RCP4.5 | Toronto (LBP Int'l Airport) | Wind | RCP4.5 | 2100 | 86.9978 | 94.0587 | 101.5938 | 109.0337 | 116.4828
Toronto (LBP Int'l Airport)Wind2023RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2023 | 85.9036 | 92.5764 | 99.6138 | 106.6397 | 113.6613
Toronto (LBP Int'l Airport)Wind2025RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2025 | 85.935 | 92.6224 | 99.6798 | 106.7227 | 113.761
Toronto (LBP Int'l Airport)Wind2030RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2030 | 85.9663 | 92.6685 | 99.7458 | 106.8057 | 113.8607
Toronto (LBP Int'l Airport)Wind2035RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2035 | 85.9977 | 92.7145 | 99.8118 | 106.8887 | 113.9604
Toronto (LBP Int'l Airport)Wind2040RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2040 | 86.029 | 92.7605 | 99.8778 | 106.9716 | 114.0601
Toronto (LBP Int'l Airport)Wind2045RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2045 | 86.0604 | 92.8066 | 99.9438 | 107.0546 | 114.1598
Toronto (LBP Int'l Airport)Wind2050RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2050 | 86.1601 | 92.9355 | 100.1108 | 107.2541 | 114.3926
Toronto (LBP Int'l Airport)Wind2055RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2055 | 86.2285 | 93.0183 | 100.2118 | 107.3706 | 114.5258
Toronto (LBP Int'l Airport)Wind2060RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2060 | 86.2969 | 93.1012 | 100.3127 | 107.4872 | 114.659
Toronto (LBP Int'l Airport)Wind2065RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2065 | 86.3653 | 93.184 | 100.4137 | 107.6037 | 114.7922
Toronto (LBP Int'l Airport)Wind2070RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2070 | 86.4336 | 93.2669 | 100.5147 | 107.7202 | 114.9253
Toronto (LBP Int'l Airport)Wind2075RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2075 | 86.5747 | 93.4649 | 100.7845 | 108.0486 | 115.3147
Toronto (LBP Int'l Airport)Wind2080RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2080 | 86.7157 | 93.6628 | 101.0542 | 108.377 | 115.7041
Toronto (LBP Int'l Airport)Wind2085RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2085 | 86.8568 | 93.8608 | 101.324 | 108.7054 | 116.0934
Toronto (LBP Int'l Airport)Wind2090RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2090 | 87.2942 | 94.4393 | 102.0789 | 109.6093 | 117.1524
Toronto (LBP Int'l Airport)Wind2095RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2095 | 87.5905 | 94.8198 | 102.564 | 110.1849 | 117.8221
Toronto (LBP Int'l Airport)Wind2100RCP6.0 | Toronto (LBP Int'l Airport) | Wind | RCP6.0 | 2100 | 87.8869 | 95.2004 | 103.0491 | 110.7604 | 118.4917
Toronto (LBP Int'l Airport)Wind2023RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2023 | 85.9036 | 92.5764 | 99.6138 | 106.6397 | 113.6613
Toronto (LBP Int'l Airport)Wind2025RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2025 | 85.9663 | 92.6685 | 99.7458 | 106.8057 | 113.8607
Toronto (LBP Int'l Airport)Wind2030RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2030 | 86.029 | 92.7605 | 99.8778 | 106.9716 | 114.0601
Toronto (LBP Int'l Airport)Wind2035RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2035 | 86.0917 | 92.8526 | 100.0098 | 107.1376 | 114.2595
Toronto (LBP Int'l Airport)Wind2040RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2040 | 86.2057 | 92.9907 | 100.1781 | 107.3318 | 114.4814
Toronto (LBP Int'l Airport)Wind2045RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2045 | 86.3197 | 93.1288 | 100.3464 | 107.526 | 114.7034
Toronto (LBP Int'l Airport)Wind2050RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2050 | 86.6217 | 93.5308 | 100.8744 | 108.1581 | 115.4445
Toronto (LBP Int'l Airport)Wind2055RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2055 | 86.8098 | 93.7948 | 101.2341 | 108.5959 | 115.9636
Toronto (LBP Int'l Airport)Wind2060RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2060 | 87.2942 | 94.4393 | 102.0789 | 109.6093 | 117.1524
Toronto (LBP Int'l Airport)Wind2065RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2065 | 87.5905 | 94.8198 | 102.564 | 110.1849 | 117.8221
Toronto (LBP Int'l Airport)Wind2070RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2070 | 88.055 | 95.4428 | 103.3857 | 111.1735 | 118.9845
Toronto (LBP Int'l Airport)Wind2075RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2075 | 88.2231 | 95.6853 | 103.7223 | 111.5867 | 119.4774
Toronto (LBP Int'l Airport)Wind2080RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2080 | 88.3912 | 95.9277 | 104.0589 | 111.9998 | 119.9702
Toronto (LBP Int'l Airport)Wind2085RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2085 | 88.6605 | 96.2776 | 104.5093 | 112.54 | 120.6022
Toronto (LBP Int'l Airport)Wind2090RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2090 | 88.9298 | 96.6275 | 104.9598 | 113.0803 | 121.2342
Toronto (LBP Int'l Airport)Wind2095RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2095 | 88.9298 | 96.6275 | 104.9598 | 113.0803 | 121.2342
Toronto (LBP Int'l Airport)Wind2100RCP8.5 | Toronto (LBP Int'l Airport) | Wind | RCP8.5 | 2100 | 88.9298 | 96.6275 | 104.9598 | 113.0803 | 121.2342
Toronto (city hall)Ice Accretion2023RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
Toronto (city hall)Ice Accretion2025RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
Toronto (city hall)Ice Accretion2030RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
Toronto (city hall)Ice Accretion2035RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
Toronto (city hall)Ice Accretion2040RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
Toronto (city hall)Ice Accretion2045RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
Toronto (city hall)Ice Accretion2050RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
Toronto (city hall)Ice Accretion2055RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
Toronto (city hall)Ice Accretion2060RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
Toronto (city hall)Ice Accretion2065RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
Toronto (city hall)Ice Accretion2070RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
Toronto (city hall)Ice Accretion2075RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
Toronto (city hall)Ice Accretion2080RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
Toronto (city hall)Ice Accretion2085RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
Toronto (city hall)Ice Accretion2090RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
Toronto (city hall)Ice Accretion2095RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
Toronto (city hall)Ice Accretion2100RCP4.5 | Toronto (city hall) | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
Toronto (city hall)Ice Accretion2023RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
Toronto (city hall)Ice Accretion2025RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
Toronto (city hall)Ice Accretion2030RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
Toronto (city hall)Ice Accretion2035RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
Toronto (city hall)Ice Accretion2040RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
Toronto (city hall)Ice Accretion2045RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
Toronto (city hall)Ice Accretion2050RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
Toronto (city hall)Ice Accretion2055RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
Toronto (city hall)Ice Accretion2060RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
Toronto (city hall)Ice Accretion2065RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
Toronto (city hall)Ice Accretion2070RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
Toronto (city hall)Ice Accretion2075RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
Toronto (city hall)Ice Accretion2080RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
Toronto (city hall)Ice Accretion2085RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
Toronto (city hall)Ice Accretion2090RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
Toronto (city hall)Ice Accretion2095RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
Toronto (city hall)Ice Accretion2100RCP6.0 | Toronto (city hall) | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
Toronto (city hall)Ice Accretion2023RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
Toronto (city hall)Ice Accretion2025RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
Toronto (city hall)Ice Accretion2030RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
Toronto (city hall)Ice Accretion2035RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
Toronto (city hall)Ice Accretion2040RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
Toronto (city hall)Ice Accretion2045RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
Toronto (city hall)Ice Accretion2050RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
Toronto (city hall)Ice Accretion2055RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
Toronto (city hall)Ice Accretion2060RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
Toronto (city hall)Ice Accretion2065RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
Toronto (city hall)Ice Accretion2070RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
Toronto (city hall)Ice Accretion2075RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
Toronto (city hall)Ice Accretion2080RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
Toronto (city hall)Ice Accretion2085RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
Toronto (city hall)Ice Accretion2090RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
Toronto (city hall)Ice Accretion2095RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
Toronto (city hall)Ice Accretion2100RCP8.5 | Toronto (city hall) | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
Toronto (city hall)Wind2023RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2023 | 85.6899 | 92.2541 | 99.1584 | 106.0677 | 112.9729
Toronto (city hall)Wind2025RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2025 | 85.7056 | 92.2879 | 99.2129 | 106.1401 | 113.0631
Toronto (city hall)Wind2030RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2030 | 85.7213 | 92.3217 | 99.2673 | 106.2125 | 113.1534
Toronto (city hall)Wind2035RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2035 | 85.7369 | 92.3554 | 99.3217 | 106.2849 | 113.2437
Toronto (city hall)Wind2040RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2040 | 85.7526 | 92.3892 | 99.3762 | 106.3573 | 113.334
Toronto (city hall)Wind2045RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2045 | 85.7683 | 92.4229 | 99.4306 | 106.4296 | 113.4243
Toronto (city hall)Wind2050RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2050 | 85.8677 | 92.5617 | 99.6178 | 106.6567 | 113.6952
Toronto (city hall)Wind2055RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2055 | 85.9515 | 92.6666 | 99.7504 | 106.8113 | 113.8757
Toronto (city hall)Wind2060RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2060 | 86.0353 | 92.7716 | 99.8831 | 106.966 | 114.0563
Toronto (city hall)Wind2065RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2065 | 86.1191 | 92.8765 | 100.0157 | 107.1207 | 114.2369
Toronto (city hall)Wind2070RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2070 | 86.2028 | 92.9815 | 100.1484 | 107.2753 | 114.4175
Toronto (city hall)Wind2075RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2075 | 86.3482 | 93.1687 | 100.3877 | 107.5596 | 114.7466
Toronto (city hall)Wind2080RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2080 | 86.4935 | 93.3559 | 100.6269 | 107.8438 | 115.0758
Toronto (city hall)Wind2085RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2085 | 86.6388 | 93.5431 | 100.8662 | 108.128 | 115.405
Toronto (city hall)Wind2090RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2090 | 86.7841 | 93.7303 | 101.1054 | 108.4123 | 115.7342
Toronto (city hall)Wind2095RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2095 | 86.9295 | 93.9175 | 101.3447 | 108.6965 | 116.0633
Toronto (city hall)Wind2100RCP4.5 | Toronto (city hall) | Wind | RCP4.5 | 2100 | 87.0748 | 94.1047 | 101.5839 | 108.9808 | 116.3925
Toronto (city hall)Wind2023RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2023 | 85.6899 | 92.2541 | 99.1584 | 106.0677 | 112.9729
Toronto (city hall)Wind2025RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2025 | 85.7056 | 92.2879 | 99.2129 | 106.1401 | 113.0631
Toronto (city hall)Wind2030RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2030 | 85.7213 | 92.3217 | 99.2673 | 106.2125 | 113.1534
Toronto (city hall)Wind2035RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2035 | 85.7369 | 92.3554 | 99.3217 | 106.2849 | 113.2437
Toronto (city hall)Wind2040RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2040 | 85.7526 | 92.3892 | 99.3762 | 106.3573 | 113.334
Toronto (city hall)Wind2045RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2045 | 85.7683 | 92.4229 | 99.4306 | 106.4296 | 113.4243
Toronto (city hall)Wind2050RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2050 | 85.8677 | 92.5617 | 99.6178 | 106.6567 | 113.6952
Toronto (city hall)Wind2055RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2055 | 85.9515 | 92.6666 | 99.7504 | 106.8113 | 113.8757
Toronto (city hall)Wind2060RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2060 | 86.0353 | 92.7716 | 99.8831 | 106.966 | 114.0563
Toronto (city hall)Wind2065RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2065 | 86.1191 | 92.8765 | 100.0157 | 107.1207 | 114.2369
Toronto (city hall)Wind2070RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2070 | 86.2028 | 92.9815 | 100.1484 | 107.2753 | 114.4175
Toronto (city hall)Wind2075RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2075 | 86.4208 | 93.2623 | 100.5073 | 107.7017 | 114.9112
Toronto (city hall)Wind2080RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2080 | 86.6388 | 93.5431 | 100.8662 | 108.128 | 115.405
Toronto (city hall)Wind2085RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2085 | 86.8568 | 93.8239 | 101.225 | 108.5544 | 115.8988
Toronto (city hall)Wind2090RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2090 | 87.525 | 94.6572 | 102.267 | 109.7753 | 117.3029
Toronto (city hall)Wind2095RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2095 | 87.9752 | 95.2096 | 102.9501 | 110.5697 | 118.2133
Toronto (city hall)Wind2100RCP6.0 | Toronto (city hall) | Wind | RCP6.0 | 2100 | 88.4254 | 95.762 | 103.6332 | 111.3642 | 119.1237
Toronto (city hall)Wind2023RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2023 | 85.6899 | 92.2541 | 99.1584 | 106.0677 | 112.9729
Toronto (city hall)Wind2025RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2025 | 85.7213 | 92.3217 | 99.2673 | 106.2125 | 113.1534
Toronto (city hall)Wind2030RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2030 | 85.7526 | 92.3892 | 99.3762 | 106.3573 | 113.334
Toronto (city hall)Wind2035RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2035 | 85.784 | 92.4567 | 99.4851 | 106.502 | 113.5146
Toronto (city hall)Wind2040RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2040 | 85.9236 | 92.6316 | 99.7062 | 106.7598 | 113.8155
Toronto (city hall)Wind2045RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2045 | 86.0632 | 92.8066 | 99.9273 | 107.0175 | 114.1165
Toronto (city hall)Wind2050RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2050 | 86.4935 | 93.3559 | 100.6269 | 107.8438 | 115.0758
Toronto (city hall)Wind2055RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2055 | 86.7841 | 93.7303 | 101.1054 | 108.4123 | 115.7342
Toronto (city hall)Wind2060RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2060 | 87.525 | 94.6572 | 102.267 | 109.7753 | 117.3029
Toronto (city hall)Wind2065RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2065 | 87.9752 | 95.2096 | 102.9501 | 110.5697 | 118.2133
Toronto (city hall)Wind2070RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2070 | 88.5594 | 95.9431 | 103.8741 | 111.6608 | 119.4698
Toronto (city hall)Wind2075RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2075 | 88.6933 | 96.1241 | 104.115 | 111.9574 | 119.8159
Toronto (city hall)Wind2080RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2080 | 88.8272 | 96.3052 | 104.3559 | 112.254 | 120.162
Toronto (city hall)Wind2085RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2085 | 89.1136 | 96.7103 | 104.9103 | 112.932 | 120.969
Toronto (city hall)Wind2090RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2090 | 89.4 | 97.1154 | 105.4647 | 113.6099 | 121.7759
Toronto (city hall)Wind2095RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2095 | 89.4 | 97.1154 | 105.4647 | 113.6099 | 121.7759
Toronto (city hall)Wind2100RCP8.5 | Toronto (city hall) | Wind | RCP8.5 | 2100 | 89.4 | 97.1154 | 105.4647 | 113.6099 | 121.7759
TrentonIce Accretion2023RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
TrentonIce Accretion2025RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
TrentonIce Accretion2030RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
TrentonIce Accretion2035RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
TrentonIce Accretion2040RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
TrentonIce Accretion2045RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
TrentonIce Accretion2050RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
TrentonIce Accretion2055RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
TrentonIce Accretion2060RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
TrentonIce Accretion2065RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
TrentonIce Accretion2070RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
TrentonIce Accretion2075RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2075 | 16.8859 | 20.3972 | 24.8292 | 28.2123 | 31.5682
TrentonIce Accretion2080RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2080 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
TrentonIce Accretion2085RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2085 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
TrentonIce Accretion2090RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2090 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
TrentonIce Accretion2095RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2095 | 16.7235 | 20.3142 | 24.8458 | 28.2877 | 31.7152
TrentonIce Accretion2100RCP4.5 | Trenton | Ice Accretion | RCP4.5 | 2100 | 16.6829 | 20.2935 | 24.85 | 28.3065 | 31.752
TrentonIce Accretion2023RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
TrentonIce Accretion2025RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2025 | 17.689 | 21.1754 | 25.5792 | 28.9421 | 32.3085
TrentonIce Accretion2030RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2030 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
TrentonIce Accretion2035RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2035 | 17.6832 | 21.1961 | 25.6375 | 29.0269 | 32.4135
TrentonIce Accretion2040RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2040 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
TrentonIce Accretion2045RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2045 | 17.6774 | 21.2169 | 25.6958 | 29.1116 | 32.5185
TrentonIce Accretion2050RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2050 | 17.5249 | 21.0654 | 25.545 | 28.9619 | 32.3631
TrentonIce Accretion2055RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2055 | 17.3753 | 20.9035 | 25.365 | 28.7698 | 32.1552
TrentonIce Accretion2060RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2060 | 17.2257 | 20.7417 | 25.185 | 28.5777 | 31.9473
TrentonIce Accretion2065RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2065 | 17.0761 | 20.5799 | 25.005 | 28.3856 | 31.7394
TrentonIce Accretion2070RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2070 | 16.9265 | 20.418 | 24.825 | 28.1935 | 31.5315
TrentonIce Accretion2075RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2075 | 16.8656 | 20.3869 | 24.8313 | 28.2217 | 31.5866
TrentonIce Accretion2080RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2080 | 16.8047 | 20.3558 | 24.8375 | 28.25 | 31.6417
TrentonIce Accretion2085RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2085 | 16.7438 | 20.3246 | 24.8438 | 28.2782 | 31.6969
TrentonIce Accretion2090RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2090 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
TrentonIce Accretion2095RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2095 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
TrentonIce Accretion2100RCP6.0 | Trenton | Ice Accretion | RCP6.0 | 2100 | 15.6565 | 19.173 | 23.6 | 26.9505 | 30.2715
TrentonIce Accretion2023RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2023 | 17.6919 | 21.165 | 25.55 | 28.8997 | 32.256
TrentonIce Accretion2025RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2025 | 17.6861 | 21.1857 | 25.6083 | 28.9845 | 32.361
TrentonIce Accretion2030RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2030 | 17.6803 | 21.2065 | 25.6667 | 29.0692 | 32.466
TrentonIce Accretion2035RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2035 | 17.6745 | 21.2272 | 25.725 | 29.154 | 32.571
TrentonIce Accretion2040RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2040 | 17.4251 | 20.9575 | 25.425 | 28.8338 | 32.2245
TrentonIce Accretion2045RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2045 | 17.1758 | 20.6877 | 25.125 | 28.5137 | 31.878
TrentonIce Accretion2050RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2050 | 16.8453 | 20.3765 | 24.8333 | 28.2312 | 31.605
TrentonIce Accretion2055RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2055 | 16.7641 | 20.335 | 24.8417 | 28.2688 | 31.6785
TrentonIce Accretion2060RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2060 | 16.3408 | 19.92 | 24.4333 | 27.8545 | 31.2585
TrentonIce Accretion2065RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2065 | 15.9987 | 19.5465 | 24.0167 | 27.4025 | 30.765
TrentonIce Accretion2070RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2070 | 15.2216 | 18.6888 | 23.05 | 26.3478 | 29.631
TrentonIce Accretion2075RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2075 | 14.7867 | 18.2047 | 22.5 | 25.7452 | 28.9905
TrentonIce Accretion2080RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2080 | 14.3518 | 17.7205 | 21.95 | 25.1425 | 28.35
TrentonIce Accretion2085RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2085 | 13.6908 | 16.9424 | 21.025 | 24.0972 | 27.1845
TrentonIce Accretion2090RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2090 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
TrentonIce Accretion2095RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2095 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
TrentonIce Accretion2100RCP8.5 | Trenton | Ice Accretion | RCP8.5 | 2100 | 13.0297 | 16.1642 | 20.1 | 23.052 | 26.019
TrentonWind2023RCP4.5 | Trenton | Wind | RCP4.5 | 2023 | 87.735 | 94.5124 | 101.6363 | 108.7616 | 115.8884
TrentonWind2025RCP4.5 | Trenton | Wind | RCP4.5 | 2025 | 87.7016 | 94.4764 | 101.6009 | 108.7238 | 115.85
TrentonWind2030RCP4.5 | Trenton | Wind | RCP4.5 | 2030 | 87.6681 | 94.4404 | 101.5656 | 108.686 | 115.8116
TrentonWind2035RCP4.5 | Trenton | Wind | RCP4.5 | 2035 | 87.6347 | 94.4043 | 101.5302 | 108.6482 | 115.7733
TrentonWind2040RCP4.5 | Trenton | Wind | RCP4.5 | 2040 | 87.6013 | 94.3683 | 101.4949 | 108.6103 | 115.7349
TrentonWind2045RCP4.5 | Trenton | Wind | RCP4.5 | 2045 | 87.5678 | 94.3323 | 101.4595 | 108.5725 | 115.6965
TrentonWind2050RCP4.5 | Trenton | Wind | RCP4.5 | 2050 | 87.6582 | 94.4616 | 101.6403 | 108.7941 | 115.9621
TrentonWind2055RCP4.5 | Trenton | Wind | RCP4.5 | 2055 | 87.7821 | 94.627 | 101.8565 | 109.0534 | 116.2661
TrentonWind2060RCP4.5 | Trenton | Wind | RCP4.5 | 2060 | 87.9059 | 94.7923 | 102.0726 | 109.3128 | 116.57
TrentonWind2065RCP4.5 | Trenton | Wind | RCP4.5 | 2065 | 88.0298 | 94.9576 | 102.2888 | 109.5722 | 116.874
TrentonWind2070RCP4.5 | Trenton | Wind | RCP4.5 | 2070 | 88.1536 | 95.1229 | 102.5049 | 109.8315 | 117.178
TrentonWind2075RCP4.5 | Trenton | Wind | RCP4.5 | 2075 | 88.2161 | 95.209 | 102.6194 | 109.9702 | 117.3411
TrentonWind2080RCP4.5 | Trenton | Wind | RCP4.5 | 2080 | 88.2786 | 95.2951 | 102.7338 | 110.1089 | 117.5042
TrentonWind2085RCP4.5 | Trenton | Wind | RCP4.5 | 2085 | 88.3411 | 95.3812 | 102.8483 | 110.2476 | 117.6673
TrentonWind2090RCP4.5 | Trenton | Wind | RCP4.5 | 2090 | 88.4036 | 95.4673 | 102.9628 | 110.3863 | 117.8304
TrentonWind2095RCP4.5 | Trenton | Wind | RCP4.5 | 2095 | 88.4661 | 95.5534 | 103.0772 | 110.525 | 117.9936
TrentonWind2100RCP4.5 | Trenton | Wind | RCP4.5 | 2100 | 88.5286 | 95.6395 | 103.1917 | 110.6637 | 118.1567
TrentonWind2023RCP6.0 | Trenton | Wind | RCP6.0 | 2023 | 87.735 | 94.5124 | 101.6363 | 108.7616 | 115.8884
TrentonWind2025RCP6.0 | Trenton | Wind | RCP6.0 | 2025 | 87.7016 | 94.4764 | 101.6009 | 108.7238 | 115.85
TrentonWind2030RCP6.0 | Trenton | Wind | RCP6.0 | 2030 | 87.6681 | 94.4404 | 101.5656 | 108.686 | 115.8116
TrentonWind2035RCP6.0 | Trenton | Wind | RCP6.0 | 2035 | 87.6347 | 94.4043 | 101.5302 | 108.6482 | 115.7733
TrentonWind2040RCP6.0 | Trenton | Wind | RCP6.0 | 2040 | 87.6013 | 94.3683 | 101.4949 | 108.6103 | 115.7349
TrentonWind2045RCP6.0 | Trenton | Wind | RCP6.0 | 2045 | 87.5678 | 94.3323 | 101.4595 | 108.5725 | 115.6965
TrentonWind2050RCP6.0 | Trenton | Wind | RCP6.0 | 2050 | 87.6582 | 94.4616 | 101.6403 | 108.7941 | 115.9621
TrentonWind2055RCP6.0 | Trenton | Wind | RCP6.0 | 2055 | 87.7821 | 94.627 | 101.8565 | 109.0534 | 116.2661
TrentonWind2060RCP6.0 | Trenton | Wind | RCP6.0 | 2060 | 87.9059 | 94.7923 | 102.0726 | 109.3128 | 116.57
TrentonWind2065RCP6.0 | Trenton | Wind | RCP6.0 | 2065 | 88.0298 | 94.9576 | 102.2888 | 109.5722 | 116.874
TrentonWind2070RCP6.0 | Trenton | Wind | RCP6.0 | 2070 | 88.1536 | 95.1229 | 102.5049 | 109.8315 | 117.178
TrentonWind2075RCP6.0 | Trenton | Wind | RCP6.0 | 2075 | 88.2474 | 95.2521 | 102.6766 | 110.0396 | 117.4227
TrentonWind2080RCP6.0 | Trenton | Wind | RCP6.0 | 2080 | 88.3411 | 95.3812 | 102.8483 | 110.2476 | 117.6673
TrentonWind2085RCP6.0 | Trenton | Wind | RCP6.0 | 2085 | 88.4349 | 95.5104 | 103.02 | 110.4556 | 117.912
TrentonWind2090RCP6.0 | Trenton | Wind | RCP6.0 | 2090 | 88.828 | 96.0027 | 103.6361 | 111.1824 | 118.7439
TrentonWind2095RCP6.0 | Trenton | Wind | RCP6.0 | 2095 | 89.1275 | 96.3659 | 104.0805 | 111.7012 | 119.3311
TrentonWind2100RCP6.0 | Trenton | Wind | RCP6.0 | 2100 | 89.4269 | 96.7291 | 104.5249 | 112.2199 | 119.9183
TrentonWind2023RCP8.5 | Trenton | Wind | RCP8.5 | 2023 | 87.735 | 94.5124 | 101.6363 | 108.7616 | 115.8884
TrentonWind2025RCP8.5 | Trenton | Wind | RCP8.5 | 2025 | 87.6681 | 94.4404 | 101.5656 | 108.686 | 115.8116
TrentonWind2030RCP8.5 | Trenton | Wind | RCP8.5 | 2030 | 87.6013 | 94.3683 | 101.4949 | 108.6103 | 115.7349
TrentonWind2035RCP8.5 | Trenton | Wind | RCP8.5 | 2035 | 87.5344 | 94.2963 | 101.4242 | 108.5347 | 115.6581
TrentonWind2040RCP8.5 | Trenton | Wind | RCP8.5 | 2040 | 87.7408 | 94.5719 | 101.7844 | 108.967 | 116.1647
TrentonWind2045RCP8.5 | Trenton | Wind | RCP8.5 | 2045 | 87.9472 | 94.8474 | 102.1447 | 109.3993 | 116.6714
TrentonWind2050RCP8.5 | Trenton | Wind | RCP8.5 | 2050 | 88.2786 | 95.2951 | 102.7338 | 110.1089 | 117.5042
TrentonWind2055RCP8.5 | Trenton | Wind | RCP8.5 | 2055 | 88.4036 | 95.4673 | 102.9628 | 110.3863 | 117.8304
TrentonWind2060RCP8.5 | Trenton | Wind | RCP8.5 | 2060 | 88.828 | 96.0027 | 103.6361 | 111.1824 | 118.7439
TrentonWind2065RCP8.5 | Trenton | Wind | RCP8.5 | 2065 | 89.1275 | 96.3659 | 104.0805 | 111.7012 | 119.3311
TrentonWind2070RCP8.5 | Trenton | Wind | RCP8.5 | 2070 | 89.3455 | 96.6383 | 104.4205 | 112.1046 | 119.7955
TrentonWind2075RCP8.5 | Trenton | Wind | RCP8.5 | 2075 | 89.2641 | 96.5475 | 104.3162 | 111.9893 | 119.6727
TrentonWind2080RCP8.5 | Trenton | Wind | RCP8.5 | 2080 | 89.1827 | 96.4567 | 104.2118 | 111.8741 | 119.5499
TrentonWind2085RCP8.5 | Trenton | Wind | RCP8.5 | 2085 | 89.3964 | 96.7808 | 104.6764 | 112.4522 | 120.2465
TrentonWind2090RCP8.5 | Trenton | Wind | RCP8.5 | 2090 | 89.61 | 97.1048 | 105.141 | 113.0304 | 120.9431
TrentonWind2095RCP8.5 | Trenton | Wind | RCP8.5 | 2095 | 89.61 | 97.1048 | 105.141 | 113.0304 | 120.9431
TrentonWind2100RCP8.5 | Trenton | Wind | RCP8.5 | 2100 | 89.61 | 97.1048 | 105.141 | 113.0304 | 120.9431
Trout CreekIce Accretion2023RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2023 | 15.5536 | 18.5704 | 22.396 | 25.3075 | 28.2467
Trout CreekIce Accretion2025RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2025 | 15.6275 | 18.6617 | 22.5097 | 25.4401 | 28.3899
Trout CreekIce Accretion2030RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2030 | 15.7015 | 18.753 | 22.6233 | 25.5727 | 28.5331
Trout CreekIce Accretion2035RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2035 | 15.7755 | 18.8443 | 22.737 | 25.7052 | 28.6763
Trout CreekIce Accretion2040RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2040 | 15.8495 | 18.9356 | 22.8507 | 25.8378 | 28.8196
Trout CreekIce Accretion2045RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2045 | 15.9235 | 19.0269 | 22.9643 | 25.9704 | 28.9628
Trout CreekIce Accretion2050RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2050 | 16.0679 | 19.2168 | 23.2144 | 26.2671 | 29.3
Trout CreekIce Accretion2055RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2055 | 16.1383 | 19.3154 | 23.3508 | 26.4312 | 29.4941
Trout CreekIce Accretion2060RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2060 | 16.2088 | 19.414 | 23.4872 | 26.5952 | 29.6881
Trout CreekIce Accretion2065RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2065 | 16.2792 | 19.5126 | 23.6236 | 26.7593 | 29.8822
Trout CreekIce Accretion2070RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2070 | 16.3496 | 19.6112 | 23.76 | 26.9234 | 30.0762
Trout CreekIce Accretion2075RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2075 | 16.3394 | 19.6173 | 23.7857 | 26.9607 | 30.1316
Trout CreekIce Accretion2080RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2080 | 16.3292 | 19.6234 | 23.8113 | 26.998 | 30.1871
Trout CreekIce Accretion2085RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2085 | 16.319 | 19.6295 | 23.837 | 27.0352 | 30.2425
Trout CreekIce Accretion2090RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2090 | 16.3088 | 19.6356 | 23.8627 | 27.0725 | 30.298
Trout CreekIce Accretion2095RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2095 | 16.2986 | 19.6417 | 23.8883 | 27.1098 | 30.3534
Trout CreekIce Accretion2100RCP4.5 | Trout Creek | Ice Accretion | RCP4.5 | 2100 | 16.2884 | 19.6478 | 23.914 | 27.1471 | 30.4088
Trout CreekIce Accretion2023RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2023 | 15.5536 | 18.5704 | 22.396 | 25.3075 | 28.2467
Trout CreekIce Accretion2025RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2025 | 15.6275 | 18.6617 | 22.5097 | 25.4401 | 28.3899
Trout CreekIce Accretion2030RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2030 | 15.7015 | 18.753 | 22.6233 | 25.5727 | 28.5331
Trout CreekIce Accretion2035RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2035 | 15.7755 | 18.8443 | 22.737 | 25.7052 | 28.6763
Trout CreekIce Accretion2040RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2040 | 15.8495 | 18.9356 | 22.8507 | 25.8378 | 28.8196
Trout CreekIce Accretion2045RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2045 | 15.9235 | 19.0269 | 22.9643 | 25.9704 | 28.9628
Trout CreekIce Accretion2050RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2050 | 16.0679 | 19.2168 | 23.2144 | 26.2671 | 29.3
Trout CreekIce Accretion2055RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2055 | 16.1383 | 19.3154 | 23.3508 | 26.4312 | 29.4941
Trout CreekIce Accretion2060RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2060 | 16.2088 | 19.414 | 23.4872 | 26.5952 | 29.6881
Trout CreekIce Accretion2065RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2065 | 16.2792 | 19.5126 | 23.6236 | 26.7593 | 29.8822
Trout CreekIce Accretion2070RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2070 | 16.3496 | 19.6112 | 23.76 | 26.9234 | 30.0762
Trout CreekIce Accretion2075RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2075 | 16.3343 | 19.6204 | 23.7985 | 26.9793 | 30.1594
Trout CreekIce Accretion2080RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2080 | 16.319 | 19.6295 | 23.837 | 27.0352 | 30.2425
Trout CreekIce Accretion2085RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2085 | 16.3037 | 19.6386 | 23.8755 | 27.0912 | 30.3257
Trout CreekIce Accretion2090RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2090 | 16.2373 | 19.6052 | 23.8773 | 27.114 | 30.3811
Trout CreekIce Accretion2095RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2095 | 16.1863 | 19.5625 | 23.8407 | 27.0808 | 30.3534
Trout CreekIce Accretion2100RCP6.0 | Trout Creek | Ice Accretion | RCP6.0 | 2100 | 16.1353 | 19.5199 | 23.804 | 27.0477 | 30.3257
Trout CreekIce Accretion2023RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2023 | 15.5536 | 18.5704 | 22.396 | 25.3075 | 28.2467
Trout CreekIce Accretion2025RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2025 | 15.7015 | 18.753 | 22.6233 | 25.5727 | 28.5331
Trout CreekIce Accretion2030RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2030 | 15.8495 | 18.9356 | 22.8507 | 25.8378 | 28.8196
Trout CreekIce Accretion2035RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2035 | 15.9975 | 19.1182 | 23.078 | 26.103 | 29.106
Trout CreekIce Accretion2040RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2040 | 16.1149 | 19.2826 | 23.3053 | 26.3765 | 29.4294
Trout CreekIce Accretion2045RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2045 | 16.2322 | 19.4469 | 23.5327 | 26.6499 | 29.7528
Trout CreekIce Accretion2050RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2050 | 16.3292 | 19.6234 | 23.8113 | 26.998 | 30.1871
Trout CreekIce Accretion2055RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2055 | 16.3088 | 19.6356 | 23.8627 | 27.0725 | 30.298
Trout CreekIce Accretion2060RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2060 | 16.2373 | 19.6052 | 23.8773 | 27.114 | 30.3811
Trout CreekIce Accretion2065RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2065 | 16.1863 | 19.5625 | 23.8407 | 27.0808 | 30.3534
Trout CreekIce Accretion2070RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2070 | 15.8852 | 19.2217 | 23.4447 | 26.6582 | 29.8822
Trout CreekIce Accretion2075RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2075 | 15.6352 | 18.9234 | 23.0853 | 26.2687 | 29.4386
Trout CreekIce Accretion2080RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2080 | 15.3852 | 18.6252 | 22.726 | 25.8793 | 28.9951
Trout CreekIce Accretion2085RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2085 | 15.1402 | 18.3696 | 22.451 | 25.5809 | 28.6902
Trout CreekIce Accretion2090RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2090 | 14.8953 | 18.1139 | 22.176 | 25.2826 | 28.3853
Trout CreekIce Accretion2095RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2095 | 14.8953 | 18.1139 | 22.176 | 25.2826 | 28.3853
Trout CreekIce Accretion2100RCP8.5 | Trout Creek | Ice Accretion | RCP8.5 | 2100 | 14.8953 | 18.1139 | 22.176 | 25.2826 | 28.3853
Trout CreekWind2023RCP4.5 | Trout Creek | Wind | RCP4.5 | 2023 | 69.6036 | 74.9803 | 80.64 | 86.3019 | 91.957
Trout CreekWind2025RCP4.5 | Trout Creek | Wind | RCP4.5 | 2025 | 69.6773 | 75.0733 | 80.7573 | 86.4389 | 92.115
Trout CreekWind2030RCP4.5 | Trout Creek | Wind | RCP4.5 | 2030 | 69.751 | 75.1663 | 80.8747 | 86.5758 | 92.2731
Trout CreekWind2035RCP4.5 | Trout Creek | Wind | RCP4.5 | 2035 | 69.8246 | 75.2593 | 80.992 | 86.7128 | 92.4312
Trout CreekWind2040RCP4.5 | Trout Creek | Wind | RCP4.5 | 2040 | 69.8983 | 75.3523 | 81.1093 | 86.8498 | 92.5893
Trout CreekWind2045RCP4.5 | Trout Creek | Wind | RCP4.5 | 2045 | 69.972 | 75.4453 | 81.2267 | 86.9867 | 92.7474
Trout CreekWind2050RCP4.5 | Trout Creek | Wind | RCP4.5 | 2050 | 69.9904 | 75.4609 | 81.2368 | 86.9936 | 92.7504
Trout CreekWind2055RCP4.5 | Trout Creek | Wind | RCP4.5 | 2055 | 69.9352 | 75.3836 | 81.1296 | 86.8635 | 92.5954
Trout CreekWind2060RCP4.5 | Trout Creek | Wind | RCP4.5 | 2060 | 69.8799 | 75.3062 | 81.0224 | 86.7333 | 92.4403
Trout CreekWind2065RCP4.5 | Trout Creek | Wind | RCP4.5 | 2065 | 69.8246 | 75.2288 | 80.9152 | 86.6032 | 92.2853
Trout CreekWind2070RCP4.5 | Trout Creek | Wind | RCP4.5 | 2070 | 69.7694 | 75.1514 | 80.808 | 86.4731 | 92.1302
Trout CreekWind2075RCP4.5 | Trout Creek | Wind | RCP4.5 | 2075 | 69.8603 | 75.268 | 80.956 | 86.6457 | 92.3309
Trout CreekWind2080RCP4.5 | Trout Creek | Wind | RCP4.5 | 2080 | 69.9513 | 75.3846 | 81.104 | 86.8184 | 92.5315
Trout CreekWind2085RCP4.5 | Trout Creek | Wind | RCP4.5 | 2085 | 70.0422 | 75.5011 | 81.252 | 86.991 | 92.7322
Trout CreekWind2090RCP4.5 | Trout Creek | Wind | RCP4.5 | 2090 | 70.1332 | 75.6177 | 81.4 | 87.1636 | 92.9328
Trout CreekWind2095RCP4.5 | Trout Creek | Wind | RCP4.5 | 2095 | 70.2241 | 75.7342 | 81.548 | 87.3363 | 93.1334
Trout CreekWind2100RCP4.5 | Trout Creek | Wind | RCP4.5 | 2100 | 70.3151 | 75.8508 | 81.696 | 87.5089 | 93.3341
Trout CreekWind2023RCP6.0 | Trout Creek | Wind | RCP6.0 | 2023 | 69.6036 | 74.9803 | 80.64 | 86.3019 | 91.957
Trout CreekWind2025RCP6.0 | Trout Creek | Wind | RCP6.0 | 2025 | 69.6773 | 75.0733 | 80.7573 | 86.4389 | 92.115
Trout CreekWind2030RCP6.0 | Trout Creek | Wind | RCP6.0 | 2030 | 69.751 | 75.1663 | 80.8747 | 86.5758 | 92.2731
Trout CreekWind2035RCP6.0 | Trout Creek | Wind | RCP6.0 | 2035 | 69.8246 | 75.2593 | 80.992 | 86.7128 | 92.4312
Trout CreekWind2040RCP6.0 | Trout Creek | Wind | RCP6.0 | 2040 | 69.8983 | 75.3523 | 81.1093 | 86.8498 | 92.5893
Trout CreekWind2045RCP6.0 | Trout Creek | Wind | RCP6.0 | 2045 | 69.972 | 75.4453 | 81.2267 | 86.9867 | 92.7474
Trout CreekWind2050RCP6.0 | Trout Creek | Wind | RCP6.0 | 2050 | 69.9904 | 75.4609 | 81.2368 | 86.9936 | 92.7504
Trout CreekWind2055RCP6.0 | Trout Creek | Wind | RCP6.0 | 2055 | 69.9352 | 75.3836 | 81.1296 | 86.8635 | 92.5954
Trout CreekWind2060RCP6.0 | Trout Creek | Wind | RCP6.0 | 2060 | 69.8799 | 75.3062 | 81.0224 | 86.7333 | 92.4403
Trout CreekWind2065RCP6.0 | Trout Creek | Wind | RCP6.0 | 2065 | 69.8246 | 75.2288 | 80.9152 | 86.6032 | 92.2853
Trout CreekWind2070RCP6.0 | Trout Creek | Wind | RCP6.0 | 2070 | 69.7694 | 75.1514 | 80.808 | 86.4731 | 92.1302
Trout CreekWind2075RCP6.0 | Trout Creek | Wind | RCP6.0 | 2075 | 69.9058 | 75.3263 | 81.03 | 86.7321 | 92.4312
Trout CreekWind2080RCP6.0 | Trout Creek | Wind | RCP6.0 | 2080 | 70.0422 | 75.5011 | 81.252 | 86.991 | 92.7322
Trout CreekWind2085RCP6.0 | Trout Creek | Wind | RCP6.0 | 2085 | 70.1787 | 75.676 | 81.474 | 87.2499 | 93.0331
Trout CreekWind2090RCP6.0 | Trout Creek | Wind | RCP6.0 | 2090 | 70.1792 | 75.6698 | 81.464 | 87.235 | 93.0149
Trout CreekWind2095RCP6.0 | Trout Creek | Wind | RCP6.0 | 2095 | 70.0434 | 75.4887 | 81.232 | 86.961 | 92.6957
Trout CreekWind2100RCP6.0 | Trout Creek | Wind | RCP6.0 | 2100 | 69.9075 | 75.3077 | 81 | 86.6871 | 92.3765
Trout CreekWind2023RCP8.5 | Trout Creek | Wind | RCP8.5 | 2023 | 69.6036 | 74.9803 | 80.64 | 86.3019 | 91.957
Trout CreekWind2025RCP8.5 | Trout Creek | Wind | RCP8.5 | 2025 | 69.751 | 75.1663 | 80.8747 | 86.5758 | 92.2731
Trout CreekWind2030RCP8.5 | Trout Creek | Wind | RCP8.5 | 2030 | 69.8983 | 75.3523 | 81.1093 | 86.8498 | 92.5893
Trout CreekWind2035RCP8.5 | Trout Creek | Wind | RCP8.5 | 2035 | 70.0457 | 75.5383 | 81.344 | 87.1237 | 92.9054
Trout CreekWind2040RCP8.5 | Trout Creek | Wind | RCP8.5 | 2040 | 69.9536 | 75.4094 | 81.1653 | 86.9068 | 92.647
Trout CreekWind2045RCP8.5 | Trout Creek | Wind | RCP8.5 | 2045 | 69.8615 | 75.2804 | 80.9867 | 86.69 | 92.3886
Trout CreekWind2050RCP8.5 | Trout Creek | Wind | RCP8.5 | 2050 | 69.9513 | 75.3846 | 81.104 | 86.8184 | 92.5315
Trout CreekWind2055RCP8.5 | Trout Creek | Wind | RCP8.5 | 2055 | 70.1332 | 75.6177 | 81.4 | 87.1636 | 92.9328
Trout CreekWind2060RCP8.5 | Trout Creek | Wind | RCP8.5 | 2060 | 70.1792 | 75.6698 | 81.464 | 87.235 | 93.0149
Trout CreekWind2065RCP8.5 | Trout Creek | Wind | RCP8.5 | 2065 | 70.0434 | 75.4887 | 81.232 | 86.961 | 92.6957
Trout CreekWind2070RCP8.5 | Trout Creek | Wind | RCP8.5 | 2070 | 70.1263 | 75.5656 | 81.3013 | 87.0267 | 92.7565
Trout CreekWind2075RCP8.5 | Trout Creek | Wind | RCP8.5 | 2075 | 70.345 | 75.8235 | 81.6027 | 87.3662 | 93.1365
Trout CreekWind2080RCP8.5 | Trout Creek | Wind | RCP8.5 | 2080 | 70.5638 | 76.0814 | 81.904 | 87.7058 | 93.5165
Trout CreekWind2085RCP8.5 | Trout Creek | Wind | RCP8.5 | 2085 | 70.6018 | 76.0814 | 81.856 | 87.6202 | 93.3888
Trout CreekWind2090RCP8.5 | Trout Creek | Wind | RCP8.5 | 2090 | 70.6398 | 76.0814 | 81.808 | 87.5346 | 93.2611
Trout CreekWind2095RCP8.5 | Trout Creek | Wind | RCP8.5 | 2095 | 70.6398 | 76.0814 | 81.808 | 87.5346 | 93.2611
Trout CreekWind2100RCP8.5 | Trout Creek | Wind | RCP8.5 | 2100 | 70.6398 | 76.0814 | 81.808 | 87.5346 | 93.2611
UxbridgeIce Accretion2023RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
UxbridgeIce Accretion2025RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
UxbridgeIce Accretion2030RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
UxbridgeIce Accretion2035RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
UxbridgeIce Accretion2040RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
UxbridgeIce Accretion2045RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
UxbridgeIce Accretion2050RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
UxbridgeIce Accretion2055RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
UxbridgeIce Accretion2060RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
UxbridgeIce Accretion2065RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
UxbridgeIce Accretion2070RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
UxbridgeIce Accretion2075RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2075 | 17.2744 | 20.8814 | 25.4167 | 28.8762 | 32.34
UxbridgeIce Accretion2080RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2080 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
UxbridgeIce Accretion2085RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2085 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
UxbridgeIce Accretion2090RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2090 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
UxbridgeIce Accretion2095RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2095 | 17.2048 | 20.9091 | 25.5833 | 29.121 | 32.676
UxbridgeIce Accretion2100RCP4.5 | Uxbridge | Ice Accretion | RCP4.5 | 2100 | 17.1874 | 20.916 | 25.625 | 29.1822 | 32.76
UxbridgeIce Accretion2023RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
UxbridgeIce Accretion2025RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2025 | 17.4309 | 20.8468 | 25.1625 | 28.4713 | 31.7625
UxbridgeIce Accretion2030RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2030 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
UxbridgeIce Accretion2035RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2035 | 17.5353 | 20.999 | 25.3875 | 28.7444 | 32.0985
UxbridgeIce Accretion2040RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2040 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
UxbridgeIce Accretion2045RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2045 | 17.6397 | 21.1512 | 25.6125 | 29.0175 | 32.4345
UxbridgeIce Accretion2050RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2050 | 17.6119 | 21.1567 | 25.655 | 29.0862 | 32.5332
UxbridgeIce Accretion2055RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2055 | 17.5318 | 21.0861 | 25.585 | 29.0184 | 32.4639
UxbridgeIce Accretion2060RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2060 | 17.4518 | 21.0156 | 25.515 | 28.9506 | 32.3946
UxbridgeIce Accretion2065RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2065 | 17.3718 | 20.9451 | 25.445 | 28.8828 | 32.3253
UxbridgeIce Accretion2070RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2070 | 17.2918 | 20.8745 | 25.375 | 28.815 | 32.256
UxbridgeIce Accretion2075RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2075 | 17.2657 | 20.8849 | 25.4375 | 28.9068 | 32.382
UxbridgeIce Accretion2080RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2080 | 17.2396 | 20.8953 | 25.5 | 28.9986 | 32.508
UxbridgeIce Accretion2085RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2085 | 17.2135 | 20.9056 | 25.5625 | 29.0904 | 32.634
UxbridgeIce Accretion2090RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2090 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
UxbridgeIce Accretion2095RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2095 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
UxbridgeIce Accretion2100RCP6.0 | Uxbridge | Ice Accretion | RCP6.0 | 2100 | 16.2654 | 19.8992 | 24.5 | 27.9957 | 31.4685
UxbridgeIce Accretion2023RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2023 | 17.3788 | 20.7707 | 25.05 | 28.3347 | 31.5945
UxbridgeIce Accretion2025RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2025 | 17.4831 | 20.9229 | 25.275 | 28.6078 | 31.9305
UxbridgeIce Accretion2030RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2030 | 17.5875 | 21.0751 | 25.5 | 28.8809 | 32.2665
UxbridgeIce Accretion2035RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2035 | 17.6919 | 21.2272 | 25.725 | 29.154 | 32.6025
UxbridgeIce Accretion2040RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2040 | 17.5585 | 21.1097 | 25.6083 | 29.041 | 32.487
UxbridgeIce Accretion2045RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2045 | 17.4251 | 20.9921 | 25.4917 | 28.928 | 32.3715
UxbridgeIce Accretion2050RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2050 | 17.257 | 20.8883 | 25.4583 | 28.9374 | 32.424
UxbridgeIce Accretion2055RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2055 | 17.2222 | 20.9022 | 25.5417 | 29.0598 | 32.592
UxbridgeIce Accretion2060RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2060 | 16.8801 | 20.5771 | 25.25 | 28.7867 | 32.3295
UxbridgeIce Accretion2065RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2065 | 16.5727 | 20.2382 | 24.875 | 28.3912 | 31.899
UxbridgeIce Accretion2070RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2070 | 15.9987 | 19.6226 | 24.2083 | 27.685 | 31.143
UxbridgeIce Accretion2075RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2075 | 15.7319 | 19.3459 | 23.9167 | 27.3742 | 30.8175
UxbridgeIce Accretion2080RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2080 | 15.4652 | 19.0693 | 23.625 | 27.0635 | 30.492
UxbridgeIce Accretion2085RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2085 | 14.8911 | 18.426 | 22.8875 | 26.2584 | 29.6258
UxbridgeIce Accretion2090RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2090 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
UxbridgeIce Accretion2095RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2095 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
UxbridgeIce Accretion2100RCP8.5 | Uxbridge | Ice Accretion | RCP8.5 | 2100 | 14.317 | 17.7828 | 22.15 | 25.4532 | 28.7595
UxbridgeWind2023RCP4.5 | Uxbridge | Wind | RCP4.5 | 2023 | 76.488 | 82.3883 | 88.5896 | 94.7909 | 101.0022
UxbridgeWind2025RCP4.5 | Uxbridge | Wind | RCP4.5 | 2025 | 76.5222 | 82.4333 | 88.6497 | 94.8646 | 101.0874
UxbridgeWind2030RCP4.5 | Uxbridge | Wind | RCP4.5 | 2030 | 76.5564 | 82.4784 | 88.7099 | 94.9384 | 101.1727
UxbridgeWind2035RCP4.5 | Uxbridge | Wind | RCP4.5 | 2035 | 76.5905 | 82.5234 | 88.77 | 95.0121 | 101.258
UxbridgeWind2040RCP4.5 | Uxbridge | Wind | RCP4.5 | 2040 | 76.6247 | 82.5684 | 88.8301 | 95.0859 | 101.3433
UxbridgeWind2045RCP4.5 | Uxbridge | Wind | RCP4.5 | 2045 | 76.6589 | 82.6134 | 88.8903 | 95.1597 | 101.4285
UxbridgeWind2050RCP4.5 | Uxbridge | Wind | RCP4.5 | 2050 | 76.7615 | 82.7386 | 89.0437 | 95.337 | 101.6302
UxbridgeWind2055RCP4.5 | Uxbridge | Wind | RCP4.5 | 2055 | 76.8299 | 82.8188 | 89.137 | 95.4406 | 101.7466
UxbridgeWind2060RCP4.5 | Uxbridge | Wind | RCP4.5 | 2060 | 76.8983 | 82.899 | 89.2302 | 95.5442 | 101.8629
UxbridgeWind2065RCP4.5 | Uxbridge | Wind | RCP4.5 | 2065 | 76.9667 | 82.9792 | 89.3235 | 95.6477 | 101.9793
UxbridgeWind2070RCP4.5 | Uxbridge | Wind | RCP4.5 | 2070 | 77.0351 | 83.0594 | 89.4168 | 95.7513 | 102.0957
UxbridgeWind2075RCP4.5 | Uxbridge | Wind | RCP4.5 | 2075 | 77.1098 | 83.1522 | 89.5312 | 95.8863 | 102.2495
UxbridgeWind2080RCP4.5 | Uxbridge | Wind | RCP4.5 | 2080 | 77.1845 | 83.2449 | 89.6456 | 96.0212 | 102.4033
UxbridgeWind2085RCP4.5 | Uxbridge | Wind | RCP4.5 | 2085 | 77.2592 | 83.3377 | 89.76 | 96.1562 | 102.5571
UxbridgeWind2090RCP4.5 | Uxbridge | Wind | RCP4.5 | 2090 | 77.3339 | 83.4304 | 89.8744 | 96.2912 | 102.711
UxbridgeWind2095RCP4.5 | Uxbridge | Wind | RCP4.5 | 2095 | 77.4087 | 83.5232 | 89.9888 | 96.4261 | 102.8648
UxbridgeWind2100RCP4.5 | Uxbridge | Wind | RCP4.5 | 2100 | 77.4834 | 83.6159 | 90.1032 | 96.5611 | 103.0186
UxbridgeWind2023RCP6.0 | Uxbridge | Wind | RCP6.0 | 2023 | 76.488 | 82.3883 | 88.5896 | 94.7909 | 101.0022
UxbridgeWind2025RCP6.0 | Uxbridge | Wind | RCP6.0 | 2025 | 76.5222 | 82.4333 | 88.6497 | 94.8646 | 101.0874
UxbridgeWind2030RCP6.0 | Uxbridge | Wind | RCP6.0 | 2030 | 76.5564 | 82.4784 | 88.7099 | 94.9384 | 101.1727
UxbridgeWind2035RCP6.0 | Uxbridge | Wind | RCP6.0 | 2035 | 76.5905 | 82.5234 | 88.77 | 95.0121 | 101.258
UxbridgeWind2040RCP6.0 | Uxbridge | Wind | RCP6.0 | 2040 | 76.6247 | 82.5684 | 88.8301 | 95.0859 | 101.3433
UxbridgeWind2045RCP6.0 | Uxbridge | Wind | RCP6.0 | 2045 | 76.6589 | 82.6134 | 88.8903 | 95.1597 | 101.4285
UxbridgeWind2050RCP6.0 | Uxbridge | Wind | RCP6.0 | 2050 | 76.7615 | 82.7386 | 89.0437 | 95.337 | 101.6302
UxbridgeWind2055RCP6.0 | Uxbridge | Wind | RCP6.0 | 2055 | 76.8299 | 82.8188 | 89.137 | 95.4406 | 101.7466
UxbridgeWind2060RCP6.0 | Uxbridge | Wind | RCP6.0 | 2060 | 76.8983 | 82.899 | 89.2302 | 95.5442 | 101.8629
UxbridgeWind2065RCP6.0 | Uxbridge | Wind | RCP6.0 | 2065 | 76.9667 | 82.9792 | 89.3235 | 95.6477 | 101.9793
UxbridgeWind2070RCP6.0 | Uxbridge | Wind | RCP6.0 | 2070 | 77.0351 | 83.0594 | 89.4168 | 95.7513 | 102.0957
UxbridgeWind2075RCP6.0 | Uxbridge | Wind | RCP6.0 | 2075 | 77.1471 | 83.1985 | 89.5884 | 95.9537 | 102.3264
UxbridgeWind2080RCP6.0 | Uxbridge | Wind | RCP6.0 | 2080 | 77.2592 | 83.3377 | 89.76 | 96.1562 | 102.5571
UxbridgeWind2085RCP6.0 | Uxbridge | Wind | RCP6.0 | 2085 | 77.3713 | 83.4768 | 89.9316 | 96.3586 | 102.7879
UxbridgeWind2090RCP6.0 | Uxbridge | Wind | RCP6.0 | 2090 | 77.7291 | 83.8969 | 90.4317 | 96.9252 | 103.4232
UxbridgeWind2095RCP6.0 | Uxbridge | Wind | RCP6.0 | 2095 | 77.9748 | 84.1779 | 90.7603 | 97.2893 | 103.8279
UxbridgeWind2100RCP6.0 | Uxbridge | Wind | RCP6.0 | 2100 | 78.2205 | 84.4589 | 91.0888 | 97.6533 | 104.2325
UxbridgeWind2023RCP8.5 | Uxbridge | Wind | RCP8.5 | 2023 | 76.488 | 82.3883 | 88.5896 | 94.7909 | 101.0022
UxbridgeWind2025RCP8.5 | Uxbridge | Wind | RCP8.5 | 2025 | 76.5564 | 82.4784 | 88.7099 | 94.9384 | 101.1727
UxbridgeWind2030RCP8.5 | Uxbridge | Wind | RCP8.5 | 2030 | 76.6247 | 82.5684 | 88.8301 | 95.0859 | 101.3433
UxbridgeWind2035RCP8.5 | Uxbridge | Wind | RCP8.5 | 2035 | 76.6931 | 82.6584 | 88.9504 | 95.2334 | 101.5138
UxbridgeWind2040RCP8.5 | Uxbridge | Wind | RCP8.5 | 2040 | 76.8071 | 82.7921 | 89.1059 | 95.4061 | 101.7078
UxbridgeWind2045RCP8.5 | Uxbridge | Wind | RCP8.5 | 2045 | 76.9211 | 82.9257 | 89.2613 | 95.5787 | 101.9017
UxbridgeWind2050RCP8.5 | Uxbridge | Wind | RCP8.5 | 2050 | 77.1845 | 83.2449 | 89.6456 | 96.0212 | 102.4033
UxbridgeWind2055RCP8.5 | Uxbridge | Wind | RCP8.5 | 2055 | 77.3339 | 83.4304 | 89.8744 | 96.2912 | 102.711
UxbridgeWind2060RCP8.5 | Uxbridge | Wind | RCP8.5 | 2060 | 77.7291 | 83.8969 | 90.4317 | 96.9252 | 103.4232
UxbridgeWind2065RCP8.5 | Uxbridge | Wind | RCP8.5 | 2065 | 77.9748 | 84.1779 | 90.7603 | 97.2893 | 103.8279
UxbridgeWind2070RCP8.5 | Uxbridge | Wind | RCP8.5 | 2070 | 78.3066 | 84.5707 | 91.2267 | 97.8165 | 104.4231
UxbridgeWind2075RCP8.5 | Uxbridge | Wind | RCP8.5 | 2075 | 78.3927 | 84.6826 | 91.3645 | 97.9798 | 104.6137
UxbridgeWind2080RCP8.5 | Uxbridge | Wind | RCP8.5 | 2080 | 78.4788 | 84.7944 | 91.5024 | 98.143 | 104.8043
UxbridgeWind2085RCP8.5 | Uxbridge | Wind | RCP8.5 | 2085 | 78.6802 | 85.0768 | 91.8984 | 98.6279 | 105.3811
UxbridgeWind2090RCP8.5 | Uxbridge | Wind | RCP8.5 | 2090 | 78.8815 | 85.3591 | 92.2944 | 99.1128 | 105.958
UxbridgeWind2095RCP8.5 | Uxbridge | Wind | RCP8.5 | 2095 | 78.8815 | 85.3591 | 92.2944 | 99.1128 | 105.958
UxbridgeWind2100RCP8.5 | Uxbridge | Wind | RCP8.5 | 2100 | 78.8815 | 85.3591 | 92.2944 | 99.1128 | 105.958
Vaughan (Woodbridge)Ice Accretion2023RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
Vaughan (Woodbridge)Ice Accretion2025RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2025 | 17.4222 | 20.9229 | 25.3542 | 28.7444 | 32.1247
Vaughan (Woodbridge)Ice Accretion2030RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2030 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
Vaughan (Woodbridge)Ice Accretion2035RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2035 | 17.5092 | 21.0612 | 25.5625 | 28.9986 | 32.4292
Vaughan (Woodbridge)Ice Accretion2040RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2040 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
Vaughan (Woodbridge)Ice Accretion2045RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2045 | 17.5962 | 21.1996 | 25.7708 | 29.2529 | 32.7338
Vaughan (Woodbridge)Ice Accretion2050RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2050 | 17.5214 | 21.1484 | 25.745 | 29.2444 | 32.7411
Vaughan (Woodbridge)Ice Accretion2055RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2055 | 17.4031 | 21.0281 | 25.615 | 29.1088 | 32.5962
Vaughan (Woodbridge)Ice Accretion2060RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2060 | 17.2848 | 20.9077 | 25.485 | 28.9732 | 32.4513
Vaughan (Woodbridge)Ice Accretion2065RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2065 | 17.1665 | 20.7873 | 25.355 | 28.8376 | 32.3064
Vaughan (Woodbridge)Ice Accretion2070RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2070 | 17.0482 | 20.667 | 25.225 | 28.702 | 32.1615
Vaughan (Woodbridge)Ice Accretion2075RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2075 | 17.0105 | 20.6497 | 25.2333 | 28.7255 | 32.2035
Vaughan (Woodbridge)Ice Accretion2080RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2080 | 16.9728 | 20.6324 | 25.2417 | 28.7491 | 32.2455
Vaughan (Woodbridge)Ice Accretion2085RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2085 | 16.9352 | 20.6151 | 25.25 | 28.7726 | 32.2875
Vaughan (Woodbridge)Ice Accretion2090RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2090 | 16.8975 | 20.5978 | 25.2583 | 28.7962 | 32.3295
Vaughan (Woodbridge)Ice Accretion2095RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2095 | 16.8598 | 20.5805 | 25.2667 | 28.8197 | 32.3715
Vaughan (Woodbridge)Ice Accretion2100RCP4.5 | Vaughan (Woodbridge) | Ice Accretion | RCP4.5 | 2100 | 16.8221 | 20.5633 | 25.275 | 28.8432 | 32.4135
Vaughan (Woodbridge)Ice Accretion2023RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
Vaughan (Woodbridge)Ice Accretion2025RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2025 | 17.4222 | 20.9229 | 25.3542 | 28.7444 | 32.1247
Vaughan (Woodbridge)Ice Accretion2030RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2030 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
Vaughan (Woodbridge)Ice Accretion2035RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2035 | 17.5092 | 21.0612 | 25.5625 | 28.9986 | 32.4292
Vaughan (Woodbridge)Ice Accretion2040RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2040 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
Vaughan (Woodbridge)Ice Accretion2045RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2045 | 17.5962 | 21.1996 | 25.7708 | 29.2529 | 32.7338
Vaughan (Woodbridge)Ice Accretion2050RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2050 | 17.5214 | 21.1484 | 25.745 | 29.2444 | 32.7411
Vaughan (Woodbridge)Ice Accretion2055RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2055 | 17.4031 | 21.0281 | 25.615 | 29.1088 | 32.5962
Vaughan (Woodbridge)Ice Accretion2060RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2060 | 17.2848 | 20.9077 | 25.485 | 28.9732 | 32.4513
Vaughan (Woodbridge)Ice Accretion2065RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2065 | 17.1665 | 20.7873 | 25.355 | 28.8376 | 32.3064
Vaughan (Woodbridge)Ice Accretion2070RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2070 | 17.0482 | 20.667 | 25.225 | 28.702 | 32.1615
Vaughan (Woodbridge)Ice Accretion2075RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2075 | 16.9917 | 20.6411 | 25.2375 | 28.7373 | 32.2245
Vaughan (Woodbridge)Ice Accretion2080RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2080 | 16.9352 | 20.6151 | 25.25 | 28.7726 | 32.2875
Vaughan (Woodbridge)Ice Accretion2085RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2085 | 16.8786 | 20.5892 | 25.2625 | 28.8079 | 32.3505
Vaughan (Woodbridge)Ice Accretion2090RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2090 | 16.5147 | 20.2382 | 24.925 | 28.4854 | 32.0355
Vaughan (Woodbridge)Ice Accretion2095RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2095 | 16.2074 | 19.9131 | 24.575 | 28.1276 | 31.6575
Vaughan (Woodbridge)Ice Accretion2100RCP6.0 | Vaughan (Woodbridge) | Ice Accretion | RCP6.0 | 2100 | 15.9001 | 19.588 | 24.225 | 27.7697 | 31.2795
Vaughan (Woodbridge)Ice Accretion2023RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2023 | 17.3788 | 20.8537 | 25.25 | 28.6172 | 31.9725
Vaughan (Woodbridge)Ice Accretion2025RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2025 | 17.4657 | 20.9921 | 25.4583 | 28.8715 | 32.277
Vaughan (Woodbridge)Ice Accretion2030RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2030 | 17.5527 | 21.1304 | 25.6667 | 29.1257 | 32.5815
Vaughan (Woodbridge)Ice Accretion2035RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2035 | 17.6397 | 21.2687 | 25.875 | 29.38 | 32.886
Vaughan (Woodbridge)Ice Accretion2040RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2040 | 17.4425 | 21.0682 | 25.6583 | 29.154 | 32.6445
Vaughan (Woodbridge)Ice Accretion2045RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2045 | 17.2454 | 20.8676 | 25.4417 | 28.928 | 32.403
Vaughan (Woodbridge)Ice Accretion2050RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2050 | 16.9728 | 20.6324 | 25.2417 | 28.7491 | 32.2455
Vaughan (Woodbridge)Ice Accretion2055RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2055 | 16.8975 | 20.5978 | 25.2583 | 28.7962 | 32.3295
Vaughan (Woodbridge)Ice Accretion2060RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2060 | 16.5147 | 20.2382 | 24.925 | 28.4854 | 32.0355
Vaughan (Woodbridge)Ice Accretion2065RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2065 | 16.2074 | 19.9131 | 24.575 | 28.1276 | 31.6575
Vaughan (Woodbridge)Ice Accretion2070RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2070 | 15.5116 | 19.173 | 23.775 | 27.2801 | 30.765
Vaughan (Woodbridge)Ice Accretion2075RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2075 | 15.1231 | 18.758 | 23.325 | 26.7904 | 30.2505
Vaughan (Woodbridge)Ice Accretion2080RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2080 | 14.7345 | 18.343 | 22.875 | 26.3007 | 29.736
Vaughan (Woodbridge)Ice Accretion2085RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2085 | 13.9691 | 17.4404 | 21.8 | 25.1001 | 28.3972
Vaughan (Woodbridge)Ice Accretion2090RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2090 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
Vaughan (Woodbridge)Ice Accretion2095RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2095 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
Vaughan (Woodbridge)Ice Accretion2100RCP8.5 | Vaughan (Woodbridge) | Ice Accretion | RCP8.5 | 2100 | 13.2037 | 16.5377 | 20.725 | 23.8995 | 27.0585
Vaughan (Woodbridge)Wind2023RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2023 | 83.201 | 89.6103 | 96.3552 | 103.1001 | 109.8449
Vaughan (Woodbridge)Wind2025RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2025 | 83.2273 | 89.6475 | 96.4064 | 103.1634 | 109.9215
Vaughan (Woodbridge)Wind2030RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2030 | 83.2535 | 89.6847 | 96.4576 | 103.2268 | 109.9981
Vaughan (Woodbridge)Wind2035RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2035 | 83.2798 | 89.7219 | 96.5088 | 103.2901 | 110.0748
Vaughan (Woodbridge)Wind2040RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2040 | 83.306 | 89.7591 | 96.56 | 103.3534 | 110.1514
Vaughan (Woodbridge)Wind2045RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2045 | 83.3323 | 89.7963 | 96.6112 | 103.4168 | 110.228
Vaughan (Woodbridge)Wind2050RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2050 | 83.4132 | 89.8853 | 96.7104 | 103.5253 | 110.3462
Vaughan (Woodbridge)Wind2055RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2055 | 83.4679 | 89.9371 | 96.7584 | 103.5705 | 110.3878
Vaughan (Woodbridge)Wind2060RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2060 | 83.5227 | 89.9889 | 96.8064 | 103.6157 | 110.4293
Vaughan (Woodbridge)Wind2065RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2065 | 83.5774 | 90.0407 | 96.8544 | 103.6609 | 110.4709
Vaughan (Woodbridge)Wind2070RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2070 | 83.6321 | 90.0924 | 96.9024 | 103.7061 | 110.5125
Vaughan (Woodbridge)Wind2075RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2075 | 83.7122 | 90.2026 | 97.0496 | 103.8842 | 110.7223
Vaughan (Woodbridge)Wind2080RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2080 | 83.7923 | 90.3127 | 97.1968 | 104.0622 | 110.932
Vaughan (Woodbridge)Wind2085RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2085 | 83.8725 | 90.4228 | 97.344 | 104.2403 | 111.1418
Vaughan (Woodbridge)Wind2090RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2090 | 83.9526 | 90.5329 | 97.4912 | 104.4183 | 111.3516
Vaughan (Woodbridge)Wind2095RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2095 | 84.0327 | 90.643 | 97.6384 | 104.5964 | 111.5613
Vaughan (Woodbridge)Wind2100RCP4.5 | Vaughan (Woodbridge) | Wind | RCP4.5 | 2100 | 84.1129 | 90.7531 | 97.7856 | 104.7744 | 111.7711
Vaughan (Woodbridge)Wind2023RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2023 | 83.201 | 89.6103 | 96.3552 | 103.1001 | 109.8449
Vaughan (Woodbridge)Wind2025RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2025 | 83.2273 | 89.6475 | 96.4064 | 103.1634 | 109.9215
Vaughan (Woodbridge)Wind2030RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2030 | 83.2535 | 89.6847 | 96.4576 | 103.2268 | 109.9981
Vaughan (Woodbridge)Wind2035RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2035 | 83.2798 | 89.7219 | 96.5088 | 103.2901 | 110.0748
Vaughan (Woodbridge)Wind2040RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2040 | 83.306 | 89.7591 | 96.56 | 103.3534 | 110.1514
Vaughan (Woodbridge)Wind2045RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2045 | 83.3323 | 89.7963 | 96.6112 | 103.4168 | 110.228
Vaughan (Woodbridge)Wind2050RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2050 | 83.4132 | 89.8853 | 96.7104 | 103.5253 | 110.3462
Vaughan (Woodbridge)Wind2055RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2055 | 83.4679 | 89.9371 | 96.7584 | 103.5705 | 110.3878
Vaughan (Woodbridge)Wind2060RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2060 | 83.5227 | 89.9889 | 96.8064 | 103.6157 | 110.4293
Vaughan (Woodbridge)Wind2065RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2065 | 83.5774 | 90.0407 | 96.8544 | 103.6609 | 110.4709
Vaughan (Woodbridge)Wind2070RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2070 | 83.6321 | 90.0924 | 96.9024 | 103.7061 | 110.5125
Vaughan (Woodbridge)Wind2075RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2075 | 83.7523 | 90.2576 | 97.1232 | 103.9732 | 110.8272
Vaughan (Woodbridge)Wind2080RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2080 | 83.8725 | 90.4228 | 97.344 | 104.2403 | 111.1418
Vaughan (Woodbridge)Wind2085RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2085 | 83.9927 | 90.588 | 97.5648 | 104.5073 | 111.4564
Vaughan (Woodbridge)Wind2090RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2090 | 84.3919 | 91.0983 | 98.2112 | 105.2709 | 112.3402
Vaughan (Woodbridge)Wind2095RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2095 | 84.671 | 91.4436 | 98.6368 | 105.7674 | 112.9092
Vaughan (Woodbridge)Wind2100RCP6.0 | Vaughan (Woodbridge) | Wind | RCP6.0 | 2100 | 84.9501 | 91.7888 | 99.0624 | 106.2638 | 113.4783
Vaughan (Woodbridge)Wind2023RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2023 | 83.201 | 89.6103 | 96.3552 | 103.1001 | 109.8449
Vaughan (Woodbridge)Wind2025RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2025 | 83.2535 | 89.6847 | 96.4576 | 103.2268 | 109.9981
Vaughan (Woodbridge)Wind2030RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2030 | 83.306 | 89.7591 | 96.56 | 103.3534 | 110.1514
Vaughan (Woodbridge)Wind2035RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2035 | 83.3585 | 89.8335 | 96.6624 | 103.4801 | 110.3046
Vaughan (Woodbridge)Wind2040RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2040 | 83.4497 | 89.9198 | 96.7424 | 103.5555 | 110.3739
Vaughan (Woodbridge)Wind2045RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2045 | 83.5409 | 90.0061 | 96.8224 | 103.6308 | 110.4432
Vaughan (Woodbridge)Wind2050RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2050 | 83.7923 | 90.3127 | 97.1968 | 104.0622 | 110.932
Vaughan (Woodbridge)Wind2055RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2055 | 83.9526 | 90.5329 | 97.4912 | 104.4183 | 111.3516
Vaughan (Woodbridge)Wind2060RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2060 | 84.3919 | 91.0983 | 98.2112 | 105.2709 | 112.3402
Vaughan (Woodbridge)Wind2065RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2065 | 84.671 | 91.4436 | 98.6368 | 105.7674 | 112.9092
Vaughan (Woodbridge)Wind2070RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2070 | 85.1629 | 92.0745 | 99.44 | 106.7192 | 114.0109
Vaughan (Woodbridge)Wind2075RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2075 | 85.3756 | 92.3602 | 99.8176 | 107.1746 | 114.5436
Vaughan (Woodbridge)Wind2080RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2080 | 85.5884 | 92.6459 | 100.1952 | 107.63 | 115.0762
Vaughan (Woodbridge)Wind2085RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2085 | 85.6961 | 92.7887 | 100.3872 | 107.856 | 115.3443
Vaughan (Woodbridge)Wind2090RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2090 | 85.8039 | 92.9316 | 100.5792 | 108.082 | 115.6124
Vaughan (Woodbridge)Wind2095RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2095 | 85.8039 | 92.9316 | 100.5792 | 108.082 | 115.6124
Vaughan (Woodbridge)Wind2100RCP8.5 | Vaughan (Woodbridge) | Wind | RCP8.5 | 2100 | 85.8039 | 92.9316 | 100.5792 | 108.082 | 115.6124
VittoriaIce Accretion2023RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
VittoriaIce Accretion2025RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2025 | 22.9175 | 27.5192 | 33.3427 | 37.7989 | 42.2402
VittoriaIce Accretion2030RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2030 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
VittoriaIce Accretion2035RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2035 | 22.6651 | 27.2464 | 33.048 | 37.4787 | 41.8975
VittoriaIce Accretion2040RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2040 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
VittoriaIce Accretion2045RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2045 | 22.4127 | 26.9736 | 32.7533 | 37.1585 | 41.5548
VittoriaIce Accretion2050RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2050 | 21.7945 | 26.2954 | 31.9872 | 36.3223 | 40.6466
VittoriaIce Accretion2055RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2055 | 21.3024 | 25.7536 | 31.3684 | 35.6461 | 39.9097
VittoriaIce Accretion2060RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2060 | 20.8103 | 25.2117 | 30.7496 | 34.9699 | 39.1729
VittoriaIce Accretion2065RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2065 | 20.3181 | 24.6699 | 30.1308 | 34.2937 | 38.436
VittoriaIce Accretion2070RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2070 | 19.826 | 24.1281 | 29.512 | 33.6175 | 37.6992
VittoriaIce Accretion2075RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2075 | 19.5895 | 23.8647 | 29.2117 | 33.2909 | 37.3422
VittoriaIce Accretion2080RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2080 | 19.3529 | 23.6013 | 28.9113 | 32.9644 | 36.9852
VittoriaIce Accretion2085RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2085 | 19.1163 | 23.3379 | 28.611 | 32.6378 | 36.6282
VittoriaIce Accretion2090RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2090 | 18.8797 | 23.0746 | 28.3107 | 32.3112 | 36.2712
VittoriaIce Accretion2095RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2095 | 18.6431 | 22.8112 | 28.0103 | 31.9846 | 35.9142
VittoriaIce Accretion2100RCP4.5 | Vittoria | Ice Accretion | RCP4.5 | 2100 | 18.4065 | 22.5478 | 27.71 | 31.6581 | 35.5572
VittoriaIce Accretion2023RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
VittoriaIce Accretion2025RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2025 | 22.9175 | 27.5192 | 33.3427 | 37.7989 | 42.2402
VittoriaIce Accretion2030RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2030 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
VittoriaIce Accretion2035RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2035 | 22.6651 | 27.2464 | 33.048 | 37.4787 | 41.8975
VittoriaIce Accretion2040RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2040 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
VittoriaIce Accretion2045RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2045 | 22.4127 | 26.9736 | 32.7533 | 37.1585 | 41.5548
VittoriaIce Accretion2050RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2050 | 21.7945 | 26.2954 | 31.9872 | 36.3223 | 40.6466
VittoriaIce Accretion2055RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2055 | 21.3024 | 25.7536 | 31.3684 | 35.6461 | 39.9097
VittoriaIce Accretion2060RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2060 | 20.8103 | 25.2117 | 30.7496 | 34.9699 | 39.1729
VittoriaIce Accretion2065RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2065 | 20.3181 | 24.6699 | 30.1308 | 34.2937 | 38.436
VittoriaIce Accretion2070RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2070 | 19.826 | 24.1281 | 29.512 | 33.6175 | 37.6992
VittoriaIce Accretion2075RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2075 | 19.4712 | 23.733 | 29.0615 | 33.1276 | 37.1637
VittoriaIce Accretion2080RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2080 | 19.1163 | 23.3379 | 28.611 | 32.6378 | 36.6282
VittoriaIce Accretion2085RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2085 | 18.7614 | 22.9429 | 28.1605 | 32.1479 | 36.0927
VittoriaIce Accretion2090RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2090 | 17.4365 | 21.4002 | 26.3613 | 30.1341 | 33.8722
VittoriaIce Accretion2095RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2095 | 16.4665 | 20.2526 | 25.0127 | 28.6101 | 32.1871
VittoriaIce Accretion2100RCP6.0 | Vittoria | Ice Accretion | RCP6.0 | 2100 | 15.4965 | 19.1049 | 23.664 | 27.0861 | 30.5021
VittoriaIce Accretion2023RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2023 | 23.0436 | 27.6556 | 33.49 | 37.959 | 42.4116
VittoriaIce Accretion2025RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2025 | 22.7913 | 27.3828 | 33.1953 | 37.6388 | 42.0689
VittoriaIce Accretion2030RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2030 | 22.5389 | 27.11 | 32.9007 | 37.3186 | 41.7262
VittoriaIce Accretion2035RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2035 | 22.2866 | 26.8372 | 32.606 | 36.9985 | 41.3834
VittoriaIce Accretion2040RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2040 | 21.4664 | 25.9342 | 31.5747 | 35.8715 | 40.1554
VittoriaIce Accretion2045RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2045 | 20.6462 | 25.0311 | 30.5433 | 34.7445 | 38.9273
VittoriaIce Accretion2050RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2050 | 19.3529 | 23.6013 | 28.9113 | 32.9644 | 36.9852
VittoriaIce Accretion2055RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2055 | 18.8797 | 23.0746 | 28.3107 | 32.3112 | 36.2712
VittoriaIce Accretion2060RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2060 | 17.4365 | 21.4002 | 26.3613 | 30.1341 | 33.8722
VittoriaIce Accretion2065RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2065 | 16.4665 | 20.2526 | 25.0127 | 28.6101 | 32.1871
VittoriaIce Accretion2070RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2070 | 15.0312 | 18.5876 | 23.052 | 26.4073 | 29.7595
VittoriaIce Accretion2075RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2075 | 14.5659 | 18.0702 | 22.44 | 25.7286 | 29.017
VittoriaIce Accretion2080RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2080 | 14.1006 | 17.5528 | 21.828 | 25.0498 | 28.2744
VittoriaIce Accretion2085RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2085 | 13.0596 | 16.297 | 20.332 | 23.3594 | 26.3894
VittoriaIce Accretion2090RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2090 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
VittoriaIce Accretion2095RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2095 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
VittoriaIce Accretion2100RCP8.5 | Vittoria | Ice Accretion | RCP8.5 | 2100 | 12.0187 | 15.0413 | 18.836 | 21.6689 | 24.5045
VittoriaWind2023RCP4.5 | Vittoria | Wind | RCP4.5 | 2023 | 88.6477 | 95.5809 | 102.8976 | 110.1877 | 117.4893
VittoriaWind2025RCP4.5 | Vittoria | Wind | RCP4.5 | 2025 | 88.724 | 95.6821 | 103.0319 | 110.3515 | 117.6792
VittoriaWind2030RCP4.5 | Vittoria | Wind | RCP4.5 | 2030 | 88.8004 | 95.7833 | 103.1662 | 110.5152 | 117.8692
VittoriaWind2035RCP4.5 | Vittoria | Wind | RCP4.5 | 2035 | 88.8767 | 95.8845 | 103.3005 | 110.6789 | 118.0591
VittoriaWind2040RCP4.5 | Vittoria | Wind | RCP4.5 | 2040 | 88.953 | 95.9857 | 103.4348 | 110.8426 | 118.249
VittoriaWind2045RCP4.5 | Vittoria | Wind | RCP4.5 | 2045 | 89.0294 | 96.0869 | 103.5691 | 111.0063 | 118.4389
VittoriaWind2050RCP4.5 | Vittoria | Wind | RCP4.5 | 2050 | 89.185 | 96.2943 | 103.8442 | 111.3381 | 118.8289
VittoriaWind2055RCP4.5 | Vittoria | Wind | RCP4.5 | 2055 | 89.2642 | 96.4005 | 103.9849 | 111.5062 | 119.0289
VittoriaWind2060RCP4.5 | Vittoria | Wind | RCP4.5 | 2060 | 89.3435 | 96.5068 | 104.1257 | 111.6742 | 119.2289
VittoriaWind2065RCP4.5 | Vittoria | Wind | RCP4.5 | 2065 | 89.4228 | 96.613 | 104.2664 | 111.8423 | 119.4289
VittoriaWind2070RCP4.5 | Vittoria | Wind | RCP4.5 | 2070 | 89.502 | 96.7193 | 104.4072 | 112.0104 | 119.6289
VittoriaWind2075RCP4.5 | Vittoria | Wind | RCP4.5 | 2075 | 89.6224 | 96.8742 | 104.6061 | 112.2469 | 119.906
VittoriaWind2080RCP4.5 | Vittoria | Wind | RCP4.5 | 2080 | 89.7428 | 97.0291 | 104.805 | 112.4833 | 120.1831
VittoriaWind2085RCP4.5 | Vittoria | Wind | RCP4.5 | 2085 | 89.8631 | 97.1841 | 105.0039 | 112.7198 | 120.4603
VittoriaWind2090RCP4.5 | Vittoria | Wind | RCP4.5 | 2090 | 89.9835 | 97.339 | 105.2028 | 112.9563 | 120.7374
VittoriaWind2095RCP4.5 | Vittoria | Wind | RCP4.5 | 2095 | 90.1039 | 97.4939 | 105.4017 | 113.1927 | 121.0145
VittoriaWind2100RCP4.5 | Vittoria | Wind | RCP4.5 | 2100 | 90.2242 | 97.6489 | 105.6006 | 113.4292 | 121.2917
VittoriaWind2023RCP6.0 | Vittoria | Wind | RCP6.0 | 2023 | 88.6477 | 95.5809 | 102.8976 | 110.1877 | 117.4893
VittoriaWind2025RCP6.0 | Vittoria | Wind | RCP6.0 | 2025 | 88.724 | 95.6821 | 103.0319 | 110.3515 | 117.6792
VittoriaWind2030RCP6.0 | Vittoria | Wind | RCP6.0 | 2030 | 88.8004 | 95.7833 | 103.1662 | 110.5152 | 117.8692
VittoriaWind2035RCP6.0 | Vittoria | Wind | RCP6.0 | 2035 | 88.8767 | 95.8845 | 103.3005 | 110.6789 | 118.0591
VittoriaWind2040RCP6.0 | Vittoria | Wind | RCP6.0 | 2040 | 88.953 | 95.9857 | 103.4348 | 110.8426 | 118.249
VittoriaWind2045RCP6.0 | Vittoria | Wind | RCP6.0 | 2045 | 89.0294 | 96.0869 | 103.5691 | 111.0063 | 118.4389
VittoriaWind2050RCP6.0 | Vittoria | Wind | RCP6.0 | 2050 | 89.185 | 96.2943 | 103.8442 | 111.3381 | 118.8289
VittoriaWind2055RCP6.0 | Vittoria | Wind | RCP6.0 | 2055 | 89.2642 | 96.4005 | 103.9849 | 111.5062 | 119.0289
VittoriaWind2060RCP6.0 | Vittoria | Wind | RCP6.0 | 2060 | 89.3435 | 96.5068 | 104.1257 | 111.6742 | 119.2289
VittoriaWind2065RCP6.0 | Vittoria | Wind | RCP6.0 | 2065 | 89.4228 | 96.613 | 104.2664 | 111.8423 | 119.4289
VittoriaWind2070RCP6.0 | Vittoria | Wind | RCP6.0 | 2070 | 89.502 | 96.7193 | 104.4072 | 112.0104 | 119.6289
VittoriaWind2075RCP6.0 | Vittoria | Wind | RCP6.0 | 2075 | 89.6826 | 96.9517 | 104.7056 | 112.3651 | 120.0446
VittoriaWind2080RCP6.0 | Vittoria | Wind | RCP6.0 | 2080 | 89.8631 | 97.1841 | 105.0039 | 112.7198 | 120.4603
VittoriaWind2085RCP6.0 | Vittoria | Wind | RCP6.0 | 2085 | 90.0437 | 97.4165 | 105.3022 | 113.0745 | 120.876
VittoriaWind2090RCP6.0 | Vittoria | Wind | RCP6.0 | 2090 | 90.4826 | 97.9841 | 106.0256 | 113.9349 | 121.8731
VittoriaWind2095RCP6.0 | Vittoria | Wind | RCP6.0 | 2095 | 90.741 | 98.3192 | 106.4506 | 114.4406 | 122.4545
VittoriaWind2100RCP6.0 | Vittoria | Wind | RCP6.0 | 2100 | 90.9993 | 98.6544 | 106.8756 | 114.9462 | 123.0359
VittoriaWind2023RCP8.5 | Vittoria | Wind | RCP8.5 | 2023 | 88.6477 | 95.5809 | 102.8976 | 110.1877 | 117.4893
VittoriaWind2025RCP8.5 | Vittoria | Wind | RCP8.5 | 2025 | 88.8004 | 95.7833 | 103.1662 | 110.5152 | 117.8692
VittoriaWind2030RCP8.5 | Vittoria | Wind | RCP8.5 | 2030 | 88.953 | 95.9857 | 103.4348 | 110.8426 | 118.249
VittoriaWind2035RCP8.5 | Vittoria | Wind | RCP8.5 | 2035 | 89.1057 | 96.188 | 103.7034 | 111.17 | 118.6289
VittoriaWind2040RCP8.5 | Vittoria | Wind | RCP8.5 | 2040 | 89.2378 | 96.3651 | 103.938 | 111.4501 | 118.9622
VittoriaWind2045RCP8.5 | Vittoria | Wind | RCP8.5 | 2045 | 89.3699 | 96.5422 | 104.1726 | 111.7303 | 119.2955
VittoriaWind2050RCP8.5 | Vittoria | Wind | RCP8.5 | 2050 | 89.7428 | 97.0291 | 104.805 | 112.4833 | 120.1831
VittoriaWind2055RCP8.5 | Vittoria | Wind | RCP8.5 | 2055 | 89.9835 | 97.339 | 105.2028 | 112.9563 | 120.7374
VittoriaWind2060RCP8.5 | Vittoria | Wind | RCP8.5 | 2060 | 90.4826 | 97.9841 | 106.0256 | 113.9349 | 121.8731
VittoriaWind2065RCP8.5 | Vittoria | Wind | RCP8.5 | 2065 | 90.741 | 98.3192 | 106.4506 | 114.4406 | 122.4545
VittoriaWind2070RCP8.5 | Vittoria | Wind | RCP8.5 | 2070 | 91.149 | 98.8663 | 107.168 | 115.3064 | 123.4661
VittoriaWind2075RCP8.5 | Vittoria | Wind | RCP8.5 | 2075 | 91.2988 | 99.0781 | 107.4604 | 115.6666 | 123.8963
VittoriaWind2080RCP8.5 | Vittoria | Wind | RCP8.5 | 2080 | 91.4485 | 99.29 | 107.7528 | 116.0267 | 124.3266
VittoriaWind2085RCP8.5 | Vittoria | Wind | RCP8.5 | 2085 | 91.792 | 99.7405 | 108.3495 | 116.7361 | 125.1638
VittoriaWind2090RCP8.5 | Vittoria | Wind | RCP8.5 | 2090 | 92.1355 | 100.1911 | 108.9462 | 117.4456 | 126.001
VittoriaWind2095RCP8.5 | Vittoria | Wind | RCP8.5 | 2095 | 92.1355 | 100.1911 | 108.9462 | 117.4456 | 126.001
VittoriaWind2100RCP8.5 | Vittoria | Wind | RCP8.5 | 2100 | 92.1355 | 100.1911 | 108.9462 | 117.4456 | 126.001
WalkertonIce Accretion2023RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2023 | 15.9885 | 19.1664 | 23.207 | 26.2759 | 29.3567
WalkertonIce Accretion2025RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2025 | 15.9938 | 19.1886 | 23.2415 | 26.3235 | 29.4195
WalkertonIce Accretion2030RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2030 | 15.9991 | 19.2109 | 23.276 | 26.3712 | 29.4823
WalkertonIce Accretion2035RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2035 | 16.0045 | 19.2332 | 23.3105 | 26.4188 | 29.5451
WalkertonIce Accretion2040RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2040 | 16.0098 | 19.2554 | 23.345 | 26.4665 | 29.6079
WalkertonIce Accretion2045RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2045 | 16.0151 | 19.2777 | 23.3795 | 26.5141 | 29.6707
WalkertonIce Accretion2050RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2050 | 16.0141 | 19.3114 | 23.4554 | 26.6242 | 29.8146
WalkertonIce Accretion2055RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2055 | 16.0077 | 19.3229 | 23.4968 | 26.6865 | 29.8958
WalkertonIce Accretion2060RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2060 | 16.0013 | 19.3344 | 23.5382 | 26.7489 | 29.9769
WalkertonIce Accretion2065RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2065 | 15.9949 | 19.3458 | 23.5796 | 26.8113 | 30.0581
WalkertonIce Accretion2070RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2070 | 15.9885 | 19.3573 | 23.621 | 26.8737 | 30.1392
WalkertonIce Accretion2075RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2075 | 15.9191 | 19.3 | 23.5827 | 26.8433 | 30.1199
WalkertonIce Accretion2080RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2080 | 15.8498 | 19.2427 | 23.5443 | 26.813 | 30.1006
WalkertonIce Accretion2085RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2085 | 15.7804 | 19.1854 | 23.506 | 26.7827 | 30.0812
WalkertonIce Accretion2090RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2090 | 15.711 | 19.1282 | 23.4677 | 26.7524 | 30.0619
WalkertonIce Accretion2095RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2095 | 15.6417 | 19.0709 | 23.4293 | 26.7221 | 30.0426
WalkertonIce Accretion2100RCP4.5 | Walkerton | Ice Accretion | RCP4.5 | 2100 | 15.5723 | 19.0136 | 23.391 | 26.6917 | 30.0233
WalkertonIce Accretion2023RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2023 | 15.9885 | 19.1664 | 23.207 | 26.2759 | 29.3567
WalkertonIce Accretion2025RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2025 | 15.9938 | 19.1886 | 23.2415 | 26.3235 | 29.4195
WalkertonIce Accretion2030RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2030 | 15.9991 | 19.2109 | 23.276 | 26.3712 | 29.4823
WalkertonIce Accretion2035RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2035 | 16.0045 | 19.2332 | 23.3105 | 26.4188 | 29.5451
WalkertonIce Accretion2040RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2040 | 16.0098 | 19.2554 | 23.345 | 26.4665 | 29.6079
WalkertonIce Accretion2045RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2045 | 16.0151 | 19.2777 | 23.3795 | 26.5141 | 29.6707
WalkertonIce Accretion2050RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2050 | 16.0141 | 19.3114 | 23.4554 | 26.6242 | 29.8146
WalkertonIce Accretion2055RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2055 | 16.0077 | 19.3229 | 23.4968 | 26.6865 | 29.8958
WalkertonIce Accretion2060RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2060 | 16.0013 | 19.3344 | 23.5382 | 26.7489 | 29.9769
WalkertonIce Accretion2065RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2065 | 15.9949 | 19.3458 | 23.5796 | 26.8113 | 30.0581
WalkertonIce Accretion2070RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2070 | 15.9885 | 19.3573 | 23.621 | 26.8737 | 30.1392
WalkertonIce Accretion2075RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2075 | 15.8844 | 19.2714 | 23.5635 | 26.8282 | 30.1102
WalkertonIce Accretion2080RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2080 | 15.7804 | 19.1854 | 23.506 | 26.7827 | 30.0812
WalkertonIce Accretion2085RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2085 | 15.6764 | 19.0995 | 23.4485 | 26.7372 | 30.0523
WalkertonIce Accretion2090RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2090 | 15.3056 | 18.7337 | 23.0767 | 26.3625 | 29.6659
WalkertonIce Accretion2095RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2095 | 15.0389 | 18.4537 | 22.7623 | 26.0333 | 29.3084
WalkertonIce Accretion2100RCP6.0 | Walkerton | Ice Accretion | RCP6.0 | 2100 | 14.7721 | 18.1737 | 22.448 | 25.7041 | 28.951
WalkertonIce Accretion2023RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2023 | 15.9885 | 19.1664 | 23.207 | 26.2759 | 29.3567
WalkertonIce Accretion2025RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2025 | 15.9991 | 19.2109 | 23.276 | 26.3712 | 29.4823
WalkertonIce Accretion2030RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2030 | 16.0098 | 19.2554 | 23.345 | 26.4665 | 29.6079
WalkertonIce Accretion2035RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2035 | 16.0205 | 19.3 | 23.414 | 26.5618 | 29.7335
WalkertonIce Accretion2040RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2040 | 16.0098 | 19.3191 | 23.483 | 26.6657 | 29.8687
WalkertonIce Accretion2045RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2045 | 15.9991 | 19.3382 | 23.552 | 26.7697 | 30.004
WalkertonIce Accretion2050RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2050 | 15.8498 | 19.2427 | 23.5443 | 26.813 | 30.1006
WalkertonIce Accretion2055RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2055 | 15.711 | 19.1282 | 23.4677 | 26.7524 | 30.0619
WalkertonIce Accretion2060RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2060 | 15.3056 | 18.7337 | 23.0767 | 26.3625 | 29.6659
WalkertonIce Accretion2065RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2065 | 15.0389 | 18.4537 | 22.7623 | 26.0333 | 29.3084
WalkertonIce Accretion2070RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2070 | 14.3347 | 17.6773 | 21.8883 | 25.089 | 28.2845
WalkertonIce Accretion2075RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2075 | 13.8972 | 17.181 | 21.3287 | 24.4739 | 27.6179
WalkertonIce Accretion2080RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2080 | 13.4598 | 16.6847 | 20.769 | 23.8588 | 26.9514
WalkertonIce Accretion2085RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2085 | 13.0196 | 16.1979 | 20.217 | 23.261 | 26.3138
WalkertonIce Accretion2090RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2090 | 12.5795 | 15.7111 | 19.665 | 22.6633 | 25.6763
WalkertonIce Accretion2095RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2095 | 12.5795 | 15.7111 | 19.665 | 22.6633 | 25.6763
WalkertonIce Accretion2100RCP8.5 | Walkerton | Ice Accretion | RCP8.5 | 2100 | 12.5795 | 15.7111 | 19.665 | 22.6633 | 25.6763
WalkertonWind2023RCP4.5 | Walkerton | Wind | RCP4.5 | 2023 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2506
WalkertonWind2025RCP4.5 | Walkerton | Wind | RCP4.5 | 2025 | 85.4139 | 92.1425 | 99.2626 | 106.3385 | 113.42
WalkertonWind2030RCP4.5 | Walkerton | Wind | RCP4.5 | 2030 | 85.4957 | 92.2428 | 99.3883 | 106.4853 | 113.5894
WalkertonWind2035RCP4.5 | Walkerton | Wind | RCP4.5 | 2035 | 85.5775 | 92.343 | 99.5141 | 106.6321 | 113.7589
WalkertonWind2040RCP4.5 | Walkerton | Wind | RCP4.5 | 2040 | 85.6593 | 92.4433 | 99.6399 | 106.7789 | 113.9283
WalkertonWind2045RCP4.5 | Walkerton | Wind | RCP4.5 | 2045 | 85.7411 | 92.5436 | 99.7656 | 106.9257 | 114.0978
WalkertonWind2050RCP4.5 | Walkerton | Wind | RCP4.5 | 2050 | 85.8364 | 92.6566 | 99.9012 | 107.0809 | 114.2739
WalkertonWind2055RCP4.5 | Walkerton | Wind | RCP4.5 | 2055 | 85.85 | 92.6693 | 99.911 | 107.0893 | 114.2806
WalkertonWind2060RCP4.5 | Walkerton | Wind | RCP4.5 | 2060 | 85.8635 | 92.6821 | 99.9208 | 107.0977 | 114.2873
WalkertonWind2065RCP4.5 | Walkerton | Wind | RCP4.5 | 2065 | 85.8771 | 92.6948 | 99.9306 | 107.1061 | 114.294
WalkertonWind2070RCP4.5 | Walkerton | Wind | RCP4.5 | 2070 | 85.8906 | 92.7076 | 99.9404 | 107.1145 | 114.3007
WalkertonWind2075RCP4.5 | Walkerton | Wind | RCP4.5 | 2075 | 85.9738 | 92.8155 | 100.0792 | 107.2805 | 114.4925
WalkertonWind2080RCP4.5 | Walkerton | Wind | RCP4.5 | 2080 | 86.057 | 92.9233 | 100.2181 | 107.4465 | 114.6843
WalkertonWind2085RCP4.5 | Walkerton | Wind | RCP4.5 | 2085 | 86.1402 | 93.0312 | 100.3569 | 107.6126 | 114.8761
WalkertonWind2090RCP4.5 | Walkerton | Wind | RCP4.5 | 2090 | 86.2234 | 93.139 | 100.4957 | 107.7786 | 115.0679
WalkertonWind2095RCP4.5 | Walkerton | Wind | RCP4.5 | 2095 | 86.3067 | 93.2469 | 100.6346 | 107.9446 | 115.2597
WalkertonWind2100RCP4.5 | Walkerton | Wind | RCP4.5 | 2100 | 86.3899 | 93.3547 | 100.7734 | 108.1107 | 115.4514
WalkertonWind2023RCP6.0 | Walkerton | Wind | RCP6.0 | 2023 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2506
WalkertonWind2025RCP6.0 | Walkerton | Wind | RCP6.0 | 2025 | 85.4139 | 92.1425 | 99.2626 | 106.3385 | 113.42
WalkertonWind2030RCP6.0 | Walkerton | Wind | RCP6.0 | 2030 | 85.4957 | 92.2428 | 99.3883 | 106.4853 | 113.5894
WalkertonWind2035RCP6.0 | Walkerton | Wind | RCP6.0 | 2035 | 85.5775 | 92.343 | 99.5141 | 106.6321 | 113.7589
WalkertonWind2040RCP6.0 | Walkerton | Wind | RCP6.0 | 2040 | 85.6593 | 92.4433 | 99.6399 | 106.7789 | 113.9283
WalkertonWind2045RCP6.0 | Walkerton | Wind | RCP6.0 | 2045 | 85.7411 | 92.5436 | 99.7656 | 106.9257 | 114.0978
WalkertonWind2050RCP6.0 | Walkerton | Wind | RCP6.0 | 2050 | 85.8364 | 92.6566 | 99.9012 | 107.0809 | 114.2739
WalkertonWind2055RCP6.0 | Walkerton | Wind | RCP6.0 | 2055 | 85.85 | 92.6693 | 99.911 | 107.0893 | 114.2806
WalkertonWind2060RCP6.0 | Walkerton | Wind | RCP6.0 | 2060 | 85.8635 | 92.6821 | 99.9208 | 107.0977 | 114.2873
WalkertonWind2065RCP6.0 | Walkerton | Wind | RCP6.0 | 2065 | 85.8771 | 92.6948 | 99.9306 | 107.1061 | 114.294
WalkertonWind2070RCP6.0 | Walkerton | Wind | RCP6.0 | 2070 | 85.8906 | 92.7076 | 99.9404 | 107.1145 | 114.3007
WalkertonWind2075RCP6.0 | Walkerton | Wind | RCP6.0 | 2075 | 86.0154 | 92.8694 | 100.1487 | 107.3635 | 114.5884
WalkertonWind2080RCP6.0 | Walkerton | Wind | RCP6.0 | 2080 | 86.1402 | 93.0312 | 100.3569 | 107.6126 | 114.8761
WalkertonWind2085RCP6.0 | Walkerton | Wind | RCP6.0 | 2085 | 86.265 | 93.1929 | 100.5652 | 107.8616 | 115.1638
WalkertonWind2090RCP6.0 | Walkerton | Wind | RCP6.0 | 2090 | 86.8017 | 93.8712 | 101.4169 | 108.8657 | 116.3229
WalkertonWind2095RCP6.0 | Walkerton | Wind | RCP6.0 | 2095 | 87.2135 | 94.3876 | 102.0605 | 109.6206 | 117.1943
WalkertonWind2100RCP6.0 | Walkerton | Wind | RCP6.0 | 2100 | 87.6253 | 94.9041 | 102.704 | 110.3756 | 118.0657
WalkertonWind2023RCP8.5 | Walkerton | Wind | RCP8.5 | 2023 | 85.3321 | 92.0423 | 99.1368 | 106.1917 | 113.2506
WalkertonWind2025RCP8.5 | Walkerton | Wind | RCP8.5 | 2025 | 85.4957 | 92.2428 | 99.3883 | 106.4853 | 113.5894
WalkertonWind2030RCP8.5 | Walkerton | Wind | RCP8.5 | 2030 | 85.6593 | 92.4433 | 99.6399 | 106.7789 | 113.9283
WalkertonWind2035RCP8.5 | Walkerton | Wind | RCP8.5 | 2035 | 85.8229 | 92.6438 | 99.8914 | 107.0725 | 114.2672
WalkertonWind2040RCP8.5 | Walkerton | Wind | RCP8.5 | 2040 | 85.8455 | 92.6651 | 99.9077 | 107.0865 | 114.2784
WalkertonWind2045RCP8.5 | Walkerton | Wind | RCP8.5 | 2045 | 85.868 | 92.6863 | 99.9241 | 107.1005 | 114.2896
WalkertonWind2050RCP8.5 | Walkerton | Wind | RCP8.5 | 2050 | 86.057 | 92.9233 | 100.2181 | 107.4465 | 114.6843
WalkertonWind2055RCP8.5 | Walkerton | Wind | RCP8.5 | 2055 | 86.2234 | 93.139 | 100.4957 | 107.7786 | 115.0679
WalkertonWind2060RCP8.5 | Walkerton | Wind | RCP8.5 | 2060 | 86.8017 | 93.8712 | 101.4169 | 108.8657 | 116.3229
WalkertonWind2065RCP8.5 | Walkerton | Wind | RCP8.5 | 2065 | 87.2135 | 94.3876 | 102.0605 | 109.6206 | 117.1943
WalkertonWind2070RCP8.5 | Walkerton | Wind | RCP8.5 | 2070 | 87.8397 | 95.1653 | 103.0241 | 110.7461 | 118.4865
WalkertonWind2075RCP8.5 | Walkerton | Wind | RCP8.5 | 2075 | 88.0541 | 95.4266 | 103.3443 | 111.1166 | 118.9073
WalkertonWind2080RCP8.5 | Walkerton | Wind | RCP8.5 | 2080 | 88.2685 | 95.6879 | 103.6644 | 111.4872 | 119.3281
WalkertonWind2085RCP8.5 | Walkerton | Wind | RCP8.5 | 2085 | 88.2896 | 95.697 | 103.6644 | 111.4714 | 119.3058
WalkertonWind2090RCP8.5 | Walkerton | Wind | RCP8.5 | 2090 | 88.3108 | 95.7061 | 103.6644 | 111.4557 | 119.2834
WalkertonWind2095RCP8.5 | Walkerton | Wind | RCP8.5 | 2095 | 88.3108 | 95.7061 | 103.6644 | 111.4557 | 119.2834
WalkertonWind2100RCP8.5 | Walkerton | Wind | RCP8.5 | 2100 | 88.3108 | 95.7061 | 103.6644 | 111.4557 | 119.2834
WallaceburgIce Accretion2023RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2023 | 15.4123 | 18.46 | 22.333 | 25.2623 | 28.2265
WallaceburgIce Accretion2025RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2025 | 15.3376 | 18.3869 | 22.2563 | 25.1843 | 28.1444
WallaceburgIce Accretion2030RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2030 | 15.2629 | 18.3137 | 22.1797 | 25.1063 | 28.0623
WallaceburgIce Accretion2035RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2035 | 15.1882 | 18.2405 | 22.103 | 25.0284 | 27.9802
WallaceburgIce Accretion2040RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2040 | 15.1135 | 18.1673 | 22.0263 | 24.9504 | 27.8981
WallaceburgIce Accretion2045RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2045 | 15.0389 | 18.0941 | 21.9497 | 24.8724 | 27.816
WallaceburgIce Accretion2050RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2050 | 14.6921 | 17.7193 | 21.5326 | 24.4306 | 27.3339
WallaceburgIce Accretion2055RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2055 | 14.42 | 17.4177 | 21.1922 | 24.0667 | 26.934
WallaceburgIce Accretion2060RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2060 | 14.1479 | 17.1161 | 20.8518 | 23.7029 | 26.5341
WallaceburgIce Accretion2065RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2065 | 13.8759 | 16.8145 | 20.5114 | 23.339 | 26.1342
WallaceburgIce Accretion2070RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2070 | 13.6038 | 16.5129 | 20.171 | 22.9752 | 25.7342
WallaceburgIce Accretion2075RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2075 | 13.2837 | 16.147 | 19.7493 | 22.503 | 25.2174
WallaceburgIce Accretion2080RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2080 | 12.9636 | 15.7811 | 19.3277 | 22.0309 | 24.7006
WallaceburgIce Accretion2085RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2085 | 12.6435 | 15.4152 | 18.906 | 21.5587 | 24.1838
WallaceburgIce Accretion2090RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2090 | 12.3234 | 15.0493 | 18.4843 | 21.0866 | 23.667
WallaceburgIce Accretion2095RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2095 | 12.0033 | 14.6834 | 18.0627 | 20.6144 | 23.1502
WallaceburgIce Accretion2100RCP4.5 | Wallaceburg | Ice Accretion | RCP4.5 | 2100 | 11.6833 | 14.3175 | 17.641 | 20.1423 | 22.6334
WallaceburgIce Accretion2023RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2023 | 15.4123 | 18.46 | 22.333 | 25.2623 | 28.2265
WallaceburgIce Accretion2025RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2025 | 15.3376 | 18.3869 | 22.2563 | 25.1843 | 28.1444
WallaceburgIce Accretion2030RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2030 | 15.2629 | 18.3137 | 22.1797 | 25.1063 | 28.0623
WallaceburgIce Accretion2035RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2035 | 15.1882 | 18.2405 | 22.103 | 25.0284 | 27.9802
WallaceburgIce Accretion2040RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2040 | 15.1135 | 18.1673 | 22.0263 | 24.9504 | 27.8981
WallaceburgIce Accretion2045RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2045 | 15.0389 | 18.0941 | 21.9497 | 24.8724 | 27.816
WallaceburgIce Accretion2050RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2050 | 14.6921 | 17.7193 | 21.5326 | 24.4306 | 27.3339
WallaceburgIce Accretion2055RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2055 | 14.42 | 17.4177 | 21.1922 | 24.0667 | 26.934
WallaceburgIce Accretion2060RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2060 | 14.1479 | 17.1161 | 20.8518 | 23.7029 | 26.5341
WallaceburgIce Accretion2065RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2065 | 13.8759 | 16.8145 | 20.5114 | 23.339 | 26.1342
WallaceburgIce Accretion2070RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2070 | 13.6038 | 16.5129 | 20.171 | 22.9752 | 25.7342
WallaceburgIce Accretion2075RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2075 | 13.1237 | 15.964 | 19.5385 | 22.2669 | 24.959
WallaceburgIce Accretion2080RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2080 | 12.6435 | 15.4152 | 18.906 | 21.5587 | 24.1838
WallaceburgIce Accretion2085RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2085 | 12.1634 | 14.8663 | 18.2735 | 20.8505 | 23.4086
WallaceburgIce Accretion2090RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2090 | 11.2031 | 13.7639 | 16.9893 | 19.4145 | 21.8316
WallaceburgIce Accretion2095RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2095 | 10.723 | 13.2103 | 16.3377 | 18.6868 | 21.0298
WallaceburgIce Accretion2100RCP6.0 | Wallaceburg | Ice Accretion | RCP6.0 | 2100 | 10.2429 | 12.6567 | 15.686 | 17.9591 | 20.228
WallaceburgIce Accretion2023RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2023 | 15.4123 | 18.46 | 22.333 | 25.2623 | 28.2265
WallaceburgIce Accretion2025RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2025 | 15.2629 | 18.3137 | 22.1797 | 25.1063 | 28.0623
WallaceburgIce Accretion2030RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2030 | 15.1135 | 18.1673 | 22.0263 | 24.9504 | 27.8981
WallaceburgIce Accretion2035RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2035 | 14.9642 | 18.021 | 21.873 | 24.7945 | 27.7339
WallaceburgIce Accretion2040RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2040 | 14.5107 | 17.5183 | 21.3057 | 24.188 | 27.0673
WallaceburgIce Accretion2045RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2045 | 14.0573 | 17.0156 | 20.7383 | 23.5816 | 26.4008
WallaceburgIce Accretion2050RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2050 | 12.9636 | 15.7811 | 19.3277 | 22.0309 | 24.7006
WallaceburgIce Accretion2055RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2055 | 12.3234 | 15.0493 | 18.4843 | 21.0866 | 23.667
WallaceburgIce Accretion2060RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2060 | 11.2031 | 13.7639 | 16.9893 | 19.4145 | 21.8316
WallaceburgIce Accretion2065RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2065 | 10.723 | 13.2103 | 16.3377 | 18.6868 | 21.0298
WallaceburgIce Accretion2070RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2070 | 9.7521 | 12.084 | 15.0037 | 17.1967 | 19.378
WallaceburgIce Accretion2075RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2075 | 9.2612 | 11.5113 | 14.3213 | 16.4343 | 18.5279
WallaceburgIce Accretion2080RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2080 | 8.7704 | 10.9386 | 13.639 | 15.672 | 17.6778
WallaceburgIce Accretion2085RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2085 | 8.1463 | 10.2036 | 12.765 | 14.6843 | 16.591
WallaceburgIce Accretion2090RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2090 | 7.5221 | 9.4686 | 11.891 | 13.6967 | 15.5043
WallaceburgIce Accretion2095RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2095 | 7.5221 | 9.4686 | 11.891 | 13.6967 | 15.5043
WallaceburgIce Accretion2100RCP8.5 | Wallaceburg | Ice Accretion | RCP8.5 | 2100 | 7.5221 | 9.4686 | 11.891 | 13.6967 | 15.5043
WallaceburgWind2023RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2023 | 85.1205 | 91.7051 | 98.637 | 105.573 | 112.502
WallaceburgWind2025RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2025 | 85.1614 | 91.7643 | 98.7203 | 105.6744 | 112.6249
WallaceburgWind2030RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2030 | 85.2023 | 91.8235 | 98.8036 | 105.7758 | 112.7478
WallaceburgWind2035RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2035 | 85.2432 | 91.8828 | 98.8869 | 105.8771 | 112.8707
WallaceburgWind2040RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2040 | 85.2841 | 91.942 | 98.9702 | 105.9785 | 112.9936
WallaceburgWind2045RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2045 | 85.325 | 92.0013 | 99.0535 | 106.0799 | 113.1165
WallaceburgWind2050RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2050 | 85.3507 | 92.0332 | 99.0956 | 106.1288 | 113.1724
WallaceburgWind2055RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2055 | 85.3355 | 92.0058 | 99.0545 | 106.0764 | 113.1053
WallaceburgWind2060RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2060 | 85.3202 | 91.9785 | 99.0133 | 106.0239 | 113.0383
WallaceburgWind2065RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2065 | 85.305 | 91.9511 | 98.9722 | 105.9715 | 112.9713
WallaceburgWind2070RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2070 | 85.2898 | 91.9238 | 98.931 | 105.9191 | 112.9042
WallaceburgWind2075RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2075 | 85.4618 | 92.1456 | 99.2136 | 106.2546 | 113.2934
WallaceburgWind2080RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2080 | 85.6339 | 92.3674 | 99.4961 | 106.5902 | 113.6825
WallaceburgWind2085RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2085 | 85.806 | 92.5891 | 99.7787 | 106.9257 | 114.0717
WallaceburgWind2090RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2090 | 85.978 | 92.8109 | 100.0613 | 107.2613 | 114.4609
WallaceburgWind2095RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2095 | 86.1501 | 93.0327 | 100.3438 | 107.5968 | 114.85
WallaceburgWind2100RCP4.5 | Wallaceburg | Wind | RCP4.5 | 2100 | 86.3222 | 93.2544 | 100.6264 | 107.9324 | 115.2392
WallaceburgWind2023RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2023 | 85.1205 | 91.7051 | 98.637 | 105.573 | 112.502
WallaceburgWind2025RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2025 | 85.1614 | 91.7643 | 98.7203 | 105.6744 | 112.6249
WallaceburgWind2030RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2030 | 85.2023 | 91.8235 | 98.8036 | 105.7758 | 112.7478
WallaceburgWind2035RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2035 | 85.2432 | 91.8828 | 98.8869 | 105.8771 | 112.8707
WallaceburgWind2040RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2040 | 85.2841 | 91.942 | 98.9702 | 105.9785 | 112.9936
WallaceburgWind2045RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2045 | 85.325 | 92.0013 | 99.0535 | 106.0799 | 113.1165
WallaceburgWind2050RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2050 | 85.3507 | 92.0332 | 99.0956 | 106.1288 | 113.1724
WallaceburgWind2055RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2055 | 85.3355 | 92.0058 | 99.0545 | 106.0764 | 113.1053
WallaceburgWind2060RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2060 | 85.3202 | 91.9785 | 99.0133 | 106.0239 | 113.0383
WallaceburgWind2065RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2065 | 85.305 | 91.9511 | 98.9722 | 105.9715 | 112.9713
WallaceburgWind2070RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2070 | 85.2898 | 91.9238 | 98.931 | 105.9191 | 112.9042
WallaceburgWind2075RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2075 | 85.5479 | 92.2565 | 99.3548 | 106.4224 | 113.488
WallaceburgWind2080RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2080 | 85.806 | 92.5891 | 99.7787 | 106.9257 | 114.0717
WallaceburgWind2085RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2085 | 86.0641 | 92.9218 | 100.2026 | 107.4291 | 114.6554
WallaceburgWind2090RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2090 | 86.6663 | 93.6615 | 101.1131 | 108.4847 | 115.8611
WallaceburgWind2095RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2095 | 87.0104 | 94.0686 | 101.5999 | 109.0369 | 116.483
WallaceburgWind2100RCP6.0 | Wallaceburg | Wind | RCP6.0 | 2100 | 87.3545 | 94.4757 | 102.0866 | 109.5892 | 117.1049
WallaceburgWind2023RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2023 | 85.1205 | 91.7051 | 98.637 | 105.573 | 112.502
WallaceburgWind2025RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2025 | 85.2023 | 91.8235 | 98.8036 | 105.7758 | 112.7478
WallaceburgWind2030RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2030 | 85.2841 | 91.942 | 98.9702 | 105.9785 | 112.9936
WallaceburgWind2035RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2035 | 85.3659 | 92.0605 | 99.1368 | 106.1812 | 113.2394
WallaceburgWind2040RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2040 | 85.3406 | 92.0149 | 99.0682 | 106.0939 | 113.1277
WallaceburgWind2045RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2045 | 85.3152 | 91.9694 | 98.9996 | 106.0065 | 113.016
WallaceburgWind2050RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2050 | 85.6339 | 92.3674 | 99.4961 | 106.5902 | 113.6825
WallaceburgWind2055RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2055 | 85.978 | 92.8109 | 100.0613 | 107.2613 | 114.4609
WallaceburgWind2060RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2060 | 86.6663 | 93.6615 | 101.1131 | 108.4847 | 115.8611
WallaceburgWind2065RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2065 | 87.0104 | 94.0686 | 101.5999 | 109.0369 | 116.483
WallaceburgWind2070RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2070 | 87.5971 | 94.7826 | 102.4655 | 110.0331 | 117.6151
WallaceburgWind2075RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2075 | 87.8397 | 95.0894 | 102.8445 | 110.477 | 118.1253
WallaceburgWind2080RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2080 | 88.0823 | 95.3962 | 103.2234 | 110.9209 | 118.6355
WallaceburgWind2085RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2085 | 88.5646 | 96.0205 | 104.0319 | 111.8804 | 119.7471
WallaceburgWind2090RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2090 | 89.047 | 96.6449 | 104.8404 | 112.8398 | 120.8587
WallaceburgWind2095RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2095 | 89.047 | 96.6449 | 104.8404 | 112.8398 | 120.8587
WallaceburgWind2100RCP8.5 | Wallaceburg | Wind | RCP8.5 | 2100 | 89.047 | 96.6449 | 104.8404 | 112.8398 | 120.8587
WaterlooIce Accretion2023RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
WaterlooIce Accretion2025RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2025 | 17.3208 | 20.7984 | 25.1958 | 28.5655 | 31.92
WaterlooIce Accretion2030RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2030 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
WaterlooIce Accretion2035RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2035 | 17.3788 | 20.8953 | 25.3375 | 28.7444 | 32.13
WaterlooIce Accretion2040RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2040 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
WaterlooIce Accretion2045RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2045 | 17.4367 | 20.9921 | 25.4792 | 28.9233 | 32.34
WaterlooIce Accretion2050RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2050 | 17.4101 | 20.9907 | 25.51 | 28.9788 | 32.4198
WaterlooIce Accretion2055RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2055 | 17.3544 | 20.9409 | 25.47 | 28.9449 | 32.3946
WaterlooIce Accretion2060RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2060 | 17.2987 | 20.8911 | 25.43 | 28.911 | 32.3694
WaterlooIce Accretion2065RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2065 | 17.2431 | 20.8413 | 25.39 | 28.8771 | 32.3442
WaterlooIce Accretion2070RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2070 | 17.1874 | 20.7915 | 25.35 | 28.8432 | 32.319
WaterlooIce Accretion2075RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2075 | 17.1555 | 20.7846 | 25.3708 | 28.8809 | 32.3768
WaterlooIce Accretion2080RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2080 | 17.1236 | 20.7777 | 25.3917 | 28.9186 | 32.4345
WaterlooIce Accretion2085RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2085 | 17.0917 | 20.7707 | 25.4125 | 28.9562 | 32.4922
WaterlooIce Accretion2090RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2090 | 17.0598 | 20.7638 | 25.4333 | 28.9939 | 32.55
WaterlooIce Accretion2095RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2095 | 17.0279 | 20.7569 | 25.4542 | 29.0316 | 32.6077
WaterlooIce Accretion2100RCP4.5 | Waterloo | Ice Accretion | RCP4.5 | 2100 | 16.996 | 20.75 | 25.475 | 29.0692 | 32.6655
WaterlooIce Accretion2023RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
WaterlooIce Accretion2025RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2025 | 17.3208 | 20.7984 | 25.1958 | 28.5655 | 31.92
WaterlooIce Accretion2030RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2030 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
WaterlooIce Accretion2035RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2035 | 17.3788 | 20.8953 | 25.3375 | 28.7444 | 32.13
WaterlooIce Accretion2040RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2040 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
WaterlooIce Accretion2045RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2045 | 17.4367 | 20.9921 | 25.4792 | 28.9233 | 32.34
WaterlooIce Accretion2050RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2050 | 17.4101 | 20.9907 | 25.51 | 28.9788 | 32.4198
WaterlooIce Accretion2055RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2055 | 17.3544 | 20.9409 | 25.47 | 28.9449 | 32.3946
WaterlooIce Accretion2060RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2060 | 17.2987 | 20.8911 | 25.43 | 28.911 | 32.3694
WaterlooIce Accretion2065RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2065 | 17.2431 | 20.8413 | 25.39 | 28.8771 | 32.3442
WaterlooIce Accretion2070RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2070 | 17.1874 | 20.7915 | 25.35 | 28.8432 | 32.319
WaterlooIce Accretion2075RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2075 | 17.1396 | 20.7811 | 25.3813 | 28.8997 | 32.4056
WaterlooIce Accretion2080RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2080 | 17.0917 | 20.7707 | 25.4125 | 28.9562 | 32.4922
WaterlooIce Accretion2085RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2085 | 17.0439 | 20.7604 | 25.4437 | 29.0127 | 32.5789
WaterlooIce Accretion2090RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2090 | 16.6887 | 20.4249 | 25.1333 | 28.7114 | 32.298
WaterlooIce Accretion2095RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2095 | 16.3814 | 20.0998 | 24.7917 | 28.3536 | 31.9305
WaterlooIce Accretion2100RCP6.0 | Waterloo | Ice Accretion | RCP6.0 | 2100 | 16.074 | 19.7747 | 24.45 | 27.9957 | 31.563
WaterlooIce Accretion2023RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2023 | 17.2918 | 20.75 | 25.125 | 28.476 | 31.815
WaterlooIce Accretion2025RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2025 | 17.3498 | 20.8468 | 25.2667 | 28.6549 | 32.025
WaterlooIce Accretion2030RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2030 | 17.4078 | 20.9437 | 25.4083 | 28.8338 | 32.235
WaterlooIce Accretion2035RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2035 | 17.4657 | 21.0405 | 25.55 | 29.0127 | 32.445
WaterlooIce Accretion2040RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2040 | 17.373 | 20.9575 | 25.4833 | 28.9562 | 32.403
WaterlooIce Accretion2045RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2045 | 17.2802 | 20.8745 | 25.4167 | 28.8997 | 32.361
WaterlooIce Accretion2050RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2050 | 17.1236 | 20.7777 | 25.3917 | 28.9186 | 32.4345
WaterlooIce Accretion2055RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2055 | 17.0598 | 20.7638 | 25.4333 | 28.9939 | 32.55
WaterlooIce Accretion2060RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2060 | 16.6887 | 20.4249 | 25.1333 | 28.7114 | 32.298
WaterlooIce Accretion2065RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2065 | 16.3814 | 20.0998 | 24.7917 | 28.3536 | 31.9305
WaterlooIce Accretion2070RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2070 | 15.6507 | 19.3182 | 23.95 | 27.4684 | 30.9855
WaterlooIce Accretion2075RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2075 | 15.2274 | 18.8617 | 23.45 | 26.9411 | 30.408
WaterlooIce Accretion2080RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2080 | 14.8041 | 18.4052 | 22.95 | 26.4137 | 29.8305
WaterlooIce Accretion2085RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2085 | 13.9778 | 17.43 | 21.7875 | 25.086 | 28.3657
WaterlooIce Accretion2090RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2090 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
WaterlooIce Accretion2095RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2095 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
WaterlooIce Accretion2100RCP8.5 | Waterloo | Ice Accretion | RCP8.5 | 2100 | 13.1515 | 16.4548 | 20.625 | 23.7582 | 26.901
WaterlooWind2023RCP4.5 | Waterloo | Wind | RCP4.5 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
WaterlooWind2025RCP4.5 | Waterloo | Wind | RCP4.5 | 2025 | 81.5488 | 87.8469 | 94.481 | 101.1097 | 107.7494
WaterlooWind2030RCP4.5 | Waterloo | Wind | RCP4.5 | 2030 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
WaterlooWind2035RCP4.5 | Waterloo | Wind | RCP4.5 | 2035 | 81.6625 | 88.0013 | 94.6909 | 101.3645 | 108.0494
WaterlooWind2040RCP4.5 | Waterloo | Wind | RCP4.5 | 2040 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
WaterlooWind2045RCP4.5 | Waterloo | Wind | RCP4.5 | 2045 | 81.7761 | 88.1558 | 94.9008 | 101.6193 | 108.3495
WaterlooWind2050RCP4.5 | Waterloo | Wind | RCP4.5 | 2050 | 81.8962 | 88.3099 | 95.096 | 101.8513 | 108.6174
WaterlooWind2055RCP4.5 | Waterloo | Wind | RCP4.5 | 2055 | 81.9595 | 88.3869 | 95.1863 | 101.9559 | 108.7353
WaterlooWind2060RCP4.5 | Waterloo | Wind | RCP4.5 | 2060 | 82.0229 | 88.4638 | 95.2765 | 102.0605 | 108.8531
WaterlooWind2065RCP4.5 | Waterloo | Wind | RCP4.5 | 2065 | 82.0862 | 88.5407 | 95.3668 | 102.1651 | 108.971
WaterlooWind2070RCP4.5 | Waterloo | Wind | RCP4.5 | 2070 | 82.1495 | 88.6177 | 95.457 | 102.2697 | 109.0889
WaterlooWind2075RCP4.5 | Waterloo | Wind | RCP4.5 | 2075 | 82.2185 | 88.7167 | 95.598 | 102.4424 | 109.2961
WaterlooWind2080RCP4.5 | Waterloo | Wind | RCP4.5 | 2080 | 82.2875 | 88.8158 | 95.739 | 102.6151 | 109.5032
WaterlooWind2085RCP4.5 | Waterloo | Wind | RCP4.5 | 2085 | 82.3564 | 88.9149 | 95.88 | 102.7877 | 109.7104
WaterlooWind2090RCP4.5 | Waterloo | Wind | RCP4.5 | 2090 | 82.4254 | 89.014 | 96.021 | 102.9604 | 109.9176
WaterlooWind2095RCP4.5 | Waterloo | Wind | RCP4.5 | 2095 | 82.4944 | 89.113 | 96.162 | 103.1331 | 110.1248
WaterlooWind2100RCP4.5 | Waterloo | Wind | RCP4.5 | 2100 | 82.5634 | 89.2121 | 96.303 | 103.3057 | 110.3319
WaterlooWind2023RCP6.0 | Waterloo | Wind | RCP6.0 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
WaterlooWind2025RCP6.0 | Waterloo | Wind | RCP6.0 | 2025 | 81.5488 | 87.8469 | 94.481 | 101.1097 | 107.7494
WaterlooWind2030RCP6.0 | Waterloo | Wind | RCP6.0 | 2030 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
WaterlooWind2035RCP6.0 | Waterloo | Wind | RCP6.0 | 2035 | 81.6625 | 88.0013 | 94.6909 | 101.3645 | 108.0494
WaterlooWind2040RCP6.0 | Waterloo | Wind | RCP6.0 | 2040 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
WaterlooWind2045RCP6.0 | Waterloo | Wind | RCP6.0 | 2045 | 81.7761 | 88.1558 | 94.9008 | 101.6193 | 108.3495
WaterlooWind2050RCP6.0 | Waterloo | Wind | RCP6.0 | 2050 | 81.8962 | 88.3099 | 95.096 | 101.8513 | 108.6174
WaterlooWind2055RCP6.0 | Waterloo | Wind | RCP6.0 | 2055 | 81.9595 | 88.3869 | 95.1863 | 101.9559 | 108.7353
WaterlooWind2060RCP6.0 | Waterloo | Wind | RCP6.0 | 2060 | 82.0229 | 88.4638 | 95.2765 | 102.0605 | 108.8531
WaterlooWind2065RCP6.0 | Waterloo | Wind | RCP6.0 | 2065 | 82.0862 | 88.5407 | 95.3668 | 102.1651 | 108.971
WaterlooWind2070RCP6.0 | Waterloo | Wind | RCP6.0 | 2070 | 82.1495 | 88.6177 | 95.457 | 102.2697 | 109.0889
WaterlooWind2075RCP6.0 | Waterloo | Wind | RCP6.0 | 2075 | 82.253 | 88.7663 | 95.6685 | 102.5287 | 109.3996
WaterlooWind2080RCP6.0 | Waterloo | Wind | RCP6.0 | 2080 | 82.3564 | 88.9149 | 95.88 | 102.7877 | 109.7104
WaterlooWind2085RCP6.0 | Waterloo | Wind | RCP6.0 | 2085 | 82.4599 | 89.0635 | 96.0915 | 103.0467 | 110.0212
WaterlooWind2090RCP6.0 | Waterloo | Wind | RCP6.0 | 2090 | 82.8421 | 89.5618 | 96.7385 | 103.8187 | 110.9213
WaterlooWind2095RCP6.0 | Waterloo | Wind | RCP6.0 | 2095 | 83.1208 | 89.9115 | 97.1741 | 104.3316 | 111.5107
WaterlooWind2100RCP6.0 | Waterloo | Wind | RCP6.0 | 2100 | 83.3995 | 90.2612 | 97.6096 | 104.8446 | 112.1001
WaterlooWind2023RCP8.5 | Waterloo | Wind | RCP8.5 | 2023 | 81.492 | 87.7697 | 94.376 | 100.9823 | 107.5994
WaterlooWind2025RCP8.5 | Waterloo | Wind | RCP8.5 | 2025 | 81.6057 | 87.9241 | 94.5859 | 101.2371 | 107.8994
WaterlooWind2030RCP8.5 | Waterloo | Wind | RCP8.5 | 2030 | 81.7193 | 88.0786 | 94.7959 | 101.4919 | 108.1995
WaterlooWind2035RCP8.5 | Waterloo | Wind | RCP8.5 | 2035 | 81.8329 | 88.233 | 95.0058 | 101.7467 | 108.4995
WaterlooWind2040RCP8.5 | Waterloo | Wind | RCP8.5 | 2040 | 81.9384 | 88.3612 | 95.1562 | 101.9211 | 108.696
WaterlooWind2045RCP8.5 | Waterloo | Wind | RCP8.5 | 2045 | 82.044 | 88.4894 | 95.3066 | 102.0954 | 108.8924
WaterlooWind2050RCP8.5 | Waterloo | Wind | RCP8.5 | 2050 | 82.2875 | 88.8158 | 95.739 | 102.6151 | 109.5032
WaterlooWind2055RCP8.5 | Waterloo | Wind | RCP8.5 | 2055 | 82.4254 | 89.014 | 96.021 | 102.9604 | 109.9176
WaterlooWind2060RCP8.5 | Waterloo | Wind | RCP8.5 | 2060 | 82.8421 | 89.5618 | 96.7385 | 103.8187 | 110.9213
WaterlooWind2065RCP8.5 | Waterloo | Wind | RCP8.5 | 2065 | 83.1208 | 89.9115 | 97.1741 | 104.3316 | 111.5107
WaterlooWind2070RCP8.5 | Waterloo | Wind | RCP8.5 | 2070 | 83.6457 | 90.5933 | 98.0451 | 105.371 | 112.718
WaterlooWind2075RCP8.5 | Waterloo | Wind | RCP8.5 | 2075 | 83.8919 | 90.9255 | 98.4807 | 105.8973 | 113.336
WaterlooWind2080RCP8.5 | Waterloo | Wind | RCP8.5 | 2080 | 84.1381 | 91.2577 | 98.9162 | 106.4237 | 113.9539
WaterlooWind2085RCP8.5 | Waterloo | Wind | RCP8.5 | 2085 | 84.3775 | 91.5768 | 99.3392 | 106.9266 | 114.5433
WaterlooWind2090RCP8.5 | Waterloo | Wind | RCP8.5 | 2090 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
WaterlooWind2095RCP8.5 | Waterloo | Wind | RCP8.5 | 2095 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
WaterlooWind2100RCP8.5 | Waterloo | Wind | RCP8.5 | 2100 | 84.617 | 91.8959 | 99.7622 | 107.4295 | 115.1327
WatfordIce Accretion2023RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2023 | 14.7422 | 17.6939 | 21.428 | 24.2634 | 27.1102
WatfordIce Accretion2025RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2025 | 14.6835 | 17.6361 | 21.3693 | 24.2054 | 27.0501
WatfordIce Accretion2030RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2030 | 14.6248 | 17.5783 | 21.3107 | 24.1473 | 26.99
WatfordIce Accretion2035RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2035 | 14.5661 | 17.5205 | 21.252 | 24.0893 | 26.93
WatfordIce Accretion2040RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2040 | 14.5075 | 17.4626 | 21.1933 | 24.0313 | 26.8699
WatfordIce Accretion2045RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2045 | 14.4488 | 17.4048 | 21.1347 | 23.9733 | 26.8099
WatfordIce Accretion2050RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2050 | 14.1207 | 17.0475 | 20.7328 | 23.5424 | 26.3451
WatfordIce Accretion2055RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2055 | 13.8512 | 16.7481 | 20.3896 | 23.1695 | 25.9404
WatfordIce Accretion2060RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2060 | 13.5818 | 16.4486 | 20.0464 | 22.7966 | 25.5357
WatfordIce Accretion2065RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2065 | 13.3124 | 16.1491 | 19.7032 | 22.4237 | 25.131
WatfordIce Accretion2070RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2070 | 13.0429 | 15.8497 | 19.36 | 22.0508 | 24.7262
WatfordIce Accretion2075RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2075 | 12.9205 | 15.7219 | 19.228 | 21.9099 | 24.5784
WatfordIce Accretion2080RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2080 | 12.798 | 15.594 | 19.096 | 21.7691 | 24.4306
WatfordIce Accretion2085RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2085 | 12.6755 | 15.4662 | 18.964 | 21.6282 | 24.2827
WatfordIce Accretion2090RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2090 | 12.5531 | 15.3384 | 18.832 | 21.4873 | 24.1349
WatfordIce Accretion2095RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2095 | 12.4306 | 15.2106 | 18.7 | 21.3465 | 23.987
WatfordIce Accretion2100RCP4.5 | Watford | Ice Accretion | RCP4.5 | 2100 | 12.3081 | 15.0828 | 18.568 | 21.2056 | 23.8392
WatfordIce Accretion2023RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2023 | 14.7422 | 17.6939 | 21.428 | 24.2634 | 27.1102
WatfordIce Accretion2025RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2025 | 14.6835 | 17.6361 | 21.3693 | 24.2054 | 27.0501
WatfordIce Accretion2030RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2030 | 14.6248 | 17.5783 | 21.3107 | 24.1473 | 26.99
WatfordIce Accretion2035RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2035 | 14.5661 | 17.5205 | 21.252 | 24.0893 | 26.93
WatfordIce Accretion2040RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2040 | 14.5075 | 17.4626 | 21.1933 | 24.0313 | 26.8699
WatfordIce Accretion2045RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2045 | 14.4488 | 17.4048 | 21.1347 | 23.9733 | 26.8099
WatfordIce Accretion2050RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2050 | 14.1207 | 17.0475 | 20.7328 | 23.5424 | 26.3451
WatfordIce Accretion2055RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2055 | 13.8512 | 16.7481 | 20.3896 | 23.1695 | 25.9404
WatfordIce Accretion2060RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2060 | 13.5818 | 16.4486 | 20.0464 | 22.7966 | 25.5357
WatfordIce Accretion2065RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2065 | 13.3124 | 16.1491 | 19.7032 | 22.4237 | 25.131
WatfordIce Accretion2070RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2070 | 13.0429 | 15.8497 | 19.36 | 22.0508 | 24.7262
WatfordIce Accretion2075RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2075 | 12.8592 | 15.6579 | 19.162 | 21.8395 | 24.5045
WatfordIce Accretion2080RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2080 | 12.6755 | 15.4662 | 18.964 | 21.6282 | 24.2827
WatfordIce Accretion2085RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2085 | 12.4918 | 15.2745 | 18.766 | 21.4169 | 24.061
WatfordIce Accretion2090RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2090 | 11.9356 | 14.6628 | 18.084 | 20.6669 | 23.2478
WatfordIce Accretion2095RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2095 | 11.5631 | 14.2428 | 17.6 | 20.1283 | 22.6565
WatfordIce Accretion2100RCP6.0 | Watford | Ice Accretion | RCP6.0 | 2100 | 11.1906 | 13.8228 | 17.116 | 19.5897 | 22.0651
WatfordIce Accretion2023RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2023 | 14.7422 | 17.6939 | 21.428 | 24.2634 | 27.1102
WatfordIce Accretion2025RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2025 | 14.6248 | 17.5783 | 21.3107 | 24.1473 | 26.99
WatfordIce Accretion2030RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2030 | 14.5075 | 17.4626 | 21.1933 | 24.0313 | 26.8699
WatfordIce Accretion2035RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2035 | 14.3901 | 17.347 | 21.076 | 23.9153 | 26.7498
WatfordIce Accretion2040RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2040 | 13.941 | 16.8479 | 20.504 | 23.2938 | 26.0753
WatfordIce Accretion2045RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2045 | 13.492 | 16.3488 | 19.932 | 22.6723 | 25.4008
WatfordIce Accretion2050RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2050 | 12.798 | 15.594 | 19.096 | 21.7691 | 24.4306
WatfordIce Accretion2055RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2055 | 12.5531 | 15.3384 | 18.832 | 21.4873 | 24.1349
WatfordIce Accretion2060RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2060 | 11.9356 | 14.6628 | 18.084 | 20.6669 | 23.2478
WatfordIce Accretion2065RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2065 | 11.5631 | 14.2428 | 17.6 | 20.1283 | 22.6565
WatfordIce Accretion2070RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2070 | 10.8997 | 13.5063 | 16.7567 | 19.2085 | 21.6493
WatfordIce Accretion2075RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2075 | 10.6089 | 13.1898 | 16.3973 | 18.8273 | 21.2335
WatfordIce Accretion2080RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2080 | 10.318 | 12.8733 | 16.038 | 18.4461 | 20.8177
WatfordIce Accretion2085RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2085 | 9.6138 | 12.0333 | 15.037 | 17.3026 | 19.5565
WatfordIce Accretion2090RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2090 | 8.9096 | 11.1934 | 14.036 | 16.159 | 18.2952
WatfordIce Accretion2095RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2095 | 8.9096 | 11.1934 | 14.036 | 16.159 | 18.2952
WatfordIce Accretion2100RCP8.5 | Watford | Ice Accretion | RCP8.5 | 2100 | 8.9096 | 11.1934 | 14.036 | 16.159 | 18.2952
WatfordWind2023RCP4.5 | Watford | Wind | RCP4.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
WatfordWind2025RCP4.5 | Watford | Wind | RCP4.5 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
WatfordWind2030RCP4.5 | Watford | Wind | RCP4.5 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
WatfordWind2035RCP4.5 | Watford | Wind | RCP4.5 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
WatfordWind2040RCP4.5 | Watford | Wind | RCP4.5 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
WatfordWind2045RCP4.5 | Watford | Wind | RCP4.5 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
WatfordWind2050RCP4.5 | Watford | Wind | RCP4.5 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
WatfordWind2055RCP4.5 | Watford | Wind | RCP4.5 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
WatfordWind2060RCP4.5 | Watford | Wind | RCP4.5 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
WatfordWind2065RCP4.5 | Watford | Wind | RCP4.5 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
WatfordWind2070RCP4.5 | Watford | Wind | RCP4.5 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
WatfordWind2075RCP4.5 | Watford | Wind | RCP4.5 | 2075 | 85.7411 | 92.542 | 99.746 | 106.9048 | 114.0736
WatfordWind2080RCP4.5 | Watford | Wind | RCP4.5 | 2080 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
WatfordWind2085RCP4.5 | Watford | Wind | RCP4.5 | 2085 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
WatfordWind2090RCP4.5 | Watford | Wind | RCP4.5 | 2090 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
WatfordWind2095RCP4.5 | Watford | Wind | RCP4.5 | 2095 | 86.3278 | 93.3015 | 100.7326 | 108.0792 | 115.444
WatfordWind2100RCP4.5 | Watford | Wind | RCP4.5 | 2100 | 86.4745 | 93.4914 | 100.9792 | 108.3728 | 115.7866
WatfordWind2023RCP6.0 | Watford | Wind | RCP6.0 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
WatfordWind2025RCP6.0 | Watford | Wind | RCP6.0 | 2025 | 85.3039 | 91.9375 | 98.9359 | 105.9173 | 112.9042
WatfordWind2030RCP6.0 | Watford | Wind | RCP6.0 | 2030 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
WatfordWind2035RCP6.0 | Watford | Wind | RCP6.0 | 2035 | 85.4167 | 92.0924 | 99.1417 | 106.1655 | 113.1947
WatfordWind2040RCP6.0 | Watford | Wind | RCP6.0 | 2040 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
WatfordWind2045RCP6.0 | Watford | Wind | RCP6.0 | 2045 | 85.5295 | 92.2474 | 99.3475 | 106.4137 | 113.4852
WatfordWind2050RCP6.0 | Watford | Wind | RCP6.0 | 2050 | 85.5877 | 92.3303 | 99.4602 | 106.5524 | 113.6505
WatfordWind2055RCP6.0 | Watford | Wind | RCP6.0 | 2055 | 85.5893 | 92.3358 | 99.47 | 106.5671 | 113.6706
WatfordWind2060RCP6.0 | Watford | Wind | RCP6.0 | 2060 | 85.591 | 92.3412 | 99.4798 | 106.5818 | 113.6907
WatfordWind2065RCP6.0 | Watford | Wind | RCP6.0 | 2065 | 85.5927 | 92.3467 | 99.4896 | 106.5965 | 113.7109
WatfordWind2070RCP6.0 | Watford | Wind | RCP6.0 | 2070 | 85.5944 | 92.3522 | 99.4994 | 106.6112 | 113.731
WatfordWind2075RCP6.0 | Watford | Wind | RCP6.0 | 2075 | 85.8144 | 92.637 | 99.8693 | 107.0516 | 114.2449
WatfordWind2080RCP6.0 | Watford | Wind | RCP6.0 | 2080 | 86.0345 | 92.9218 | 100.2393 | 107.492 | 114.7588
WatfordWind2085RCP6.0 | Watford | Wind | RCP6.0 | 2085 | 86.2545 | 93.2066 | 100.6093 | 107.9324 | 115.2727
WatfordWind2090RCP6.0 | Watford | Wind | RCP6.0 | 2090 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
WatfordWind2095RCP6.0 | Watford | Wind | RCP6.0 | 2095 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
WatfordWind2100RCP6.0 | Watford | Wind | RCP6.0 | 2100 | 87.5746 | 94.8494 | 102.6452 | 110.3127 | 117.9987
WatfordWind2023RCP8.5 | Watford | Wind | RCP8.5 | 2023 | 85.2475 | 91.86 | 98.833 | 105.7933 | 112.759
WatfordWind2025RCP8.5 | Watford | Wind | RCP8.5 | 2025 | 85.3603 | 92.0149 | 99.0388 | 106.0414 | 113.0495
WatfordWind2030RCP8.5 | Watford | Wind | RCP8.5 | 2030 | 85.4731 | 92.1699 | 99.2446 | 106.2896 | 113.3399
WatfordWind2035RCP8.5 | Watford | Wind | RCP8.5 | 2035 | 85.586 | 92.3248 | 99.4504 | 106.5378 | 113.6304
WatfordWind2040RCP8.5 | Watford | Wind | RCP8.5 | 2040 | 85.5888 | 92.3339 | 99.4667 | 106.5622 | 113.6639
WatfordWind2045RCP8.5 | Watford | Wind | RCP8.5 | 2045 | 85.5916 | 92.343 | 99.4831 | 106.5867 | 113.6974
WatfordWind2050RCP8.5 | Watford | Wind | RCP8.5 | 2050 | 85.8878 | 92.7319 | 99.9927 | 107.1984 | 114.4162
WatfordWind2055RCP8.5 | Watford | Wind | RCP8.5 | 2055 | 86.1811 | 93.1117 | 100.4859 | 107.7856 | 115.1014
WatfordWind2060RCP8.5 | Watford | Wind | RCP8.5 | 2060 | 86.8412 | 93.9441 | 101.5345 | 109.0194 | 116.524
WatfordWind2065RCP8.5 | Watford | Wind | RCP8.5 | 2065 | 87.2079 | 94.3967 | 102.0899 | 109.6661 | 117.2613
WatfordWind2070RCP8.5 | Watford | Wind | RCP8.5 | 2070 | 87.882 | 95.2383 | 103.1385 | 110.8929 | 118.669
WatfordWind2075RCP8.5 | Watford | Wind | RCP8.5 | 2075 | 88.1895 | 95.6271 | 103.6317 | 111.4732 | 119.3393
WatfordWind2080RCP8.5 | Watford | Wind | RCP8.5 | 2080 | 88.4969 | 96.016 | 104.125 | 112.0534 | 120.0096
WatfordWind2085RCP8.5 | Watford | Wind | RCP8.5 | 2085 | 88.8396 | 96.4489 | 104.664 | 112.6826 | 120.7358
WatfordWind2090RCP8.5 | Watford | Wind | RCP8.5 | 2090 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
WatfordWind2095RCP8.5 | Watford | Wind | RCP8.5 | 2095 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
WatfordWind2100RCP8.5 | Watford | Wind | RCP8.5 | 2100 | 89.1824 | 96.8818 | 105.203 | 113.3117 | 121.462
WawaIce Accretion2023RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2023 | 12.9761 | 15.4778 | 18.666 | 21.0926 | 23.5192
WawaIce Accretion2025RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2025 | 12.9741 | 15.4729 | 18.654 | 21.0756 | 23.5003
WawaIce Accretion2030RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2030 | 12.972 | 15.4679 | 18.642 | 21.0587 | 23.4814
WawaIce Accretion2035RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2035 | 12.9699 | 15.4629 | 18.63 | 21.0417 | 23.4625
WawaIce Accretion2040RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2040 | 12.9678 | 15.4579 | 18.618 | 21.0248 | 23.4436
WawaIce Accretion2045RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2045 | 12.9657 | 15.4529 | 18.606 | 21.0078 | 23.4247
WawaIce Accretion2050RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2050 | 13.0162 | 15.5137 | 18.6768 | 21.0885 | 23.5146
WawaIce Accretion2055RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2055 | 13.0688 | 15.5794 | 18.7596 | 21.1861 | 23.6235
WawaIce Accretion2060RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2060 | 13.1214 | 15.6452 | 18.8424 | 21.2838 | 23.7324
WawaIce Accretion2065RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2065 | 13.174 | 15.7109 | 18.9252 | 21.3814 | 23.8412
WawaIce Accretion2070RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2070 | 13.2266 | 15.7766 | 19.008 | 21.479 | 23.9501
WawaIce Accretion2075RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2075 | 13.2392 | 15.7991 | 19.041 | 21.5231 | 24.003
WawaIce Accretion2080RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2080 | 13.2517 | 15.8215 | 19.074 | 21.5672 | 24.0559
WawaIce Accretion2085RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2085 | 13.2642 | 15.8439 | 19.107 | 21.6112 | 24.1088
WawaIce Accretion2090RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2090 | 13.2767 | 15.8663 | 19.14 | 21.6553 | 24.1618
WawaIce Accretion2095RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2095 | 13.2893 | 15.8887 | 19.173 | 21.6994 | 24.2147
WawaIce Accretion2100RCP4.5 | Wawa | Ice Accretion | RCP4.5 | 2100 | 13.3018 | 15.9111 | 19.206 | 21.7435 | 24.2676
WawaIce Accretion2023RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2023 | 12.9761 | 15.4778 | 18.666 | 21.0926 | 23.5192
WawaIce Accretion2025RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2025 | 12.9741 | 15.4729 | 18.654 | 21.0756 | 23.5003
WawaIce Accretion2030RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2030 | 12.972 | 15.4679 | 18.642 | 21.0587 | 23.4814
WawaIce Accretion2035RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2035 | 12.9699 | 15.4629 | 18.63 | 21.0417 | 23.4625
WawaIce Accretion2040RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2040 | 12.9678 | 15.4579 | 18.618 | 21.0248 | 23.4436
WawaIce Accretion2045RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2045 | 12.9657 | 15.4529 | 18.606 | 21.0078 | 23.4247
WawaIce Accretion2050RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2050 | 13.0162 | 15.5137 | 18.6768 | 21.0885 | 23.5146
WawaIce Accretion2055RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2055 | 13.0688 | 15.5794 | 18.7596 | 21.1861 | 23.6235
WawaIce Accretion2060RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2060 | 13.1214 | 15.6452 | 18.8424 | 21.2838 | 23.7324
WawaIce Accretion2065RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2065 | 13.174 | 15.7109 | 18.9252 | 21.3814 | 23.8412
WawaIce Accretion2070RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2070 | 13.2266 | 15.7766 | 19.008 | 21.479 | 23.9501
WawaIce Accretion2075RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2075 | 13.2454 | 15.8103 | 19.0575 | 21.5451 | 24.0295
WawaIce Accretion2080RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2080 | 13.2642 | 15.8439 | 19.107 | 21.6112 | 24.1088
WawaIce Accretion2085RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2085 | 13.283 | 15.8775 | 19.1565 | 21.6774 | 24.1882
WawaIce Accretion2090RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2090 | 13.1557 | 15.7468 | 19.026 | 21.5401 | 24.0484
WawaIce Accretion2095RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2095 | 13.0095 | 15.5824 | 18.846 | 21.3367 | 23.8291
WawaIce Accretion2100RCP6.0 | Wawa | Ice Accretion | RCP6.0 | 2100 | 12.8634 | 15.4181 | 18.666 | 21.1333 | 23.6099
WawaIce Accretion2023RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2023 | 12.9761 | 15.4778 | 18.666 | 21.0926 | 23.5192
WawaIce Accretion2025RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2025 | 12.972 | 15.4679 | 18.642 | 21.0587 | 23.4814
WawaIce Accretion2030RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2030 | 12.9678 | 15.4579 | 18.618 | 21.0248 | 23.4436
WawaIce Accretion2035RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2035 | 12.9636 | 15.448 | 18.594 | 20.9909 | 23.4058
WawaIce Accretion2040RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2040 | 13.0513 | 15.5575 | 18.732 | 21.1536 | 23.5872
WawaIce Accretion2045RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2045 | 13.139 | 15.6671 | 18.87 | 21.3163 | 23.7686
WawaIce Accretion2050RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2050 | 13.2517 | 15.8215 | 19.074 | 21.5672 | 24.0559
WawaIce Accretion2055RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2055 | 13.2767 | 15.8663 | 19.14 | 21.6553 | 24.1618
WawaIce Accretion2060RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2060 | 13.1557 | 15.7468 | 19.026 | 21.5401 | 24.0484
WawaIce Accretion2065RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2065 | 13.0095 | 15.5824 | 18.846 | 21.3367 | 23.8291
WawaIce Accretion2070RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2070 | 12.9594 | 15.5426 | 18.822 | 21.3231 | 23.8216
WawaIce Accretion2075RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2075 | 13.0555 | 15.6671 | 18.978 | 21.5129 | 24.0332
WawaIce Accretion2080RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2080 | 13.1515 | 15.7916 | 19.134 | 21.7028 | 24.2449
WawaIce Accretion2085RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2085 | 13.0638 | 15.7169 | 19.062 | 21.6316 | 24.1769
WawaIce Accretion2090RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2090 | 12.9761 | 15.6422 | 18.99 | 21.5604 | 24.1088
WawaIce Accretion2095RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2095 | 12.9761 | 15.6422 | 18.99 | 21.5604 | 24.1088
WawaIce Accretion2100RCP8.5 | Wawa | Ice Accretion | RCP8.5 | 2100 | 12.9761 | 15.6422 | 18.99 | 21.5604 | 24.1088
WawaWind2023RCP4.5 | Wawa | Wind | RCP4.5 | 2023 | 82.3118 | 88.7138 | 95.4758 | 102.2094 | 108.9496
WawaWind2025RCP4.5 | Wawa | Wind | RCP4.5 | 2025 | 82.3957 | 88.8143 | 95.5949 | 102.3469 | 109.1032
WawaWind2030RCP4.5 | Wawa | Wind | RCP4.5 | 2030 | 82.4796 | 88.9149 | 95.7139 | 102.4843 | 109.2568
WawaWind2035RCP4.5 | Wawa | Wind | RCP4.5 | 2035 | 82.5634 | 89.0154 | 95.833 | 102.6218 | 109.4104
WawaWind2040RCP4.5 | Wawa | Wind | RCP4.5 | 2040 | 82.6473 | 89.1159 | 95.9521 | 102.7592 | 109.564
WawaWind2045RCP4.5 | Wawa | Wind | RCP4.5 | 2045 | 82.7312 | 89.2165 | 96.0711 | 102.8967 | 109.7176
WawaWind2050RCP4.5 | Wawa | Wind | RCP4.5 | 2050 | 82.7907 | 89.2681 | 96.1094 | 102.9275 | 109.7383
WawaWind2055RCP4.5 | Wawa | Wind | RCP4.5 | 2055 | 82.7663 | 89.2191 | 96.0285 | 102.8209 | 109.6054
WawaWind2060RCP4.5 | Wawa | Wind | RCP4.5 | 2060 | 82.742 | 89.1701 | 95.9477 | 102.7143 | 109.4725
WawaWind2065RCP4.5 | Wawa | Wind | RCP4.5 | 2065 | 82.7176 | 89.1212 | 95.8668 | 102.6077 | 109.3396
WawaWind2070RCP4.5 | Wawa | Wind | RCP4.5 | 2070 | 82.6933 | 89.0722 | 95.786 | 102.5011 | 109.2068
WawaWind2075RCP4.5 | Wawa | Wind | RCP4.5 | 2075 | 82.7325 | 89.113 | 95.8283 | 102.5463 | 109.255
WawaWind2080RCP4.5 | Wawa | Wind | RCP4.5 | 2080 | 82.7718 | 89.1538 | 95.8706 | 102.5916 | 109.3032
WawaWind2085RCP4.5 | Wawa | Wind | RCP4.5 | 2085 | 82.811 | 89.1946 | 95.9129 | 102.6369 | 109.3514
WawaWind2090RCP4.5 | Wawa | Wind | RCP4.5 | 2090 | 82.8502 | 89.2354 | 95.9552 | 102.6821 | 109.3996
WawaWind2095RCP4.5 | Wawa | Wind | RCP4.5 | 2095 | 82.8894 | 89.2762 | 95.9975 | 102.7274 | 109.4479
WawaWind2100RCP4.5 | Wawa | Wind | RCP4.5 | 2100 | 82.9287 | 89.317 | 96.0398 | 102.7726 | 109.4961
WawaWind2023RCP6.0 | Wawa | Wind | RCP6.0 | 2023 | 82.3118 | 88.7138 | 95.4758 | 102.2094 | 108.9496
WawaWind2025RCP6.0 | Wawa | Wind | RCP6.0 | 2025 | 82.3957 | 88.8143 | 95.5949 | 102.3469 | 109.1032
WawaWind2030RCP6.0 | Wawa | Wind | RCP6.0 | 2030 | 82.4796 | 88.9149 | 95.7139 | 102.4843 | 109.2568
WawaWind2035RCP6.0 | Wawa | Wind | RCP6.0 | 2035 | 82.5634 | 89.0154 | 95.833 | 102.6218 | 109.4104
WawaWind2040RCP6.0 | Wawa | Wind | RCP6.0 | 2040 | 82.6473 | 89.1159 | 95.9521 | 102.7592 | 109.564
WawaWind2045RCP6.0 | Wawa | Wind | RCP6.0 | 2045 | 82.7312 | 89.2165 | 96.0711 | 102.8967 | 109.7176
WawaWind2050RCP6.0 | Wawa | Wind | RCP6.0 | 2050 | 82.7907 | 89.2681 | 96.1094 | 102.9275 | 109.7383
WawaWind2055RCP6.0 | Wawa | Wind | RCP6.0 | 2055 | 82.7663 | 89.2191 | 96.0285 | 102.8209 | 109.6054
WawaWind2060RCP6.0 | Wawa | Wind | RCP6.0 | 2060 | 82.742 | 89.1701 | 95.9477 | 102.7143 | 109.4725
WawaWind2065RCP6.0 | Wawa | Wind | RCP6.0 | 2065 | 82.7176 | 89.1212 | 95.8668 | 102.6077 | 109.3396
WawaWind2070RCP6.0 | Wawa | Wind | RCP6.0 | 2070 | 82.6933 | 89.0722 | 95.786 | 102.5011 | 109.2068
WawaWind2075RCP6.0 | Wawa | Wind | RCP6.0 | 2075 | 82.7521 | 89.1334 | 95.8494 | 102.569 | 109.2791
WawaWind2080RCP6.0 | Wawa | Wind | RCP6.0 | 2080 | 82.811 | 89.1946 | 95.9129 | 102.6369 | 109.3514
WawaWind2085RCP6.0 | Wawa | Wind | RCP6.0 | 2085 | 82.8698 | 89.2558 | 95.9763 | 102.7048 | 109.4238
WawaWind2090RCP6.0 | Wawa | Wind | RCP6.0 | 2090 | 83.1722 | 89.5968 | 96.3563 | 103.1213 | 109.8819
WawaWind2095RCP6.0 | Wawa | Wind | RCP6.0 | 2095 | 83.4157 | 89.8765 | 96.6727 | 103.47 | 110.2676
WawaWind2100RCP6.0 | Wawa | Wind | RCP6.0 | 2100 | 83.6592 | 90.1562 | 96.9892 | 103.8187 | 110.6534
WawaWind2023RCP8.5 | Wawa | Wind | RCP8.5 | 2023 | 82.3118 | 88.7138 | 95.4758 | 102.2094 | 108.9496
WawaWind2025RCP8.5 | Wawa | Wind | RCP8.5 | 2025 | 82.4796 | 88.9149 | 95.7139 | 102.4843 | 109.2568
WawaWind2030RCP8.5 | Wawa | Wind | RCP8.5 | 2030 | 82.6473 | 89.1159 | 95.9521 | 102.7592 | 109.564
WawaWind2035RCP8.5 | Wawa | Wind | RCP8.5 | 2035 | 82.815 | 89.317 | 96.1902 | 103.0342 | 109.8711
WawaWind2040RCP8.5 | Wawa | Wind | RCP8.5 | 2040 | 82.7745 | 89.2354 | 96.0555 | 102.8565 | 109.6497
WawaWind2045RCP8.5 | Wawa | Wind | RCP8.5 | 2045 | 82.7339 | 89.1538 | 95.9207 | 102.6788 | 109.4282
WawaWind2050RCP8.5 | Wawa | Wind | RCP8.5 | 2050 | 82.7718 | 89.1538 | 95.8706 | 102.5916 | 109.3032
WawaWind2055RCP8.5 | Wawa | Wind | RCP8.5 | 2055 | 82.8502 | 89.2354 | 95.9552 | 102.6821 | 109.3996
WawaWind2060RCP8.5 | Wawa | Wind | RCP8.5 | 2060 | 83.1722 | 89.5968 | 96.3563 | 103.1213 | 109.8819
WawaWind2065RCP8.5 | Wawa | Wind | RCP8.5 | 2065 | 83.4157 | 89.8765 | 96.6727 | 103.47 | 110.2676
WawaWind2070RCP8.5 | Wawa | Wind | RCP8.5 | 2070 | 83.7539 | 90.2466 | 97.0738 | 103.8991 | 110.7249
WawaWind2075RCP8.5 | Wawa | Wind | RCP8.5 | 2075 | 83.8486 | 90.3369 | 97.1584 | 103.9796 | 110.7963
WawaWind2080RCP8.5 | Wawa | Wind | RCP8.5 | 2080 | 83.9433 | 90.4272 | 97.243 | 104.0601 | 110.8677
WawaWind2085RCP8.5 | Wawa | Wind | RCP8.5 | 2085 | 84.1746 | 90.6939 | 97.5532 | 104.4071 | 111.2589
WawaWind2090RCP8.5 | Wawa | Wind | RCP8.5 | 2090 | 84.4059 | 90.9605 | 97.8634 | 104.7541 | 111.65
WawaWind2095RCP8.5 | Wawa | Wind | RCP8.5 | 2095 | 84.4059 | 90.9605 | 97.8634 | 104.7541 | 111.65
WawaWind2100RCP8.5 | Wawa | Wind | RCP8.5 | 2100 | 84.4059 | 90.9605 | 97.8634 | 104.7541 | 111.65
WellandIce Accretion2023RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
WellandIce Accretion2025RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2025 | 21.9182 | 26.3121 | 31.8773 | 36.1299 | 40.3738
WellandIce Accretion2030RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2030 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
WellandIce Accretion2035RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2035 | 21.7104 | 26.0819 | 31.632 | 35.8526 | 40.0781
WellandIce Accretion2040RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2040 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
WellandIce Accretion2045RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2045 | 21.5026 | 25.8517 | 31.3867 | 35.5754 | 39.7824
WellandIce Accretion2050RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2050 | 20.9221 | 25.2001 | 30.6368 | 34.7425 | 38.8765
WellandIce Accretion2055RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2055 | 20.4456 | 24.6636 | 30.0096 | 34.0483 | 38.1185
WellandIce Accretion2060RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2060 | 19.9691 | 24.1271 | 29.3824 | 33.354 | 37.3605
WellandIce Accretion2065RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2065 | 19.4926 | 23.5906 | 28.7552 | 32.6597 | 36.6025
WellandIce Accretion2070RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2070 | 19.0161 | 23.0541 | 28.128 | 31.9654 | 35.8445
WellandIce Accretion2075RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2075 | 18.8379 | 22.8682 | 27.9307 | 31.7605 | 35.6294
WellandIce Accretion2080RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2080 | 18.6598 | 22.6822 | 27.7333 | 31.5556 | 35.4144
WellandIce Accretion2085RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2085 | 18.4817 | 22.4963 | 27.536 | 31.3507 | 35.1994
WellandIce Accretion2090RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2090 | 18.3035 | 22.3104 | 27.3387 | 31.1458 | 34.9843
WellandIce Accretion2095RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2095 | 18.1254 | 22.1245 | 27.1413 | 30.9409 | 34.7693
WellandIce Accretion2100RCP4.5 | Welland | Ice Accretion | RCP4.5 | 2100 | 17.9473 | 21.9386 | 26.944 | 30.736 | 34.5542
WellandIce Accretion2023RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
WellandIce Accretion2025RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2025 | 21.9182 | 26.3121 | 31.8773 | 36.1299 | 40.3738
WellandIce Accretion2030RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2030 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
WellandIce Accretion2035RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2035 | 21.7104 | 26.0819 | 31.632 | 35.8526 | 40.0781
WellandIce Accretion2040RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2040 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
WellandIce Accretion2045RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2045 | 21.5026 | 25.8517 | 31.3867 | 35.5754 | 39.7824
WellandIce Accretion2050RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2050 | 20.9221 | 25.2001 | 30.6368 | 34.7425 | 38.8765
WellandIce Accretion2055RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2055 | 20.4456 | 24.6636 | 30.0096 | 34.0483 | 38.1185
WellandIce Accretion2060RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2060 | 19.9691 | 24.1271 | 29.3824 | 33.354 | 37.3605
WellandIce Accretion2065RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2065 | 19.4926 | 23.5906 | 28.7552 | 32.6597 | 36.6025
WellandIce Accretion2070RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2070 | 19.0161 | 23.0541 | 28.128 | 31.9654 | 35.8445
WellandIce Accretion2075RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2075 | 18.7489 | 22.7752 | 27.832 | 31.6581 | 35.5219
WellandIce Accretion2080RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2080 | 18.4817 | 22.4963 | 27.536 | 31.3507 | 35.1994
WellandIce Accretion2085RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2085 | 18.2145 | 22.2174 | 27.24 | 31.0434 | 34.8768
WellandIce Accretion2090RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2090 | 17.2199 | 21.1063 | 25.9733 | 29.6633 | 33.3581
WellandIce Accretion2095RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2095 | 16.4925 | 20.2741 | 25.0027 | 28.5905 | 32.1619
WellandIce Accretion2100RCP6.0 | Welland | Ice Accretion | RCP6.0 | 2100 | 15.7651 | 19.4419 | 24.032 | 27.5178 | 30.9658
WellandIce Accretion2023RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2023 | 22.0221 | 26.4272 | 32 | 36.2685 | 40.5216
WellandIce Accretion2025RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2025 | 21.8143 | 26.197 | 31.7547 | 35.9913 | 40.2259
WellandIce Accretion2030RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2030 | 21.6065 | 25.9668 | 31.5093 | 35.714 | 39.9302
WellandIce Accretion2035RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2035 | 21.3987 | 25.7366 | 31.264 | 35.4368 | 39.6346
WellandIce Accretion2040RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2040 | 20.6045 | 24.8425 | 30.2187 | 34.2797 | 38.3712
WellandIce Accretion2045RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2045 | 19.8103 | 23.9483 | 29.1733 | 33.1226 | 37.1078
WellandIce Accretion2050RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2050 | 18.6598 | 22.6822 | 27.7333 | 31.5556 | 35.4144
WellandIce Accretion2055RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2055 | 18.3035 | 22.3104 | 27.3387 | 31.1458 | 34.9843
WellandIce Accretion2060RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2060 | 17.2199 | 21.1063 | 25.9733 | 29.6633 | 33.3581
WellandIce Accretion2065RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2065 | 16.4925 | 20.2741 | 25.0027 | 28.5905 | 32.1619
WellandIce Accretion2070RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2070 | 15.4014 | 19.0258 | 23.5627 | 26.9995 | 30.4013
WellandIce Accretion2075RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2075 | 15.0377 | 18.6097 | 23.0933 | 26.4812 | 29.8368
WellandIce Accretion2080RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2080 | 14.674 | 18.1936 | 22.624 | 25.9629 | 29.2723
WellandIce Accretion2085RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2085 | 13.8501 | 17.2242 | 21.456 | 24.643 | 27.8006
WellandIce Accretion2090RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2090 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
WellandIce Accretion2095RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2095 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
WellandIce Accretion2100RCP8.5 | Welland | Ice Accretion | RCP8.5 | 2100 | 13.0262 | 16.2547 | 20.288 | 23.3232 | 26.329
WellandWind2023RCP4.5 | Welland | Wind | RCP4.5 | 2023 | 88.11 | 95.1229 | 102.5655 | 109.9612 | 117.3507
WellandWind2025RCP4.5 | Welland | Wind | RCP4.5 | 2025 | 88.0809 | 95.0932 | 102.5335 | 109.927 | 117.3142
WellandWind2030RCP4.5 | Welland | Wind | RCP4.5 | 2030 | 88.0519 | 95.0634 | 102.5015 | 109.8928 | 117.2778
WellandWind2035RCP4.5 | Welland | Wind | RCP4.5 | 2035 | 88.0228 | 95.0337 | 102.4695 | 109.8586 | 117.2413
WellandWind2040RCP4.5 | Welland | Wind | RCP4.5 | 2040 | 87.9937 | 95.0039 | 102.4376 | 109.8243 | 117.2048
WellandWind2045RCP4.5 | Welland | Wind | RCP4.5 | 2045 | 87.9647 | 94.9742 | 102.4056 | 109.7901 | 117.1684
WellandWind2050RCP4.5 | Welland | Wind | RCP4.5 | 2050 | 87.9931 | 95.0177 | 102.4685 | 109.8661 | 117.2609
WellandWind2055RCP4.5 | Welland | Wind | RCP4.5 | 2055 | 88.0507 | 95.091 | 102.5635 | 109.9764 | 117.3898
WellandWind2060RCP4.5 | Welland | Wind | RCP4.5 | 2060 | 88.1083 | 95.1642 | 102.6584 | 110.0866 | 117.5188
WellandWind2065RCP4.5 | Welland | Wind | RCP4.5 | 2065 | 88.1658 | 95.2375 | 102.7534 | 110.1968 | 117.6477
WellandWind2070RCP4.5 | Welland | Wind | RCP4.5 | 2070 | 88.2234 | 95.3108 | 102.8483 | 110.307 | 117.7767
WellandWind2075RCP4.5 | Welland | Wind | RCP4.5 | 2075 | 88.3048 | 95.4251 | 103.0049 | 110.498 | 118.0051
WellandWind2080RCP4.5 | Welland | Wind | RCP4.5 | 2080 | 88.3862 | 95.5393 | 103.1614 | 110.6889 | 118.2334
WellandWind2085RCP4.5 | Welland | Wind | RCP4.5 | 2085 | 88.4676 | 95.6536 | 103.3179 | 110.8798 | 118.4618
WellandWind2090RCP4.5 | Welland | Wind | RCP4.5 | 2090 | 88.549 | 95.7679 | 103.4745 | 111.0707 | 118.6901
WellandWind2095RCP4.5 | Welland | Wind | RCP4.5 | 2095 | 88.6304 | 95.8822 | 103.6311 | 111.2617 | 118.9185
WellandWind2100RCP4.5 | Welland | Wind | RCP4.5 | 2100 | 88.7118 | 95.9965 | 103.7876 | 111.4526 | 119.1469
WellandWind2023RCP6.0 | Welland | Wind | RCP6.0 | 2023 | 88.11 | 95.1229 | 102.5655 | 109.9612 | 117.3507
WellandWind2025RCP6.0 | Welland | Wind | RCP6.0 | 2025 | 88.0809 | 95.0932 | 102.5335 | 109.927 | 117.3142
WellandWind2030RCP6.0 | Welland | Wind | RCP6.0 | 2030 | 88.0519 | 95.0634 | 102.5015 | 109.8928 | 117.2778
WellandWind2035RCP6.0 | Welland | Wind | RCP6.0 | 2035 | 88.0228 | 95.0337 | 102.4695 | 109.8586 | 117.2413
WellandWind2040RCP6.0 | Welland | Wind | RCP6.0 | 2040 | 87.9937 | 95.0039 | 102.4376 | 109.8243 | 117.2048
WellandWind2045RCP6.0 | Welland | Wind | RCP6.0 | 2045 | 87.9647 | 94.9742 | 102.4056 | 109.7901 | 117.1684
WellandWind2050RCP6.0 | Welland | Wind | RCP6.0 | 2050 | 87.9931 | 95.0177 | 102.4685 | 109.8661 | 117.2609
WellandWind2055RCP6.0 | Welland | Wind | RCP6.0 | 2055 | 88.0507 | 95.091 | 102.5635 | 109.9764 | 117.3898
WellandWind2060RCP6.0 | Welland | Wind | RCP6.0 | 2060 | 88.1083 | 95.1642 | 102.6584 | 110.0866 | 117.5188
WellandWind2065RCP6.0 | Welland | Wind | RCP6.0 | 2065 | 88.1658 | 95.2375 | 102.7534 | 110.1968 | 117.6477
WellandWind2070RCP6.0 | Welland | Wind | RCP6.0 | 2070 | 88.2234 | 95.3108 | 102.8483 | 110.307 | 117.7767
WellandWind2075RCP6.0 | Welland | Wind | RCP6.0 | 2075 | 88.3455 | 95.4822 | 103.0831 | 110.5934 | 118.1192
WellandWind2080RCP6.0 | Welland | Wind | RCP6.0 | 2080 | 88.4676 | 95.6536 | 103.3179 | 110.8798 | 118.4618
WellandWind2085RCP6.0 | Welland | Wind | RCP6.0 | 2085 | 88.5897 | 95.825 | 103.5528 | 111.1662 | 118.8043
WellandWind2090RCP6.0 | Welland | Wind | RCP6.0 | 2090 | 88.8978 | 96.2344 | 104.0872 | 111.8092 | 119.5614
WellandWind2095RCP6.0 | Welland | Wind | RCP6.0 | 2095 | 89.0839 | 96.4724 | 104.3869 | 112.1659 | 119.9759
WellandWind2100RCP6.0 | Welland | Wind | RCP6.0 | 2100 | 89.2699 | 96.7103 | 104.6865 | 112.5225 | 120.3904
WellandWind2023RCP8.5 | Welland | Wind | RCP8.5 | 2023 | 88.11 | 95.1229 | 102.5655 | 109.9612 | 117.3507
WellandWind2025RCP8.5 | Welland | Wind | RCP8.5 | 2025 | 88.0519 | 95.0634 | 102.5015 | 109.8928 | 117.2778
WellandWind2030RCP8.5 | Welland | Wind | RCP8.5 | 2030 | 87.9937 | 95.0039 | 102.4376 | 109.8243 | 117.2048
WellandWind2035RCP8.5 | Welland | Wind | RCP8.5 | 2035 | 87.9356 | 94.9444 | 102.3736 | 109.7559 | 117.1319
WellandWind2040RCP8.5 | Welland | Wind | RCP8.5 | 2040 | 88.0315 | 95.0666 | 102.5318 | 109.9396 | 117.3468
WellandWind2045RCP8.5 | Welland | Wind | RCP8.5 | 2045 | 88.1274 | 95.1887 | 102.6901 | 110.1233 | 117.5618
WellandWind2050RCP8.5 | Welland | Wind | RCP8.5 | 2050 | 88.3862 | 95.5393 | 103.1614 | 110.6889 | 118.2334
WellandWind2055RCP8.5 | Welland | Wind | RCP8.5 | 2055 | 88.549 | 95.7679 | 103.4745 | 111.0707 | 118.6901
WellandWind2060RCP8.5 | Welland | Wind | RCP8.5 | 2060 | 88.8978 | 96.2344 | 104.0872 | 111.8092 | 119.5614
WellandWind2065RCP8.5 | Welland | Wind | RCP8.5 | 2065 | 89.0839 | 96.4724 | 104.3869 | 112.1659 | 119.9759
WellandWind2070RCP8.5 | Welland | Wind | RCP8.5 | 2070 | 89.331 | 96.8137 | 104.8515 | 112.7386 | 120.6514
WellandWind2075RCP8.5 | Welland | Wind | RCP8.5 | 2075 | 89.392 | 96.917 | 105.0164 | 112.9548 | 120.9124
WellandWind2080RCP8.5 | Welland | Wind | RCP8.5 | 2080 | 89.4531 | 97.0203 | 105.1814 | 113.1709 | 121.1733
WellandWind2085RCP8.5 | Welland | Wind | RCP8.5 | 2085 | 89.5185 | 97.1283 | 105.338 | 113.3654 | 121.4151
WellandWind2090RCP8.5 | Welland | Wind | RCP8.5 | 2090 | 89.5839 | 97.2363 | 105.4945 | 113.56 | 121.6569
WellandWind2095RCP8.5 | Welland | Wind | RCP8.5 | 2095 | 89.5839 | 97.2363 | 105.4945 | 113.56 | 121.6569
WellandWind2100RCP8.5 | Welland | Wind | RCP8.5 | 2100 | 89.5839 | 97.2363 | 105.4945 | 113.56 | 121.6569
West LorneIce Accretion2023RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2023 | 20.5414 | 24.6261 | 29.79 | 33.7305 | 37.6866
West LorneIce Accretion2025RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2025 | 20.4126 | 24.4974 | 29.66 | 33.5949 | 37.5417
West LorneIce Accretion2030RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2030 | 20.2839 | 24.3688 | 29.53 | 33.4593 | 37.3968
West LorneIce Accretion2035RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2035 | 20.1552 | 24.2401 | 29.4 | 33.3237 | 37.2519
West LorneIce Accretion2040RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2040 | 20.0265 | 24.1115 | 29.27 | 33.1881 | 37.107
West LorneIce Accretion2045RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2045 | 19.8977 | 23.9828 | 29.14 | 33.0525 | 36.9621
West LorneIce Accretion2050RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2050 | 19.2972 | 23.3263 | 28.404 | 32.2525 | 36.0914
West LorneIce Accretion2055RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2055 | 18.8254 | 22.7984 | 27.798 | 31.588 | 35.3657
West LorneIce Accretion2060RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2060 | 18.3536 | 22.2706 | 27.192 | 30.9236 | 34.6399
West LorneIce Accretion2065RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2065 | 17.8819 | 21.7427 | 26.586 | 30.2591 | 33.9142
West LorneIce Accretion2070RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2070 | 17.4101 | 21.2148 | 25.98 | 29.5947 | 33.1884
West LorneIce Accretion2075RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2075 | 16.9543 | 20.6877 | 25.365 | 28.911 | 32.4324
West LorneIce Accretion2080RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2080 | 16.4985 | 20.1607 | 24.75 | 28.2274 | 31.6764
West LorneIce Accretion2085RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2085 | 16.0427 | 19.6336 | 24.135 | 27.5437 | 30.9204
West LorneIce Accretion2090RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2090 | 15.587 | 19.1066 | 23.52 | 26.8601 | 30.1644
West LorneIce Accretion2095RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2095 | 15.1312 | 18.5795 | 22.905 | 26.1764 | 29.4084
West LorneIce Accretion2100RCP4.5 | West Lorne | Ice Accretion | RCP4.5 | 2100 | 14.6754 | 18.0525 | 22.29 | 25.4928 | 28.6524
West LorneIce Accretion2023RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2023 | 20.5414 | 24.6261 | 29.79 | 33.7305 | 37.6866
West LorneIce Accretion2025RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2025 | 20.4126 | 24.4974 | 29.66 | 33.5949 | 37.5417
West LorneIce Accretion2030RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2030 | 20.2839 | 24.3688 | 29.53 | 33.4593 | 37.3968
West LorneIce Accretion2035RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2035 | 20.1552 | 24.2401 | 29.4 | 33.3237 | 37.2519
West LorneIce Accretion2040RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2040 | 20.0265 | 24.1115 | 29.27 | 33.1881 | 37.107
West LorneIce Accretion2045RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2045 | 19.8977 | 23.9828 | 29.14 | 33.0525 | 36.9621
West LorneIce Accretion2050RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2050 | 19.2972 | 23.3263 | 28.404 | 32.2525 | 36.0914
West LorneIce Accretion2055RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2055 | 18.8254 | 22.7984 | 27.798 | 31.588 | 35.3657
West LorneIce Accretion2060RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2060 | 18.3536 | 22.2706 | 27.192 | 30.9236 | 34.6399
West LorneIce Accretion2065RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2065 | 17.8819 | 21.7427 | 26.586 | 30.2591 | 33.9142
West LorneIce Accretion2070RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2070 | 17.4101 | 21.2148 | 25.98 | 29.5947 | 33.1884
West LorneIce Accretion2075RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2075 | 16.7264 | 20.4242 | 25.0575 | 28.5692 | 32.0544
West LorneIce Accretion2080RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2080 | 16.0427 | 19.6336 | 24.135 | 27.5437 | 30.9204
West LorneIce Accretion2085RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2085 | 15.3591 | 18.8431 | 23.2125 | 26.5183 | 29.7864
West LorneIce Accretion2090RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2090 | 13.6316 | 16.8075 | 20.78 | 23.7865 | 26.7498
West LorneIce Accretion2095RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2095 | 12.5879 | 15.5625 | 19.27 | 22.0802 | 24.8472
West LorneIce Accretion2100RCP6.0 | West Lorne | Ice Accretion | RCP6.0 | 2100 | 11.5441 | 14.3175 | 17.76 | 20.3739 | 22.9446
West LorneIce Accretion2023RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2023 | 20.5414 | 24.6261 | 29.79 | 33.7305 | 37.6866
West LorneIce Accretion2025RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2025 | 20.2839 | 24.3688 | 29.53 | 33.4593 | 37.3968
West LorneIce Accretion2030RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2030 | 20.0265 | 24.1115 | 29.27 | 33.1881 | 37.107
West LorneIce Accretion2035RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2035 | 19.769 | 23.8542 | 29.01 | 32.9169 | 36.8172
West LorneIce Accretion2040RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2040 | 18.9827 | 22.9744 | 28 | 31.8095 | 35.6076
West LorneIce Accretion2045RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2045 | 18.1964 | 22.0946 | 26.99 | 30.7021 | 34.398
West LorneIce Accretion2050RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2050 | 16.4985 | 20.1607 | 24.75 | 28.2274 | 31.6764
West LorneIce Accretion2055RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2055 | 15.587 | 19.1066 | 23.52 | 26.8601 | 30.1644
West LorneIce Accretion2060RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2060 | 13.6316 | 16.8075 | 20.78 | 23.7865 | 26.7498
West LorneIce Accretion2065RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2065 | 12.5879 | 15.5625 | 19.27 | 22.0802 | 24.8472
West LorneIce Accretion2070RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2070 | 10.9665 | 13.6286 | 16.93 | 19.4247 | 21.8862
West LorneIce Accretion2075RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2075 | 10.389 | 12.9397 | 16.1 | 18.4755 | 20.8278
West LorneIce Accretion2080RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2080 | 9.8114 | 12.2508 | 15.27 | 17.5263 | 19.7694
West LorneIce Accretion2085RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2085 | 9.0182 | 11.2921 | 14.115 | 16.2211 | 18.3141
West LorneIce Accretion2090RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2090 | 8.2249 | 10.3335 | 12.96 | 14.916 | 16.8588
West LorneIce Accretion2095RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2095 | 8.2249 | 10.3335 | 12.96 | 14.916 | 16.8588
West LorneIce Accretion2100RCP8.5 | West Lorne | Ice Accretion | RCP8.5 | 2100 | 8.2249 | 10.3335 | 12.96 | 14.916 | 16.8588
West LorneWind2023RCP4.5 | West Lorne | Wind | RCP4.5 | 2023 | 85.8694 | 92.5119 | 99.5148 | 106.5126 | 113.5146
West LorneWind2025RCP4.5 | West Lorne | Wind | RCP4.5 | 2025 | 85.9592 | 92.6332 | 99.6765 | 106.7086 | 113.7441
West LorneWind2030RCP4.5 | West Lorne | Wind | RCP4.5 | 2030 | 86.049 | 92.7544 | 99.8382 | 106.9046 | 113.9736
West LorneWind2035RCP4.5 | West Lorne | Wind | RCP4.5 | 2035 | 86.1387 | 92.8756 | 99.9999 | 107.1005 | 114.203
West LorneWind2040RCP4.5 | West Lorne | Wind | RCP4.5 | 2040 | 86.2285 | 92.9968 | 100.1616 | 107.2965 | 114.4325
West LorneWind2045RCP4.5 | West Lorne | Wind | RCP4.5 | 2045 | 86.3182 | 93.1181 | 100.3233 | 107.4925 | 114.662
West LorneWind2050RCP4.5 | West Lorne | Wind | RCP4.5 | 2050 | 86.5174 | 93.3848 | 100.6751 | 107.9172 | 115.1601
West LorneWind2055RCP4.5 | West Lorne | Wind | RCP4.5 | 2055 | 86.6268 | 93.5302 | 100.8652 | 108.1461 | 115.4287
West LorneWind2060RCP4.5 | West Lorne | Wind | RCP4.5 | 2060 | 86.7363 | 93.6757 | 101.0552 | 108.3749 | 115.6973
West LorneWind2065RCP4.5 | West Lorne | Wind | RCP4.5 | 2065 | 86.8457 | 93.8212 | 101.2453 | 108.6037 | 115.9659
West LorneWind2070RCP4.5 | West Lorne | Wind | RCP4.5 | 2070 | 86.9551 | 93.9666 | 101.4354 | 108.8325 | 116.2345
West LorneWind2075RCP4.5 | West Lorne | Wind | RCP4.5 | 2075 | 87.1403 | 94.2076 | 101.7456 | 109.1997 | 116.6634
West LorneWind2080RCP4.5 | West Lorne | Wind | RCP4.5 | 2080 | 87.3255 | 94.4485 | 102.0558 | 109.5669 | 117.0922
West LorneWind2085RCP4.5 | West Lorne | Wind | RCP4.5 | 2085 | 87.5107 | 94.6894 | 102.366 | 109.9342 | 117.5211
West LorneWind2090RCP4.5 | West Lorne | Wind | RCP4.5 | 2090 | 87.696 | 94.9303 | 102.6762 | 110.3014 | 117.95
West LorneWind2095RCP4.5 | West Lorne | Wind | RCP4.5 | 2095 | 87.8812 | 95.1712 | 102.9864 | 110.6686 | 118.3789
West LorneWind2100RCP4.5 | West Lorne | Wind | RCP4.5 | 2100 | 88.0664 | 95.4121 | 103.2966 | 111.0358 | 118.8077
West LorneWind2023RCP6.0 | West Lorne | Wind | RCP6.0 | 2023 | 85.8694 | 92.5119 | 99.5148 | 106.5126 | 113.5146
West LorneWind2025RCP6.0 | West Lorne | Wind | RCP6.0 | 2025 | 85.9592 | 92.6332 | 99.6765 | 106.7086 | 113.7441
West LorneWind2030RCP6.0 | West Lorne | Wind | RCP6.0 | 2030 | 86.049 | 92.7544 | 99.8382 | 106.9046 | 113.9736
West LorneWind2035RCP6.0 | West Lorne | Wind | RCP6.0 | 2035 | 86.1387 | 92.8756 | 99.9999 | 107.1005 | 114.203
West LorneWind2040RCP6.0 | West Lorne | Wind | RCP6.0 | 2040 | 86.2285 | 92.9968 | 100.1616 | 107.2965 | 114.4325
West LorneWind2045RCP6.0 | West Lorne | Wind | RCP6.0 | 2045 | 86.3182 | 93.1181 | 100.3233 | 107.4925 | 114.662
West LorneWind2050RCP6.0 | West Lorne | Wind | RCP6.0 | 2050 | 86.5174 | 93.3848 | 100.6751 | 107.9172 | 115.1601
West LorneWind2055RCP6.0 | West Lorne | Wind | RCP6.0 | 2055 | 86.6268 | 93.5302 | 100.8652 | 108.1461 | 115.4287
West LorneWind2060RCP6.0 | West Lorne | Wind | RCP6.0 | 2060 | 86.7363 | 93.6757 | 101.0552 | 108.3749 | 115.6973
West LorneWind2065RCP6.0 | West Lorne | Wind | RCP6.0 | 2065 | 86.8457 | 93.8212 | 101.2453 | 108.6037 | 115.9659
West LorneWind2070RCP6.0 | West Lorne | Wind | RCP6.0 | 2070 | 86.9551 | 93.9666 | 101.4354 | 108.8325 | 116.2345
West LorneWind2075RCP6.0 | West Lorne | Wind | RCP6.0 | 2075 | 87.2329 | 94.328 | 101.9007 | 109.3833 | 116.8778
West LorneWind2080RCP6.0 | West Lorne | Wind | RCP6.0 | 2080 | 87.5107 | 94.6894 | 102.366 | 109.9342 | 117.5211
West LorneWind2085RCP6.0 | West Lorne | Wind | RCP6.0 | 2085 | 87.7886 | 95.0508 | 102.8313 | 110.485 | 118.1644
West LorneWind2090RCP6.0 | West Lorne | Wind | RCP6.0 | 2090 | 88.4596 | 95.9062 | 103.917 | 111.7632 | 119.6466
West LorneWind2095RCP6.0 | West Lorne | Wind | RCP6.0 | 2095 | 88.8529 | 96.4004 | 104.5374 | 112.4906 | 120.4856
West LorneWind2100RCP6.0 | West Lorne | Wind | RCP6.0 | 2100 | 89.2461 | 96.8945 | 105.1578 | 113.218 | 121.3245
West LorneWind2023RCP8.5 | West Lorne | Wind | RCP8.5 | 2023 | 85.8694 | 92.5119 | 99.5148 | 106.5126 | 113.5146
West LorneWind2025RCP8.5 | West Lorne | Wind | RCP8.5 | 2025 | 86.049 | 92.7544 | 99.8382 | 106.9046 | 113.9736
West LorneWind2030RCP8.5 | West Lorne | Wind | RCP8.5 | 2030 | 86.2285 | 92.9968 | 100.1616 | 107.2965 | 114.4325
West LorneWind2035RCP8.5 | West Lorne | Wind | RCP8.5 | 2035 | 86.408 | 93.2393 | 100.485 | 107.6884 | 114.8915
West LorneWind2040RCP8.5 | West Lorne | Wind | RCP8.5 | 2040 | 86.5904 | 93.4817 | 100.8018 | 108.0698 | 115.3392
West LorneWind2045RCP8.5 | West Lorne | Wind | RCP8.5 | 2045 | 86.7727 | 93.7242 | 101.1186 | 108.4511 | 115.7868
West LorneWind2050RCP8.5 | West Lorne | Wind | RCP8.5 | 2050 | 87.3255 | 94.4485 | 102.0558 | 109.5669 | 117.0922
West LorneWind2055RCP8.5 | West Lorne | Wind | RCP8.5 | 2055 | 87.696 | 94.9303 | 102.6762 | 110.3014 | 117.95
West LorneWind2060RCP8.5 | West Lorne | Wind | RCP8.5 | 2060 | 88.4596 | 95.9062 | 103.917 | 111.7632 | 119.6466
West LorneWind2065RCP8.5 | West Lorne | Wind | RCP8.5 | 2065 | 88.8529 | 96.4004 | 104.5374 | 112.4906 | 120.4856
West LorneWind2070RCP8.5 | West Lorne | Wind | RCP8.5 | 2070 | 89.4285 | 97.1216 | 105.4383 | 113.5464 | 121.6969
West LorneWind2075RCP8.5 | West Lorne | Wind | RCP8.5 | 2075 | 89.6108 | 97.3487 | 105.7188 | 113.8748 | 122.0694
West LorneWind2080RCP8.5 | West Lorne | Wind | RCP8.5 | 2080 | 89.7932 | 97.5758 | 105.9993 | 114.2031 | 122.4418
West LorneWind2085RCP8.5 | West Lorne | Wind | RCP8.5 | 2085 | 90.2976 | 98.2111 | 106.8012 | 115.1459 | 123.5309
West LorneWind2090RCP8.5 | West Lorne | Wind | RCP8.5 | 2090 | 90.8019 | 98.8464 | 107.6031 | 116.0887 | 124.62
West LorneWind2095RCP8.5 | West Lorne | Wind | RCP8.5 | 2095 | 90.8019 | 98.8464 | 107.6031 | 116.0887 | 124.62
West LorneWind2100RCP8.5 | West Lorne | Wind | RCP8.5 | 2100 | 90.8019 | 98.8464 | 107.6031 | 116.0887 | 124.62
WhitbyIce Accretion2023RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
WhitbyIce Accretion2025RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
WhitbyIce Accretion2030RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
WhitbyIce Accretion2035RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
WhitbyIce Accretion2040RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
WhitbyIce Accretion2045RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
WhitbyIce Accretion2050RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
WhitbyIce Accretion2055RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
WhitbyIce Accretion2060RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
WhitbyIce Accretion2065RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
WhitbyIce Accretion2070RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
WhitbyIce Accretion2075RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
WhitbyIce Accretion2080RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
WhitbyIce Accretion2085RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
WhitbyIce Accretion2090RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
WhitbyIce Accretion2095RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
WhitbyIce Accretion2100RCP4.5 | Whitby | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
WhitbyIce Accretion2023RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
WhitbyIce Accretion2025RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
WhitbyIce Accretion2030RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
WhitbyIce Accretion2035RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
WhitbyIce Accretion2040RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
WhitbyIce Accretion2045RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
WhitbyIce Accretion2050RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
WhitbyIce Accretion2055RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
WhitbyIce Accretion2060RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
WhitbyIce Accretion2065RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
WhitbyIce Accretion2070RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
WhitbyIce Accretion2075RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
WhitbyIce Accretion2080RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
WhitbyIce Accretion2085RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
WhitbyIce Accretion2090RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
WhitbyIce Accretion2095RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
WhitbyIce Accretion2100RCP6.0 | Whitby | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
WhitbyIce Accretion2023RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
WhitbyIce Accretion2025RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
WhitbyIce Accretion2030RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
WhitbyIce Accretion2035RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
WhitbyIce Accretion2040RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
WhitbyIce Accretion2045RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
WhitbyIce Accretion2050RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
WhitbyIce Accretion2055RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
WhitbyIce Accretion2060RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
WhitbyIce Accretion2065RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
WhitbyIce Accretion2070RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
WhitbyIce Accretion2075RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
WhitbyIce Accretion2080RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
WhitbyIce Accretion2085RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
WhitbyIce Accretion2090RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
WhitbyIce Accretion2095RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
WhitbyIce Accretion2100RCP8.5 | Whitby | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
WhitbyWind2023RCP4.5 | Whitby | Wind | RCP4.5 | 2023 | 85.6899 | 92.2541 | 99.1584 | 106.0677 | 112.9729
WhitbyWind2025RCP4.5 | Whitby | Wind | RCP4.5 | 2025 | 85.7056 | 92.2879 | 99.2129 | 106.1401 | 113.0631
WhitbyWind2030RCP4.5 | Whitby | Wind | RCP4.5 | 2030 | 85.7213 | 92.3217 | 99.2673 | 106.2125 | 113.1534
WhitbyWind2035RCP4.5 | Whitby | Wind | RCP4.5 | 2035 | 85.7369 | 92.3554 | 99.3217 | 106.2849 | 113.2437
WhitbyWind2040RCP4.5 | Whitby | Wind | RCP4.5 | 2040 | 85.7526 | 92.3892 | 99.3762 | 106.3573 | 113.334
WhitbyWind2045RCP4.5 | Whitby | Wind | RCP4.5 | 2045 | 85.7683 | 92.4229 | 99.4306 | 106.4296 | 113.4243
WhitbyWind2050RCP4.5 | Whitby | Wind | RCP4.5 | 2050 | 85.8677 | 92.5617 | 99.6178 | 106.6567 | 113.6952
WhitbyWind2055RCP4.5 | Whitby | Wind | RCP4.5 | 2055 | 85.9515 | 92.6666 | 99.7504 | 106.8113 | 113.8757
WhitbyWind2060RCP4.5 | Whitby | Wind | RCP4.5 | 2060 | 86.0353 | 92.7716 | 99.8831 | 106.966 | 114.0563
WhitbyWind2065RCP4.5 | Whitby | Wind | RCP4.5 | 2065 | 86.1191 | 92.8765 | 100.0157 | 107.1207 | 114.2369
WhitbyWind2070RCP4.5 | Whitby | Wind | RCP4.5 | 2070 | 86.2028 | 92.9815 | 100.1484 | 107.2753 | 114.4175
WhitbyWind2075RCP4.5 | Whitby | Wind | RCP4.5 | 2075 | 86.3482 | 93.1687 | 100.3877 | 107.5596 | 114.7466
WhitbyWind2080RCP4.5 | Whitby | Wind | RCP4.5 | 2080 | 86.4935 | 93.3559 | 100.6269 | 107.8438 | 115.0758
WhitbyWind2085RCP4.5 | Whitby | Wind | RCP4.5 | 2085 | 86.6388 | 93.5431 | 100.8662 | 108.128 | 115.405
WhitbyWind2090RCP4.5 | Whitby | Wind | RCP4.5 | 2090 | 86.7841 | 93.7303 | 101.1054 | 108.4123 | 115.7342
WhitbyWind2095RCP4.5 | Whitby | Wind | RCP4.5 | 2095 | 86.9295 | 93.9175 | 101.3447 | 108.6965 | 116.0633
WhitbyWind2100RCP4.5 | Whitby | Wind | RCP4.5 | 2100 | 87.0748 | 94.1047 | 101.5839 | 108.9808 | 116.3925
WhitbyWind2023RCP6.0 | Whitby | Wind | RCP6.0 | 2023 | 85.6899 | 92.2541 | 99.1584 | 106.0677 | 112.9729
WhitbyWind2025RCP6.0 | Whitby | Wind | RCP6.0 | 2025 | 85.7056 | 92.2879 | 99.2129 | 106.1401 | 113.0631
WhitbyWind2030RCP6.0 | Whitby | Wind | RCP6.0 | 2030 | 85.7213 | 92.3217 | 99.2673 | 106.2125 | 113.1534
WhitbyWind2035RCP6.0 | Whitby | Wind | RCP6.0 | 2035 | 85.7369 | 92.3554 | 99.3217 | 106.2849 | 113.2437
WhitbyWind2040RCP6.0 | Whitby | Wind | RCP6.0 | 2040 | 85.7526 | 92.3892 | 99.3762 | 106.3573 | 113.334
WhitbyWind2045RCP6.0 | Whitby | Wind | RCP6.0 | 2045 | 85.7683 | 92.4229 | 99.4306 | 106.4296 | 113.4243
WhitbyWind2050RCP6.0 | Whitby | Wind | RCP6.0 | 2050 | 85.8677 | 92.5617 | 99.6178 | 106.6567 | 113.6952
WhitbyWind2055RCP6.0 | Whitby | Wind | RCP6.0 | 2055 | 85.9515 | 92.6666 | 99.7504 | 106.8113 | 113.8757
WhitbyWind2060RCP6.0 | Whitby | Wind | RCP6.0 | 2060 | 86.0353 | 92.7716 | 99.8831 | 106.966 | 114.0563
WhitbyWind2065RCP6.0 | Whitby | Wind | RCP6.0 | 2065 | 86.1191 | 92.8765 | 100.0157 | 107.1207 | 114.2369
WhitbyWind2070RCP6.0 | Whitby | Wind | RCP6.0 | 2070 | 86.2028 | 92.9815 | 100.1484 | 107.2753 | 114.4175
WhitbyWind2075RCP6.0 | Whitby | Wind | RCP6.0 | 2075 | 86.4208 | 93.2623 | 100.5073 | 107.7017 | 114.9112
WhitbyWind2080RCP6.0 | Whitby | Wind | RCP6.0 | 2080 | 86.6388 | 93.5431 | 100.8662 | 108.128 | 115.405
WhitbyWind2085RCP6.0 | Whitby | Wind | RCP6.0 | 2085 | 86.8568 | 93.8239 | 101.225 | 108.5544 | 115.8988
WhitbyWind2090RCP6.0 | Whitby | Wind | RCP6.0 | 2090 | 87.525 | 94.6572 | 102.267 | 109.7753 | 117.3029
WhitbyWind2095RCP6.0 | Whitby | Wind | RCP6.0 | 2095 | 87.9752 | 95.2096 | 102.9501 | 110.5697 | 118.2133
WhitbyWind2100RCP6.0 | Whitby | Wind | RCP6.0 | 2100 | 88.4254 | 95.762 | 103.6332 | 111.3642 | 119.1237
WhitbyWind2023RCP8.5 | Whitby | Wind | RCP8.5 | 2023 | 85.6899 | 92.2541 | 99.1584 | 106.0677 | 112.9729
WhitbyWind2025RCP8.5 | Whitby | Wind | RCP8.5 | 2025 | 85.7213 | 92.3217 | 99.2673 | 106.2125 | 113.1534
WhitbyWind2030RCP8.5 | Whitby | Wind | RCP8.5 | 2030 | 85.7526 | 92.3892 | 99.3762 | 106.3573 | 113.334
WhitbyWind2035RCP8.5 | Whitby | Wind | RCP8.5 | 2035 | 85.784 | 92.4567 | 99.4851 | 106.502 | 113.5146
WhitbyWind2040RCP8.5 | Whitby | Wind | RCP8.5 | 2040 | 85.9236 | 92.6316 | 99.7062 | 106.7598 | 113.8155
WhitbyWind2045RCP8.5 | Whitby | Wind | RCP8.5 | 2045 | 86.0632 | 92.8066 | 99.9273 | 107.0175 | 114.1165
WhitbyWind2050RCP8.5 | Whitby | Wind | RCP8.5 | 2050 | 86.4935 | 93.3559 | 100.6269 | 107.8438 | 115.0758
WhitbyWind2055RCP8.5 | Whitby | Wind | RCP8.5 | 2055 | 86.7841 | 93.7303 | 101.1054 | 108.4123 | 115.7342
WhitbyWind2060RCP8.5 | Whitby | Wind | RCP8.5 | 2060 | 87.525 | 94.6572 | 102.267 | 109.7753 | 117.3029
WhitbyWind2065RCP8.5 | Whitby | Wind | RCP8.5 | 2065 | 87.9752 | 95.2096 | 102.9501 | 110.5697 | 118.2133
WhitbyWind2070RCP8.5 | Whitby | Wind | RCP8.5 | 2070 | 88.5594 | 95.9431 | 103.8741 | 111.6608 | 119.4698
WhitbyWind2075RCP8.5 | Whitby | Wind | RCP8.5 | 2075 | 88.6933 | 96.1241 | 104.115 | 111.9574 | 119.8159
WhitbyWind2080RCP8.5 | Whitby | Wind | RCP8.5 | 2080 | 88.8272 | 96.3052 | 104.3559 | 112.254 | 120.162
WhitbyWind2085RCP8.5 | Whitby | Wind | RCP8.5 | 2085 | 89.1136 | 96.7103 | 104.9103 | 112.932 | 120.969
WhitbyWind2090RCP8.5 | Whitby | Wind | RCP8.5 | 2090 | 89.4 | 97.1154 | 105.4647 | 113.6099 | 121.7759
WhitbyWind2095RCP8.5 | Whitby | Wind | RCP8.5 | 2095 | 89.4 | 97.1154 | 105.4647 | 113.6099 | 121.7759
WhitbyWind2100RCP8.5 | Whitby | Wind | RCP8.5 | 2100 | 89.4 | 97.1154 | 105.4647 | 113.6099 | 121.7759
Whitby (Brooklin)Ice Accretion2023RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
Whitby (Brooklin)Ice Accretion2025RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
Whitby (Brooklin)Ice Accretion2030RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
Whitby (Brooklin)Ice Accretion2035RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
Whitby (Brooklin)Ice Accretion2040RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
Whitby (Brooklin)Ice Accretion2045RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
Whitby (Brooklin)Ice Accretion2050RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
Whitby (Brooklin)Ice Accretion2055RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
Whitby (Brooklin)Ice Accretion2060RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
Whitby (Brooklin)Ice Accretion2065RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
Whitby (Brooklin)Ice Accretion2070RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
Whitby (Brooklin)Ice Accretion2075RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2075 | 15.7754 | 19.1937 | 23.4792 | 26.748 | 30.0195
Whitby (Brooklin)Ice Accretion2080RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2080 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
Whitby (Brooklin)Ice Accretion2085RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2085 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
Whitby (Brooklin)Ice Accretion2090RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2090 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
Whitby (Brooklin)Ice Accretion2095RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2095 | 15.6246 | 19.1107 | 23.4958 | 26.8422 | 30.1455
Whitby (Brooklin)Ice Accretion2100RCP4.5 | Whitby (Brooklin) | Ice Accretion | RCP4.5 | 2100 | 15.587 | 19.09 | 23.5 | 26.8657 | 30.177
Whitby (Brooklin)Ice Accretion2023RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
Whitby (Brooklin)Ice Accretion2025RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2025 | 16.9352 | 20.3454 | 24.6583 | 27.9345 | 31.2218
Whitby (Brooklin)Ice Accretion2030RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2030 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
Whitby (Brooklin)Ice Accretion2035RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2035 | 16.883 | 20.3246 | 24.675 | 27.9816 | 31.2952
Whitby (Brooklin)Ice Accretion2040RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2040 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
Whitby (Brooklin)Ice Accretion2045RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2045 | 16.8308 | 20.3039 | 24.6917 | 28.0287 | 31.3687
Whitby (Brooklin)Ice Accretion2050RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2050 | 16.6064 | 20.0777 | 24.455 | 27.7867 | 31.122
Whitby (Brooklin)Ice Accretion2055RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2055 | 16.4081 | 19.8619 | 24.21 | 27.5211 | 30.8385
Whitby (Brooklin)Ice Accretion2060RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2060 | 16.2097 | 19.6461 | 23.965 | 27.2556 | 30.555
Whitby (Brooklin)Ice Accretion2065RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2065 | 16.0114 | 19.4303 | 23.72 | 26.99 | 30.2715
Whitby (Brooklin)Ice Accretion2070RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2070 | 15.8131 | 19.2145 | 23.475 | 26.7245 | 29.988
Whitby (Brooklin)Ice Accretion2075RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2075 | 15.7566 | 19.1834 | 23.4813 | 26.7598 | 30.0352
Whitby (Brooklin)Ice Accretion2080RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2080 | 15.7 | 19.1522 | 23.4875 | 26.7951 | 30.0825
Whitby (Brooklin)Ice Accretion2085RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2085 | 15.6435 | 19.1211 | 23.4937 | 26.8304 | 30.1298
Whitby (Brooklin)Ice Accretion2090RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2090 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
Whitby (Brooklin)Ice Accretion2095RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2095 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
Whitby (Brooklin)Ice Accretion2100RCP6.0 | Whitby (Brooklin) | Ice Accretion | RCP6.0 | 2100 | 14.491 | 17.928 | 22.225 | 25.4815 | 28.728
Whitby (Brooklin)Ice Accretion2023RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2023 | 16.9612 | 20.3558 | 24.65 | 27.911 | 31.185
Whitby (Brooklin)Ice Accretion2025RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2025 | 16.9091 | 20.335 | 24.6667 | 27.9581 | 31.2585
Whitby (Brooklin)Ice Accretion2030RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2030 | 16.8569 | 20.3142 | 24.6833 | 28.0052 | 31.332
Whitby (Brooklin)Ice Accretion2035RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2035 | 16.8047 | 20.2935 | 24.7 | 28.0522 | 31.4055
Whitby (Brooklin)Ice Accretion2040RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2040 | 16.4742 | 19.9338 | 24.2917 | 27.6097 | 30.933
Whitby (Brooklin)Ice Accretion2045RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2045 | 16.1436 | 19.5742 | 23.8833 | 27.1671 | 30.4605
Whitby (Brooklin)Ice Accretion2050RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2050 | 15.7377 | 19.173 | 23.4833 | 26.7716 | 30.051
Whitby (Brooklin)Ice Accretion2055RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2055 | 15.6623 | 19.1315 | 23.4917 | 26.8187 | 30.114
Whitby (Brooklin)Ice Accretion2060RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2060 | 15.2216 | 18.7027 | 23.075 | 26.4043 | 29.694
Whitby (Brooklin)Ice Accretion2065RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2065 | 14.8563 | 18.3153 | 22.65 | 25.9429 | 29.211
Whitby (Brooklin)Ice Accretion2070RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2070 | 14.0735 | 17.4646 | 21.7 | 24.9071 | 28.1085
Whitby (Brooklin)Ice Accretion2075RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2075 | 13.656 | 17.0012 | 21.175 | 24.3327 | 27.489
Whitby (Brooklin)Ice Accretion2080RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2080 | 13.2385 | 16.5377 | 20.65 | 23.7582 | 26.8695
Whitby (Brooklin)Ice Accretion2085RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2085 | 12.3339 | 15.4484 | 19.3375 | 22.2892 | 25.2157
Whitby (Brooklin)Ice Accretion2090RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2090 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
Whitby (Brooklin)Ice Accretion2095RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2095 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
Whitby (Brooklin)Ice Accretion2100RCP8.5 | Whitby (Brooklin) | Ice Accretion | RCP8.5 | 2100 | 11.4293 | 14.359 | 18.025 | 20.8202 | 23.562
Whitby (Brooklin)Wind2023RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2023 | 82.2277 | 88.5267 | 95.152 | 101.7821 | 108.4083
Whitby (Brooklin)Wind2025RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2025 | 82.2427 | 88.5591 | 95.2043 | 101.8516 | 108.4949
Whitby (Brooklin)Wind2030RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2030 | 82.2578 | 88.5915 | 95.2565 | 101.9211 | 108.5816
Whitby (Brooklin)Wind2035RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2035 | 82.2728 | 88.6239 | 95.3088 | 101.9905 | 108.6682
Whitby (Brooklin)Wind2040RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2040 | 82.2879 | 88.6563 | 95.361 | 102.06 | 108.7549
Whitby (Brooklin)Wind2045RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2045 | 82.3029 | 88.6887 | 95.4132 | 102.1294 | 108.8415
Whitby (Brooklin)Wind2050RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2050 | 82.3983 | 88.8218 | 95.5928 | 102.3473 | 109.1014
Whitby (Brooklin)Wind2055RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2055 | 82.4787 | 88.9225 | 95.7201 | 102.4957 | 109.2747
Whitby (Brooklin)Wind2060RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2060 | 82.5591 | 89.0232 | 95.8474 | 102.6441 | 109.448
Whitby (Brooklin)Wind2065RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2065 | 82.6395 | 89.1239 | 95.9747 | 102.7925 | 109.6213
Whitby (Brooklin)Wind2070RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2070 | 82.7199 | 89.2247 | 96.102 | 102.941 | 109.7945
Whitby (Brooklin)Wind2075RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2075 | 82.8593 | 89.4043 | 96.3316 | 103.2137 | 110.1104
Whitby (Brooklin)Wind2080RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2080 | 82.9988 | 89.584 | 96.5612 | 103.4865 | 110.4263
Whitby (Brooklin)Wind2085RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2085 | 83.1382 | 89.7636 | 96.7908 | 103.7592 | 110.7422
Whitby (Brooklin)Wind2090RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2090 | 83.2777 | 89.9432 | 97.0203 | 104.032 | 111.058
Whitby (Brooklin)Wind2095RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2095 | 83.4172 | 90.1229 | 97.2499 | 104.3048 | 111.3739
Whitby (Brooklin)Wind2100RCP4.5 | Whitby (Brooklin) | Wind | RCP4.5 | 2100 | 83.5566 | 90.3025 | 97.4795 | 104.5775 | 111.6898
Whitby (Brooklin)Wind2023RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2023 | 82.2277 | 88.5267 | 95.152 | 101.7821 | 108.4083
Whitby (Brooklin)Wind2025RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2025 | 82.2427 | 88.5591 | 95.2043 | 101.8516 | 108.4949
Whitby (Brooklin)Wind2030RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2030 | 82.2578 | 88.5915 | 95.2565 | 101.9211 | 108.5816
Whitby (Brooklin)Wind2035RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2035 | 82.2728 | 88.6239 | 95.3088 | 101.9905 | 108.6682
Whitby (Brooklin)Wind2040RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2040 | 82.2879 | 88.6563 | 95.361 | 102.06 | 108.7549
Whitby (Brooklin)Wind2045RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2045 | 82.3029 | 88.6887 | 95.4132 | 102.1294 | 108.8415
Whitby (Brooklin)Wind2050RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2050 | 82.3983 | 88.8218 | 95.5928 | 102.3473 | 109.1014
Whitby (Brooklin)Wind2055RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2055 | 82.4787 | 88.9225 | 95.7201 | 102.4957 | 109.2747
Whitby (Brooklin)Wind2060RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2060 | 82.5591 | 89.0232 | 95.8474 | 102.6441 | 109.448
Whitby (Brooklin)Wind2065RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2065 | 82.6395 | 89.1239 | 95.9747 | 102.7925 | 109.6213
Whitby (Brooklin)Wind2070RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2070 | 82.7199 | 89.2247 | 96.102 | 102.941 | 109.7945
Whitby (Brooklin)Wind2075RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2075 | 82.9291 | 89.4941 | 96.4464 | 103.3501 | 110.2684
Whitby (Brooklin)Wind2080RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2080 | 83.1382 | 89.7636 | 96.7908 | 103.7592 | 110.7422
Whitby (Brooklin)Wind2085RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2085 | 83.3474 | 90.0331 | 97.1351 | 104.1684 | 111.216
Whitby (Brooklin)Wind2090RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2090 | 83.9886 | 90.8326 | 98.135 | 105.3399 | 112.5634
Whitby (Brooklin)Wind2095RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2095 | 84.4207 | 91.3627 | 98.7905 | 106.1023 | 113.437
Whitby (Brooklin)Wind2100RCP6.0 | Whitby (Brooklin) | Wind | RCP6.0 | 2100 | 84.8527 | 91.8928 | 99.446 | 106.8646 | 114.3107
Whitby (Brooklin)Wind2023RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2023 | 82.2277 | 88.5267 | 95.152 | 101.7821 | 108.4083
Whitby (Brooklin)Wind2025RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2025 | 82.2578 | 88.5915 | 95.2565 | 101.9211 | 108.5816
Whitby (Brooklin)Wind2030RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2030 | 82.2879 | 88.6563 | 95.361 | 102.06 | 108.7549
Whitby (Brooklin)Wind2035RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2035 | 82.3179 | 88.7211 | 95.4655 | 102.1989 | 108.9281
Whitby (Brooklin)Wind2040RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2040 | 82.4519 | 88.8889 | 95.6777 | 102.4463 | 109.2169
Whitby (Brooklin)Wind2045RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2045 | 82.5859 | 89.0568 | 95.8898 | 102.6936 | 109.5057
Whitby (Brooklin)Wind2050RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2050 | 82.9988 | 89.584 | 96.5612 | 103.4865 | 110.4263
Whitby (Brooklin)Wind2055RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2055 | 83.2777 | 89.9432 | 97.0203 | 104.032 | 111.058
Whitby (Brooklin)Wind2060RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2060 | 83.9886 | 90.8326 | 98.135 | 105.3399 | 112.5634
Whitby (Brooklin)Wind2065RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2065 | 84.4207 | 91.3627 | 98.7905 | 106.1023 | 113.437
Whitby (Brooklin)Wind2070RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2070 | 84.9812 | 92.0666 | 99.6772 | 107.1493 | 114.6428
Whitby (Brooklin)Wind2075RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2075 | 85.1097 | 92.2403 | 99.9083 | 107.4339 | 114.9749
Whitby (Brooklin)Wind2080RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2080 | 85.2382 | 92.4141 | 100.1395 | 107.7185 | 115.307
Whitby (Brooklin)Wind2085RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2085 | 85.513 | 92.8028 | 100.6715 | 108.3691 | 116.0814
Whitby (Brooklin)Wind2090RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2090 | 85.7878 | 93.1916 | 101.2035 | 109.0196 | 116.8557
Whitby (Brooklin)Wind2095RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2095 | 85.7878 | 93.1916 | 101.2035 | 109.0196 | 116.8557
Whitby (Brooklin)Wind2100RCP8.5 | Whitby (Brooklin) | Wind | RCP8.5 | 2100 | 85.7878 | 93.1916 | 101.2035 | 109.0196 | 116.8557
White RiverIce Accretion2023RCP4.5 | White River | Ice Accretion | RCP4.5 | 2023 | 10.6569 | 12.6741 | 15.225 | 17.1873 | 19.1457
White RiverIce Accretion2025RCP4.5 | White River | Ice Accretion | RCP4.5 | 2025 | 10.7039 | 12.7301 | 15.2925 | 17.2608 | 19.2276
White RiverIce Accretion2030RCP4.5 | White River | Ice Accretion | RCP4.5 | 2030 | 10.7508 | 12.7861 | 15.36 | 17.3342 | 19.3095
White RiverIce Accretion2035RCP4.5 | White River | Ice Accretion | RCP4.5 | 2035 | 10.7978 | 12.8422 | 15.4275 | 17.4077 | 19.3914
White RiverIce Accretion2040RCP4.5 | White River | Ice Accretion | RCP4.5 | 2040 | 10.8448 | 12.8982 | 15.495 | 17.4811 | 19.4733
White RiverIce Accretion2045RCP4.5 | White River | Ice Accretion | RCP4.5 | 2045 | 10.8917 | 12.9542 | 15.5625 | 17.5545 | 19.5552
White RiverIce Accretion2050RCP4.5 | White River | Ice Accretion | RCP4.5 | 2050 | 10.9825 | 13.065 | 15.699 | 17.7127 | 19.7316
White RiverIce Accretion2055RCP4.5 | White River | Ice Accretion | RCP4.5 | 2055 | 11.0264 | 13.1198 | 15.768 | 17.7975 | 19.8261
White RiverIce Accretion2060RCP4.5 | White River | Ice Accretion | RCP4.5 | 2060 | 11.0702 | 13.1746 | 15.837 | 17.8822 | 19.9206
White RiverIce Accretion2065RCP4.5 | White River | Ice Accretion | RCP4.5 | 2065 | 11.1141 | 13.2294 | 15.906 | 17.967 | 20.0151
White RiverIce Accretion2070RCP4.5 | White River | Ice Accretion | RCP4.5 | 2070 | 11.1579 | 13.2841 | 15.975 | 18.0517 | 20.1096
White RiverIce Accretion2075RCP4.5 | White River | Ice Accretion | RCP4.5 | 2075 | 11.177 | 13.3111 | 16.015 | 18.0969 | 20.1632
White RiverIce Accretion2080RCP4.5 | White River | Ice Accretion | RCP4.5 | 2080 | 11.1962 | 13.3381 | 16.055 | 18.1421 | 20.2167
White RiverIce Accretion2085RCP4.5 | White River | Ice Accretion | RCP4.5 | 2085 | 11.2153 | 13.3651 | 16.095 | 18.1873 | 20.2702
White RiverIce Accretion2090RCP4.5 | White River | Ice Accretion | RCP4.5 | 2090 | 11.2344 | 13.392 | 16.135 | 18.2325 | 20.3238
White RiverIce Accretion2095RCP4.5 | White River | Ice Accretion | RCP4.5 | 2095 | 11.2536 | 13.419 | 16.175 | 18.2777 | 20.3773
White RiverIce Accretion2100RCP4.5 | White River | Ice Accretion | RCP4.5 | 2100 | 11.2727 | 13.446 | 16.215 | 18.3229 | 20.4309
White RiverIce Accretion2023RCP6.0 | White River | Ice Accretion | RCP6.0 | 2023 | 10.6569 | 12.6741 | 15.225 | 17.1873 | 19.1457
White RiverIce Accretion2025RCP6.0 | White River | Ice Accretion | RCP6.0 | 2025 | 10.7039 | 12.7301 | 15.2925 | 17.2608 | 19.2276
White RiverIce Accretion2030RCP6.0 | White River | Ice Accretion | RCP6.0 | 2030 | 10.7508 | 12.7861 | 15.36 | 17.3342 | 19.3095
White RiverIce Accretion2035RCP6.0 | White River | Ice Accretion | RCP6.0 | 2035 | 10.7978 | 12.8422 | 15.4275 | 17.4077 | 19.3914
White RiverIce Accretion2040RCP6.0 | White River | Ice Accretion | RCP6.0 | 2040 | 10.8448 | 12.8982 | 15.495 | 17.4811 | 19.4733
White RiverIce Accretion2045RCP6.0 | White River | Ice Accretion | RCP6.0 | 2045 | 10.8917 | 12.9542 | 15.5625 | 17.5545 | 19.5552
White RiverIce Accretion2050RCP6.0 | White River | Ice Accretion | RCP6.0 | 2050 | 10.9825 | 13.065 | 15.699 | 17.7127 | 19.7316
White RiverIce Accretion2055RCP6.0 | White River | Ice Accretion | RCP6.0 | 2055 | 11.0264 | 13.1198 | 15.768 | 17.7975 | 19.8261
White RiverIce Accretion2060RCP6.0 | White River | Ice Accretion | RCP6.0 | 2060 | 11.0702 | 13.1746 | 15.837 | 17.8822 | 19.9206
White RiverIce Accretion2065RCP6.0 | White River | Ice Accretion | RCP6.0 | 2065 | 11.1141 | 13.2294 | 15.906 | 17.967 | 20.0151
White RiverIce Accretion2070RCP6.0 | White River | Ice Accretion | RCP6.0 | 2070 | 11.1579 | 13.2841 | 15.975 | 18.0517 | 20.1096
White RiverIce Accretion2075RCP6.0 | White River | Ice Accretion | RCP6.0 | 2075 | 11.1866 | 13.3246 | 16.035 | 18.1195 | 20.1899
White RiverIce Accretion2080RCP6.0 | White River | Ice Accretion | RCP6.0 | 2080 | 11.2153 | 13.3651 | 16.095 | 18.1873 | 20.2702
White RiverIce Accretion2085RCP6.0 | White River | Ice Accretion | RCP6.0 | 2085 | 11.244 | 13.4055 | 16.155 | 18.2552 | 20.3506
White RiverIce Accretion2090RCP6.0 | White River | Ice Accretion | RCP6.0 | 2090 | 11.1718 | 13.3339 | 16.085 | 18.1817 | 20.2797
White RiverIce Accretion2095RCP6.0 | White River | Ice Accretion | RCP6.0 | 2095 | 11.0709 | 13.2219 | 15.955 | 18.0404 | 20.1285
White RiverIce Accretion2100RCP6.0 | White River | Ice Accretion | RCP6.0 | 2100 | 10.97 | 13.1098 | 15.825 | 17.8992 | 19.9773
White RiverIce Accretion2023RCP8.5 | White River | Ice Accretion | RCP8.5 | 2023 | 10.6569 | 12.6741 | 15.225 | 17.1873 | 19.1457
White RiverIce Accretion2025RCP8.5 | White River | Ice Accretion | RCP8.5 | 2025 | 10.7508 | 12.7861 | 15.36 | 17.3342 | 19.3095
White RiverIce Accretion2030RCP8.5 | White River | Ice Accretion | RCP8.5 | 2030 | 10.8448 | 12.8982 | 15.495 | 17.4811 | 19.4733
White RiverIce Accretion2035RCP8.5 | White River | Ice Accretion | RCP8.5 | 2035 | 10.9387 | 13.0102 | 15.63 | 17.628 | 19.6371
White RiverIce Accretion2040RCP8.5 | White River | Ice Accretion | RCP8.5 | 2040 | 11.0118 | 13.1015 | 15.745 | 17.7692 | 19.7946
White RiverIce Accretion2045RCP8.5 | White River | Ice Accretion | RCP8.5 | 2045 | 11.0848 | 13.1928 | 15.86 | 17.9105 | 19.9521
White RiverIce Accretion2050RCP8.5 | White River | Ice Accretion | RCP8.5 | 2050 | 11.1962 | 13.3381 | 16.055 | 18.1421 | 20.2167
White RiverIce Accretion2055RCP8.5 | White River | Ice Accretion | RCP8.5 | 2055 | 11.2344 | 13.392 | 16.135 | 18.2325 | 20.3238
White RiverIce Accretion2060RCP8.5 | White River | Ice Accretion | RCP8.5 | 2060 | 11.1718 | 13.3339 | 16.085 | 18.1817 | 20.2797
White RiverIce Accretion2065RCP8.5 | White River | Ice Accretion | RCP8.5 | 2065 | 11.0709 | 13.2219 | 15.955 | 18.0404 | 20.1285
White RiverIce Accretion2070RCP8.5 | White River | Ice Accretion | RCP8.5 | 2070 | 10.9874 | 13.1472 | 15.885 | 17.9726 | 20.0655
White RiverIce Accretion2075RCP8.5 | White River | Ice Accretion | RCP8.5 | 2075 | 11.0048 | 13.1845 | 15.945 | 18.0461 | 20.1537
White RiverIce Accretion2080RCP8.5 | White River | Ice Accretion | RCP8.5 | 2080 | 11.0222 | 13.2219 | 16.005 | 18.1195 | 20.2419
White RiverIce Accretion2085RCP8.5 | White River | Ice Accretion | RCP8.5 | 2085 | 10.9074 | 13.0849 | 15.8475 | 17.95 | 20.0529
White RiverIce Accretion2090RCP8.5 | White River | Ice Accretion | RCP8.5 | 2090 | 10.7926 | 12.948 | 15.69 | 17.7805 | 19.8639
White RiverIce Accretion2095RCP8.5 | White River | Ice Accretion | RCP8.5 | 2095 | 10.7926 | 12.948 | 15.69 | 17.7805 | 19.8639
White RiverIce Accretion2100RCP8.5 | White River | Ice Accretion | RCP8.5 | 2100 | 10.7926 | 12.948 | 15.69 | 17.7805 | 19.8639
White RiverWind2023RCP4.5 | White River | Wind | RCP4.5 | 2023 | 72.2926 | 77.7998 | 83.581 | 89.3784 | 95.1783
White RiverWind2025RCP4.5 | White River | Wind | RCP4.5 | 2025 | 72.3308 | 77.8435 | 83.6308 | 89.4332 | 95.2382
White RiverWind2030RCP4.5 | White River | Wind | RCP4.5 | 2030 | 72.369 | 77.8873 | 83.6806 | 89.4879 | 95.2981
White RiverWind2035RCP4.5 | White River | Wind | RCP4.5 | 2035 | 72.4072 | 77.931 | 83.7304 | 89.5427 | 95.358
White RiverWind2040RCP4.5 | White River | Wind | RCP4.5 | 2040 | 72.4455 | 77.9748 | 83.7802 | 89.5974 | 95.418
White RiverWind2045RCP4.5 | White River | Wind | RCP4.5 | 2045 | 72.4837 | 78.0185 | 83.83 | 89.6522 | 95.4779
White RiverWind2050RCP4.5 | White River | Wind | RCP4.5 | 2050 | 72.5491 | 78.0854 | 83.8997 | 89.7247 | 95.5511
White RiverWind2055RCP4.5 | White River | Wind | RCP4.5 | 2055 | 72.5764 | 78.1086 | 83.9196 | 89.7425 | 95.5643
White RiverWind2060RCP4.5 | White River | Wind | RCP4.5 | 2060 | 72.6036 | 78.1317 | 83.9396 | 89.7603 | 95.5776
White RiverWind2065RCP4.5 | White River | Wind | RCP4.5 | 2065 | 72.6308 | 78.1549 | 83.9595 | 89.778 | 95.5908
White RiverWind2070RCP4.5 | White River | Wind | RCP4.5 | 2070 | 72.6581 | 78.178 | 83.9794 | 89.7958 | 95.604
White RiverWind2075RCP4.5 | White River | Wind | RCP4.5 | 2075 | 72.7106 | 78.2334 | 84.0375 | 89.8565 | 95.6687
White RiverWind2080RCP4.5 | White River | Wind | RCP4.5 | 2080 | 72.7632 | 78.2887 | 84.0956 | 89.9172 | 95.7334
White RiverWind2085RCP4.5 | White River | Wind | RCP4.5 | 2085 | 72.8157 | 78.344 | 84.1537 | 89.9779 | 95.798
White RiverWind2090RCP4.5 | White River | Wind | RCP4.5 | 2090 | 72.8683 | 78.3993 | 84.2118 | 90.0385 | 95.8627
White RiverWind2095RCP4.5 | White River | Wind | RCP4.5 | 2095 | 72.9209 | 78.4546 | 84.2699 | 90.0992 | 95.9273
White RiverWind2100RCP4.5 | White River | Wind | RCP4.5 | 2100 | 72.9734 | 78.5099 | 84.328 | 90.1599 | 95.992
White RiverWind2023RCP6.0 | White River | Wind | RCP6.0 | 2023 | 72.2926 | 77.7998 | 83.581 | 89.3784 | 95.1783
White RiverWind2025RCP6.0 | White River | Wind | RCP6.0 | 2025 | 72.3308 | 77.8435 | 83.6308 | 89.4332 | 95.2382
White RiverWind2030RCP6.0 | White River | Wind | RCP6.0 | 2030 | 72.369 | 77.8873 | 83.6806 | 89.4879 | 95.2981
White RiverWind2035RCP6.0 | White River | Wind | RCP6.0 | 2035 | 72.4072 | 77.931 | 83.7304 | 89.5427 | 95.358
White RiverWind2040RCP6.0 | White River | Wind | RCP6.0 | 2040 | 72.4455 | 77.9748 | 83.7802 | 89.5974 | 95.418
White RiverWind2045RCP6.0 | White River | Wind | RCP6.0 | 2045 | 72.4837 | 78.0185 | 83.83 | 89.6522 | 95.4779
White RiverWind2050RCP6.0 | White River | Wind | RCP6.0 | 2050 | 72.5491 | 78.0854 | 83.8997 | 89.7247 | 95.5511
White RiverWind2055RCP6.0 | White River | Wind | RCP6.0 | 2055 | 72.5764 | 78.1086 | 83.9196 | 89.7425 | 95.5643
White RiverWind2060RCP6.0 | White River | Wind | RCP6.0 | 2060 | 72.6036 | 78.1317 | 83.9396 | 89.7603 | 95.5776
White RiverWind2065RCP6.0 | White River | Wind | RCP6.0 | 2065 | 72.6308 | 78.1549 | 83.9595 | 89.778 | 95.5908
White RiverWind2070RCP6.0 | White River | Wind | RCP6.0 | 2070 | 72.6581 | 78.178 | 83.9794 | 89.7958 | 95.604
White RiverWind2075RCP6.0 | White River | Wind | RCP6.0 | 2075 | 72.7369 | 78.261 | 84.0666 | 89.8868 | 95.701
White RiverWind2080RCP6.0 | White River | Wind | RCP6.0 | 2080 | 72.8157 | 78.344 | 84.1537 | 89.9779 | 95.798
White RiverWind2085RCP6.0 | White River | Wind | RCP6.0 | 2085 | 72.8946 | 78.427 | 84.2408 | 90.0689 | 95.895
White RiverWind2090RCP6.0 | White River | Wind | RCP6.0 | 2090 | 73.2266 | 78.8136 | 84.6904 | 90.5744 | 96.4588
White RiverWind2095RCP6.0 | White River | Wind | RCP6.0 | 2095 | 73.4799 | 79.1172 | 85.0529 | 90.9888 | 96.9256
White RiverWind2100RCP6.0 | White River | Wind | RCP6.0 | 2100 | 73.7331 | 79.4208 | 85.4153 | 91.4033 | 97.3924
White RiverWind2023RCP8.5 | White River | Wind | RCP8.5 | 2023 | 72.2926 | 77.7998 | 83.581 | 89.3784 | 95.1783
White RiverWind2025RCP8.5 | White River | Wind | RCP8.5 | 2025 | 72.369 | 77.8873 | 83.6806 | 89.4879 | 95.2981
White RiverWind2030RCP8.5 | White River | Wind | RCP8.5 | 2030 | 72.4455 | 77.9748 | 83.7802 | 89.5974 | 95.418
White RiverWind2035RCP8.5 | White River | Wind | RCP8.5 | 2035 | 72.5219 | 78.0622 | 83.8798 | 89.707 | 95.5378
White RiverWind2040RCP8.5 | White River | Wind | RCP8.5 | 2040 | 72.5673 | 78.1008 | 83.913 | 89.7366 | 95.5599
White RiverWind2045RCP8.5 | White River | Wind | RCP8.5 | 2045 | 72.6127 | 78.1394 | 83.9462 | 89.7662 | 95.582
White RiverWind2050RCP8.5 | White River | Wind | RCP8.5 | 2050 | 72.7632 | 78.2887 | 84.0956 | 89.9172 | 95.7334
White RiverWind2055RCP8.5 | White River | Wind | RCP8.5 | 2055 | 72.8683 | 78.3993 | 84.2118 | 90.0385 | 95.8627
White RiverWind2060RCP8.5 | White River | Wind | RCP8.5 | 2060 | 73.2266 | 78.8136 | 84.6904 | 90.5744 | 96.4588
White RiverWind2065RCP8.5 | White River | Wind | RCP8.5 | 2065 | 73.4799 | 79.1172 | 85.0529 | 90.9888 | 96.9256
White RiverWind2070RCP8.5 | White River | Wind | RCP8.5 | 2070 | 73.9338 | 79.6498 | 85.6754 | 91.6904 | 97.7078
White RiverWind2075RCP8.5 | White River | Wind | RCP8.5 | 2075 | 74.1345 | 79.8788 | 85.9354 | 91.9776 | 98.0232
White RiverWind2080RCP8.5 | White River | Wind | RCP8.5 | 2080 | 74.3351 | 80.1078 | 86.1955 | 92.2647 | 98.3386
White RiverWind2085RCP8.5 | White River | Wind | RCP8.5 | 2085 | 74.6075 | 80.4551 | 86.6312 | 92.7754 | 98.9252
White RiverWind2090RCP8.5 | White River | Wind | RCP8.5 | 2090 | 74.8798 | 80.8025 | 87.067 | 93.286 | 99.5119
White RiverWind2095RCP8.5 | White River | Wind | RCP8.5 | 2095 | 74.8798 | 80.8025 | 87.067 | 93.286 | 99.5119
White RiverWind2100RCP8.5 | White River | Wind | RCP8.5 | 2100 | 74.8798 | 80.8025 | 87.067 | 93.286 | 99.5119
WiartonIce Accretion2023RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2023 | 13.9865 | 16.7162 | 20.18 | 22.8486 | 25.4772
WiartonIce Accretion2025RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2025 | 13.9958 | 16.7383 | 20.2167 | 22.8938 | 25.536
WiartonIce Accretion2030RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2030 | 14.0051 | 16.7605 | 20.2533 | 22.939 | 25.5948
WiartonIce Accretion2035RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2035 | 14.0143 | 16.7826 | 20.29 | 22.9842 | 25.6536
WiartonIce Accretion2040RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2040 | 14.0236 | 16.8047 | 20.3267 | 23.0294 | 25.7124
WiartonIce Accretion2045RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2045 | 14.0329 | 16.8269 | 20.3633 | 23.0746 | 25.7712
WiartonIce Accretion2050RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2050 | 13.9921 | 16.8025 | 20.36 | 23.0836 | 25.7947
WiartonIce Accretion2055RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2055 | 13.942 | 16.756 | 20.32 | 23.0475 | 25.7594
WiartonIce Accretion2060RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2060 | 13.8919 | 16.7096 | 20.28 | 23.0113 | 25.7242
WiartonIce Accretion2065RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2065 | 13.8418 | 16.6631 | 20.24 | 22.9752 | 25.6889
WiartonIce Accretion2070RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2070 | 13.7917 | 16.6166 | 20.2 | 22.939 | 25.6536
WiartonIce Accretion2075RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2075 | 13.7406 | 16.5806 | 20.18 | 22.9277 | 25.6536
WiartonIce Accretion2080RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2080 | 13.6896 | 16.5447 | 20.16 | 22.9164 | 25.6536
WiartonIce Accretion2085RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2085 | 13.6386 | 16.5087 | 20.14 | 22.9051 | 25.6536
WiartonIce Accretion2090RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2090 | 13.5876 | 16.4727 | 20.12 | 22.8938 | 25.6536
WiartonIce Accretion2095RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2095 | 13.5365 | 16.4368 | 20.1 | 22.8825 | 25.6536
WiartonIce Accretion2100RCP4.5 | Wiarton | Ice Accretion | RCP4.5 | 2100 | 13.4855 | 16.4008 | 20.08 | 22.8712 | 25.6536
WiartonIce Accretion2023RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2023 | 13.9865 | 16.7162 | 20.18 | 22.8486 | 25.4772
WiartonIce Accretion2025RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2025 | 13.9958 | 16.7383 | 20.2167 | 22.8938 | 25.536
WiartonIce Accretion2030RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2030 | 14.0051 | 16.7605 | 20.2533 | 22.939 | 25.5948
WiartonIce Accretion2035RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2035 | 14.0143 | 16.7826 | 20.29 | 22.9842 | 25.6536
WiartonIce Accretion2040RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2040 | 14.0236 | 16.8047 | 20.3267 | 23.0294 | 25.7124
WiartonIce Accretion2045RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2045 | 14.0329 | 16.8269 | 20.3633 | 23.0746 | 25.7712
WiartonIce Accretion2050RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2050 | 13.9921 | 16.8025 | 20.36 | 23.0836 | 25.7947
WiartonIce Accretion2055RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2055 | 13.942 | 16.756 | 20.32 | 23.0475 | 25.7594
WiartonIce Accretion2060RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2060 | 13.8919 | 16.7096 | 20.28 | 23.0113 | 25.7242
WiartonIce Accretion2065RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2065 | 13.8418 | 16.6631 | 20.24 | 22.9752 | 25.6889
WiartonIce Accretion2070RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2070 | 13.7917 | 16.6166 | 20.2 | 22.939 | 25.6536
WiartonIce Accretion2075RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2075 | 13.7151 | 16.5626 | 20.17 | 22.922 | 25.6536
WiartonIce Accretion2080RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2080 | 13.6386 | 16.5087 | 20.14 | 22.9051 | 25.6536
WiartonIce Accretion2085RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2085 | 13.562 | 16.4547 | 20.11 | 22.8881 | 25.6536
WiartonIce Accretion2090RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2090 | 13.2489 | 16.1518 | 19.8067 | 22.5849 | 25.3512
WiartonIce Accretion2095RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2095 | 13.0123 | 15.9028 | 19.5333 | 22.2987 | 25.0488
WiartonIce Accretion2100RCP6.0 | Wiarton | Ice Accretion | RCP6.0 | 2100 | 12.7757 | 15.6538 | 19.26 | 22.0124 | 24.7464
WiartonIce Accretion2023RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2023 | 13.9865 | 16.7162 | 20.18 | 22.8486 | 25.4772
WiartonIce Accretion2025RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2025 | 14.0051 | 16.7605 | 20.2533 | 22.939 | 25.5948
WiartonIce Accretion2030RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2030 | 14.0236 | 16.8047 | 20.3267 | 23.0294 | 25.7124
WiartonIce Accretion2035RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2035 | 14.0422 | 16.849 | 20.4 | 23.1198 | 25.83
WiartonIce Accretion2040RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2040 | 13.9587 | 16.7715 | 20.3333 | 23.0595 | 25.7712
WiartonIce Accretion2045RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2045 | 13.8752 | 16.6941 | 20.2667 | 22.9993 | 25.7124
WiartonIce Accretion2050RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2050 | 13.6896 | 16.5447 | 20.16 | 22.9164 | 25.6536
WiartonIce Accretion2055RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2055 | 13.5876 | 16.4727 | 20.12 | 22.8938 | 25.6536
WiartonIce Accretion2060RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2060 | 13.2489 | 16.1518 | 19.8067 | 22.5849 | 25.3512
WiartonIce Accretion2065RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2065 | 13.0123 | 15.9028 | 19.5333 | 22.2987 | 25.0488
WiartonIce Accretion2070RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2070 | 12.4232 | 15.2609 | 18.82 | 21.5378 | 24.234
WiartonIce Accretion2075RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2075 | 12.0706 | 14.8681 | 18.38 | 21.0632 | 23.7216
WiartonIce Accretion2080RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2080 | 11.718 | 14.4752 | 17.94 | 20.5886 | 23.2092
WiartonIce Accretion2085RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2085 | 11.1196 | 13.7863 | 17.13 | 19.6733 | 22.2012
WiartonIce Accretion2090RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2090 | 10.5212 | 13.0974 | 16.32 | 18.758 | 21.1932
WiartonIce Accretion2095RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2095 | 10.5212 | 13.0974 | 16.32 | 18.758 | 21.1932
WiartonIce Accretion2100RCP8.5 | Wiarton | Ice Accretion | RCP8.5 | 2100 | 10.5212 | 13.0974 | 16.32 | 18.758 | 21.1932
WiartonWind2023RCP4.5 | Wiarton | Wind | RCP4.5 | 2023 | 82.8943 | 89.1818 | 95.7696 | 102.3913 | 109.0022
WiartonWind2025RCP4.5 | Wiarton | Wind | RCP4.5 | 2025 | 82.9703 | 89.2755 | 95.888 | 102.5283 | 109.1609
WiartonWind2030RCP4.5 | Wiarton | Wind | RCP4.5 | 2030 | 83.0463 | 89.3693 | 96.0064 | 102.6652 | 109.3196
WiartonWind2035RCP4.5 | Wiarton | Wind | RCP4.5 | 2035 | 83.1223 | 89.463 | 96.1248 | 102.8022 | 109.4783
WiartonWind2040RCP4.5 | Wiarton | Wind | RCP4.5 | 2040 | 83.1983 | 89.5568 | 96.2432 | 102.9391 | 109.637
WiartonWind2045RCP4.5 | Wiarton | Wind | RCP4.5 | 2045 | 83.2742 | 89.6505 | 96.3616 | 103.0761 | 109.7957
WiartonWind2050RCP4.5 | Wiarton | Wind | RCP4.5 | 2050 | 83.3469 | 89.7353 | 96.4608 | 103.1884 | 109.9215
WiartonWind2055RCP4.5 | Wiarton | Wind | RCP4.5 | 2055 | 83.3436 | 89.7264 | 96.4416 | 103.1638 | 109.8887
WiartonWind2060RCP4.5 | Wiarton | Wind | RCP4.5 | 2060 | 83.3403 | 89.7175 | 96.4224 | 103.1391 | 109.8559
WiartonWind2065RCP4.5 | Wiarton | Wind | RCP4.5 | 2065 | 83.337 | 89.7085 | 96.4032 | 103.1144 | 109.823
WiartonWind2070RCP4.5 | Wiarton | Wind | RCP4.5 | 2070 | 83.3337 | 89.6996 | 96.384 | 103.0898 | 109.7902
WiartonWind2075RCP4.5 | Wiarton | Wind | RCP4.5 | 2075 | 83.3516 | 89.719 | 96.4048 | 103.112 | 109.8139
WiartonWind2080RCP4.5 | Wiarton | Wind | RCP4.5 | 2080 | 83.3696 | 89.7383 | 96.4256 | 103.1343 | 109.8376
WiartonWind2085RCP4.5 | Wiarton | Wind | RCP4.5 | 2085 | 83.3875 | 89.7576 | 96.4464 | 103.1566 | 109.8613
WiartonWind2090RCP4.5 | Wiarton | Wind | RCP4.5 | 2090 | 83.4055 | 89.777 | 96.4672 | 103.1788 | 109.8851
WiartonWind2095RCP4.5 | Wiarton | Wind | RCP4.5 | 2095 | 83.4235 | 89.7963 | 96.488 | 103.2011 | 109.9088
WiartonWind2100RCP4.5 | Wiarton | Wind | RCP4.5 | 2100 | 83.4414 | 89.8157 | 96.5088 | 103.2233 | 109.9325
WiartonWind2023RCP6.0 | Wiarton | Wind | RCP6.0 | 2023 | 82.8943 | 89.1818 | 95.7696 | 102.3913 | 109.0022
WiartonWind2025RCP6.0 | Wiarton | Wind | RCP6.0 | 2025 | 82.9703 | 89.2755 | 95.888 | 102.5283 | 109.1609
WiartonWind2030RCP6.0 | Wiarton | Wind | RCP6.0 | 2030 | 83.0463 | 89.3693 | 96.0064 | 102.6652 | 109.3196
WiartonWind2035RCP6.0 | Wiarton | Wind | RCP6.0 | 2035 | 83.1223 | 89.463 | 96.1248 | 102.8022 | 109.4783
WiartonWind2040RCP6.0 | Wiarton | Wind | RCP6.0 | 2040 | 83.1983 | 89.5568 | 96.2432 | 102.9391 | 109.637
WiartonWind2045RCP6.0 | Wiarton | Wind | RCP6.0 | 2045 | 83.2742 | 89.6505 | 96.3616 | 103.0761 | 109.7957
WiartonWind2050RCP6.0 | Wiarton | Wind | RCP6.0 | 2050 | 83.3469 | 89.7353 | 96.4608 | 103.1884 | 109.9215
WiartonWind2055RCP6.0 | Wiarton | Wind | RCP6.0 | 2055 | 83.3436 | 89.7264 | 96.4416 | 103.1638 | 109.8887
WiartonWind2060RCP6.0 | Wiarton | Wind | RCP6.0 | 2060 | 83.3403 | 89.7175 | 96.4224 | 103.1391 | 109.8559
WiartonWind2065RCP6.0 | Wiarton | Wind | RCP6.0 | 2065 | 83.337 | 89.7085 | 96.4032 | 103.1144 | 109.823
WiartonWind2070RCP6.0 | Wiarton | Wind | RCP6.0 | 2070 | 83.3337 | 89.6996 | 96.384 | 103.0898 | 109.7902
WiartonWind2075RCP6.0 | Wiarton | Wind | RCP6.0 | 2075 | 83.3606 | 89.7286 | 96.4152 | 103.1232 | 109.8258
WiartonWind2080RCP6.0 | Wiarton | Wind | RCP6.0 | 2080 | 83.3875 | 89.7576 | 96.4464 | 103.1566 | 109.8613
WiartonWind2085RCP6.0 | Wiarton | Wind | RCP6.0 | 2085 | 83.4145 | 89.7867 | 96.4776 | 103.1899 | 109.8969
WiartonWind2090RCP6.0 | Wiarton | Wind | RCP6.0 | 2090 | 83.574 | 89.9764 | 96.704 | 103.4459 | 110.1805
WiartonWind2095RCP6.0 | Wiarton | Wind | RCP6.0 | 2095 | 83.7067 | 90.1371 | 96.8992 | 103.6684 | 110.4286
WiartonWind2100RCP6.0 | Wiarton | Wind | RCP6.0 | 2100 | 83.8393 | 90.2978 | 97.0944 | 103.891 | 110.6767
WiartonWind2023RCP8.5 | Wiarton | Wind | RCP8.5 | 2023 | 82.8943 | 89.1818 | 95.7696 | 102.3913 | 109.0022
WiartonWind2025RCP8.5 | Wiarton | Wind | RCP8.5 | 2025 | 83.0463 | 89.3693 | 96.0064 | 102.6652 | 109.3196
WiartonWind2030RCP8.5 | Wiarton | Wind | RCP8.5 | 2030 | 83.1983 | 89.5568 | 96.2432 | 102.9391 | 109.637
WiartonWind2035RCP8.5 | Wiarton | Wind | RCP8.5 | 2035 | 83.3502 | 89.7443 | 96.48 | 103.2131 | 109.9544
WiartonWind2040RCP8.5 | Wiarton | Wind | RCP8.5 | 2040 | 83.3447 | 89.7294 | 96.448 | 103.172 | 109.8996
WiartonWind2045RCP8.5 | Wiarton | Wind | RCP8.5 | 2045 | 83.3392 | 89.7145 | 96.416 | 103.1309 | 109.8449
WiartonWind2050RCP8.5 | Wiarton | Wind | RCP8.5 | 2050 | 83.3696 | 89.7383 | 96.4256 | 103.1343 | 109.8376
WiartonWind2055RCP8.5 | Wiarton | Wind | RCP8.5 | 2055 | 83.4055 | 89.777 | 96.4672 | 103.1788 | 109.8851
WiartonWind2060RCP8.5 | Wiarton | Wind | RCP8.5 | 2060 | 83.574 | 89.9764 | 96.704 | 103.4459 | 110.1805
WiartonWind2065RCP8.5 | Wiarton | Wind | RCP8.5 | 2065 | 83.7067 | 90.1371 | 96.8992 | 103.6684 | 110.4286
WiartonWind2070RCP8.5 | Wiarton | Wind | RCP8.5 | 2070 | 83.9084 | 90.3811 | 97.1904 | 104.0006 | 110.8044
WiartonWind2075RCP8.5 | Wiarton | Wind | RCP8.5 | 2075 | 83.9775 | 90.4644 | 97.2864 | 104.1101 | 110.932
WiartonWind2080RCP8.5 | Wiarton | Wind | RCP8.5 | 2080 | 84.0465 | 90.5478 | 97.3824 | 104.2197 | 111.0597
WiartonWind2085RCP8.5 | Wiarton | Wind | RCP8.5 | 2085 | 84.3657 | 90.9763 | 97.9536 | 104.9079 | 111.8641
WiartonWind2090RCP8.5 | Wiarton | Wind | RCP8.5 | 2090 | 84.6848 | 91.4049 | 98.5248 | 105.5962 | 112.6685
WiartonWind2095RCP8.5 | Wiarton | Wind | RCP8.5 | 2095 | 84.6848 | 91.4049 | 98.5248 | 105.5962 | 112.6685
WiartonWind2100RCP8.5 | Wiarton | Wind | RCP8.5 | 2100 | 84.6848 | 91.4049 | 98.5248 | 105.5962 | 112.6685
WindsorIce Accretion2023RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2023 | 17.1352 | 20.5218 | 24.825 | 28.0805 | 31.374
WindsorIce Accretion2025RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2025 | 17.0975 | 20.4941 | 24.8042 | 28.0711 | 31.3635
WindsorIce Accretion2030RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2030 | 17.0598 | 20.4664 | 24.7833 | 28.0617 | 31.353
WindsorIce Accretion2035RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2035 | 17.0221 | 20.4387 | 24.7625 | 28.0522 | 31.3425
WindsorIce Accretion2040RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2040 | 16.9844 | 20.4111 | 24.7417 | 28.0428 | 31.332
WindsorIce Accretion2045RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2045 | 16.9468 | 20.3834 | 24.7208 | 28.0334 | 31.3215
WindsorIce Accretion2050RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2050 | 16.5437 | 19.949 | 24.24 | 27.5155 | 30.7629
WindsorIce Accretion2055RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2055 | 16.1784 | 19.5423 | 23.78 | 27.007 | 30.2148
WindsorIce Accretion2060RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2060 | 15.8131 | 19.1357 | 23.32 | 26.4985 | 29.6667
WindsorIce Accretion2065RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2065 | 15.4478 | 18.729 | 22.86 | 25.99 | 29.1186
WindsorIce Accretion2070RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2070 | 15.0825 | 18.3223 | 22.4 | 25.4815 | 28.5705
WindsorIce Accretion2075RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2075 | 14.7374 | 17.928 | 21.9375 | 24.9683 | 28.0088
WindsorIce Accretion2080RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2080 | 14.3924 | 17.5338 | 21.475 | 24.4551 | 27.447
WindsorIce Accretion2085RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2085 | 14.0474 | 17.1395 | 21.0125 | 23.9419 | 26.8853
WindsorIce Accretion2090RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2090 | 13.7024 | 16.7452 | 20.55 | 23.4287 | 26.3235
WindsorIce Accretion2095RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2095 | 13.3573 | 16.351 | 20.0875 | 22.9155 | 25.7618
WindsorIce Accretion2100RCP4.5 | Windsor | Ice Accretion | RCP4.5 | 2100 | 13.0123 | 15.9567 | 19.625 | 22.4022 | 25.2
WindsorIce Accretion2023RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2023 | 17.1352 | 20.5218 | 24.825 | 28.0805 | 31.374
WindsorIce Accretion2025RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2025 | 17.0975 | 20.4941 | 24.8042 | 28.0711 | 31.3635
WindsorIce Accretion2030RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2030 | 17.0598 | 20.4664 | 24.7833 | 28.0617 | 31.353
WindsorIce Accretion2035RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2035 | 17.0221 | 20.4387 | 24.7625 | 28.0522 | 31.3425
WindsorIce Accretion2040RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2040 | 16.9844 | 20.4111 | 24.7417 | 28.0428 | 31.332
WindsorIce Accretion2045RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2045 | 16.9468 | 20.3834 | 24.7208 | 28.0334 | 31.3215
WindsorIce Accretion2050RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2050 | 16.5437 | 19.949 | 24.24 | 27.5155 | 30.7629
WindsorIce Accretion2055RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2055 | 16.1784 | 19.5423 | 23.78 | 27.007 | 30.2148
WindsorIce Accretion2060RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2060 | 15.8131 | 19.1357 | 23.32 | 26.4985 | 29.6667
WindsorIce Accretion2065RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2065 | 15.4478 | 18.729 | 22.86 | 25.99 | 29.1186
WindsorIce Accretion2070RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2070 | 15.0825 | 18.3223 | 22.4 | 25.4815 | 28.5705
WindsorIce Accretion2075RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2075 | 14.5649 | 17.7309 | 21.7063 | 24.7117 | 27.7279
WindsorIce Accretion2080RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2080 | 14.0474 | 17.1395 | 21.0125 | 23.9419 | 26.8853
WindsorIce Accretion2085RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2085 | 13.5299 | 16.5481 | 20.3188 | 23.1721 | 26.0426
WindsorIce Accretion2090RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2090 | 12.1773 | 14.9607 | 18.4333 | 21.0557 | 23.6985
WindsorIce Accretion2095RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2095 | 11.3423 | 13.9648 | 17.2417 | 19.7091 | 22.197
WindsorIce Accretion2100RCP6.0 | Windsor | Ice Accretion | RCP6.0 | 2100 | 10.5073 | 12.9688 | 16.05 | 18.3625 | 20.6955
WindsorIce Accretion2023RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2023 | 17.1352 | 20.5218 | 24.825 | 28.0805 | 31.374
WindsorIce Accretion2025RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2025 | 17.0598 | 20.4664 | 24.7833 | 28.0617 | 31.353
WindsorIce Accretion2030RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2030 | 16.9844 | 20.4111 | 24.7417 | 28.0428 | 31.332
WindsorIce Accretion2035RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2035 | 16.9091 | 20.3558 | 24.7 | 28.024 | 31.311
WindsorIce Accretion2040RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2040 | 16.3002 | 19.6779 | 23.9333 | 27.1765 | 30.3975
WindsorIce Accretion2045RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2045 | 15.6913 | 19.0001 | 23.1667 | 26.329 | 29.484
WindsorIce Accretion2050RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2050 | 14.3924 | 17.5338 | 21.475 | 24.4551 | 27.447
WindsorIce Accretion2055RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2055 | 13.7024 | 16.7452 | 20.55 | 23.4287 | 26.3235
WindsorIce Accretion2060RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2060 | 12.1773 | 14.9607 | 18.4333 | 21.0557 | 23.6985
WindsorIce Accretion2065RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2065 | 11.3423 | 13.9648 | 17.2417 | 19.7091 | 22.197
WindsorIce Accretion2070RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2070 | 9.9506 | 12.3117 | 15.2583 | 17.4679 | 19.698
WindsorIce Accretion2075RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2075 | 9.3939 | 11.6546 | 14.4667 | 16.5733 | 18.7005
WindsorIce Accretion2080RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2080 | 8.8372 | 10.9975 | 13.675 | 15.6787 | 17.703
WindsorIce Accretion2085RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2085 | 7.9413 | 9.9185 | 12.3625 | 14.1956 | 16.0335
WindsorIce Accretion2090RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2090 | 7.0454 | 8.8395 | 11.05 | 12.7125 | 14.364
WindsorIce Accretion2095RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2095 | 7.0454 | 8.8395 | 11.05 | 12.7125 | 14.364
WindsorIce Accretion2100RCP8.5 | Windsor | Ice Accretion | RCP8.5 | 2100 | 7.0454 | 8.8395 | 11.05 | 12.7125 | 14.364
WindsorWind2023RCP4.5 | Windsor | Wind | RCP4.5 | 2023 | 84.0928 | 90.5618 | 97.3686 | 104.174 | 110.9781
WindsorWind2025RCP4.5 | Windsor | Wind | RCP4.5 | 2025 | 84.1096 | 90.5829 | 97.3961 | 104.2069 | 111.0168
WindsorWind2030RCP4.5 | Windsor | Wind | RCP4.5 | 2030 | 84.1263 | 90.6039 | 97.4236 | 104.2398 | 111.0555
WindsorWind2035RCP4.5 | Windsor | Wind | RCP4.5 | 2035 | 84.1431 | 90.625 | 97.4511 | 104.2726 | 111.0942
WindsorWind2040RCP4.5 | Windsor | Wind | RCP4.5 | 2040 | 84.1598 | 90.646 | 97.4785 | 104.3055 | 111.1329
WindsorWind2045RCP4.5 | Windsor | Wind | RCP4.5 | 2045 | 84.1766 | 90.6671 | 97.506 | 104.3384 | 111.1716
WindsorWind2050RCP4.5 | Windsor | Wind | RCP4.5 | 2050 | 84.133 | 90.6033 | 97.4171 | 104.2301 | 111.0422
WindsorWind2055RCP4.5 | Windsor | Wind | RCP4.5 | 2055 | 84.0727 | 90.5185 | 97.3007 | 104.0889 | 110.8741
WindsorWind2060RCP4.5 | Windsor | Wind | RCP4.5 | 2060 | 84.0124 | 90.4337 | 97.1843 | 103.9478 | 110.7061
WindsorWind2065RCP4.5 | Windsor | Wind | RCP4.5 | 2065 | 83.9521 | 90.3489 | 97.0679 | 103.8066 | 110.538
WindsorWind2070RCP4.5 | Windsor | Wind | RCP4.5 | 2070 | 83.8918 | 90.2641 | 96.9515 | 103.6655 | 110.3699
WindsorWind2075RCP4.5 | Windsor | Wind | RCP4.5 | 2075 | 84.0928 | 90.5333 | 97.3056 | 104.091 | 110.8675
WindsorWind2080RCP4.5 | Windsor | Wind | RCP4.5 | 2080 | 84.2938 | 90.8024 | 97.6596 | 104.5165 | 111.3651
WindsorWind2085RCP4.5 | Windsor | Wind | RCP4.5 | 2085 | 84.4949 | 91.0715 | 98.0137 | 104.9421 | 111.8627
WindsorWind2090RCP4.5 | Windsor | Wind | RCP4.5 | 2090 | 84.6959 | 91.3406 | 98.3677 | 105.3676 | 112.3603
WindsorWind2095RCP4.5 | Windsor | Wind | RCP4.5 | 2095 | 84.8969 | 91.6098 | 98.7218 | 105.7931 | 112.8579
WindsorWind2100RCP4.5 | Windsor | Wind | RCP4.5 | 2100 | 85.0979 | 91.8789 | 99.0758 | 106.2187 | 113.3556
WindsorWind2023RCP6.0 | Windsor | Wind | RCP6.0 | 2023 | 84.0928 | 90.5618 | 97.3686 | 104.174 | 110.9781
WindsorWind2025RCP6.0 | Windsor | Wind | RCP6.0 | 2025 | 84.1096 | 90.5829 | 97.3961 | 104.2069 | 111.0168
WindsorWind2030RCP6.0 | Windsor | Wind | RCP6.0 | 2030 | 84.1263 | 90.6039 | 97.4236 | 104.2398 | 111.0555
WindsorWind2035RCP6.0 | Windsor | Wind | RCP6.0 | 2035 | 84.1431 | 90.625 | 97.4511 | 104.2726 | 111.0942
WindsorWind2040RCP6.0 | Windsor | Wind | RCP6.0 | 2040 | 84.1598 | 90.646 | 97.4785 | 104.3055 | 111.1329
WindsorWind2045RCP6.0 | Windsor | Wind | RCP6.0 | 2045 | 84.1766 | 90.6671 | 97.506 | 104.3384 | 111.1716
WindsorWind2050RCP6.0 | Windsor | Wind | RCP6.0 | 2050 | 84.133 | 90.6033 | 97.4171 | 104.2301 | 111.0422
WindsorWind2055RCP6.0 | Windsor | Wind | RCP6.0 | 2055 | 84.0727 | 90.5185 | 97.3007 | 104.0889 | 110.8741
WindsorWind2060RCP6.0 | Windsor | Wind | RCP6.0 | 2060 | 84.0124 | 90.4337 | 97.1843 | 103.9478 | 110.7061
WindsorWind2065RCP6.0 | Windsor | Wind | RCP6.0 | 2065 | 83.9521 | 90.3489 | 97.0679 | 103.8066 | 110.538
WindsorWind2070RCP6.0 | Windsor | Wind | RCP6.0 | 2070 | 83.8918 | 90.2641 | 96.9515 | 103.6655 | 110.3699
WindsorWind2075RCP6.0 | Windsor | Wind | RCP6.0 | 2075 | 84.1933 | 90.6678 | 97.4826 | 104.3038 | 111.1163
WindsorWind2080RCP6.0 | Windsor | Wind | RCP6.0 | 2080 | 84.4949 | 91.0715 | 98.0137 | 104.9421 | 111.8627
WindsorWind2085RCP6.0 | Windsor | Wind | RCP6.0 | 2085 | 84.7964 | 91.4752 | 98.5447 | 105.5804 | 112.6091
WindsorWind2090RCP6.0 | Windsor | Wind | RCP6.0 | 2090 | 85.4748 | 92.3299 | 99.6125 | 106.8276 | 114.0448
WindsorWind2095RCP6.0 | Windsor | Wind | RCP6.0 | 2095 | 85.8517 | 92.781 | 100.1493 | 107.4365 | 114.7341
WindsorWind2100RCP6.0 | Windsor | Wind | RCP6.0 | 2100 | 86.2287 | 93.232 | 100.686 | 108.0454 | 115.4234
WindsorWind2023RCP8.5 | Windsor | Wind | RCP8.5 | 2023 | 84.0928 | 90.5618 | 97.3686 | 104.174 | 110.9781
WindsorWind2025RCP8.5 | Windsor | Wind | RCP8.5 | 2025 | 84.1263 | 90.6039 | 97.4236 | 104.2398 | 111.0555
WindsorWind2030RCP8.5 | Windsor | Wind | RCP8.5 | 2030 | 84.1598 | 90.646 | 97.4785 | 104.3055 | 111.1329
WindsorWind2035RCP8.5 | Windsor | Wind | RCP8.5 | 2035 | 84.1933 | 90.6881 | 97.5335 | 104.3712 | 111.2103
WindsorWind2040RCP8.5 | Windsor | Wind | RCP8.5 | 2040 | 84.0928 | 90.5468 | 97.3395 | 104.136 | 110.9302
WindsorWind2045RCP8.5 | Windsor | Wind | RCP8.5 | 2045 | 83.9923 | 90.4055 | 97.1455 | 103.9007 | 110.65
WindsorWind2050RCP8.5 | Windsor | Wind | RCP8.5 | 2050 | 84.2938 | 90.8024 | 97.6596 | 104.5165 | 111.3651
WindsorWind2055RCP8.5 | Windsor | Wind | RCP8.5 | 2055 | 84.6959 | 91.3406 | 98.3677 | 105.3676 | 112.3603
WindsorWind2060RCP8.5 | Windsor | Wind | RCP8.5 | 2060 | 85.4748 | 92.3299 | 99.6125 | 106.8276 | 114.0448
WindsorWind2065RCP8.5 | Windsor | Wind | RCP8.5 | 2065 | 85.8517 | 92.781 | 100.1493 | 107.4365 | 114.7341
WindsorWind2070RCP8.5 | Windsor | Wind | RCP8.5 | 2070 | 86.4939 | 93.5508 | 101.074 | 108.4917 | 115.9247
WindsorWind2075RCP8.5 | Windsor | Wind | RCP8.5 | 2075 | 86.7591 | 93.8695 | 101.462 | 108.938 | 116.426
WindsorWind2080RCP8.5 | Windsor | Wind | RCP8.5 | 2080 | 87.0243 | 94.1883 | 101.85 | 109.3843 | 116.9273
WindsorWind2085RCP8.5 | Windsor | Wind | RCP8.5 | 2085 | 87.351 | 94.5762 | 102.3108 | 109.9136 | 117.5244
WindsorWind2090RCP8.5 | Windsor | Wind | RCP8.5 | 2090 | 87.6777 | 94.9641 | 102.7715 | 110.4429 | 118.1216
WindsorWind2095RCP8.5 | Windsor | Wind | RCP8.5 | 2095 | 87.6777 | 94.9641 | 102.7715 | 110.4429 | 118.1216
WindsorWind2100RCP8.5 | Windsor | Wind | RCP8.5 | 2100 | 87.6777 | 94.9641 | 102.7715 | 110.4429 | 118.1216
WinghamIce Accretion2023RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2023 | 15.9725 | 19.1854 | 23.253 | 26.3539 | 29.4437
WinghamIce Accretion2025RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2025 | 16.0498 | 19.2841 | 23.3795 | 26.5055 | 29.6176
WinghamIce Accretion2030RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2030 | 16.1272 | 19.3827 | 23.506 | 26.6571 | 29.7914
WinghamIce Accretion2035RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2035 | 16.2045 | 19.4813 | 23.6325 | 26.8087 | 29.9653
WinghamIce Accretion2040RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2040 | 16.2819 | 19.58 | 23.759 | 26.9603 | 30.1392
WinghamIce Accretion2045RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2045 | 16.3592 | 19.6786 | 23.8855 | 27.1119 | 30.3131
WinghamIce Accretion2050RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2050 | 16.443 | 19.8078 | 24.0764 | 27.3415 | 30.5913
WinghamIce Accretion2055RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2055 | 16.4494 | 19.8383 | 24.1408 | 27.4194 | 30.6956
WinghamIce Accretion2060RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2060 | 16.4558 | 19.8689 | 24.2052 | 27.4974 | 30.7999
WinghamIce Accretion2065RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2065 | 16.4622 | 19.8994 | 24.2696 | 27.5754 | 30.9043
WinghamIce Accretion2070RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2070 | 16.4686 | 19.93 | 24.334 | 27.6534 | 31.0086
WinghamIce Accretion2075RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2075 | 16.4179 | 19.8981 | 24.3187 | 27.6577 | 31.0231
WinghamIce Accretion2080RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2080 | 16.3672 | 19.8663 | 24.3033 | 27.662 | 31.0376
WinghamIce Accretion2085RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2085 | 16.3165 | 19.8345 | 24.288 | 27.6664 | 31.0521
WinghamIce Accretion2090RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2090 | 16.2659 | 19.8027 | 24.2727 | 27.6707 | 31.0666
WinghamIce Accretion2095RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2095 | 16.2152 | 19.7709 | 24.2573 | 27.675 | 31.0811
WinghamIce Accretion2100RCP4.5 | Wingham | Ice Accretion | RCP4.5 | 2100 | 16.1645 | 19.7391 | 24.242 | 27.6793 | 31.0955
WinghamIce Accretion2023RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2023 | 15.9725 | 19.1854 | 23.253 | 26.3539 | 29.4437
WinghamIce Accretion2025RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2025 | 16.0498 | 19.2841 | 23.3795 | 26.5055 | 29.6176
WinghamIce Accretion2030RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2030 | 16.1272 | 19.3827 | 23.506 | 26.6571 | 29.7914
WinghamIce Accretion2035RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2035 | 16.2045 | 19.4813 | 23.6325 | 26.8087 | 29.9653
WinghamIce Accretion2040RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2040 | 16.2819 | 19.58 | 23.759 | 26.9603 | 30.1392
WinghamIce Accretion2045RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2045 | 16.3592 | 19.6786 | 23.8855 | 27.1119 | 30.3131
WinghamIce Accretion2050RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2050 | 16.443 | 19.8078 | 24.0764 | 27.3415 | 30.5913
WinghamIce Accretion2055RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2055 | 16.4494 | 19.8383 | 24.1408 | 27.4194 | 30.6956
WinghamIce Accretion2060RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2060 | 16.4558 | 19.8689 | 24.2052 | 27.4974 | 30.7999
WinghamIce Accretion2065RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2065 | 16.4622 | 19.8994 | 24.2696 | 27.5754 | 30.9043
WinghamIce Accretion2070RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2070 | 16.4686 | 19.93 | 24.334 | 27.6534 | 31.0086
WinghamIce Accretion2075RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2075 | 16.3926 | 19.8822 | 24.311 | 27.6599 | 31.0303
WinghamIce Accretion2080RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2080 | 16.3165 | 19.8345 | 24.288 | 27.6664 | 31.0521
WinghamIce Accretion2085RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2085 | 16.2405 | 19.7868 | 24.265 | 27.6729 | 31.0738
WinghamIce Accretion2090RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2090 | 15.8978 | 19.4654 | 23.9583 | 27.3761 | 30.7864
WinghamIce Accretion2095RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2095 | 15.631 | 19.1918 | 23.6747 | 27.0729 | 30.4773
WinghamIce Accretion2100RCP6.0 | Wingham | Ice Accretion | RCP6.0 | 2100 | 15.3643 | 18.9182 | 23.391 | 26.7697 | 30.1682
WinghamIce Accretion2023RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2023 | 15.9725 | 19.1854 | 23.253 | 26.3539 | 29.4437
WinghamIce Accretion2025RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2025 | 16.1272 | 19.3827 | 23.506 | 26.6571 | 29.7914
WinghamIce Accretion2030RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2030 | 16.2819 | 19.58 | 23.759 | 26.9603 | 30.1392
WinghamIce Accretion2035RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2035 | 16.4366 | 19.7772 | 24.012 | 27.2635 | 30.487
WinghamIce Accretion2040RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2040 | 16.4473 | 19.8281 | 24.1193 | 27.3935 | 30.6608
WinghamIce Accretion2045RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2045 | 16.4579 | 19.8791 | 24.2267 | 27.5234 | 30.8347
WinghamIce Accretion2050RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2050 | 16.3672 | 19.8663 | 24.3033 | 27.662 | 31.0376
WinghamIce Accretion2055RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2055 | 16.2659 | 19.8027 | 24.2727 | 27.6707 | 31.0666
WinghamIce Accretion2060RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2060 | 15.8978 | 19.4654 | 23.9583 | 27.3761 | 30.7864
WinghamIce Accretion2065RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2065 | 15.631 | 19.1918 | 23.6747 | 27.0729 | 30.4773
WinghamIce Accretion2070RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2070 | 14.8735 | 18.3646 | 22.7623 | 26.0853 | 29.4147
WinghamIce Accretion2075RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2075 | 14.3827 | 17.811 | 22.1337 | 25.4009 | 28.6612
WinghamIce Accretion2080RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2080 | 13.8919 | 17.2574 | 21.505 | 24.7165 | 27.9077
WinghamIce Accretion2085RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2085 | 13.1717 | 16.4079 | 20.493 | 23.5729 | 26.6471
WinghamIce Accretion2090RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2090 | 12.4515 | 15.5583 | 19.481 | 22.4294 | 25.3865
WinghamIce Accretion2095RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2095 | 12.4515 | 15.5583 | 19.481 | 22.4294 | 25.3865
WinghamIce Accretion2100RCP8.5 | Wingham | Ice Accretion | RCP8.5 | 2100 | 12.4515 | 15.5583 | 19.481 | 22.4294 | 25.3865
WinghamWind2023RCP4.5 | Wingham | Wind | RCP4.5 | 2023 | 85.2136 | 91.8691 | 98.8918 | 105.8981 | 112.9042
WinghamWind2025RCP4.5 | Wingham | Wind | RCP4.5 | 2025 | 85.2588 | 91.9223 | 98.9555 | 105.9698 | 112.9862
WinghamWind2030RCP4.5 | Wingham | Wind | RCP4.5 | 2030 | 85.3039 | 91.9754 | 99.0192 | 106.0414 | 113.0681
WinghamWind2035RCP4.5 | Wingham | Wind | RCP4.5 | 2035 | 85.349 | 92.0286 | 99.0829 | 106.1131 | 113.15
WinghamWind2040RCP4.5 | Wingham | Wind | RCP4.5 | 2040 | 85.3942 | 92.0818 | 99.1466 | 106.1847 | 113.2319
WinghamWind2045RCP4.5 | Wingham | Wind | RCP4.5 | 2045 | 85.4393 | 92.1349 | 99.2103 | 106.2564 | 113.3139
WinghamWind2050RCP4.5 | Wingham | Wind | RCP4.5 | 2050 | 85.4929 | 92.1936 | 99.274 | 106.3259 | 113.3869
WinghamWind2055RCP4.5 | Wingham | Wind | RCP4.5 | 2055 | 85.5013 | 92.199 | 99.274 | 106.3238 | 113.3779
WinghamWind2060RCP4.5 | Wingham | Wind | RCP4.5 | 2060 | 85.5098 | 92.2045 | 99.274 | 106.3217 | 113.369
WinghamWind2065RCP4.5 | Wingham | Wind | RCP4.5 | 2065 | 85.5183 | 92.21 | 99.274 | 106.3197 | 113.36
WinghamWind2070RCP4.5 | Wingham | Wind | RCP4.5 | 2070 | 85.5267 | 92.2155 | 99.274 | 106.3176 | 113.3511
WinghamWind2075RCP4.5 | Wingham | Wind | RCP4.5 | 2075 | 85.6212 | 92.3446 | 99.4488 | 106.5308 | 113.6043
WinghamWind2080RCP4.5 | Wingham | Wind | RCP4.5 | 2080 | 85.7157 | 92.4737 | 99.6235 | 106.744 | 113.8576
WinghamWind2085RCP4.5 | Wingham | Wind | RCP4.5 | 2085 | 85.8102 | 92.6028 | 99.7983 | 106.9572 | 114.1108
WinghamWind2090RCP4.5 | Wingham | Wind | RCP4.5 | 2090 | 85.9047 | 92.7319 | 99.9731 | 107.1704 | 114.364
WinghamWind2095RCP4.5 | Wingham | Wind | RCP4.5 | 2095 | 85.9992 | 92.861 | 100.1478 | 107.3836 | 114.6173
WinghamWind2100RCP4.5 | Wingham | Wind | RCP4.5 | 2100 | 86.0937 | 92.9901 | 100.3226 | 107.5968 | 114.8705
WinghamWind2023RCP6.0 | Wingham | Wind | RCP6.0 | 2023 | 85.2136 | 91.8691 | 98.8918 | 105.8981 | 112.9042
WinghamWind2025RCP6.0 | Wingham | Wind | RCP6.0 | 2025 | 85.2588 | 91.9223 | 98.9555 | 105.9698 | 112.9862
WinghamWind2030RCP6.0 | Wingham | Wind | RCP6.0 | 2030 | 85.3039 | 91.9754 | 99.0192 | 106.0414 | 113.0681
WinghamWind2035RCP6.0 | Wingham | Wind | RCP6.0 | 2035 | 85.349 | 92.0286 | 99.0829 | 106.1131 | 113.15
WinghamWind2040RCP6.0 | Wingham | Wind | RCP6.0 | 2040 | 85.3942 | 92.0818 | 99.1466 | 106.1847 | 113.2319
WinghamWind2045RCP6.0 | Wingham | Wind | RCP6.0 | 2045 | 85.4393 | 92.1349 | 99.2103 | 106.2564 | 113.3139
WinghamWind2050RCP6.0 | Wingham | Wind | RCP6.0 | 2050 | 85.4929 | 92.1936 | 99.274 | 106.3259 | 113.3869
WinghamWind2055RCP6.0 | Wingham | Wind | RCP6.0 | 2055 | 85.5013 | 92.199 | 99.274 | 106.3238 | 113.3779
WinghamWind2060RCP6.0 | Wingham | Wind | RCP6.0 | 2060 | 85.5098 | 92.2045 | 99.274 | 106.3217 | 113.369
WinghamWind2065RCP6.0 | Wingham | Wind | RCP6.0 | 2065 | 85.5183 | 92.21 | 99.274 | 106.3197 | 113.36
WinghamWind2070RCP6.0 | Wingham | Wind | RCP6.0 | 2070 | 85.5267 | 92.2155 | 99.274 | 106.3176 | 113.3511
WinghamWind2075RCP6.0 | Wingham | Wind | RCP6.0 | 2075 | 85.6685 | 92.4091 | 99.5361 | 106.6374 | 113.731
WinghamWind2080RCP6.0 | Wingham | Wind | RCP6.0 | 2080 | 85.8102 | 92.6028 | 99.7983 | 106.9572 | 114.1108
WinghamWind2085RCP6.0 | Wingham | Wind | RCP6.0 | 2085 | 85.9519 | 92.7965 | 100.0605 | 107.277 | 114.4907
WinghamWind2090RCP6.0 | Wingham | Wind | RCP6.0 | 2090 | 86.4688 | 93.4519 | 100.8877 | 108.2505 | 115.619
WinghamWind2095RCP6.0 | Wingham | Wind | RCP6.0 | 2095 | 86.844 | 93.9137 | 101.4529 | 108.9041 | 116.3676
WinghamWind2100RCP6.0 | Wingham | Wind | RCP6.0 | 2100 | 87.2192 | 94.3755 | 102.018 | 109.5577 | 117.1161
WinghamWind2023RCP8.5 | Wingham | Wind | RCP8.5 | 2023 | 85.2136 | 91.8691 | 98.8918 | 105.8981 | 112.9042
WinghamWind2025RCP8.5 | Wingham | Wind | RCP8.5 | 2025 | 85.3039 | 91.9754 | 99.0192 | 106.0414 | 113.0681
WinghamWind2030RCP8.5 | Wingham | Wind | RCP8.5 | 2030 | 85.3942 | 92.0818 | 99.1466 | 106.1847 | 113.2319
WinghamWind2035RCP8.5 | Wingham | Wind | RCP8.5 | 2035 | 85.4844 | 92.1881 | 99.274 | 106.328 | 113.3958
WinghamWind2040RCP8.5 | Wingham | Wind | RCP8.5 | 2040 | 85.4985 | 92.1972 | 99.274 | 106.3245 | 113.3809
WinghamWind2045RCP8.5 | Wingham | Wind | RCP8.5 | 2045 | 85.5126 | 92.2063 | 99.274 | 106.321 | 113.366
WinghamWind2050RCP8.5 | Wingham | Wind | RCP8.5 | 2050 | 85.7157 | 92.4737 | 99.6235 | 106.744 | 113.8576
WinghamWind2055RCP8.5 | Wingham | Wind | RCP8.5 | 2055 | 85.9047 | 92.7319 | 99.9731 | 107.1704 | 114.364
WinghamWind2060RCP8.5 | Wingham | Wind | RCP8.5 | 2060 | 86.4688 | 93.4519 | 100.8877 | 108.2505 | 115.619
WinghamWind2065RCP8.5 | Wingham | Wind | RCP8.5 | 2065 | 86.844 | 93.9137 | 101.4529 | 108.9041 | 116.3676
WinghamWind2070RCP8.5 | Wingham | Wind | RCP8.5 | 2070 | 87.4956 | 94.737 | 102.4917 | 110.124 | 117.7789
WinghamWind2075RCP8.5 | Wingham | Wind | RCP8.5 | 2075 | 87.772 | 95.0985 | 102.9653 | 110.6902 | 118.4418
WinghamWind2080RCP8.5 | Wingham | Wind | RCP8.5 | 2080 | 88.0484 | 95.46 | 103.439 | 111.2565 | 119.1047
WinghamWind2085RCP8.5 | Wingham | Wind | RCP8.5 | 2085 | 88.2642 | 95.7471 | 103.8163 | 111.7074 | 119.6298
WinghamWind2090RCP8.5 | Wingham | Wind | RCP8.5 | 2090 | 88.48 | 96.0342 | 104.1936 | 112.1583 | 120.1549
WinghamWind2095RCP8.5 | Wingham | Wind | RCP8.5 | 2095 | 88.48 | 96.0342 | 104.1936 | 112.1583 | 120.1549
WinghamWind2100RCP8.5 | Wingham | Wind | RCP8.5 | 2100 | 88.48 | 96.0342 | 104.1936 | 112.1583 | 120.1549
WoodstockIce Accretion2023RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
WoodstockIce Accretion2025RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2025 | 20.3952 | 24.4642 | 29.605 | 33.5328 | 37.4661
WoodstockIce Accretion2030RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2030 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
WoodstockIce Accretion2035RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2035 | 20.3117 | 24.3895 | 29.535 | 33.4763 | 37.4031
WoodstockIce Accretion2040RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2040 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
WoodstockIce Accretion2045RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2045 | 20.2282 | 24.3148 | 29.465 | 33.4198 | 37.3401
WoodstockIce Accretion2050RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2050 | 20.0571 | 24.153 | 29.316 | 33.2762 | 37.2028
WoodstockIce Accretion2055RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2055 | 19.9276 | 24.0285 | 29.202 | 33.161 | 37.0969
WoodstockIce Accretion2060RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2060 | 19.7982 | 23.904 | 29.088 | 33.0457 | 36.9911
WoodstockIce Accretion2065RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2065 | 19.6688 | 23.7795 | 28.974 | 32.9305 | 36.8852
WoodstockIce Accretion2070RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2070 | 19.5394 | 23.655 | 28.86 | 32.8152 | 36.7794
WoodstockIce Accretion2075RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2075 | 19.4837 | 23.6135 | 28.84 | 32.8095 | 36.7857
WoodstockIce Accretion2080RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2080 | 19.428 | 23.572 | 28.82 | 32.8039 | 36.792
WoodstockIce Accretion2085RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2085 | 19.3724 | 23.5305 | 28.8 | 32.7982 | 36.7983
WoodstockIce Accretion2090RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2090 | 19.3167 | 23.489 | 28.78 | 32.7926 | 36.8046
WoodstockIce Accretion2095RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2095 | 19.261 | 23.4475 | 28.76 | 32.7869 | 36.8109
WoodstockIce Accretion2100RCP4.5 | Woodstock | Ice Accretion | RCP4.5 | 2100 | 19.2054 | 23.406 | 28.74 | 32.7813 | 36.8172
WoodstockIce Accretion2023RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
WoodstockIce Accretion2025RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2025 | 20.3952 | 24.4642 | 29.605 | 33.5328 | 37.4661
WoodstockIce Accretion2030RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2030 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
WoodstockIce Accretion2035RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2035 | 20.3117 | 24.3895 | 29.535 | 33.4763 | 37.4031
WoodstockIce Accretion2040RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2040 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
WoodstockIce Accretion2045RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2045 | 20.2282 | 24.3148 | 29.465 | 33.4198 | 37.3401
WoodstockIce Accretion2050RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2050 | 20.0571 | 24.153 | 29.316 | 33.2762 | 37.2028
WoodstockIce Accretion2055RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2055 | 19.9276 | 24.0285 | 29.202 | 33.161 | 37.0969
WoodstockIce Accretion2060RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2060 | 19.7982 | 23.904 | 29.088 | 33.0457 | 36.9911
WoodstockIce Accretion2065RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2065 | 19.6688 | 23.7795 | 28.974 | 32.9305 | 36.8852
WoodstockIce Accretion2070RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2070 | 19.5394 | 23.655 | 28.86 | 32.8152 | 36.7794
WoodstockIce Accretion2075RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2075 | 19.4559 | 23.5927 | 28.83 | 32.8067 | 36.7888
WoodstockIce Accretion2080RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2080 | 19.3724 | 23.5305 | 28.8 | 32.7982 | 36.7983
WoodstockIce Accretion2085RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2085 | 19.2889 | 23.4682 | 28.77 | 32.7898 | 36.8077
WoodstockIce Accretion2090RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2090 | 18.7739 | 22.9412 | 28.21 | 32.2163 | 36.1998
WoodstockIce Accretion2095RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2095 | 18.3425 | 22.4764 | 27.68 | 31.6513 | 35.5824
WoodstockIce Accretion2100RCP6.0 | Woodstock | Ice Accretion | RCP6.0 | 2100 | 17.9111 | 22.0116 | 27.15 | 31.0863 | 34.965
WoodstockIce Accretion2023RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2023 | 20.437 | 24.5016 | 29.64 | 33.561 | 37.4976
WoodstockIce Accretion2025RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2025 | 20.3535 | 24.4269 | 29.57 | 33.5045 | 37.4346
WoodstockIce Accretion2030RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2030 | 20.27 | 24.3522 | 29.5 | 33.448 | 37.3716
WoodstockIce Accretion2035RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2035 | 20.1865 | 24.2775 | 29.43 | 33.3915 | 37.3086
WoodstockIce Accretion2040RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2040 | 19.9708 | 24.07 | 29.24 | 33.1994 | 37.1322
WoodstockIce Accretion2045RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2045 | 19.7551 | 23.8625 | 29.05 | 33.0073 | 36.9558
WoodstockIce Accretion2050RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2050 | 19.428 | 23.572 | 28.82 | 32.8039 | 36.792
WoodstockIce Accretion2055RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2055 | 19.3167 | 23.489 | 28.78 | 32.7926 | 36.8046
WoodstockIce Accretion2060RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2060 | 18.7739 | 22.9412 | 28.21 | 32.2163 | 36.1998
WoodstockIce Accretion2065RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2065 | 18.3425 | 22.4764 | 27.68 | 31.6513 | 35.5824
WoodstockIce Accretion2070RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2070 | 17.5353 | 21.6049 | 26.71 | 30.6117 | 34.461
WoodstockIce Accretion2075RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2075 | 17.1596 | 21.1982 | 26.27 | 30.1371 | 33.957
WoodstockIce Accretion2080RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2080 | 16.7838 | 20.7915 | 25.83 | 29.6625 | 33.453
WoodstockIce Accretion2085RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2085 | 15.8549 | 19.7208 | 24.57 | 28.2387 | 31.9032
WoodstockIce Accretion2090RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2090 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
WoodstockIce Accretion2095RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2095 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
WoodstockIce Accretion2100RCP8.5 | Woodstock | Ice Accretion | RCP8.5 | 2100 | 14.9259 | 18.6501 | 23.31 | 26.8149 | 30.3534
WoodstockWind2023RCP4.5 | Woodstock | Wind | RCP4.5 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
WoodstockWind2025RCP4.5 | Woodstock | Wind | RCP4.5 | 2025 | 87.206 | 94.102 | 101.4083 | 108.6746 | 115.9494
WoodstockWind2030RCP4.5 | Woodstock | Wind | RCP4.5 | 2030 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
WoodstockWind2035RCP4.5 | Woodstock | Wind | RCP4.5 | 2035 | 87.3672 | 94.316 | 101.685 | 109.0063 | 116.337
WoodstockWind2040RCP4.5 | Woodstock | Wind | RCP4.5 | 2040 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
WoodstockWind2045RCP4.5 | Woodstock | Wind | RCP4.5 | 2045 | 87.5283 | 94.5299 | 101.9617 | 109.338 | 116.7246
WoodstockWind2050RCP4.5 | Woodstock | Wind | RCP4.5 | 2050 | 87.678 | 94.7205 | 102.206 | 109.6258 | 117.0575
WoodstockWind2055RCP4.5 | Woodstock | Wind | RCP4.5 | 2055 | 87.7471 | 94.8042 | 102.312 | 109.7478 | 117.1966
WoodstockWind2060RCP4.5 | Woodstock | Wind | RCP4.5 | 2060 | 87.8162 | 94.8879 | 102.418 | 109.8697 | 117.3356
WoodstockWind2065RCP4.5 | Woodstock | Wind | RCP4.5 | 2065 | 87.8852 | 94.9716 | 102.524 | 109.9917 | 117.4747
WoodstockWind2070RCP4.5 | Woodstock | Wind | RCP4.5 | 2070 | 87.9543 | 95.0553 | 102.63 | 110.1137 | 117.6138
WoodstockWind2075RCP4.5 | Woodstock | Wind | RCP4.5 | 2075 | 88.0407 | 95.1746 | 102.7917 | 110.3117 | 117.8494
WoodstockWind2080RCP4.5 | Woodstock | Wind | RCP4.5 | 2080 | 88.127 | 95.294 | 102.9533 | 110.5096 | 118.085
WoodstockWind2085RCP4.5 | Woodstock | Wind | RCP4.5 | 2085 | 88.2134 | 95.4134 | 103.115 | 110.7075 | 118.3206
WoodstockWind2090RCP4.5 | Woodstock | Wind | RCP4.5 | 2090 | 88.2997 | 95.5327 | 103.2767 | 110.9055 | 118.5562
WoodstockWind2095RCP4.5 | Woodstock | Wind | RCP4.5 | 2095 | 88.3861 | 95.6521 | 103.4383 | 111.1034 | 118.7918
WoodstockWind2100RCP4.5 | Woodstock | Wind | RCP4.5 | 2100 | 88.4724 | 95.7714 | 103.6 | 111.3014 | 119.0274
WoodstockWind2023RCP6.0 | Woodstock | Wind | RCP6.0 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
WoodstockWind2025RCP6.0 | Woodstock | Wind | RCP6.0 | 2025 | 87.206 | 94.102 | 101.4083 | 108.6746 | 115.9494
WoodstockWind2030RCP6.0 | Woodstock | Wind | RCP6.0 | 2030 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
WoodstockWind2035RCP6.0 | Woodstock | Wind | RCP6.0 | 2035 | 87.3672 | 94.316 | 101.685 | 109.0063 | 116.337
WoodstockWind2040RCP6.0 | Woodstock | Wind | RCP6.0 | 2040 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
WoodstockWind2045RCP6.0 | Woodstock | Wind | RCP6.0 | 2045 | 87.5283 | 94.5299 | 101.9617 | 109.338 | 116.7246
WoodstockWind2050RCP6.0 | Woodstock | Wind | RCP6.0 | 2050 | 87.678 | 94.7205 | 102.206 | 109.6258 | 117.0575
WoodstockWind2055RCP6.0 | Woodstock | Wind | RCP6.0 | 2055 | 87.7471 | 94.8042 | 102.312 | 109.7478 | 117.1966
WoodstockWind2060RCP6.0 | Woodstock | Wind | RCP6.0 | 2060 | 87.8162 | 94.8879 | 102.418 | 109.8697 | 117.3356
WoodstockWind2065RCP6.0 | Woodstock | Wind | RCP6.0 | 2065 | 87.8852 | 94.9716 | 102.524 | 109.9917 | 117.4747
WoodstockWind2070RCP6.0 | Woodstock | Wind | RCP6.0 | 2070 | 87.9543 | 95.0553 | 102.63 | 110.1137 | 117.6138
WoodstockWind2075RCP6.0 | Woodstock | Wind | RCP6.0 | 2075 | 88.0838 | 95.2343 | 102.8725 | 110.4106 | 117.9672
WoodstockWind2080RCP6.0 | Woodstock | Wind | RCP6.0 | 2080 | 88.2134 | 95.4134 | 103.115 | 110.7075 | 118.3206
WoodstockWind2085RCP6.0 | Woodstock | Wind | RCP6.0 | 2085 | 88.3429 | 95.5924 | 103.3575 | 111.0045 | 118.674
WoodstockWind2090RCP6.0 | Woodstock | Wind | RCP6.0 | 2090 | 88.8264 | 96.2271 | 104.18 | 111.9862 | 119.8216
WoodstockWind2095RCP6.0 | Woodstock | Wind | RCP6.0 | 2095 | 89.1805 | 96.6828 | 104.76 | 112.671 | 120.6158
WoodstockWind2100RCP6.0 | Woodstock | Wind | RCP6.0 | 2100 | 89.5345 | 97.1385 | 105.34 | 113.3558 | 121.41
WoodstockWind2023RCP8.5 | Woodstock | Wind | RCP8.5 | 2023 | 87.1254 | 93.9951 | 101.27 | 108.5087 | 115.7556
WoodstockWind2025RCP8.5 | Woodstock | Wind | RCP8.5 | 2025 | 87.2866 | 94.209 | 101.5467 | 108.8404 | 116.1432
WoodstockWind2030RCP8.5 | Woodstock | Wind | RCP8.5 | 2030 | 87.4477 | 94.4229 | 101.8233 | 109.1721 | 116.5308
WoodstockWind2035RCP8.5 | Woodstock | Wind | RCP8.5 | 2035 | 87.6089 | 94.6368 | 102.1 | 109.5038 | 116.9184
WoodstockWind2040RCP8.5 | Woodstock | Wind | RCP8.5 | 2040 | 87.7241 | 94.7763 | 102.2767 | 109.7071 | 117.1502
WoodstockWind2045RCP8.5 | Woodstock | Wind | RCP8.5 | 2045 | 87.8392 | 94.9158 | 102.4533 | 109.9104 | 117.382
WoodstockWind2050RCP8.5 | Woodstock | Wind | RCP8.5 | 2050 | 88.127 | 95.294 | 102.9533 | 110.5096 | 118.085
WoodstockWind2055RCP8.5 | Woodstock | Wind | RCP8.5 | 2055 | 88.2997 | 95.5327 | 103.2767 | 110.9055 | 118.5562
WoodstockWind2060RCP8.5 | Woodstock | Wind | RCP8.5 | 2060 | 88.8264 | 96.2271 | 104.18 | 111.9862 | 119.8216
WoodstockWind2065RCP8.5 | Woodstock | Wind | RCP8.5 | 2065 | 89.1805 | 96.6828 | 104.76 | 112.671 | 120.6158
WoodstockWind2070RCP8.5 | Woodstock | Wind | RCP8.5 | 2070 | 89.759 | 97.4392 | 105.7367 | 113.8337 | 121.9724
WoodstockWind2075RCP8.5 | Woodstock | Wind | RCP8.5 | 2075 | 89.9835 | 97.7399 | 106.1333 | 114.3117 | 122.5348
WoodstockWind2080RCP8.5 | Woodstock | Wind | RCP8.5 | 2080 | 90.208 | 98.0406 | 106.53 | 114.7896 | 123.0972
WoodstockWind2085RCP8.5 | Woodstock | Wind | RCP8.5 | 2085 | 90.6484 | 98.6172 | 107.285 | 115.6937 | 124.1517
WoodstockWind2090RCP8.5 | Woodstock | Wind | RCP8.5 | 2090 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
WoodstockWind2095RCP8.5 | Woodstock | Wind | RCP8.5 | 2095 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
WoodstockWind2100RCP8.5 | Woodstock | Wind | RCP8.5 | 2100 | 91.0888 | 99.1938 | 108.04 | 116.5979 | 125.2062
WyomingIce Accretion2023RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2023 | 15.4123 | 18.4982 | 22.402 | 25.3662 | 28.3424
WyomingIce Accretion2025RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2025 | 15.3509 | 18.4378 | 22.3407 | 25.3056 | 28.2797
WyomingIce Accretion2030RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2030 | 15.2896 | 18.3773 | 22.2793 | 25.245 | 28.2169
WyomingIce Accretion2035RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2035 | 15.2282 | 18.3169 | 22.218 | 25.1843 | 28.1541
WyomingIce Accretion2040RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2040 | 15.1669 | 18.2564 | 22.1567 | 25.1237 | 28.0913
WyomingIce Accretion2045RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2045 | 15.1055 | 18.196 | 22.0953 | 25.063 | 28.0285
WyomingIce Accretion2050RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2050 | 14.7625 | 17.8224 | 21.6752 | 24.6125 | 27.5426
WyomingIce Accretion2055RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2055 | 14.4808 | 17.5093 | 21.3164 | 24.2227 | 27.1195
WyomingIce Accretion2060RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2060 | 14.1992 | 17.1963 | 20.9576 | 23.8328 | 26.6964
WyomingIce Accretion2065RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2065 | 13.9175 | 16.8832 | 20.5988 | 23.443 | 26.2733
WyomingIce Accretion2070RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2070 | 13.6358 | 16.5701 | 20.24 | 23.0531 | 25.8502
WyomingIce Accretion2075RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2075 | 13.5078 | 16.4365 | 20.102 | 22.9059 | 25.6956
WyomingIce Accretion2080RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2080 | 13.3797 | 16.3029 | 19.964 | 22.7586 | 25.541
WyomingIce Accretion2085RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2085 | 13.2517 | 16.1692 | 19.826 | 22.6113 | 25.3865
WyomingIce Accretion2090RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2090 | 13.1237 | 16.0356 | 19.688 | 22.464 | 25.2319
WyomingIce Accretion2095RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2095 | 12.9956 | 15.902 | 19.55 | 22.3167 | 25.0774
WyomingIce Accretion2100RCP4.5 | Wyoming | Ice Accretion | RCP4.5 | 2100 | 12.8676 | 15.7683 | 19.412 | 22.1695 | 24.9228
WyomingIce Accretion2023RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2023 | 15.4123 | 18.4982 | 22.402 | 25.3662 | 28.3424
WyomingIce Accretion2025RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2025 | 15.3509 | 18.4378 | 22.3407 | 25.3056 | 28.2797
WyomingIce Accretion2030RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2030 | 15.2896 | 18.3773 | 22.2793 | 25.245 | 28.2169
WyomingIce Accretion2035RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2035 | 15.2282 | 18.3169 | 22.218 | 25.1843 | 28.1541
WyomingIce Accretion2040RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2040 | 15.1669 | 18.2564 | 22.1567 | 25.1237 | 28.0913
WyomingIce Accretion2045RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2045 | 15.1055 | 18.196 | 22.0953 | 25.063 | 28.0285
WyomingIce Accretion2050RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2050 | 14.7625 | 17.8224 | 21.6752 | 24.6125 | 27.5426
WyomingIce Accretion2055RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2055 | 14.4808 | 17.5093 | 21.3164 | 24.2227 | 27.1195
WyomingIce Accretion2060RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2060 | 14.1992 | 17.1963 | 20.9576 | 23.8328 | 26.6964
WyomingIce Accretion2065RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2065 | 13.9175 | 16.8832 | 20.5988 | 23.443 | 26.2733
WyomingIce Accretion2070RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2070 | 13.6358 | 16.5701 | 20.24 | 23.0531 | 25.8502
WyomingIce Accretion2075RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2075 | 13.4437 | 16.3697 | 20.033 | 22.8322 | 25.6183
WyomingIce Accretion2080RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2080 | 13.2517 | 16.1692 | 19.826 | 22.6113 | 25.3865
WyomingIce Accretion2085RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2085 | 13.0596 | 15.9688 | 19.619 | 22.3904 | 25.1546
WyomingIce Accretion2090RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2090 | 12.4781 | 15.3293 | 18.906 | 21.6064 | 24.3046
WyomingIce Accretion2095RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2095 | 12.0887 | 14.8902 | 18.4 | 21.0432 | 23.6863
WyomingIce Accretion2100RCP6.0 | Wyoming | Ice Accretion | RCP6.0 | 2100 | 11.6993 | 14.4511 | 17.894 | 20.4801 | 23.0681
WyomingIce Accretion2023RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2023 | 15.4123 | 18.4982 | 22.402 | 25.3662 | 28.3424
WyomingIce Accretion2025RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2025 | 15.2896 | 18.3773 | 22.2793 | 25.245 | 28.2169
WyomingIce Accretion2030RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2030 | 15.1669 | 18.2564 | 22.1567 | 25.1237 | 28.0913
WyomingIce Accretion2035RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2035 | 15.0442 | 18.1355 | 22.034 | 25.0024 | 27.9657
WyomingIce Accretion2040RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2040 | 14.5747 | 17.6137 | 21.436 | 24.3526 | 27.2605
WyomingIce Accretion2045RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2045 | 14.1053 | 17.0919 | 20.838 | 23.7029 | 26.5553
WyomingIce Accretion2050RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2050 | 13.3797 | 16.3029 | 19.964 | 22.7586 | 25.541
WyomingIce Accretion2055RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2055 | 13.1237 | 16.0356 | 19.688 | 22.464 | 25.2319
WyomingIce Accretion2060RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2060 | 12.4781 | 15.3293 | 18.906 | 21.6064 | 24.3046
WyomingIce Accretion2065RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2065 | 12.0887 | 14.8902 | 18.4 | 21.0432 | 23.6863
WyomingIce Accretion2070RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2070 | 11.3952 | 14.1202 | 17.5183 | 20.0816 | 22.6334
WyomingIce Accretion2075RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2075 | 11.0911 | 13.7893 | 17.1427 | 19.6831 | 22.1987
WyomingIce Accretion2080RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2080 | 10.787 | 13.4585 | 16.767 | 19.2846 | 21.764
WyomingIce Accretion2085RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2085 | 10.0508 | 12.5803 | 15.7205 | 18.089 | 20.4454
WyomingIce Accretion2090RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2090 | 9.3146 | 11.7022 | 14.674 | 16.8935 | 19.1268
WyomingIce Accretion2095RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2095 | 9.3146 | 11.7022 | 14.674 | 16.8935 | 19.1268
WyomingIce Accretion2100RCP8.5 | Wyoming | Ice Accretion | RCP8.5 | 2100 | 9.3146 | 11.7022 | 14.674 | 16.8935 | 19.1268
WyomingWind2023RCP4.5 | Wyoming | Wind | RCP4.5 | 2023 | 84.3776 | 90.9227 | 97.8245 | 104.7137 | 111.6084
WyomingWind2025RCP4.5 | Wyoming | Wind | RCP4.5 | 2025 | 84.4334 | 90.9993 | 97.9263 | 104.8365 | 111.7521
WyomingWind2030RCP4.5 | Wyoming | Wind | RCP4.5 | 2030 | 84.4893 | 91.076 | 98.0282 | 104.9594 | 111.8959
WyomingWind2035RCP4.5 | Wyoming | Wind | RCP4.5 | 2035 | 84.5451 | 91.1527 | 98.13 | 105.0822 | 112.0397
WyomingWind2040RCP4.5 | Wyoming | Wind | RCP4.5 | 2040 | 84.601 | 91.2294 | 98.2319 | 105.205 | 112.1834
WyomingWind2045RCP4.5 | Wyoming | Wind | RCP4.5 | 2045 | 84.6568 | 91.3061 | 98.3337 | 105.3278 | 112.3272
WyomingWind2050RCP4.5 | Wyoming | Wind | RCP4.5 | 2050 | 84.7143 | 91.3881 | 98.4453 | 105.4652 | 112.4908
WyomingWind2055RCP4.5 | Wyoming | Wind | RCP4.5 | 2055 | 84.716 | 91.3936 | 98.455 | 105.4797 | 112.5107
WyomingWind2060RCP4.5 | Wyoming | Wind | RCP4.5 | 2060 | 84.7177 | 91.399 | 98.4647 | 105.4942 | 112.5306
WyomingWind2065RCP4.5 | Wyoming | Wind | RCP4.5 | 2065 | 84.7193 | 91.4044 | 98.4744 | 105.5088 | 112.5505
WyomingWind2070RCP4.5 | Wyoming | Wind | RCP4.5 | 2070 | 84.721 | 91.4098 | 98.4841 | 105.5233 | 112.5704
WyomingWind2075RCP4.5 | Wyoming | Wind | RCP4.5 | 2075 | 84.8662 | 91.5977 | 98.7282 | 105.8139 | 112.9096
WyomingWind2080RCP4.5 | Wyoming | Wind | RCP4.5 | 2080 | 85.0114 | 91.7857 | 98.9723 | 106.1045 | 113.2487
WyomingWind2085RCP4.5 | Wyoming | Wind | RCP4.5 | 2085 | 85.1566 | 91.9736 | 99.2165 | 106.3951 | 113.5878
WyomingWind2090RCP4.5 | Wyoming | Wind | RCP4.5 | 2090 | 85.3017 | 92.1615 | 99.4606 | 106.6857 | 113.9269
WyomingWind2095RCP4.5 | Wyoming | Wind | RCP4.5 | 2095 | 85.4469 | 92.3495 | 99.7047 | 106.9764 | 114.266
WyomingWind2100RCP4.5 | Wyoming | Wind | RCP4.5 | 2100 | 85.5921 | 92.5374 | 99.9488 | 107.267 | 114.6051
WyomingWind2023RCP6.0 | Wyoming | Wind | RCP6.0 | 2023 | 84.3776 | 90.9227 | 97.8245 | 104.7137 | 111.6084
WyomingWind2025RCP6.0 | Wyoming | Wind | RCP6.0 | 2025 | 84.4334 | 90.9993 | 97.9263 | 104.8365 | 111.7521
WyomingWind2030RCP6.0 | Wyoming | Wind | RCP6.0 | 2030 | 84.4893 | 91.076 | 98.0282 | 104.9594 | 111.8959
WyomingWind2035RCP6.0 | Wyoming | Wind | RCP6.0 | 2035 | 84.5451 | 91.1527 | 98.13 | 105.0822 | 112.0397
WyomingWind2040RCP6.0 | Wyoming | Wind | RCP6.0 | 2040 | 84.601 | 91.2294 | 98.2319 | 105.205 | 112.1834
WyomingWind2045RCP6.0 | Wyoming | Wind | RCP6.0 | 2045 | 84.6568 | 91.3061 | 98.3337 | 105.3278 | 112.3272
WyomingWind2050RCP6.0 | Wyoming | Wind | RCP6.0 | 2050 | 84.7143 | 91.3881 | 98.4453 | 105.4652 | 112.4908
WyomingWind2055RCP6.0 | Wyoming | Wind | RCP6.0 | 2055 | 84.716 | 91.3936 | 98.455 | 105.4797 | 112.5107
WyomingWind2060RCP6.0 | Wyoming | Wind | RCP6.0 | 2060 | 84.7177 | 91.399 | 98.4647 | 105.4942 | 112.5306
WyomingWind2065RCP6.0 | Wyoming | Wind | RCP6.0 | 2065 | 84.7193 | 91.4044 | 98.4744 | 105.5088 | 112.5505
WyomingWind2070RCP6.0 | Wyoming | Wind | RCP6.0 | 2070 | 84.721 | 91.4098 | 98.4841 | 105.5233 | 112.5704
WyomingWind2075RCP6.0 | Wyoming | Wind | RCP6.0 | 2075 | 84.9388 | 91.6917 | 98.8503 | 105.9592 | 113.0791
WyomingWind2080RCP6.0 | Wyoming | Wind | RCP6.0 | 2080 | 85.1566 | 91.9736 | 99.2165 | 106.3951 | 113.5878
WyomingWind2085RCP6.0 | Wyoming | Wind | RCP6.0 | 2085 | 85.3743 | 92.2555 | 99.5826 | 106.831 | 114.0964
WyomingWind2090RCP6.0 | Wyoming | Wind | RCP6.0 | 2090 | 85.955 | 92.9855 | 100.4985 | 107.907 | 115.3349
WyomingWind2095RCP6.0 | Wyoming | Wind | RCP6.0 | 2095 | 86.318 | 93.4335 | 101.0481 | 108.547 | 116.0648
WyomingWind2100RCP6.0 | Wyoming | Wind | RCP6.0 | 2100 | 86.6809 | 93.8815 | 101.5978 | 109.1871 | 116.7946
WyomingWind2023RCP8.5 | Wyoming | Wind | RCP8.5 | 2023 | 84.3776 | 90.9227 | 97.8245 | 104.7137 | 111.6084
WyomingWind2025RCP8.5 | Wyoming | Wind | RCP8.5 | 2025 | 84.4893 | 91.076 | 98.0282 | 104.9594 | 111.8959
WyomingWind2030RCP8.5 | Wyoming | Wind | RCP8.5 | 2030 | 84.601 | 91.2294 | 98.2319 | 105.205 | 112.1834
WyomingWind2035RCP8.5 | Wyoming | Wind | RCP8.5 | 2035 | 84.7126 | 91.3827 | 98.4356 | 105.4506 | 112.4709
WyomingWind2040RCP8.5 | Wyoming | Wind | RCP8.5 | 2040 | 84.7154 | 91.3918 | 98.4518 | 105.4749 | 112.5041
WyomingWind2045RCP8.5 | Wyoming | Wind | RCP8.5 | 2045 | 84.7182 | 91.4008 | 98.4679 | 105.4991 | 112.5373
WyomingWind2050RCP8.5 | Wyoming | Wind | RCP8.5 | 2050 | 85.0114 | 91.7857 | 98.9723 | 106.1045 | 113.2487
WyomingWind2055RCP8.5 | Wyoming | Wind | RCP8.5 | 2055 | 85.3017 | 92.1615 | 99.4606 | 106.6857 | 113.9269
WyomingWind2060RCP8.5 | Wyoming | Wind | RCP8.5 | 2060 | 85.955 | 92.9855 | 100.4985 | 107.907 | 115.3349
WyomingWind2065RCP8.5 | Wyoming | Wind | RCP8.5 | 2065 | 86.318 | 93.4335 | 101.0481 | 108.547 | 116.0648
WyomingWind2070RCP8.5 | Wyoming | Wind | RCP8.5 | 2070 | 86.9853 | 94.2664 | 102.086 | 109.7614 | 117.4581
WyomingWind2075RCP8.5 | Wyoming | Wind | RCP8.5 | 2075 | 87.2896 | 94.6513 | 102.5743 | 110.3357 | 118.1216
WyomingWind2080RCP8.5 | Wyoming | Wind | RCP8.5 | 2080 | 87.5939 | 95.0362 | 103.0625 | 110.91 | 118.785
WyomingWind2085RCP8.5 | Wyoming | Wind | RCP8.5 | 2085 | 87.9331 | 95.4647 | 103.596 | 111.5327 | 119.5038
WyomingWind2090RCP8.5 | Wyoming | Wind | RCP8.5 | 2090 | 88.2723 | 95.8932 | 104.1295 | 112.1555 | 120.2226
WyomingWind2095RCP8.5 | Wyoming | Wind | RCP8.5 | 2095 | 88.2723 | 95.8932 | 104.1295 | 112.1555 | 120.2226
WyomingWind2100RCP8.5 | Wyoming | Wind | RCP8.5 | 2100 | 88.2723 | 95.8932 | 104.1295 | 112.1555 | 120.2226
TBD
Climate inputs developed through the use of ECCC and CSA data. Use of this climate data is optional and links to to tab '3. Climate Severity Calculator'.

## Int VA Calcs
Risk Heatmap
|  | Location | Thedford
[7 empty] | Annual Event Probability Forecast | [19 empty] | Total Annual Probability Across Perils
|  | Asset Class | Sub Class | Climate Peril | Severity Threshold | 2023 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2055 | 2060 | 2065 | 2070 | 2075 | 2080 | 2085 | 2090 | 2095 | 2100 |  | Asset Class | Sub Class | 2023 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2055 | 2060 | 2065 | 2070 | 2075 | 2080 | 2085 | 2090 | 2095 | 2100 | Unique Asset List | Class List | Sub Class List
ThedfordPoleClass 5 | ThedfordWind80 | Pole | Class 5 | Wind | 80 | 0.11607 | 0.1166 | 0.11712 | 0.11765 | 0.11782 | 0.11798 | 0.11876 | 0.11937 | 0.12087 | 0.12176 | 0.12344 | 0.12423 | 0.12502 | 0.12606 | 0.1271 | 0.1271 | 0.1271 | ThedfordPoleClass 5 | Pole | Class 5 | 11.61% | 11.66% | 11.71% | 11.77% | 11.78% | 11.8% | 11.88% | 11.94% | 12.09% | 12.18% | 12.34% | 12.42% | 12.5% | 12.61% | 12.71% | 12.71% | 12.71% | Pole-Class 5 | Pole | Class 5
ThedfordPoleClass 4 | ThedfordWind85 | Pole | Class 4 | Wind | 85 | 0.10145 | 0.10194 | 0.10243 | 0.10292 | 0.10308 | 0.10323 | 0.10395 | 0.10452 | 0.10592 | 0.10675 | 0.10831 | 0.10905 | 0.10978 | 0.11075 | 0.11173 | 0.11173 | 0.11173 | ThedfordPoleClass 4 | Pole | Class 4 | 10.15% | 10.19% | 10.24% | 10.29% | 10.31% | 10.32% | 10.4% | 10.45% | 10.59% | 10.67% | 10.83% | 10.9% | 10.98% | 11.08% | 11.17% | 11.17% | 11.17% | Pole-Class 4 | Pole | Class 4
ThedfordPoleClass 3 | ThedfordWind100 | Pole | Class 3 | Wind | 100 | 0.018976 | 0.019562 | 0.020204 | 0.020995 | 0.021223 | 0.021452 | 0.02265 | 0.023636 | 0.02589 | 0.027176 | 0.029906 | 0.031338 | 0.032797 | 0.034672 | 0.036595 | 0.036595 | 0.036595 | ThedfordPoleClass 3 | Pole | Class 3 | 1.898% | 1.956% | 2.02% | 2.1% | 2.122% | 2.145% | 2.265% | 2.364% | 2.589% | 2.718% | 2.991% | 3.134% | 3.28% | 3.467% | 3.659% | 3.659% | 3.659% | Pole-Class 3 | Pole | Class 3
ThedfordPoleClass 2 | ThedfordWind115 | Pole | Class 2 | Wind | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ThedfordPoleClass 2 | Pole | Class 2 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Pole-Class 2 | Pole | Class 2

## Revenue Requirement Calculation
GLOBAL ASSUMPTIONS |  |  | Baseline Customer Revenue Requirement Multiplier |  |  |  | Scenario Customer Revenue Requirement Multiplier
|  |  | Asset Lifetime | 40 |  | Customer PV of Revenue Requirement for a $1 Investment | Asset Lifetime | 40 |  | Customer PV of Revenue Requirement for a $1 Investment
Asset Capital Cost | 1 |  | Depreciation | 2.5% |  | 1.4824 | Depreciation | 2.5% |  | 1.4824
|  |  |  | Opening Book Value | Nominal Revenue Requirement by Year | Present Value of Revenue Requirement in Year 1 Constant Dollars |  | Opening Book Value | Nominal Revenue Requirement by Year | Present Value of Revenue Requirement in Year 1 Constant Dollars
|  |  | Year |  |  |  | Year
Per IESO Guide for NWAs |  |  | 1 | 1 | 0.11 | 0.11 | 1 | 1 | 0.11 | 0.11
IESO_NWA_Guide_Regional_Planning |  |  | 2 | 0.975 | 0.10855 | 0.10241 | 2 | 0.975 | 0.10855 | 0.10241
Inflation Rate | 2% |  | 3 | 0.95 | 0.10711 | 0.095324 | 3 | 0.95 | 0.10711 | 0.095324
Social Discount Rate | 4% |  | 4 | 0.925 | 0.10567 | 0.088721 | 4 | 0.925 | 0.10567 | 0.088721
Pre-tax WACC | 7% |  | 5 | 0.9 | 0.10424 | 0.082565 | 5 | 0.9 | 0.10424 | 0.082565
|  |  | 6 | 0.875 | 0.10281 | 0.076827 | 6 | 0.875 | 0.10281 | 0.076827
|  |  | 7 | 0.85 | 0.10139 | 0.071478 | 7 | 0.85 | 0.10139 | 0.071478
OEB Cost of Capital Parameters |  |  | 8 | 0.825 | 0.09998 | 0.066493 | 8 | 0.825 | 0.09998 | 0.066493
|  |  | 9 | 0.8 | 0.098575 | 0.061847 | 9 | 0.8 | 0.098575 | 0.061847
Other Assumptions |  |  | 10 | 0.775 | 0.097176 | 0.057519 | 10 | 0.775 | 0.097176 | 0.057519
Tax Rate | 26.5% | 15% federal and 11.5% provincial | 11 | 0.75 | 0.095785 | 0.053486 | 11 | 0.75 | 0.095785 | 0.053486
Base OM&A Costs | 1.5% |  | 12 | 0.725 | 0.094401 | 0.049729 | 12 | 0.725 | 0.094401 | 0.049729
Scenario OM&A Costs | 1.5% |  | 13 | 0.7 | 0.093024 | 0.04623 | 13 | 0.7 | 0.093024 | 0.04623
|  |  | 14 | 0.675 | 0.091654 | 0.042971 | 14 | 0.675 | 0.091654 | 0.042971
Federal Tax Rate |  |  | 15 | 0.65 | 0.090292 | 0.039936 | 15 | 0.65 | 0.090292 | 0.039936
Provincial Tax Rate |  |  | 16 | 0.625 | 0.088938 | 0.037111 | 16 | 0.625 | 0.088938 | 0.037111
|  |  | 17 | 0.6 | 0.087592 | 0.03448 | 17 | 0.6 | 0.087592 | 0.03448
|  |  | 18 | 0.575 | 0.086254 | 0.032032 | 18 | 0.575 | 0.086254 | 0.032032
|  |  | 19 | 0.55 | 0.084924 | 0.029752 | 19 | 0.55 | 0.084924 | 0.029752
|  |  | 20 | 0.525 | 0.083602 | 0.027632 | 20 | 0.525 | 0.083602 | 0.027632
|  |  | 21 | 0.5 | 0.082289 | 0.025658 | 21 | 0.5 | 0.082289 | 0.025658
|  |  | 22 | 0.475 | 0.080985 | 0.023822 | 22 | 0.475 | 0.080985 | 0.023822
|  |  | 23 | 0.45 | 0.07969 | 0.022114 | 23 | 0.45 | 0.07969 | 0.022114
|  |  | 24 | 0.425 | 0.078403 | 0.020526 | 24 | 0.425 | 0.078403 | 0.020526
|  |  | 25 | 0.4 | 0.077127 | 0.019049 | 25 | 0.4 | 0.077127 | 0.019049
|  |  | 26 | 0.375 | 0.075859 | 0.017675 | 26 | 0.375 | 0.075859 | 0.017675
|  |  | 27 | 0.35 | 0.074601 | 0.016398 | 27 | 0.35 | 0.074601 | 0.016398
|  |  | 28 | 0.325 | 0.073353 | 0.015211 | 28 | 0.325 | 0.073353 | 0.015211
|  |  | 29 | 0.3 | 0.072115 | 0.014108 | 29 | 0.3 | 0.072115 | 0.014108
|  |  | 30 | 0.275 | 0.070888 | 0.013083 | 30 | 0.275 | 0.070888 | 0.013083
|  |  | 31 | 0.25 | 0.06967 | 0.01213 | 31 | 0.25 | 0.06967 | 0.01213
|  |  | 32 | 0.225 | 0.068464 | 0.011246 | 32 | 0.225 | 0.068464 | 0.011246
|  |  | 33 | 0.2 | 0.067268 | 0.010424 | 33 | 0.2 | 0.067268 | 0.010424
|  |  | 34 | 0.175 | 0.066083 | 0.0096605 | 34 | 0.175 | 0.066083 | 0.0096605
|  |  | 35 | 0.15 | 0.06491 | 0.0089519 | 35 | 0.15 | 0.06491 | 0.0089519
|  |  | 36 | 0.125 | 0.063748 | 0.008294 | 36 | 0.125 | 0.063748 | 0.008294
|  |  | 37 | 0.1 | 0.062598 | 0.0076834 | 37 | 0.1 | 0.062598 | 0.0076834
|  |  | 38 | 0.075 | 0.06146 | 0.0071167 | 38 | 0.075 | 0.06146 | 0.0071167
|  |  | 39 | 0.05 | 0.060334 | 0.0065909 | 39 | 0.05 | 0.060334 | 0.0065909
|  |  | 40 | 0.025 | 0.059221 | 0.0061031 | 40 | 0.025 | 0.059221 | 0.0061031
|  |  | 41 | 0 | 0 | 0 | 41 | 0 | 0 | 0
|  |  | 42 | 0 | 0 | 0 | 42 | 0 | 0 | 0
|  |  | 43 | 0 | 0 | 0 | 43 | 0 | 0 | 0
|  |  | 44 | 0 | 0 | 0 | 44 | 0 | 0 | 0
|  |  | 45 | 0 | 0 | 0 | 45 | 0 | 0 | 0
|  |  | 46 | 0 | 0 | 0 | 46 | 0 | 0 | 0
|  |  | 47 | 0 | 0 | 0 | 47 | 0 | 0 | 0
|  |  | 48 | 0 | 0 | 0 | 48 | 0 | 0 | 0
|  |  | 49 | 0 | 0 | 0 | 49 | 0 | 0 | 0
|  |  | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0
|  |  | 51 | 0 | 0 | 0 | 51 | 0 | 0 | 0
|  |  | 52 | 0 | 0 | 0 | 52 | 0 | 0 | 0
|  |  | 53 | 0 | 0 | 0 | 53 | 0 | 0 | 0
|  |  | 54 | 0 | 0 | 0 | 54 | 0 | 0 | 0
|  |  | 55 | 0 | 0 | 0 | 55 | 0 | 0 | 0
|  |  | 56 | 0 | 0 | 0 | 56 | 0 | 0 | 0
|  |  | 57 | 0 | 0 | 0 | 57 | 0 | 0 | 0
|  |  | 58 | 0 | 0 | 0 | 58 | 0 | 0 | 0
|  |  | 59 | 0 | 0 | 0 | 59 | 0 | 0 | 0
|  |  | 60 | 0 | 0 | 0 | 60 | 0 | 0 | 0
|  |  | 61 | 0 | 0 | 0 | 61 | 0 | 0 | 0
|  |  | 62 | 0 | 0 | 0 | 62 | 0 | 0 | 0
|  |  | 63 | 0 | 0 | 0 | 63 | 0 | 0 | 0
|  |  | 64 | 0 | 0 | 0 | 64 | 0 | 0 | 0
|  |  | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0
|  |  | 66 | 0 | 0 | 0 | 66 | 0 | 0 | 0
|  |  | 67 | 0 | 0 | 0 | 67 | 0 | 0 | 0
|  |  | 68 | 0 | 0 | 0 | 68 | 0 | 0 | 0
|  |  | 69 | 0 | 0 | 0 | 69 | 0 | 0 | 0
|  |  | 70 | 0 | 0 | 0 | 70 | 0 | 0 | 0
|  |  | 71 | 0 | 0 | 0 | 71 | 0 | 0 | 0
|  |  | 72 | 0 | 0 | 0 | 72 | 0 | 0 | 0
|  |  | 73 | 0 | 0 | 0 | 73 | 0 | 0 | 0
|  |  | 74 | 0 | 0 | 0 | 74 | 0 | 0 | 0
|  |  | 75 | 0 | 0 | 0 | 75 | 0 | 0 | 0
|  |  | 76 | 0 | 0 | 0 | 76 | 0 | 0 | 0
|  |  | 77 | 0 | 0 | 0 | 77 | 0 | 0 | 0
|  |  | 78 | 0 | 0 | 0 | 78 | 0 | 0 | 0
|  |  | 79 | 0 | 0 | 0 | 79 | 0 | 0 | 0
|  |  | 80 | 0 | 0 | 0 | 80 | 0 | 0 | 0
|  |  | 81 | 0 | 0 | 0 | 81 | 0 | 0 | 0
|  |  | 82 | 0 | 0 | 0 | 82 | 0 | 0 | 0
|  |  | 83 | 0 | 0 | 0 | 83 | 0 | 0 | 0
|  |  | 84 | 0 | 0 | 0 | 84 | 0 | 0 | 0
|  |  | 85 | 0 | 0 | 0 | 85 | 0 | 0 | 0
|  |  | 86 | 0 | 0 | 0 | 86 | 0 | 0 | 0
|  |  | 87 | 0 | 0 | 0 | 87 | 0 | 0 | 0
|  |  | 88 | 0 | 0 | 0 | 88 | 0 | 0 | 0
|  |  | 89 | 0 | 0 | 0 | 89 | 0 | 0 | 0
|  |  | 90 | 0 | 0 | 0 | 90 | 0 | 0 | 0
|  |  | 91 | 0 | 0 | 0 | 91 | 0 | 0 | 0
|  |  | 92 | 0 | 0 | 0 | 92 | 0 | 0 | 0
|  |  | 93 | 0 | 0 | 0 | 93 | 0 | 0 | 0
|  |  | 94 | 0 | 0 | 0 | 94 | 0 | 0 | 0
|  |  | 95 | 0 | 0 | 0 | 95 | 0 | 0 | 0
|  |  | 96 | 0 | 0 | 0 | 96 | 0 | 0 | 0
|  |  | 97 | 0 | 0 | 0 | 97 | 0 | 0 | 0
|  |  | 98 | 0 | 0 | 0 | 98 | 0 | 0 | 0
|  |  | 99 | 0 | 0 | 0 | 99 | 0 | 0 | 0
|  |  | 100 | 0 | 0 | 0 | 100 | 0 | 0 | 0
|  |  | 101 |  |  |  | 101
Calculates the baseline and scenario utility cost to PV customer cost multiplier. This value is applied to utility investment spending to estimate the PV of lifetime customer rate impacts from the investment. The multiplier considers OM&A changes from the investment as well as tax, WACC, and project lifetime. This multiplier aligns the VASH BCA methodology with the DST to allow for consistent evaluation of customer benefits from resiliency investments.

## Int BCA Costs
Early Retirement Cost Adjustment
Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101
Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 4 | -652247.502 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | -36201.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
For early retirement projects, the BCA cost is adjusted to account for what would have occurred in the absence of the resiliency investment. The assumption is that the LDC would have replaced the existing assets with standard assets after the RUL period is over. This tab calculates the credit that should be applied to the full upfront cost of the replacement assets (in customer revenue requirement) to account for the avoided future investment at the end of the RUL period.

## Int BCA Ann Fail Prob
Asset Class Annual Probability of Failure Uncalibrated | [79 empty] | Asset Class Annual Probability of Failure Calibrated | [79 empty] | Total Existing Asset Class Annual Probability of Failure Calibrated | [79 empty] | Total Replacement Asset Class Annual Probability of Failure Calibrated | [79 empty] | Total Standard Asset Class Annual Probability of Failure Calibrated
Asset Class | Asset Sub-Class | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | Asset Class | Asset Sub-Class | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | Asset Class | Asset Sub-Class | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | Asset Class | Asset Sub-Class | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | Asset Class | Asset Sub-Class | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100
Pole | Class 5 | 0.11607 | 0.11633 | 0.1166 | 0.1167 | 0.11681 | 0.11691 | 0.11702 | 0.11712 | 0.11723 | 0.11733 | 0.11744 | 0.11755 | 0.11765 | 0.11768 | 0.11772 | 0.11775 | 0.11778 | 0.11782 | 0.11785 | 0.11788 | 0.11792 | 0.11795 | 0.11798 | 0.11814 | 0.11829 | 0.11845 | 0.1186 | 0.11876 | 0.11888 | 0.119 | 0.11912 | 0.11925 | 0.11937 | 0.11967 | 0.11997 | 0.12027 | 0.12057 | 0.12087 | 0.12105 | 0.12123 | 0.12141 | 0.12159 | 0.12176 | 0.1221 | 0.12244 | 0.12277 | 0.12311 | 0.12344 | 0.1236 | 0.12376 | 0.12391 | 0.12407 | 0.12423 | 0.12439 | 0.12454 | 0.1247 | 0.12486 | 0.12502 | 0.12522 | 0.12543 | 0.12564 | 0.12585 | 0.12606 | 0.12627 | 0.12648 | 0.12668 | 0.12689 | 0.1271 | 0.1271 | 0.1271 | 0.1271 | 0.1271 | 0.1271 | 0.1271 | 0.1271 | 0.1271 | 0.1271 | 0.1271 | Pole | Class 5 | 0.025049 | 0.025106 | 0.025163 | 0.025185 | 0.025208 | 0.025231 | 0.025254 | 0.025276 | 0.025299 | 0.025322 | 0.025345 | 0.025368 | 0.02539 | 0.025398 | 0.025405 | 0.025412 | 0.025419 | 0.025426 | 0.025433 | 0.02544 | 0.025447 | 0.025455 | 0.025462 | 0.025495 | 0.025529 | 0.025562 | 0.025596 | 0.025629 | 0.025655 | 0.025682 | 0.025708 | 0.025735 | 0.025761 | 0.025826 | 0.025891 | 0.025956 | 0.026021 | 0.026085 | 0.026124 | 0.026162 | 0.026201 | 0.02624 | 0.026278 | 0.026351 | 0.026423 | 0.026495 | 0.026568 | 0.02664 | 0.026674 | 0.026708 | 0.026742 | 0.026776 | 0.02681 | 0.026844 | 0.026878 | 0.026912 | 0.026946 | 0.02698 | 0.027025 | 0.02707 | 0.027115 | 0.02716 | 0.027205 | 0.02725 | 0.027295 | 0.02734 | 0.027385 | 0.02743 | 0.02743 | 0.02743 | 0.02743 | 0.02743 | 0.02743 | 0.02743 | 0.02743 | 0.02743 | 0.02743 | 0.02743 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 4 | 0.10145 | 0.1017 | 0.10194 | 0.10204 | 0.10214 | 0.10224 | 0.10233 | 0.10243 | 0.10253 | 0.10263 | 0.10273 | 0.10282 | 0.10292 | 0.10295 | 0.10298 | 0.10301 | 0.10304 | 0.10308 | 0.10311 | 0.10314 | 0.10317 | 0.1032 | 0.10323 | 0.10337 | 0.10352 | 0.10366 | 0.10381 | 0.10395 | 0.10406 | 0.10418 | 0.10429 | 0.10441 | 0.10452 | 0.1048 | 0.10508 | 0.10536 | 0.10564 | 0.10592 | 0.10608 | 0.10625 | 0.10642 | 0.10658 | 0.10675 | 0.10706 | 0.10738 | 0.10769 | 0.108 | 0.10831 | 0.10846 | 0.10861 | 0.10875 | 0.1089 | 0.10905 | 0.10919 | 0.10934 | 0.10949 | 0.10963 | 0.10978 | 0.10997 | 0.11017 | 0.11036 | 0.11056 | 0.11075 | 0.11095 | 0.11114 | 0.11134 | 0.11153 | 0.11173 | 0.11173 | 0.11173 | 0.11173 | 0.11173 | 0.11173 | 0.11173 | 0.11173 | 0.11173 | 0.11173 | 0.11173 | Pole | Class 4 | 0.021894 | 0.021947 | 0.022 | 0.022021 | 0.022042 | 0.022063 | 0.022085 | 0.022106 | 0.022127 | 0.022148 | 0.022169 | 0.022191 | 0.022212 | 0.022218 | 0.022225 | 0.022232 | 0.022238 | 0.022245 | 0.022251 | 0.022258 | 0.022265 | 0.022271 | 0.022278 | 0.022309 | 0.02234 | 0.022371 | 0.022402 | 0.022434 | 0.022458 | 0.022483 | 0.022507 | 0.022532 | 0.022556 | 0.022617 | 0.022677 | 0.022737 | 0.022798 | 0.022858 | 0.022894 | 0.02293 | 0.022966 | 0.023002 | 0.023038 | 0.023105 | 0.023173 | 0.02324 | 0.023308 | 0.023375 | 0.023407 | 0.023439 | 0.02347 | 0.023502 | 0.023533 | 0.023565 | 0.023597 | 0.023628 | 0.02366 | 0.023692 | 0.023734 | 0.023776 | 0.023818 | 0.02386 | 0.023902 | 0.023944 | 0.023986 | 0.024028 | 0.02407 | 0.024112 | 0.024112 | 0.024112 | 0.024112 | 0.024112 | 0.024112 | 0.024112 | 0.024112 | 0.024112 | 0.024112 | 0.024112 | Pole | Class 4 | 2.1894 | 2.1947 | 2.2 | 2.2021 | 2.2042 | 2.2063 | 2.2085 | 2.2106 | 2.2127 | 2.2148 | 2.2169 | 2.2191 | 2.2212 | 2.2218 | 2.2225 | 2.2232 | 2.2238 | 2.2245 | 2.2251 | 2.2258 | 2.2265 | 2.2271 | 2.2278 | 2.2309 | 2.234 | 2.2371 | 2.2402 | 2.2434 | 2.2458 | 2.2483 | 2.2507 | 2.2532 | 2.2556 | 2.2617 | 2.2677 | 2.2737 | 2.2798 | 2.2858 | 2.2894 | 2.293 | 2.2966 | 2.3002 | 2.3038 | 2.3105 | 2.3173 | 2.324 | 2.3308 | 2.3375 | 2.3407 | 2.3439 | 2.347 | 2.3502 | 2.3533 | 2.3565 | 2.3597 | 2.3628 | 2.366 | 2.3692 | 2.3734 | 2.3776 | 2.3818 | 2.386 | 2.3902 | 2.3944 | 2.3986 | 2.4028 | 2.407 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | Pole | Class 4 | 2.1894 | 2.1947 | 2.2 | 2.2021 | 2.2042 | 2.2063 | 2.2085 | 2.2106 | 2.2127 | 2.2148 | 2.2169 | 2.2191 | 2.2212 | 2.2218 | 2.2225 | 2.2232 | 2.2238 | 2.2245 | 2.2251 | 2.2258 | 2.2265 | 2.2271 | 2.2278 | 2.2309 | 2.234 | 2.2371 | 2.2402 | 2.2434 | 2.2458 | 2.2483 | 2.2507 | 2.2532 | 2.2556 | 2.2617 | 2.2677 | 2.2737 | 2.2798 | 2.2858 | 2.2894 | 2.293 | 2.2966 | 2.3002 | 2.3038 | 2.3105 | 2.3173 | 2.324 | 2.3308 | 2.3375 | 2.3407 | 2.3439 | 2.347 | 2.3502 | 2.3533 | 2.3565 | 2.3597 | 2.3628 | 2.366 | 2.3692 | 2.3734 | 2.3776 | 2.3818 | 2.386 | 2.3902 | 2.3944 | 2.3986 | 2.4028 | 2.407 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | Pole | Class 4 | 2.1894 | 2.1947 | 2.2 | 2.2021 | 2.2042 | 2.2063 | 2.2085 | 2.2106 | 2.2127 | 2.2148 | 2.2169 | 2.2191 | 2.2212 | 2.2218 | 2.2225 | 2.2232 | 2.2238 | 2.2245 | 2.2251 | 2.2258 | 2.2265 | 2.2271 | 2.2278 | 2.2309 | 2.234 | 2.2371 | 2.2402 | 2.2434 | 2.2458 | 2.2483 | 2.2507 | 2.2532 | 2.2556 | 2.2617 | 2.2677 | 2.2737 | 2.2798 | 2.2858 | 2.2894 | 2.293 | 2.2966 | 2.3002 | 2.3038 | 2.3105 | 2.3173 | 2.324 | 2.3308 | 2.3375 | 2.3407 | 2.3439 | 2.347 | 2.3502 | 2.3533 | 2.3565 | 2.3597 | 2.3628 | 2.366 | 2.3692 | 2.3734 | 2.3776 | 2.3818 | 2.386 | 2.3902 | 2.3944 | 2.3986 | 2.4028 | 2.407 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112 | 2.4112
Pole | Class 3 | 0.018976 | 0.019269 | 0.019562 | 0.01969 | 0.019819 | 0.019947 | 0.020075 | 0.020204 | 0.020362 | 0.02052 | 0.020679 | 0.020837 | 0.020995 | 0.021041 | 0.021086 | 0.021132 | 0.021177 | 0.021223 | 0.021269 | 0.021315 | 0.021361 | 0.021406 | 0.021452 | 0.021692 | 0.021931 | 0.022171 | 0.02241 | 0.02265 | 0.022847 | 0.023044 | 0.023242 | 0.023439 | 0.023636 | 0.024087 | 0.024538 | 0.024988 | 0.025439 | 0.02589 | 0.026147 | 0.026404 | 0.026662 | 0.026919 | 0.027176 | 0.027722 | 0.028268 | 0.028814 | 0.02936 | 0.029906 | 0.030193 | 0.030479 | 0.030765 | 0.031052 | 0.031338 | 0.03163 | 0.031922 | 0.032213 | 0.032505 | 0.032797 | 0.033172 | 0.033547 | 0.033922 | 0.034297 | 0.034672 | 0.035056 | 0.035441 | 0.035826 | 0.03621 | 0.036595 | 0.036595 | 0.036595 | 0.036595 | 0.036595 | 0.036595 | 0.036595 | 0.036595 | 0.036595 | 0.036595 | 0.036595 | Pole | Class 3 | 0.0040952 | 0.0041585 | 0.0042217 | 0.0042494 | 0.0042771 | 0.0043048 | 0.0043325 | 0.0043602 | 0.0043943 | 0.0044285 | 0.0044626 | 0.0044968 | 0.0045309 | 0.0045408 | 0.0045506 | 0.0045605 | 0.0045703 | 0.0045801 | 0.00459 | 0.0045999 | 0.0046098 | 0.0046197 | 0.0046296 | 0.0046813 | 0.004733 | 0.0047847 | 0.0048364 | 0.0048881 | 0.0049306 | 0.0049732 | 0.0050158 | 0.0050584 | 0.005101 | 0.0051982 | 0.0052955 | 0.0053928 | 0.00549 | 0.0055873 | 0.0056428 | 0.0056983 | 0.0057539 | 0.0058094 | 0.0058649 | 0.0059827 | 0.0061006 | 0.0062184 | 0.0063362 | 0.0064541 | 0.0065159 | 0.0065777 | 0.0066395 | 0.0067013 | 0.0067631 | 0.0068261 | 0.006889 | 0.006952 | 0.007015 | 0.0070779 | 0.0071588 | 0.0072398 | 0.0073207 | 0.0074016 | 0.0074825 | 0.0075655 | 0.0076485 | 0.0077316 | 0.0078146 | 0.0078976 | 0.0078976 | 0.0078976 | 0.0078976 | 0.0078976 | 0.0078976 | 0.0078976 | 0.0078976 | 0.0078976 | 0.0078976 | 0.0078976 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Climate data given in 5-year increments in linearly interpolated to provide annual probability of failures at the asset sub-class level. These failure probabilities are calibrated using the calibration multiplier derived on the Calibration tab and then scaled to the asset counts by sub-class for the existing, standard, and replacement cases. These are used to scale VOLL benefits calibrated to annual expected outage counts.

## Int BCA Ann Fail Costs
Asset Class Annual Failure Repair and Replace Cost
Asset Class | Asset Sub-Class | Unit Basis | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100
Pole | Class 5 | pole | 2240.2922 | 2245.098 | 2250 | 2255 | 2260.1 | 2265.302 | 2270.608 | 2276.0202 | 2281.5406 | 2287.1714 | 2292.9148 | 2298.7731 | 2304.7486 | 2310.8436 | 2317.0604 | 2323.4017 | 2329.8697 | 2336.4671 | 2343.1964 | 2350.0604 | 2357.0616 | 2364.2028 | 2371.4868 | 2378.9166 | 2386.4949 | 2394.2248 | 2402.1093 | 2410.1515 | 2418.3545 | 2426.7216 | 2435.2561 | 2443.9612 | 2452.8404 | 2461.8972 | 2471.1351 | 2480.5579 | 2490.169 | 2499.9724 | 2509.9718 | 2520.1713 | 2530.5747 | 2541.1862 | 2552.0099 | 2563.0501 | 2574.3111 | 2585.7973 | 2597.5133 | 2609.4636 | 2621.6528 | 2634.0859 | 2646.7676 | 2659.7029 | 2672.897 | 2686.3549 | 2700.082 | 2714.0837 | 2728.3654 | 2742.9327 | 2757.7913 | 2772.9471 | 2788.4061 | 2804.1742 | 2820.2577 | 2836.6629 | 2853.3961 | 2870.464 | 2887.8733 | 2905.6308 | 2923.7434 | 2942.2183 | 2961.0626 | 2980.2839 | 2999.8896 | 3019.8873 | 3040.2851 | 3061.0908 | 3082.3126 | 3103.9589
Pole | Class 4 | pole | 2440.2922 | 2445.098 | 2450 | 2455 | 2460.1 | 2465.302 | 2470.608 | 2476.0202 | 2481.5406 | 2487.1714 | 2492.9148 | 2498.7731 | 2504.7486 | 2510.8436 | 2517.0604 | 2523.4017 | 2529.8697 | 2536.4671 | 2543.1964 | 2550.0604 | 2557.0616 | 2564.2028 | 2571.4868 | 2578.9166 | 2586.4949 | 2594.2248 | 2602.1093 | 2610.1515 | 2618.3545 | 2626.7216 | 2635.2561 | 2643.9612 | 2652.8404 | 2661.8972 | 2671.1351 | 2680.5579 | 2690.169 | 2699.9724 | 2709.9718 | 2720.1713 | 2730.5747 | 2741.1862 | 2752.0099 | 2763.0501 | 2774.3111 | 2785.7973 | 2797.5133 | 2809.4636 | 2821.6528 | 2834.0859 | 2846.7676 | 2859.7029 | 2872.897 | 2886.3549 | 2900.082 | 2914.0837 | 2928.3654 | 2942.9327 | 2957.7913 | 2972.9471 | 2988.4061 | 3004.1742 | 3020.2577 | 3036.6629 | 3053.3961 | 3070.464 | 3087.8733 | 3105.6308 | 3123.7434 | 3142.2183 | 3161.0626 | 3180.2839 | 3199.8896 | 3219.8873 | 3240.2851 | 3261.0908 | 3282.3126 | 3303.9589
Pole | Class 3 | pole | 2660.2922 | 2665.098 | 2670 | 2675 | 2680.1 | 2685.302 | 2690.608 | 2696.0202 | 2701.5406 | 2707.1714 | 2712.9148 | 2718.7731 | 2724.7486 | 2730.8436 | 2737.0604 | 2743.4017 | 2749.8697 | 2756.4671 | 2763.1964 | 2770.0604 | 2777.0616 | 2784.2028 | 2791.4868 | 2798.9166 | 2806.4949 | 2814.2248 | 2822.1093 | 2830.1515 | 2838.3545 | 2846.7216 | 2855.2561 | 2863.9612 | 2872.8404 | 2881.8972 | 2891.1351 | 2900.5579 | 2910.169 | 2919.9724 | 2929.9718 | 2940.1713 | 2950.5747 | 2961.1862 | 2972.0099 | 2983.0501 | 2994.3111 | 3005.7973 | 3017.5133 | 3029.4636 | 3041.6528 | 3054.0859 | 3066.7676 | 3079.7029 | 3092.897 | 3106.3549 | 3120.082 | 3134.0837 | 3148.3654 | 3162.9327 | 3177.7913 | 3192.9471 | 3208.4061 | 3224.1742 | 3240.2577 | 3256.6629 | 3273.3961 | 3290.464 | 3307.8733 | 3325.6308 | 3343.7434 | 3362.2183 | 3381.0626 | 3400.2839 | 3419.8896 | 3439.8873 | 3460.2851 | 3481.0908 | 3502.3126 | 3523.9589
Pole | Class 2 | pole | 2902.2922 | 2907.098 | 2912 | 2917 | 2922.1 | 2927.302 | 2932.608 | 2938.0202 | 2943.5406 | 2949.1714 | 2954.9148 | 2960.7731 | 2966.7486 | 2972.8436 | 2979.0604 | 2985.4017 | 2991.8697 | 2998.4671 | 3005.1964 | 3012.0604 | 3019.0616 | 3026.2028 | 3033.4868 | 3040.9166 | 3048.4949 | 3056.2248 | 3064.1093 | 3072.1515 | 3080.3545 | 3088.7216 | 3097.2561 | 3105.9612 | 3114.8404 | 3123.8972 | 3133.1351 | 3142.5579 | 3152.169 | 3161.9724 | 3171.9718 | 3182.1713 | 3192.5747 | 3203.1862 | 3214.0099 | 3225.0501 | 3236.3111 | 3247.7973 | 3259.5133 | 3271.4636 | 3283.6528 | 3296.0859 | 3308.7676 | 3321.7029 | 3334.897 | 3348.3549 | 3362.082 | 3376.0837 | 3390.3654 | 3404.9327 | 3419.7913 | 3434.9471 | 3450.4061 | 3466.1742 | 3482.2577 | 3498.6629 | 3515.3961 | 3532.464 | 3549.8733 | 3567.6308 | 3585.7434 | 3604.2183 | 3623.0626 | 3642.2839 | 3661.8896 | 3681.8873 | 3702.2851 | 3723.0908 | 3744.3126 | 3765.9589
Expected annual avoided asset damages cost are the weighted repair and replacement costs from tab '6. Generic BCA Inputs'. This tab calculates the per unit weighted value for a single failure.

## Int BCA Ann PWFC
Asset Class Annual Probability Weighted Failure Repair and Replace Cost | [78 empty] | Baseline Asset Class Annual Probability Weighted Failure Repair and Replace Cost | [78 empty] | Replacement Asset Class Annual Probability Weighted Failure Repair and Replace Cost
Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101
Pole | Class 5 | 3908.8427 | 263.1611 | 263.9949 | 264.8417 | 265.7017 | 266.5753 | 267.4627 | 268.3643 | 269.2804 | 270.2111 | 271.1569 | 271.9502 | 272.7583 | 273.5815 | 274.42 | 275.2741 | 276.1443 | 277.0308 | 277.9339 | 278.854 | 279.7914 | 281.0371 | 282.3027 | 283.5886 | 284.8953 | 286.2231 | 287.4928 | 288.784 | 290.0972 | 291.4329 | 292.7914 | 294.6128 | 296.4614 | 298.3377 | 300.2425 | 302.1762 | 303.833 | 305.5176 | 307.2306 | 308.9726 | 310.7442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 4 | 3713.7118 | 250.5065 | 251.2682 | 252.0413 | 252.826 | 253.6227 | 254.4317 | 255.2531 | 256.0872 | 256.9342 | 257.7944 | 258.4987 | 259.216 | 259.9465 | 260.6904 | 261.448 | 262.2197 | 263.0056 | 263.8062 | 264.6216 | 265.4522 | 266.5913 | 267.7479 | 268.9224 | 270.1151 | 271.3266 | 272.4769 | 273.6462 | 274.8348 | 276.0432 | 277.2718 | 278.9634 | 280.6791 | 282.4194 | 284.1849 | 285.9761 | 287.4858 | 289.0201 | 290.5794 | 292.1644 | 293.7756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 550513.4688 | 37134.597 | 37247.5064 | 37362.1099 | 37478.4429 | 37596.5416 | 37716.464 | 37838.2266 | 37961.8679 | 38087.4273 | 38214.9447 | 38319.3541 | 38425.68 | 38533.961 | 38644.2371 | 38756.5485 | 38870.9388 | 38987.4479 | 39106.119 | 39226.9958 | 39350.1231 | 39518.9759 | 39690.4267 | 39864.5308 | 40041.3445 | 40220.9254 | 40391.4487 | 40564.782 | 40740.9844 | 40920.1162 | 41102.2388 | 41352.9937 | 41607.3216 | 41865.3016 | 42127.0145 | 42392.543 | 42616.3371 | 42843.7741 | 43074.9317 | 43309.8896 | 43548.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 550513.4688 | 37134.597 | 37247.5064 | 37362.1099 | 37478.4429 | 37596.5416 | 37716.464 | 37838.2266 | 37961.8679 | 38087.4273 | 38214.9447 | 38319.3541 | 38425.68 | 38533.961 | 38644.2371 | 38756.5485 | 38870.9388 | 38987.4479 | 39106.119 | 39226.9958 | 39350.1231 | 39518.9759 | 39690.4267 | 39864.5308 | 40041.3445 | 40220.9254 | 40391.4487 | 40564.782 | 40740.9844 | 40920.1162 | 41102.2388 | 41352.9937 | 41607.3216 | 41865.3016 | 42127.0145 | 42392.543 | 42616.3371 | 42843.7741 | 43074.9317 | 43309.8896 | 43548.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 3 | 831.6133 | 52.6717 | 53.1161 | 53.5639 | 54.0151 | 54.4698 | 55.0088 | 55.5519 | 56.099 | 56.6504 | 57.2061 | 57.4586 | 57.7142 | 57.973 | 58.235 | 58.5004 | 58.7699 | 59.0429 | 59.3195 | 59.5997 | 59.8837 | 60.7134 | 61.55 | 62.3935 | 63.2443 | 64.1023 | 64.8482 | 65.6011 | 66.3612 | 67.1286 | 67.9036 | 69.4164 | 70.9419 | 72.4803 | 74.0319 | 75.5972 | 76.61 | 77.6332 | 78.6671 | 79.7119 | 80.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Caclulates the probability weighted annual expected failure costs for repair/replacement of assets from climate peril projections. Scales to baseline scenario assets (existing for pre-RUL and standard for post-RUL) and replacement scenario asset counts by sub-class from tab '7. Project Characteristics'. Avoided repair and replace benefits are adjusted to represent avoided PV revenue requirement to align with BCA costs and the DST perspective.

## Int BCA Ann PWVOLL
Baseline Scenario Asset Class Annual Probability Weighted VOLL (Per Event Method) - with Dual | [78 empty] | Replacement Scenario Asset Class Annual Probability Weighted VOLL (Per Event Method) | [78 empty] | Replacement Scenario Asset Class Annual Probability Weighted VOLL Criticality Reduction (Per Event Method)
Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | Asset Class | Asset Sub-Class | PV 2026$ | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101
Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 4 | 720852.7582 | 39552.2158 | 39590.2316 | 39628.2474 | 39666.2631 | 39704.2789 | 39742.317 | 39780.355 | 39818.3931 | 39856.4311 | 39894.4692 | 39906.3606 | 39918.252 | 39930.1434 | 39942.0348 | 39953.9261 | 39965.8197 | 39977.7132 | 39989.6067 | 40001.5002 | 40013.3937 | 40069.3212 | 40125.2488 | 40181.1763 | 40237.1039 | 40293.0314 | 40337.0914 | 40381.1513 | 40425.2113 | 40469.2713 | 40513.3313 | 40621.8104 | 40730.2895 | 40838.7686 | 40947.2478 | 41055.7269 | 41120.1738 | 41184.6207 | 41249.0676 | 41313.5145 | 41377.9614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 720852.7582 | 39552.2158 | 39590.2316 | 39628.2474 | 39666.2631 | 39704.2789 | 39742.317 | 39780.355 | 39818.3931 | 39856.4311 | 39894.4692 | 39906.3606 | 39918.252 | 39930.1434 | 39942.0348 | 39953.9261 | 39965.8197 | 39977.7132 | 39989.6067 | 40001.5002 | 40013.3937 | 40069.3212 | 40125.2488 | 40181.1763 | 40237.1039 | 40293.0314 | 40337.0914 | 40381.1513 | 40425.2113 | 40469.2713 | 40513.3313 | 40621.8104 | 40730.2895 | 40838.7686 | 40947.2478 | 41055.7269 | 41120.1738 | 41184.6207 | 41249.0676 | 41313.5145 | 41377.9614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 179320.2006 | 9839.0569 | 9848.5137 | 9857.9706 | 9867.4274 | 9876.8843 | 9886.3467 | 9895.809 | 9905.2714 | 9914.7338 | 9924.1962 | 9927.1543 | 9930.1125 | 9933.0706 | 9936.0287 | 9938.9868 | 9941.9454 | 9944.9041 | 9947.8627 | 9950.8214 | 9953.78 | 9967.6926 | 9981.6052 | 9995.5178 | 10009.4304 | 10023.343 | 10034.3034 | 10045.2639 | 10056.2243 | 10067.1847 | 10078.1451 | 10105.1305 | 10132.1159 | 10159.1013 | 10186.0867 | 10213.0721 | 10229.104 | 10245.1359 | 10261.1677 | 10277.1996 | 10293.2315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Calculates the expected value of last load (VOLL) to customers from resulting modeled and calibrated frequency of outages in the baseline and replacement scenarios. Annual outage event projections are taken from 'Int BCA Ann Fail Prob' for each scenario and includes dual baseline for the baseline scenario. The replacement scenario VOLL is calculated from remaining outage projections after hardening investments. The criticality VOLL is calculated from the remaining replacement scenario frequency and the updated per outage VOLL from '7. Project Characteristics'.

## Int BCA Ann CMI
Baseline Scenario Asset Class Annual CMI (Per Event Method) | [78 empty] | Scenario Asset Class Annual Probability Weighted CMI (Per Event Method)
Asset Class | Asset Sub-Class | Lifetime Total CMI Reduction | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | Asset Class | Asset Sub-Class | Lifetime Total CMI Reduction | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101
Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 4 | 1140418.4105 | 28010.9228 | 28037.8456 | 28064.7685 | 28091.6913 | 28118.6141 | 28145.5527 | 28172.4913 | 28199.4299 | 28226.3685 | 28253.3071 | 28261.7286 | 28270.1501 | 28278.5715 | 28286.993 | 28295.4145 | 28303.8375 | 28312.2605 | 28320.6835 | 28329.1065 | 28337.5295 | 28377.1375 | 28416.7454 | 28456.3534 | 28495.9613 | 28535.5692 | 28566.7726 | 28597.9759 | 28629.1792 | 28660.3825 | 28691.5859 | 28768.4109 | 28845.2359 | 28922.061 | 28998.886 | 29075.711 | 29121.3524 | 29166.9938 | 29212.6351 | 29258.2765 | 29303.9178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 4 | 806899.8187 | 19819.0492 | 19838.0983 | 19857.1475 | 19876.1967 | 19895.2458 | 19914.3062 | 19933.3665 | 19952.4268 | 19971.4871 | 19990.5474 | 19996.5061 | 20002.4647 | 20008.4233 | 20014.3819 | 20020.3405 | 20026.3001 | 20032.2598 | 20038.2195 | 20044.1791 | 20050.1388 | 20078.1633 | 20106.1878 | 20134.2123 | 20162.2368 | 20190.2613 | 20212.3391 | 20234.4169 | 20256.4947 | 20278.5726 | 20300.6504 | 20355.0077 | 20409.365 | 20463.7224 | 20518.0797 | 20572.4371 | 20604.7305 | 20637.0239 | 20669.3173 | 20701.6107 | 20733.9041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pole | Class 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Calculates the expected annual CMI from outages caused by climate perils modeled in the VASH Toolkit for the baseline and replacement scenarios. Modeled outage frequency from 'Int BCA Ann Fail Prob' are scaled to the number of customers and duration from '7. Project Characteristics'.