## Sheet 1
# | Region | Primary Project Code | Project Name | 2027-2031 CAPEX ($MM) | Project Grouping | System Need | Gate 0 - Portfolio Pre-screen | Gate 1 - Binary Screen | Gate 2 - Technical Feasibility | Gate 3 - BCA & engineering | Explanation
1 | Eastern York | 101489 | Markham TS#5 Feeder Integration - Part 1 | 17.4 | Markham TS#5 (Markham/Richmond Hill area) | System Integration: Integrate new Markham TS#5 into Alectra's distribution system. | N/A | N/A | N/A | N/A | - Combined with Project Group - Markham TS#5 (Markham/Richmond Hill area)
2 | Eastern York | 101490 | Markham TS#5 Feeder Integration - Phase 2 | 16.8 | Markham TS#5 (Markham/Richmond Hill area) | System Integration: Integrate new Markham TS#5 into Alectra's distribution system. | N/A | N/A | N/A | N/A | - Combined with Project Group - Markham TS#5 (Markham/Richmond Hill area)
3 | Eastern York | 100461 | New Barrie 20MVA Substation - 13.8kV Feeder Integration | 2 | Barrie MS | System Integration: Integrate new Barrie MS into Alectra's distribution system | N/A | N/A | N/A | N/A | - Combined with Project Group - Barrie MS
4 | Eastern York | 101571 | New Alliston 2 x 20MVA Substation - 13.8kV Feeder Integration | 1 | Alliston MS | System Integration: Integrate new Alliston MS into Alectra's distribution system | N/A | N/A | N/A | N/A | - Combined with Project Group - Alliston MS
5 | Eastern York | 152763 | VTS#5 Feeder Integration Part 1 | 11.1 | Vaughan MTS#5 (Vaughan area) | System Integration: Integrate new Vaughan VTS#5 into Alectra's distribution system. | N/A | N/A | N/A | N/A | - Combined with Project Group - Vaughan MTS#5 (Vaughan area)
6 | Eastern York | 100904 | Install Double Cct Pole Line on Major Mackenzie - Highway 27 to Huntington Rd | 3.2 |  | Backup/Supply: Provide redundancy for areas served by single circuits to prevent extended outages. | PASS | PASS | FAIL |  | - Need is for a physical loop (redundancy) to restore power during main feeder loss. NWS cannot provide the physical connectivity or indefinite backup required.
7 | Eastern York | 100917 | Add one additional 27.6kV Cct on 19th Ave from Bayview to Bathurst St | 2.4 |  | Intensification: Upgrade feeders to support increased density. | PASS | PASS | FAIL |  | - Project adds a physical circuit to an existing pole line to increase transfer capability. NWS cannot create a new physical path for load transfer.
8 | Eastern York | 150007 | Extend 153M10 to Transfer MS322 | 2.4 |  | Backup/Transfer: Provide load transfer capability to support the upgraded Melbourne MS322. | PASS | PASS | FAIL |  | - The need is for a physical tie-point to allow load transfer between stations. NWS cannot simulate a physical connection between two distinct electrical points.
9 | Eastern York | 100924 | Install two additional 27.6kV ccts on Highway 7 from Jane St to Weston Rd | 2.2 |  | Intensification: Support high density growth corridors. | PASS | PASS | FAIL |  | Physical circuits required to deliver firm capacity to intensified area.
10 | Eastern York | 152749 | Rebuild pole line on 19th Ave into 2 ccts from McCowan Rd to Highway 48 | 2 |  | Greenfield: Transfer station capacity to developing areas. | PASS | PASS | FAIL |  | - Physical rebuilding of line required to carry capacity.
11 | Eastern York | 103633 | Install Two 27.6kV Ccts on 16th Ave from Highway 404 to Woodbine Ave | 1.9 |  | Greenfield: Capacity transfer. | PASS | FAIL |  |  | - The project cost to address the system need is below the $2M threshold
12 | Eastern York | 100281 | Build Four 27.6kV Ccts on 19th Ave from Woodbine Ave to Warden Ave | 1.7 |  | Greenfield: Feeder capacity for FUA. | PASS | FAIL |  |  | - The project cost to address the system need is below the $2M threshold
13 | Eastern York | 152751 | Rebuild existing pole line on Nashville Rd into 2 ccts from Huntington Rdto Highway 50 | 1.6 |  | Greenfield: Extension into West Vaughan. | PASS | FAIL |  |  | - The project cost to address the system need is below the $2M threshold
14 | Eastern York | 100913 | Pole Line Installation Double Cct on Major Mack - Huntington Rd to Highway 50 | 1.5 |  | Greenfield: Support West Vaughan/Kleinburg. | PASS | FAIL |  |  | - The project cost to address the system need is below the $2M threshold
15 | Eastern York | 101487 | Add one Additional 27.6kV Cct on Major Mack Dr and 9th Line | 1.3 |  | Greenfield: Support Markham/Stouffville border. | PASS | FAIL |  |  | - The project cost to address the system need is below the $2M threshold
16 | Eastern York | 152757 | Rebuild existing pole line on Keele St into 2 ccts from Teston Rd to Kirby Sdrd | 1.2 |  | Greenfield: Extension to support forecast demand. | PASS | FAIL |  |  | - The project cost to address the system need is below the $2M threshold
17 | Eastern York | 102386 | Rebuild 44kV pole line into 2 Ccts on Tiffin Street from Ferndale Ave to Miller Drive | 1.2 |  | Intensification: Addressing load growth in Barrie. | PASS | FAIL |  |  | - The project cost to address the system need is below the $2M threshold
18 | Central South | 152893 | Feeder Integration Plan (I) - 27.6kV Lakeview TS - South Mississauga | 7.6 | Lakeview TS | Integrate new Lakeview TS into Alectra's distribution system. | N/A | N/A | N/A | N/A | - Combined with Project Group - Lakeview TS
19 | Central South | 152890 | Webb MS 20MVA Substation - Feeder Integration Plan (I) | 1.5 | Webb MS | Integrate new Webb MS into Alectra's distribution system | N/A | N/A | N/A | N/A | - Combined with Project Group - Webb MS
20 | Central South | 152967 | Webb MS 20MVA Substation - Feeder Integration Plan (II) | 1.3 | Webb MS | Integrate new Webb MS into Alectra's distribution system | N/A | N/A | N/A | N/A | - Combined with Project Group - Webb MS
21 | Central South | 150369 | New build – 44kV Feeder Extension York/Meadowpine, Mississauga | 2.1 |  | Backup Supply: Provide redundancy for areas served by single circuits. | PASS | PASS | FAIL |  | - Need is for N-1 physical backup path. NWS cannot provide network connectivity.
22 | Central North | 153068 | New 4 Feeders Common Elements - Goreway TS 2 | 15.2 | Goreway TS (Brampton) | Integrate new Goreway TS into Alectra's distribution system. | N/A | N/A | N/A | N/A | - Combined with Project Group - Goreway TS (Brampton)
23 | Central North | 152879 | Feeder 1 Integration - Goreway TS 2 | 7.1 | Goreway TS (Brampton) | Integrate new Goreway TS into Alectra's distribution system. | N/A | N/A | N/A | N/A | - Combined with Project Group - Goreway TS (Brampton)
24 | Central North | 152881 | Feeder 3 Integration - Goreway TS 2 | 2.4 | Goreway TS (Brampton) | Integrate new Goreway TS into Alectra's distribution system | N/A | N/A | N/A | N/A | - Combined with Project Group - Goreway TS (Brampton)
25 | Central North | 153111 | Feeder 2 integration 4xCct Ductbank - Goreway TS 2 | 1.2 | Goreway TS (Brampton) | Integrate new Goreway TS into Alectra's distribution system | N/A | N/A | N/A | N/A | - Combined with Project Group - Goreway TS (Brampton)
26 | Central North | 152882 | Feeder 4 Integration - Goreway TS 2 | 3.4 | Goreway TS (Brampton) | Integrate new Goreway TS into Alectra's distribution system | N/A | N/A | N/A | N/A | - Combined with Project Group - Goreway TS (Brampton)
27 | Central North | 153073 | 3 Feeder Integration out of Goreway TS 2 - Along Castlemore Road | 3.3 | Goreway TS (Brampton) | Integrate new Goreway TS into Alectra's distribution system | N/A | N/A | N/A | N/A | - Combined with Project Group - Goreway TS (Brampton)
28 | Central North | 152880 | Feeder 2 Integration - Goreway TS 2 | 3 | Goreway TS (Brampton) | Integrate new Goreway TS into Alectra's distribution system | N/A | N/A | N/A | N/A | - Combined with Project Group - Goreway TS (Brampton)
29 | Central North | 151676 | 136M10 Feeder Extension Goreway TS to Highway 410 | 8.4 |  | Intensification: Extend feeder from Goreway TS to Hwy 410 to support load growth. | PASS | PASS | FAIL |  | - Physical extension of the grid is required to serve the specific location of the intensification.
30 | Central North | 150716 | 42M69 Feeder Extension - Williams Pkwy to Heart Lake/Sandalwood | 8.9 |  | Intensification: Extend feeder to Williams Pkwy/Sandalwood to support 12MVA of new load where existing feeder is overloaded. | PASS | PASS | FAIL |  | - The project extends a feeder to reach a specific geographic location. NWS cannot bridge the physical distance to connect new loads that are far from existing capacity.
31 | West | 152865 | New Station - Hamilton South-West (Egress) | 10.4 | Hamilton TS | Integrate new Hamilton South-West station into Alectra's distribution system. | N/A | N/A | N/A | N/A | - Combined with Project Group - Hamilton TS
32 | West | 152853 | New Station - Newton TS (Feeder Consolidation) | 8 | Newton TS | Integrate new Newton TS into Alectra's distribution system. | N/A | N/A | N/A | N/A | - Combined with Project Group - Newton TS
33 | West | 152496 | New Build - Waterdown 4th Feeder, Hamilton | 8.8 |  | Backup/Redundancy: Install a 4th feeder to create a second physical routing (loop) for backup, preventing extended outages. | PASS | PASS | FAIL |  | - The need is for a physical N-1 backup path to restore power during a permanent fault. NWS cannot provide the indefinite duration or the network connectivity required to restore a radial outage.
34 | West | 152852 | New Build - Nebo 3101X Extension, Hamilton | 2.4 |  | Greenfield: Extension to transfer capacity to developing areas. | PASS | PASS | FAIL |  | - Physical extension required to reach new loads.
35 | West | 152854 | St. Catharines Downtown - Feeder Consolidation | 15.3 |  | Intensification/Condition: Upgrade existing 300A-rated 500MCM cables to 600A industry standard to support intensification and address undersized/aging assets. | PASS | PASS | FAIL |  | - The driver includes replacing non-standard, undersized assets that limit operational flexibility. NWS cannot resolve the physical obsolescence or condition of the underground cables.
36 | West | 150368 | New Build - Carlton TS to Linwell Rd/Lake St, St. Catharines | 2.1 |  | Intensification: Upgrades feeders to support load growth in St. Catharines urban centers. | PASS | PASS | FAIL |  | - Physical extension of the grid is required to serve the specific location of the intensification
37 | West | 152849 | New Build - Carlton TS to Martindale Rd/Port, St. Catharines | 2 |  | Intensification: Upgrades feeders to support load growth in St. Catharines urban centers. | PASS | PASS | FAIL |  | - Physical extension of the grid is required to serve the specific location of the intensification
38 | Southwest | 151238 | New Build - Maltby Rd W (Crawley to Gordon), Guelph | 1.3 |  | Greenfield: Connect Clair-Maltby developments. | PASS | FAIL |  |  | - The project cost to address the system need is below the $2M threshold
39 | Southwest | 152942 | New Build - Guelph Downtown | 5.9 |  | Intensification: Support downtown growth and greenfield in North-West Guelph where stations are reaching limits. | PASS | PASS | FAIL |  | - Requires physical connection to deliver capacity to the intensification area. NWS cannot create the connection.